## REPORT P1
CIRCUIT NUMBER | SUBSTATION NAME | SUBSTATION NUMBER | SUBSTATION COUNTY | SUBSTATION ROAD | SUBSTATION TOWN | CIRCUIT NAME | CIRCUIT ID | CIRCUIT NUMBER | CIRCUIT TOWN | CIRCUIT ROAD | CIRCUIT GENERAL AREA | TOTAL CIRCUIT LENGTH (miles) | CUSTOMER COUNT FOR THIS CIRCUIT | DATE OF LAST CIRCUIT TRIM (VEGETATION MANAGEMENT) | CIRCUIT 5-YEAR AVERAGE (SAIDI) | REPORTING YEAR (2020) SAIDI | DID SAIDI INCREASE IN 2020? | CIRCUIT 5-YEAR AVERAGE (SAIFI) | REPORTING YEAR (2020) SAIFI | DID SAIFI INCREASE IN 2020?
H9320090042 | KENTON | 9 | KENTON |  | LAKEVIEW | KENTON 42 | H9320090042 | 42 | TAYLOR MILL |  | Taylor Mill | 14.471 | 947 | 2016-05-11 | 205.108 | 129.9863 | NO | 1.1687 | 1.2492 | YES
H9320420042 | CONSTANCE | 42 | BOONE |  | ERLANGER | CONSTANCE 42 | H9320420042 | 42 | VILLA HILLS |  | Villa Hills | 45.321 | 1774 | 2016-03-28 | 133.3282 | 117.4336 | NO | 0.77328 | 0.96221 | YES
H9320550045 | DONALDSON | 55 | KENTON |  | ERLANGER | DONALDSON 45 | H9320550045 | 45 | ERLANGER |  | Erlanger, Florence, CVG | 8.621 | 1 | New Circuit 2020 | 0 | 72.3759 | YES | 0 | 1.5 | YES
H9320550046 | DONALDSON | 55 | KENTON |  | ERLANGER | DONALDSON 46 | H9320550046 | 46 | ERLANGER |  | Erlanger | 16.514 | 669 | New Circuit 2019 | 0 | 125.8034 | YES | 0 | 1.3623 | YES
H9320550048 | DONALDSON | 55 | KENTON |  | ERLANGER | DONALDSON 48 | H9320550048 | 48 | ERLANGER |  | Erlanger | 7.903 | 349 | New Circuit 2019 | 0 | 34.463 | YES | 0 | 0.16206 | YES
H9320590040 | WILDER | 59 | KENTON |  | WILDER | WILDER 40 | H9320590040 | 40 | NEWPORT |  | Newport | 7.341 | 770 | 2015-08-15 | 63.6427 | 91.269 | YES | 0.27829 | 0.36856 | YES
H9320590045 | WILDER | 59 | KENTON |  | WILDER | WILDER 45 | H9320590045 | 45 | WILDER |  | Wilder, Southgate, Ft. Thomas | 13.682 | 1640 | 2017-12-11 | 100.7 | 94.5097 | NO | 0.66173 | 0.68879 | YES
H9320590046 | WILDER | 59 | KENTON |  | WILDER | WILDER 46 | H9320590046 | 46 | FT. THOMAS |  | Ft. Thomas | 15.859 | 1089 | 2016-12-17 | 134.4848 | 147.9302 | YES | 0.70795 | 2.4905 | YES
H9320590047 | WILDER | 59 | KENTON |  | WILDER | WILDER 47 | H9320590047 | 47 | NEWPORT |  | Southgate | 13.248 | 1854 | 2017-07-10 | 47.1795 | 55.8945 | YES | 0.29788 | 1.0376 | YES
H9320590048 | WILDER | 59 | KENTON |  | WILDER | WILDER 48 | H9320590048 | 48 | NEWPORT |  | Newport | 5.53 | 591 | 2020-11-21 | 8.3311 | 219.1566 | YES | 0.061569 | 1.8029 | YES
H9320670043 | BUFFINGTON | 67 | KENTON |  | FLORENCE | BUFFINGTON 43 | H9320670043 | 43 | FLORENCE |  | Florence | 2.429 | 14 | 2019-08-31 | 23.1084 | 24.9123 | YES | 0.19672 | 0.1 | NO
H9320670045 | BUFFINGTON | 67 | KENTON |  | FLORENCE | BUFFINGTON 45 | H9320670045 | 45 | INDEPENDENCE |  | Florence | 16.029 | 2257 | 2020-06-06 | 87.0004 | 85.9547 | NO | 0.46703 | 1.0928 | YES
H9320700041 | CRESCENT | 70 | KENTON |  | FT. MITCHELL | CRESCENT 41 | H9320700041 | 41 | CRESCENT SPRINGS |  | Crescent Springs | 10.489 | 1606 | 2018-12-27 | 167.645 | 184.5679 | YES | 0.88428 | 1.5251 | YES
H9320700044 | CRESCENT | 70 | KENTON |  | FT. MITCHELL | CRESCENT 44 | H9320700044 | 44 | CRESCENT SPRINGS |  | Crescent Springs | 10.329 | 680 | 2020-06-03 | 123.0652 | 391.794 | YES | 0.38249 | 2.2075 | YES
H9320760043 | DAYTON | 76 | CAMPBELL |  | DAYTON | DAYTON 43 | H9320760043 | 43 | DAYTON |  | Dayton | 8.853 | 1466 | 2015-12-19 | 51.5717 | 109.439 | YES | 0.63872 | 0.73898 | YES
H9320860041 | BEAVER | 86 | BOONE |  | WALTON | BEAVER 41 | H9320860041 | 41 | WALTON |  | Walton | 50.419 | 1310 | 2017-12-18 | 165.5851 | 422.8837 | YES | 1.1591 | 2.1994 | YES
H9320890046 | DIXIE | 89 | BOONE |  | FLORENCE | DIXIE 46 | H9320890046 | 46 | FLORENCE |  | Florence | 2.165 | 5 | New Circuit 2019 | 0 | 97.2089 | YES | 0 | 0.22222 | YES
H9320980041 | LONGBRANCH | 98 | BOONE |  | FLORENCE | LONGBRANCH 41 | H9320980041 | 41 | FLORENCE |  | FLORENCE | 19.144 | 2248 | 2015-08-22 | 2.6545 | 25.5413 | YES | 0.026909 | 0.070985 | YES
H9321240041 | CRITTENDEN | 124 | GRANT |  | CRITTENDEN | CRITTENDEN 41 | H9321240041 | 41 | CRITTENDEN |  | Crittenden | 39.685 | 1662 | 2017-12-04 | 165.4253 | 290.4139 | YES | 1.3264 | 1.4402 | YES
H9321250042 | VERONA | 125 | KENTON |  | CRITTENDEN | VERONA 42 | H9321250042 | 42 | CRITTENDEN |  | Walton | 29.041 | 759 | 2017-12-27 | 140.0931 | 362.6163 | YES | 0.80584 | 1.7989 | YES
H9321250043 | VERONA | 125 | KENTON |  | CRITTENDEN | VERONA 43 | H9321250043 | 43 | WALTON |  | Crittenden, Walton | 22.482 | 517 | New Circuit 2019 | 35.8581 | 48.5571 | YES | 0.35421 | 0.26264 | NO
H9321280041 | HANDS | 128 | KENTON |  | COVINGTON | HANDS 41 | H9321280041 | 41 | Hands Pl |  | Covington & Independence | 25.97 | 1690 | 2017-12-27 | 102.6452 | 192.6416 | YES | 0.66297 | 1.2507 | YES
H9321280042 | HANDS | 128 | KENTON |  | COVINGTON | HANDS 42 | H9321280042 | 42 | TAYLOR MILL |  | Taylor Mill | 11.546 | 422 | 2016-04-19 | 191.4481 | 222.8099 | YES | 1.6494 | 1.0139 | NO
H9321280043 | HANDS | 128 | KENTON |  | COVINGTON | HANDS 43 | H9321280043 | 43 | INDEPENDENCE |  | Independence, Taylor Mill | 24.884 | 1840 | 2016-03-31 | 77.2785 | 286.26 | YES | 0.73222 | 2.0288 | YES
H9321280045 | HANDS | 128 | KENTON |  | COVINGTON | HANDS 45 | H9321280045 | 45 | TAYLOR MILL |  | Taylor Mill | 18.735 | 874 | 2019-02-23 | 60.6289 | 70.1975 | YES | 0.62564 | 0.25626 | NO
H9321310042 | BELLEVUE | 131 | CAMPBELL |  | NEWPORT | BELLEVUE 42 | H9321310042 | 42 | BELLEVUE |  | Fort Thomas, Dayton and Bellevue | 22.851 | 2272 | 2020-05-10 | 91.289 | 96.6089 | YES | 0.96734 | 0.63664 | NO
H9321320042 | COLD SPRING | 132 | CAMPBELL |  | COLD SPRINGS | COLD SPRING 42 | H9321320042 | 42 | COLD SPRINGS |  | Cold Springs, Brookstone Crossing | 37.916 | 2718 | 2019-12-26 | 101.4081 | 16.8106 | NO | 0.94511 | 1.055 | YES
H9321340042 | THOMAS MORE | 134 | BOONE |  | EDGEWOOD | THOMAS MORE 42 | H9321340042 | 42 | EDGEWOOD |  | Edgewood | 8.834 | 437 | 2019-11-18 | 145.2532 | 116.2392 | NO | 0.67444 | 2.0296 | YES
H9321520042 | HEBRON | 152 | BOONE |  | HEBRON | HEBRON 42 | H9321520042 | 42 | PETERSBURG |  | Petersburg | 47.992 | 658 | 2019-09-23 | 72.2813 | 73.3263 | YES | 0.65577 | 0.66467 | YES
H9321520044 | HEBRON | 152 | BOONE |  | HEBRON | HEBRON 44 | H9321520044 | 44 | HEBRON |  | Park West International | 3.762 | 22 | Nothing to trim | 7.8018 | 380.947 | YES | 0.45505 | 0.78261 | YES
H9321890042 | LIMABURG | 189 | BOONE |  | LIMABURG | LIMABURG 42 | H9321890042 | 42 | LIMABURG |  | Limaburg | 39.561 | 1808 | 2020-08-19 | 67.8378 | 63.4124 | NO | 0.66585 | 1.2787 | YES
H9321990041 | RICHWOOD | 199 | BOONE |  | RICHWOOD | RICHWOOD 41 | H9321990041 | 41 | RICHWOOD |  | Richwood | 8.722 | 92 | 2018-10-01 | 121.9976 | 530.3756 | YES | 0.32645 | 3.0686 | YES
H9321990043 | RICHWOOD | 199 | BOONE |  | RICHWOOD | RICHWOOD 43 | H9321990043 | 43 | RICHWOOD |  | Union | 18.247 | 1276 | 2019-09-07 | 47.6779 | 127.3542 | YES | 0.49919 | 1.2206 | YES
H9322100041 | OAKBROOK | 210 | BOONE |  | FLORENCE | OAKBROOK 41 | H9322100041 | 41 | ALEXANDRIA |  | Alexandria, Ross and Oneonta | 13.61 | 747 | 2018-12-31 | 112.2642 | 266.9001 | YES | 0.98101 | 2.2731 | YES
H9322170043 | COVINGTON KY | 217 | KENTON |  | COVINGTON | COVINGTON 43 | H9322170043 | 43 | COVINGTON |  | Covington | 6.436 | 1787 | 2018-05-12 | 86.9682 | 160.8719 | YES | 0.94768 | 1.0556 | YES
H9322410046 | FLORENCE | 241 | BOONE |  | FLORENCE | FLORENCE 46 | H9322410046 | 46 | FLORENCE |  | Florence | 15.365 | 1598 | 2015-07-25 | 65.6291 | 85.3602 | YES | 0.68634 | 0.55522 | NO
H9322870042 | KENTUCKY UNIVERSITY | 287 | CAMPBELL |  | NEWPORT | KY UNIV 42 | H9322870042 | 42 | HIGHLAND HEIGHTS |  | Northern Kentucky University | 15.018 | 1831 | 2018-07-28 | 39.0177 | 85.5698 | YES | 0.25492 | 1.0767 | YES
H9322890041 | EMPIRE | 289 | BOONE |  | FLORENCE | EMPIRE 41 | H9322890041 | 41 | FLORENCE |  | Florence, Union | 26.902 | 1880 | 2019-01-26 | 64.6661 | 99.1831 | YES | 0.51064 | 1.4169 | YES
H9323040042 | WHITE TOWER | 304 | KENTON |  | INDEPENDENCE | WHITE TOWER 42 | H9323040042 | 42 | INDEPENDENCE |  | Independence, White Tower | 9.961 | 490 | 2016-09-03 | 90.2953 | 91.5504 | YES | 1.2988 | 1.0264 | NO
H9323040043 | WHITE TOWER | 304 | KENTON |  | INDEPENDENCE | WHITE TOWER 43 | H9323040043 | 43 | INDEPENDENCE |  | Independence, White Tower | 28.104 | 1233 | 2015-11-24 | 132.2539 | 166.3145 | YES | 1.3471 | 1.8751 | YES
H9323050041 | MT ZION | 305 | BOONE |  | FLORENCE | MT ZION 41 | H9323050041 | 41 | DEVON |  | Florence | 2.404 | 68 | 2020-02-14 | 25.3044 | 97.2919 | YES | 0.29933 | 0.97101 | YES
H9323050043 | MT ZION | 305 | BOONE |  | FLORENCE | MT ZION 43 | H9323050043 | 43 | FLORENCE |  | FLORENCE | 12.594 | 965 | 2018-12-04 | 33.601 | 1002.2494 | YES | 0.18495 | 7.6872 | YES
H9323050044 | MT ZION | 305 | BOONE |  | FLORENCE | MT ZION 44 | H9323050044 | 44 | FLORENCE |  | FLORENCE | 3.678 | 1 | New Circuit 2019 | 0 | 1.4234 | YES | 0 | 0.014888 | YES

## REPORT P2
SUBSTATION - CIRCUIT | CIRCUIT NAME | CIRCUIT ID | OUTAGE CAUSE | PERCENT OF TOTAL OUTAGE MINUTES | CORRECTIVE ACTION PLAN
BEAVER - H9320860041 | BEAVER | H9320860041 | 03 Vegetation | 61.43% | The majority of the Vegetation outage minutes are due to trees falling onto the lines from outside the right-of-way & breaking equipment. The majority of the Equipment Failure outage minutes are due to failed underground cables affecting less than 30 customers each time. All repairs were made at the time of the outages in both cases. No further action required. This circuit is scheduled to be trimmed in 2022.
|  |  | 20 Equipment failure | 35.81%
|  |  | EA Weather | 1.624%
|  |  | 09 Public Accident/Damage | 0.5637%
|  |  | 05 Planned (IEEE) | 0.4876%
|  |  | 04 Wildlife | 0.07813%
100%
BELLEVUE - H9321310042 | BELLEVUE | H9321310042 | 20 Equipment failure | 54.57% | The majority of the Equipment Failure outage minutes are due to failed underground cables. The majority of the Weather outage minutes are due to a live oak tree branch 15 feet from the center line falling across conductors & locking out a recloser. All repairs were made at the time of the outages in both cases. No further action required.
|  |  | EA Weather | 42.86%
|  |  | 03 Vegetation | 1.281%
|  |  | 05 Planned (IEEE) | 0.7883%
|  |  | 04 Wildlife | 0.4165%
|  |  | 28 Other Cause | 0.08826%
100%
BUFFINGTON - H9320670043 | BUFFINGTON | H9320670043 | 05 Planned (IEEE) | 70.85% | The majority of the Planned outage minutes are from terminal cable replacement. The majority of the Wildlife outage minutes are due to blown fuses caused by wildlife on the lines. All repairs were made at the time of the outages in all cases. No further action required.
|  |  | 04 Wildlife | 29.15%
100%
BUFFINGTON - H9320670045 | BUFFINGTON | H9320670045 | 20 Equipment failure | 73.03% | The majority of the Equipment Failure outage minutes are due to a burned duck bill hotline clamp, causing the c-phase primary to burn down to the ground. The majority of the Public Accident/Damage outage minutes are due to a garbage truck hitting the lines. All repairs were made at the time of the outages in both cases. No further action required.
|  |  | 09 Public Accident/Damage | 22.92%
|  |  | 04 Wildlife | 1.643%
|  |  | 03 Vegetation | 1.532%
|  |  | 05 Planned (IEEE) | 0.8377%
|  |  | 11 Unknown Cause | 0.03365%
100%
COLD SPRING - H9321320042 | COLD SPRING | H9321320042 | 20 Equipment failure | 65.57% | The majority of the Equipment Failure outage minutes are due to a burned jumper. The majority of the Other Cause outage minutes are due to a melted out fuse caused by unreliable design. The majority of the Lightning Strike outage minutes are due to a clearing fuse that blew due to a lightning strike. All repairs were made at the time of the outages in all cases. No further action required.
|  |  | 28 Other Cause | 14.07%
|  |  | 19 Lightning strike | 10.52%
|  |  | 03 Vegetation | 8.792%
|  |  | 05 Planned (IEEE) | 1.043%
100%
CONSTANCE - H9320420042 | CONSTANCE | H9320420042 | 20 Equipment failure | 47% | The majority of the Equipment Failure outage minutes are due to a failed underground cable. The majority of the Public Accident/Damage outage minutes are due to a padmount transformer that was hit, causing damage to the underground cable as well. All repairs were made at the time of the outages in both cases. No further action required.
|  |  | 09 Public Accident/Damage | 30.96%
|  |  | 03 Vegetation | 7.982%
|  |  | 28 Other Cause | 6.276%
|  |  | EA Weather | 4.823%
|  |  | 05 Planned (IEEE) | 1.892%
|  |  | 11 Unknown Cause | 0.864%
|  |  | 04 Wildlife | 0.2058%
100%
COVINGTON - H9322170043 | COVINGTON | H9322170043 | 20 Equipment failure | 93.06% | The majority of the Equipment Failure outage minutes are due to a blown lightning arrester at an unfused transformer. A work order has been generated to have the lightning arrester replaced & the transformer retrofitted. The work order is in the process of being worked.
|  |  | 05 Planned (IEEE) | 6.767%
|  |  | 03 Vegetation | 0.1356%
|  |  | 11 Unknown Cause | 0.03586%
100%
CRESCENT - H9320700041 | CRESCENT | H9320700041 | EA Weather | 82.03% | The majority of the Weather outage minutes are due to a live locust tree branch 12 feet from the center line falling into the primary & neutral, causing a recloser lockout. Vegetation was contacted to remove the limb. The majority of the Unknown Cause outage minutes are due to a broken head guy insulator, resulting in a recloser lockout. After investigating, a work order was generated to repair the secondary neutral, replace the head guy, replace the pole ground & have the tap fused.
|  |  | 11 Unknown Cause | 15.75%
|  |  | 04 Wildlife | 2.089%
|  |  | 09 Public Accident/Damage | 0.1228%
100%
CRESCENT - H9320700044 | CRESCENT | H9320700044 | EA Weather | 89.68% | The majority of the Weather outage minutes are due to a tree limb that fell across phases, causing a recloser lockout & another separate event that was due to conductors down in rear property. All repairs were made at the time of the outages in both cases. No further action required.
|  |  | 20 Equipment failure | 9.2%
|  |  | 05 Planned (IEEE) | 0.7701%
|  |  | 04 Wildlife | 0.1899%
|  |  | 03 Vegetation | 0.1393%
|  |  | 28 Other Cause | 0.02176%
100%
CRITTENDEN - H9321240041 | CRITTENDEN | H9321240041 | 28 Other Cause | 45.63% | The majority of the Other Cause outage minutes are due to conductors making contact with each other during high winds. There have been no issues since. The majority of the Equipment Failure outage minutes are due to a recloser lockout caused by a fault in rear property. The majority of the Weather outage minutes are due to a circuit breaker lockout while the breaker had a hot line tag in place. All repairs were made at the time of the outages in all cases. No further action required.
|  |  | 20 Equipment failure | 29.05%
|  |  | EA Weather | 23.5%
|  |  | 03 Vegetation | 0.9105%
|  |  | 19 Lightning strike | 0.6807%
|  |  | 11 Unknown Cause | 0.08409%
|  |  | 09 Public Accident/Damage | 0.0683%
|  |  | 04 Wildlife | 0.05658%
|  |  | 05 Planned (IEEE) | 0.01086%
100%
DAYTON - H9320760043 | DAYTON | H9320760043 | 20 Equipment failure | 88.78% | The majority of the Equipment Failure outage minutes are due to a burned lead termination connector/pothead, causing a circuit lockout. The pothead was replaced. No further action required.
|  |  | 03 Vegetation | 6.938%
|  |  | 28 Other Cause | 2.419%
|  |  | 05 Planned (IEEE) | 0.989%
|  |  | 04 Wildlife | 0.8703%
100%
DIXIE - H9320890046 | DIXIE | H9320890046 | 19 Lightning strike | 89.9% | The majority of the Lightning Strike outage minutes are due to lightning striking an overhead transformer. The majority of the Public Accident/Damage outage minutes are due to a recloser lockout caused by a vehicle accident. All repairs were made at the time of the outages in both cases. No further action required.
|  |  | 09 Public Accident/Damage | 10.1%
100%
DONALDSON - H9320550045 | DONALDSON | H9320550045 | 20 Equipment failure | 97.53% | The majority of the Equipment Failure outage minutes are due to a switchgear failure. The switchgear has been replaced. No further action required.
|  |  | 04 Wildlife | 2.47%
100%
DONALDSON - H9320550046 | DONALDSON | H9320550046 | 09 Public Accident/Damage | 93.52% | The majority of the Public Accident/Damage outage minutes are due to a low hanging communication wire that was repeatedly struck by a double box railroad car causing two poles to break, locking out the circuit. All repairs were made at the time of the outage. No further action required.
|  |  | 04 Wildlife | 3.046%
|  |  | 28 Other Cause | 1.861%
|  |  | 03 Vegetation | 0.7929%
|  |  | 20 Equipment failure | 0.4878%
|  |  | 05 Planned (IEEE) | 0.2941%
100%
DONALDSON - H9320550048 | DONALDSON | H9320550048 | 03 Vegetation | 82.91% | The majority of the Vegetation outage minutes are due to fuse outages caused by vegetation. All vegetation was removed & all repairs were made at the time of the outages. No further action required. This circuit is scheduled to be trimmed this year (2021).
|  |  | 04 Wildlife | 8.891%
|  |  | 20 Equipment failure | 7.007%
|  |  | 19 Lightning strike | 0.8255%
|  |  | 28 Other Cause | 0.3657%
100%
EMPIRE - H9322890041 | EMPIRE | H9322890041 | 20 Equipment failure | 33.3% | The majority of the Equipment Failure outage minutes & the Unknown Cause outage minutes are both due to a bonded transmission pole guy that made contact with the Empire 41 primary conductor during construction work on the Transmission side to accommodate a road improvement project. The majority of the Weather outage minutes are due to a tree that fell on a double circuit pole. All repairs were made at the time of the outages in both cases. No further action required.
|  |  | 11 Unknown Cause | 31.43%
|  |  | EA Weather | 27.88%
|  |  | 03 Vegetation | 6.798%
|  |  | 04 Wildlife | 0.4576%
|  |  | 05 Planned (IEEE) | 0.1393%
100%
FLORENCE - H9322410046 | FLORENCE | H9322410046 | 20 Equipment failure | 43.24% | The majority of the Equipment Failure outage minutes are due to a leaking transformer that had to be replaced. The majority of the Weather outage minutes are due to a blown fuse that led to a recloser lockout during inclement weather. The majority of the Vegetation outage minutes are due to fuse & overhead transformer outages caused by vegetation. All repairs were made at the time of the outages in all cases. No further action required. This circuit is scheduled to be trimmed this year (2021).
|  |  | EA Weather | 37.97%
|  |  | 03 Vegetation | 11.16%
|  |  | 11 Unknown Cause | 6.644%
|  |  | 04 Wildlife | 0.4975%
|  |  | 05 Planned (IEEE) | 0.3879%
|  |  | 09 Public Accident/Damage | 0.09465%
100%
HANDS - H9321280041 | HANDS | H9321280041 | 03 Vegetation | 80.9% | The majority of the Vegetation outage minutes are due to a fallen tree resulting in a circuit lockout & a fuse outage caused by vegetation. All repairs were made at the time of the outages in both cases. No further action required. This circuit is scheduled to be trimmed in 2022.
|  |  | EA Weather | 9.83%
|  |  | 04 Wildlife | 4.23%
|  |  | 20 Equipment failure | 4.118%
|  |  | 09 Public Accident/Damage | 0.3265%
|  |  | 05 Planned (IEEE) | 0.3156%
|  |  | 19 Lightning strike | 0.1822%
|  |  | Blank | 0.05259%
|  |  | 28 Other Cause | 0.04551%
100%
HANDS - H9321280042 | HANDS | H9321280042 | 28 Other Cause | 91.52% | The majority of the Other Cause outage minutes are due to over 6 inches of water entering the disconnect cabinets inside the Hands Substation, resulting in both Hands 42 & Hands 43 locking out. The cabinets were disconnected from the circuits & the drainage for the substation was investigated.
|  |  | 03 Vegetation | 7.853%
|  |  | 20 Equipment failure | 0.551%
|  |  | 05 Planned (IEEE) | 0.07441%
100%
HANDS - H9321280043 | HANDS | H9321280043 | 28 Other Cause | 67.81% | The majority of the Other Cause outage minutes are due to over 6 inches of water entering the disconnect cabinets inside the Hands Substation, resulting in both Hands 42 & Hands 43 locking out. The cabinets were disconnected from the circuits & the drainage for the substation was investigated. The majority of the Vegetation outage minutes are due to a large tree that came down on the lines, locking out the circuit. All repairs were made at the time of the outage. No further action required. This circuit is scheduled to be trimmed this year (2021).
|  |  | 03 Vegetation | 31.22%
|  |  | 20 Equipment failure | 0.8404%
|  |  | 05 Planned (IEEE) | 0.05806%
|  |  | 09 Public Accident/Damage | 0.04918%
|  |  | 04 Wildlife | 0.0244%
100%
HANDS - H9321280045 | HANDS | H9321280045 | 28 Other Cause | 89.18% | The majority of the Other Cause outage minutes & the Vegetation outage minutes are both due to a large tree that fell into the lines, causing a recloser lockout. Road improvement has been completed and the vegetation has been cleared.
|  |  | 03 Vegetation | 9.095%
|  |  | 05 Planned (IEEE) | 0.9903%
|  |  | 20 Equipment failure | 0.7322%
100%
HEBRON - H9321520042 | HEBRON | H9321520042 | 09 Public Accident/Damage | 59.56% | The majority of the Public Accident/Damage outage minutes are due to a guy wire being hit, causing it to wrap around the primary. The majority of the Vegetation outage minutes are due to fuse outages caused by vegetation. All repairs were made at the time of the outages in all cases. No further action required.
|  |  | 03 Vegetation | 26.97%
|  |  | 19 Lightning strike | 9.847%
|  |  | 20 Equipment failure | 2.823%
|  |  | 04 Wildlife | 0.5023%
|  |  | 05 Planned (IEEE) | 0.3028%
100%
HEBRON - H9321520044 | HEBRON | H9321520044 | 20 Equipment failure | 99.39% | The majority of the Equipment Failure outage minutes are due to a blown bayonet fuse. All repairs were made at the time of the outage. No further action required.
|  |  | 28 Other Cause | 0.607%
100%
KENTON - H9320090042 | KENTON | H9320090042 | EA Weather | 75.73% | The majority of the Weather outage minutes are due to a recloser locking out during high winds. The majority of the Planned outage minutes are due to transformer retrofits.
|  |  | 05 Planned (IEEE) | 12.38%
|  |  | 03 Vegetation | 5.063%
|  |  | 04 Wildlife | 4.307%
|  |  | 28 Other Cause | 1.222%
|  |  | 11 Unknown Cause | 1.145%
|  |  | 20 Equipment failure | 0.1587%
100%
KY UNIV - H9322870042 | KY UNIV | H9322870042 | 03 Vegetation | 66.47% | The majority of the Vegetation outage minutes are due to a tree that came down on the lines, resulting in a circuit lockout. The majority of the Equipment Failure outage minutes are due to a failed direct bury underground cable. All repairs were made at the time of the outages in both cases. No further action required.
|  |  | 20 Equipment failure | 29.39%
|  |  | 11 Unknown Cause | 3.84%
|  |  | 04 Wildlife | 0.3036%
100%
LIMABURG - H9321890042 | LIMABURG | H9321890042 | 09 Public Accident/Damage | 64.57% | The majority of the Public Accident/Damage outage minutes are due to a recloser lockout caused by a vehicle hitting a pole, requiring it to be replaced. The majority of the Equipment Failure outage minutes are due to a circuit lockout while the breaker had a hot line tag in place & a defective cutout. The majority of the Vegetation outage minutes are due to fuse outages caused by vegetation. All repairs were made at the time of the outages in all cases. No further action required. This circuit was trimmed in 2020.
|  |  | 20 Equipment failure | 21.07%
|  |  | 03 Vegetation | 11.81%
|  |  | 05 Planned (IEEE) | 1.445%
|  |  | 19 Lightning strike | 0.9201%
|  |  | 04 Wildlife | 0.1016%
|  |  | EA Weather | 0.06938%
|  |  | 28 Other Cause | 0.01125%
100%
LONGBRANCH - H9320980041 | LONGBRANCH | H9320980041 | 09 Public Accident/Damage | 98.52% | The majority of the Public Accident/Damage outage minutes are due to a damaged switching module. The switching module has been replaced.
|  |  | 05 Planned (IEEE) | 0.938%
|  |  | 20 Equipment failure | 0.544%
100%
MT ZION - H9323050041 | MT ZION | H9323050041 | 11 Unknown Cause | 94.89% | The majority of the Unknown Cause outage minutes are due to a problem that occurred inside the substation, resulting in a circuit lockout. The substation was investigated & all necessary repairs were completed to return to normal operation.
|  |  | 20 Equipment failure | 5.111%
100%
MT ZION - H9323050043 | MT ZION | H9323050043 | 28 Other Cause | 54.21% | The majority of the Other Cause outage minutes are due to a temporary patent jumper that burned off. The temporary patent jumpers have been replaced with permanent jumpers. The majority of the Equipment Failure outage minutes are due to a burned jumper causing the wire to come down, resulting in a circuit lockout & another circuit lockout that occurred while the breaker had a hot line tag in place when a rope let go while pulling in new wire. The majority of the Planned outage minutes are due a Planned Outage taken to transfer underground. All repairs were made at the time of the outages in all cases. No further action required.
|  |  | 20 Equipment failure | 33.15%
|  |  | 05 Planned (IEEE) | 10.21%
|  |  | 11 Unknown Cause | 1%
|  |  | 09 Public Accident/Damage | 0.8601%
|  |  | 19 Lightning strike | 0.4645%
|  |  | 04 Wildlife | 0.1041%
100%
MT ZION - H9323050044 | MT ZION | H9323050044 | 05 Planned (IEEE) | 78.38% | The majority of the Planned outage minutes & the Other Cause outage minutes are both due to Planned Outages taken to transfer wire to new poles.
|  |  | 28 Other Cause | 21.62%
100%
OAKBROOK STA - H9322100041 | OAKBROOK STA | H9322100041 | 20 Equipment failure | 51.19% | The majority of the Equipment Failure outage minutes are due to a burned up switchgear. The majority of the Weather outage minutes are due to blown fuses during inclement weather. The majority of the Public Accident/Damage outage minutes are due to two different dig-ins. All repairs were made at the time of the outages in all cases. No further action required.
|  |  | EA Weather | 28.75%
|  |  | 09 Public Accident/Damage | 12.2%
|  |  | 28 Other Cause | 4.188%
|  |  | 11 Unknown Cause | 2.149%
|  |  | 05 Planned (IEEE) | 1.138%
|  |  | 03 Vegetation | 0.279%
|  |  | 04 Wildlife | 0.1015%
100%
RICHWOOD - H9321990041 | RICHWOOD | H9321990041 | 09 Public Accident/Damage | 43.38% | The majority of the Public Accident/Damage outage minutes are due to a vehicle accident in which a pole was struck, causing the conductor to fall to the ground. The majority of the Lightning Strike outage minutes are due to a blown suspension insulator & fuses caused by lightning. The majority of the Equipment Failure outage minutes are due to a circuit lockout caused by a downed wire. All repairs were made at the time of the outages in all cases. No further action required.
|  |  | 19 Lightning strike | 33.56%
|  |  | 20 Equipment failure | 21.81%
|  |  | 05 Planned (IEEE) | 0.9505%
|  |  | 28 Other Cause | 0.1749%
|  |  | 04 Wildlife | 0.1218%
100%
RICHWOOD - H9321990043 | RICHWOOD | H9321990043 | 05 Planned (IEEE) | 47.69% | The majority of the Planned outage minutes are from transferring conductor & installing new/upgraded equipment. The majority of the Weather outage minutes are due to a sectionalizer that locked out due to an unknown/unsustained fault. Crews closed the sectionalizer back in & it held. The majority of the Vegetation outage minutes are due to fuse outages caused by vegetation. All vegetation was removed & all repairs were made at the time of the outages. No further action required.
|  |  | EA Weather | 29.31%
|  |  | 03 Vegetation | 22.49%
|  |  | 20 Equipment failure | 0.4047%
|  |  | 11 Unknown Cause | 0.05901%
|  |  | 28 Other Cause | 0.04996%
100%
THOMAS MORE - H9321340042 | THOMAS MORE | H9321340042 | 20 Equipment failure | 99.41% | The majority of the Equipment Failure outage minutes are due to a burned lead termination connector/pothead, causing a circuit lockout. The pothead was replaced. No further action required.
|  |  | 04 Wildlife | 0.5927%
100%
VERONA - H9321250042 | VERONA | H9321250042 | 09 Public Accident/Damage | 79.9% | The majority of the Public Accident/Damage outage minutes are due to a recloser lockout caused by a vehicle hitting a pole, requiring it to be replaced. All repairs were made at the time of the outage. No further action required. The majority of the Planned outage minutes were from installing a cutout to safely change out a pole damaged by a vehicle accident.
|  |  | 05 Planned (IEEE) | 11.87%
|  |  | 03 Vegetation | 4.395%
|  |  | EA Weather | 2.113%
|  |  | 20 Equipment failure | 1.518%
|  |  | 19 Lightning strike | 0.1402%
|  |  | 04 Wildlife | 0.03656%
|  |  | 28 Other Cause | 0.02327%
100%
VERONA - H9321250043 | VERONA | H9321250043 | 03 Vegetation | 86.52% | The majority of the Vegetation outage minutes are due to a phase & neutral downed by a tree & a fuse that was opened for tree trimming. All vegetation was removed & all repairs were made at the time of the outage. No further action required.
|  |  | 20 Equipment failure | 8.892%
|  |  | 09 Public Accident/Damage | 2.209%
|  |  | 05 Planned (IEEE) | 1.11%
|  |  | 04 Wildlife | 0.6194%
|  |  | EA Weather | 0.4945%
|  |  | 28 Other Cause | 0.154%
100%
WHITE TOWER - H9323040042 | WHITE TOWER | H9323040042 | 20 Equipment failure | 90.14% | The majority of the Equipment Failure outage minutes are due to a failed cross arm on Transmission Circuit 5967 that feeds White Tower. Once the fault was identified, Transmission crews were able to restore from an alternate source.
|  |  | 03 Vegetation | 8.863%
|  |  | 05 Planned (IEEE) | 0.9991%
100%
WHITE TOWER - H9323040043 | WHITE TOWER | H9323040043 | 20 Equipment failure | 49.45% | The majority of the Equipment Failure outage minutes are due to a failed cross arm on Transmission Circuit 5967 that feeds White Tower. Once the fault was identified, Transmission crews were able to restore from an alternate source. The majority of the Public Accident/Damage outage minutes are due a public vehicle hitting a down guy, causing it to contact the primary. A Service Request has been submitted to replace the down guy & anchor.
|  |  | 09 Public Accident/Damage | 43.45%
|  |  | 11 Unknown Cause | 5.426%
|  |  | 05 Planned (IEEE) | 0.8241%
|  |  | 03 Vegetation | 0.4651%
|  |  | 04 Wildlife | 0.3605%
|  |  | 28 Other Cause | 0.02557%
100%
WILDER - H9320590040 | WILDER | H9320590040 | 05 Planned (IEEE) | 95.7% | The majority of the Planned outage minutes are due to swapping phases & changing out poles.
|  |  | 20 Equipment failure | 3.816%
|  |  | 03 Vegetation | 0.3639%
|  |  | 09 Public Accident/Damage | 0.1221%
100%
WILDER - H9320590045 | WILDER | H9320590045 | 11 Unknown Cause | 49.79% | The majority of the Unknown Cause outage minutes are due to a circuit lockout caused by an unknown fault. The majority of the Other Cause outage minutes are due to a fuse outage caused by insufficient capability. The majority of the Vegetation outage minutes are due to two spans of primary in rear property brought down by vegetation & a fuse outage caused by vegetation. All vegetation was removed & all repairs were made at the time of the outages. No further action required.
|  |  | 28 Other Cause | 24.71%
|  |  | 03 Vegetation | 15.54%
|  |  | 05 Planned (IEEE) | 9.11%
|  |  | 20 Equipment failure | 0.6199%
|  |  | 04 Wildlife | 0.2368%
100%
WILDER - H9320590046 | WILDER | H9320590046 | 20 Equipment failure | 49.28% | The majority of the Equipment Failure outage minutes are due to the circuit breaker being opened to safely replace a burned up switch. The majority of the Unknown Cause outage minutes are due to a recloser lockout. After investigation, it was found that a sectionalizer was not in switch mode when it should have been, causing a mis-operation of the self-healing team & resulting in more than 600 additional customers seeing an outage that should not have. The sectionalizer has been placed back into switch mode. The majority of the Other Cause outage minutes are due to lines down, resulting in a switch being opened. All repairs were made at the time of the outages in all cases. No further action required.
|  |  | 11 Unknown Cause | 32.05%
|  |  | 28 Other Cause | 11.13%
|  |  | 04 Wildlife | 7.538%
100%
WILDER - H9320590047 | WILDER | H9320590047 | 09 Public Accident/Damage | 78.04% | The majority of the Public Accident/Damage outage minutes are due to a public vehicle that hit & broke a pole. The circuit breaker was opened for safety to replace the pole & make repairs. The majority of the Vegetation outage minutes are due to a primary phase & secondary brought down by vegetation in rear property. All repairs were made at the time of the outages in both cases. No further action required. This circuit is scheduled for hazard tree removal this year (2021).
|  |  | 03 Vegetation | 13.11%
|  |  | 28 Other Cause | 7.078%
|  |  | 20 Equipment failure | 0.7619%
|  |  | 04 Wildlife | 0.753%
|  |  | 11 Unknown Cause | 0.2516%
100%
WILDER - H9320590048 | WILDER | H9320590048 | 19 Lightning strike | 43.64% | The majority of the Lightning Strike outage minutes are due to a damaged pothead that was changed out. The majority of the Planned outage minutes are due to a planned underground outage. The majority of the Vegetation outage minutes are due a landslide that caused vegetation to make contact with conductors, locking out the circuit. All repairs were made at the time of the outages in all cases. No further action required. This circuit is scheduled for hazard tree removal this year (2021).
|  |  | 05 Planned (IEEE) | 38.19%
|  |  | 03 Vegetation | 13.34%
|  |  | 04 Wildlife | 3.849%
|  |  | 20 Equipment failure | 0.9769%
100%