## KU Section 1-4
KENTUCKY PUBLIC SERVICE COMMISSION
ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT
SECTION 1: CONTACT INFORMATION
UTILITY NAME |  |  |  | KENTUCKY UTILITIES COMPANY
REPORT PREPARD BY |  |  |  | Steve Woodworth (Dir. System Ops & Planning)
E-MAIL ADDRESS OF PREPARER |  |  |  | steve.woodworth@lge-ku.com
PHONE NUMBER OF PREPARER |  |  |  | (502) 627-3828
SECTION 2: REPORTING YEAR
CALENDAR YEAR OF REPORT |  |  |  | 2020
SECTION 3: MAJOR EVENT DAYS (MED)
TMED |  |  |  | 3.941
FIRST DATE USED TO DETERMINE TMED |  |  |  | 2015-01-01
LAST DATE USED TO DETERMINE TMED |  |  |  | 2019-12-31
NUMBER OF MED IN REPORTING YEAR |  |  |  | 3
NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years. If five years of data are not available, then utilities should use what is available until five years are accumulated.
SECTION 4: SYSTEM RELIABILTIY INFORMATION AND RESULTS
System-wide Information
TOTAL CUSTOMERS |  | 546042 |  | TOTAL CIRCUITS |  | 1113
Excluding MED
| 5 YEAR AVERAGE |  |  |  | REPORTING YEAR
SAIDI | 84.64 |  |  | SAIDI | 58.7
SAIFI | 0.777 |  |  | SAIFI | 0.588
Including MED
| 5 YEAR AVERAGE |  |  |  | REPORTING YEAR
SAIDI | 157.74 |  |  | SAIDI | 77.46
SAIFI | 0.899 |  |  | SAIFI | 0.678
Notes:
1) | All duration indices (SAIDI) are to be reported in units of minutes.
2) | Reports are due on the first business day of May of each year
3) | Reports cover the calendar year ending in the December before the reports are due.
4) | IEEE 1366 (latest version) is used to define SAIDI, SAIFI, and TMED
SECTION 5: CIRCUIT REPORTING
BEGIN ON NEXT PAGE

## Excel KU Section 5
Substation Name | Substation Location (County - Road - Town) | Circuit Number | Circuit Location (Town - Road - General Area) | Total Circuit Length (Miles) | Average 2020 OMS Custs | Date of Last Circuit Trim (VM) | Animal | Construction | Lightning | Non-Company | Other/Unknown | Overload | Planned Work | Trees | Vehicle | Utility Equipment | 2016-2020 SAIDI Average | 2020 SAIDI | 2016-2020 SAIFI Average | 2020 SAIFI | LIST OF CORRECTION ACTION, IF ANY, TAKEN OR TO BE TAKEN
LEXINGTON PLANT | Fayette - 745 N Limestone - Lexington | 1 | Lexington - N. Broadway - SW of Station | 2.9899 | 525 | 2017-10-21 | 0% | 0% | 0% | 0% | 0% | 0% | 5.823% | 0% | 93.17% | 1.011% | 50.5538 | 168.5891 | 0.66966 | 1.8544 | Continue to Monitor
LEXINGTON PLANT | Fayette - 745 N Limestone - Lexington | 3 | Lexington - N. Upper St. and 6th St. - W of Station | 4.6684 | 978 | 2017-10-21 | 0% | 0% | 0% | 0% | 1.519% | 0% | 16.61% | 0% | 81.87% | 0% | 21.099 | 65.3528 | 0.16225 | 0.41719 | Continue to Monitor
LEXINGTON PLANT | Fayette - 745 N Limestone - Lexington | 6 | Lexington - N. Limestone St. SW of Station | 2.6372 | 377 | 2018-05-05 | 0% | 0% | 0% | 0% | 0.00382% | 0% | 0.2636% | 0.128% | 99.34% | 0.2642% | 117.858 | 413.9007 | 0.78349 | 1.0928 | Continue to Monitor
LEXINGTON PLANT | Fayette - 745 N Limestone - Lexington | 7 | Lexington - N. Limestone St and York St. - NE amd SE of Station | 6.4481 | 1206 | 2018-05-05 | 0% | 0% | 0% | 0% | 3.857% | 0% | 4.535% | 32.57% | 57.31% | 1.725% | 15.5011 | 35.1799 | 0.20702 | 0.50463 | Continue to Monitor
RACE STREET 4KV | Fayette - 420 Corral St - Lexington | 14 | Lexington - Race St. and E Third St. and Chestnut Street - N of Station | 5.7576 | 919 | 2018-12-08 | 0% | 0% | 0% | 0% | 3.707% | 0% | 32.61% | 44.68% | 12.04% | 6.968% | 13.1321 | 14.1464 | 0.091394 | 0.1001 | Continue to Monitor
LEXINGTON WATER COMPANY 4KV | Fayette - 2300 Richmond Rd. - Lexington | 16 | Lexington - Fontaine Rd - W of Substation | 3.6186 | 699 | 2020-09-12 | 0% | 0% | 39.17% | 0% | 0% | 0% | 60.83% | 0% | 0% | 0% | 31.1003 | 25.8276 | 0.15558 | 0.166 | Continue to Monitor
SCOTT STREET | Fayette - 301 Scott St. - Lexington | 18 | Lexington - Limestone St. - SE of Substation | 3.2568 | 780 | 2019-07-20 | 0% | 0% | 0% | 0% | 8.131% | 0% | 80.1% | 7.517% | 0% | 4.256% | 17.3213 | 8.7006 | 0.16829 | 0.28842 | Continue to Monitor
KUNKEL | Fayette - 2000 Versailles Rd. - Lexington | 19 | Lexington - Versailles Rd. - NE of Substation | 2.0339 | 173 | 2020-03-28 | 0% | 0% | 0% | 0% | 0% | 0% | 60.34% | 39.66% | 0% | 0% | 24.1928 | 12.9906 | 0.22067 | 0.28977 | Trees Trimmed in 2020
HIGBY MILL 12KV | Fayette - 308 Waveland Museum Ln. - Lexington | 23 | Lexington - Nicholasville Rd - S of Substation | 56.4077 | 1708 | 2019-01-27 | 3.098% | 0% | 0% | 7.131% | 19.22% | 0% | 17.59% | 21.04% | 0% | 31.91% | 91.5042 | 78.9124 | 0.9844 | 1.9038 | Continue to Monitor
KUNKEL | Fayette - 2000 Versailles Rd. - Lexington | 26 | Lexington - Duntreath Dr. & Pine Mt. Rd. - SE of Substation | 4.6641 | 570 | 2020-03-28 | 0% | 0% | 0% | 0% | 0% | 0% | 5.836% | 91.37% | 0% | 2.799% | 74.919 | 229.4489 | 0.33732 | 1.105 | Trees Trimmed in 2020
RACE STREET 4KV | Fayette - 420 Corral St - Lexington | 30 | Lexington - Midland Ave. & Winchester Rd. - E of Substation | 5.181 | 854 | 2018-12-08 | 0% | 0% | 0% | 0% | 0% | 0% | 7.024% | 0% | 85.44% | 7.534% | 45.9032 | 48.5379 | 0.73382 | 0.95788 | Continue to Monitor
RACE STREET 4KV | Fayette - 420 Corral St - Lexington | 31 | Lexington - Corral St. & MLK Blvd. - NE of Substation | 2.8321 | 502 | 2018-12-08 | 0% | 0% | 0% | 0% | 1.789% | 84.41% | 13.81% | 0% | 0% | 0% | 14.992 | 19.5769 | 0.30361 | 0.17066 | Continue to Monitor
G E LAMP WORKS | Fayette - 1809 Edision Dr - Lexington | 32 | Lexington - Edision Dr. - Rosemont Garden | 2.1393 | 279 | 2020-05-09 | 9.369% | 0% | 0% | 0% | 81.98% | 0% | 5.848% | 0% | 0% | 2.807% | 11.3743 | 16.3891 | 0.17204 | 0.22508 | Continue to Monitor
HUGHES LANE | Fayette - 251 Hughes Ln. - Lexington | 37 | Lexington - Mir Station Rd. & US 27 - SW of Substation | 138.1792 | 1098 | 2020-01-25 | 0.4906% | 0% | 0.07673% | 1.26% | 2.774% | 0% | 1.462% | 27.57% | 63.59% | 2.781% | 242.3469 | 338.8597 | 1.6312 | 3.1805 | Trees Trimmed in 2020
LEXINGTON WATER COMPANY 12KV | Fayette - 2300 Richmond Rd. - Lexington | 39 | Lexington - St. Phillip Dr. & Richmond Rd. - E of Substation | 13.866 | 2044 | 2020-01-04 | 0.4782% | 0% | 0% | 0% | 0.1426% | 0% | 0.9762% | 59.91% | 0% | 38.49% | 42.0945 | 82.0899 | 0.43357 | 0.36871 | Trees Trimmed in 2020
REYNOLDS | Fayette - 200 W. Reynold Rd. - Lexington | 40 | Lexington - Reynolds Rd. - W of Substation | 12.6989 | 1094 | 2017-08-31 | 2.66% | 0% | 10.37% | 0% | 6.852% | 0% | 2.127% | 68.8% | 0% | 9.195% | 9.2668 | 14.1042 | 0.065503 | 0.11591 | Continue to Monitor
VILEY ROAD | Fayette - 308 Alexandria Rd. - Lexington | 41 | Lexington - Leestown Rd. & Adams Ln. - NE of Substation | 63.128 | 1113 | 2016-05-21 | 0.03933% | 0% | 0.1518% | 0.01352% | 11.98% | 0% | 8.78% | 16.42% | 0.6784% | 61.94% | 99.4132 | 146.0119 | 0.8827 | 0.52382 | Continue to Monitor
HALEY | Fayette - 5481 Winchester Rd - Lexington | 46 | Lexington - Winchester & Haley Rd - W of Substation | 45.8746 | 389 | 2015-10-31 | 0.721% | 0% | 5.495% | 0% | 40.38% | 0% | 2.166% | 48.01% | 0% | 3.227% | 182.0555 | 137.8209 | 1.2386 | 2.0491 | Tree Trim Scheduled for 2021
ASHLAND AVENUE | Fayette - 448 S Ashland Ave. - Lexington | 48 | Lexington - Tates Creek Rd. - S of Substation | 6.2588 | 538 | 2020-09-18 | 0% | 0% | 0% | 6.075% | 6.089% | 0% | 17.16% | 16.45% | 52.72% | 1.512% | 49.2218 | 105.2884 | 0.50322 | 1.4889 | Continue to Monitor
AMERICAN AVENUE | Fayette - 96 Burley Ave. - Lexington | 52 | Lexington - Waller Ave. & St. Joseph Dr. - SE of Substation | 0.45888 | 88 | 2019-07-20 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.0816 | 3.8621 | 0.022676 | 0.090909 | Continue to Monitor
HAEFLING | Fayette - 1555 Baunmann Dr - Lexington | 55 | Lexington - Fairman Rd & Leestown Rd - S of Substation | 17.0276 | 1271 | 2016-04-20 | 35.05% | 32.46% | 0% | 0% | 8.836% | 0% | 0.4432% | 9.599% | 6.326% | 7.279% | 52.6957 | 48.8765 | 0.46334 | 0.48851 | Continue to Monitor
HAEFLING | Fayette - 1555 Baunmann Dr - Lexington | 60 | Lexington - Mercer Rd - W of Substation | 12.2481 | 420 | 2016-09-10 | 0.5138% | 0% | 0% | 0% | 15.29% | 0% | 6.436% | 0.09013% | 0% | 77.67% | 70.6711 | 78.4798 | 1.1996 | 1.4645 | Continue to Monitor
PICADOME 12KV | Fayette - 1620 Harrodsburg Rd - Lexington | 62 | Lexington - Mason Headley Rd - NW of Substation | 3.9782 | 291 | 2020-04-11 | 4.459% | 0% | 0% | 0% | 83.13% | 0% | 0% | 6.751% | 0% | 5.661% | 61.3542 | 52.127 | 0.73644 | 1.041 | Continue to Monitor
PROCTOR & GAMBLE | Fayette - 120 Zesta Pl - Lexington | 66 | Lexington - Zesta Pl - W of Substation | 0.38246 | 5 | 2019-10-19 | 0% | 0% | 0% | 0% | 28.05% | 0% | 71.95% | 0% | 0% | 0% | 121.0689 | 32.8 | 0.49333 | 0.8 | Continue to Monitor
PROCTOR & GAMBLE | Fayette - 120 Zesta Pl - Lexington | 68 | Lexington - Delware Rd - SE of Substation | 3.3296 | 379 | 2019-10-19 | 0% | 0.1301% | 0% | 0% | 13.32% | 0% | 1.71% | 79.41% | 0% | 5.434% | 42.8306 | 42.687 | 0.28437 | 0.34635 | Continue to Monitor
WILSON DOWNING | Fayette - 680 Wilson Downing Rd - Lexington | 72 | Lexington - Tates Creek Rd & Trent Blvd - NE of Substation | 8.3162 | 1369 | 2019-02-16 | 3.973% | 0.04761% | 0.2139% | 0% | 5.377% | 0% | 1.871% | 87.02% | 0% | 1.494% | 24.8017 | 39.5376 | 0.43608 | 0.28866 | Continue to Monitor
LOUDON AVENUE | Fayette - 811 E Loudon Ave - Lexington | 75 | Lexington - Floyd Dr - NE of Substation | 11.8045 | 1288 | 2018-06-16 | 1.857% | 0% | 0% | 0% | 0.6303% | 0% | 0.6631% | 0.6356% | 0% | 96.21% | 55.7733 | 263.4626 | 0.25822 | 1.1683 | Continue to Monitor
TRAFTON AVENUE 4KV | Fayette - 141 Trafton St - Lexington | 78 | Lexington - Versailles Rd - W of Substation | 5.2262 | 498 | 2020-01-22 | 0% | 0% | 0% | 0% | 12.06% | 0% | 16.39% | 1.971% | 68.92% | 0.6595% | 9.6988 | 26.0023 | 0.083983 | 0.17746 | Continue to Monitor
TRAFTON AVENUE 12KV | Fayette - 141 Trafton St - Lexington | 79 | Lexington - Red Mile Rd - S of Substation | 7.2248 | 1192 | 2020-01-25 | 0.3406% | 0% | 0% | 0% | 0% | 0% | 0.7331% | 98.93% | 0% | 0% | 28.9209 | 62.9459 | 0.38331 | 1.01 | Trees Trimmed in 2020
PICADOME 4KV | Fayette - 1620 Harrodsburg Rd - Lexington | 80 | Lexington - Lafayette Pky - S of Substation | 7.2313 | 852 | 2019-12-28 | 0.3666% | 1.009% | 0% | 0% | 0.08483% | 0% | 2.99% | 95.23% | 0% | 0.3163% | 75.1547 | 162.3244 | 1.2243 | 1.1511 | Continue to Monitor
TRAFTON AVENUE 12KV | Fayette - 141 Trafton St - Lexington | 88 | Lexington - Dunkirk Dr - W of Substation | 9.4725 | 1655 | 2020-06-13 | 2.456% | 0% | 0% | 0% | 17.26% | 0% | 5.971% | 36.44% | 0% | 37.87% | 24.566 | 40.594 | 0.37256 | 1.0991 | Trees Trimmed in 2020
HAEFLING | Fayette - 1555 Baunmann Dr - Lexington | 89 | Lexington - Baumann Dr - W of Substation | 0.58289 | 3 | 2016-09-10 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 143.6556 | 558.2278 | 0.4 | 0.66667 | Continue to Monitor
AMERICAN AVENUE | Fayette - 96 Burley Ave. - Lexington | 90 | Lexington - Stanley Ave. & Waller Ave. - W of Substation | 1.1549 | 220 | 2019-07-20 | 0% | 0% | 0% | 0% | 0% | 0% | 2.08% | 97.92% | 0% | 0% | 14.4653 | 25.0149 | 0.10861 | 0.22684 | Continue to Monitor
LIBERTY ROAD | Fayette - 2125 Liberty Rd. - Lexington | 92 | Lexington - New Circule Rd. & Winchester Rd. - E of Substation | 19.0471 | 1379 | 2019-07-20 | 1.72% | 0% | 0% | 0% | 14.2% | 0% | 0.4071% | 0% | 0% | 83.67% | 35.1925 | 111.9295 | 0.57891 | 1.6336 | Continue to Monitor
STONEWALL | Fayette - 3060 Arrowhead Dr - Lexington | 96 | Lexington - New Circle Rd & Southview Dr - NE of Substation | 13.0258 | 1295 | 2017-02-16 | 0.3835% | 0.234% | 0% | 0% | 13.25% | 0% | 2.807% | 83.11% | 0% | 0.2172% | 133.499 | 365.4678 | 0.99621 | 2.4153 | Tree Trim Scheduled for 2021
STONEWALL | Fayette - 3060 Arrowhead Dr - Lexington | 98 | Lexington - Chelsea Dr & Clays Mill Dr - S of Substation | 5.736 | 476 | 2017-08-31 | 9.442% | 0% | 0% | 0% | 72.19% | 0% | 6.307% | 11.7% | 0% | 0.3662% | 61.2109 | 119.688 | 0.87453 | 1.3524 | Continue to Monitor
JOYLAND | Fayette - 2375 Paris Pike - Lexington | 99 | Lexington - I-64 & I-75 - NW of Substation | 14.4684 | 2028 | 2020-07-25 | 10.06% | 30.06% | 0% | 0% | 0.447% | 0% | 1.7% | 54.54% | 0% | 3.19% | 143.9135 | 69.2675 | 1.4386 | 1.7103 | Trees Trimmed in 2020
STONEWALL | Fayette - 3060 Arrowhead Dr - Lexington | 108 | Lexington - Tomahawk Tr & Harrodsburg Rd - W of Substation | 4.5711 | 362 | 2017-02-25 | 4.444% | 0% | 0% | 0% | 94.13% | 0% | 1.422% | 0% | 0% | 0% | 43.6703 | 98.4644 | 0.39982 | 1.0911 | Continue to Monitor
IBM | Fayette - 740 W New Circle Rd - Lexington | 110 | Lexington - Russell Cave Rd - NE of Substation | 21.9808 | 2033 | 2017-12-23 | 6.059% | 0.1715% | 0% | 78.06% | 0.2961% | 0% | 0.1155% | 11.64% | 0% | 3.654% | 30.7808 | 26.8204 | 0.6667 | 1.2246 | Continue to Monitor
ASHLAND AVENUE | Fayette - 448 S Ashland Ave. - Lexington | 111 | Lexington - Ashland Dr & Preston Ave. - E of Substation | 5.3347 | 973 | 2019-12-21 | 0% | 0% | 0% | 0% | 31.21% | 0% | 12.28% | 19.34% | 29.43% | 7.742% | 46.0933 | 59.5536 | 0.61278 | 0.87671 | Continue to Monitor
VILEY ROAD | Fayette - 308 Alexandria Rd. - Lexington | 115 | Lexington - Alexandria Rd & Leestown Rd - NE of Substation | 2.1087 | 22 | 2016-07-09 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 6.5332 | 31.5826 | 0.025725 | 0.086957 | Continue to Monitor
DONERAIL | Fayette - 4601 Old Iron Works Rd - Lexington | 117 | Lexington - Lisle Rd - N of Substation | 7.516 | 471 | 2019-07-06 | 0.1448% | 0% | 0% | 0% | 99.15% | 0% | 0.09127% | 0% | 0% | 0.6111% | 31.1464 | 107.9363 | 0.31466 | 1.0794 | Continue to Monitor
LANSDOWNE SWITCHING | Fayette - 3200 Montavesta Rd - Lexington | 118 | Lexington - New Circle Rd. & Chinoe Rd. - SW of Substation | 13.8122 | 1089 | 2020-06-27 | 0.2629% | 0.9486% | 0% | 0% | 14.71% | 0% | 5.884% | 71.82% | 0% | 6.374% | 51.7551 | 95.4569 | 0.61524 | 1.2066 | Trees Trimmed in 2020
FMC | Fayette - 2641 Palumbo Dr - Lexington | 120 | Lexington - Palumbo Dr & Man O War Blvd - S of Substation | 7.1494 | 274 | 2016-07-23 | 0% | 0% | 0% | 0% | 98.95% | 0% | 0% | 1.051% | 0% | 0% | 21.4583 | 60.899 | 0.21584 | 0.50933 | Continue to Monitor
FMC | Fayette - 2641 Palumbo Dr - Lexington | 123 | Lexington - Palumbo Dr - W of Substation | 4.6845 | 363 | 2016-07-23 | 5.516% | 0% | 0% | 0% | 0.47% | 0% | 1.271% | 0% | 0% | 92.74% | 18.9285 | 71.7547 | 0.069538 | 0.19583 | Continue to Monitor
FMC | County - Road - Town | 124 | Town - Road - General Area | 0.022366 | 1 | 2018-02-10 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 69.34 | 346.7 | 0.2 | 1 | Continue to Monitor
HIGBY MILL 12KV | Fayette - 308 Waveland Museum Ln - Lexington | 128 | Lexington - Wyndham Hills Dr - W of Substation | 6.493 | 531 | 2018-06-16 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 88.79% | 0% | 11.21% | 10.9753 | 48.3007 | 0.51443 | 2.5045 | Continue to Monitor
BELT LINE | Fayette - 1090 W. New Circle Rd - Lexington | 129 | Lexington - Georgtown Rd, Price Rd, & Main St - S of Substation | 16.0425 | 1975 | 2017-08-12 | 0.5432% | 0% | 2.658% | 0% | 16.1% | 0% | 2.758% | 52.83% | 25.11% | 0% | 49.5974 | 42.8649 | 0.39521 | 0.52273 | Tree Trim Scheduled for 2021
LEXINGTON WATER COMPANY 12KV | Fayette - 2300 Richmond Rd - Lexington | 130 | Lexington - Richmond Rd. - E of Substation | 24.5238 | 3212 | 2020-08-22 | 22.67% | 1.804% | 0.4034% | 0% | 18.55% | 0% | 20.65% | 5.336% | 0% | 30.58% | 31.8664 | 46.9039 | 0.31118 | 0.41262 | Continue to Monitor
LAKESHORE | Fayette - 3710 Richmond Rd - Lexington | 132 | Lexington - Richmond Rd - SE of Substation | 59.8512 | 1109 | 2019-01-19 | 0.2067% | 0.1647% | 49.09% | 0.2342% | 20.61% | 0% | 3.629% | 8.215% | 0% | 17.85% | 149.596 | 52.8719 | 1.1166 | 1.2959 | Continue to Monitor
LAKESHORE | Fayette - 3710 Richmond Rd - Lexington | 133 | Lexington - Richmond Rd - N of Substation | 8.4736 | 1326 | 2018-03-03 | 7.371% | 0% | 0% | 0% | 92.61% | 0% | 0% | 0% | 0% | 0.02135% | 17.9093 | 73.851 | 0.13843 | 0.53307 | Continue to Monitor
LAKESHORE | Fayette - 3710 Richmond Rd - Lexington | 134 | Lexington - Richmond Rd & Yorkshire Blvd - N of Substation | 7.4225 | 1055 | 2018-03-03 | 13.79% | 0% | 0% | 0% | 1.244% | 0% | 4.317% | 0% | 80.65% | 0% | 8.4102 | 23.9194 | 0.1719 | 0.74065 | Continue to Monitor
RACE STREET 12KV | Fayette - 420 Corral St - Lexington | 139 | Lexington - Midland Ave. , Mian St. & water St. - W of Substation | 2.7484 | 16 | Underground Circuit | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 25.6508 | 89.4333 | 0.33205 | 0.5 | Continue to Monitor
IBM | Fayette - 740 W New Circle Rd - Lexington | 140 | Lexington - Newtown Rd - N of Substation | 26.0329 | 944 | 2017-12-30 | 0.1117% | 0% | 0% | 0% | 0.7172% | 0% | 3.433% | 0% | 33.43% | 62.31% | 55.6631 | 98.4899 | 0.80807 | 2.1667 | Continue to Monitor
CLAYS MILL | Fayette - 4454 Clays Mill Rd - Lexington | 145 | Lexington - Glenview Dr - NW of Substation | 30.2696 | 1907 | 2018-02-03 | 0.5935% | 0% | 0.06183% | 0% | 85.38% | 0% | 3.567% | 7.422% | 0% | 2.979% | 39.2223 | 22.6078 | 0.34938 | 0.43154 | Continue to Monitor
CLAYS MILL | Fayette - 4454 Clays Mill Rd - Lexington | 146 | Lexington - Clays Mill Rd & Man O War Blvd - N of Substation | 11.8053 | 926 | 2017-04-08 | 13.87% | 0% | 10.41% | 0% | 5.573% | 0% | 1.75% | 42.98% | 0% | 25.42% | 82.8826 | 119.8743 | 0.58738 | 0.53986 | Tree Trim Scheduled for 2021
CLAYS MILL | Fayette - 4454 Clays Mill Rd - Lexington | 148 | Lexington - Weber Way - E of Substation | 10.2327 | 1099 | 2017-10-21 | 55.08% | 0% | 3.112% | 0% | 17.55% | 0% | 6.288% | 0.6654% | 0% | 17.3% | 24.8659 | 43.6012 | 0.26362 | 0.61999 | Continue to Monitor
LAKESHORE | Fayette - 3710 Richmond Rd - Lexington | 152 | Lexington - Richmond Rd - NW of Substation | 1.6104 | 8 | 2018-09-01 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 21.6508 | 49.7542 | 0.1 | 0.25 | Continue to Monitor
STANFORD | Lincoln - 746 KY Highway 78 - Stanford | 155 | Stanford - KY Highway 78 & US Highway 27 - SE of Substation | 18.0526 | 297 | 2018-08-11 | 1.1% | 0% | 1.286% | 0% | 0.9402% | 0% | 2.679% | 86.33% | 0% | 7.664% | 33.5782 | 37.7188 | 0.25757 | 0.16777 | Continue to Monitor
PICADOME 4KV | Fayette - 1620 Harrodsburg Rd - Lexington | 158 | Lexington - St Joseph Dr - SE of Substation | 2.2144 | 458 | 2019-12-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 98.32% | 0% | 1.677% | 15.0859 | 26.508 | 0.1188 | 0.069731 | Continue to Monitor
VILEY ROAD | Fayette - 308 Alexandria Rd. - Lexington | 159 | Lexington - Leestown Rd & Masterson Station - NW of Substation | 11.9863 | 1093 | 2016-07-09 | 0% | 0% | 0% | 0% | 92.53% | 0% | 0.3272% | 0% | 0% | 7.143% | 29.6384 | 15.0393 | 0.1925 | 0.20051 | Continue to Monitor
DANVILLE 1 12KV | Boyle - 494 S 4TH ST - Danville | 162 | Danville - 4th St - S of Substation | 13.3294 | 1275 | 2020-11-07 | 5.622% | 0% | 0% | 65.39% | 0% | 1.762% | 22.64% | 4.584% | 0% | 0% | 32.9673 | 46.3902 | 0.27352 | 0.4531 | Continue to Monitor
DANVILLE WEST | Boyle - 1353 Lebanon Rd - Danville | 167 | Danville - Lebanaon Rd - SW of Substation | 6.548 | 23 | 2016-07-11 | 32.82% | 0% | 0% | 0% | 0% | 0% | 67.18% | 0% | 0% | 0% | 24.5189 | 56.3036 | 0.31268 | 0.3913 | Continue to Monitor
EASTLAND | Fayette - 1159 Industry Rd - Lexington | 182 | Lexington - Eastland Pky - E of Substation | 17.6689 | 2256 | 2019-01-24 | 0.3064% | 0% | 1.497% | 0% | 0.1732% | 0% | 0.04503% | 97.76% | 0% | 0.221% | 90.9552 | 261.5286 | 0.71213 | 1.1145 | Reliability Improvements Scheduled for 2021
ASHLAND AVENUE | Fayette - 448 S Ashland Ave. - Lexington | 187 | Lexington - High St. - NW of Substation | 3.8066 | 853 | 2019-12-21 | 0% | 0% | 0% | 0.6163% | 22.59% | 0% | 13.09% | 4.329% | 53% | 6.383% | 26.8919 | 39.371 | 0.35763 | 0.2386 | Continue to Monitor
HUME ROAD | Fayette - 2319 Hume Rd. - Lexington | 193 | Lexington - I75, Man O' War Blvd, & Blackford Pkwy - SE of Substation | 6.9323 | 531 | 2021-04-17 | 0% | 0% | 98.97% | 0% | 1.029% | 0% | 0% | 0% | 0% | 0% | 34.512 | 8.6324 | 0.89104 | 1.0019 | Continue to Monitor
HUME ROAD | Fayette - 2319 Hume Rd. - Lexington | 194 | Lexington - Winchester Rd, Sir Barton Way, Executive Dr, & Elkhorn Rd - E of Substation | 8.1433 | 314 | 2021-04-17 | 0% | 0% | 0% | 16.75% | 2.098% | 0% | 0.1566% | 55.92% | 24.22% | 0.8508% | 93.8856 | 60.6859 | 0.37916 | 1.0765 | Trees Trimmed in 2021
LAKESHORE | Fayette - 3710 Richmond Rd - Lexington | 195 | Lexington - Hays Blvd & Chilesburg Rd - E of Substation | 12.6748 | 939 | 2019-01-19 | 0% | 0% | 10.52% | 0% | 14.5% | 0% | 14.94% | 31.13% | 0% | 28.92% | 0.5476 | 1.4658 | 0.0059543 | 0.011861 | Continue to Monitor
LONDON | Laurel - Near corner of Foster Heights & Substation Rd - London | 203 | London - Locus St - SW of Substation | 1.7023 | 96 | 2019-12-31 | 59.59% | 0% | 0% | 0% | 1.471% | 0% | 4.156% | 0% | 0% | 34.78% | 11.5973 | 10.6316 | 0.17691 | 0.23958 | Continue to Monitor
LONDON 2 | Laurel - Near corner of Foster Heights & Substation Rd - London | 205 | London - S & N on McWhorter Rd | 40.5075 | 1827 | 2019-12-31 | 1.884% | 0% | 3.456% | 0% | 22.2% | 0% | 3.649% | 54.08% | 1.43% | 13.29% | 94.6133 | 226.1243 | 1.5965 | 4.6378 | Continue to Monitor
CAMPBELLSVILLE 2 | Taylor - 620 Clem Haskins Blvd. - Campbellsville | 208 | Campbellsville - Industrial Rd - SE of Substation | 1.7879 | 11 | 2019-12-31 | 0% | 0% | 0% | 0% | 90.36% | 0% | 0% | 0% | 0% | 9.637% | 35.3864 | 167.8939 | 0.27273 | 1.1818 | Continue to Monitor
COLUMBIA | Taylor - 114 Lindsey Wilson St - Columbia | 209 | Columbia - KY HWY 3491 & KY 55 - N of Substation | 43.3921 | 919 | 2019-03-30 | 1.275% | 0% | 1.482% | 0% | 92.37% | 0% | 0.7607% | 2.909% | 0% | 1.203% | 74.123 | 52.7499 | 0.86799 | 1.1392 | Continue to Monitor
CARON | Laurel - 1136 South Laurel Rd - London | 213 | London - S Laurel Rd - S of Substation | 3.4556 | 146 | 2019-06-15 | 19.08% | 0% | 0% | 0% | 8.992% | 0% | 11.11% | 11.55% | 41.3% | 7.962% | 182.6856 | 127.5576 | 1.5757 | 1.9474 | Continue to Monitor
FARISTON | Laurel - 57 Rocky Branch Rd - North Corbin | 216 | North Corbin - S Laurel Rd - S of Substation | 3.2127 | 90 | 2019-03-26 | 0% | 0% | 0% | 0% | 1.601% | 0% | 6.764% | 90.74% | 0% | 0.8988% | 46.381 | 158.1468 | 0.34491 | 1.1671 | Continue to Monitor
WILLIAMSBURG SOUTH | Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg | 226 | Williamsburg - Highway 25 - N of Substation | 34.8371 | 1283 | 2019-01-22 | 0.02998% | 0% | 3.901% | 0.1822% | 8.144% | 0% | 0.8023% | 84.32% | 0% | 2.615% | 113.7271 | 116.307 | 0.76616 | 0.65466 | Continue to Monitor
WILLIAMSBURG SOUTH | Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg | 227 | Williamsburg - Savoy Clear Creek Rd - N of Substation | 5.3659 | 68 | 2018-12-31 | 0% | 0% | 3.524% | 0% | 4.536% | 0% | 0.105% | 91.41% | 0% | 0.4273% | 119.6048 | 209.1787 | 0.68313 | 0.65217 | Continue to Monitor
WILLIAMSBURG SOUTH | Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg | 230 | Williamsburg - Highway 92 - N of Substation | 25.6012 | 653 | 2018-12-29 | 0% | 0% | 0.02468% | 0% | 19.93% | 0% | 0.7394% | 53.86% | 0% | 25.45% | 208.5216 | 717.6118 | 0.45364 | 0.83784 | Continue to Monitor
WILLIAMSBURG | Whitley - Corner of 2nd and 3rd St - Williamsburg | 235 | Williamsburg - 5th St - W of Substation | 3.3259 | 274 | 2018-12-31 | 0% | 0% | 0% | 0% | 6.571% | 0% | 32.74% | 58.64% | 0% | 2.05% | 14.6813 | 65.9472 | 0.06622 | 0.23113 | Continue to Monitor
MANCHESTER | Clay - 1195 HWY 687 (Town Branch Rd) - Manchester | 250 | Manchester - Town Branch Rd - NE of Substation | 23.9809 | 1054 | 2020-02-29 | 0.1378% | 0% | 0% | 20.16% | 1.306% | 0% | 5.633% | 68.65% | 0% | 4.109% | 234.972 | 225.8177 | 1.7694 | 2.8319 | Trees Trimmed in 2020
CORBIN EAST | Knox - Corner of State HWY 1232 and E Barbourville Rd - Corbin | 275 | Corbin - Barbourville Rd - E of Substation | 30.2304 | 860 | 2015-10-20 | 0.3113% | 0% | 0.9839% | 0% | 2.451% | 0% | 0.3044% | 95.37% | 0% | 0.5825% | 172.2496 | 134.7043 | 1.1 | 1.2301 | Reliability Improvements Scheduled for 2021
CORBIN EAST | Knox - Corner of State HWY 1232 and E Barbourville Rd - Corbin | 279 | Corbin - Pennington Rd - S of Substation | 9.0101 | 391 | 2016-10-28 | 0.2274% | 0% | 0.06336% | 0% | 10.27% | 0% | 0.3029% | 87.01% | 0% | 2.13% | 68.8022 | 255.6212 | 0.43032 | 1.2861 | Tree Trim Scheduled for 2021
PINEVILLE | Bell - Corner of E Park Ave and Maple St - Pineville | 301 | Pineville - US HWY 25E & KY HWY 66 - N of Substation | 25.2713 | 1148 | 2017-01-02 | 0.6729% | 0% | 0% | 0.04094% | 15.23% | 0% | 1.16% | 64% | 0% | 18.9% | 140.2796 | 203.0862 | 1.6862 | 1.6579 | Tree Trim Scheduled for 2021
CROCKETT | Bell - On HWY 66 across the street from Chaz Coal Co - Pineville | 305 | Pineville - State HWY 66 - SW of Substation | 1.7748 | 11 | 2019-01-22 | 0% | 0% | 0% | 0% | 1.224% | 0% | 2.045% | 81.79% | 0% | 14.94% | 395.3736 | 653.4333 | 1.5239 | 2.6364 | Continue to Monitor
MELDRUM | Bell - HWY 25/Wilderness Rd S of HWY 2486 Middlesborough | 308 | Middlesborough - US HWY 25E - N of Substation | 49.7599 | 831 | 2016-06-24 | 0.1213% | 0% | 0.04407% | 0% | 1.306% | 0% | 0.3167% | 98.03% | 0% | 0.1783% | 547.5724 | 607.0359 | 3.367 | 2.8013 | Continue to Monitor
GREASY CREEK 12KV | Bell - US HWY 25 at HWY 3085 - Pineville US HWY 25 AT HWY 3085 PINEVILLE | 310 | Pineville - Mocking Bird - E of Substation | 6.9951 | 168 | 2020-08-27 | 0.6424% | 0% | 0% | 4.329% | 0.07836% | 0% | 0.7251% | 93.66% | 0% | 0.5649% | 131.5571 | 284.1676 | 1.518 | 2.7319 | Trees Trimmed in 2020
STINKING CREEK | Knox - Croner of New US HWY 25 E and HWY 930 - Barbourville | 313 | Barbourville - US HWY 25E - S of Substation | 36.4007 | 827 | 2020-08-15 | 0.2103% | 0% | 0.4121% | 0.5784% | 8.116% | 0% | 1.903% | 88.77% | 0% | 0.008755% | 180.4711 | 263.5746 | 1.7692 | 2.4858 | Trees Trimmed in 2020
MILL CREEK - KU | Bell - 5539 HWY 221 Kettle Island - Pineville | 315 | Pineville - Martha Lock Branch Rd - SW of Substation | 14.2453 | 342 | 2017-02-03 | 0% | 0% | 0.09318% | 0.06916% | 3.09% | 0% | 3.505% | 93.04% | 0% | 0.2004% | 130.5954 | 67.1001 | 1.0563 | 1.0719 | Tree Trim Scheduled for 2021
MILL CREEK - KU | Bell - 5539 HWY 221 Kettle Island - Pineville | 316 | Pineville - State HWY 221 - NE of Substation | 30.6064 | 337 | 2017-04-07 | 0.1549% | 0% | 0% | 0% | 7.513% | 0% | 20.96% | 67.59% | 0% | 3.776% | 438.3586 | 888.1025 | 2.1257 | 2.5419 | Tree Trim Scheduled for 2021
STRAIGHT CREEK | Bell - 3582 HWY 66 Arjay - Pineville | 317 | Pineville - State HWY 66 - NE of Substation | 8.0711 | 219 | 2018-01-16 | 0% | 0% | 0% | 29.12% | 17.08% | 0% | 6.322% | 41.28% | 0% | 6.195% | 31.9099 | 48.7047 | 0.38956 | 0.42343 | Continue to Monitor
DEER BRANCH | Bell - HWY 66 0.5 miles S of Buffalo Hollow Rd, 7.5 miles N of HWY 221 - Pineville | 319 | Pineville - State HWY 66 - S of Substation | 13.6752 | 228 | 2018-02-23 | 0.1407% | 0% | 0% | 0% | 0.3973% | 0% | 7.95% | 70.85% | 0% | 20.66% | 402.0374 | 426.1295 | 2.2781 | 1.2351 | Reliability Improvements Scheduled for 2021
DEER BRANCH | Bell - Hwy 66 0.5 miles S of Buffalo Hollow Rd - Pineville | 320 | Pineville - Hwy 66 & Buffalo Hollow Rd - N of Substation | 2.567 | 27 | 2018-03-02 | 0% | 0% | 7.839% | 0% | 0% | 0% | 34.69% | 57.47% | 0% | 0% | 100.1562 | 174.3216 | 0.65 | 1.3333 | Continue to Monitor
PUCKETT CREEK | Harlan - 5627 E HWY 72 Pathfork - Alva | 321 | Alva - E Highway 72 - SE of Substation | 3.4034 | 62 | 2018-01-02 | 0% | 0% | 0% | 0% | 2.065% | 0% | 1.442% | 94.52% | 0% | 1.972% | 198.6436 | 295.3113 | 1.0401 | 2.1129 | Continue to Monitor
PUCKETT CREEK | Harlan - 5627 E HWY 72 Pathfork - Alva | 322 | Alva - E Highway 72 - NW of Substation | 10.5193 | 295 | 2018-01-02 | 0.6028% | 0% | 0.7716% | 0% | 8.437% | 0% | 70.59% | 18.89% | 0% | 0.702% | 120.6257 | 125.8265 | 0.98455 | 1.186 | Continue to Monitor
WACO | Madison - 3761 New Irvine Rd - Madison East | 330 | Madison East - College Hill Rd - N of Substation | 7.4893 | 184 | 2018-11-10 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 4.8643 | 2.4596 | 0.036808 | 0.048475 | Continue to Monitor
YELLOW ROCK NORTH | Lee Ky - 584 New Yellow Rock Rd - Beattyville | 332 | Beattyville - New Yellow Rock Rd - N of Substation | 0 | 57 | 2016-05-12 | 0% | 0% | 0% | 0% | 99.76% | 0% | 0.237% | 0% | 0% | 0% | 320.9401 | 313.3939 | 1.6176 | 2.0175 | Continue to Monitor
BEAR TRACK | Lee Ky - 584 New Yellow Rock Rd - Beattyville | 333 | Beattyville - New Yellow Rock Rd - S of Substation | 9.9809 | 17 | 2020-10-31 | 0% | 0% | 0% | 0% | 10.08% | 0% | 2.441% | 87.47% | 0% | 0% | 161.3647 | 443.7678 | 0.94235 | 3.6737 | Trees Trimmed in 2020
RICHMOND INDUSTRIAL | Madison - 110 Mikron Way - Richmond | 344 | Richmond - 1.51 miles S of Substation | 1.5373 | 4 | 2019-09-07 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 17.6973 | 88.4867 | 0.12 | 0.6 | Continue to Monitor
MIDDLESBORO 2 12KV #2 | Bell - Intersection of Cumberland Ace and S 38th St - Middlesborough | 356 | Middlesborough - S 38th St - S of Substation | 7.4295 | 556 | 2019-03-02 | 6.161% | 0% | 0.03503% | 0% | 6.691% | 0% | 2.377% | 83.05% | 0% | 1.682% | 33.0307 | 35.8696 | 0.55241 | 0.73255 | Continue to Monitor
MIDDLESBORO 2 12KV | Bell - Intersection of Cumberland Ace and S 38th St - Middlesborough | 360 | Middlesborough - State HWY 74 - E of Substation | 30.4807 | 400 | 2016-07-01 | 0.08659% | 0% | 0.1176% | 0% | 36.75% | 0% | 11% | 51.5% | 0% | 0.5471% | 240.0154 | 386.4223 | 1.1203 | 1.2345 | Tree Trim Scheduled for 2021
MIDDLESBORO 1 12KV | Bell - Corner of N 19th and Ironwood Rd - Middlesborough | 364 | Middlesborough - Nutwood Rd - N of Substation | 10.1918 | 560 | 2018-03-29 | 0.9957% | 0% | 2.177% | 0% | 9.078% | 0% | 30.01% | 55.29% | 0% | 2.446% | 85.3487 | 74.2142 | 1.1139 | 1.3751 | Continue to Monitor
MIDDLESBORO 1 12KV | Bell - Corner of N 19th and Ironwood Rd - Middlesborough | 366 | Middlesborough - Asbury Rd & N 12th St - E of Substation | 10.8462 | 446 | 2018-05-03 | 0% | 0% | 0% | 0% | 7.363% | 0% | 1.727% | 90.45% | 0% | 0.4584% | 112.6406 | 226.7837 | 0.83361 | 1.7847 | Continue to Monitor
MIDDLESBORO 1 4KV | Bell - Corner of N 19th and Ironwood Rd - Middlesborough | 371 | Middlesborough - N 19th St - S of Substation | 0 | 200 | 2018-02-23 | 0% | 0% | 0% | 0% | 0% | 0% | 89.55% | 0% | 0% | 10.45% | 7.7338 | 15.289 | 0.078849 | 0.16008 | Continue to Monitor
MIDDLESBORO 1 4KV | Bell - Corner of N 19th and Ironwood Rd - Middlesborough | 372 | Middlesborough - Lynnwood Dr - E of Substation | 0 | 402 | 2018-02-23 | 0% | 0% | 0% | 0% | 0.8013% | 0% | 7.089% | 92.11% | 0% | 0% | 25.9998 | 34.4565 | 0.18312 | 0.19156 | Continue to Monitor
DELAPLAIN | Scott Ky - 413 Triport Cir - Sadieville | 403 | Sadieville - 0.41 Miles N of Substation | 0.1219 | 1 | 2019-09-28 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 106.31 | 31.55 | 0.8 | 1 | Continue to Monitor
DAYHOIT | Harlan - Dayhoit Dr (Keith Tremont Rd) - Harlan | 414 | Harlan - US HWY 119 - N of Substation | 14.7681 | 575 | 2019-10-19 | 0.7579% | 0% | 0% | 0% | 36.69% | 0% | 1.705% | 60.85% | 0% | 0% | 227.1914 | 201.2107 | 1.9285 | 2.4489 | Continue to Monitor
DAYHOIT | Harlan - Dayhoit Dr (Keith Tremont Rd) - Harlan | 415 | Harlan - S US HWY 119 - S of Substation | 14.4663 | 400 | 2019-11-09 | 0.6596% | 0% | 0% | 0% | 23.29% | 0% | 3.378% | 72.67% | 0% | 0% | 262.7079 | 366.2814 | 2.1525 | 2.4882 | Continue to Monitor
CAWOOD | Bell - Off Slack Hollow Rd just N of S Old US HWY 421 - Cawood | 418 | Cawood - US HWY 421 Bypass - W of Substation | 31.7763 | 697 | 2021-03-31 | 1.821% | 0% | 0% | 0% | 68.09% | 0% | 3.172% | 20.15% | 0% | 6.764% | 181.06 | 118.7262 | 1.5306 | 1.574 | Continue to Monitor
CAWOOD | Bell - Off Slack Hollow Rd just N of S Old US HWY 421 - Cawood | 419 | Cawood - US HWY 421 Bypass - E of Substation | 23.0101 | 309 | 2021-01-07 | 0.4042% | 0% | 0% | 0% | 11.15% | 0% | 7.124% | 75.56% | 0% | 5.756% | 451.7113 | 963.1832 | 2.4576 | 5.8824 | Trees Trimmed in 2021
GEORGETOWN 4KV | Scott Ky - 207 W Clinton St - Georgetown | 420 | Georgetown - W & E on Clinton St | 3.9572 | 458 | 2018-10-20 | 0% | 0% | 0% | 0% | 13.83% | 0% | 84.09% | 0.8334% | 0% | 1.238% | 12.5229 | 18.3273 | 0.091393 | 0.12196 | Continue to Monitor
NEWTOWN | Scott Ky - 5849 Paris Pike - Georgetown | 430 | Georgetown - US 460 Pike - E of Substation | 68.1783 | 797 | 2021-01-16 | 4.002% | 0.4367% | 4.295% | 0% | 2.163% | 0% | 3.915% | 5.733% | 73.41% | 6.046% | 25.4632 | 24.2097 | 0.18816 | 0.21944 | Continue to Monitor
TURTLE CREEK | Harlan - HWY 990 - Cawood | 432 | Cawood - HWY 990 - SW of Substation | 3.646 | 90 | 2019-07-06 | 0% | 0% | 0% | 0% | 89.92% | 0% | 9.621% | 0.4602% | 0% | 0% | 196.4468 | 236.5628 | 1.314 | 1.7518 | Continue to Monitor
LEMONS MILL | Scott Ky - 125 Carley Ct - Georgetown | 441 | Georgetown - Lemons Mill Rd - SE of Substation | 27.2051 | 1317 | 2018-11-10 | 0.3976% | 0% | 4.426% | 0% | 80.99% | 0% | 1.716% | 0.02555% | 0% | 12.45% | 89.7207 | 164.0881 | 0.69124 | 1.0746 | Continue to Monitor
LEMONS MILL | Scott Ky - 125 Carley Ct - Georgetown | 442 | Georgetown - Holmes Dr - N of Substation | 1.5243 | 56 | 2018-11-10 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0.68 | 3.4 | 0.0070175 | 0.035088 | Continue to Monitor
POOLE | Webster - 211 S Route 56 - Poole | 446 | Poole - US Hwy 41A - W of Substation | 7.0416 | 200 | 2019-07-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 31.4334 | 126.4176 | 0.25036 | 1.005 | Continue to Monitor
ROGERS GAP | Scott Ky - 192 Harbor Village Dr - Stamping Ground | 451 | Stamping Ground - Cincinnati Rd - N of Substation | 70.0595 | 1142 | 2020-01-11 | 0.6124% | 0% | 1.656% | 0.1558% | 37.23% | 0% | 0.8405% | 0.9531% | 4.118% | 54.43% | 371.9094 | 155.6946 | 3.4887 | 3.5735 | Continue to Monitor
ADAMS 12KV | Scott - 900 W Main St - Georgetown | 453 | Georgetown Rd - Frankfort Rd - E of Substation | 42.6685 | 1550 | 2019-04-20 | 6.067% | 0.2345% | 0% | 0% | 56.38% | 0% | 0.3172% | 37% | 0% | 0% | 41.6814 | 44.2745 | 0.85439 | 1.1472 | Continue to Monitor
CUMBERLAND | Harlan - Russel Dr just S of E Main St - Cumberland | 454 | Cumberland - Raymond D Hatfield Blvd - N of Substation | 9.7426 | 542 | 2016-02-12 | 0% | 0% | 0% | 0% | 2.407% | 0% | 1.119% | 91.24% | 0% | 5.239% | 147.7539 | 404.9636 | 0.87807 | 1.284 | Continue to Monitor
CUMBERLAND | Harlan - Russel Dr just S of E Main St - Cumberland | 455 | Cumberland - N US HWY 119 - S & E of Substation | 5.5448 | 229 | 2016-02-12 | 0% | 0% | 0% | 0% | 14.38% | 0% | 0% | 63.98% | 21.58% | 0.05775% | 44.4156 | 171.4101 | 0.36398 | 1.3739 | Continue to Monitor
CLOVERLICK | Harlan - HWY 179 1/4 miles W from intersection of HWY 2006 and HWY 179 - Cumberland | 458 | Cumberland - State Hwy 2006 - S of Substation | 8.8058 | 147 | 2016-03-15 | 0.06418% | 0% | 0% | 0% | 1.02% | 0% | 9.487% | 89.43% | 0% | 0% | 117.9321 | 229.3809 | 1.0698 | 0.96122 | Continue to Monitor
BLACK MOUNTAIN | Harlan - Black Mountain Rd - Lynch | 467 | Lynch - Radar Station Rd - SW of Substation | 4.1409 | 10 | 2018-09-26 | 0% | 0% | 0% | 0% | 38.73% | 0% | 0% | 61.27% | 0% | 0% | 753.5155 | 1102 | 2.4909 | 4 | Continue to Monitor
OXFORD | Scott Ky - 1827 Oxford Dr - Georgetown | 472 | Georgetown - Oxford Rd - S of Substation | 17.5142 | 1082 | 2019-08-31 | 0% | 0% | 0.09853% | 3.88% | 0.221% | 0% | 0% | 93.91% | 0% | 1.888% | 26.2202 | 34.6814 | 0.36317 | 0.4442 | Continue to Monitor
SHADRACK | Franklin - 74 Bethel Ln - Frankfort | 475 | Frankfort - US HWY 127 - N of Substation | 47.1241 | 568 | 2018-03-09 | 5.591% | 0% | 0% | 0% | 10.98% | 0% | 21.21% | 57.88% | 3.437% | 0.8948% | 72.1315 | 12.9916 | 0.5113 | 0.61946 | Continue to Monitor
HIGHSPLINT | Harlan - KY 38 - Highsplint | 483 | Highsplint - Gano St - E of Substation | 0.059622 | 1 | Only0.05milesofcircuit | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 105.8167 | 55.5667 | 0.75 | 1 | Continue to Monitor
ALEXANDER | Woodford - 2915 Troy Pike - Versailles | 501 | Woodford South - Troy Pike - N of Substation | 55.7721 | 1993 | 2020-03-21 | 1.022% | 0.2364% | 0.7024% | 0% | 4.935% | 0% | 3.601% | 56.63% | 0% | 32.88% | 36.9118 | 49.5503 | 0.27099 | 0.19479 | Trees Trimmed in 2020
VERSAILLES | Woodford - 150 Tanner Alley - Versailles | 505 | Versailles - Main St - N of Substation | 5.2591 | 546 | 2020-06-10 | 0% | 0% | 0% | 0% | 44.86% | 0% | 25.83% | 26.39% | 0% | 2.912% | 34.7686 | 50.6778 | 0.45005 | 0.42315 | Trees Trimmed in 2020
VERSAILLES | Woodford - 150 Tanner Alley - Versailles | 506 | Versailles - Main St - S of Substation | 4.937 | 501 | 2020-06-10 | 0% | 0.4871% | 0% | 0.2972% | 0% | 0% | 1.392% | 16.02% | 0% | 81.8% | 73.4583 | 182.0539 | 0.62132 | 1.1397 | Continue to Monitor
VERSAILLES BYPASS | Woodford - 350 Markham Dr - Versailles | 508 | Versailles - US 60 Bypass - SE of Substation | 4.0763 | 339 | 2020-06-10 | 24.09% | 0% | 0% | 0% | 0.173% | 32.75% | 5.8% | 0% | 0% | 37.2% | 134.543 | 78.2029 | 1.148 | 1.9973 | Continue to Monitor
VERSAILLES BYPASS | Woodford - 350 Markham Dr - Versailles | 511 | Versailles - 0.28 miles E of Substation | 0.29036 | 4 | 2020-06-20 | 0% | 0% | 0% | 0% | 71.84% | 0% | 28.16% | 0% | 0% | 0% | 17.365 | 86.825 | 0.1 | 0.5 | Continue to Monitor
VERSAILLES WEST | Woodford - 115 Rutter Rd - Versailles | 513 | Versailles - Clifton Rd - N of Substation | 25.9434 | 879 | 2021-04-03 | 6.249% | 0% | 0% | 0.2916% | 1.172% | 0% | 1.334% | 80.05% | 0% | 10.9% | 49.3112 | 56.2541 | 0.39977 | 0.28346 | Trees Trimmed in 2021
ALEXANDER | Woodford - 2915 Troy Pike - Versailles | 515 | Versailles - N & S on McCowans Ferry Rd - E of Substation | 49.1063 | 1377 | 2015-08-29 | 1.633% | 0% | 0.04806% | 0% | 27.29% | 0% | 0.04337% | 0.8669% | 0.4279% | 69.7% | 90.3534 | 128.7567 | 1.1273 | 1.0042 | Continue to Monitor
WOODLAKE | Franklin - 1635 Woodlake Rd - Frankfort | 525 | Frankfort - Woodlake Rd - N of Substation | 0.0035017 | 1 | No Trimming Necessary | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 69.79 | 97.95 | 0.6 | 1 | Continue to Monitor
SCIENCE HILL | Pulaski - 45 E HWY 635 neat the intersection of E hWY 635 and Maple Ln - Science Hill | 527 | Science Hill - N Highway 27 - NW of Substation | 5.3718 | 190 | 2018-05-19 | 0% | 0% | 98.01% | 0% | 0% | 0% | 1.988% | 0% | 0% | 0% | 42.2805 | 34.2318 | 0.64386 | 1.0209 | Continue to Monitor
WAYNESBURG | Lincoln - On Old Somerset Rd (HWY 1247) just S of Clear Fork Rd - Waynesburg | 546 | Waynesburg - KY HWY 1247 - S of Substation | 9.9742 | 263 | 2017-12-02 | 0.3547% | 0% | 0.6819% | 0.3122% | 1.219% | 0% | 0% | 97.43% | 0% | 0% | 10.4982 | 17.4944 | 0.10252 | 0.14365 | Continue to Monitor
WAYNESBURG | Lincoln - On Old Somerset Rd (HWY 1247) just S of Clear Fork Rd - Waynesburg | 547 | Waynesburg - KY HWY 1247 - N of Substation | 14.9645 | 361 | 2018-02-10 | 0.3627% | 0% | 36.22% | 0% | 8.328% | 0% | 0% | 32.23% | 0% | 22.87% | 103.1024 | 235.4978 | 1.0889 | 2.6716 | Reliability Improvements Scheduled for 2021
LIBERTY | Casey - 1351 E KY HWY 70 - Liberty | 551 | Liberty - E KY 70 - SW of Substation | 22.6611 | 696 | 2017-04-12 | 3.787% | 0% | 1.361% | 0.09497% | 0% | 0% | 1.686% | 86.62% | 0% | 6.456% | 80.6808 | 257.0456 | 0.50211 | 1.2734 | Tree Trim Scheduled for 2021
LIBERTY | Casey - 1351 E KY HWY 70 - Liberty | 552 | Liberty - E KY 70 - NE of Substation | 29.4938 | 514 | 2017-10-21 | 2.775% | 0% | 0% | 0.06757% | 0% | 0% | 1.328% | 94.34% | 0% | 1.492% | 90.005 | 135.5334 | 0.74287 | 0.93666 | Continue to Monitor
SHELBY CITY | Boyle - 401 Grubbs Ln - Junction City | 553 | Junction City - Hustonville Rd & Hwy 127 - SE & NE of Substation | 20.1283 | 877 | 2017-09-30 | 0.9887% | 0% | 85.43% | 0% | 4.909% | 0% | 4.782% | 3.894% | 0% | 0% | 26.4255 | 75.3641 | 0.23886 | 0.62469 | Continue to Monitor
EDDYVILLE | Lyon - 1765 S R 3305 - Eddyville | 560 | Eddyville - US HWY 62 & Riley Rd - NE of Substation | 48.2389 | 487 | 2016-04-09 | 2.354% | 0% | 20.04% | 0% | 18.04% | 0% | 7.434% | 31% | 21.05% | 0.08987% | 59.4871 | 95.5798 | 0.64727 | 0.88195 | Continue to Monitor
REVELO | McCreary - N of 4850 S HWY 1651 - Stearns-Whitley City | 577 | Stearns-Whitley City - N & S on State HWY 1651 | 16.9978 | 538 | 2015-06-30 | 0.6378% | 0% | 0.5275% | 3.026% | 17.99% | 0% | 0% | 77.7% | 0% | 0.1226% | 103.95 | 178.0581 | 0.84736 | 1.2867 | Tree Trim Scheduled for 2021
WILMORE 12KV | Jessamine - 210 W Linden St - Wilmore | 586 | Wilmore - Lexington Rd - N of Substation | 49.528 | 1284 | 2021-04-10 | 2.272% | 0% | 0.4651% | 0% | 15.16% | 0% | 0.9115% | 14.9% | 0% | 66.28% | 89.058 | 107.7649 | 0.61563 | 0.41669 | Continue to Monitor
MOUNT STERLING 12KV | Montgomery 346 Calk Ave - Mount Sterling | 601 | Mount Sterling - 686 Bypass - N of Substation | 18.063 | 1354 | 2019-01-12 | 9.677% | 0% | 3.496% | 0% | 3.067% | 0% | 1.144% | 19.18% | 0% | 63.44% | 7.0441 | 15.8695 | 0.098845 | 0.2029 | Continue to Monitor
MOUNT STERLING 12KV | Montgomery 346 Calk Ave - Mount Sterling | 602 | Mount Sterling - Richmond Ave - N of Substation | 3.9868 | 377 | 2019-01-12 | 0% | 0% | 0% | 0% | 0% | 0% | 86.97% | 0% | 0% | 13.03% | 5.4166 | 11.565 | 0.052353 | 0.074015 | Continue to Monitor
CAMARGO | Montgomery - 555 S Queen St - Mt Sterling | 603 | Mount Sterling - S Queen St - N of Substation | 16.4203 | 1295 | 2018-12-29 | 0.9676% | 1.941% | 4.469% | 0% | 2.451% | 0% | 1.957% | 16.04% | 71.45% | 0.7145% | 22.7708 | 63.3907 | 0.37427 | 1.2032 | Continue to Monitor
A O SMITH | Montgomery - 1871 Owingsville Rd - Mt. Sterling | 606 | Mount Sterling - Owingsville Rd - E of Substation | 1.5295 | 22 | 2018-02-26 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 37.2687 | 54.3758 | 0.35714 | 0.72727 | Continue to Monitor
A O SMITH | Montgomery - 1871 Owingsville Rd - Mt. Sterling | 608 | Mount Sterling - 6 miles W of Substation | 6.3244 | 211 | 2018-02-26 | 9.233% | 0% | 26.36% | 0% | 44.68% | 0% | 9.829% | 0% | 0% | 9.903% | 6.2927 | 6.3517 | 0.090608 | 0.14187 | Continue to Monitor
OWINGSVILLE | Montgomery - 69 W Paul Lewis Dr - Owingsville | 610 | Owingsville - Slate Ave - S of Substation | 8.6725 | 473 | 2017-12-23 | 16.72% | 0.4372% | 0% | 0% | 1.17% | 0% | 0.5096% | 0% | 0% | 81.17% | 41.2213 | 73.0868 | 0.62289 | 1.433 | Continue to Monitor
OWINGSVILLE | Montgomery - 69 W Paul Lewis Dr - Owingsville | 611 | Owingsville - W Main St - SW of Substation | 25.1064 | 721 | 2018-05-08 | 6.167% | 0.1797% | 0% | 0% | 65.59% | 0% | 1.87% | 0% | 0% | 26.2% | 29.2251 | 59.3147 | 0.41733 | 0.4265 | Continue to Monitor
SALT LICK | Bath - 11457 US HWY 60 E - Salt Lick | 612 | Salt Lick - US HWY 60 - SW of Substation | 30.0312 | 704 | 2018-02-19 | 0.2408% | 0% | 0% | 0.0555% | 2.713% | 0% | 0% | 10.92% | 85.33% | 0.7399% | 89.3989 | 341.5441 | 0.5123 | 1.3683 | Continue to Monitor
SALT LICK | Bath - 11457 US HWY 60 E - Salt Lick | 613 | Salt Lick - US HWY 60 - NE of Substation | 9.7189 | 232 | 2017-10-24 | 0.6059% | 0% | 0% | 0% | 57.07% | 0% | 0% | 38.68% | 0% | 3.646% | 22.0464 | 50.9302 | 0.22394 | 0.46517 | Continue to Monitor
FARMERS | Rowan - 6901 US 60 W - Morehead | 615 | Morehead - US HWY 60 - NE of Substation | 22.3323 | 620 | 2017-08-17 | 0.1422% | 1.176% | 4.832% | 0.7112% | 31.85% | 0% | 3.791% | 19.64% | 0% | 37.86% | 29.1498 | 67.9131 | 0.27999 | 0.82271 | Continue to Monitor
MOREHEAD 4KV | Rowan - 100 E Wilkinson Blvd - Morehead | 618 | Morehead - Wilkinson Blvd - SW of Substation | 1.1712 | 109 | 2016-11-12 | 0% | 0% | 41.29% | 0% | 0% | 0% | 58.71% | 0% | 0% | 0% | 11.949 | 12.8037 | 0.087428 | 0.12844 | Continue to Monitor
PARKER SEAL | Clark - 390 Mt Sterling Rd - Winchester | 629 | Winchester - Mt Sterling Rd - NE & S of Substation | 16.3349 | 403 | 2016-10-10 | 3.53% | 0% | 0.2419% | 0% | 22.93% | 0% | 16.36% | 3.02% | 47.39% | 6.528% | 39.4301 | 67.2347 | 0.55917 | 1.3018 | Continue to Monitor
WINCHESTER | Clark - 2 Almond St - Winchester | 632 | Winchester - 1st St - S of Substation | 0.60306 | 77 | 2016-07-24 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 7.3363 | 7.9232 | 0.067987 | 0.064935 | Continue to Monitor
WINCHESTER | Clark - 2 Almond St - Winchester | 633 | Winchester - Winn Ave - E of Substation | 0 | 190 | 2017-02-18 | 0% | 0% | 0% | 0% | 7.131% | 0% | 44.35% | 29.48% | 12.65% | 6.398% | 59.9699 | 266.9668 | 0.79754 | 3.5004 | Continue to Monitor
SYLVANIA 4KV | Clark - 439 E Washington St - Winchester | 635 | Winchester - New St - NW of Substation | 0 | 93 | 2017-02-18 | 0% | 0% | 0% | 0% | 96.62% | 0% | 3.379% | 0% | 0% | 0% | 25.508 | 52.2667 | 0.67559 | 2 | Continue to Monitor
BOONE AVENUE | Clark - 660 Boone Ave. - Winchester | 638 | Winchester - Boonesboro Rd & Hillcrest Dr - SW of Substation | 5.3401 | 307 | 2017-06-06 | 7.894% | 0% | 0% | 0% | 3.038% | 0% | 67.43% | 0% | 0% | 21.64% | 8.6956 | 15.7654 | 0.093781 | 0.14984 | Continue to Monitor
BOONESBORO | Clark - 170 Settlers Ln. - Winchester | 643 | Boonesboro - Ford Rd and HWY 418 - N and S of Substation | 8.9693 | 114 | 2018-08-22 | 1.974% | 0% | 0% | 0% | 8.328% | 0% | 85.73% | 3.968% | 0% | 0% | 50.9511 | 78.1532 | 0.43013 | 0.80702 | Continue to Monitor
EWINGTON | Montgomery - 4006 Old Owingsville Rd - Mt Sterling | 646 | Mt. Sterling - Old Owingsville Rd, Arlington Ave - S of Substation | 9.5324 | 608 | 2018-06-01 | 0% | 0% | 0% | 0% | 3.303% | 0% | 0% | 5.197% | 0% | 91.5% | 20.839 | 77.2462 | 0.31599 | 1.2181 | Continue to Monitor
EWINGTON | Montgomery - 4006 Old Owingsville Rd - Mt Sterling | 647 | Mt. Sterling - Owingsville Rd, Quisenberry Rd - N of Substation | 9.4944 | 59 | 2018-06-01 | 2.798% | 0% | 0% | 0% | 19.46% | 0% | 3.599% | 14.08% | 50.04% | 10.03% | 102.4286 | 93.9134 | 0.65816 | 0.7548 | Continue to Monitor
CAMARGO | Montgomery - 555 S Queen St - Mt Sterling | 658 | Mt Sterling - US 460 Hwy, By-Pass, Burley Dr - SW of Substation | 4.923 | 337 | 2018-08-22 | 0% | 0.6251% | 0% | 0% | 8.75% | 0% | 0.29% | 2.1% | 0% | 88.24% | 58.9661 | 228.7327 | 0.56075 | 2.3515 | Continue to Monitor
CAMARGO | Montgomery - 555 S Queen St - Mt Sterling | 659 | Mt Sterling - US Hwy 460 - SE of Substation | 47.1745 | 1011 | 2018-11-17 | 0.2854% | 0% | 0.8204% | 0% | 86.34% | 0% | 0.03696% | 7.856% | 4.162% | 0.501% | 135.5353 | 194.6145 | 1.6083 | 3.1736 | Continue to Monitor
BEECHMONT | Muhlenberg - 3660 Merle Travis Hwy - Beechmont | 695 | Beechmont - US Hwy 431 - N of Substation | 11.2716 | 315 | 2018-09-15 | 0.104% | 0% | 0.5874% | 0% | 80.92% | 8.653% | 0.141% | 8.728% | 0% | 0.8676% | 81.7992 | 188.0181 | 0.59469 | 1.3328 | Continue to Monitor
BEECHMONT | Muhlenberg - 3660 Merle Travis Hwy - Beechmont | 696 | Beechmont - US Hwy 431, Hazel Creek Rd - SE of Substation | 16.2553 | 371 | 2018-09-08 | 0% | 0% | 0% | 0.1184% | 90.08% | 0.2528% | 2.366% | 0% | 0% | 7.186% | 77.9058 | 117.4543 | 0.63358 | 1.2388 | Continue to Monitor
BROMLEY | Owen - 7205 Hwy 127 - New Liberty | 701 | Bromley - State Hwy 36, St Hwy 227, & Alexander Rd - W of Subst. | 75.6929 | 950 | 2018-12-08 | 0.6989% | 0% | 0.1065% | 1.078% | 20.04% | 0% | 1.381% | 64.82% | 0% | 11.88% | 190.8828 | 165.9483 | 1.2499 | 1.2668 | Continue to Monitor
CARROLLTON 4KV | Carroll - 802 Mason St - Carrollton | 705 | Carrollton - 9th St - N of Substation | 5.2957 | 499 | 2020-03-19 | 0% | 0% | 2.372% | 0% | 0% | 22.66% | 19.56% | 27.91% | 0% | 27.5% | 8.1436 | 10.6204 | 0.094008 | 0.13009 | Trees Trimmed in 2020
CARROLLTON 12KV | Carroll - 802 Mason St - Carrollton | 707 | Carrollton - HWY 227 - SE of Substation | 30.5357 | 747 | 2020-03-19 | 0.9265% | 0% | 2.359% | 0% | 8.97% | 0% | 14.68% | 52.68% | 6.243% | 14.15% | 162.4908 | 85.2894 | 1.4703 | 1.9658 | Trees Trimmed in 2020
CARROLLTON 12KV | Carroll - 802 Mason St - Carrollton | 709 | Carrollton - KY 36 - NW of Substation | 22.089 | 387 | 2016-02-16 | 0.9585% | 0% | 0% | 80.14% | 1.505% | 0% | 1.662% | 10.23% | 0% | 5.505% | 87.652 | 154.4043 | 0.58148 | 0.588 | Continue to Monitor
DAYTON-WALTHER | Carroll - 5220 Highway 42 E - Carrollton | 710 | Carrollton - D Rd & US HWY 42 - SW of Substation | 5.4501 | 48 | 2016-03-05 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 50.6794 | 59.6167 | 0.51854 | 1 | Continue to Monitor
OWENTON | Owen - 327 Gayle Avenue - Owenton | 715 | Owenton - Madison St - S of Substation | 1.4126 | 169 | 2016-09-10 | 0% | 0% | 0% | 0% | 8.074% | 0% | 91.93% | 0% | 0% | 0% | 5.8453 | 4.2639 | 0.059195 | 0.11291 | Continue to Monitor
GHENT | Carroll - 402 Liberty - Ghent | 717 | Ghent - US HWY 42 - NE & SW of Substation | 8.7257 | 287 | 2015-12-26 | 0.6088% | 0% | 53.61% | 0% | 0.3889% | 0% | 9.105% | 10.81% | 0% | 25.48% | 44.3011 | 103.9698 | 0.35077 | 1.115 | Continue to Monitor
HUNTERS BOTTOM | Trimble - 400 Hunter Heights Rd - Milton | 719 | Milton - N Spillman Lan, HWY 421 N - SE of Substation | 25.5417 | 502 | 2020-10-23 | 0.1891% | 0% | 26.05% | 0% | 9.433% | 0% | 0.2929% | 63.03% | 0% | 1.003% | 123.6692 | 149.4232 | 1.1831 | 1.1132 | Trees Trimmed in 2020
SCHOLLS | Owen - 970 HWY 127 N - Owenton | 724 | Owenton - HWY 127 N, State HWY 845 - NE of Substation | 12.5776 | 179 | 2016-05-13 | 19.66% | 0% | 0% | 0% | 0% | 0% | 47% | 0% | 0% | 33.33% | 16.7961 | 6.9369 | 0.082668 | 0.083433 | Continue to Monitor
WARSAW | Gallatin - RR 1 Box 51 - Warsaw | 728 | Warsaw - Dry Creek Rd - S & E of Substation | 9.6576 | 92 | 2018-12-31 | 2.774% | 0% | 3.987% | 0% | 32.5% | 0% | 3.484% | 25.4% | 0% | 31.86% | 69.4622 | 125.404 | 0.36954 | 0.58696 | Continue to Monitor
SPARTA | Owen - RR 1 Box 136C - Sparta | 730 | Sparta - State HWY 467 - NE & SE of Substation | 28.2516 | 374 | 2018-12-31 | 1.07% | 0% | 0% | 0% | 0.5232% | 0% | 3.608% | 82.66% | 1.2% | 10.94% | 108.801 | 88.6688 | 0.40148 | 0.48523 | Continue to Monitor
SPARTA | Owen - RR 1 Box 136C - Sparta | 731 | Sparta - State HWY 467 - SW of Substation | 5.8038 | 107 | 2018-12-31 | 0% | 0% | 0% | 0% | 0% | 0% | 61.08% | 0% | 0% | 38.92% | 5.6463 | 6.744 | 0.056472 | 0.046159 | Continue to Monitor
WARSAW | Gallatin - RR 1 Box 51 - Warsaw | 734 | Warsaw - Smith Ave, Center Ave, E Main St - NE of Substation | 3.2932 | 443 | 2016-01-16 | 0% | 0% | 0% | 0% | 0% | 0% | 20.3% | 0% | 0% | 79.7% | 4.7553 | 4.7128 | 0.03149 | 0.040668 | Continue to Monitor
BOONE AVENUE | Clark - 660 Boone Ave. - Winchester | 769 | Winchester - Boone Ave, Harkins Ave, Skylark Dr- NW of Subst. | 16.7191 | 1440 | 2017-01-03 | 6.181% | 0% | 3.254% | 0% | 1.208% | 0% | 13.37% | 38.29% | 0% | 37.69% | 25.1405 | 37.4847 | 0.23884 | 0.3705 | Continue to Monitor
HARRODSBURG NORTH | Mercer - 1000 Warwick Rd - Harrodsburg | 773 | Harrodsburg - Warwick Rd, N Greenville St - S of Substation | 4.1629 | 193 | 2016-11-19 | 28.46% | 0% | 15.05% | 0% | 0% | 0% | 12.53% | 0% | 0% | 43.96% | 37.358 | 123.9107 | 0.47489 | 1.5677 | Continue to Monitor
MOREHEAD 12KV | Rowan - 100 E Wilkinson Blvd - Morehead | 779 | Morehead - Wilkinson Blvd - N of Substation | 7.0003 | 468 | 2017-01-27 | 0.02044% | 0% | 0% | 0% | 26.34% | 0% | 0.5424% | 15.85% | 0% | 57.24% | 75.1226 | 290.4853 | 0.7647 | 3.1492 | Continue to Monitor
PARIS 12KV | Bourbon - 520 Scott Ave - Paris | 795 | Paris - Clintonville Rd - SW of Substation | 16.8643 | 1034 | 2021-03-15 | 11.71% | 0% | 0% | 0% | 0% | 0% | 0% | 60.43% | 0% | 27.86% | 7.1714 | 7.698 | 0.09835 | 0.06673 | Trees Trimmed in 2021
CORPORATE DRIVE | Clark - 4011 Corporate Dr - Winchester | 799 | Winchester - Corporate Dr & Fortune Dr - NW of Substation | 5.4173 | 37 | 2017-09-01 | 0% | 0% | 0% | 0% | 0% | 0% | 95.29% | 0% | 0% | 4.706% | 3.1733 | 4.5864 | 0.058752 | 0.053343 | Continue to Monitor
PARIS 12KV | Bourbon - 520 Scott Ave - Paris | 805 | Paris - Spears Mill Rd and WHY 460 - SE of Substation | 81.9703 | 864 | 2015-08-29 | 0.1438% | 0.4947% | 0.8711% | 45.26% | 10.88% | 0% | 10.4% | 27.05% | 0% | 4.913% | 100.606 | 189.2502 | 1.0912 | 1.9094 | Tree Trim Scheduled for 2021
MILLERSBURG | Bourbon - Vimont Ln. – Millersburg | 807 | Millersburg - Vimont Ln, W 5th St - N & E of Substation | 3.2311 | 103 | 2015-06-22 | 58.89% | 0% | 0% | 0% | 26% | 0% | 0% | 0% | 0% | 15.11% | 1.9065 | 5.0793 | 0.030813 | 0.07767 | Continue to Monitor
HANSON | Hopkins - 235 Fowler Rd - Hanson | 811 | Hanson - US HWY 41 & City of Hanson - N of Substation | 17.3777 | 617 | 2019-08-03 | 5.382% | 0% | 39.39% | 0% | 8.734% | 0% | 32.67% | 0.8971% | 0% | 12.93% | 147.3412 | 19.5474 | 0.97975 | 1.1651 | Continue to Monitor
DOZIER HEIGHTS | Hopkins - 200 Claire Ln - Madisonville | 814 | Madisonville - Circuit no longer exists - N/A | 0.38634 | 2 | 2017-12-30 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 35.2933 | 132.4667 | 0.4 | 1 | Continue to Monitor
DOZIER HEIGHTS | Hopkins - 200 Claire Ln - Madisonville | 816 | Madisonville - Sandcut Ln, Mcleod Ln, Grapvine Rd - N&E of Subs. | 21.479 | 804 | 2019-09-07 | 1.681% | 4.438% | 0.7922% | 0% | 14.75% | 0% | 4.759% | 71.82% | 0% | 1.762% | 43.4585 | 46.2299 | 0.69869 | 0.62332 | Continue to Monitor
NORTONVILLE | Hopkins - 55 Holly Ln - Nortonville | 818 | Nortonville - Mockingbird St, US 41, & Wells Rd - N of Substation | 17.7942 | 367 | 2017-04-15 | 1.796% | 0% | 0.6693% | 1.845% | 66.16% | 0% | 17.16% | 12.37% | 0% | 0% | 10.1301 | 16.6323 | 0.13026 | 0.2933 | Continue to Monitor
EAST DIAMOND | Hopkins - 550 East Diamond Rd - Madisonville | 825 | Madisonville - Randall Dr, Meadowlark Ln - W of Substation | 9.4838 | 302 | 2019-11-16 | 0% | 0% | 13.87% | 4.441% | 9.487% | 0% | 71.02% | 0% | 0% | 1.182% | 9.4551 | 11.4674 | 0.157 | 0.12562 | Continue to Monitor
EAST DIAMOND | Hopkins - 550 East Diamond Rd - Madisonville | 827 | Madisonville - Hwy 85, Hwy 892, & Hwy 1221 - NE & SE of Substation | 22.9586 | 357 | 2020-03-28 | 0% | 1.685% | 0% | 0% | 49.72% | 12.23% | 16.75% | 19.61% | 0% | 0% | 54.9888 | 59.2131 | 0.82371 | 0.79824 | Continue to Monitor
FIES CITY | Hopkins - 2436 Central City Rd - Madisonville | 841 | Madisonville - Central City Rd & Fies Ln - NW & SE of Substation | 1.195 | 16 | 2018-12-31 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 95.99 | 479.95 | 0.6 | 3 | Continue to Monitor
ASHBYBURG PUMP | Hopkins - 250 High Banks Ferry - Ashbyburg | 844 | Ashbyburg - Highbanks Ferry Rd - E of Substation | 0.051632 | 1 | 2018-12-31 | 0% | 0% | 0% | 42.46% | 57.54% | 0% | 0% | 0% | 0% | 0% | 35.8333 | 179.1667 | 0.4 | 2 | Continue to Monitor
KAWNEER | Harrison - RR 7 Box 729 White Oak Pike - Cynthiana | 856 | Cynthiana - Western Ave, Ladish Rd, Hwy 27 - S of Substation | 13.5053 | 438 | 2020-11-21 | 0.7845% | 0% | 0% | 97.71% | 0% | 0% | 0.5581% | 0% | 0% | 0.9425% | 50.2243 | 43.1678 | 0.64101 | 1.016 | Continue to Monitor
KAWNEER | Harrison - RR 7 Box 729 White Oak Pike - Cynthiana | 857 | Harrison - White Oak Pike - WNW of Substation | 0.72305 | 5 | 2020-11-21 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 4.6347 | 23.1733 | 0.08 | 0.4 | Continue to Monitor
WEST HICKMAN | Fayette - 3172 Ashgrove Rd - Lexington | 865 | Lexington - Saron Dr, Tates Creek Rd, Kenesaw Dr - NE of Subst | 24.0818 | 1288 | 2019-02-16 | 6.864% | 0.06458% | 2.689% | 0% | 0.1614% | 0% | 0% | 65.23% | 0% | 24.99% | 31.7134 | 90.8551 | 0.27993 | 0.97462 | Continue to Monitor
SHANNON RUN | Woodford - 2770 Shannon Run Rd - Versailles | 868 | Versailles - Shannon Run, Lexington Rd, Pisgah Rd - N of Subst | 65.5931 | 1111 | 2015-04-10 | 1.375% | 0% | 6.713% | 0% | 10.51% | 0% | 2.792% | 66.68% | 0% | 11.94% | 135.6396 | 168.4426 | 1.0409 | 0.96269 | Tree Trim Scheduled for 2021
CARLISLE 12KV | Nicholas - 104 S Elm St - Carlisle | 877 | Carlisle/Sharpsburg - S Upper Jackstown, Hwy 1285, Hwy 11 - SSE of Subst | 44.6832 | 670 | 2020-01-18 | 1.164% | 0% | 1.538% | 0% | 89.13% | 0% | 0.4829% | 0.3132% | 0% | 7.369% | 71.85 | 106.7108 | 0.67602 | 1.1513 | Continue to Monitor
MAYSVILLE WEST | Mason - 210 Cox Alley - Maysville | 900 | Maysville - Maddox Aly, 4th St, Hwy 62 - SE of Substation | 1.5799 | 169 | 2019-09-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 2.2019 | 8.2596 | 0.033425 | 0.11243 | Continue to Monitor
MAYSVILLE WEST | Mason - 210 Cox Alley - Maysville | 901 | Maysville - Maddox Aly, 4th St, Plum St, Mulberry St- SE of Subst. | 1.9816 | 381 | 2019-09-07 | 0% | 0% | 0% | 0% | 0% | 0% | 0.9375% | 2.344% | 0% | 96.72% | 9.0884 | 10.0233 | 0.22939 | 0.065207 | Continue to Monitor
MAYSVILLE WEST | Mason - 210 Cox Alley - Maysville | 902 | Maysville - Washington St, E 6th, Edgemont Rd - SW of Subst. | 3.7788 | 163 | 2019-09-07 | 0% | 0.7446% | 0% | 0% | 0% | 0% | 0.5352% | 98.72% | 0% | 0% | 122.5489 | 541.3205 | 0.66547 | 2.693 | Continue to Monitor
MAYSVILLE WEST | Mason - 210 Cox Alley - Maysville | 903 | Maysville - W 2nd St, W Mcdonald Pkwy - NW of Subst. | 3.3352 | 353 | 2019-09-07 | 0% | 0% | 0% | 0% | 0.3298% | 0% | 0% | 0% | 99.67% | 0% | 30.5782 | 76.2246 | 0.44958 | 0.57136 | Continue to Monitor
MAYSVILLE MID | Mason - 314 Lexington St - Maysville | 909 | Maysville - E 2nd St, Lexington St - NW & NE of Substation | 3.3277 | 488 | 2019-10-12 | 0% | 0% | 0% | 0% | 1.634% | 0% | 86.19% | 6.861% | 0% | 5.318% | 13.3006 | 43.8195 | 0.31187 | 0.17237 | Continue to Monitor
MAYSVILLE EAST | Mason - 1107 Forest Ave - Maysville | 913 | Maysville - Bryant ln, Hwy 10, Buckner St - E of Substation | 10.179 | 832 | 2019-10-12 | 1.908% | 0% | 0% | 58.55% | 2.292% | 0% | 2.99% | 29.04% | 0% | 5.219% | 14.6789 | 16.8614 | 0.17029 | 0.18852 | Continue to Monitor
KENTON | Mason - 801 Kenton Station Rd - Maysville | 921 | Maysville - W Maple Leaf Rd, Jersey Ridge Rd - E&NE of Subst. | 20.5116 | 887 | 2016-01-15 | 0.721% | 0.3554% | 2.861% | 0% | 0.1189% | 0% | 1.958% | 84.91% | 0% | 9.078% | 61.3085 | 85.2277 | 0.69669 | 0.71288 | Continue to Monitor
KENTON | Mason - 801 Kenton Station Rd - Maysville | 922 | Maysville - Parker Rd, Hwy 10, Martha Comer Dr - W of Subst. | 4.2532 | 115 | 2021-01-23 | 3.976% | 0% | 0% | 0% | 30.5% | 0% | 5.887% | 0% | 0% | 59.63% | 7.221 | 11.3719 | 0.14676 | 0.35652 | Continue to Monitor
KENTON | Mason - 801 Kenton Station Rd - Maysville | 923 | Maysville - Hwy 10, Market Square Dr - SE of Substation | 19.5945 | 361 | 2021-01-23 | 6.894% | 0% | 89.43% | 0% | 0% | 0% | 2.241% | 0.6428% | 0% | 0.7962% | 14.5886 | 46.6774 | 0.3319 | 1.2056 | Continue to Monitor
AUGUSTA | Bracken - 318 E 4th St. - Augusta | 929 | Augusta - 5th Street, Old August-Brooksville Rd - W&SW of Subst. | 20.886 | 646 | 2018-05-08 | 0.04262% | 0.1837% | 1.89% | 0.3057% | 4.394% | 0% | 1.245% | 84.96% | 0% | 6.978% | 85.4065 | 210.7102 | 0.95086 | 1.905 | Continue to Monitor
SHARON | Bracken - 3061 Asbury Rd - Augusta | 935 | Augusta - Mt Zion Rd, City of Brooksville, Hwy 10&19 - NW&SW of Subst | 77.0357 | 1186 | 2019-01-19 | 0.0702% | 0.04167% | 2.832% | 0% | 1.498% | 0% | 0.2325% | 3.855% | 0% | 91.47% | 41.6081 | 56.9109 | 0.46991 | 0.25904 | Continue to Monitor
SHARON | Bracken - 3061 Asbury Rd - Augusta | 937 | Augusta - Woodward Rd, Clarks Run Rd - S&SE of Substation | 45.6238 | 558 | 2019-03-16 | 0.1624% | 0% | 0.08411% | 0% | 2.99% | 0% | 0.0991% | 54.15% | 0% | 42.51% | 70.6144 | 195.5408 | 0.82019 | 1.8499 | Continue to Monitor
SARDIS | Mason - 4000 Blue Lick Rd - Mays Lick | 940 | Mays Lick/Mt Olivet - Hwy 62, Brierly Ridge Rd - W&NW of Subst. | 20.6627 | 465 | 2020-01-18 | 0.06444% | 0% | 0.05942% | 1.823% | 40.12% | 0% | 3.552% | 54.14% | 0% | 0.2452% | 165.5107 | 242.7486 | 1.7348 | 3.1516 | Trees Trimmed in 2020
CARNTOWN | Pendleton - 15125 Hwy 8 - Foster | 948 | Foster - Hwy 8 - S&SE of Substation | 23.4015 | 229 | 2018-02-06 | 3.855% | 0% | 1.059% | 0% | 2.146% | 0% | 3.134% | 6.579% | 0% | 83.23% | 88.177 | 46.407 | 0.68287 | 0.68969 | Continue to Monitor
BUTLER | Pendleton - 11095 Hwy 27 N - Burnside Butler | 950 | Butler - City of Butler, Flour Creek Rd, Hwy 10 - ESE of Substation | 58.384 | 929 | 2017-05-01 | 0.8191% | 0% | 0.1582% | 0% | 4.143% | 0% | 0.01998% | 76.79% | 0% | 18.07% | 181.3243 | 397.0845 | 1.4389 | 3.5067 | Tree Trim Scheduled for 2021
WEDONIA | Mason - 6964 KY Hwy 11 - Maysville | 965 | Maysville - Hwy 11 - N of Substation | 32.6491 | 382 | 2017-01-07 | 0.4996% | 0% | 4.575% | 0% | 18.39% | 0% | 1.566% | 1.059% | 73.49% | 0.4235% | 148.2694 | 248.721 | 1.1543 | 3.201 | Continue to Monitor
WEDONIA | Mason - 6964 KY Hwy 11 - Maysville | 966 | Flemingsburg - Hwy 170, City of Ewing - SW of Substation | 27.2896 | 523 | 2016-12-17 | 0.2045% | 0% | 0.02419% | 0% | 96.75% | 0% | 0.02207% | 1.273% | 0.08021% | 1.646% | 279.5133 | 447.3978 | 1.0076 | 1.0311 | Continue to Monitor
WEDONIA | Mason - 6964 KY Hwy 11 - Maysville | 967 | Flemingsbur - Hwy 11 - S of Substation | 17.5488 | 298 | 2016-05-27 | 4.724% | 0% | 0.4195% | 0% | 5.014% | 0% | 0.3821% | 27.41% | 0% | 62.06% | 160.5172 | 152.6198 | 0.71 | 1.3919 | Continue to Monitor
BARLOW | Ballard - 433 Oscar Rd. - Barlow | 1312 | Barlow - N 6th St - City of Barlow | 6.3643 | 326 | 2017-09-09 | 37.93% | 0% | 0% | 0% | 1.338% | 0% | 0% | 1.262% | 0% | 59.47% | 92.9609 | 44.8304 | 0.39547 | 0.63789 | Continue to Monitor
FORESTDALE | McCracken - 4250 Rice Springs Rd - Kevil | 1320 | Kevil - SR 1154, SR 996, & Cairo Rd - E of Substation | 41.0971 | 926 | 2019-11-23 | 1.232% | 0% | 0.125% | 0% | 1.459% | 0% | 0.1897% | 86.74% | 0% | 10.25% | 132.2765 | 171.3929 | 0.89131 | 1.4856 | Reliability Improvements Scheduled for 2021
FORESTDALE | McCracken - 4250 Rice Springs Rd - Kevil | 1322 | Kevil - Clarkline Rd, Kevil Rd, Woodville Rd, & Hwy 473 - NW of Substation | 25.9523 | 605 | 2019-12-07 | 0.658% | 0.1831% | 70.16% | 0% | 23.92% | 0% | 1.403% | 0% | 0.09014% | 3.582% | 79.2254 | 239.3268 | 0.52833 | 1.6523 | Continue to Monitor
CHRISTIAN | Webster - 1678 S R 493 - Wheatcroft | 1404 | Wheatcroft - City of Wheatcroft - NW of Substation | 10.8465 | 198 | 2019-09-21 | 0% | 0% | 0% | 0% | 88.51% | 0% | 0% | 11.49% | 0% | 0% | 5.6508 | 5.1878 | 0.060537 | 0.090126 | Continue to Monitor
DIAMOND | Webster - 830 Bill Dorris Rd - Providence | 1410 | Providence - Bill Dorris Rd, S R 109 - SW of Substation | 6.5633 | 122 | 2019-06-29 | 5.989% | 0% | 92.02% | 0% | 0% | 0% | 1.988% | 0% | 0% | 0% | 34.949 | 33.3902 | 0.62733 | 0.64754 | Continue to Monitor
CENTRAL CITY SOUTH | Muhlenberg - 500 E Second Ave - Central City | 1416 | Central City - Everly Brothers Blvd - SW of Substation | 0.092171 | 1 | No Trimming Necessary | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 122.2333 | 488.9333 | 0.5 | 2 | Continue to Monitor
CORYDON | Henderson - 5430 Greenlick Rd - Corydon | 1429 | Corydon - King Mill Rd - W of Substation | 6.5984 | 46 | 2020-09-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0.6773% | 71.27% | 0% | 28.06% | 33.9643 | 137.04 | 0.31344 | 1.1032 | Trees Trimmed in 2020
CORYDON | Henderson - 5430 Greenlick Rd - Corydon | 1431 | Corydon - City of Corydon - E of Substation | 14.6493 | 435 | 2020-09-05 | 0% | 0% | 17.82% | 0% | 16.93% | 0% | 3.903% | 61.34% | 0% | 0% | 25.9381 | 56.0487 | 0.26032 | 0.38602 | Trees Trimmed in 2020
SPENCER CHEMICAL 12KV | Henderson - 1413 Hwy 136 W - Henderson | 1437 | Henderson - Hwy 136 & Hwy 60 - S of Substation | 4.2816 | 84 | 2020-03-21 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 4.6494 | 6.0347 | 0.064027 | 0.070588 | Continue to Monitor
MANITOU | Hopkins - 7615 Nebo Rd - Nebo | 1451 | Nebo - US 41 ALT & Happy Ln - E of Substation | 8.4923 | 133 | 2019-01-26 | 0% | 0% | 0% | 0% | 1.695% | 0% | 12.93% | 0.9582% | 0% | 84.42% | 36.8348 | 101.3228 | 0.47799 | 1.1498 | Continue to Monitor
ZION | Henderson - 7485 HWY 351 - Henderson | 1468 | Henderson - HWY 351/Zion Rd, Adams Ln, & Spring Garden Rd - W of Substation | 12.9665 | 721 | 2020-08-29 | 0.1728% | 0% | 0% | 0.1358% | 0.3277% | 0% | 4.454% | 94.91% | 0% | 0% | 76.0725 | 349.2185 | 0.33644 | 1.1276 | Trees Trimmed in 2020
SEBREE | Webster - 199 N Railroad St - Sebree | 1472 | Sebree - SR 56, College St, Jefferson St, & Old Beech Grove Rd - W/E of Substation | 12.2558 | 429 | 2020-04-25 | 2.428% | 0% | 5.494% | 0% | 61.83% | 0% | 30.24% | 0% | 0% | 0% | 5.768 | 9.4877 | 0.10055 | 0.27724 | Continue to Monitor
KUTTAWA | Lyon - 3487 Lake Barkley Dr - Kuttawa | 1501 | Kuttawa - Hwy 295, Lake Shore Dr, & Holley St - SW & SE of Substation | 11.1445 | 412 | 2021-02-03 | 0.6284% | 0% | 0% | 0% | 0.4652% | 0% | 0.4229% | 2.29% | 0% | 96.19% | 90.8156 | 80.1586 | 0.77342 | 1.0582 | Continue to Monitor
FREDONIA | Caldwell - 150 Wigginton Ln - Fredonia | 1507 | Fredonia - City of Fredonia & Hwy 641 - S of Substation | 11.0356 | 249 | 2016-09-10 | 0.3273% | 0% | 0% | 0% | 0% | 0% | 1.113% | 0% | 96.34% | 2.219% | 101.2545 | 60.6731 | 0.92797 | 1.0281 | Continue to Monitor
FREDONIA | Caldwell - 150 Wigginton Ln - Fredonia | 1509 | Fredonia - Hwy 91, Princeton Fredonia Rd, & Marion Rd - SE of Substation | 34.8212 | 191 | 2016-09-10 | 0% | 0% | 0.9952% | 0% | 0.5804% | 0% | 0.1567% | 98.11% | 0% | 0.1611% | 150.886 | 236.0173 | 1.1127 | 1.5287 | Tree Trim Scheduled for 2021
BARNHILL | Webster - 7390 Rabbit Ridge Rd - Providence | 1520 | Providence - Hwy 109 - S of Substation | 5.3191 | 29 | 2017-02-11 | 0% | 0% | 0% | 0% | 5.643% | 0% | 94.36% | 0% | 0% | 0% | 175.265 | 81.2603 | 0.4069 | 1.0345 | Continue to Monitor
DAWSON SPRINGS | Hopkins - 205 Munn St - Dawson Springs | 1525 | Dawson Springs - N Trim St, Sycamore St - NW of Substation | 2.3047 | 156 | 2017-02-11 | 3.953% | 0% | 39.21% | 0% | 12.02% | 0% | 39.45% | 0% | 0% | 5.375% | 5.0795 | 8.1668 | 0.074645 | 0.12271 | Continue to Monitor
CALHOUN | McLean - 530 W First St - Calhoun | 1606 | Calhoun - High St, W 7th St, S R 81 - N of Subst. | 6.5872 | 327 | 2018-10-06 | 12.12% | 0% | 0% | 0% | 6.062% | 0% | 19.07% | 5.297% | 8.652% | 48.79% | 6.1487 | 5.1866 | 0.049662 | 0.051904 | Continue to Monitor
SHAVERS CHAPEL | Muhlenberg - 7870 S R 181 N - Bremen | 1609 | Bremen - S R 181, Buttermilk Rd, S R 175, & S R 81 - NW of Substation | 95.0561 | 1656 | 2019-08-03 | 8.082% | 0% | 6.323% | 0% | 4.373% | 0% | 0.4699% | 1.325% | 16.66% | 62.77% | 60.7948 | 31.0814 | 0.67952 | 1.4854 | Continue to Monitor
GREENVILLE 12KV | Muhlenberg - 200 N Boggess Ave - Greenville | 1614 | Greenville - Outer York, Lake Rd, & Rogers Ave - N of Substation | 2.6222 | 65 | 2016-05-21 | 4.169% | 0% | 0% | 0% | 0% | 0% | 93.49% | 0% | 0% | 2.337% | 13.1324 | 24.3544 | 0.56368 | 2.0308 | Continue to Monitor
GREENVILLE | Muhlenberg - 117 E Depot St - Greenville | 1623 | Greenville - N Main St & Broad St - N & S of Substation | 2.2648 | 152 | 2016-07-02 | 0% | 0% | 0% | 13.55% | 29.14% | 0% | 52.39% | 0% | 0% | 4.923% | 52.9518 | 107.4471 | 0.7165 | 1.2096 | Continue to Monitor
POWDERLY | Muhlenberg - Opportunity Way - Greenville | 1626 | Greenville - Main St - NE of Substation | 24.7308 | 838 | 2015-12-12 | 0.2786% | 0% | 0% | 0% | 0.1878% | 0% | 6.775% | 35.46% | 0% | 57.3% | 83.7505 | 207.8245 | 0.79998 | 2.5535 | Tree Trim Scheduled for 2021
LIVERMORE | McLean - 190 Main St - Livermore | 1642 | Livermore - Hill St, Hwy 431, & Comy Dock Rd - NE of Substation | 6.498 | 350 | 2018-12-22 | 0.3313% | 0% | 53.29% | 0% | 44.92% | 0% | 0% | 1.461% | 0% | 0% | 88.8648 | 184.184 | 0.75555 | 2.0229 | Continue to Monitor
LIVERMORE | McLean - 190 Main St - Livermore | 1643 | Livermore - Main St, 2nd St, 3rd St, & Broadway St - N of Substation | 6.8408 | 420 | 2018-12-22 | 0% | 0% | 53.51% | 0% | 44.93% | 0% | 0.7102% | 0.5509% | 0% | 0.3009% | 177.2142 | 186.5138 | 0.88088 | 2.1164 | Reliability Improvements Scheduled for 2021
CENTRAL CITY | Muhlenberg - 106 Pendleton St - Central City | 1645 | Central City - Hwy 70, S Cherry Hill Rd - W of Substation | 12.2398 | 419 | 2020-11-07 | 0.9927% | 0% | 0% | 0% | 0% | 0% | 0.5998% | 89.97% | 0% | 8.438% | 113.7534 | 114.2571 | 1.4276 | 1.2123 | Reliability Improvements Scheduled for 2021
BEECH CREEK 1 | Muhlenberg - 169 Beech Creek Browder Rd - Beech Creek | 1668 | Beech Creek - Arnold Hill Rd, State Route 1163 - SW of Subst. | 21.3873 | 278 | 2018-09-08 | 1.746% | 0% | 0.3178% | 0% | 0.122% | 0% | 95.85% | 0% | 0% | 1.968% | 121.6596 | 138.5828 | 1.0404 | 1.2229 | Continue to Monitor
BEECH CREEK 1 | Muhlenberg - 169 Beech Creek Browder Rd - Beech Creek | 1671 | Beech Creek - Beech Creek Browder Rd - NE of Substation | 4.2478 | 104 | 2018-07-21 | 0% | 0% | 0% | 0% | 2.637% | 0% | 94.67% | 0% | 0% | 2.697% | 72.2046 | 127.4555 | 0.50672 | 1.1698 | Continue to Monitor
DRAKESBORO | Muhlenberg - 201 S Mine St - Drakesboro | 1673 | Drakesboro - Simmons St, S R 176, Merle Travis Hwy - SW of Subs | 19.6479 | 298 | 2018-11-17 | 0.8338% | 0% | 0% | 7.512% | 23.19% | 0% | 0% | 14.33% | 53.92% | 0.2136% | 159.2124 | 130.2373 | 1.6362 | 2.3129 | Continue to Monitor
GREEN RIVER STEEL | Daviess - 4575 US 60 E - Owensboro | 1676 | Owensboro - Ellis Smeathers Rd & US 60 - NE of Substation | 2.2071 | 14 | 2017-10-04 | 0% | 0% | 0% | 0% | 0% | 0% | 9.395% | 0% | 0% | 90.6% | 128.2618 | 264.519 | 0.64004 | 1.4286 | Continue to Monitor
REED MINERALS | Muhlenberg - 4661 S R 176 Drakesboro - Drakesboro | 1693 | Drakesboro - S R 176 & P&M Haul Rd - NNE of Substation | 5.6163 | 11 | 2020-03-28 | 59.1% | 0% | 33.19% | 0% | 0% | 0% | 0% | 7.716% | 0% | 0% | 140.2224 | 411.1561 | 1.0182 | 2.7273 | Continue to Monitor
MEXICO | Crittenden - 2747 S R 70 - Crayne | 1708 | Crayne - S R 70 & Ken Spar - NE of Substation | 8.9725 | 118 | 2016-07-09 | 0% | 0% | 0% | 0% | 0% | 0% | 58.86% | 0% | 41.14% | 0% | 1.8422 | 2.6819 | 0.023259 | 0.050847 | Continue to Monitor
MARION SOUTH | Crittenden - 505 Chappell Hill Rd - Marion | 1710 | Marion - Hwy 60, N Main St, Sturgis Rd, & Old Fords Ferry Rd - N & W of Substation | 26.5934 | 901 | 2016-10-01 | 1.686% | 0% | 0.2629% | 0% | 1.152% | 0% | 0.5735% | 13.79% | 0% | 82.53% | 78.5168 | 97.4285 | 0.88033 | 1.2084 | Continue to Monitor
MARION SOUTH | Crittenden - 505 Chappell Hill Rd - Marion | 1712 | Marion - Chapel Hill Rd, Autumn Ln, & Earl Patmore Rd - SW of Substation | 3.062 | 70 | 2016-10-01 | 7.904% | 0% | 7.088% | 0% | 85.01% | 0% | 0% | 0% | 0% | 0% | 49.99 | 224.8336 | 0.56242 | 2.4288 | Continue to Monitor
MARION | Crittenden - 106 Sparmill Rd - Marion | 1714 | Marion - E Depot St, E Bellville St, & Old Shady Grove Rd - N of Substation | 8.099 | 514 | 2016-10-01 | 0% | 0% | 0% | 0% | 0.8566% | 0% | 63.14% | 5.22% | 30.79% | 0% | 16.3916 | 24.0462 | 0.20603 | 0.2254 | Continue to Monitor
MARION | Crittenden - 106 Sparmill Rd - Marion | 1715 | Marion - Gum St, Mill Rd, Sturgis Rd/Main St - N of Substation | 9.4089 | 301 | 2016-10-08 | 0% | 0% | 0% | 0% | 4.555% | 0% | 90.04% | 0% | 0% | 5.403% | 4.1962 | 3.7379 | 0.064476 | 0.066963 | Continue to Monitor
STURGIS 12KV | Union - 1402 N Washington St - Sturgis | 1728 | Sturgis - Hwy 60, King St, Hwy 270, & Hwy 143 - S & N of Substation | 46.0851 | 980 | 2019-11-15 | 7.196% | 0% | 20.9% | 0% | 7.388% | 0% | 1.888% | 3.47% | 42.89% | 16.28% | 28.8242 | 30.208 | 0.24475 | 0.31168 | Continue to Monitor
SUNOCO | Union - 2823 S R 130 S - Morganfield | 1731 | Morganfield - S R 130 & Adamson Rd - SW of Substation | 23.198 | 182 | 2020-02-29 | 74.13% | 0% | 25.3% | 0% | 0.5683% | 0% | 0% | 0% | 0% | 0% | 21.4361 | 54.8482 | 0.33968 | 1.0822 | Continue to Monitor
SUNOCO | Union - 2823 S R 130 S - Morganfield | 1732 | Morganfield - S R 130 - NE of Substation | 4.0771 | 31 | 2020-02-29 | 18.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 81.4% | 57.7349 | 139.8073 | 0.45546 | 1.375 | Continue to Monitor
SUNOCO | Union - 2823 S R 130 S - Morganfield | 1733 | Morganfield - Robinson Rd & US HWY 60 - SSE of Substation | 5.6682 | 36 | 2020-02-29 | 0.6543% | 0% | 0% | 0% | 0% | 0% | 0% | 99.35% | 0% | 0% | 54.1792 | 246.2694 | 0.28194 | 1.0278 | Trees Trimmed in 2020
MORGANFIELD | Union - 305 Rhea St - Morganfield | 1750 | Morganfield - S R 947, N Chapman St, & Hedge Rd - NW of Substation | 9.2027 | 286 | 2019-11-23 | 0% | 0% | 0% | 0% | 80.88% | 0% | 0% | 19.12% | 0% | 0% | 3.178 | 8.0898 | 0.03598 | 0.034795 | Continue to Monitor
CAMP BRECKINRIDGE | Union - 1820 S Route 2091 - Morganfield | 1759 | Morganfield - Marshall Rd, Headquarters Rd, & Patton Rd - NE of Substation | 19.5602 | 255 | 2020-01-11 | 1.807% | 0% | 1.36% | 0% | 16.15% | 0% | 0.7446% | 4.584% | 0% | 75.36% | 31.9519 | 60.3331 | 0.63912 | 1.707 | Continue to Monitor
MORGANFIELD INDUSTRIAL | Union - 3324 U S HWY 60 E - Morganfield | 1761 | Morganfield - Hwy 60 E - W of Substation | 3.9909 | 39 | 2020-01-18 | 0% | 0% | 10.95% | 0% | 89.05% | 0% | 0% | 0% | 0% | 0% | 12.7226 | 38.3829 | 0.26128 | 0.82051 | Continue to Monitor
MORGANFIELD INDUSTRIAL | Union - 3324 U S HWY 60 E - Morganfield | 1763 | Morganield - Buchanan Rd - E & W of Substation | 2.1528 | 25 | 2020-01-18 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 50.18 | 105.9 | 0.4 | 1 | Continue to Monitor
WAVERLY | Union - 178 Blessed Martin Rd - Waverly | 1765 | Waverly - Blessed Martin Rd - W of Substation | 0.045158 | 4 | 2020-01-18 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 13.5233 | 67.6167 | 0.2 | 1 | Continue to Monitor
MANNINGTON | Christian - 2535 Mannington Loop - Mannington | 1801 | Mannington - HWY 407 & US 41- E of Substation | 3.2459 | 27 | 2018-04-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 50.1098 | 73.8333 | 0.73077 | 1 | Continue to Monitor
HARTFORD | Ohio - 425 Walnut St - Hartford | 1911 | Hartford - US HWY 231, Old Main St, HWY 1543- E of Substation | 8.7736 | 396 | 2017-11-18 | 65.82% | 0% | 11.09% | 0% | 6.059% | 0% | 4.056% | 2.981% | 0% | 9.993% | 10.7472 | 10.346 | 0.16272 | 0.22242 | Continue to Monitor
BEAVER DAM | Ohio - 310 Ridgecrest Dr. - Beaver Dam | 1914 | Beaver Dam - Ridge Crest Rd & US Hwy 62 - City of Beaver Dam | 13.3088 | 528 | 2019-05-25 | 0.8904% | 0% | 11.75% | 0% | 0.1461% | 0% | 1.659% | 0.3644% | 83.43% | 1.76% | 39.9778 | 109.7202 | 0.4047 | 1.2052 | Continue to Monitor
ATOKA | Boyle - 20 Parksville Cross Pike - Danville | 2101 | Perryville - City of Perryville & Perryville Rd - W of Substation | 29.9176 | 585 | 2020-10-10 | 0.9821% | 0% | 34.13% | 0% | 3.028% | 0% | 0.6813% | 57.3% | 0% | 3.874% | 35.8097 | 68.6628 | 0.35069 | 0.56862 | Trees Trimmed in 2020
ATOKA | Boyle - 20 Parksville Cross Pike - Danville | 2102 | Danville – Parksville Cross Pike & Lebanon Rd - S of Substation | 12.6207 | 207 | 2020-10-10 | 4.313% | 0% | 0.6833% | 0% | 50.31% | 0% | 20.95% | 22.22% | 0% | 1.523% | 36.2355 | 34.0458 | 0.19841 | 0.21303 | Continue to Monitor
BUENA VISTA | Garrard - 164 High Bridge Rd. - Lancaster | 2104 | Lancaster - High Bridge Rd, Pine Crest Rd, & Camp Dix Rd - NW & SE of Substation | 35.1383 | 613 | 2017-09-04 | 0.6452% | 0.2193% | 12.63% | 0% | 66.1% | 0% | 1.876% | 18.05% | 0.4706% | 0% | 51.7022 | 76.9156 | 0.71141 | 1.2382 | Continue to Monitor
BUENA VISTA | Garrard - 164 High Bridge Rd. - Lancaster | 2106 | Lancaster - Kennedy Bridge Rd, Ashley Camp Rd, & Chminey Rock Rd - W of Substation | 30.0006 | 1082 | 2017-06-03 | 1.178% | 0% | 0.2529% | 8.033% | 1.076% | 0% | 13.45% | 75.63% | 0.3838% | 0% | 50.0407 | 60.1674 | 0.49828 | 0.67453 | Tree Trim Scheduled for 2021
CRAB ORCHARD | Lincoln - 635 KY HWY 39 N - Crab Orchard | 2108 | Crab Orchard - KY 39 - NNW of Substation | 9.1293 | 124 | 2018-12-08 | 47.23% | 0% | 0% | 0% | 0% | 0% | 0.3257% | 0.5682% | 51.87% | 0% | 94.0123 | 328.6753 | 0.94096 | 3.0161 | Continue to Monitor
DANVILLE E 4KV | Boyle - 805 East Dr - Danville | 2112 | Danville - Stanford Dr, Terrell Dr, & S 2nd St - SW of Substation | 3.332 | 168 | 2016-05-20 | 0% | 0% | 0% | 0% | 18.75% | 0% | 81.25% | 0% | 0% | 0% | 16.2067 | 16.1889 | 0.14303 | 0.16667 | Continue to Monitor
HARRODSBURG 1 | Mercer - 231 N Chiles St - Harrodsburg | 2126 | Harrodsburg - W Broadway St, Chiles St, & Hill St - W of Substation | 3.9315 | 480 | 2016-08-13 | 0% | 0% | 0% | 0% | 51.65% | 0% | 35.02% | 1.609% | 0% | 11.72% | 8.5554 | 5.4093 | 0.10853 | 0.11201 | Continue to Monitor
HARRODSBURG 1 | Mercer - 231 N Chiles St - Harrodsburg | 2127 | Harrodsburg - Factory St, N Main St, & Greenville St - N/E/S of Substation | 2.248 | 308 | 2016-08-13 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 1.9471 | 3.6693 | 0.021167 | 0.038835 | Continue to Monitor
HARRODSBURG 2 4KV | Mercer - 709 E Office St - Harrodsburg | 2128 | Harrodsburg - E Office St & Beaumont Ave - W of Substation | 4.1267 | 437 | 2016-07-30 | 0% | 0% | 43.99% | 0% | 0% | 0% | 29.38% | 20.66% | 0% | 5.973% | 7.5734 | 22.0262 | 0.079808 | 0.26673 | Continue to Monitor
HARRODSBURG 2 4KV | Mercer - 709 E Office St - Harrodsburg | 2129 | Harrodsburg - Cane Run St, N East St, & Cogar Ave - W of Substation | 3.73 | 413 | 2016-07-30 | 0% | 0% | 0% | 0% | 1.193% | 1.336% | 93.35% | 4.123% | 0% | 0% | 21.0984 | 98.7218 | 0.23443 | 1.0826 | Continue to Monitor
HARRODSBURG 2 12KV | Mercer - 709 E Office St - Harrodsburg | 2131 | Harrodsburg - Lexington Rd, Burgin Rd, & City of Burgin - NE/SE of Substation | 42.5082 | 816 | 2016-09-13 | 0.1649% | 0% | 6.111% | 0.1198% | 8.577% | 0% | 1.334% | 80.35% | 3.039% | 0.3067% | 49.5418 | 93.9359 | 0.69071 | 1.9098 | Tree Trim Scheduled for 2021
HARRODSBURG 3 | Mercer - 1020 N College St - Harrodsburg | 2132 | Harrodsburg - Louisville Rd, Virginia Ave, & Sleepy Hollow Rd - N of Substation | 24.3552 | 708 | 2016-11-26 | 1.287% | 0% | 0% | 0% | 88.49% | 0% | 2.625% | 6.838% | 0% | 0.7631% | 35.5454 | 100.7679 | 0.40683 | 1.0679 | Continue to Monitor
KENTUCKY STATE HOSPITAL | Boyle - 4180 Shakertown Rd - Danville | 2136 | Danville - Shakertown Rd, Gwinn Island Rd, & Spears Ln - S of Substation | 17.8817 | 340 | 2017-03-30 | 0.2941% | 0.02236% | 0% | 0% | 11.32% | 0% | 0.5985% | 48.45% | 0% | 39.32% | 90.2308 | 170.3387 | 1.2746 | 1.9922 | Continue to Monitor
KENTUCKY STATE HOSPITAL | Boyle - 4180 Shakertown Rd - Danville | 2138 | Danville - Shakertown Rd, Faulkner Ln, & Curdsville Rd - N of Substation | 33.0498 | 582 | 2017-03-25 | 0.7006% | 0% | 0.5679% | 0% | 8.587% | 0% | 1.72% | 13.26% | 72.16% | 3.012% | 59.2078 | 64.7922 | 0.77261 | 1.1852 | Continue to Monitor
LANCASTER 1 | Garrard - 104 Hamilton Ave - Lancaster | 2140 | Lancaster - Danville St, Campbell St, & Waterworks Rd - NW of Substation | 16.1249 | 844 | 2017-12-09 | 0% | 0% | 0% | 0% | 0.1851% | 0% | 0% | 12.35% | 87.41% | 0.05288% | 25.9165 | 103.1381 | 0.20673 | 0.76237 | Continue to Monitor
LANCASTER 1 | Garrard - 104 Hamilton Ave - Lancaster | 2141 | Lancaster - Richmond St, Cowden Ct, & Hamilton Ave - N/E/SE of Substation | 4.6137 | 358 | 2018-02-03 | 0% | 0% | 0% | 0% | 0.07676% | 0% | 40.27% | 6.755% | 0% | 52.9% | 13.8935 | 25.6112 | 0.29957 | 1.1067 | Continue to Monitor
PINE HILL | Rockcastle - 501 Flat Rock Rd - Mt. Vernon | 2149 | Mt. Vernon - Wilderness Rd, Limestone - W of Substation | 8.1354 | 80 | 2020-07-18 | 0.5448% | 0% | 0% | 0% | 33.92% | 0% | 0% | 64.77% | 0% | 0.7677% | 301.4714 | 405.2687 | 1.7514 | 3.2442 | Trees Trimmed in 2020
SALVISA | Mercer - 4455 Louisville Rd - Salvisa | 2150 | Salvisa - Main St, Louisville Rd, & Talmage Rd - NW & SW of Substation | 38.4781 | 679 | 2016-11-12 | 1.537% | 0% | 0.1158% | 0% | 2.394% | 0% | 1.307% | 21.87% | 0% | 72.78% | 36.1416 | 71.2644 | 0.46638 | 0.79988 | Continue to Monitor
RICHMOND 3 4KV | Madison - 950 Vickers Dr - Richmond | 2161 | Richmond - Eastern Byp, Boggs Ln, & Opal Dr - E of Substation | 4.6388 | 179 | 2020-01-18 | 0% | 0% | 0% | 0% | 48.64% | 0% | 0% | 0% | 0% | 51.36% | 35.8758 | 113.5574 | 0.57532 | 2.1955 | Continue to Monitor
MOUNT VERNON | Rockcastle - 56 Old Somerset Rd - Mt. Vernon | 2166 | Mt. Vernon - Richmond St and Williams St - NE of Substation | 15.1857 | 836 | 2020-08-08 | 9.294% | 0% | 0.4807% | 0% | 7.289% | 0% | 2.459% | 28.28% | 0% | 52.19% | 18.3627 | 51.9451 | 0.11289 | 0.2929 | Trees Trimmed in 2020
CAMPBELLSVILLE 1 | Taylor - 101 Old Greensburg Rd. - Campbellsville | 2205 | Campbellsville - HWY 3350 Bypass - N of Substation | 17.2888 | 1224 | 2019-12-31 | 2.447% | 0% | 7.732% | 0% | 0.1657% | 0% | 6.041% | 6.693% | 0% | 76.92% | 28.3632 | 44.5024 | 0.36158 | 0.44661 | Continue to Monitor
COLUMBIA | Adair - 114 Lindsey Wilson St - Columbia | 2210 | Columbia - Guthrie St, Miller Ave, & Adair Ave - S & SE of Substation | 2.1315 | 150 | 2019-03-23 | 0% | 0% | 0% | 0% | 95.15% | 0% | 2.417% | 1.288% | 0% | 1.141% | 17.6534 | 59.0263 | 0.25426 | 0.51333 | Continue to Monitor
GREENSBURG | Green - 424 Old Hodgenville Rd - Greensburg | 2214 | Greensburg - Buckner Hill Rd, Hawthorne Rd, HWY 1464, & HWY 88 - SW of Substation | 19.7338 | 210 | 2019-12-31 | 0.07295% | 0% | 5.268% | 0% | 46.22% | 0% | 0% | 47.58% | 0% | 0.8679% | 76.4871 | 299.0826 | 0.32146 | 0.77922 | Continue to Monitor
LEBANON | Marion - 351 E Water St - Lebanon | 2216 | Lebanon - MLK Ave, Spalding Ave, Walnut St, & W Main St - SW of Substation | 6.1479 | 621 | 2019-12-31 | 10.54% | 0% | 0% | 0% | 0.1025% | 0% | 6.642% | 5.734% | 0% | 76.98% | 23.3844 | 72.4715 | 0.32948 | 1.2248 | Continue to Monitor
LEBANON SOUTH | Marion - 1157 Bradfordsville - Bradfordsville | 2219 | Lebanon - Mulberry St, Old Calvary Pike, & Hwy 208 - NW & S of Substation | 12.8866 | 532 | 2019-11-02 | 5.565% | 0% | 0% | 0% | 15.59% | 0% | 5.97% | 34.38% | 0% | 38.49% | 17.8779 | 19.8759 | 0.18256 | 0.15765 | Continue to Monitor
LEBANON SOUTH | Marion - 1157 Bradfordsville - Bradfordsville | 2220 | Lebanon - Metts Dr, Hill Creek Rd, & Hamilton Hts - W of Substation | 5.4233 | 160 | 2019-09-07 | 0% | 0% | 0% | 0% | 0% | 0% | 16.05% | 0% | 0% | 83.95% | 18.9432 | 38.7712 | 0.16976 | 0.25735 | Continue to Monitor
RUSSELL SPRINGS | Russell - 1183 HWY 1870 - Russell Springs | 2221 | Russell Springs - Old Columbia Rd & Providence Rd - W of Substation | 12.5624 | 139 | 2018-12-31 | 0.7759% | 0% | 0% | 0% | 0.2524% | 0% | 0% | 97.96% | 0% | 1.008% | 74.0782 | 178.0193 | 0.82242 | 2.4591 | Continue to Monitor
SPRINGFIELD | Washinton - 107 Commercial Ave - Springfield | 2226 | Springfield - State HWY 55 & Bloomfield Rd - S & N of Substation | 37.5414 | 366 | 2020-06-27 | 1.642% | 0% | 0% | 0% | 2.717% | 0% | 1.158% | 92.76% | 0% | 1.722% | 32.9997 | 61.4802 | 0.21 | 0.27833 | Trees Trimmed in 2020
WOODLAWN | Nelson – 285 Spencer Mattingly Ln. – Bardstown | 2232 | Bardstown - My Old KY Home St Park & Gilkey Run Rd - SW of Substation | 6.5951 | 132 | 2018-10-13 | 1.968% | 0% | 0% | 0% | 66.18% | 0% | 3.125% | 28.73% | 0% | 0% | 90.6262 | 80.83 | 0.7524 | 1.0252 | Continue to Monitor
LEBANON WEST | Marion - 2255 Saint Mary's Rd - St Mary | 2235 | St Mary - Warehouse Rd & Campbellsville Rd - E of Substation | 7.0516 | 219 | 2019-11-16 | 25.19% | 0% | 0% | 0% | 0% | 0% | 55.52% | 0% | 0% | 19.28% | 1.9137 | 2.9247 | 0.029883 | 0.072733 | Continue to Monitor
LEBANON INDUSTRIAL | Marion - 700 Corporate Dr - Lebanon | 2236 | Lebanon - Corporate Dr - NE of Substation | 0.011158 | 1 | No Trimming Necessary | 28.13% | 0% | 0% | 0% | 71.87% | 0% | 0% | 0% | 0% | 0% | 329.0333 | 775.1333 | 0.75 | 2 | Continue to Monitor
BEATTYVILLE 4KV | Lee - 950 W Main St. - Beattyville | 2301 | Beattyville - W Main St, Lee Ave, & Grand Ave - E of Substation | 8.1622 | 234 | 2020-11-21 | 0% | 0% | 0% | 0% | 23.22% | 0% | 15.09% | 61.69% | 0% | 0% | 25.5934 | 41.695 | 0.18366 | 0.40506 | Trees Trimmed in 2020
OKONITE | Madison - 1742 Berea Rd - Richmond | 2306 | Richmond - Berea Rd - N of Substation | 2.3853 | 24 | 2019-09-28 | 0% | 0% | 0% | 0% | 16.82% | 0% | 0% | 83.18% | 0% | 0% | 14.1128 | 25.8514 | 0.20968 | 0.29167 | Continue to Monitor
PAINT LICK | Garrard - 11811 HWY 52 E - Paint Lick | 2309 | Paint Lick - HWY 52, Kirksville Rd, & Curtis Pike - N of Substation | 18.0091 | 308 | 2020-04-18 | 0.3105% | 0% | 0% | 0% | 0% | 0% | 0.327% | 98.77% | 0% | 0.5895% | 129.4069 | 235.8479 | 0.67694 | 0.6676 | Trees Trimmed in 2020
PAINT LICK | Garrard - 11811 HWY 52 E - Paint Lick | 2310 | Paint Lick - HWY 52, White Lick Rd, & Noe Rd - S of Substation | 9.6196 | 139 | 2020-04-18 | 10.83% | 0% | 1.739% | 0% | 1.002% | 0% | 0% | 86.43% | 0% | 0% | 47.909 | 51.3231 | 0.35413 | 0.3425 | Trees Trimmed in 2020
RED HOUSE | Madison - 3858 Boonesboro Rd - Richmond | 2311 | Richmond - Lost Fork Rd, Red House Rd, & Boonesboro Rd - S of Substation | 9.3862 | 96 | 2021-01-16 | 0.1545% | 0% | 1.465% | 0% | 20.22% | 0% | 0% | 78.16% | 0% | 0% | 48.7819 | 96.412 | 0.35529 | 0.86598 | Trees Trimmed in 2021
RICHMOND SOUTH | Madison - 464 Eastern Bypass - Richmond | 2323 | Richmond - S Killarney Dr, Barnes Mill Rd, & Martin Dr - NW of Substation | 5.3206 | 659 | 2019-12-28 | 1.831% | 0% | 1.38% | 0% | 11.92% | 0% | 0.9407% | 72.19% | 0% | 11.74% | 13.4889 | 11.0709 | 0.16884 | 0.17443 | Continue to Monitor
RICHMOND 1 | Madison - 315 Clay Dr - Richmond | 2325 | Richmond - US 25, Keeneland Dr, & Jacks Creek Rd - NW of Substation | 4.3027 | 356 | 2019-06-22 | 0% | 0% | 97.74% | 0% | 0% | 0% | 0.7733% | 0% | 0% | 1.49% | 34.4903 | 49.6783 | 0.34247 | 0.53391 | Continue to Monitor
ELIZABETHTOWN 3 | Hardin - 100 Crucible Steel Rd - Elizabethtown | 2332 | Elizabethtown - Leitchfield Rd, Blackbranch Rd, & Nicholas St - SW of Substation | 18.6184 | 873 | 2021-01-23 | 37.7% | 0.7587% | 19.06% | 0% | 1.043% | 0% | 37.28% | 0% | 0% | 4.146% | 9.956 | 8.4521 | 0.12463 | 0.14892 | Continue to Monitor
NEW HAVEN | Nelson - 256 Lyons Station Rd - New Haven | 2333 | New Haven - Center St, First St, & Depot St - SE of substation | 1.4868 | 150 | 2017-11-11 | 14.13% | 85.87% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 5.6159 | 6.8509 | 0.1087 | 0.14685 | Continue to Monitor
RINEYVILLE | Hardin - Rineyville Big Springs Rd - Radcliff | 2334 | Radcliff - Rineyville Big Springs Rd & Rineyville Rd - SW of Substation | 26.4371 | 744 | 2019-06-22 | 8.557% | 0% | 3.231% | 0% | 3.489% | 0% | 0.672% | 84.05% | 0% | 0% | 22.7154 | 29.203 | 0.22175 | 0.16806 | Continue to Monitor
BOSTON | Nelson - 1100 Old Nelsonville Rd. - Boston | 2402 | Lebanon Junction - City of Lebanon Junction - NW of Substation | 15.6254 | 709 | 2017-02-04 | 0.65% | 0% | 0% | 0% | 0% | 0% | 80.49% | 13.5% | 3.248% | 2.11% | 45.2905 | 64.5455 | 0.58077 | 1.0608 | Continue to Monitor
BOSTON | Nelson - 1100 Old Nelsonville Rd. - Boston | 2403 | Boston - Lebanon Junction Rd, Boston Rd, KY 52 & Nelsonville Rd - SE of Substation | 29.506 | 345 | 2017-03-11 | 1.604% | 2.36% | 2.758% | 0% | 0% | 0% | 1.7% | 89.05% | 0% | 2.523% | 60.7701 | 72.6386 | 0.53735 | 1.0985 | Tree Trim Scheduled for 2021
CLARKSON | Grayson - 405 Peonia Rd - Clarkson | 2405 | Leitchfield - Farmview Ln, Hwy 3155, & Grayson Springs Rd - W of Substation | 7.4341 | 135 | 2017-04-01 | 0% | 63.42% | 0% | 0% | 0% | 0% | 36.58% | 0% | 0% | 0% | 3.5025 | 5.4707 | 0.046316 | 0.065822 | Continue to Monitor
EASTVIEW | Hardin - 12540 Sonora - Hardin Springs | 2408 | Sonora - W Main St, Skees St, & St. Paul Rd - SW of Substation | 39.292 | 601 | 2019-09-21 | 0.4975% | 0% | 0.2446% | 0% | 0.9506% | 0.2279% | 2.538% | 0% | 0% | 95.54% | 37.4605 | 60.1435 | 0.52853 | 0.70047 | Continue to Monitor
ELIZABETHTOWN 2 | Hardin - 1011 Woodland Dr - Elizabethtown | 2415 | Elizabethtown - Woodland Dr, Saint John Rd, & Westport Rd - S of Substation | 8.3779 | 549 | 2017-01-07 | 0% | 0% | 9.822% | 0% | 85.26% | 0% | 4.641% | 0% | 0% | 0.2801% | 29.9499 | 48.1205 | 0.75212 | 1.0892 | Continue to Monitor
ELIZABETHTOWN 4 | Hardin - 201 Sportsman Lake Rd - Elizabethtown | 2418 | Elizabethtown - Dixie Hwy, New Glendale Rd, & Nicholas St - W & SW of Substation | 19.1104 | 517 | 2020-05-30 | 0% | 0% | 0% | 0% | 0.4063% | 0% | 6.335% | 1.547% | 0% | 91.71% | 35.424 | 59.5021 | 0.26008 | 0.43518 | Continue to Monitor
ELIZABETHTOWN 4 | Hardin - 201 Sportsman Lake Rd - Elizabethtown | 2419 | Elizabethtown - Sportsman Lake Rd & Hodenville Rd - SE of Substation | 23.0764 | 730 | 2020-05-16 | 3.606% | 2.627% | 1.194% | 0% | 12.53% | 0% | 52.31% | 9.645% | 0% | 18.08% | 10.3137 | 12.0453 | 0.19427 | 0.15891 | Continue to Monitor
ELIZABETHTOWN 5 | Hardin - 800 N Mulberry St - Elizabethtown | 2422 | Elizabethtown - KY 61/62, Navaho Dr, & Ring Rd - NE of Substation | 5.8571 | 360 | 2016-07-09 | 18.93% | 0% | 0% | 0% | 0% | 0% | 65.42% | 15.17% | 0.4877% | 0% | 28.9584 | 35.488 | 0.42322 | 0.47154 | Continue to Monitor
ELIZABETHTOWN 5 | Hardin - 800 N Mulberry St - Elizabethtown | 2423 | Elizabethtown - Brooks Str, N Main St, & Guthrie St - S & E of Substation | 5.6418 | 564 | 2020-11-14 | 2.412% | 0% | 0% | 0% | 56.24% | 0% | 13.93% | 10.21% | 0% | 17.21% | 42.6091 | 116.5834 | 0.57314 | 2.4881 | Continue to Monitor
ELIZABETHTOWN WEST | Hardin - 300 College Street Rd - Elizabethtown | 2425 | Elizabethtown - College Street Rd - E of Substation | 0.63147 | 2 | 2021-02-06 | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 15.0189 | 10.0389 | 0.26667 | 0.33333 | Continue to Monitor
ELIZABETHTOWN WEST | Hardin - 300 College Street Rd - Elizabethtown | 2427 | Elizabethtown - Peterson Dr, Geoargetown Rd, & Leitchfield Rd - W of Substation | 5.3951 | 261 | 2021-02-06 | 0% | 93.84% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 6.158% | 76.7029 | 145.5957 | 0.86602 | 2.0805 | Continue to Monitor
HORSE CAVE | Hart - 501 Shewey Ave - Horse Cave | 2433 | Horse Cave - W Main St, KY 335, New St, US 31 - N & NW of Substation | 22.6615 | 887 | 2018-11-10 | 0% | 0% | 0% | 0% | 93.73% | 0% | 0.6626% | 0% | 5.299% | 0.3071% | 26.8025 | 72.516 | 0.24775 | 0.58749 | Continue to Monitor
HORSE CAVE | Hart - 501 Shewey Ave - Horse Cave | 2435 | Horse Cave - E Main St, KY 218, & US HWY 31 E - E of Substation | 18.3651 | 373 | 2018-12-15 | 29.68% | 1.265% | 36.52% | 0% | 12.54% | 0% | 0% | 5.705% | 14.29% | 0% | 28.5716 | 49.2323 | 0.28273 | 0.55097 | Continue to Monitor
HORSE CAVE | Hart - 501 Shewey Ave - Horse Cave | 2436 | Hiseville - Old Glasgow Rd & Hiseville Main St - SE of Substation | 28.1491 | 356 | 2018-12-01 | 0.5739% | 0% | 10.69% | 0% | 0% | 0% | 0.5303% | 28.19% | 0% | 60.02% | 92.4163 | 160.7515 | 0.66273 | 1.4016 | Continue to Monitor
MILLWOOD | Grayson - 6649 Beaver Dam Rd - Millwood | 2441 | Millwood - US HWY 62, School House Rd, & Rock Quarry Rd - NE of Substation | 11.6867 | 171 | 2017-05-27 | 0% | 0% | 44.84% | 0% | 8.633% | 0% | 39.09% | 0% | 7.434% | 0% | 5.6628 | 4.8812 | 0.060603 | 0.088065 | Continue to Monitor
NEW HAVEN | Nelson - 256 Lyons Station Rd - New Haven | 2444 | New Haven - 3rd St, Center St, New Hope Rd, & Rogers Rd - ESE of Substation | 24.3732 | 572 | 2017-12-02 | 0.481% | 0% | 0% | 0.4284% | 0.2176% | 0% | 2.402% | 2.485% | 84.01% | 9.978% | 74.9042 | 101.958 | 0.82999 | 1.182 | Continue to Monitor
RIO | Hart - 301 Glen Lily Rd E - Munfordville | 2451 | Munfordville - E US 31, S Jackson HWY & J McGuire Rd - S of Substation | 16.7121 | 252 | 2020-03-14 | 1.5% | 0.444% | 0% | 0% | 16.5% | 0% | 0.2901% | 76.38% | 0% | 4.888% | 55.6461 | 173.4219 | 0.39626 | 0.93547 | Trees Trimmed in 2020
SONORA | Hardin - 1340 Old Sonora Rd - Sonora | 2457 | Sonora - Sonora Hardin Springs Rd, Nolin Rd, Gilead Church Rd, & KY 222 - N of Substation | 24.2033 | 496 | 2018-02-10 | 0.4098% | 0% | 0% | 0% | 17.46% | 0% | 0.3421% | 9.501% | 70.82% | 1.466% | 35.1048 | 49.2548 | 0.29417 | 0.40267 | Continue to Monitor
SONORA | Hardin - 1340 Old Sonora Rd - Sonora | 2458 | Sonora - Maple St, US 31, & City of Upton - S of Substation | 17.3274 | 492 | 2018-03-10 | 1.963% | 0% | 0% | 0% | 5.484% | 0% | 27.86% | 29.31% | 0% | 35.37% | 71.0675 | 22.3217 | 0.68991 | 1.2864 | Continue to Monitor
VINE GROVE | Hardin - 108 Crutcher St - Vine Grove | 2459 | Vine Grove - Park St, Edgebrook Dr, Brown St, & 1st St - W of Substation | 8.1992 | 530 | 2016-05-21 | 0% | 0% | 0% | 0% | 42.12% | 0% | 3.614% | 1.892% | 0% | 52.38% | 45.2949 | 115.6211 | 0.55405 | 1.244 | Continue to Monitor
LEITCHFIELD EAST | Grayson - 705 Wallace Ave - Leitchfield | 2465 | Leitchfield - Mill St, Lee Ave, & Grayson Springs Rd - N of Substation | 6.3034 | 380 | 2017-04-01 | 3.27% | 2.022% | 51.43% | 0% | 0% | 0% | 0% | 15.62% | 0% | 27.66% | 24.5591 | 27.3224 | 0.32208 | 0.20097 | Continue to Monitor
RADCLIFF SOUTH | Hardin - 100 Energy Dr - Radcliff | 2471 | Hardin - S Wilson Rd & Medical Center Dr - SE of Substation | 3.0544 | 106 | 2019-04-06 | 0% | 0% | 0% | 82.71% | 14.05% | 0% | 0.4677% | 0% | 1.627% | 1.14% | 52.5551 | 243.7343 | 0.3452 | 1.3558 | Continue to Monitor
LA GRANGE E 12KV | Oldham - 1810 E Highway 146 - La Grange | 2472 | La Grange - Jericho Rd, Adams St, 1st St, Hwy 53, & Zale Smith Ln - S of Substation | 29.3999 | 943 | 2021-01-16 | 0.9972% | 0% | 51.18% | 0% | 0% | 0% | 0% | 33.71% | 0% | 14.11% | 23.083 | 78.2695 | 0.22186 | 0.64146 | Trees Trimmed in 2021
HORSE CAVE INDUSTRIAL | Hart - 400 Cherry St - Horse Cave | 2473 | Horse Cave - Old Dixie Hwy - W of Substation | 0.38851 | 3 | 2018-09-29 | 0% | 0% | 23.76% | 0% | 0% | 0% | 0% | 0% | 0% | 76.24% | 46.0311 | 94.05 | 0.3 | 0.66667 | Continue to Monitor
BLACK BRANCH | Hardin - 1220 N Black Branch Rd - Elizabethtown | 2477 | Elizabethtown - City of Elizabethtown, W Main St, & St. Paul Rd- NE & SW of Substation | 23.167 | 675 | 2019-05-18 | 1.978% | 0% | 0% | 0% | 87.36% | 0% | 1.626% | 0% | 0% | 9.038% | 26.3092 | 28.223 | 0.86821 | 0.36062 | Continue to Monitor
FLORIDA TILE | Anderson - 1247 Alton Rd - Lawrenceburg | 2505 | Lawrenceburg - Alton Rd - N of Substation | 15.8409 | 639 | 2016-05-21 | 1.258% | 0% | 0.9324% | 0% | 4.039% | 0% | 0.4707% | 0.6427% | 0% | 92.66% | 57.8121 | 86.547 | 0.48971 | 1.0937 | Continue to Monitor
LA GRANGE E 12KV | Oldham - 1810 E Highway 146 - La Grange | 2509 | La Grange - Grange Dr, Hwy 53, & Hwy 22 - S of Substation | 71.5679 | 1968 | 2015-12-12 | 0.1392% | 0.05747% | 0.3415% | 0% | 88.13% | 0% | 0.6924% | 10.08% | 0% | 0.5543% | 66.859 | 224.2819 | 0.43788 | 1.0184 | Continue to Monitor
LAGRANGE PENAL | Oldham - 3011 W Highway 146 - La Grange | 2512 | La Grange - W Highway 146 - W of Substation | 0.0093291 | 1 | No Trimming Necessary | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 78.5333 | 190.6667 | 0.6 | 2 | Continue to Monitor
LAGRANGE PENAL | Oldham - 3011 W Highway 146 - La Grange | 2513 | La Grange - HWY 146, Jefferson St, & Allen Ln - NE of Substation | 24.0986 | 1500 | 2021-03-31 | 4.131% | 0% | 12.33% | 0% | 0.5275% | 0% | 0% | 66.56% | 9.965% | 6.492% | 31.7166 | 51.1646 | 0.26537 | 0.42051 | Trees Trimmed in 2021
LAWRENCEBURG 12KV | Anderson - 108 E Broadway st - Lawrenceburg | 2516 | Lawrenceburg - Main St - N of Substation | 38.8431 | 2384 | 2016-08-13 | 3.362% | 0% | 4.73% | 0% | 9.13% | 0% | 5.908% | 56.69% | 0.1931% | 19.99% | 45.8602 | 68.5231 | 0.42725 | 0.39963 | Tree Trim Scheduled for 2021
LAWRENCEBURG 12KV | Anderson - 108 E Broadway st - Lawrenceburg | 2517 | Lawrenceburg - Industry Rd & Tyron Rd - NE of Substation | 10.6366 | 176 | 2016-10-31 | 0% | 0% | 2.172% | 0.8998% | 4.673% | 0% | 0% | 75.87% | 0% | 16.39% | 32.7101 | 72.889 | 0.31477 | 0.35612 | Tree Trim Scheduled for 2021
LAWRENCEBURG 12KV | Anderson - 108 E Broadway st - Lawrenceburg | 2518 | Lawrenceburg - Waterfill Rd - N of Substation | 12.6216 | 987 | 2016-07-02 | 2.036% | 0% | 0.8326% | 0% | 0.919% | 0% | 5.577% | 52.18% | 0% | 38.46% | 30.1666 | 60.8813 | 0.47561 | 0.39341 | Tree Trim Scheduled for 2021
SHELBYVILLE 12KV | Shelby - 1201 Willow St - Shelbyville | 2521 | Shelbyville - Walnut St, 10th St, Henry Clay St, & Beechwood Ave - S of Substation | 5.9269 | 704 | 2017-08-05 | 0% | 0% | 1.584% | 0.1966% | 0% | 0% | 76.37% | 10.85% | 0% | 11% | 14.8361 | 39.0868 | 0.098355 | 0.24133 | Continue to Monitor
SHELBYVILLE EAST | Shelby - 183 Boone Station Rd - Shelbyville | 2522 | Shelbyville - KY 60, HWY 395, & Benson Pike - E of Substation | 54.3859 | 1684 | 2019-11-16 | 14.51% | 10.28% | 0.1475% | 0% | 0.5592% | 0% | 9.763% | 37.5% | 25.04% | 2.197% | 88.3443 | 90.6794 | 1.2106 | 1.5515 | Continue to Monitor
SHELBYVILLE SOUTH | Shelby - 614 Mack Walters Rd - Shelbyville | 2525 | Shelbyville - Medical Ave, Shelby House Apt, & Village Ln - N of Substation | 3.443 | 464 | 2017-08-05 | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 10.4312 | 24.5414 | 0.12585 | 0.30603 | Continue to Monitor
SIMPSONVILLE | Shelby - 6801 Shelbyville Rd - Simpsonville | 2528 | Simpsonville - Shelbyville Rd, Champions Way, Veechdale Rd & Hwy 60 - SW & E of Substation | 24.1569 | 285 | 2019-04-13 | 0.6419% | 0% | 0% | 0% | 0% | 0% | 5.831% | 93.53% | 0% | 0% | 53.9743 | 109.5444 | 0.55471 | 0.47247 | Continue to Monitor
LOCKPORT | Henry - 88 Sawmill Rd - Bethlehem | 2531 | Bethlehem - KY 22, KY 389 & Six Mile Creek Rd - NE of Substation | 13.2267 | 167 | 2016-10-22 | 0% | 0% | 94.14% | 1.154% | 1.054% | 0% | 0.9934% | 2.659% | 0% | 0% | 155.7889 | 120.015 | 0.9709 | 1.0839 | Continue to Monitor
LOCKPORT | Henry - 88 Sawmill Rd - Bethlehem | 2532 | Bethlehem - KY 22, Hwy 1360, Sewell Rd, & Bethlehem Rd - SW of Substation | 53.094 | 952 | 2016-12-24 | 0.1474% | 0% | 32.85% | 0% | 3.845% | 0% | 1.445% | 48.85% | 0.0569% | 12.81% | 102.11 | 62.519 | 1.0598 | 1.1044 | Tree Trim Scheduled for 2021
SHELBYVILLE SOUTH | Shelby - 614 Mack Walters Rd - Shelbyville | 2534 | Shelbyville - Main St/US 60, Sunset Way, Old KY 55, & Haven Hill Rd - NW of Substation | 11.1721 | 861 | 2017-08-05 | 39.87% | 0% | 0% | 0% | 0% | 0% | 14.69% | 17.13% | 5.269% | 23.05% | 15.5302 | 23.4211 | 0.13873 | 0.18413 | Continue to Monitor
EMINENCE | Henry - 1257 Ballardsville Rd - Eminence | 2535 | Eminence - Giltner Rd, Smithfield Rd, & Hwy 22 - W of Substation | 14.0133 | 249 | 2016-04-23 | 0.143% | 0% | 0.1545% | 0% | 0.06865% | 0% | 0% | 39.84% | 59.64% | 0.1502% | 101.8907 | 281.8838 | 0.65429 | 1.7173 | Continue to Monitor
MID VALLEY CLARKSON | Grayson - 1960 Peonia Rd - Clarkson | 2538 | Clarkson - No Road - W of Substation | 0.0059206 | 1 | No Trimming Necessary | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 121.8267 | 62.6333 | 0.4 | 1 | Continue to Monitor
GREEN RIVER | Muhlenberg - 811 Power Plant Dr - South Carrollton | 3412 | Muhlenberg - HWY 431 & 138 - N of Substation | 7.7179 | 1 | 2017-10-31 | 0% | 0% | 99.96% | 0% | 0.03773% | 0% | 0% | 0% | 0% | 0% | 86.12 | 338.1 | 2.1 | 4 | Continue to Monitor
Earlington - Oak Hill (Sec 3B) | Hopkins - 202 Russ Hill Rd - Nortonville | 3418 | Nortonville - Daniel Boone Rd & Hwy 41 Alt, & Hwy 62 - S of Substation | 18.4335 | 3127 | 2017-01-07 | 0% | 0% | 0% | 0% | 28.29% | 0% | 0% | 0% | 0% | 71.71% | 16.8681 | 3.0003 | 2.3917 | 3 | Continue to Monitor
Princeton - Hardesty Tap | Caldwell - 320 Marion Rd - Princeton | 3423 | Princeton - Watson Rd, Mt. Hebron Rd, & Mill Dam Rd - E of Substation | 19.6276 | 945 | 2017-03-28 | 0% | 0% | 75.27% | 0% | 24.73% | 0% | 0% | 0% | 0% | 0% | 7.3257 | 9.9986 | 2.8187 | 10 | Continue to Monitor
Green River - Rumsey | County - Road - Town | 3424 | Town - Road - General Area | 9.7099 | 1 | 2017-10-31 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0.40002 | 2.0001 | 0.4 | 2 | Continue to Monitor
GARDNER | Clay - HWY 66/Redbird Rd - Ashers Fork | 4336 | Ashers Fork - State Hwy 66 - N of Substation | 5.9155 | 30 | 2017-12-29 | 0% | 0% | 0% | 0% | 1.846% | 0% | 0% | 98.15% | 0% | 0% | 93.3092 | 352.3267 | 1.0245 | 3.0333 | Continue to Monitor
FOURMILE | Bell - Hwy 2014 - Pineville | 4340 | Pineville - Hwy 2014 & 2015, US 25, & Hwy 92 - SW & N of Substation | 14.9922 | 175 | 2016-10-03 | 0.382% | 0% | 0% | 0% | 8.714% | 0% | 2.792% | 76.23% | 0% | 11.88% | 226.4697 | 517.0371 | 1.3722 | 2.6857 | Tree Trim Scheduled for 2021
SHAWNEE GAS 12KV | Harlan - Ball Park Rd - Harlan | 4402 | Harlan - Hwy 421 & Hwy 990 - E of Substation | 17.2152 | 498 | 2020-05-08 | 1.594% | 0% | 0% | 0% | 50.54% | 0% | 35.23% | 11.11% | 0% | 1.529% | 61.0668 | 73.5569 | 0.54988 | 0.89994 | Reliability Improvements Completed in 2020
HARLAN 12KV | Harlan - Corner of River St and Rain St - Harlan | 4407 | Harlan - State HWY 38 - SW of Substation | 4.5979 | 116 | 2018-10-11 | 0% | 0% | 0% | 0% | 40.68% | 24.91% | 8.527% | 25.88% | 0% | 0% | 108.4559 | 164.3075 | 1.3296 | 2.7993 | Continue to Monitor
HARLAN WYE 4KV | Harlan - Sunshine Pike Rd just W of US HWY 421 - Harlan | 4411 | Harlan - US HWY 421 - E of Substation | 4.8634 | 405 | 2018-01-02 | 36.12% | 0% | 0% | 0% | 35.73% | 0% | 20.82% | 7.335% | 0% | 0% | 28.9291 | 35.9772 | 0.27859 | 0.52347 | Continue to Monitor
CATRONS CREEK | Harlan - Near 6872 Hwy 72 - Gulston | 4427 | Gulston - Hwy 72 & Bardo Hollow Rd - SW of Substation | 3.0168 | 94 | 2020-02-15 | 0.5306% | 0% | 0% | 0% | 61.45% | 0% | 0.706% | 37.31% | 0% | 0% | 106.1418 | 468.5362 | 0.58005 | 2.2776 | Trees Trimmed in 2020
CATRONS CREEK | Harlan - Near 6872 Hwy 72 - Gulston | 4428 | Gulston - Hwy 1216, Hwy 72, & Hwy 2425 - N of Substation | 8.8168 | 321 | 2020-03-16 | 0.3209% | 0% | 0% | 0% | 6.734% | 0% | 5.196% | 87.75% | 0% | 0% | 104.4026 | 161.7927 | 0.84118 | 1.3472 | Trees Trimmed in 2020
VERDA | Harlan - Corner of School St - Evarts | 4479 | Evarts - Hwy 38, Nolan Ln, & Ages Creek Rd - W of Substation | 13.8074 | 496 | 2016-09-02 | 0.2987% | 0% | 0% | 0% | 94.35% | 0% | 0.1891% | 5.161% | 0% | 0% | 99.9841 | 73.4883 | 0.79136 | 1.2375 | Continue to Monitor
SOMERSET 3 | Pulaski - 125 Young St. - Somerset | 4501 | Somerset - E Mt. Vernon St & Eller St - E & SW of Substation | 8.6521 | 720 | 2020-10-10 | 0.5336% | 0% | 0% | 2.579% | 82.8% | 0% | 1.756% | 11.7% | 0% | 0.6281% | 19.2326 | 24.7644 | 0.42202 | 1.0679 | Continue to Monitor
SOMERSET 3 | Pulaski - 125 Young St. - Somerset | 4502 | Somerset - Pumphouse Rd, Speedway Dr, & College St - W of Substation | 13.1405 | 885 | 2020-10-10 | 71.28% | 0% | 0% | 0% | 0.01041% | 0% | 0% | 28.24% | 0% | 0.4731% | 47.9326 | 120.7755 | 0.61642 | 1.7605 | Trees Trimmed in 2020
SOMERSET 2 | Pulaski - 105 Tandy Ave - Somerset | 4506 | Somerset - N Main St, Robin Dr, & Elliott Dr - NW of Substation | 1.718 | 100 | 2020-07-25 | 0% | 0% | 0% | 0% | 7.165% | 0% | 92.84% | 0% | 0% | 0% | 14.593 | 22.669 | 0.18996 | 0.35644 | Continue to Monitor

## KU Section 6-7
KENTUCKY PUBLIC SERVICE COMMISSION
ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT
SECTION 6: VEGETATION MANAGEMENT PLAN REVIEW
The Companies’ Vegetation Management Plan was submitted December 19, 2007. The Distribution Vegetation Management Program encompasses right of way maintenance for Louisville Gas and Electric Company and Kentucky Utilities Company (referred to as the “Companies”). The program is centralized and managed by a Forestry Manager and eight company Utility Arborists. All are certified arborists by the International Society of Arboriculture.
The Companies’ plan is to maintain a proactive trim cycle while balancing the reactive needs of worst performing circuits. The Companies’ goal is to maintain an average trim cycle of five years or less. The effectiveness of the plan is evaluated by the cycle and system performance as measured by system SAIDI, SAIFI, and CAIDI.
Effectiveness of the program
KU/LG&E Tree Cycle – 4.90 years
KU (Kentucky) Tree SAIDI – 21.90 minutes
KU (Kentucky) Tree SAIFI – 0.145
KU (Kentucky) Tree CAIDI – 151.1 minutes
The hazard tree program, mid cycle, herbicide, and worst performing circuits were completed as planned.
Adjustments made to the tree plan in 2020 included
No changes made to plan.
Changes to be implemented in 2021
No changes made to plan. Continue targeted hazard tree and mid-cycle trim work.
SECTION 7: UTILITY COMMENTS
SAIDI, SAIFI and CAIDI all improved in 2020 compared to the previous 5 year average including and excluding major events. 358 Circuits were above their previous 5 year average SAIDI and/or SAIFI in 2020.