## LGE Section 1-4
KENTUCKY PUBLIC SERVICE COMMISSION
ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT
SECTION 1: CONTACT INFORMATION
UTILITY NAME |  |  |  | LOUISVILLE GAS AND ELECTRIC
REPORT PREPARD BY |  |  |  | Steve Woodworth (Dir. System Ops & Planning)
E-MAIL ADDRESS OF PREPARER |  |  |  | steve.woodworth@lge-ku.com
PHONE NUMBER OF PREPARER |  |  |  | (502) 627-3828
SECTION 2: REPORTING YEAR
CALENDAR YEAR OF REPORT |  |  |  | 2020
SECTION 3: MAJOR EVENT DAYS (MED)
TMED |  |  |  | 3.344
FIRST DATE USED TO DETERMINE TMED |  |  |  | 2015-01-01
LAST DATE USED TO DETERMINE TMED |  |  |  | 2019-12-31
NUMBER OF MED IN REPORTING YEAR |  |  |  | 5
NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years. If five years of data are not available, then utilities should use what is available until five years are accumulated.
SECTION 4: SYSTEM RELIABILTIY INFORMATION AND RESULTS
System-wide Information
TOTAL CUSTOMERS |  | 434471 |  | TOTAL CIRCUITS |  | 619
Excluding MED
| 5 YEAR AVERAGE |  |  |  | REPORTING YEAR
SAIDI | 77.82 |  |  | SAIDI | 71.44
SAIFI | 0.926 |  |  | SAIFI | 0.736
Including MED
| 5 YEAR AVERAGE |  |  |  | REPORTING YEAR
SAIDI | 187.75 |  |  | SAIDI | 106.88
SAIFI | 1.164 |  |  | SAIFI | 0.866
Notes:
1) | All duration indices (SAIDI) are to be reported in units of minutes.
2) | Reports are due on the first business day of May of each year
3) | Reports cover the calendar year ending in the December before the reports are due.
4) | IEEE 1366 (latest version) is used to define SAIDI, SAIFI, and TMED
SECTION 5: CIRCUIT REPORTING
BEGIN ON NEXT PAGE

## Excel LGE Section 5
Substation Name | Substation Location (County - Road - Town) | Circuit Number | Circuit Location (Town - Road - General Area) | Total Circuit Length (Miles) | Average 2020 OMS Custs | Date of Last Circuit Trim (VM) | Animal | Construction | Lightning | Non-Company | Other/Unknown | Overload | Planned Work | Trees | Vehicle | Utility Equipment | 2016-2020 SAIDI Average | 2020 SAIDI | 2016-2020 SAIFI Average | 2020 SAIFI | LIST OF CORRECTION ACTION, IF ANY, TAKEN OR TO BE TAKEN
ASHBY | Jefferson - 5400 Vesper Ln - Lousivlle | AB1202 | Louisville - Greentree Ln & Dixie Hwy - S of Substation | 19.4016 | 1863 | 2020-09-19 | 2.285% | 0% | 0% | 2.864% | 1.099% | 0% | 24.15% | 0.2489% | 55.05% | 14.3% | 65.7466 | 101.9605 | 0.74475 | 1.1301 | Continue to Monitor
ASHBY | Jefferson - 5400 Vesper Ln - Lousivlle | AB1203 | Louisville - Ashby Ln & Bethany Ln - W of Substation | 17.3418 | 1212 | 2020-09-19 | 8.801% | 0% | 34.31% | 0% | 3.164% | 0% | 21% | 15.45% | 0% | 17.28% | 62.7951 | 78.3095 | 0.89317 | 1.3826 | Continue to Monitor
ASHBY | Jefferson - 5400 Vesper Ln - Lousivlle | AB1205 | Louisville - Valley Station Rd & Dodge Ln - E of Substation | 24.5548 | 2199 | 2020-09-05 | 0.8653% | 0% | 3.259% | 0% | 12.85% | 0% | 8.149% | 12.76% | 52.25% | 9.864% | 110.3508 | 114.2371 | 1.3058 | 1.7875 | Continue to Monitor
AIKEN | Jefferson - 12909 Shelbyville Rd. - Louisville | AK1293 | Louisville - New English Station Rd - NE of Substation | 4.4189 | 143 | 2020-11-21 | 0% | 0% | 0% | 0% | 98.37% | 0% | 1.625% | 0% | 0% | 0% | 80.5106 | 127.8537 | 1.5619 | 2.0072 | Continue to Monitor
AIKEN | Jefferson - 12909 Shelbyville Rd. - Louisville | AK1294 | Louisville - Old Shelbyville Rd - W of Substation | 6.6787 | 491 | 2020-02-29 | 17.94% | 0% | 0% | 0% | 41% | 0% | 1.769% | 39.29% | 0% | 0% | 68.5718 | 64.7848 | 0.79362 | 1.448 | Trees Trimmed in 2020
AIKEN | Jefferson - 12909 Shelbyville Rd. - Louisville | AK1296 | Louisville - ShelbyvilleRd & N Beckley Station - NE of Substation | 35.7881 | 1588 | 2020-02-29 | 0.5374% | 0% | 0% | 0% | 0% | 0% | 22.67% | 0.4914% | 0% | 76.3% | 33.67 | 139.8015 | 0.35494 | 0.47308 | Continue to Monitor
ALGONQUIN | Jefferson - 1800 S 11th St - Louisville | AL1374 | Louisville - S 7th St & Algonquin Pky - SE of Substation | 3.5851 | 450 | 2019-02-09 | 10.5% | 0% | 0% | 9.533% | 21.51% | 0% | 0% | 0% | 0% | 58.46% | 29.8142 | 149.058 | 0.37711 | 1.8833 | Continue to Monitor
ALGONQUIN | Jefferson - 1800 S 11th St - Louisville | AL1377 | Louisville - W Hill St & S 10th St - N of Substation | 1.1776 | 4 | 2019-02-09 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 61.5533 | 297.3667 | 0.36 | 1.4 | Continue to Monitor
ASHBOTTOM | Fayette - 96 Burley Ave. - Lexington | AS1416 | Louisville - Grade Ln - N of Substation | 6.2422 | 53 | 2019-02-02 | 0% | 0% | 0% | 0% | 2.476% | 0% | 0% | 96.58% | 0% | 0.9447% | 212.5274 | 375.8398 | 1.8235 | 1.0556 | Continue to Monitor
ASHBOTTOM | Jefferson - 8113 Grade Ln - Louisville | AS1418 | Louisville - Outer Loop - S of Substation | 8.6668 | 54 | 2019-02-02 | 0% | 0% | 5.8% | 0% | 86.89% | 0% | 0% | 0% | 0% | 7.314% | 63.9624 | 99.6249 | 0.59652 | 1 | Continue to Monitor
BISHOP | Jefferson - 3920 Bishop Ln - Louisville | BI1218 | Louisivlle - Bishop Ln - N of Substation | 2.7785 | 131 | 2017-04-15 | 11.64% | 0% | 0% | 0% | 66.99% | 0% | 0% | 0% | 0% | 21.37% | 15.4716 | 11.2813 | 0.13454 | 0.17822 | Continue to Monitor
BISHOP | Jefferson - 3920 Bishop Ln - Louisville | BI1221 | Louisville - Robards Ln - N of Substation | 2.6568 | 64 | 2017-04-15 | 0% | 0% | 0% | 0% | 11.23% | 0% | 70.26% | 0% | 0% | 18.51% | 17.4305 | 59.8903 | 0.11979 | 0.23126 | Continue to Monitor
BROOK | Jefferson - 913 S 1st Street - Louisivlle | BK0002 | Louisville - S Brook St & S Floyd St - E of Substation | 2.0731 | 181 | 2020-02-08 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 20.6327 | 17.9034 | 0.18487 | 0.19376 | Continue to Monitor
BRECKENRIDGE | Jefferson - 3920 Dutchmans Ln. - Louisville | BR1181 | Louisville - Browns Ln - SE of Substation | 24.1414 | 2062 | 2020-08-01 | 1.392% | 6.077% | 0% | 0% | 26.98% | 0% | 8.722% | 48.17% | 0% | 8.665% | 103.3249 | 148.4281 | 1.405 | 1.7545 | Trees Trimmed in 2020
BRECKENRIDGE | Jefferson - 3920 Dutchmans Ln. - Louisville | BR1182 | Louisville - I - 264 East - E of Substation | 6.0485 | 226 | 2020-08-01 | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 38.9759 | 43.1 | 0.51973 | 1 | Continue to Monitor
BRECKENRIDGE | Jefferson - 3920 Dutchmans Ln. - Louisville | BR1184 | Louisville - I - 264 East - E of Substation | 1.2677 | 8 | 2020-07-17 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 171.1867 | 744.3333 | 0.28 | 1 | Continue to Monitor
BRECKENRIDGE | Jefferson - 3920 Dutchmans Ln. - Louisville | BR1185 | Louisville - Taylorsville Rd - S of Substation | 14.8767 | 1827 | 2021-01-16 | 5.429% | 2.165% | 0% | 0% | 25.75% | 0% | 7.55% | 38.79% | 0% | 20.32% | 121.1241 | 207.1144 | 1.2325 | 2.0186 | Trees Trimmed in 2021
BRECKENRIDGE | Jefferson - 3920 Dutchmans Ln. - Louisville | BR1351 | Louisville - Brekenridge Ln & Shelbyville Rd - NW of Substation | 8.5492 | 353 | 2019-01-05 | 0.1049% | 0% | 0% | 0% | 55.1% | 0% | 0% | 0% | 0% | 44.8% | 113.8675 | 406.8449 | 1.1441 | 2.0006 | Continue to Monitor
BRECKENRIDGE | Jefferson - 3920 Dutchmans Ln. - Louisville | BR1352 | Louisville - Brekenridge Ln - NW of Substation | 3.3863 | 107 | 2020-07-17 | 8.612% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 91.39% | 19.3285 | 54.8352 | 0.40601 | 1.6204 | Continue to Monitor
BLUEGRASS PARKWAY | Jefferson - 11240 Bluegrass Parkway - Louisville | BY1279 | Louisville - Watterson Way - N of Substation | 13.7762 | 868 | 2017-09-23 | 0% | 0% | 0% | 0% | 1.156% | 0% | 10.02% | 0% | 0% | 88.83% | 36.6075 | 70.2702 | 0.21196 | 0.53338 | Continue to Monitor
BLUEGRASS PARKWAY | Jefferson - 11240 Bluegrass Parkway - Louisville | BY1283 | Louisivlle - Blankenbaker Rd - S of Substation | 7.9803 | 432 | 2017-09-09 | 0% | 2.618% | 0% | 0% | 37.06% | 0.4971% | 40.44% | 10.63% | 0% | 8.762% | 18.7486 | 20.9537 | 0.38437 | 0.23599 | Continue to Monitor
BLUEGRASS PARKWAY | Jefferson - 11240 Bluegrass Parkway - Louisville | BY1285 | Louisivlle - Moser Rd - NW of Substation | 10.7888 | 516 | 2017-09-09 | 0% | 0% | 0.3954% | 0% | 0.803% | 0% | 0% | 98.63% | 0% | 0.1749% | 39.0785 | 39.141 | 0.91036 | 2.0536 | Tree Trim Scheduled for 2021
CANAL | Jefferson - 2005 Northwestern Parkway - Louisville | CA1341 | Louisville - S 20th St & W Market St - S of Substation | 5.6257 | 1049 | 2019-02-23 | 0% | 0% | 0% | 1.023% | 96.19% | 0% | 0% | 0% | 0% | 2.784% | 37.5705 | 45.6899 | 1.8351 | 1.6124 | Continue to Monitor
CANAL | Jefferson - 2005 Northwestern Parkway - Louisville | CA1345 | Louiville - S 20th St & W Broadway - S of Substation | 2.8168 | 1100 | 2019-02-23 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 10.7294 | 14.2139 | 0.56667 | 0.16667 | Continue to Monitor
CANAL | Jefferson - 2005 Northwestern Parkway - Louisville | CA1346 | Louisivlle - Northwestern PKY & W Market St - W fo Substation | 5.5882 | 2196 | 2019-02-23 | 0% | 30.05% | 0% | 0% | 69.49% | 0% | 0.4581% | 0% | 0% | 0% | 42.2312 | 102.002 | 1.3928 | 2.3824 | Continue to Monitor
CENTERFIELD | Oldham - 4210 Hwy 393 - Centerfield | CF1201 | Centerfield - Dawkins Rd - N of Substation | 52.1901 | 532 | 2018-03-24 | 0.09823% | 0.04155% | 2.113% | 0% | 9.755% | 0% | 0.5181% | 47.07% | 0.04753% | 40.35% | 232.6742 | 305.3153 | 1.444 | 2.065 | Continue to Monitor
CENTERFIELD | Oldham - 4210 Hwy 393 - Centerfield | CF1202 | Centerfield - W HWY 22 & Payton Way - SE of Substation | 57.3389 | 995 | 2018-05-12 | 2.216% | 0.08543% | 3.109% | 0% | 62.79% | 0% | 4.439% | 25.64% | 0% | 1.724% | 214.2721 | 230.6229 | 2.1916 | 1.8891 | Continue to Monitor
CAMPGROUND | Jefferson - 4300 Campground Rd. - Louisville | CG1437 | Louisville - Campgraound Rd - SE of Substation | 0.55484 | 1 | 2017-07-17 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 18.56 | 52.8 | 0.4 | 1 | Continue to Monitor
CAMPGROUND | Jefferson - 4300 Campground Rd. - Louisville | CG1438 | Shepherdsville - Campground Rd - SE of Substation | 0.45844 | 1 | 2017-07-17 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 73.7083 | 294.8333 | 0.25 | 1 | Continue to Monitor
CLARKS LANE | Jefferson - 934 Clarks Ln - Louisville | CK0002 | Louisville - Pindell Ave - S of Substation | 2.9885 | 453 | 2019-09-28 | 0% | 4.308% | 6.904% | 0% | 37.64% | 0% | 16.87% | 5.266% | 0% | 29.01% | 32.6485 | 55.0879 | 0.21634 | 0.41959 | Continue to Monitor
CLARKS LANE | Jefferson - 934 Clarks Ln - Louisville | CK0003 | Louisville - Eastern PKY - W of Substation | 1.3705 | 222 | 2019-09-28 | 0% | 11.38% | 0% | 0% | 13.99% | 0% | 0% | 57.15% | 0% | 17.48% | 43.8964 | 48.0414 | 0.35598 | 0.35135 | Continue to Monitor
CLIFTON | Jefferson - 2009 New Main Street - Louisville | CL1227 | Louisville - Frankfort Ave, Clifton Ave, & Ewing Ave - E of Substation | 3.1153 | 647 | 2018-09-15 | 1.287% | 0% | 0% | 0% | 0% | 0% | 17.41% | 77.89% | 0% | 3.412% | 25.4363 | 34.3569 | 0.4156 | 1.0941 | Continue to Monitor
CLIFTON | Jefferson - 2009 New Main Street - Louisville | CL1230 | Louisville - Mellwood Ave, Shiloh Ave, & River Rd - N of Substation | 15.6281 | 2092 | 2018-11-03 | 2.81% | 0% | 0% | 0% | 56.02% | 0% | 5.754% | 24.38% | 7.144% | 3.891% | 47.3585 | 40.2388 | 0.49412 | 1.1392 | Continue to Monitor
CLIFTON | Jefferson - 2009 New Main Street - Louisville | CL1232 | Louisville - Frankfort Ave, Story Ave, & E Main St - W of Substation | 12.5373 | 1777 | 2018-11-03 | 0.131% | 0.6474% | 0% | 6.104% | 51% | 0% | 10.87% | 25.03% | 0.3863% | 5.829% | 42.3491 | 59.8474 | 1.0414 | 0.54392 | Continue to Monitor
CLIFTON | Jefferson - 2009 New Main Street - Louisville | CL1405 | Louisville - Mellwood Ave, River Rd, & River Green Cir - N of Substation | 5.4197 | 82 | 2018-07-28 | 0% | 0% | 0% | 0% | 0.828% | 0% | 6.574% | 92.32% | 0% | 0.2805% | 96.4392 | 269.0886 | 0.98601 | 1.0459 | Continue to Monitor
CLIFTON | Jefferson - 2009 New Main Street - Louisville | CL1407 | Louisville - Payne St, Spring St, & Story Ave - W of Substation | 1.4995 | 5 | 2018-07-28 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 52.3367 | 72.5333 | 1.08 | 0.2 | Continue to Monitor
COLLINS | Jefferson - 3401 Coillins Ln. - Louisville | CO1197 | Louisville - La Grange Rd, Reamers Rd, & Chamberlain Ln - E of Substation | 25.9992 | 1110 | 2019-12-21 | 8.923% | 0% | 0% | 0% | 19.66% | 0% | 0% | 9.069% | 50.93% | 11.42% | 37.2975 | 33.8716 | 0.27796 | 0.32251 | Continue to Monitor
CANE RUN | Jefferson - 5252 Cane Run Rd. - Louisville | CR1422 | Louisville - No Road - At Substation | 0.5249 | 4 | 2017-07-22 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 7.5433 | 11.7167 | 0.16667 | 0.5 | Continue to Monitor
CARTER | Jefferson - Opposite 2215 Carter St - Louisville | CT0001 | Louisville - N 22nd St & Griffiths Ave - S of Substation | 2.3977 | 354 | 2019-02-23 | 0% | 0% | 0% | 0.3366% | 0% | 0% | 12.82% | 0% | 86.85% | 0% | 15.438 | 41.3549 | 0.11873 | 0.15599 | Continue to Monitor
CARTER | Jefferson - Opposite 2215 Carter St - Louisville | CT0002 | Louisville - Portland Ave, 24th St, & Northwestern Pky - W of Substation | 1.8553 | 276 | 2019-02-23 | 0% | 0% | 0% | 0% | 1.414% | 0% | 96.36% | 1.425% | 0% | 0.8034% | 29.3389 | 34.6981 | 0.21237 | 0.33933 | Continue to Monitor
CARTER | Jefferson - Opposite 2215 Carter St - Louisville | CT0003 | Louisville - Portland Ave & N 20th St - SE of Substation | 0.48511 | 44 | 2019-02-23 | 0% | 0% | 0% | 0% | 0% | 0% | 67.72% | 0% | 32.28% | 0% | 12.0287 | 10.8309 | 0.43252 | 0.56439 | Continue to Monitor
CRESTWOOD | Oldham - Floydsburg Rd. - Crestwood | CW1227 | Crestwood - HWY 22, Carriage Hill Dr, & Mary Clayton Ln - NE of Substation | 32.4773 | 958 | 2018-01-27 | 0.874% | 0% | 0.7079% | 0% | 46.85% | 0% | 0.4635% | 51.1% | 0% | 0% | 61.2033 | 112.8146 | 0.41216 | 0.62475 | Continue to Monitor
CRESTWOOD | Oldham - Floydsburg Rd. - Crestwood | CW1228 | Crestwood - HWY 329, I 71, Covered Bridge Rd, & Halls Hill Rd - N of Substation | 71.7515 | 1214 | 2019-12-31 | 0.6641% | 0% | 0.04625% | 0% | 4.673% | 0.1394% | 2.456% | 38.32% | 0% | 53.7% | 204.4369 | 523.1389 | 1.8134 | 3.1639 | Continue to Monitor
CLAY | Jefferson - 908 Clay St. - Louisville | CY1483 | Louisville - Breckinridge St, Vine St, Highland Ave, & Barrett Ave - E of Substation | 2.0879 | 14 | 2018-07-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 23.729 | 22.8889 | 0.21418 | 0.33333 | Continue to Monitor
CLAY | Jefferson - 908 Clay St. - Louisville | CY1484 | Louisville - Jackson St, Jacob St, Floyd St, & 1st St - NW of Substation | 4.1271 | 66 | 2018-07-06 | 6.445% | 0% | 0% | 0% | 88.95% | 0% | 4.609% | 0% | 0% | 0% | 59.1678 | 63.1998 | 0.53567 | 1.2059 | Continue to Monitor
CLAY | Jefferson - 908 Clay St. - Louisville | CY1486 | Louisville - Caldwell St, Logan St, Jackson St, Goss Ave, & Ash St - S of Substation | 4.2213 | 257 | 2018-07-06 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 18.2893 | 82.2448 | 0.37844 | 1.8263 | Continue to Monitor
DAHLIA | Jefferson - 2135 Dahlia Ave. - Louisville | DA1239 | Louisville - Gardiner Ln, I 265 E, & Newburg Rd - SW of Substation | 14.0004 | 1409 | 2018-10-30 | 6.381% | 4.283% | 0% | 0% | 20.84% | 0% | 7.907% | 46.67% | 0% | 13.93% | 89.0729 | 61.108 | 0.59039 | 0.71886 | Continue to Monitor
DEL PARK | Jefferson - 3135 Del Park Terrance - Louisville | DE1410 | Louisville - River Park Dr, Cecil Ave, Greenwood Ave, & Virginia Ave - SW of Substation | 5.5405 | 1624 | 2020-03-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 93.792 | 20.4895 | 3.4577 | 6.0816 | Continue to Monitor
DUMESNIL | Jefferson - 1309 Dumesnil St - Louisville | DU0002 | Louisville - S 13th St, W Hill St, & S 15th St - S of Substation | 3.8243 | 120 | 2019-02-09 | 0% | 0% | 0% | 14.37% | 72.52% | 0% | 13.11% | 0% | 0% | 0% | 47.7373 | 37.0654 | 0.26776 | 0.30368 | Continue to Monitor
DIXIE | Jefferson - 1706 Bernheim Ln. - Louisville | DX1222 | Louisville - Millers Ln, Cane Run Rd, Bells Ln, & Algonquin PKY - W of Substation | 26.7403 | 2408 | 2019-03-01 | 2.805% | 0% | 0% | 2.117% | 5.299% | 0% | 1.212% | 44.93% | 4.083% | 39.55% | 110.788 | 129.4447 | 1.3795 | 0.93768 | Reliability Improvements Scheduled for 2021
DIXIE | Jefferson - 1706 Bernheim Ln. - Louisville | DX1223 | Louisville - Dixie Hwy, S 2nd St, & Hale Ave - NW of Substation | 17.3579 | 2625 | 2019-01-05 | 0.716% | 0% | 0.415% | 2.29% | 10.25% | 0.3771% | 39.16% | 34.38% | 3.584% | 8.829% | 84.6769 | 100.2372 | 1.2883 | 1.0243 | Reliability Improvements Scheduled for 2021
EIGHTH | Jefferson - 841 S 8th St - Louisville | EI0002 | Louisville - W Breckenridge St, S 6th St, & S 4th St - E of Substation | 2.0385 | 162 | 2019-12-21 | 0% | 0% | 0% | 0% | 0% | 0% | 21.8% | 0% | 78.2% | 0% | 14.3188 | 43.2251 | 0.098429 | 0.2263 | Continue to Monitor
EIGHTH | Jefferson - 841 S 8th St - Louisville | EI0003 | Louisville - S 9th St, W Kentucky St, & S 8th St - SW of Substation | 0.58854 | 30 | 2019-12-21 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 11.5283 | 4.3061 | 0.049795 | 0.060606 | Continue to Monitor
ETHEL | Jefferson - 3532 Ethel Ave. - Louisville | ET1168 | Louisville - Ethel Ave, Bardstown Rd, Buechel Bank Rd, & Bradford Dr - E of Substation | 11.8284 | 1459 | 2020-06-27 | 3.275% | 0% | 0% | 0% | 0.5111% | 0% | 0.3694% | 75.89% | 17.12% | 2.836% | 107.2103 | 130.3333 | 1.1036 | 1.2531 | Trees Trimmed in 2020
ETHEL | Jefferson - 3532 Ethel Ave. - Louisville | ET1169 | Louisville - Hikes Ln, Champ Trace Ln, & Bashford Manor Ln - N of Substation | 5.6072 | 697 | 2020-06-27 | 2.158% | 0% | 0% | 0% | 13.86% | 0% | 0% | 43.39% | 0% | 40.59% | 133.7921 | 136.1469 | 0.69176 | 0.58703 | Trees Trimmed in 2020
ETHEL | Jefferson - 3532 Ethel Ave. - Louisville | ET1172 | Louisville - Hikes Ln - NE of Substation | 13.598 | 2026 | 2020-07-11 | 3.583% | 0% | 20.77% | 0% | 0.02119% | 0% | 7.336% | 14.93% | 38.14% | 15.22% | 37.8933 | 32.5841 | 0.27145 | 0.32686 | Continue to Monitor
ETHEL | Jefferson - 3532 Ethel Ave. - Louisville | ET1423 | Louisville - Jennings Ln, Bishop Ln, & Robards Ln - W of Substation | 5.1809 | 59 | 2020-06-13 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 37.8018 | 55 | 0.47204 | 1 | Continue to Monitor
EASTWOOD | Jefferson - 100 Flat Road Rd. - Louisville | EW1240 | Louisville - Shelbyville Rd & Beckley Creek PKWY - W of Substation | 13.5704 | 364 | 2020-02-29 | 46.08% | 0% | 0% | 0% | 41.22% | 0% | 1.949% | 4.602% | 0% | 6.144% | 19.867 | 22.2123 | 0.20904 | 0.35819 | Continue to Monitor
FARNSLEY | Jefferson - 2428 Farnsley Rd. - Louisvlle | FA1123 | Louisville - Kramers Ln, Campground Rd, & Lees Ln - SW of Substation | 17.2543 | 910 | 2017-06-10 | 0.003851% | 0% | 0.002407% | 0% | 7.583% | 0% | 0.3521% | 81.96% | 9.973% | 0.1266% | 79.9271 | 92.3889 | 1.0881 | 1.2905 | Tree Trim Scheduled for 2021
FARNSLEY | Jefferson - 2428 Farnsley Rd. - Louisvlle | FA1214 | Louisville - Farnsley Rd, Cane Run Rd, Ralph Ave, & Campground Rd - N & E of Substation | 12.9625 | 970 | 2017-07-15 | 0.9385% | 1.689% | 0% | 55.29% | 0.338% | 0% | 4.202% | 36.32% | 0.8838% | 0.3401% | 46.5049 | 106.6078 | 0.53837 | 0.52455 | Tree Trim Scheduled for 2021
FARNSLEY | Jefferson - 2428 Farnsley Rd. - Louisvlle | FA1216 | Louisville - Crums Ln, Hillview Ave, & Garrs Ln - SE of Substation | 10.318 | 1321 | 2017-06-03 | 4.089% | 0.2101% | 4.614% | 0.1359% | 3.758% | 0% | 15.9% | 48.02% | 11.18% | 12.1% | 118.2225 | 118.3666 | 1.9499 | 2.4168 | Reliability Improvements Scheduled for 2021
FALLS CITY | Jefferson - 1048 S 43rd St - Louisville | FC0003 | Louisville - S 43rd St, Fordson Way, & Cecil Ave - S of Substation | 1.9055 | 277 | 2019-01-05 | 0% | 83.6% | 0% | 0% | 0% | 0% | 0% | 0% | 16.4% | 0% | 8.2022 | 8.3359 | 0.27667 | 0.09353 | Continue to Monitor
FREYS HILL | Jefferson - 3300 Freys Hill Rd. - Louisville | FH1209 | Louisville - Westport Rd, Langdon Dr, & Tiverton Way - SW of Substation | 13.7324 | 1547 | 2019-08-10 | 0.2061% | 0% | 4.446% | 0% | 15.51% | 0% | 1.928% | 77.25% | 0% | 0.6624% | 55.6822 | 140.3785 | 0.27238 | 0.69331 | Continue to Monitor
FREYS HILL | Jefferson - 3300 Freys Hill Rd. - Louisville | FH1211 | Louisville - Springhurst Blvd & Champion Farms Dr - N of Substation | 5.7423 | 366 | Underground Circuit | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 35.5861 | 24.1882 | 0.33661 | 0.3406 | Continue to Monitor
FREYS HILL | Jefferson - 3300 Freys Hill Rd. - Louisville | FH1213 | Louisville - Westport Rd, Blossom Ln, Goose Creek Rd & Brownsboro Rd - W of Substation | 28.287 | 1986 | 2019-07-20 | 3.64% | 0% | 11.27% | 0% | 33.93% | 0% | 1.344% | 49.17% | 0% | 0.6466% | 61.4588 | 119.1458 | 0.53299 | 1.5551 | Continue to Monitor
FREYS HILL | Jefferson - 3300 Freys Hill Rd. - Louisville | FH1214 | Louisville - Freys Hill Rd, Evergreen Rd, & Park Rd - SE of Substation | 26.285 | 720 | 2019-05-04 | 0.1009% | 0% | 0% | 0% | 0.7524% | 0% | 2.315% | 91.84% | 0% | 4.991% | 84.4118 | 191.2942 | 1.1066 | 1.7293 | Continue to Monitor
FREYS HILL | Jefferson - 3300 Freys Hill Rd. - Louisville | FH1216 | Louisville - Springhurst Blvd & N Hurstbourne PKY - NW of Substation | 15.7925 | 903 | 2019-08-10 | 0.08106% | 0% | 0% | 0% | 83.22% | 0% | 16.7% | 0% | 0% | 0% | 18.3758 | 47.0918 | 0.21769 | 0.64915 | Continue to Monitor
FLOYD | Jefferson - 1806 S Floyd St. - Louisville | FL1496 | Louisville - Floyd St, Warnock St, & Crittenden Dr - SE of Substation | 3.763 | 1122 | 2016-02-12 | 0.5434% | 0% | 0% | 0% | 61.96% | 0% | 37.49% | 0% | 0% | 0% | 29.1158 | 79.8649 | 0.7535 | 1.7746 | Continue to Monitor
FAIRMOUNT | Jefferson - 10713 Fairmount Rd. - Louisville | FM1256 | Louisville - Bardstown Rd, Lands Ln, & HWY 44 - S of Substation | 36.4678 | 1911 | 2018-08-25 | 0.02035% | 0% | 0.03468% | 0% | 0.6512% | 0% | 0.4259% | 93.73% | 0.009534% | 5.129% | 23.6836 | 67.6782 | 0.39954 | 1.3181 | Continue to Monitor
FAIRMOUNT | Jefferson - 10713 Fairmount Rd. - Louisville | FM1257 | Louisville - Brentlinger Ln, Seatonville Rd, Brush Run Rd, & Routt Rd - E of Substation | 93.0811 | 2011 | 2019-01-05 | 0.5363% | 0.0341% | 3.035% | 0% | 26.17% | 0% | 12.76% | 51.91% | 0.04744% | 5.504% | 65.1238 | 128.0051 | 0.46763 | 0.89007 | Continue to Monitor
FORTY FOURTH | Jefferson - 128 N 44th St - Louisville | FO0001 | Louisville - N 44th St & Bank St - N of Substation | 1.3422 | 212 | 2020-04-18 | 0% | 0% | 0% | 0% | 9.214% | 0% | 16.85% | 43.42% | 0% | 30.52% | 13.0927 | 16.0253 | 0.39485 | 0.41065 | Trees Trimmed in 2020
FERN VALLEY | Jefferson - 1256 Old Fern Valley Rd. - Louisville | FV1135 | Louisville - Forest Dr, E Indian Trl, & Poplar Level Rd - N of Substation | 16.955 | 2101 | 2017-04-15 | 1.281% | 0% | 0% | 0.1785% | 12.85% | 0% | 29.43% | 1.127% | 51.11% | 4.015% | 57.6984 | 61.8883 | 0.6619 | 1.2734 | Continue to Monitor
FERN VALLEY | Jefferson - 1256 Old Fern Valley Rd. - Louisville | FV1138 | Louisville - Fern Valley Rd & Shepherdsville Rd - E of Substation | 10.862 | 1554 | 2017-04-01 | 0% | 0% | 0% | 0% | 0.7696% | 0% | 3.494% | 0.09162% | 1.519% | 94.13% | 25.8418 | 35.1012 | 0.42113 | 0.23669 | Continue to Monitor
FERN VALLEY | Jefferson - 1256 Old Fern Valley Rd. - Louisville | FV1139 | Louisville - Industrial Blvd, Grade Ln, & Knopp Ave - W of Substation | 8.4904 | 216 | 2017-04-01 | 0% | 0% | 0% | 0% | 0.5648% | 0% | 2.786% | 94.48% | 0.896% | 1.269% | 114.0622 | 252.4711 | 1.347 | 2.1069 | Tree Trim Scheduled for 2021
FERN VALLEY | Jefferson - 1256 Old Fern Valley Rd. - Louisville | FV1142 | Louisville - Mile of Sunshine Dr, Whispering Hills Blvd, & Yellow Sands Dr - E of Substation | 19.62 | 2173 | 2017-04-15 | 0.2881% | 0% | 0% | 0% | 0% | 0% | 0.06794% | 0.8007% | 98.27% | 0.5683% | 87.517 | 356.3603 | 0.43249 | 0.80437 | Continue to Monitor
FERN VALLEY | Jefferson - 1256 Old Fern Valley Rd. - Louisville | FV1143 | Louisville - Preston Hwy, Clay Ave, Minor Ln, Foreman Ln, & Bonaventure Blvd - S of Substation | 17.876 | 1504 | 2017-04-01 | 0.1476% | 0% | 2.525% | 0% | 20.38% | 0% | 11.06% | 5.456% | 29.02% | 31.41% | 101.9652 | 113.4972 | 1.5818 | 2.1273 | Continue to Monitor
FERN VALLEY | Jefferson - 1256 Old Fern Valley Rd. - Louisville | FV1144 | Louisville - Preston Hwy & Oaklawn Dr - S of Substation | 1.2451 | 30 | 2017-04-15 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 32.8369 | 0.99997 | 0.38628 | 1 | Continue to Monitor
FERN VALLEY | Jefferson - 1256 Old Fern Valley Rd. - Louisville | FV1478 | Louisville - Preston Hwy, & Standiford Ave/Ln - NW of Substation | 6.9455 | 115 | 2021-03-29 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 66.1486 | 10.393 | 0.94017 | 0.99138 | Continue to Monitor
GAULBERT | Jefferson - 2950 Wilson Ave - Louisville | GA0002 | Louisville - Wilson Ave - SW of Substation | 0.13817 | 17 | 2019-01-11 | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 47.9588 | 74.7941 | 0.27059 | 0.35294 | Continue to Monitor
GILLIGAN | Jefferson - 35th Street & Gilligan Ave - Louisville | GI0002 | Louisville - S 32nd St - S of Substation | 2.3136 | 167 | 2020-04-04 | 0% | 0% | 0% | 72.36% | 13.68% | 0% | 13.96% | 0% | 0% | 0% | 101.4242 | 167.8989 | 1.4035 | 2.1679 | Continue to Monitor
GILLIGAN | Jefferson - 35th Street & Gilligan Ave - Louisville | GI0003 | Louisville - Bank St, N 39th St, & S 38th St - W of Substation | 3.2909 | 465 | 2020-04-04 | 5.974% | 0% | 0% | 0% | 13.4% | 0% | 5.197% | 0% | 0% | 75.43% | 39.6022 | 55.2699 | 0.48911 | 1.2835 | Continue to Monitor
GRADE LANE | Jefferson - 6909 Grade Lane - Louisville | GL1330 | Shepherdsville - Grade Lane - NE of Substation | 0.5535 | 2 | 2017-04-01 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 299.9125 | 997.1417 | 0.375 | 0.5 | Continue to Monitor
GRADE LANE | Jefferson - 6909 Grade Lane - Louisville | GL1331 | Shepherdsville - Grade Lane - NE of Substation | 0.50823 | 1 | 2017-04-01 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 561.4333 | 1881.7333 | 0.5 | 1 | Continue to Monitor
GRADE LANE | Jefferson - 6909 Grade Lane - Louisville | GL1332 | Shepherdsville - Grade Lane - NE of Substation | 0.51162 | 1 | 2017-04-01 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 221.1 | 596.4 | 0.5 | 1 | Continue to Monitor
GRADE LANE | Jefferson - 6909 Grade Lane - Louisville | GL1335 | Louisville - Grade Ln & Midfield Access Rd - N of Substation | 2.7715 | 1 | Underground Circuit | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 294.9033 | 289.5167 | 0.4 | 1 | Continue to Monitor
GRADY | Jefferson - 1838 S 39th St. - Louisville | GR1124 | Louisville - I 264 East & Stratton Ave - N of Substation | 2.0575 | 253 | 2019-01-05 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 27.54% | 0% | 72.46% | 23.0598 | 105.3433 | 0.25697 | 1.0433 | Continue to Monitor
GRADY | Jefferson - 1838 S 39th St. - Louisville | GR1464 | Louisville - Algonquin Pky, Virgina Ave, & S 43rd St - NW of Substation | 3.3997 | 776 | 2019-03-16 | 0% | 0% | 14.96% | 0% | 13.5% | 0% | 0% | 33.51% | 0% | 38.03% | 19.0424 | 89.7833 | 1.0286 | 4 | Continue to Monitor
HALE | Jefferson - Rear 185 Hale Ave - Louisville | HA0002 | Louisville - Dixie Hwy, Hale Ave, Dumesnil St, & St Louis Ave - S of Substation | 2.7721 | 562 | 2019-02-09 | 0.6706% | 0% | 0% | 1.777% | 0.4862% | 0% | 30.58% | 0% | 61.42% | 5.066% | 31.0112 | 72.335 | 0.24462 | 0.36315 | Continue to Monitor
HURSTBOURNE | Jefferson - 1830 Plantside Drive - Louisville | HB1141 | Louisville - Embassy Square Blvd, Doral Ct, & Bunsen Pky - NW of Substation | 7.3255 | 920 | 2019-12-14 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 99.63% | 0.3685% | 13.8967 | 7.7696 | 0.081568 | 0.090292 | Continue to Monitor
HURSTBOURNE | Jefferson - 1830 Plantside Drive - Louisville | HB1144 | Louisville - Old Hickory Rd, Waterson Trl, & Blankenbaker Access Dr - SE of Substation | 6.5383 | 279 | 2019-11-26 | 0% | 0% | 0% | 0% | 0% | 0% | 20.57% | 78.84% | 0% | 0.5833% | 72.8252 | 162.5123 | 0.91727 | 0.2464 | Continue to Monitor
HURSTBOURNE | Jefferson - 1830 Plantside Drive - Louisville | HB1147 | Louisville - I 64 W, Linn Station Rd, & Timberwood Cir - NNW of Substation | 10.1287 | 570 | 2019-12-14 | 10.6% | 0% | 8.208% | 0% | 59.05% | 0% | 0.3048% | 21.16% | 0% | 0.6751% | 142.9362 | 366.0929 | 2.3499 | 5.8846 | Continue to Monitor
HURSTBOURNE | Jefferson - 1830 Plantside Drive - Louisville | HB1148 | Louisville - Old Hickory Rd, Taylorsville Rd, College Dr, & Rown Tree Rd - S of Substation | 19.8603 | 2250 | 2020-07-17 | 3.471% | 0% | 3.367% | 0% | 8.046% | 0% | 22.4% | 60.1% | 0.338% | 2.281% | 37.6643 | 60.1749 | 0.28156 | 0.37718 | Trees Trimmed in 2020
HURSTBOURNE | Jefferson - 1830 Plantside Drive - Louisville | HB1149 | Louisville - Plantside Dr, Production Dr, & Research Dr - E of Substation | 2.382 | 31 | 2019-11-26 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 14.6624 | 19.6527 | 0.16554 | 0.032258 | Continue to Monitor
HURSTBOURNE | Jefferson - 1830 Plantside Drive - Louisville | HB1150 | Louisville - Bunsen Way & Production Dr - E of Substation | 2.785 | 324 | 2019-11-26 | 0.2924% | 0% | 0% | 0% | 84.92% | 0% | 13.63% | 0% | 0% | 1.15% | 20.0966 | 48.7999 | 0.14159 | 0.43769 | Continue to Monitor
HILLCREST | Jefferson - 3015 Frankfort Ave. - Louisville | HC1292 | Louisville - Grinstead Dr, Lexington Rd, & Alta Vista Rd - S of Substation | 14.4113 | 848 | 2019-12-14 | 12.16% | 0% | 0% | 0% | 11.43% | 0% | 4.239% | 14.58% | 0% | 57.6% | 58.7379 | 82.1081 | 0.5474 | 0.75951 | Continue to Monitor
HILLCREST | Jefferson - 3015 Frankfort Ave. - Louisville | HC1431 | Louisville - Hillcrest Ave & Zorn Ave - N of Substation | 2.2255 | 4 | 2017-04-24 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 80.585 | 88.925 | 0.25 | 0.25 | Continue to Monitor
HILLCREST | Jefferson - 3015 Frankfort Ave. - Louisville | HC1433 | Louisville - No Road - E of Substation | 0.13001 | 1 | 2017-04-24 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 9.0733 | 45.3667 | 0.2 | 1 | Continue to Monitor
HILLCREST | Jefferson - 3015 Frankfort Ave. - Louisville | HC1434 | Louisville - Stilz Ave, Lexington Rd, & Alta Vista Rd - S & E of Substation | 3.2479 | 1 | 2017-04-24 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 84.4814 | 369.9167 | 0.65069 | 1 | Continue to Monitor
HERMAN | Jefferson - Rear 3619 Jefferson St - Louisville | HE0003 | Louisville - 38th St, Amy Ave, & W Muhammad Ali Blvd - N & SW of Substation | 3.0746 | 648 | 2020-03-21 | 0% | 0% | 0% | 0% | 32.23% | 0% | 0% | 14.93% | 0% | 52.85% | 21.6362 | 11.2295 | 0.13563 | 0.15262 | Continue to Monitor
HIGHLAND | Jefferson - 1917 Stevens Ave. - Louisville | HI1102 | Louisville - Bardstown Rd, Baringer Ave & Highland Ave - NW of Substation | 5.6543 | 1492 | 2017-03-31 | 0% | 0% | 1.154% | 0% | 30.91% | 0% | 9.984% | 10.58% | 17.28% | 30.1% | 96.9509 | 65.4437 | 1.5398 | 2.394 | Continue to Monitor
HIGHLAND | Jefferson - 1917 Stevens Ave. - Louisville | HI1473 | Louisville - Eastern Pky, Poplar Level Rd, & Nightingale Rd - SW of Substation | 5.653 | 1180 | 2017-04-01 | 0% | 0% | 0% | 0% | 0% | 0% | 1.712% | 0% | 0% | 98.29% | 56.9211 | 62.9383 | 0.86714 | 1.3 | Continue to Monitor
HIGHLAND | Jefferson - 1917 Stevens Ave. - Louisville | HI1475 | Louisville - Cherokee Pky, Bardstown Rd, & Richmond Dr - N & SE of Substation | 4.6473 | 21 | 2017-04-01 | 59.65% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 40.35% | 0% | 57.367 | 103.1333 | 0.8 | 2 | Continue to Monitor
HARRODS CREEK | Jefferson - 6611 Del Haven Rd. - Louisville | HK1234 | Louisville - HWY 42, Wolf Pen Branch Rd, & Barbour Ln - SE of Substation | 52.496 | 1998 | 2018-11-13 | 0.5358% | 0.3141% | 0.1183% | 0% | 1.572% | 0% | 6.049% | 87.91% | 0% | 3.499% | 239.7677 | 377.2007 | 2.2204 | 1.0911 | Continue to Monitor
HARRODS CREEK | Jefferson - 6611 Del Haven Rd. - Louisville | HK1242 | Louisville - River Rd, Shirley Ave, & Duroc Ave - N of Substation | 10.806 | 585 | 2018-06-09 | 3.801% | 0% | 0% | 0% | 3.457% | 0% | 0.204% | 91.51% | 1.029% | 0% | 18.5079 | 44.4748 | 0.15379 | 0.28618 | Continue to Monitor
HARRODS CREEK | Jefferson - 6611 Del Haven Rd. - Louisville | HK1243 | Louisville - US 42, Covered Bridge Rd, Rose Island Rd, & River Bluff Rd - NNE of Substation | 53.1672 | 1493 | 2018-04-20 | 0.1089% | 0% | 0% | 0% | 18.74% | 0% | 3.828% | 72.37% | 1.024% | 3.929% | 197.0012 | 267.2871 | 1.8717 | 1.832 | Continue to Monitor
HARMONY LANDING | Oldham - 11943 W Hwy 42 - Goshen | HL1155 | Goshen - Goshen Ln - NW of Substation | 15.0892 | 381 | 2018-01-13 | 0% | 18.29% | 0% | 0% | 2.815% | 0% | 3.395% | 75.5% | 0% | 0% | 26.1483 | 39.6939 | 0.3138 | 0.12849 | Continue to Monitor
HARMONY LANDING | Oldham - 11943 W Hwy 42 - Goshen | HL1157 | Goshen - Meadowridge Trl, Hwy 1793, & Rose Island Rd - W of Substation | 33.0648 | 1280 | 2017-11-18 | 0.7784% | 0% | 31.88% | 4.268% | 5.401% | 0.04147% | 0.1378% | 52.88% | 0.0264% | 4.588% | 307.281 | 710.1336 | 2.6167 | 2.9375 | Reliability Improvements Scheduled for 2021
HARMONY LANDING | Oldham - 11943 W Hwy 42 - Goshen | HL1158 | Goshen - US 42 & Buckeye Ln - NE of Substation | 31.923 | 521 | 2017-11-10 | 0.1024% | 1.2% | 7.644% | 0% | 1.817% | 0% | 3.217% | 77.15% | 0% | 8.867% | 216.8219 | 234.0409 | 1.5326 | 1.0434 | Tree Trim Scheduled for 2021
HANCOCK | Jefferson - 630 E Caldwell St - Louisville | HN1200 | Louisville - Shelby St, E Broadway, Baxter Ave, & Cherokee Rd - NE of Substation | 6.4032 | 1876 | 2018-07-06 | 1.392% | 0% | 37.43% | 0% | 1.815% | 0% | 21.8% | 8.503% | 0% | 29.06% | 59.8773 | 37.3787 | 0.89666 | 1.1931 | Continue to Monitor
HANCOCK | Jefferson - 630 E Caldwell St - Louisville | HN1204 | Louisville - S Preston St, E Broadway, S Shelby St, & E Madison St - N of Substation | 8.6264 | 1209 | 2018-07-06 | 0.6471% | 0% | 0% | 0% | 71.34% | 0% | 3.763% | 0% | 0% | 24.25% | 25.1619 | 30.4309 | 0.5802 | 0.3974 | Continue to Monitor
INTERNATIONAL | Jefferson - 5599 Cane Run Rd. - Louisville | IN1290 | Louisville - Cane Run Rd, Greenbelt Hwy, & Rockaway Dr - ENE of Substation | 13.9415 | 998 | 2017-07-22 | 3.29% | 0% | 17.08% | 0% | 11.5% | 0% | 3.831% | 6.238% | 4.222% | 53.85% | 86.683 | 117.8263 | 0.84958 | 1.9203 | Continue to Monitor
INTERNATIONAL | Jefferson - 5599 Cane Run Rd. - Louisville | IN1298 | Louisville - Cane Run Rd & Distribution Dr - S of Substation | 3.7043 | 43 | 2017-07-22 | 3.565% | 0% | 0% | 0% | 80.21% | 0% | 0% | 0% | 0% | 16.22% | 50.524 | 16.2217 | 0.64175 | 1.0698 | Continue to Monitor
JEFFERSONTOWN | Jefferson - 11412 Taylorsville Rd. - Louisville | JT1123 | Louisville - Taylorsville Rd, I 265 S, & Eastwood Fisherville Rd - E of Substation | 67.6469 | 1397 | 2020-08-08 | 4.391% | 0.924% | 0.749% | 0% | 4.235% | 0% | 0.333% | 55.49% | 0% | 33.88% | 74.6043 | 100.0415 | 0.71078 | 0.80924 | Trees Trimmed in 2020
KENWOOD | Jefferson - 115 Steedly Dr. - Louisville | KE1156 | Louisville - Strawberry Ln, Southside Dr, & National TPke - S of Substation | 12.5444 | 1249 | 2020-12-19 | 8.41% | 0% | 0% | 0% | 12.64% | 0% | 7.367% | 0.5699% | 8.714% | 62.3% | 45.7441 | 77.9592 | 0.42028 | 0.83509 | Continue to Monitor
KENWOOD | Jefferson - 115 Steedly Dr. - Louisville | KE1157 | Louisville - S 3rd St - NW of Substation | 2.0326 | 299 | 2020-12-19 | 0% | 0% | 0% | 0% | 0% | 0% | 4.948% | 0% | 85.37% | 9.681% | 24.2817 | 49.8523 | 0.25309 | 0.76042 | Continue to Monitor
KENWOOD | Jefferson - 115 Steedly Dr. - Louisville | KE1159 | Louisville - Kenwood Dr, Homestead Dr, & Southside Dr - SW of Substation | 12.4408 | 1426 | 2017-03-18 | 3.758% | 8.02% | 11.23% | 9.973% | 7.942% | 0% | 31.74% | 20.46% | 1.829% | 5.042% | 51.7794 | 89.2252 | 0.70526 | 2.1013 | Continue to Monitor
KENWOOD | Jefferson - 115 Steedly Dr. - Louisville | KE1161 | Louisville - Southside Dr, 3rd St, & W Kenwood Way - N of Substation | 5.8075 | 731 | 2017-03-18 | 10.95% | 0% | 0% | 0% | 5.369% | 0% | 6.817% | 71.62% | 0% | 5.24% | 52.1666 | 66.0459 | 0.61551 | 0.83237 | Tree Trim Scheduled for 2021
KENWOOD | Jefferson - 115 Steedly Dr. - Louisville | KE1162 | Louisville - Strawberry Ln & Eiler Ave - E of Substation | 2.4571 | 76 | 2020-12-19 | 0% | 0% | 0% | 0% | 39.24% | 0% | 60.76% | 0% | 0% | 0% | 18.5441 | 24.4863 | 0.11695 | 0.18703 | Continue to Monitor
LYNN | Jefferson - Rear of 2071 S Preston St & Lynn St - Louisville | LN0001 | Louisville - Shelby St - NE & SE of Substation | 2.989 | 534 | 2018-07-21 | 0% | 0% | 0% | 0% | 54.05% | 0% | 3.52% | 2.163% | 23.82% | 16.45% | 47.483 | 74.2853 | 0.48698 | 1.2811 | Continue to Monitor
LYNN | Jefferson - Rear of 2071 S Preston St & Lynn St - Louisville | LN0002 | Louisville - Preston St & Miller Ave - S of Substation | 2.5554 | 480 | 2018-07-21 | 0% | 0% | 0% | 0% | 0% | 9.718% | 63.56% | 7.521% | 0% | 19.2% | 35.8734 | 38.6892 | 0.3334 | 0.35132 | Continue to Monitor
LOCUST | Jefferson - 2929 Preston Hwy - Louisville | LO1191 | Louisville - Hess Ln & Polar Level Rd - E of Substation | 1.777 | 55 | 2019-12-21 | 0% | 0% | 0% | 0% | 77.63% | 0% | 0% | 0% | 0% | 22.37% | 36.9932 | 64.2642 | 1.0283 | 1.9451 | Continue to Monitor
LYNDON SOUTH | Jefferson - 918 Ormsby Ln. - Bellemeade | LS1241 | Bellemeade - Old Whipps Mill Rd, Dorchester Rd, & Shelbyville Rd - S & SE of Substation | 5.8002 | 454 | 2021-01-23 | 0% | 0% | 0% | 0% | 12.59% | 0% | 58.07% | 27.8% | 0% | 1.543% | 83.0618 | 104.9916 | 0.61718 | 0.89865 | Trees Trimmed in 2021
LYNDON SOUTH | Jefferson - 918 Ormsby Ln. - Louisville | LS1243 | Louisville - Ormsby Ln & LaGrange Rd - NE of Substation | 9.5361 | 809 | 2018-04-20 | 2.957% | 0% | 0% | 0% | 20.08% | 3.453% | 7.17% | 7.094% | 58.43% | 0.8233% | 43.6913 | 29.3277 | 0.66152 | 0.80872 | Continue to Monitor
LYNDON SOUTH | Jefferson - 918 Ormsby Ln. - Bellemeade | LS1244 | Lyndon - New La Grange Rd, La Grange Rd, Whipps Mill Rd - N & NE of Substation | 16.8947 | 1902 | 2017-03-31 | 2.059% | 0.2482% | 0% | 0% | 14.32% | 1.174% | 6.259% | 48.03% | 0% | 27.91% | 67.7441 | 79.8847 | 0.45539 | 0.54466 | Tree Trim Scheduled for 2021
LYNDON SOUTH | Jefferson - 918 Ormsby Ln. - Louisville | LS1246 | Louisville - New La Grange Rd - NW of Substation | 2.08 | 385 | 2021-01-23 | 41.58% | 0% | 0% | 0% | 0% | 0% | 3.606% | 0% | 0% | 54.81% | 20.5071 | 49.144 | 0.27476 | 0.4875 | Continue to Monitor
LYNDON | Jefferson - 8407 LaGrange Rd. - Louisville | LY1111 | Louisville - Ormsby Ln, Herr Ln, & Graymoor Rd - NW of Substation | 24.5187 | 2147 | 2021-01-23 | 3.487% | 1.032% | 0% | 0.02274% | 18.08% | 0% | 8.464% | 59.73% | 0% | 9.186% | 92.8124 | 135.0124 | 0.5961 | 0.92273 | Trees Trimmed in 2021
MILL CREEK - LGE | Jefferson - 14660 Dixie Hwy - Louisville | MC1261 | Louisville - Dixie Hwy, Pendleton Rd, & Blevins Gap Rd - NE of Substation | 63.8117 | 2423 | 2017-02-04 | 1.532% | 0% | 0% | 0% | 8.511% | 0% | 18.18% | 34.15% | 32.9% | 4.726% | 110.8808 | 92.7092 | 1.0843 | 1.7877 | Reliability Improvements Completed in 2020
MAGAZINE | Jefferson - 646 S 13th St. - Louisville | MG0411 | Louisville - W Broadway, 15th St, Garland Ave, & 16th St - SW of Substation | 4.3509 | 370 | 2020-02-01 | 0% | 1.052% | 0% | 0% | 0.294% | 0% | 11.19% | 4.676% | 82.55% | 0.2367% | 83.5266 | 134.4909 | 0.9547 | 1.2122 | Continue to Monitor
MAGAZINE | Jefferson - 646 S 13th St. - Louisville | MG0451 | Louisville - W Broadway - S of Substation | 0.76826 | 31 | 2020-02-01 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 22.4391 | 27.0586 | 0.085161 | 0.096774 | Continue to Monitor
MAGAZINE | Jefferson - 646 S 13th St. - Louisville | MG0452 | Louisville - 12th St, W Kentucky St, & W Oak St - S of Substation | 2.5412 | 60 | 2020-02-01 | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 112.2039 | 77.1997 | 0.68134 | 1.0164 | Continue to Monitor
MAGAZINE | Jefferson - 646 S 13th St. - Louisville | MG1327 | Louisville - Magazine St, Dr W J Hodge St, & 28th St - W of Substation | 3.007 | 15 | 2020-02-01 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0.65381 | 0.99998 | 0.21429 | 1 | Continue to Monitor
MANSLICK | Jefferson - 8703 Manslick Rd. - Louisville | MK1291 | Louisville - Saint Anthonys Church Rd - NW of Substation | 8.1817 | 137 | 2018-01-06 | 0% | 0% | 0% | 0% | 17.63% | 0% | 0% | 82.37% | 0% | 0% | 49.5204 | 92.1545 | 0.63918 | 0.39006 | Continue to Monitor
MANSLICK | Jefferson - 8703 Manslick Rd. - Louisville | MK1293 | Louisville - Manslick Rd and Brown Austin Rd - SE of Substation | 18.6436 | 1268 | 2019-01-26 | 0.733% | 0% | 0% | 0% | 51.68% | 0% | 1.877% | 0% | 9.435% | 36.28% | 32.6849 | 30.188 | 0.2206 | 0.2311 | Continue to Monitor
MANSLICK | Jefferson - 8703 Manslick Rd. - Louisville | MK1295 | Louisville - Outer Loop, New Cut Rd, & Scottsdale Blvd - NE of Substation | 19.0244 | 1772 | 2017-10-07 | 0% | 0% | 0.3603% | 0% | 0.8887% | 0% | 45.1% | 6.366% | 0% | 47.29% | 42.0866 | 46.2358 | 0.48782 | 0.2751 | Continue to Monitor
MANSLICK | Jefferson - 8703 Manslick Rd. - Louisville | MK1296 | Louisville - 3rd St Rd, Christland Rd, & Manslick Rd - N of Substation | 17.2497 | 1729 | 2018-01-06 | 6.594% | 0% | 0.8015% | 0% | 7.518% | 0% | 0.3609% | 77.56% | 1.235% | 5.928% | 43.3146 | 89.0607 | 0.35266 | 0.44661 | Continue to Monitor
MANSLICK | Jefferson - 8703 Manslick Rd. - Louisville | MK1297 | Louisville - Outer Loop & National Tpke - NE of Substation | 8.2707 | 579 | 2017-10-07 | 0% | 0% | 0% | 0% | 64.63% | 0% | 5.708% | 0.5096% | 0% | 29.15% | 43.2677 | 50.9469 | 0.57833 | 0.50012 | Continue to Monitor
MANSLICK | Jefferson - 8703 Manslick Rd. - Louisville | MK1298 | Louisville - Manslick Rd, Belvins Gap Rd, & Brown Austin Rd - SW & SE of Substation | 8.985 | 584 | 2019-05-04 | 0.6919% | 0% | 0% | 0% | 35.14% | 0% | 0.2609% | 51.55% | 0% | 12.35% | 212.5306 | 500.5782 | 1.5064 | 2.2146 | Continue to Monitor
MUD LANE | Jefferson - 4900 Mud Ln. - Louisville | ML1283 | Louisville - Preston Hwy, Cooper Chapel Rd, & Charleswood Rd - N of Substation | 28.0204 | 1868 | 2019-07-13 | 0.009588% | 0.2755% | 0.2523% | 0% | 52.29% | 0% | 0.33% | 0.8503% | 0% | 45.99% | 87.8492 | 100.8753 | 1.0267 | 1.3822 | Continue to Monitor
MUD LANE | Jefferson - 4900 Mud Ln. - Louisville | ML1284 | Louisville - Christman Dr, Mount Washington Rd, & Cedar Creek Rd- E of Substation | 48.9912 | 2515 | 2019-08-24 | 14.42% | 0% | 0.2311% | 0% | 14.94% | 0% | 3.551% | 54.24% | 4.953% | 7.664% | 22.9249 | 32.7997 | 0.24535 | 0.36154 | Continue to Monitor
MUD LANE | Jefferson - 4900 Mud Ln. - Louisville | ML1285 | Louisville - Preston Hwy, Lees Ln, Rogers Ave, & Zoneton Rd - S of Substation | 26.1654 | 1621 | 2019-06-15 | 10.93% | 0% | 23.59% | 0% | 4.171% | 0% | 0.4614% | 0% | 0% | 60.85% | 70.7528 | 70.2075 | 0.337 | 0.43215 | Continue to Monitor
MUD LANE | Jefferson - 4900 Mud Ln. - Louisville | ML1286 | Louisville - Overdale Dr, Blossom Rd, Summers Dr, & Summit Dr - SW of Substation | 26.742 | 2542 | 2019-06-15 | 39.56% | 0% | 0% | 0% | 17.22% | 0% | 2.415% | 2.238% | 1.534% | 37.03% | 19.4566 | 19.919 | 0.3824 | 0.29451 | Continue to Monitor
MUD LANE | Jefferson - 4900 Mud Ln. - Louisville | ML1288 | Louisville - Preston Hwy, Hebron Ln, & Bells Mill Rd - S of Substation | 38.0101 | 1586 | 2019-08-03 | 4.536% | 0% | 0% | 0% | 57.55% | 0% | 2.26% | 2.375% | 3.571% | 29.71% | 56.2915 | 50.8477 | 0.56299 | 0.56966 | Continue to Monitor
MUD LANE | Jefferson - 4900 Mud Ln. - Louisville | ML1289 | Louisville - Holgate Dr, 1st, 2nd, & 3rd St - SE of Substation | 6.386 | 813 | 2019-07-13 | 2.53% | 0% | 0% | 0% | 20.45% | 0% | 0.5844% | 29.55% | 0% | 46.89% | 108.9084 | 139.083 | 1.7674 | 3.484 | Continue to Monitor
MUD LANE | Jefferson - 4900 Mud Ln. - Louisville | ML1290 | Louisville - Southpoint Dr - NW of Substation | 0.74793 | 2 | 2019-07-13 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 38.1233 | 190.6167 | 0.2 | 1 | Continue to Monitor
MULDRAUGH | Meade - 100 Carpenter Test Rd. - Muldraugh | MU1101 | Muldraugh - Carpenter Test Rd, Main St, & Dixie Hwy - E & SE of Substation | 10.3755 | 554 | 2018-01-13 | 0.1254% | 0% | 0% | 0% | 30.8% | 0% | 0% | 0% | 0% | 69.07% | 54.0662 | 146.8808 | 1.1454 | 2.463 | Continue to Monitor
NACHAND | Jefferson - 7201 Verona Way - Louisville | NA1265 | Louisville - Hunsinger Ln - NNE of Substation | 15.9667 | 1343 | 2017-06-13 | 2.802% | 0% | 0% | 0% | 3.167% | 0% | 0% | 0% | 0% | 94.03% | 72.9746 | 114.1613 | 0.71014 | 0.32847 | Continue to Monitor
NACHAND | Jefferson - 7201 Verona Way - Louisville | NA1271 | Louisville - Nachand Ln, Watterson Trl, & Hurstbourne Pky - SE of Substation | 19.1742 | 1560 | 2017-05-31 | 1.313% | 0% | 0% | 0% | 93.44% | 0% | 0% | 0.2054% | 0% | 5.041% | 21.0443 | 45.9881 | 0.18988 | 0.41615 | Continue to Monitor
OLD HENRY | Jefferson - 13601 Terra View Trail - Louisville | OH1170 | Louisville - Old Henry Rd, Nelson Miller Pky, & Stanley Gault Pky - W of Substation | 8.9039 | 141 | 2020-11-07 | 0% | 14.22% | 0% | 0% | 0% | 0% | 2.46% | 0% | 0% | 83.32% | 5.8338 | 16.0906 | 0.048099 | 0.11511 | Continue to Monitor
OKOLONA | Jefferson - 811 N 27th St. - Louisville | OK1272 | Louisville - Outer Loop, Shepherdsville Rd, & Applegate Ln - E of Substation | 18.6203 | 1664 | 2019-04-06 | 9.128% | 0% | 0.2666% | 1.014% | 13.14% | 0% | 6.529% | 66.08% | 0% | 3.837% | 40.7638 | 58.2008 | 0.52843 | 1.0043 | Continue to Monitor
OKOLONA | Jefferson - 811 N 27th St. - Louisville | OK1274 | Louisville - Preston Hwy, Miles Ln, & Cooper Ave - S of Substation | 12.8039 | 1341 | 2019-05-04 | 12.54% | 1.725% | 0% | 0% | 10.99% | 0% | 17.04% | 42.68% | 15.02% | 0% | 40.4853 | 44.9792 | 0.31986 | 0.22303 | Continue to Monitor
OXMOOR | Jefferson - 8004 Shelbyville Rd - Louisville | OX1275 | Louisville - Christian Way & Oxmoor Ln - W of Substation | 0.83349 | 96 | Underground Circuit | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 88.8131 | 1 | 0.4043 | 1 | Continue to Monitor
OXMOOR | Jefferson - 8004 Shelbyville Rd - Louisville | OX1276 | Louisville - No Road - At Substation | 0.10244 | 1 | Underground Circuit | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 51.1933 | 255.9667 | 0.2 | 1 | Continue to Monitor
OXMOOR | Jefferson - 8004 Shelbyville Rd - Louisville | OX1278 | Louisville - Christian Way & Oxmoor Ln - W of Substation | 0.95192 | 5 | Underground Circuit | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 179.1433 | 106.3333 | 0.6 | 1 | Continue to Monitor
OXMOOR | Jefferson - 8004 Shelbyville Rd - Louisville | OX1279 | Louisville - Shelbyville Rd, New La Grange Rd, & Wood Rd - N of Substation | 13.1713 | 1467 | 2020-08-22 | 0.1574% | 0% | 0% | 0% | 38.86% | 0% | 5.286% | 54.16% | 0% | 1.533% | 113.8223 | 156.9906 | 1.1495 | 1.5725 | Trees Trimmed in 2020
PIRTLE | Jefferson - Rear 1506 W Main St - Louisville | PI0002 | Louisville - W Market St, 22nd St, 19th St, & Cedar St - W of Substation | 4.7019 | 525 | 2019-01-12 | 0% | 29.19% | 0% | 0.4709% | 38.28% | 0% | 20.34% | 0% | 0.666% | 11.06% | 98.0333 | 45.7487 | 0.79306 | 1.2483 | Continue to Monitor
PIRTLE | Jefferson - Rear 1506 W Main St - Louisville | PI0004 | Louisville - Market St & 10th St - SE of Substation | 2.269 | 316 | 2018-12-04 | 0% | 47.91% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 52.09% | 44.3957 | 48.6261 | 0.35105 | 0.36957 | Continue to Monitor
PLEASURE RIDGE | Jefferson - 4400 Atlas Power Rd. - Louisville | PL1270 | Louisville - St. Andrews Church Rd & St. Anthonys Church Rd - NE of Substation | 24.312 | 2491 | 2018-10-13 | 0.4799% | 0% | 0% | 0% | 14.1% | 0% | 7.488% | 15.08% | 13.12% | 49.73% | 50.0879 | 50.9551 | 0.94368 | 0.74225 | Continue to Monitor
PLEASURE RIDGE | Jefferson - 4400 Atlas Power Rd. - Louisville | PL1271 | Louisville - Dixie Hwy, Pages Ln, & Maryman Rd - S of Substation | 27.8557 | 2095 | 2018-08-25 | 0.8008% | 0% | 0.1489% | 0% | 25.8% | 0% | 3.162% | 1.966% | 2.965% | 65.15% | 102.3054 | 118.1637 | 1.1536 | 0.3476 | Continue to Monitor
PLEASURE RIDGE | Jefferson - 4400 Atlas Power Rd. - Louisville | PL1273 | Louisville - Atlas Power Rd, Greenwood Rd & St. Pauls Church Rd - N of Substation | 2.3164 | 82 | 2018-10-06 | 0% | 0% | 0% | 0% | 26.45% | 0% | 18.2% | 0% | 0% | 55.35% | 85.2567 | 230.0728 | 0.57329 | 1.5488 | Continue to Monitor
PADDYS RUN | Floyd - 4222 Hwy 111 - New Albany | PR1387 | New Albany - No Road - SE of Substation | 0.30052 | 1 | 2019-01-09 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 51.1367 | 255.6833 | 0.2 | 1 | Continue to Monitor
PADDYS RUN | Floyd - 4222 Hwy 111 - New Albany | PR1390 | New Albany - Algonquin Pky & Gibson Ln - NE of Substation | 2.8557 | 13 | 2019-01-09 | 0% | 0% | 20.32% | 0% | 79.68% | 0% | 0% | 0% | 0% | 0% | 96.492 | 369.3639 | 1.0628 | 4 | Continue to Monitor
PLAINVIEW | Jefferson - 9900 Shelbyville Rd - Louisville | PV1250 | Louisville - Shelbyville Rd, Dorsey Ln, & Ward Ave - NE of Substation | 34.1923 | 2863 | 2020-02-08 | 12.44% | 0% | 5.918% | 0% | 68.55% | 0% | 2.268% | 0% | 0% | 10.82% | 42.76 | 58.3901 | 0.28646 | 0.28346 | Continue to Monitor
SEVENTH | Louisville - 1231 S 7th St - Louisville | SE0001 | Louisville - 7th St, oak St, & 8th St - N of Substation | 1.7802 | 333 | 2019-12-21 | 0% | 0% | 0% | 0% | 1.429% | 0% | 98.57% | 0% | 0% | 0% | 15.9694 | 22.0309 | 0.16332 | 0.087362 | Continue to Monitor
SHIVELY | Jefferson - 3624 Elderwood Way - Louisville | SH1282 | Louisville - Berry Blvd, Powell Ave, Wheeler Ave & Southgate Ave - E of Substation | 10.3603 | 2039 | 2017-08-05 | 10.27% | 0% | 13.5% | 0% | 28.13% | 0% | 1.47% | 32.01% | 8.025% | 6.585% | 59.2705 | 75.723 | 1.1633 | 2.4054 | Tree Trim Scheduled for 2021
SHIVELY | Jefferson - 3624 Elderwood Way - Louisville | SH1284 | Louisville - Manslick Rd - S of Substation | 9.0736 | 1311 | 2017-08-12 | 0% | 7.637% | 0% | 0% | 64.3% | 0% | 6.936% | 0% | 0% | 21.13% | 66.3174 | 62.9745 | 0.90174 | 1.4419 | Continue to Monitor
SHIVELY | Jefferson - 3624 Elderwood Way - Louisville | SH1285 | Louisville - Nobel Pl, Dixie Hwy, & Appleton Ln - NW & SW of Substation | 8.2407 | 1117 | 2017-08-12 | 2.375% | 0% | 0% | 0.1314% | 9.224% | 0% | 21.59% | 18.94% | 6.288% | 41.45% | 55.3085 | 59.9323 | 0.60037 | 0.45091 | Continue to Monitor
SHIVELY | Jefferson - 3624 Elderwood Way - Louisville | SH1456 | Louisville - Dixie Hwy, Ralph Ave, & Fitzgerald Rd - N of Substation of Substation | 3.457 | 22 | 2017-08-05 | 0% | 0% | 0% | 0% | 99.53% | 0% | 0% | 0% | 0% | 0.4728% | 170.867 | 547.9924 | 1.0373 | 0.090909 | Continue to Monitor
SHIVELY | Jefferson - 3624 Elderwood Way - Louisville | SH1458 | Louisville - 7th Street Rd, Arcade Ave, Taylor Blvd, & Berry Blvd - NE of Substation | 5.2571 | 7 | 2017-08-05 | 0% | 0% | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 17.5142 | 0.99949 | 0.48571 | 1 | Continue to Monitor
SHIVELY | Jefferson - 3624 Elderwood Way - Louisville | SH1459 | Louisville - Manslick Rd, Bluegrass Ave, & Taylor Blvd - SE of Substation | 4.45 | 16 | 2017-08-05 | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 95.8326 | 217.4688 | 0.84167 | 0.9375 | Continue to Monitor
SKYLIGHT | Oldham - 8617 W Hwy 42 - Skylight | SK1128 | Skylight - Hwy 42, Hwy 393, & Hwy 524 - NE of Substation | 152.3964 | 1437 | 2018-03-06 | 0.1228% | 0.005952% | 18.15% | 5.779% | 4.903% | 0% | 0.08788% | 46.89% | 15.45% | 8.608% | 456.7719 | 730.3549 | 2.1685 | 3.3779 | Reliability Improvements Scheduled for 2021
SEMINOLE | Jefferson - 4161 Park Blvd. - Louisville | SM1234 | Louisville - Whitney Ave, Taylor Blvd, & Ashland Ave - W of Substation | 13.6613 | 2256 | 2017-09-16 | 20.27% | 0% | 0% | 0% | 8.668% | 0% | 21.16% | 23.55% | 19.31% | 7.043% | 63.2959 | 59.8573 | 0.7678 | 0.98943 | Continue to Monitor
SEMINOLE | Jefferson - 4161 Park Blvd. - Louisville | SM1235 | Louisville - Fairmont Ave, 3rd St, 5th St, & 4th St - NW of Substation | 12.3407 | 2209 | 2017-09-16 | 2.876% | 10.28% | 0% | 0.5646% | 1.601% | 0% | 80.13% | 0% | 2.88% | 1.672% | 59.9326 | 71.032 | 0.76398 | 0.539 | Continue to Monitor
SEMINOLE | Jefferson - 4161 Park Blvd. - Louisville | SM1363 | Louisville - Crittenden Dr - NE of Substation | 1.3754 | 12 | 2017-09-16 | 4.65% | 0% | 0% | 0% | 82.39% | 0% | 0% | 0% | 0% | 12.96% | 117.8334 | 264.0209 | 1.1533 | 3.1667 | Continue to Monitor
SEMINOLE | Jefferson - 4161 Park Blvd. - Louisville | SM1364 | Louisville - Park Blvd, Farmington Ave, & Floyd St - N of Substation | 2.2489 | 48 | 2017-09-16 | 0% | 0% | 0% | 0% | 29.28% | 0% | 67.01% | 0% | 0% | 3.71% | 36.9309 | 119.6769 | 0.43583 | 0.85465 | Continue to Monitor
SEMINOLE | Jefferson - 4161 Park Blvd. - Louisville | SM1366 | Louisville - Crittenden Dr, Woodlawn Ave, Phillips Ln, & Preston Hwy - S & E of Substation | 7.9021 | 35 | 2017-09-16 | 0% | 0% | 0% | 0% | 25.47% | 0% | 0% | 0% | 0% | 74.53% | 115.0563 | 161.25 | 1.934 | 2.0857 | Continue to Monitor
SHAWNEE | Jefferson - Rear of 3908 W Broadway - Louisville | SN0002 | Louisville - Broadway, 37th St, & Lindell Ave - E of Substation | 2.4536 | 519 | 2020-02-29 | 0% | 0% | 28.16% | 0% | 0.04678% | 0% | 65.37% | 6.424% | 0% | 0% | 23.7523 | 25.0319 | 0.74995 | 0.20162 | Continue to Monitor
SHAWNEE | Jefferson - Rear of 3908 W Broadway - Louisville | SN0004 | Louisville - Broadway, 40th, 41st, 42nd, 43rd, & 44th St - W of Substation | 2.727 | 618 | 2020-02-29 | 0% | 0% | 0% | 73.77% | 3.775% | 0% | 6.632% | 2.267% | 13.49% | 0.06514% | 61.5988 | 194.0595 | 0.55297 | 1.5057 | Continue to Monitor
SOUTHERN | Jefferson - 1475 S 3rd Street - Louisville | SO0410 | Louisville - 4th St & Hill St - W of Substation | 1.6467 | 694 | 2020-02-01 | 4.509% | 0% | 0% | 0% | 11.59% | 0% | 7.633% | 0% | 74.21% | 2.063% | 46.2151 | 163.6334 | 0.54373 | 2.0257 | Continue to Monitor
SOUTHERN | Jefferson - 1475 S 3rd Street - Louisville | SO0422 | Louisville - 2nd St & 3rd St - N of Substation | 1.4786 | 776 | 2020-02-01 | 0% | 0% | 0% | 0% | 0% | 0% | 31.5% | 0% | 2.18% | 66.32% | 32.7263 | 36.4261 | 0.34122 | 0.57908 | Continue to Monitor
SOUTHERN | Jefferson - 1475 S 3rd Street - Louisville | SO0451 | Louisville - 3rd St & Lee St - S of Substation | 2.4784 | 538 | 2020-02-01 | 0% | 0% | 0% | 0% | 58.6% | 0% | 0% | 15.63% | 0% | 25.78% | 72.7571 | 79.5829 | 0.56099 | 0.26724 | Continue to Monitor
SOUTHERN | Jefferson - 1475 S 3rd Street - Louisville | SO0453 | Louisville - 3rd St, Oak St, & Brook St - N of Substation | 2.3091 | 626 | 2020-02-01 | 0% | 0% | 55.21% | 0% | 0% | 0% | 0% | 20.19% | 0% | 24.61% | 26.2337 | 53.3658 | 0.16259 | 0.35163 | Continue to Monitor
SOUTH PARK | Jefferson - 1412 Fairdale Rd. - Louisville | SP1114 | Louisville - Farmers Ln, South Park Rd, & Minor Ln - NE & S of Substation | 9.3262 | 526 | 2019-10-12 | 0.4936% | 0% | 1.361% | 0% | 0.107% | 0% | 0.03668% | 0.7456% | 97.26% | 0% | 248.8354 | 683.0191 | 1.3011 | 0.97242 | Continue to Monitor
STEWART | Jefferson - 4701 Stewart Ln. - Louisville | SW1184 | Louisville - Romania Dr, Meyers Ln, & Blanton Ln - SW of Substation | 16.1233 | 1269 | 2018-02-10 | 1.961% | 0% | 0.1115% | 0% | 1.025% | 0% | 23.64% | 7.661% | 48.43% | 17.17% | 125.472 | 113.412 | 1.1484 | 1.3806 | Continue to Monitor
STEWART | Jefferson - 4701 Stewart Ln. - Louisville | SW1186 | Louisville - Gagel Ave, Hazelwood Ave, Bluegrass Ave, & Lonsdale Ave - E of Substation | 13.9664 | 2025 | 2017-12-16 | 2.733% | 0% | 0.01318% | 0% | 4.673% | 0% | 5.982% | 81.72% | 4.067% | 0.8104% | 119.2959 | 146.0672 | 0.8838 | 0.92112 | Reliability Improvements Completed in 2020
STEWART | Jefferson - 4701 Stewart Ln. - Louisville | SW1187 | Louisville - San Jose Ave, Dixie Hwy, Sadie Ln, & Estate Dr - NE of Substation | 14.2698 | 1526 | 2018-02-10 | 3.284% | 8.139% | 1.053% | 0% | 49.93% | 0% | 10.99% | 19.61% | 0% | 6.982% | 56.1788 | 65.5075 | 0.93156 | 0.61082 | Continue to Monitor
STEWART | Jefferson - 4701 Stewart Ln. - Louisville | SW1188 | Louisville - Rockford Ln, Imperial Ter, & Dover Rd - W of Substation | 14.1075 | 1871 | 2018-02-10 | 28.47% | 0.4799% | 0% | 0.389% | 10.78% | 0% | 9.607% | 35.01% | 13.36% | 1.919% | 74.4001 | 94.1907 | 0.65049 | 1.1012 | Continue to Monitor
STEWART | Jefferson - 4701 Stewart Ln. - Louisville | SW1191 | Louisville - Gagel Ave, Manslick Rd, & Parkwood Rd - SE of Substation | 17.4693 | 1352 | 2018-02-03 | 0.4022% | 0% | 0% | 0.114% | 94.98% | 0% | 1.197% | 0.6306% | 0% | 2.68% | 51.7253 | 146.7109 | 0.31242 | 0.58234 | Continue to Monitor
STEWART | Jefferson - 4701 Stewart Ln. - Louisville | SW1451 | Louisville - Gagel Ave, Hazelwood Ave, Manslick Rd, & Brick Kiln Ln - E & SW of Substation | 10.5981 | 38 | 2017-12-02 | 0% | 0% | 0% | 0% | 0% | 0% | 6.675% | 64.69% | 12.99% | 15.65% | 193.565 | 801.8997 | 1.508 | 4.1565 | Tree Trim Scheduled for 2021
SMYRNA | Jefferson - 7000 Manslick Rd. - Louisville | SY1250 | Louisville - Vaughn Mill Rd, Outer Loop & Fegenbush Ln - N of Substation | 28.2984 | 2035 | 2018-07-06 | 3.632% | 1.202% | 0% | 0% | 24.84% | 0% | 15.7% | 4.936% | 0% | 49.69% | 46.0443 | 26.8005 | 0.48312 | 0.6242 | Continue to Monitor
SMYRNA | Jefferson - 7000 Manslick Rd. - Louisville | SY1255 | Louisville - Manslick Rd, Beulah Church Rd, & Fegenbush Ln - NE of Substation | 32.7123 | 2740 | 2018-05-05 | 7.886% | 0% | 3.903% | 0% | 3.987% | 0.7261% | 3.086% | 0% | 0% | 80.41% | 31.3326 | 43.6146 | 0.46724 | 1.3742 | Continue to Monitor
TAYLOR | Jefferson - 4488 Brownsboro Rd. - Louisville | TA1105 | Louisville - Brownsboro Rd & Springcrest Dr - NE of Substation | 25.0136 | 1477 | 2019-11-02 | 0.7084% | 0% | 0% | 0% | 4.493% | 0% | 2.814% | 2.52% | 76.12% | 13.35% | 134.1758 | 139.0826 | 1.172 | 1.027 | Reliability Improvements Completed in 2020
TAYLOR | Jefferson - 4488 Brownsboro Rd. - Louisville | TA1106 | Louisville - Blankenbaker Ln, Riviera Dr, & Woodside Rd - NW of Substation | 40.9066 | 1210 | 2020-04-18 | 8.542% | 0% | 1.229% | 0% | 47.3% | 0% | 0.8749% | 28.17% | 0% | 13.89% | 151.2146 | 70.0204 | 1.4688 | 1.4746 | Trees Trimmed in 2020
TAYLOR | Jefferson - 4488 Brownsboro Rd. - Louisville | TA1130 | Louisville - Hubbards Ln, Shelbyville Rd, & Browns Ln - S of Substation | 14.133 | 1742 | 2018-11-03 | 0.2568% | 0% | 0% | 0% | 4.185% | 0% | 4.4% | 80.77% | 0% | 10.39% | 131.8518 | 152.0281 | 1.6327 | 1.5426 | Reliability Improvements Completed in 2020
TAYLOR | Jefferson - 4488 Brownsboro Rd. - Louisville | TA1138 | Louisville - Brownsboro Rd, Chenoweth Ln, Canoe Ln, & Wampum Rd - W of Substation | 11.8679 | 571 | 2018-03-06 | 0.4571% | 0% | 0.05834% | 0% | 13% | 0% | 0.5282% | 32.57% | 0% | 53.38% | 188.5086 | 265.3349 | 1.1824 | 1.7683 | Continue to Monitor
TAYLOR | Jefferson - 4488 Brownsboro Rd. - Louisville | TA1172 | Louisville - Chenoweth Ln, Cherrywood Rd, & Washington Sq - SW of Substation | 10.7339 | 1117 | 2019-01-26 | 2.948% | 38.61% | 0% | 0% | 15.61% | 0% | 0.723% | 20.37% | 0% | 21.74% | 118.2502 | 144.4173 | 0.83584 | 1.8541 | Continue to Monitor
TAYLOR | Jefferson - 4488 Brownsboro Rd. - Louisville | TA1173 | Louisville - Hubbards Ln, Rudy Ln, Massie Ave, & Westport Rd - S of Substation | 25.7643 | 1970 | 2019-03-16 | 0.3209% | 1.103% | 0% | 0% | 5.638% | 0% | 0.4832% | 66.48% | 0% | 25.98% | 160.8069 | 323.117 | 1.6761 | 3.4569 | Continue to Monitor
TERRY | Jefferson - 8408 Terry Ln. - Louisville | TE1242 | Louisville - Pages Ln & Robbins Rd - E of Substation | 7.9513 | 856 | 2020-09-12 | 8.542% | 0% | 0% | 0% | 8.177% | 0% | 2.168% | 64.41% | 0% | 16.7% | 48.7272 | 64.15 | 0.6061 | 0.86361 | Trees Trimmed in 2020
TERRY | Jefferson - 8408 Terry Ln. - Louisville | TE1243 | Louisville - Terry Rd, Greenwood Rd, & Westbrook Rd - N of Substation | 19.687 | 1775 | 2020-09-05 | 3.055% | 0% | 0% | 0% | 0.7408% | 0% | 0.9459% | 0.6315% | 81.36% | 13.27% | 79.5987 | 108.8195 | 0.77664 | 1.2991 | Continue to Monitor
TERRY | Jefferson - 8408 Terry Ln. - Louisville | TE1244 | Louisville - Terry Rd, Johnsontown Rd, & Dixie Hwy - S of Substation | 19.4832 | 1852 | 2020-09-19 | 0.6957% | 0% | 0% | 0% | 0.6867% | 0% | 20.8% | 0.3399% | 0% | 77.48% | 21.5519 | 23.8743 | 0.37737 | 0.198 | Continue to Monitor
TERRY | Jefferson - 8408 Terry Ln. - Louisville | TE1245 | Louisville - Pages Ln, Poinsettia Dr, Greenwood Rd, & Feyhurst Dr - NE of Substation | 23.7434 | 2344 | 2020-09-12 | 11.86% | 0% | 0% | 0% | 0% | 0% | 25.94% | 1.299% | 27.31% | 33.6% | 25.6084 | 40.7499 | 0.35267 | 0.81495 | Continue to Monitor
TERRY | Jefferson - 8408 Terry Ln. - Louisville | TE1247 | Louisville - Cane Run Rd - W of Substation | 7.6011 | 363 | 2020-09-19 | 0% | 0% | 0% | 0% | 1.73% | 0% | 0% | 0% | 94.93% | 3.343% | 25.9296 | 32.6995 | 0.63946 | 1.0358 | Continue to Monitor
TERRY | Jefferson - 8408 Terry Ln. - Louisville | TE1248 | Louisville - Greenbelt Hwy, Greenwood Rd, & Cane Run Rd - NW of Substation | 10.6628 | 606 | 2020-09-19 | 2.696% | 0% | 0% | 0% | 17.42% | 0% | 0% | 0% | 79.55% | 0.3288% | 98.7496 | 182.2787 | 0.65823 | 0.51897 | Continue to Monitor
Tip Top | Meade - US 60 - Tip Top | TT3314 | Tip Top - Chaffee Ave, Gold Vault Rd, & 5th Ave - SE of Substation | 6.4142 | 1 | 2020-02-15 | 0% | 0% | 0% | 0% | 100% | 0% | 0% | 0% | 0% | 0% | 1649.0133 | 8232.8167 | 0.4 | 1 | Continue to Monitor
VERMONT | Jefferson - Rear 529 Southwestern Pkwy - Louisville | VE0002 | Louisville - River Park Dr, 44th, 43rd, & 42nd St - SE of Substation | 1.2006 | 305 | 2020-03-21 | 0% | 0% | 0% | 0% | 0% | 0% | 28.68% | 20.76% | 50.56% | 0% | 22.8305 | 60.5793 | 0.21309 | 0.3456 | Continue to Monitor
WESTERN | Jefferson - 2807 W Broadway - Louisville | WE0001 | Louisville - 28th St, Chestnut St, 26th St, & Muhammad Ali Blvd - NE of Substation | 5.0958 | 811 | 2019-02-23 | 0% | 6.458% | 0% | 47.89% | 5.27% | 0% | 1.779% | 29.48% | 8.038% | 1.077% | 19.2912 | 40.7535 | 0.17109 | 0.20454 | Continue to Monitor
WESTERN | Jefferson - 2807 W Broadway - Louisville | WE0006 | Louisville - 28th St, Chestnut St, 30th St, & 31st St - NW of Substation | 1.8407 | 223 | 2019-02-23 | 0% | 0% | 0% | 0% | 97.22% | 0% | 0.4311% | 2.349% | 0% | 0% | 105.0853 | 435.9281 | 0.33733 | 0.38397 | Continue to Monitor
WHAS | Jefferson - 1310 Flat Road Rd. - Louisville | WH1116 | Louisville - Flat Rock Rd, Long Run Rd, & Aiken Rd - NW & SE of Substation | 31.3327 | 1153 | 2020-12-19 | 0.5107% | 0% | 0% | 0% | 27.1% | 0% | 15.56% | 0.5592% | 0% | 56.27% | 61.2496 | 176.8078 | 0.53446 | 1.43 | Continue to Monitor
WORTHINGTON | Jefferson - 10300 Ballardsville Rd. - Louisville | WO1177 | Louisville - Ballardsville Rd, Murphy Ln, & Tazwell Dr - E of Substation | 23.2196 | 2088 | 2017-07-01 | 0.05954% | 0% | 0% | 0% | 0.01287% | 0.7555% | 0.6703% | 16.92% | 22.03% | 59.55% | 69.8812 | 116.8658 | 0.66954 | 0.66378 | Continue to Monitor
WORTHINGTON | Jefferson - 10300 Ballardsville Rd. - Louisville | WO1179 | Louisville - Chamberlain Ln - NW of Substation | 26.1047 | 1103 | 2017-07-01 | 0.02115% | 0% | 0% | 0% | 70.1% | 0% | 0.2015% | 29.68% | 0% | 0% | 42.1201 | 161.855 | 0.299 | 1.0231 | Tree Trim Scheduled for 2021
WORTHINGTON | Jefferson - 10300 Ballardsville Rd. - Louisville | WO1182 | Louisville - Brownsboro Rd, Park Plaza Ave, & Ten Broeck Way - W of Substation | 18.5641 | 1011 | 2017-08-18 | 0.6412% | 0% | 0% | 0% | 76.04% | 0% | 0.06603% | 15.06% | 0% | 8.197% | 49.9682 | 54.7247 | 0.61105 | 0.29788 | Continue to Monitor
WORTHINGTON | Jefferson - 10300 Ballardsville Rd. - Louisville | WO1183 | Louisville - Ballardsville Rd, Haunz Ln, & Hitt Ln - NE of Substation | 36.6702 | 1671 | 2017-05-31 | 0.5254% | 0% | 15.3% | 1.797% | 11.95% | 0.2042% | 0% | 44.63% | 19.34% | 6.259% | 195.1068 | 218.6508 | 1.6372 | 1.1455 | Tree Trim Scheduled for 2021
WORTHINGTON | Jefferson - 10300 Ballardsville Rd. - Louisville | WO1184 | Louisville - Brownsboro Rd & Worthington Ln - N of Substation | 33.6324 | 2557 | 2017-08-18 | 0% | 0% | 38.05% | 1.301% | 12.67% | 0% | 24.66% | 0% | 0% | 23.33% | 16.4726 | 61.3482 | 0.14483 | 0.59888 | Continue to Monitor
WATERSIDE | Jefferson - 221 North Third St. - Louisville | WS1322 | Louisville - Main St, 13th St, Market St, 10th St, & Portland Ave - W of Substation | 5.5114 | 52 | 2016-04-07 | 3.601% | 3.034% | 0% | 40.87% | 52.5% | 0% | 0% | 0% | 0% | 0% | 53.2111 | 97.9519 | 1.0335 | 2.434 | Continue to Monitor
WATTERSON | Jefferson - 5239 Bardstown Rd. - Louisville | WT1154 | Louisville - Walt Lee Rd, Fairground Rd, Billtown Rd, & Easum Rd - E of Substation | 20.0487 | 2830 | 2017-08-05 | 0.6143% | 0.1841% | 0% | 0% | 30.46% | 0% | 5.957% | 32.86% | 15.21% | 14.71% | 43.8255 | 76.1191 | 0.56907 | 1.3209 | Tree Trim Scheduled for 2021
WATTERSON | Jefferson - 5239 Bardstown Rd. - Louisville | WT1209 | Louisville - Laverne Dr, Watterson Trl, & Dell Rd - NE of Substation | 9.7899 | 1517 | 2017-07-29 | 0% | 0% | 0% | 0% | 9.732% | 0% | 18.88% | 14.22% | 2.296% | 54.87% | 30.3504 | 28.8358 | 0.23635 | 0.28408 | Continue to Monitor

## LGE Section 6-7
KENTUCKY PUBLIC SERVICE COMMISSION
ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT
SECTION 6: VEGETATION MANAGEMENT PLAN REVIEW
The Companies’ Vegetation Management Plan was submitted December 19, 2007. The Distribution Vegetation Management Program encompasses right of way maintenance for Louisville Gas and Electric Company and Kentucky Utilities Company (referred to as the “Companies”). The program is centralized and managed by a Forestry Manager and eight company Utility Arborists. All are certified arborists by the International Society of Arboriculture.
The Companies’ plan is to maintain a proactive trim cycle while balancing the reactive needs of worst performing circuits. The Companies’ goal is to maintain an average trim cycle of five years or less. The effectiveness of the plan is evaluated by the cycle and system performance as measured by system SAIDI, SAIFI, and CAIDI.
Effectiveness of the program
KU/LG&E Tree Cycle – 4.90 years
LGE Tree SAIDI – 21.13 minutes
LGE Tree SAIFI – 0.115
LGE Tree CAIDI – 183.9 minutes
The hazard tree program, mid cycle, herbicide, and worst performing circuits were completed as planned.
Adjustments made to the tree plan in 2020 included
No changes made to plan.
Changes to be implemented in 2021
No changes made to plan. Continue targeted hazard tree and mid-cycle trim work.
SECTION 7: UTILITY COMMENTS
SAIDI and SAIFI improved in 2020 compared to the previous 5 year average including and excluding major events. 215 Circuits were above their previous 5 year average SAIDI and/or SAIFI in 2020.