## G1 2011 Outage
Work Order Number | Location | W/O Description | Status
5589409 | GN001TGNMGCGENERATORSTATOR | STATOR OUTLET TEMP IS HIGH. BELIEVE THAT THE ALARM IS STUCK IN.:Max | Complete
5591188 | GN001TGNMTCBEARINGSANDPEDESTAL | G1 Thurst Thermocouple Needs to be replaeced:Max | Complete
5692500 | GN001TGNMTCBEARINGSANDPEDESTAL | G-1 TURBINE---NO.1 BEARING METAL TEMP. ALARM:Max | Complete
5818034 | GN001TGNMGCSEALOILSYSTEM | G1 SEAL OIL UNIT SEAL OIL VACUUM PUMP INSTALL NEW PUMP | Complete
5832643 | GN001TGNTGCTURBINEMISCINST | G1 Stator cooling water runback did not operate. Inst thinks problem may be caused by the local:Max | Complete
5866294 | GN001SGUMBCBURNERS | 1D Lower Burner Deck. Atomizing Air valve.:Max | Complete
5870328 | GN001FGDARTABSORBERTOWEREQUIP | 1B BLEED LINE THICKNER ISOLATION VALVE NEEDS:Max | Complete
5871878 | GN001SGUMBCBOILER | G1 BOILER DOORS INSPECTION - REFRACTORY AS NEEDED 2011 | Complete
5871993 | GN001SGUMBCBOILERSECTOINS | PM-OUTAGE-G1 BOILER TUBE SAMPLES-1 SH OUTLET-1 RH INTERMEDIATE, 1 FROM EACH PRIMARY, 1 ECONOMIZER, 1 WATERWALL FOR LIFE ASSESSMENT | Complete
5960426 | GN001SGUCTLBOILERMISCINST | G-1 east superheat spray regulator:Max New positioner not showing feedback on DCS | Complete
5984397 | GN002TGNMTCLUBEOILSYSTEM | G2 WEST Lube oil cololer ON LUBE OIL TANK LEAKING AT FLANGE:Max | Complete
6001680 | GN001BFWFWCDA-STORAGETANK | G1 DA & #4 HEATER DOORS- REPLACE DOORS AND FLANGE FACES TO CORRECT MISALIGNMENT:Max | Complete
6002743 | GN001SGUFDEAIR-GASDUCTS | G1 PRECIP. OUTLET NOZZLE A AND B INSPECTION 2011 | Complete
6002774 | GN001SGUFDEAIR-GASDUCTS | 1A & B SIDE THE GAS IN DAMPERS ABOVE AIR HEATER NEEDS REPAIR WORK DONE ON LINKAGE BARS:Max | Complete
6002780 | GN001SGUFDEAIRPREHEATERS | G1 AIR HEATERS REPLACE SEALS 2011 | Complete
6002782 | GN001SGUFDEAIRPREHEATERS | G1 AIR HEATER REPAIR SECTOR PLATE GAS IN TO PA ON A & B, BOTH HAVE:Max | Complete
6002934 | GN001TGNMTCELECTRO-HYDSYSTEM | Remove old 'high filter differential' alarms from G1 EHC unit. (Indicating lights & reset PB) No:Max | Complete
6003254 | GN001CWSCCSCONDENSER | G1 CONDENSER - CHECK INTEGRITY OF ALL CONDENSER WATERBOX DRAIN VALVES & PIPING. METAL IS THIN | Complete
6005999 | GN001CWSCCSCONDENSER | G1 CIRC WATERBOX REPLACE BOTTOM WEST CONDENSER WATERBOX DOOR (SOUTH SIDE) | Complete
6006122 | GN001BFWFWCHPFEEDWATERHEATERS | G1 #5 HTR. BLEED STEAM BEFORE SEAT DRAIN IS LEAKING THROUGH.:Max | Complete
6012592 | GN001FGDARTABSORBERTOWEREQUIP | G1 Replace pressure gauge and piping on recycle headers:Max | Complete
6013490 | GN001RIDBTGREC-IND.DEVICES | G1 1 ST VALVE NOZZLE INNER SURFACE (TAG# 140TE2010 ):Max | Complete
6013500 | GN001RIDBTGREC-IND.DEVICES | G1 R.H. BOWL INNER SURFACE UPPER READING 953 DEG.:Max | Complete
6013741 | GN001BFWFWCHPFEEDWATERHEATERS | G1 #5 HIGH PRESSURE HEATER FEEDWATER BYPASS VALVE EQUALIZING VALVE HANDWHEEL IS BROKE OFF | Complete
6029330 | GN001SGUPCPPRECIPITATOR | G1 B Side Outlet Nozzle, Screen Wall on East Side Bowed Out, Hung Up in Rappers | Complete
6030016 | GN001SGUFDEAIRPREHEATERS | Replace valves on secondary air line from air heaters to Steam Coils | Complete
6030142 | GN001TGNMGCGENERATORSTATOR | G1 2011 GENERATOR HIT SKID TEST | Complete
6030329 | GN001ASHARSASHSYSTEM | G1 AIR HEATER HOPPERS-REPLACE POKE HOLE PIPE AND CAPS | Complete
6030553 | GN001SGUFPECOALPULVERIZERS | All G1 Mills- Install new seal air isolation valves at top of mills. | Complete
6030557 | GN001SGUFPECOALPULVERIZERS | G1 MILLS- REPLACE ALL DIRECT COOLING WATER ISOLATION VALVES GOING TO OIL COOLERS. | Complete
6032055 | GN001CDSCSCLOWPRESSUREHEATERS | G1 #3 Heater 2011 Retube Installation | Complete
6032056 | GN001CDSCSCLOWPRESSUREHEATERS | G1 #3 Heater 2011 Retube REMOVAL | Complete
6032119 | GN001ASHARSWETBOTTOMHOPPER | Install new SS dog house and guillotine gate for 1B bottom ash hopper | Complete
6032202 | GN001RIDBTGBTGBOARDRECORDERS | Replace G1 Core Monitor during Fall 2011 Outage. INSTALLATION of new Condition Monitor | Complete
6032205 | GN001RIDBTGBTGBOARDRECORDERS | Replace G1 Core Monitor during Fall 2011 Outage. REMOVAL of existing Core Monitor. | Complete
6033277 | GN000CHSCON1DCONVEYOR | G1& G2 D Conveyor Discharge Chutes to E Belts-- Install new chutes. Chutes are Here. | Complete
6034919 | GN001SGUFDEAIRPREHEATERS | G1 AIR HEATERS A & B REPLACE T-BARS | Complete
6034968 | GN001SGURBN-BURNER | G1 BURNER COAL PIPE TIPS- REPLACE 2011 | Complete
6035184 | GN001TGNMTCMAINSTOPVALVES | G1 2011 TURBINE VALVE INSPECTION | Complete
6035236 | GN001CDSCSCLOWPRESSUREHEATERS | G-1 #2 HEATER BLEED STEAM MOV HAS PACKING LEAK... | Complete
6035663 | GN001SGUFDEAIRPREHEATERS | G1 2011 AIR HEATER LUBRICATION | Complete
6036377 | GN001SGUMBCVALVESANDFITTINGS | 2011 G1 BOILER AND HEATER SAFETY VALVE INSPECTIONS | Complete
6036380 | GN001SGUMBCVALVESANDFITTINGS | 2011 G1 RCV INSPECTIONS-#6, #5, #4-1, #4-2, #3, #2 CONTACTOR LABOR ONLY | Complete
6036675 | GN001SGUFPECOALPULVERIZERS | G1 COAL FINENESS SAMPLE TAPS- INSPECT AND REPAIR AS NEEDED. 5F HAS FEEL OFF, TEMP REPAIRS MADE | Complete
6036822 | GN001TGNMGCVOLTAGEREGULATOR | G1 Voltage Regulator Controls (Alterrex) Replacement - Purchase, Installation & Spare Parts (Capital Project) | Complete
6036824 | GN001TGNMGCVOLTAGEREGULATOR | G1 Voltage Regulator Controls (Alterrex) Replacement - Removal | Complete
6036829 | GN001TGNMGCVOLTAGEREGULATOR | G1 Generator Alterrex Bridge Rectifier Replacement - Purchase & Installation (Capital Project) | Complete
6036831 | GN001TGNMGCVOLTAGEREGULATOR | G1 Generator Alterrex Bridge Rectifier Replacement - Removal | Complete
6036856 | GN001SGUMBCBOILER | G1 MAIN STEAM HANGERS MSH-5 AND MSH-6 REPLACEMENT 2011 INSTALL | Complete
6036857 | GN001SGUMBCBOILER | G1 MAIN STEAM HANGERS MSH-5 AND MSH-6 REPLACEMENT 2011 removal | Complete
6036858 | GN001SGUMBCBOILER | G1 HOT REHEAT HANGERS HRH-4, HRH-5 AND HRH -6 REPLACEMENT 2011 INSTALL | Complete
6036859 | GN001SGUMBCBOILER | G1 HOT REHEAT HANGERS HRH-4, HRH-5 AND HRH -6 REPLACEMENT 2011 REMOVAL | Complete
6036860 | GN001SGUMBCBOILER | G1 COLD REHEAT HANGERS CRH-6, REPLACEMENT 2011 INSTALL | Complete
6036861 | GN001SGUMBCBOILER | G1 COLD REHEAT HANGERS CRH-6, REPLACEMENT 2011 REMOVAL | Complete
6036912 | GN001ASHARSFLYASHSYSTEM | G1 2011 REPLACE NUVA FEEDER STONES AND GASKETS | Complete
6037398 | GN001SGUMBCBOILER | G1 FALL OUTAGE 2011 MASTER WORK ORDER | Complete
6037827 | GN001CWSCCSCONDENSER | G1 CIRC. WATERBOX SACRIFICIAL ANODES NEED TO BE REPLACED DURING THE OUTAGE. SOME STUDS REPLACED AS WELL. | Complete
6038054 | GN001SGUFPECOALPULVERIZERS | G-1. B Mill is off and the PA flow damper is closed but showing 60.2 KLB/HR | Complete
6038473 | GN001SGUFDEAIRPREHEATERS | G1 AIR HEATER COLD END BASKET REPLACEMENT 2011 INSTALL | Complete
6038476 | GN001SGUFDEAIRPREHEATERS | G1 AIR HEATER COLD END BASKET REPLACEMENT 2011 REMOVAL | Complete
6038501 | GN001BFWFWCFWPIPETOECONOMIZER | G1 MAIN FW REGULATOR INSPECT 2011 | Complete
6038503 | GN001BFWFWCSTMATTEMPERATRPPG | G1 EAST AND WEST SH SPRAY REBUILD 2011 | Complete
6038599 | GN001BFWFWCFWPIPETOECONOMIZER | G1 START UP FW REG. REBUILD 2011 | Complete
6038670 | GN001SGUFDEPRIMARYAIRFANS | G1 INSPECT A & B PA FAN BEARINGS 2011 | Complete
6038672 | GN001SGUFDEFORCEDDRAFTFANS | G1 INSPECT A & B FD FAN BEARINGS 2011 | Complete
6038677 | GN001SGUFDEINDUCEDDRAFTFANS | G1 INSPECT A & B ID FAN BEARINGS 2011 | Complete
6038684 | GN001SGUMBCVALVESANDFITTINGS | G1 ELECTROMATIC INSPECTION 2011 | Complete
6038709 | GN001ASHARSBOTTOMASHREMOVALSYS | G1 BOTTOM ASH HOPPER INSPECTION 2011 | Complete
6038710 | GN001ASHARSPYRITESYSTEM | G1 TRANSFER TANK INSPECTION 2011 | Complete
6038711 | GN000SWYSPETHICKENERTANKS | 1A, 1B, 2A, 2B,THICKENER INSPECTIONS 2011 | Complete
6038712 | GN001SGUFDESEALAIRFANS | G1 A & B PULVERZIER SEAL AIR FAN INSPECTION 2011 | Complete
6038713 | GN001SGUMBCBURNERS | G1 A & B FLAME SCANNER COOLING AIR FAN INSPECTIONS | Complete
6038723 | GN001SGUMBCBURNERS | G1 INSPECT AIR REGISTERS AND BURNERS 2011 | Complete
6038795 | GN001SGUMBCBOILERSECTOINS | G1 INSPECT THE TUBE SHIELDS IN THE CONVECTION PASS 2011 | Complete
6038796 | GN001SGUMBCBOILERSECTOINS | G1 IR & IK SOOTBLOWER PENTETRATION INSPECTIONS, UT AND REFRAC AS NEEDED 2011 | Complete
6038803 | GN001SGUFDEPRIMARYAIRFANS | 1A & B PA FAN WHEELS INSPECT AND DYE CHECK. 2011 | Complete
6038812 | GN001BFWFWCFEEDWATER | G1 INSPECT FOR FLOW ACCLERATED CORROSION ON CONDENSATE & FEEDWATER PIPING PER B&W PLANT SERVICE BULLITEN #47 | Complete
6038813 | GN001SGUFDEINDUCEDDRAFTFANS | G1 ID FANS INSPECT SHAFT AND CARBON SEALS 2011 | Complete
6038879 | GN000CWSMUSMAKEUPCLARIFIERS | G1 & G2 CLARIFIERS- PERFORM OUTAGE INSPECTION 2011 | Complete
6038880 | GN001CWSCCSCONDENSER | G1 INSPECT STEAM SIDE CONDENSER 2011 | Complete
6038886 | GN001SGUFDEINDUCEDDRAFTFANS | G1 ID FAN DUCTWORK- REPAIR METAL -2011 | Complete
6038887 | GN001SGUFDEFORCEDDRAFTFANS | G1 FD FAN INLET DAMPERS-MECHANICALLY STROKE AND FREE UP DAMPERS | Complete
6038888 | GN001SGUFDEPRIMARYAIRFANS | G1 PA FAN DISCHARGE DAMPERS- INSPECT AND REPAIR LINKAGE | Complete
6038889 | GN001CWSCCSCIRCWATERPUMPS | G1 A & B CIRC WATER PUMPS-INSPECT INTERNAL TURN VANES ON DISCHARGE IN TUNNEL- | Complete
6038909 | GN001FGDARTGASDUCTS | G1 SCRUBBER OUTLET DUCT - REPAIR FLOOR 2011 | Complete
6038911 | GN001FGDARTGASDUCTS | G1 SCRUBBER INLET DUCT INSPECTIONS 2011 | Complete
6038951 | GN001FGDARTABSORBERTOWEREQUIP | G1 RECYCLE HEADER CLEANING 2011 | Complete
6038953 | GN001FGDARTABSORBERTOWEREQUIP | G1 DEMISTER WASH HEADERS AND MIST ELIMINATOR CLEANING 2011 | Complete
6038954 | GN001FGDARTABSORBERTOWEREQUIP | G1 2011 OUTAGE RENTAL EQUIPMENT | Complete
6038955 | GN001FGDARTABSORBERTOWEREQUIP | G1 2011 OUTAGE SCAFFOLDING RENTALS | Complete
6038956 | GN001FGDARTABSORBERTOWEREQUIP | G1 REACTION TANK CLEANING 2011 | Complete
6038957 | GN001FGDARTABSORBERTOWEREQUIP | G1 CLEAN ALL SLURRY LINES 2011 | Complete
6038958 | GN001FGDARTABSORBERTOWEREQUIP | G1 OUTAGE CLEAN UP 3 MEN 2011 | Complete
6038961 | GN001SGUMBCBOILER | G1 OUTAGE OPERATE ELEVATOR-2011 | Complete
6038964 | GN001CWSCCSCIRCWATERPUMPS | G1 A & B CIRC WATER TUNNEL OPEN/CLOSE FOR INSPECTION 2011 | Complete
6038965 | GN001CWSCCSCIRCWATERPUMPS | G1 A & B CIRC WATER PUMP INSPECTIONS 2011 | Complete
6038970 | GN001CWSCCSCOOLINGTOWER | G1 COOLING TOWER CELL VALVES LEAKING THROUGH-2011 A SIDE-2C, 2D, 2E, 1F, 2G, 1H, 2H, B-SIDE 1D, 1G, 2H. | Complete
6038977 | GN001SGUMBCBOILER | G1 BOILER INSPECTION BY B&W 2011 | Complete
6038978 | GN001SGUMBCBOILER | G1 BOILER HANGER INSPECTION 2011 | Complete
6039253 | GN001FGDARTABSORBERTOWEREQUIP | 1B RECYCLE PUMP. THE DRAIN VALVE WILL NOT OPEN. | Complete
6039255 | GN001FGDARTABSORBERTOWEREQUIP | 1A RECYCLE PUMP.THE DRAIN VALVE WILL NOT OPEN. | Complete
6039343 | GN001TGNMTCMAINSTOPVALVES | G1 2011 TURBINE VALVE INSPECTION-CMS | Complete
6040227 | GN001SGUFDESEALAIRFANS | G1 PENTHOUSE SEAL AIR FAN INSPECTION 2011 | Complete
6040228 | GN001SGUMBCBOILER | G1 2011 TITAN SUPV, 2 CLERKS, 2 TOOL ROOM, 3 LABORERS | Complete
6040557 | GN001SGUFDEAIRPREHEATERS | G-1 "A" SIDE AIR HEATER HAS A GAS LEAK ON THE UPPER EAST SIDE OF AIR HEATER. | Complete
6040858 | GN001SGUFDESTEAMCOILAIRHEATER | G1 STEAM COIL DRAIN TANK REPLACEMENT INSTALLATION 2011 | Complete
6040861 | GN001SGUFDESTEAMCOILAIRHEATER | G1 STEAM COIL DRAIN TANK REPLACEMENT REMOVAL 2011 | Complete
6040912 | GN001ENVCEMAIREMISSIONS | G1 PM, INSPECT & CALIBRATE CEM EQUIPMENT | Complete
6040941 | GN001BFWFWCFEEDPUMPRECIRC | G1 INSPECT & STROKE A, B & C B.F.P. CONTROL VALVES | Complete
6040945 | GN001PCSBC-BOILERCONTROLS | G1 PROVIDE COVERAGE FOR UNIT START UP | Complete
6040954 | GN001SGUFDEINDUCEDDRAFTFANS | G1 INSPECT & CLEAN A & B ID FAN SUCTION TAPS | Complete
6040956 | GN001SGUMBCBOILERDRUM | G1 INSPECT THE DRUM CAMERA AND MONITOR | Complete
6040958 | GN001ENVCEMAIREMISSIONS | G1 INSPECT & CALIBRATE THE OPACITY MONITORS | Complete
6040963 | GN001PCSBC-BOILERCONTROLS | G1 INSPECT DCS CONTROL CABINETS | Complete
6040964 | GN001SGUCTLBOILERMISCINST | G1 INSPECT & CALIBRATE BOILER TRIPS | Complete
6040968 | GN001SGUPCPPRECIPITATOR | G1 PRECIP. CLEAN AND INSPECT SUPPORT BUSHINGS | Complete
6040977 | GN001SGUPCPPRECIPITATOR | G1 RUN AND CHECK RAPPER LIFT | Complete
6040979 | GN001SGUPCPPRECIPITATOR | G1 CLEAN AND INSPECT AVC CONTROLS | Complete
6040980 | GN001SGUFDEPRIMARYAIRFANS | G1 P.A. FANS CHECK BEARING OIL HEATERS AND THERMOSTATS | Complete
6040981 | GN001SGUFDEFORCEDDRAFTFANS | G1 F.D. FANS / CHECK BEARING OIL HEATERS AND THERMOSTATS | Complete
6040995 | GN001SGUFDEINDUCEDDRAFTFANS | G1 A&B ID FANS - CHANGE BEARING OIL. | Complete
6040999 | GN001EDTMCCMOTORCONT.CTR. | G1 CHECK AND CLEAN MCC'S | Complete
6041001 | GN001SGUFDEPRIMARYAIRFANS | G1 A&B PA FANS - CHANGE BEARING OIL | Complete
6041003 | GN001EDTTSG480VBUS | G1 CLEAN & INSPECT 480V SUBS. | Complete
6041006 | GN001SGUMBCSOOTBLOWERS | G1 CLEAN AND INSPECT SOOT BLOWERS | Complete
6041011 | GN001SGUMBCSOOTBLOWERS | G1 INSPECT SOOTBLOWING CONTROLS | Complete
6041015 | GN001CWSCCSCOOLINGTOWER | G1 INSPECT COOLING TOWER FAN GEAR BOX HEATERS | Complete
6041021 | GN001CWSCCSCIRCWATERPUMPS | G1 INSPECT LUBE SYSTEM ON CIRC. WATER PUMPS | Complete
6041022 | GN001TGNTGCTRBNSUPERVISORYINST | G-1 INSPECT TURBINE AND GENERATOR VIBRATION PROBES | Complete
6041023 | GN001TGNTGCTURBINEMISCINST | G-1 CHECK TURBINE AND GENERATOR CALIBRATIONS | Complete
6041025 | GN001TGNMTCMAINSTOPVALVES | G-1 INSPECT TURBINE CONTROLS AND STROKE VALAVES | Complete
6041026 | GN001CWSCCSCONDENSER | G1 CHANGE BEARING OIL IN BOTH 1A & 1B VACUM PUMP MOTORS | Complete
6041095 | GN001TGNMGCHYDROGENCOOLINGSYS | G1 HYDROGEN COOLERS OPEN CLOSE FOR CLEANING 2011 | Complete
6041098 | GN001TGNMTCLUBEOILSYSTEM | G1 TURBINE LUBE OIL COOLER OPEN CLOSE FOR CLEANING 2011 | Complete
6041100 | GN001TGNMTCELECTRO-HYDSYSTEM | G1 EH UNIT OUTAGE PM-CHANGE ALL FILTERS -DISCHARGE AND FULLER EARTH AND DRYER DESSICIANT - Change EHC Fluid | Complete
6041106 | GN001CWSCCSCOOLINGTOWER | G-1 INSPECT COOLING TOWER OIL PRESSURE | Complete
6041107 | GN001CWSCCSCOOLINGTOWER | G-1 INSPECT COOLING TOWER OIL PRESSURE | Cancelled
6041117 | GN001SGUFDEAIRPREHEATERS | G-1 CLEAN & INSPECT AIR HEATER PRESSURE | Complete
6041118 | GN001SGUFDESTEAMCOILAIRHEATER | G-1 STROKE STEAM COIL CONTROL VALVE & CONTROLLER | Complete
6041119 | GN001CDSCSCCONTRLACTUATOR | G-1 INSPECT CONDENSER LEVEL CONTROLLER & VALVE | Complete
6041120 | GN001SGUMBCBOILERSECTOINS | G-1 STROKE EAST & WEST REHEAT & SUPER HEAT | Complete
6041121 | GN001TGNMTCLUBEOILSYSTEM | G1 E BOP TEST. | Complete
6041122 | GN001SGUMBCBURNERS | G-1 INSPECT IGNITOR RODS AND TRANSFORMERS | Complete
6041123 | GN001SGUPCPPRECIPITATOR | G1 PRECIP KEY INTERLOCK SYSTEM, UNLOCK & LOCK | Complete
6041124 | GN001EDTDCDDCDIST.SYS. | G1 LOAD TEST STATION BATTERIES | Complete
6041125 | GN001SGUMBCBOILER | G-1 INSPECT AND CLEAN BOILER TAPS | Complete
6041126 | GN001IB-BICCALIBRATION | G-1 INSTRUMENT CALS ALL UNIT. | Complete
6041161 | GN001TGNMGCSEALOILSYSTEM | G1 SEAL OIL UNIT CHANGE FILTERS 2011 | Complete
6041167 | GN001SGUFDEPRIMARYAIRFANS | G1 MILL HOT /COLD AIR DAMPERS -INSPECT REPLACE BEARINGS AS NEEDED. | Complete
6042510 | GN001SGUPCPPRECIPITATOR | G1 Precip. Repair Field | Complete
6042983 | GN001SGUPCPPRECIPITATOR | G1 A PRECIP INLET DUCT-REPLACE PERFORATED PLATES | Complete
6043716 | GN001RIDBTGBTGBOARDMETERS | Green Unit 1 Gross & Net Watthour Meter Replacements | Complete
6043718 | GN001RIDBTGBTGBOARDMETERS | Green Unit 1 Gross & Net Watthour Meter Replacements - REMOVAL | Complete
6043721 | GN001SGUMBCBOILERTEMPPROBES | G1 Install New O2 Probes | Complete
6043857 | GN001TGNMGCGENERATOREXCITER | G1 CLEAN EXCITER AND REPLACE GROUND STRAPS | Complete
6043859 | GN001CWSCCSCIRCWATERPUMPS | G1 CHANGE OIL IN 1A & 1B CIRC. WATER PUMP MOTORS | Complete
6044131 | GN001CWSCCSCIRCWATERPUMPS | G1 SERVICE WATER STRAINER BLOWDOWN VALVE-REPLACE | Complete
6044193 | GN001CWSCCSCOOLINGTOWER | G1 COOLING TOWER WOOD STRUCTURE INSPECTION AND REPAIR 2011 | Complete
6044249 | GN001EDTTSG4160VSWITCHGEAR | G1 Inspect 4160 & 480 Volt Breakers | Complete
6044252 | GN001SGUPCPPRECIPITATOR | G1 PRECIPITATOR WASH | Complete
6044256 | GN001TGNMGCVOLTAGEREGULATOR | G1 SERC/NERC Gen. PT's, CT's Record Ratio, Inspect | Complete
6044257 | GN001SGUPCPPRECIPITATOR | G1 Precip. Replace Support Bushings | Complete
6044258 | GN001FGDFG-FGDS(SCRUBBER) | G1 Underflow Area Replace Conduit | Complete
6044259 | GN001TGNMGCVOLTAGEREGULATOR | G1 SERC/NERC Voltage Regulator Inspection/Calibration | Complete
6044267 | GN001SGUMBCBOILER | G1 BOILER DRAIN LINE INSPECTION 2011- INSPECT PER LIST FOR PIPE THICKNESS AND INTEGRITY | Complete
6044329 | GN001SGUMBCSOOTBLOWERS | G1 IR SYSTEM ROOT VALVE HAS A PACKING LEAK. | Complete
6044387 | GN001SGUFPESTOCKCOALFEEDERS | 1B COAL FEEDER TRANSISTION CHUTE - REPLACE | Complete
6044389 | GN001SGUFPESTOCKCOALFEEDERS | 1D COAL FEEDER TRANSISTION CHUTE - REPLACE | Complete
6044395 | GN001SGUFDEFORCEDDRAFTFANS | G1 Recond. A Cir. Water, A P.A., A&B F.D. Motors | Complete
6044497 | GN001TGNMTCTURBINE | G1 TURBINE FRONT STANDARD- OPEN/CLOSE FOR OTHER WOTK INSIDE | Complete
6044557 | GN001OHCTUCTURBINECRANE | G1 Overhead Turbine Crane Inspection and Load Test | Complete
6044806 | GN001EDTTSG4160VSWITCHGEAR | G1 Thermography Inspection | Complete
6044913 | GN001SGUFDEAIRPREHEATERS | G1 B AIR HEATER SUPPORT BEARING INSPECTION 2011 | Complete
6045393 | GN001ASHARSCLINKERGRINDERS | G1 BOTTOM ASH GRINDERS INSPECTION AND REPAIR 2011 | Complete
6045399 | GN001SGUMBCBOILERSECTOINS | G1 INSPECT THE KNEE SLOPE TUBE SHIELDS | Complete
6045503 | GN001SGUFDEAIR-GASDUCTS | G1 ECONOMIZER GAS OUT DUCT INSPECT AND REPAIR JOINTS AS NEEDED 2011 | Complete
6045639 | GN000EDTTBDSTART-UPTRANS. | Green Startup Transformer doble testing by Transmissions | Complete
6045647 | GN001SGURBN-EASTDUCT | G-1 Stroke and calibrate jordan drives on OFA | Complete
6045674 | GN000CWSMUSMAKEUPCLARIFIERS | 2011 G2 CLARIFER RECOATING | Complete
6046656 | GN001CWSCCSCOOLINGTOWER | G1 - Cooling Tower Decks & Support Replacement -Removal | Complete
6046660 | GN001CWSCCSCOOLINGTOWER | G1 - Cooling Tower Decks & Support Replacement -Installation | Complete
6047775 | GN001SGUMBCBOILERSECTOINS | G1 WATER WALL MAPPING 2011 | Complete
6048810 | GN001SGUFDEAIRPREHEATERS | B air heater/ p.a. duct out access door gasket leaking (by guide bearing) | Complete
6048866 | GN001TGNMGCHYDROGENCOOLINGSYS | top hydrogen add valve leaking | Complete
6048884 | GN001EDTTSG480VBUS | Green Station Emergency Diesel Generator - Purchase & Installation (Capital Project) | Complete
6049278 | GN001FGDSTKSTACK | G-1 stack drain plugged | Complete
6049376 | GN001BFWFWCBOILERFEEDPUMPS | 1A BOILER FEED PUMP R.H. SPRAYS CHECK VALVE IS LEAKING THROUGH . | Complete
6050025 | GN001TGNMTCHIGHPRESSCYLINDER | 2011 G1 Turbine HP Shell Horz. Joint leak repair | Complete
6050089 | GN001SGUMBCBOILER | G1 Fall Outage 2011 Machine Shop Work Order | Complete
6050141 | GN001FGDARTTKNRRETURNWATER | INSPECT PIPING FROM BOTH THICKENERS TO THICKENER RETURN TANK | Complete
6050566 | GN001CWSCCSCOOLINGTOWER | G1 Cooling Tower Cleaning 2011 | Complete
6050888 | GN001SGUFDEFORCEDDRAFTFANS | G1 A FD Fan Housing -repair holes | Complete
6051249 | GN001SGUMBCBLOWDOWNTANK | G1 Blowdown Tank Leaks - repair as needed | Complete

## G1 2010 Outage
Work Order Number | Location | Description | Failure Remarks
5831319 | GN001BFWFWCFEEDWATERPIPETOECONOMIZER | DISCHARGE LINE CHECK VALVE LEAKS THROUGH ON 1B BOILER FEED PUMP | T&W Valve repaired, Welded up seat, remachined ¦face of seat and welded up and remachined face of valve disc. INstalled new springs and pressure seal gaskets
5845495 | GN001SGUMBCMOV2344 | TURBINE DRAIN MOV-3244 ISOL VALVE LEAKING THROUGH. | THIS IS A NEW VALVE i BELIEVE IT WAS NOT CLOSED
5845496 | GN001SGUMBCVALVESANDFITTINGS | TURBINE DRAIN MOV-1442 AND 1444 ISOL VALVE LEAKING THROUGH. | REPLACED BOTH ISOLATION VALVES TO THESE MOV'S
5867231 | GN001SGUFPECOALPULVERIZERS | G1A MILL MAINTANCE DAMPER IS LEAKING THROUGH WHEN DAMPER IS CLOSED . | Installedd new seal around damper
5978409 | GN001SGUMBCBOILERSECTOINS | G1 A AND B ECONOMIZER OUTLET DUCTS LAGGING REPAIR | general insulation replaced insulation and lagging ¦Titan welded standoffs fcor lagging
5981673 | GN001SGUMBCVALVESANDFITTINGS | 2ND FROM NORTH COLD REHEAT STEAM LINE: ONE OF THE SAFETIES IS | replaced disc and lap seats
5986394 | GN001SGUFDEAIRPREHEATERS | A & B UPPER GUIDE BEARINGS NEED TO BE REPACKED | changed packing on A & B guide ¦bearings at post shaft and torgue arms. Also changed oil and filters in A & B upper guide and lower support bearings
5988546 | GN001SGUFDEPRIMARYAIRFANS | 1A PA FAN INLET SCREEN ON EAST SIDE INLET DUCT HAS BROKEN LOOSE | pulled screen back up and installed new anchors
5988364 | GN001SGUMBCVALVESANDFITTINGS | G1 SEC. S.H. INLET HEADER DRAIN MANUAL ISOL. VALVE IS LEAKING THROUGH . | WELDED IN NEW VALVE USED 9018-B3 RODS
5988786 | GN001SGUMBCBOILERDRUM | G-1 CBD ROOT VALVE TO THE BLOW DOWN TAKE WILL NOT SEAT COMPLETELY | WELDED IN NEW VALVE USED 9018-B3 WELDING RODS
5988802 | GN001SGUMBCBOILERDRUM | DRUM PRESSURE TRANSMITTER ROOT VALVE REPLACE-HAS BEEN PUMPED BY COLT | INSTALLED NEW VALVE WELDED IN WITH 9018-B3 RODS
5989654 | GN001SGUFDEAIRPREHEATERS | PM-OUTAGE-G1 INSPECT A & B AIR HEATER SEALS | 1A & B air heater, replaced ¦cold end radial seals, adjusted hot end radial seals, adjusted axial seals, replaced gas in to PA sector plate circ seal, repaired many holes on gas in at corners and seal plate for sector plate. Welded seams at lower T Bar o
5989727 | GN001SGUFDEPRIMARYAIRFANS | PM-OUTAGE-G1 INSPECT A & B PA FAN BEARINGS | changd oil only
5989728 | GN001SGUFDEFORCEDDRAFTFANS | PM-OUTAGE- G1 INSPECT A & B FD FAN BEARINGS | CHAnged oil only
5989729 | GN001SGUFDEAIR-GASDUCTS | PM-OUTAGE- G1 PRECIP OUTLET NOZZLE BLOCK INSPECTION | Titan-- ¦Welded corten plate over many holes found above inlets to A and B ID fans. Also repaired holes above inspection door on B side. I am going to write a work order for spring outage 2011.
5989730 | GN001SGUFDEAIRPREHEATERS | PM-OUTAGE G1 AIR HEATER SOOTBLOWER INSPECTIONS | A & B sootblower lances in good condition, ¦alignment good, blow holes at spec, changed oil in both gearboxes, replaced bad rollers on wallbox, did not repack lances.
5989738 | GN001SGUFDEINDUCEDDRAFTFANS | PM-OUTAGE-G1 INSPECT REPAIR METAL IN I.D. FAN INLET & OUTLET | Cut out and iserted corten metal in various holes ¦found in A and B ID Fan Inlet and outlets. Fans were in good shape overall.
5989749 | GN001ASHARSFLYASHSYSTEM | PM- OUTAGE G1 INSPECT THE NUVA FEEDERS-WASH BAKE STONES | REPLACED ALL STONES AFTER OUTAGE
5989778 | GN001TGNMTCSTEAMCHEST | STEAM SEAL REGULATOR FEED VALVE 2318 IS SHOWING A DOUBLE LIGHT ON THE CONTROL ROOM DCS. | Replaced MOV operator and freed up valve
5989782 | GN001SGUFDEAIRPREHEATERS | PM-G1 OUTAGE-AIR HEATER WASH RAILS- INSTALL-REMOVE | installed wash rails, opened duct doors, removed ¦blanks in air heater outlet ducts. removed rails and installed in reverse.
5989800 | GN001SGUMBCBOILER | PM-OUTAGE-G1 PROVIDE COVERAGE FOR THE UNIT START UP | PROVIDED COVERAGE FOR OUTAGE STARTUP
5989802 | GN001SGUFDEAIR-GASDUCTS | PM-OUTAGE-G1 FREE UP , LUBE, & STROKE DAMPERS | repaired dampers as needed
5989803 | GN001SGUFDEINDUCEDDRAFTFANS | PM-OUTAGE-G1 INSPECT A&B ID FAN SHAFT AND SHAFT SEALS | Installed 1 new seal on B fan east shaft ¦Installed 1 new seal on A Fan East
5989814 | GN001SGUMBCBURNERS | PM-OUTAGE-G1 FREE UP STROKE THE AIR REGISTERS & SPIN VANES | freed up all register vanes and turn vanes, ¦repaired many linkages. welded frames on register housings, repaired many quadrants.
5989815 | GN001SGUMBCBOILERDRUM | PM-OUTAGE G1 18 MONTH DRUM INSPECTION FOR BOILER PERMIT RENE | Doug Schwartz completed Inspection, ¦Weld repairs completed to welds on east and west end drum gauge internal covers.
5989911 | GN001SGUMBCBOILERSECTOINS | G1 WEST ECON. OUTLET HDR VENT ROOT & ISOLATION VALVE ARE LEAKING THRU | REPLACED 2 VALVES INSPECTED PIPING TO THE HEADER ¦REPLACED WHAT WAS BAD
5989912 | GN001SGUMBCBOILERSECTOINS | G1 WEST PRIMARY SH OUTLET HEADER VENT LINE ISOLATION VALVE STEM TWISTED OFF. | REPLACED VALVE
5989969 | GN001SGUMBCVALVESANDFITTINGS | G 1 AUX. STEAM MOV 890 HAS BONNET LEAK NEW GASKET AND PRESSURE SEAL RING IN MIDDLE CRIB | DISASSEMBLED VALVE FOUND THE TAPER SEAL AREA HAD 2 ¦CUTS IN IT. MACHINE SHOP REPAIRED THIS PART. BODY HAS SOME WEAR IN THIS AREA CLEANED THE BEST WE COULD. THE GATE HAS SOME CUTS IN IT BUT DIDN'T HAVE TIME TO RESEAT. VALVE NEED TO BE REPLACED OR OR HAVE E
5989974 | GN001SGUMBCSOOTBLOWERS | G1 AH SOOTBLOWING CROSSTIE VALVE LEAKS THROUGH | WELDED IN NEW VALVE WITH 9018-B3 WELDING RODS ¦BAUGHN AND KOLODEY
5992832 | GN001SGUMBCBOILERDRUM | SECOND ISOLATION VALVE FROM DRUM FOR THE EAST SIDE DRUM LEVEL MONITOR HAS A PACKING LEAK. | Repacked.
5992833 | GN001SGUFDEAIRPREHEATERS | FLEXIBLE CONDUIT GOING TO THE SOLENOID FOR THE AIR DRIVE FOR "A" AIR HEATER | Made Temp. repairs until outage. 1/25/10. replaced ¦seal tight and fittings
5995860 | GN001SGUPCPPRECIPITATOR | PM-OUTAGE-G1 CLEAN & INSPECT PRECIP. HEATERS & THERMOSTATS | replaced bad heaters and wiring
5995862 | GN001SGUPCPPRECIPITATOR | PM-OUTAGE-G1 OPENING / CLOSING PRECIP. | opened and closed precips
5995863 | GN001SGUPCPPRECIPITATOR | PM-OUTAGE-G1 PRECIP. KEY INTERLOCK SYSTEM, UNLOCK - LOCK | unlocked and locked precips
5995878 | GN001BFWFWCFEEDWATERPIPETOECONOMIZER | PM-OUTAGE-G1 STROKE & INSPECT FEEDWATER AND STARTUP REGULATOR | added feedback module and stroked
5995453 | GN000ASHASPPUMPSSLUICE | PM-OUTAGE-G1 CHANGE OIL IN A,B&C ASH SLUICE PUMP MOTORS | changed oil in ash sluice pumps, seal water pumps, ¦service water pumps,and river water make-up pumps
5995454 | GN001CDSCSCCONDENSATE | PM-OUTAGE-G1 A&B CONDENSATE PUMP MOTOR CHANGE OIL | changed oil and claened sight glass
5995455 | GN001SGUFDEFORCEDDRAFTFANS | PM-OUTAGE-G1 A&B FD FAN BEARING OIL HEATERS / THERMOSTATS | changed oil and cleaned sight glass
5995457 | GN001SGUFDEFORCEDDRAFTFANS | PM-OUTAGE-G1 A & B FD FAN MOTOR CHANGE OIL | cahnged oil and repalced sight glass
5995459 | GN001SGUFDEINDUCEDDRAFTFANS | PM-OUTAGE-G1 A & B ID FAN MOTOR BEARING CHANGE OIL | changed oil and cleaned sight glasses
5995462 | GN001SGUFDEINDUCEDDRAFTFANS | PM-OUTAGE-G1 ID FAN BEARING OIL HEATER / THERMOSTATS | changed oil and cleaned sight glasses
5995464 | GN001SGUFDEPRIMARYAIRFANS | PM-OUTAGE-G1 PA FAN BEARING OIL HEATER / THERMOSTATS | hibbs reapaired
5995465 | GN001SGUFDEPRIMARYAIRFANS | PM-OUTAGE-G1 A & B PA FAN BEARINGS CHANGE OIL | changed oil and cleaned sight glasses
5995466 | GN001SGUFPECOALPULVERIZERS | PM-OUTAGE-G1 A,B,C & D MILL MOTORS CHANGE OIL | changed oil and cleaned sight glasses
5995468 | GN001SGUMBCBOILER | PM-OUTAGE-G1 ASSIST CONSTRUCTION | assist construction
5995469 | GN001SGUPCPPRECIPITATOR | PM-OUTAGE-G1 PRECIPITATOR INSPECT & CLEAN CONTROLS | cleaned and vacuumed control cabinets and ¦checked connections
5995492 | GN001SGUPCPPRECIPITATOR | PM-OUTAGE-G1 PRICIPITATOR INSPECT & CLEAN BUSHINGS & SUPPORT | cleaned and inspected. changed bad bushings
5994698 | GN001SGUMBCBOILER | G 1 BOILER PORT MOUNTING PLATE HAS COME LOOSE FROM THE BOILER | FOUND PIPE BETWEEN PORT AND BOILER WAS BURN UP ¦REPLACED PIPE. ALSO MADE THE SAME REPAIR ON PORT JUST ABOVE THIS ONE.
5995346 | GN001SGUMBCBOILER | TITAN SUPT, TOOL ROOM , CLERK AND 2 LABORERS | TITAN SUPT, TOOL ROOM , CLERK AND 2 LABORERS
5994405 | GN001CDSCSCLOWPRESSUREHEATERS | #3 HEATER CONDENSATE OUTLET VALVE LEAKING THROUGH | Rebuild valve (T & W Valve)
5994407 | GN001SGUMBCVALVESANDFITTINGS | #3 HEATER BLEED STEAM MOV 162 LEAKING THROUGH | Rebuilt valve (T & W Valve)
5995881 | GN001SGUMBCVALVESANDFITTINGS | PM-OUTAGE-G1 STROKE EAST & WEST REHEAT & SUPERHEAT REGULATOR | Stroked valves and actuators.
5995882 | GN001SGUMBCBOILER | PM-OUTAGE-G1 STROKE & INSPECT D.A. LEVEL CONTROL & VALVE | stroked da vlv
5995884 | GN001CDSCSCHOTWELL | PM-OUTAGE-G1 INSPECT CONDENSER LEVEL CONTROLLER & VALVE | stroked and inspected for leaks
5995887 | GN001RIDBTGBTGBOARDGAUGES | PM-OUTAGE-G1 INSTRUMENT CALIBRATIONS | performed calibrations
5995891 | GN001SGUCTLBOILERMISCELLANEOUSINSTRUMENTS | PM-OUTAGE-G1 CLEAN SECONDARY AIR TAPS | blue taps
5995895 | GN001SGUFDEFORCEDDRAFTFANS | PM-OUTAGE-G1 STROKE & INSPECT A & B FD FAN INLET & OUTLET | A&B FD FAN INLET LOOKS GOOD
5995896 | GN001SGUFDEINDUCEDDRAFTFANS | PM-OUTAGE-G1 STROKE & INSPECT A & B ID FAN INLET & OUTLET | done
5995898 | GN001SGUFDEPRIMARYAIRFANS | PM-OUTAGE-G1 STROKE & INSPECT A & B PA FAN INLET & OUTLET | strokked dmprs
5995901 | GN001SGUFDESEALAIRFANS | PM-OUTAGE-G1 STROKE & INSPECT A,B,C & D MILL DAMPERS | complete
5995902 | GN001SGUFDESTEAMCOILAIRHEATER | PM-OUTAGE-G1 STROKE STEAM COIL CONTROL VALVE & CONTROLLER | steam stroked vlv coil
5995905 | GN001SGUFPECOALPULVERIZERS | PM-OUTAGE-G1 INSPECT & CLEAN A,B,C & D MILL TAPS & T/C | inps/clnd taps
5995911 | GN001SGUCTLBOILERMISCELLANEOUSINSTRUMENTS | PM-OUTAGE-G1 PROVIDE COVERAGE FOR UNIT START UP | coverd
5995912 | GN001SGUMBCBOILER | PM-OUTAGE-G1 INSPECT & CLEAN BOILER TAPS | cleaned taps and blew back sensing lines
5995914 | GN001SGUMBCBOILERDRUM | PM-OUTAGE-G1 INSPECT DRUM CAMERA AND MONITOR | repl bulbs alined tuned monitor
5995915 | GN001SGUMBCBURNERS | PM-OUTAGE-G1 CLEAN & INSPECT SCANNER & INGNITOR PACKAGES | cleand scanners tested-repaired ign.
5995916 | GN001SGUMBCBURNERS | PM-OUTAGE-G1 INSPECT A,B,C & D SECONDARY AIR DAMPERS | per demand-ok
5995918 | GN001SGUMBCBLOWDOWNTANK | PM- OUTAGE-G1 INSPECT AND CALIBRATE THE ELECTROMATIC RELIEF | inspectamatic'd vlv
5997622 | GN001SGUFDEPRIMARYAIRFANS | 1A MILL HOT AIR AND COLD DAMPERS NEEDS NEW BEARINGS AND PACKING | REPACED BEARINGS, REPACKED SEAL BOX
5996202 | GN001TGNTGCMISCELLANEOUSTURBINEINSTRUMENTS | PM-OUTAGE-G1 COLD REHEAT DRIP POT HIGH-HIGH HAS A STEAM LEAK IN LEVEL SWITCH ASSEMBLY
5996203 | GN001SGUCTLBOILERMISCELLANEOUSINSTRUMENTS | PM-OUTAGE-G1 INSTALL SOE
5997669 | GN001SGUFDEPRIMARYAIRFANS | 1 B PA FAN FLOATING FAN BEARING IS LEAKING OIL thermocouple
5997685 | GN001BFWFWCFEEDWATERPIPETOECONOMIZER | G1 STARTUP FW REGULATOR INSTALL NEW POSITIONER PURCHASED ON WO 5918531 | Installed a feedback signal stroked and tested ¦wired in permanent.
5996703 | GN001SGUMBCSOOTBLOWERS | IK & IR SOOT BLOWING HEADER ROOT VALVE REPACK | Repacked valves.
5996709 | GN001SGUMBCBOILERDRUM | G1 EAST AND WEST SIDE DRUM VENT ISO.VLV. PACKING LEAKING BAD WHEN VALVE IS CLOSED | REPLACED BOTH THE EAST AND WEST DRUM ISOLATION ¦VALVES
5996710 | GN001SGUMBCBOILERDRUM | G1 EAST SIDE DRUM VENT MOV 3602-2 IS LEAKING THRU | replaced valve
5996711 | GN001SGUMBCVALVESANDFITTINGS | COLD REHEAT STUB VENT ROOT VALVE LEAKING BY A.H. | DUE TO TO MUCH ACTIVITY IN THIS AREA DID NOT GET ¦TO THIS VALVE TILL LATE IN THE OUTAGE. RE ABLE TO ADJUST A LITTLE BUT THIS VALVE NEEDS TO BE REPLACED DURING NEXT OUTAGE SPRINS OUTAGE. WILL WRITE A WORK ORDER FOR THIS.
5996716 | GN001SGUMBCVALVESANDFITTINGS | G1 R.H. OUTLET DRAIN ISO.VLV. ON 12TH FLOOR LEAKING THRU. | REPLACED VALVE
5997878 | GN001CDSCSCLOWPRESSUREHEATERS | Heater number 3 has internal problem with high level alarm, | Removed old float assembly, full of water. ¦Replaced with new assembly.
6000703 | GN001SGUMBCMOV2344 | MOV DRAIN VLV.BEFORE TURBINE STOP 2 (north) LEAKING THROUGH | DUPLICATE WORK ORDER SAME AS 5845495
6000706 | GN001SGUFDEAIRPREHEATERS | G1 AIR HEATER DRIVE INSTALL ALARMS FOR ROTOR STOPPAGE | pulled cable wired and made changes in dcs
6000272 | GN001BFWFWCDEAREATORSTORAGETANK | G1 DA AND #4 HEATER INSTALL NEW DOOR GASKETS | USED DIFFERENT GASKET SEE NOTES ¦HAD TO PURCHASE A DIFFERENT GASKET BESIDES WHAT WAS INVENTORY PURCHASED FROM BIG RIVERS RUBBER AND GASKKET WINDING .187 THICK 17.907 ID X18 11/16 OD CHANG
6000346 | GN001SGUFDEPRIMARYAIRFANS | G1 B PA Fan Motor Outboard Bearing Running Hot | replaced bearing and oil
5999953 | GN001SGUFDESTEAMCOILAIRHEATER | 1A TOP TWO STEAM COIL BANKS ON A SIDE ARE LEAKING INTERNALLY | plugged two tubes on second from top and 1 on top
6001492 | GN001SGUFDEAIRPREHEATERS | fabricate pointer for A/H per Bubba | COMPLETED
6001510 | GN001SGUFPESTOCKCOALFEEDERS | 1A COAL FEEDER CHANGE TRANSISTION CHUTE | changed transition chute on 1A coal feeder by ¦TITAN CONT. on 5/3/10. Had to move feeder to allow this change. had to cut out window on top of raw coal pipe and weld in. 8" X 12". also pad welded 4" X 2" on oppisite corner of pipe.
6001571 | GN001SGUFDEFORCEDDRAFTFANS | G1 A & B FD FAN INLET DAMPERS-FREE UP | inspcted inlet vanes. two were loose on B West ¦side. Ball and socket joints are worn on all vanes. Might want to look at replacing during next major outage
6001894 | GN001CW-CCWCLOSEDCOOLWTR | CCW Isolation Valves.> Inlet and Outlet valve are seize and breaking off. | Replaced five valves ¦1A FD Fan inlet inboard 1B FD Fan Outlet Inboard !B PA Fan Outlet otboard 1B PA Fan Inlet Outboard 1A PA Fan outlet outboard
6002014 | GN001CWSCCSCOOLINGTOWER | G1 COOLING TOWER SCREENS LAYING OUT BY COOLING TOWER, TWO SCREENS NEED REPAIRS, ONE IS BENT BADLY | Welded stiffners on screens and patched bottom
6002093 | GN001ASHARSWETBOTTOMHOPPER | G1 BOTTOM ASH REPAIRS | TITAN REPAIRED SEVERAL LEAKS ON WET BOTTOM AS NEED
5995449 | GN001SGUPCPPRECIPITATOR | PM-OUTAGE -G1 PRECIPITATORS PLATE RAPPER (RUN & CHECK LIFT) | replaced hammers and inspected rapper shafts and ¦bearings
5995450 | GN001SGUPCPPRECIPITATOR | PM-OUTAGE-G1 PRECIPITATIOR FIELD REPAIR | removed electrodes, repaired plates, and ¦repaired holes in walls
5996591 | GN001SGURBN-BOOSTAIR | THERE IS A BAD PA DUCT LEAK WHERE THE BOOST AIR DUCT CONNECTS | removed lagging and patched duct
5996740 | GN001SGUFDEAIR-GASDUCTS | SECONDARY AIR LEAK ON DUCTWORK AS IT ENTERS AIR REGISTERS FROM OUTSIDE | pulled grating and patched ductwork
6001926 | GN001SGUMBCVALVESANDFITTINGS | MACHINE COUPLING AND PIPE AS NECESSARY TO INSTALL NEW VALVES | Do machine work necessary to install pipe
5981289 | GN001SGUMBCVALVESANDFITTINGS | G1 EAST SIDE NORTH DRUM SAFETY IS LEAKING THROUGH. | Replaced disc and replap seats ¦Also repaired South east drum safety-lapped seat
5989810 | GN001SGUMBCBOILERSECTOINS | PM-OUTAGE-G1 INSPECT THE TUBE SHIELDS IN THE CONVECTION PASS | inspected tube sheild on convection pass and in re ¦reheat section replaced several shields in ik lanes
5989812 | GN001SGUMBCBOILERSECTOINS | PM-OUTAGE-G1 INSPECT WATERWALL TUBES AT EACH IR SOOTBLOWER | all soot blower pent. were good ut readings ¦onwalls were there was no overlay work done be titan cont work done from sky climbers
5989813 | GN001SGUMBCBOILERSECTOINS | PM-OUTAGE-G1 INSPECT THE KNEE SLOPE TUBE SHIELDS | inspected all four corners found several sheilds ¦missing did not replace at this time work done by titan cont from sky climber
5834205 | GN001CWSCCSCOOLINGTOWER | G1 COOLING TOWER HEADER ISOLATION VALVE ON THE SOUTHWEST SIDE OF H CELL IS BROKEN, WILL NOT ISOLATE | PRecision Cooling Tower repaired .3 cell valves
5891738 | GN001TGNMTCLUBEOILSYSTEM | G1 TURBINE LUBE OIL TANK LEVEL HIGH ALARM HAS BEEN IN SINCE OCTOBER. APPEARS TO BE PROBLEM WITH FLOA | replaced missing pin@resv.section
5985872 | GN001EDTTSGAUXILIARYTRANSFORMER | DOBLE TESTING OF G1 AUX TRANSFORMER BY BREC ET&S | Testing completed by ET&S on 5/4/2010.
5989656 | GN001TGNMTCMAINSTOPVALVES | PERFORM INSPECTION OF RIGHT HAND MSV-2010 | SEE LONG DESCRIPTION ¦PPSI COMPLETED INSPECTION. REPLACED STEM AND BYPASS VAVLE DISK, IT HAD ERODED AND CAUSE DAMAGE TO THE VALVE STEM. THE MAIN VALVE DISK NEEDS TO BE REPLACED NEXT INSPECTION HAD EXCESSIVE EROSION DUE TO BYPASS VAVLE LEAK THROUGH. BYPASS
5989783 | GN001CWSCCSCONDENSER | PM-OUTAGE-G1-INSPECT STEAM SIDE CONDENSER | Inspected, No issues reported
5989792 | GN001TGNMGCGENERATORSTATOR | PM-OUTAGE-G1 STATOR COOLING WATER SYSTEM PM | REPLACED FILTER LAB WAS TO REPLACE RESIN
5989857 | GN001CWSCCSCOOLINGTOWER | 2010 G1 COOLING TOWER WOOD STRUCTURE INSPECTION AND REPAIR | PRECISION COOLING TOWER REPAIRED ¦WOOD STRUCTURE AS REQUIRED BY INSPECTION
5995867 | GN001CWSCCSCIRCULATINGWATERPUMPS | PM-OUTAGE-G1 A & B CIRCULATING WATER PUMP MOTORS (CHANGE OIL) | changed oil and cleaned sight glasses
5995868 | GN001CWSCCSCONDENSER | PM-OUTAGE-G1 A&B VACUUM PUMP MOTORS (CHANGE OIL) | changed oil and cleaned sight glasses
5995872 | GN001TGNMGCGENERATORVOLTAGEREGULATOR | PM-OUTAGE-G1 INSPECT & CLEAN GENERATOR BRUSHES & HOLDERS | cleaned and repalced brushes
5995873 | GN001TGNMGCGENERATORVOLTAGEREGULATOR | PM-OUTAGE-G1 INSPECT VOLTAGE REGULATOR | assisted protec
5995876 | GN001TGNMGCGENERATORVOLTAGEREGULATOR | PM-OUTAGE-G1 INSPECT FIELD BREAKER | pro-tech calibrated and inspected
5995936 | GN001CWSCCSCIRCULATINGWATERPUMPS | PM- OUTAGE-G1 INSPECT CIRCULATING WATER PUMPS: COOLING WATER TO MOTOR UPPER THRUST BEARING | complete
5996019 | GN001CWSCCSCOOLINGTOWER | PM-OUTAGE-G1 CALIBRATE COOLING TOWER OIL PRESSURE SWITCHES | cal'd/tested ok
5996020 | GN001TGNMTCSTEAMCHEST | PM-OUTAGE-G1 TURBINE & GENERATOR CALIBRATIONS | performed calibrations
5996021 | GN001TGNMTCMAINSTOPVALVES | PM-OUTAGE-G1 INSPECT TURBINE CONTROLS & STROKE VALVES | calibrated & stroked vlvs
5997556 | GN001SGUMBCVALVESANDFITTINGS | SOUTH MAIN STEAM STOP VALVE: THE BEFORE SEAT | ISOLATION VALVE FOR THIS MOV IS NOT BUT 2YEARS OLD ¦DID NOT CHECK THIS BEFORE UNIT WAS BROUGHT OFF. WE DO NOT BELIEVE THIS VALVE LEAKS THRU. THIS VALVE SHOULD BE CLOSED DURING NORMAL OPERATION. THE MOV DOES NOT LAST BECAUSE IT IS THROTTLED DURING START UP
5996643 | GN001CWSCCSCONDENSER | CONDENSER WATER SIDE-OPEN CLOSE FOR CLEANING | DID NOT REPLACE ANY ANODES
5996242 | GN001TGNMTCREHEATVALVES | PM-OUTAGE-G1 HOT REHEAT STEAM PRESSURE READING IS OUT. | troubleshot and repaired
5997741 | GN000CWSMUSMAKEUPCLARIFIERS | INSPECT G1 & G2 CLARIFIERS | COULD ONLY GET G-2 CLARIFIER DONE
5998285 | GN001TGNMTCMAINSTOPVALVES | G-1 RIGHT SIDE (#2) MAIN STEAM STOP VALVE CYLINDER HAS AN EHC LEAK. | PPSI installed new o-rings and tightened
6000268 | GN001CWSCCSCIRCULATINGWATERPUMPS | G1 CIRCULATING WATER TUNNEL INSPECTION 2010 | opended lower door and ops inspected. ¦need to inspect turning vanes at pump during next major outage
6001423 | GN001TGNMTCTURBINE | MANUAL ROOT VALVE FOR TURBINE INLET PRESSURE TRANSMITTER HAS A PACKING LEAK. MUST BE REPAIRED ON | Valve was broken replaced valve
6001597 | GN001CWSCCSCONDENSER | REPAIR AIR IN LEAKAGE PER A.E.S REPORT | welded in new piece of pipe on #1 heater drain ¦repacked all valves on report and vac pump. welded cap on penetration through skirt on turbine
6001598 | GN001EDTTSG4160VSWITCHGEAR | GREEN UNIT 1 THERMOGRAPHY INSPECTION OF ELECTRICAL DISTRIBUTION EQUIPMENT | Completed partial inspection. See more... ¦Thermography Inspection performed on the following major electrcial equipment: G1'A' & 'B', Bus 2DS & Coal Handling 4160V switchgear, 480V Loadcenters, Station Batteries, Chargers and UPS-Inverter, Step-Up
6001929 | GN001TGNMTCMAINSTOPVALVES | G1 SOUTH TURBINE STOP VALVE INSPECTION 2010 | MACHINE SHOP WORK
6001938 | GN001TGNMTCELECTRO-HYDRAULICFLUIDSYSTEM | G1 TOP CONTROL VALVE EHC ACCUMALATOR CHECKED | PPSI installed new seal kit
6001753 | GN001TGNMGCGENERATORBEARINGS | G1 Turbine #8 Bearing Vibration Spikes | Mid American completed vibration checks
5978865 | GN001SGUFDEINDUCEDDRAFTFANS | GAS LEAK ON G-1 ID FAN SOUTH SIDE OF FAN ABOUT SAME LEVEL AS FLYASH POLK HOLES | Welded new corten metal over holes
5981594 | GN001FGDARTABSORBERTOWEREQUIPMENT | GREEN 1 DEMISTER WASH DISCHARGE LINE AT THE SPLIT ON | Installed 2 new 3" valves and new 1/2" valve ¦for instrument probe.
5989022 | GN001FGDCTLCONTROLSYSTEM | G1 B SIDE PH SAMPLE LINE ISOLATION VALVE LEAKS THRU - REPLACE VALVE | Installed new 3/4" valve
5989799 | GN001FGDARTGASDUCTS | PM-OUTAGE-G1 A & B INLET DUCTS. INSPECT & REPAIR BASE METAL | Titan-- ¦Welded new plate on roof of A side at probe pipes. Installed 1 new probe pipe and capped. RTW sprayed gunnite around inlet joints on A and B sides. RTW repaired a 4' x 4' place on B side roof going down to ID fan with mastic and brick. Inlet duct
5989804 | GN001FGDARTABSORBERTOWEREQUIPMENT | PM-OUTAGE-G1 CLEAN AND FLUSH THE RECYCLE HEADERS | General Insulation-- ¦Cleaned all pigtail nozzles A and B sides and Installed missing 3" and 4" pipe plugs.
5989805 | GN001FGDARTABSORBERTOWEREQUIPMENT | PM-OUTAGE-G1 CLEAN AND FLUSH THE DEMISTER WASH HEADERS | General Insulation-- ¦Removed all nozzles on A and B sides and cleaned nozzles. Bill Sterling pressure washed all demister headers. Found 2 headers plugged on A side, Titan cut headers and Bill Sterling cleaned. Titan welded headers back. General Insulati
5989806 | GN001FGDARTABSORBERTOWEREQUIPMENT | PM-OUTAGE-G1 DISCONNECT/CONNECT AUX. BLEED LINES | Disconnected A and B and installed ¦flange reducer to fit to flush hose. Bill Nelson Flushed. Reconnected lines to main header.
5989807 | GN001FGDFG-SLURRYHOLDTANK | PM-OUTAGE-G1 CLEAN AND FLUSH THE SLURRY LINES | Ttan-- ¦Broke suction lines on A and B Bleed Pumps, lines were just white coated. Broke A and B Bleed lines going into Reaction Tanks, Bill Sterling cleaned lines going into tanks. Broke A and B Bleed discharge lines as they leave the building, th
5989808 | GN001FGDARTABSORBERTOWEREQUIPMENT | PM-OUTAGE-G1 CLEAN THE MIST ELIMINATOR PANELS | Bill Sterling Cleaned A and B Sides ¦Chevrons are all in place and look good.
5989809 | GN001FGDARTABSORBERTOWEREQUIPMENT | PM-OUTAGE-G1 CLEAN A&B REACTION TANKS & SCREEN TANKS | Bill Sterling washed and vacuumed out ¦A and B screen tanks and reaction tanks. Also, washed all screens and installed.
5989981 | GN001FGDARTGASDUCTS | SCAFFOLDING NEEDS FOR G1 2010 OUTAGE | General Insulation-- ¦Provided SCAFFOLDING NEEDS FOR G1 2010 OUTAGE.
5995470 | GN001FGDARTABSORBERTOWEREQUIPMENT | G1 SPRING 2010 OUTAGE EQUIPMENT RENTAL | Cover cost of G1 SPRING 2010 OUTAGE EQUIPMENT RENT
5995351 | GN000SWYSPETHICKENERTANKS | G1 A & B THICKENER INSPECTIONS | INSPECTED BOTH THICKNERS ¦RUBBER COATING IN BOTH A AND B THICKNERS ARE GETTING IN BAD CONDITION. MAY NEED RECOATED OR REPLACED WITH IN THE FUTURE.
5995885 | GN001ENVCEMAIREMISSIONS | PM-OUTAGE-G1 INSPECT & CALIBRATE OPACITY MONITORS | remov/clnd clear pth cal'd
5995886 | GN001ENVCEMAIREMISSIONS | PM-OUTAGE-G1 CLEAN & INSPECT CEM EQUIPMENT | compl w/tech instr.
5995935 | GN001FGDCTLCONTROLSYSTEM | PM- OUTAGE-G1 CALIBRATE SCRUBBER PROBES | cleaned and cal'ed
5996016 | GN001FGDARTABSORBERTOWEREQUIPMENT | 1C RECYCLE PUMP - INSTALL DISCHARGE EXPANSION JOINT | repaired seal and replaced expansion jopint
6000566 | GN001CWSCCSCIRCULATINGWATERPUMPS | Replace seal water lines in G1 Pump house | replace line
6002138 | GN001FGDSTKSTACK | INSPECT G1 STACK TITANIUM LINER OF STACK AND PROVIDE SERVICES FOR REPAIR | R and P Chimney Inspected Stack Liner ¦from top to bottom and found no other breaks in Titanium Liner. A and D Construction repaired 2ea. 1' breaks in the Titanium where the outlet duct roof meets the stack opening radius by welding Titanium Patches to th
5989962 | GN001FGDARTGASDUCTS | G1 SCRUBBER OUTLET DUCT REPAIR-2010 | Titan-- ¦Solid Platforms came in 1 week before the outage start and installed a scaffold from the ground up to the bad wall on the east and west sides of the duct. The east wall did not show signs of deterioration like the west wall did. Solid Platforms supplied person to Tag scaffold each day of outage for first and second shift tagging. Cut out 10' wide of Titanium from the expansion joint going towards the stack cone to the next vertical beam. Cut out 20' high towards ceiling in same area. 10' x 20' total. Cut out slightly bigger area in old outside wall. Cleaned out all rust that had fallen between remaining Titanium and old wall. Flew new 1/4" Corten Metal up with crane and set inside duct. Hung each piece and seal welded all new metal back into 10' x 20' cutout. Installed 4 new 4" channel iron cross braces on outside of duct wall in the horizonal position to better support new met
5982895 | GN001SGURBN-EASTDUCT | G-1 FRONT AND REAR WALL OFA REXA DRIVE DAMPERS NEED TO BE INSPECTED INSIDE DUCT FOR FULL OPEN AND | Dampers stroked by ops. Everything worked well
5989811 | GN001SGURBN-BURNER | PM-G1 OUTAGE-INSPECT THE BURNERS | inspected all burners. Found hole in ¦2R and 2F. Welded 10" X 14" patch on 2R burner tip and 2 ea. patches on 2F burner tip 6" X 6" and 4" X 4".
5989978 | GN001SGURBN-COALINJECTOR | G1 COAL INJECTORS-REPLACE TIPS | replaced old tips installed new gaskets and bolts ¦replaced probes and put in pipe plugs
5989740 | GN001ASHARSFLYASHSYSTEM | PM-OUTAGE- OPERATIONS-G1 VACUUM FLYASH HOPPERS | A/T completed
5989741 | GN001CWSCCSCONDENSER | PM-OUTAGE-OPERATION-G1-HIGH PRESSURE WASH CONDENSER | Tubes very dirty, has a lot of scale- A/T high ¦pressure washed
5989744 | GN001SGUFDEINDUCEDDRAFTFANS | PM-OUTAGE OPERATIONS-G1 HP WASH ID FANS | A/T completed
5989745 | GN001FGDARTABSORBERTOWEREQUIPMENT | PM-OUTAGE OPERATIONS-G1 HP WASH RECYCLE HEADERS | CLEAN NOZZLES ON RECYCLE HEADERS ¦CLEANED HEADERS AND NOZZLES ON DEMISTER WASH LINE
5989746 | GN001FGDFG-FGDS(SCRUBBER) | PM-OUTAGE OPERATIONS-G1 HP ADDITIVE FEED LINES | A/T CLEANED BLEED LINES INO REACTION TANKS
5989747 | GN001FGDFG-FGDS(SCRUBBER) | PM-OUTAGE OPERATIONS-G1 HP WASH/DESLAG BOILER | Expro completed, had delays due to Lighting storm ¦in area
5994623 | GN001SGUFDEAIRPREHEATERS | PM-OUTAGE-OPERATIONS-G1 WASH AIR HEATERS | A/T completed