## Cost Detail
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | TOTAL
New-Build CC (Brownfield @ BS site) | [11 empty] | Cost per kW
Cash Flow | [8 empty] | 0% |  |  | Nominal | '2011 $'/kW
Assuming 2x1 Mitsubishi 501-GAC | [11 empty] | ('As-Spent')$
Contingency-Adjusted
Nominal k$
Project Estimate (Per S&L/Kiewet Study) | 0 | 0 | 5000 | 57000 | 310000 | 476000 | 186000 | 0 | 1034000 |  | w/o Corp OH and Contingency
Contingency Adder @ 10% (Per EP&FS) | 0 | 0 | 500 | 5700 | 31000 | 47600 | 18600 | 0 | 103400
Total EPC | 0 | 0 | 5500 | 62700 | 341000 | 523600 | 204600 | 0 | 1137400 |  | Total (Nominal), excl. AFUDC | 1258.1858
AEP Allocated Costs/OH (Increm 8.5%) | 0 | 0 | 467.5 | 5329.5 | 28985 | 44506 | 17391 | 0 | 96679 |  | 1234079 | 106.9458
GRAND CC @ BS | 0 | 0 | 5967.5 | 68029.5 | 369985 | 568106 | 221991 | 0 | 1234079
2011 $ |  | 0 | 5679.9524 | 63172.1536 | 335188.1493 | 502122.9239 |  |  | 1189.1905 | $/kW
|  | 0 | 0.62681 | 6.9714 | 36.9898 | 55.412 |  |  | 100 | expenditure profile
100
Total '2011 $' EPC | 0 | 0 | 5500 | 62700 | 341000 | 523600 | 204600 | 0 | 1137400 |  |  |  | 1258.1858
Total '2011 $' OH | 0 | 0 | 467.5 | 5329.5 | 28985 | 44506 | 17391 | 0 | 96679
Total '2011 $' TOTAL | 0 | 0 | 5967.5 | 68029.5 | 369985 | 568106 | 221991 | 0 | 1234079 |  |  |  | 1365.1316

## BS Brownfield CC
Current Ongoing O&M and Capital Costs (as spent $000) Plan |  | 2011 | 2012 | 2013 | 2014 | 2015-03-01
Big Sandy 1BCO |  | 2699.7627 | 2329.3346 | 2593.4276 | 2905.3715 | 734.3028
Big Sandy 1Environmental Capital |  | 63.2623 | 76.0377 | 39.2453 | 69.1302 | 17.4719
Big Sandy 1G&A Expense |  | 539.9525 | 465.8669 | 518.6855 | 581.0743 | 146.8606
Big Sandy 1Major Projects |  | 0 | 820.9628 | 1926.132 | 4173.366 | 1054.7754
Big Sandy 1NOMI |  | 425.4166 | 222.4717 | 244.9811 | 1324.9064 | 334.8565
Big Sandy 1OPC |  | 331.676 | 310.8691 | 120.5149 | 6116.8715 | 1545.9764
Big Sandy 1Removal |  | 109.6307 | 108.1137 | 57.9398 | 1113.653 | 281.4644
Big Sandy 1Scheduled Outage |  | 143.4842 | 323.4528 | 469.9057 | 2922.4528 | 738.6199
Existing Unit
$000 | On-going Capital + Major Environ | 394.9382 | 1207.8695 | 2085.8922 | 10359.3676 | 2618.2237 | 0
$000 | Fixed O&M | 3808.6161 | 3341.1261 | 3827 | 7733.805 | 1954.6398 | 0
| Fixed Costs | 3861.2218 | 3554.62 | 4318.3348 | 9605.0076 | 98119.7096 | 0
BS1 Brownfield |  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017
Pre 2012 Costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capital Cash Flow Project Detail |  | 0 | 0 | 5000 | 57000 | 310000 | 476000 | 161000
|  | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
| Total FOM $000 | 161000 2017: 9993.5653; 161000 2018: 17654.7703
FOM | Fixed Annual Capacity Rate ($/kW-yr) | [6 empty] | 13.1149 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169 | 23.169
| Fixed Costs ($000) for 2017 Capital | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 29569.2012 | 163730.5947
| Gas Pipeline Recovery ($000) | 0 | 0 | 0 | 0 | 0 | 0 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626 | 16379.9626
| Total Fixed Costs ($000) | 0 | 0 | 0 | 0 | 0 | 0 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 45949.1638 | 180110.5573
|  | 50% | CF
| Annual VOM 2011 $000 | 0 2011: 8874
VOM | GWh based on 50% CF | 0 2011: 3263.1
| 2011 $/MWH | 0 2011: 2.7195
Note on J36: $20.14/kw-year based on 5/20/11 assumption data

## BROWNFIELD
| FTCA_CSAPR | NO CARBON | EARLY CARBON | HIGH BAND | LOW BAND |  | Fixed Reservation Cost |  |  | FTCA_CSAPR | NO CARBON | EARLY CARBON | HIGH BAND | LOW BAND
| Henry Hub | Henry Hub | Henry Hub | Henry Hub | Henry Hub |  | Brownfield |  | =henry hub (under diff commodity prices) + basis diff / (1-retainage)+ Pipeline Transportation Adder
[7 empty] | $000 |  | 2011 | 1 | 1 | 1 | 1 | 1
2012 | 4.4808 | 4.4808 | 4.4808 | 4.4808 | 3.9433 | 2011 | 0 |  | 2012 | 4.5243 | 4.5243 | 4.5243 | 4.5243 | 3.9868
2013 | 4.9392 | 4.9392 | 4.9392 | 5.4325 | 4.3458 | 2012 | 0 |  | 2013 | 4.9362 | 4.9362 | 4.9362 | 5.4296 | 4.3429
2014 | 5.375 | 5.375 | 5.375 | 6.0192 | 4.7292 | 2013 | 0 |  | 2014 | 5.376 | 5.376 | 5.376 | 6.0202 | 4.7302
2015 | 5.5192 | 5.5192 | 5.5192 | 6.2925 | 4.8567 | 2014 | 0 |  | 2015 | 5.5227 | 5.5227 | 5.5227 | 6.2961 | 4.8602
2016 | 5.985 | 5.985 | 5.985 | 6.9417 | 5.2658 | 2015 | 0 |  | 2016 | 5.9909 | 5.9909 | 5.9909 | 6.9475 | 5.2717
2017 | 6.1267 | 6.1267 | 6.415 | 7.2292 | 5.3917 | 2016 | 0 |  | 2017 | 6.1356 | 6.1356 | 6.4239 | 7.2381 | 5.4006
2018 | 6.32 | 6.32 | 6.6 | 7.4592 | 5.5625 | 2017 | 16379.9626 | 8189.9813 | 2018 | 6.3299 | 6.3299 | 6.6099 | 7.4691 | 5.5724
2019 | 6.4575 | 6.4575 | 6.7275 | 7.62 | 5.6825 | 2018 | 16379.9626 | 8189.9813 | 2019 | 6.4668 | 6.4668 | 6.7368 | 7.6293 | 5.6918
2020 | 6.515 | 6.515 | 6.78 | 7.6867 | 5.7325 | 2019 | 16379.9626 | 8189.9813 | 2020 | 6.5293 | 6.5293 | 6.7943 | 7.7009 | 5.7468
2021 | 6.7525 | 6.6 | 7.0633 | 7.9675 | 5.9425 | 2020 | 16379.9626 | 8189.9813 | 2021 | 6.7775 | 6.625 | 7.0883 | 7.9925 | 5.9675
2022 | 7.065 | 6.6758 | 7.215 | 8.3367 | 6.2167 | 2021 | 16379.9626 | 8189.9813 | 2022 | 7.0971 | 6.708 | 7.2471 | 8.3688 | 6.2488
2023 | 7.2617 | 6.8625 | 7.35 | 8.5692 | 6.39 | 2022 | 16379.9626 | 8189.9813 | 2023 | 7.2854 | 6.8862 | 7.3737 | 8.5929 | 6.4137
2024 | 7.5075 | 7.095 | 7.5075 | 8.8592 | 6.6067 | 2023 | 16379.9626 | 8189.9813 | 2024 | 7.5307 | 7.1182 | 7.5307 | 8.8824 | 6.6299
2025 | 7.745 | 7.3192 | 7.745 | 9.1392 | 6.815 | 2024 | 16379.9626 | 8189.9813 | 2025 | 7.7722 | 7.3464 | 7.7722 | 9.1664 | 6.8422
2026 | 7.8492 | 7.4167 | 7.8492 | 9.2617 | 6.9067 | 2025 | 16379.9626 | 8189.9813 | 2026 | 7.8835 | 7.451 | 7.8835 | 9.296 | 6.941
2027 | 8.04 | 7.5992 | 8.04 | 9.4875 | 7.0758 | 2026 | 16379.9626 | 8189.9813 | 2027 | 8.0642 | 7.6234 | 8.0642 | 9.5117 | 7.1
2028 | 8.22 | 7.7675 | 8.22 | 9.78 | 7.2333 | 2027 | 16379.9626 | 8189.9813 | 2028 | 8.2434 | 7.7909 | 8.2434 | 9.8034 | 7.2568
2029 | 8.405 | 7.9433 | 8.405 | 10.08 | 7.3967 | 2028 | 16379.9626 | 8189.9813 | 2029 | 8.4333 | 7.9717 | 8.4333 | 10.1083 | 7.425
2030 | 8.5225 | 8.05 | 8.5225 | 10.48 | 7.4992 | 2029 | 16379.9626 | 8189.9813 | 2030 | 8.5546 | 8.0821 | 8.5546 | 10.5121 | 7.5313
2031 | 8.6898 | 8.2062 | 8.6898 | 10.8335 | 7.6459 | 2030 | 16379.9626 | 8189.9813 | 2031 | 8.7288 | 8.2453 | 8.7288 | 10.8726 | 7.685
2032 | 8.8523 | 8.358 | 8.8523 | 11.2094 | 7.7886 | 2031 | 16379.9626 | 8189.9813 | 2032 | 8.8902 | 8.3959 | 8.8902 | 11.2473 | 7.8265
2033 | 9.0066 | 8.5009 | 9.0066 | 11.6133 | 7.9239 | 2032 | 16379.9626 | 8189.9813 | 2033 | 9.0445 | 8.5388 | 9.0445 | 11.6512 | 7.9617
2034 | 9.174 | 8.6568 | 9.174 | 12.0177 | 8.0707 | 2033 | 16379.9626 | 8189.9813 | 2034 | 9.2107 | 8.6934 | 9.2107 | 12.0543 | 8.1073
2035 | 9.3414 | 8.8124 | 9.3414 | 12.4405 | 8.2175 | 2034 | 16379.9626 | 8189.9813 | 2035 | 9.3818 | 8.8529 | 9.3818 | 12.4809 | 8.2579
2036 | 9.5104 | 8.9694 | 9.5104 | 12.8802 | 8.3657 | 2035 | 16379.9626 | 8189.9813 | 2036 | 9.5581 | 9.017 | 9.5581 | 12.9279 | 8.4133
2037 | 9.6845 | 9.1312 | 9.6845 | 13.3325 | 8.5183 | 2036 | 16379.9626 | 8189.9813 | 2037 | 9.7439 | 9.1906 | 9.7439 | 13.392 | 8.5777
2038 | 9.8609 | 9.295 | 9.8609 | 13.8021 | 8.673 | 2037 | 16379.9626 | 8189.9813 | 2038 | 9.9312 | 9.3653 | 9.9312 | 13.8724 | 8.7433
2039 | 10.0404 | 9.4616 | 10.0404 | 14.2882 | 8.8303 | 2038 | 16379.9626 | 8189.9813 | 2039 | 10.1212 | 9.5425 | 10.1212 | 14.3691 | 8.9112
2040 | 10.2235 | 9.6317 | 10.2235 | 14.791 | 8.9909 | 2039 | 16379.9626 | 8189.9813 | 2040 | 10.3149 | 9.723 | 10.3149 | 14.8824 | 9.0823
[6 empty] | 2040 | 16379.9626 | 8189.9813

## Data Source
Big Sandy Unit 1
Input Assumptions
| 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
Current EFOR Forcast | 10.3% | 11.8% | 13% | 13% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
| 2011 | 2011 | 2011 | 2012 | 2012 | 2012 | 2012 | 2012 | 2012 | 2012 | 2012 | 2012 | 2012 | 2012 | 2012 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2018 | 2019 | 2019 | 2019 | 2019 | 2019 | 2019 | 2019 | 2019 | 2019 | 2019 | 2019 | 2019 | 2020 | 2020 | 2020 | 2020 | 2020 | 2020 | 2020 | 2020 | 2020 | 2020 | 2020 | 2020 | 2021 | 2021 | 2021 | 2021 | 2021 | 2021 | 2021 | 2021 | 2021 | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2023 | 2023 | 2023 | 2023 | 2023 | 2023 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2024 | 2024 | 2024 | 2024 | 2024 | 2024 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025 | 2025 | 2025 | 2025 | 2025 | 2025 | 2025 | 2025 | 2025 | 2025 | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2026 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2027 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2028 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2029 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030 | 2030
 | time axis 2011-10-01 to 2030-12-01
Current outage days per month | 31 | 27 | 0 | 0 | 0 | 29 | 1 | 0 | 0 | 0 | 0 | 16 | 31 | 30 | 9 | 0 | 0 | 2 | 28 | 0 | 0 | 0 | 0 | 17 | 31 | 30 | 8 | 0 | 14 | 31 | 30 | 31 | 8 | 0 | 0 | 18 | 31 | 30 | 7 | 0 | 15 | 31 | 30 | 31 | 7 | 0 | 0 | 19 | 31 | 30 | 6 | 31 | 29 | 31 | 30 | 31 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 31 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 31 | 27 | 0 | 0 | 0 | 29 | 1 | 0 | 0 | 0 | 0 | 16 | 31 | 30 | 9 | 0 | 0 | 2 | 28 | 0 | 0 | 0 | 0 | 17 | 31 | 30 | 8 | 0 | 14 | 31 | 30 | 31 | 8 | 0 | 0 | 18 | 31 | 30 | 7 | 0 | 15 | 31 | 30 | 31 | 7 | 0 | 0 | 19 | 31 | 30 | 6 | 31 | 29 | 31 | 30 | 31 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 31 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 0
Current Ongoing O&M and Capital Costs (as spent $000) Plan | 2011-10-01: 2011; 2011-11-01: 2012; 2011-12-01: 2013; 2012-01-01: 2014
Big Sandy 1BCO | 2011-10-01: 2699.7627; 2011-11-01: 2329.3346; 2011-12-01: 2593.4276; 2012-01-01: 2905.3715
Big Sandy 1Environmental Capital | 2011-10-01: 63.2623; 2011-11-01: 76.0377; 2011-12-01: 39.2453; 2012-01-01: 69.1302
Big Sandy 1G&A Expense | 2011-10-01: 539.9525; 2011-11-01: 465.8669; 2011-12-01: 518.6855; 2012-01-01: 581.0743
Big Sandy 1Major Projects | 2011-10-01: 0; 2011-11-01: 820.9628; 2011-12-01: 1926.132; 2012-01-01: 4173.366
Big Sandy 1NOMI | 2011-10-01: 425.4166; 2011-11-01: 222.4717; 2011-12-01: 244.9811; 2012-01-01: 1324.9064
Big Sandy 1OPC | 2011-10-01: 331.676; 2011-11-01: 310.8691; 2011-12-01: 120.5149; 2012-01-01: 6116.8715
Big Sandy 1Removal | 2011-10-01: 109.6307; 2011-11-01: 108.1137; 2011-12-01: 57.9398; 2012-01-01: 1113.653
Big Sandy 1Scheduled Outage | 2011-10-01: 143.4842; 2011-11-01: 323.4528; 2011-12-01: 469.9057; 2012-01-01: 2922.4528
Note 1
BS1 can reach 285 MW net in the summer and 295 MW net in the winter
constrained now to 278 MW by particulate emmisions
4.5 MW of aux power will be gained due to removal of precips, pulvs, pa fans, etc.
Propose full load to be 260 MW due to fan limitations in winter and higher HR on gas
Note 2
Sorted last 5 yrs GADS data removing EFOR for pulv, opacity, precips, etc.
Applied this ave to proposed EFOR
Note 3
Includes Proposed U1 Plant labor and Contract labor such as mowing, roofing, trash disposal, janitoral
Values were obtained from Current year contract labor
To separate U1 and U2 used MW ratio of 0.26 along with a capacity factor of 0.15
Plant labor was calculated removing system codes not used after project and staffing U1 by dispatching from U2 as needed
Note 4
Values obtained from Current year non labor such as chemicals, gases, env fees, etc.
To separate U1 and U2 used MW ratio of 0.26 along with a capacity factor of 0.15
Note 5
Values obtained from Current year NOMI
To separate U1 and U2 used MW ratio of 0.26 along with a capacity factor of 0.15
Note 6
Forecasted projects over the future years projections such as
combustion coils, chart recorders, communications (PA), obsolete pump replacements, plant batteries, lighting projects
Major Projects
2014 - Inspect and Repair Gas Outlet Duct $1,200,000 O&M, this is moved down to the Scheduled Outage row
2016 - Inspect and Repair Cooling Tower Fill Structure @ $490,000 O&M, this is moved down to the Scheduled Outage row
2018-Main steam attemp is on site, will install when existing fails,
attemp is a 6 month lead time, so having onsite reduces risk exposure
$334,000 labor to install Capital
2020 -Generator Rewind- inspect for changes during turbine outages
Suspect Rewind in 2021 @ $3,500,000 Capital
Outage schedule every other year until major projects (liabilities) are completed
Then schedule will switch to every three years to perform required turbine inspections
Major scheduled outage projects - year
2014 - 11 week outage - turbine valves, safety valves, FAC, ORM & circular letter requirements
2016 - 6 week outage - turbine valves, safety valves, ORM & circular letter requirements
2018 - 6 week outage - BFP replace, ORM & circular letter requirements
2020 - 6 week outage - BFPT replace, ORM & circular letter requirements
2023 - 10 week outage - turbine inspections, air heater repairs, ORM & circular letter requirements
2026 - 10 week outage - turbine inspections, drum & deaerator repairs, ORM & circular letter requirements
2029- no outage, near end of life
Gas conversion project costs
Assumed a $35.5M gas line plus contingency, escalation, mgmt reserve and uncontrollables
Assumed first 5 SSH inlet tubes require replacement
Assumed conversion cost at 50% of MR5 costs
Assumed on site gas line costs are the same as MR5
Assumed needed project for HAPs or for a 2015 operation

## Template Capital Input
KPCo
30 year rate | 13.32%
NPV | 8.62% | [33 empty] | Existing | [33 empty] | BFCC | Capital + Gas Pipeline Recovery
|  |  | CAP | [33 empty] | CAP
Current Big Sandy 1 |  |  | EX | [33 empty] | EX
Retire 4/1/2015
|  | 2011 | 394.9382 | 0 | 52.6058 | [29 empty] | 52.6058 | 2011 | 0 | 0 | 0 | [29 empty] | 0
|  | 2012 | 1207.8695 | 0 | 52.6058 | 160.8882 | [28 empty] | 213.494 | 2012 | 0 | 0 | 0 | 0 | [28 empty] | 0
|  | 2013 | 2085.8922 | 0 | 52.6058 | 160.8882 | 277.8408 | [27 empty] | 491.3348 | 2013 | 0 | 0 | 0 | 0 | 0 | [27 empty] | 0
|  | 2014 | 10359.3676 | 0 | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | [26 empty] | 1871.2026 | 2014 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0
|  | 2015 | 2618.2237 | 0 | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | [25 empty] | 96165.0698 | 2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [25 empty] | 0
|  | 2016 | 0 | 0 | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | [24 empty] | 2219.95 | 2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [24 empty] | 0
|  | 2017 | 0 | 0 | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | [23 empty] | 2219.95 | 2017 | 221991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | [23 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2018 | 0 | 0 | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | [22 empty] | 2219.95 | 2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | [22 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2019 | 0 | 0 | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | [21 empty] | 2219.95 | 2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | [21 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2020 | 0 | 0 | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | [20 empty] | 2219.95 | 2020 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | [20 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2021 | 0 | 0 | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | [19 empty] | 2219.95 | 2021 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | [19 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2022 | 0 | 0 | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [18 empty] | 2219.95 | 2022 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | [18 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2023 | 0 | 0 | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [17 empty] | 2219.95 | 2023 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | [17 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2024 | 0 | 0 | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 2219.95 | 2024 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2025 | 0 | 0 | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 2219.95 | 2025 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2026 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 2219.95 | 2026 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2027 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 2219.95 | 2027 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2028 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 2219.95 | 2028 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2029 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 2219.95 | 2029 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2030 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 2219.95 | 2030 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2031 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 2219.95 | 2031 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2032 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 2219.95 | 2032 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2033 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 2219.95 | 2033 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2034 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 2219.95 | 2034 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2035 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 2219.95 | 2035 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 29569.2012 | 45949.1638 | 22974.5819
|  | 2036 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2219.95 | 2036 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 29569.2012 | 45949.1638 | 22974.5819
|  | 2037 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 2219.95 | 2037 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 29569.2012 | 45949.1638 | 22974.5819
|  | 2038 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2219.95 | 2038 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 29569.2012 | 45949.1638 | 22974.5819
|  | 2039 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2219.95 | 2039 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 29569.2012 | 45949.1638 | 22974.5819
|  | 2040 | 0 |  | 52.6058 | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2219.95 | 2040 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163730.5947 | 180110.5573 | 90055.2787
|  |  | 0 |  |  | 160.8882 | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2167.3442 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012
|  |  | 0 |  |  |  | 277.8408 | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2006.456 | [5 empty] | 0 | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012
|  |  | 0 |  |  |  |  | 1379.8678 | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1728.6152 | [6 empty] | 0 | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012
|  |  | 0 | [5 empty] | 348.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 348.7474 | [7 empty] | 0 | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012
|  |  | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0 | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012
|  |  | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 29569.2012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29569.2012
|  |  | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[25 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[27 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[28 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[29 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [27 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[30 empty] | 0 | 0 | 0 | 0 | 0 | 0 | [28 empty] | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | [29 empty] | 0 | 0 | 0 | 0 | 0
[32 empty] | 0 | 0 | 0 | 0 | [30 empty] | 0 | 0 | 0 | 0
[33 empty] | 0 | 0 | 0 | [31 empty] | 0 | 0 | 0
[34 empty] | 0 | 0 | [32 empty] | 0 | 0
|  | 2011 | 0 | 0 | 0 | [29 empty] | 0
|  | 2012 | 0 | 0 | 0 | 0 | [28 empty] | 0
|  | 2013 | 0 | 0 | 0 | 0 | 0 | [27 empty] | 0
|  | 2014 | 0 | 0 | 0 | 0 | 0 | 0 | [26 empty] | 0
|  | 2015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [25 empty] | 0
|  | 2016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [24 empty] | 0
|  | 2017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [23 empty] | 0
|  | 2018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0
|  | 2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [21 empty] | 0
|  | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [20 empty] | 0
|  | 2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [19 empty] | 0
|  | 2022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [18 empty] | 0
|  | 2023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [17 empty] | 0
|  | 2024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [16 empty] | 0
|  | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [15 empty] | 0
|  | 2026 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [14 empty] | 0
|  | 2027 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 0
|  | 2028 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [12 empty] | 0
|  | 2029 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0
|  | 2030 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | 0
|  | 2031 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0
|  | 2032 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 0
|  | 2033 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0
|  | 2034 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0
|  | 2035 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 2036 | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0
|  | 2037 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0
|  | 2038 | 0 | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0
|  | 2039 | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
|  | 2040 | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [17 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [21 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [24 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [25 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [26 empty] | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [27 empty] | 0 | 0 | 0 | 0 | 0
|  |  | 0 | [28 empty] | 0 | 0 | 0 | 0
|  |  | 0 | [29 empty] | 0 | 0 | 0
|  |  | 0 | [30 empty] | 0 | 0

## Re-Analysis Update
KYPCo Re-Analysis Update
Big Sandy 2 - DFGD & Assoc Work Project |  | Big Sandy 1 CC Repower |  | Big Sandy CC Brownfield Replacement
Phase 1 Cost Estimate - May 2012 |  | S&L Cost Estimate Study - 9/16/2011 |  | S&L Cost Estimate Study - 5/31/2011
|  | MHI501GAC |  | MHI501GAC
|  | 745 MW Net Output |  | 762 MW Net Output
June 2017 In Service - As Spent - $000 |  | June 2017 In Service - As Spent - $000 |  | June 2017 In Service - As Spent - $000
DFGD | 610000 | NGCC | 835000 | NGCC | 979000
Assoc Work | 184000 | Natural Gas Supply | 51000 | Natural Gas Supply | 51000
Landfill & Haul Road | 64000 | Transmission SWYD | 7000 | Transmission SWYD | 4000
Total Project Cost | 858000 | Total Project Cost | 893000 | Total Project Cost | 1034000
AEP Allocations | 90000 | AEP Allocations | 93000 | AEP Allocations | 108000
Total | 948000 | Total | 986000 | Total | 1142000
Cash Flow - $000 |  | Cash Flow - $000 |  | Cash Flow - $000
Pre 2012 Costs | 29552 | Pre 2012 Costs | 29552 | Pre 2012 Costs | 29552
2013 | 9000 | 2013 | 4000 | 2013 | 5000
2014 | 135000 | 2014 | 49000 | 2014 | 57000
2015 | 205000 | 2015 | 268000 | 2015 | 310000
2016 | 299000 | 2016 | 411000 | 2016 | 476000
2017 | 210000 | 2017 | 161000 | 2017 | 186000
Plant Performance |  | Plant Performance |  | Plant Performance
Inlet SO2 Loading Design Basis - lbs SO2 per MMBtu | 4.5 | Net Output - Annual Avg Unfired - MW | 745 | Net Output - Annual Avg Unfired - MW | 762 | 381
SO2 Removal Efficiency | 98% | Net Plant Heat Rate - Annual Average Unfired - Btu/kWH | 6862 | Net Plant Heat Rate - Annual Average Unfired - Btu/kWH | 6707
Net Aux Load (MW) | 12 | Net Output - Annual Avg Fired - MW | 802 | Net Output - Annual Avg Fired - MW | 918
Fixed O&M Costs (2010-$'s) - $/yr | 5066000 | Net Plant Heat Rate - Annual Average Fired - Btu/kWH | 7042 | Net Plant Heat Rate - Annual Average Fired - Btu/kWH | 7143
SO2 Removal Costs (2010-$'s) - $/Ton SO2 removed | 298.04 | Variable O&M (2011-$) - $/yr | 9088000 | Variable O&M (2011-$) - $/yr | 8874000
|  | Fixed O&M (2011-$) - $/yr | 9605000 | Fixed O&M (2011-$) - $/yr | 9605000
|  | 107.651 | 1.0765 |  | 120.4724 | 116.4724 | (minus forced outage)
Notes: |  | 103.651 | (minus forced outage)
1. Total Project Cost estimate is classified as a Class III estimate using AACE recommended practices and includes the results of the P100 Risk Analysis.
2. Natural Gas Supply capital cost estimate is based on the Class IV budgetary cost estimate provided by Tennessee Pipeline in May 2011 escalated to a 2017 in service date.
3. AEP Allocations is calculated using the 2012 operating company overhead rate of 10.46% provided by Mike Huggett 9/25/2012 e-mail.
4. Pre 2012 Costs include Wet and Dry FGD, Landfill and Repowering Combined Cycle Study projects actual costs as of August 31, 2012 provided by Mike Huggett 09/25/2012 e-mail.

## Rates
Kentucky Power
Annual Investment Carrying Charges
For Economic Analyses
As of 12/31/2011
Investment Life (Years)
| 2 | 3 | 4 | 5 | 10 | 15 | 20 | 25 | 30 | 33 | 40 | 50
Return (1) | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62 | 8.62
Depreciation (2) | 48.9097 | 31.6446 | 23.0084 | 17.8491 | 7.7087 | 4.5032 | 3.0061 | 2.1744 | 1.6629 | 1.4453 | 1.0916 | 0.79524
FIT (3) (4) | 2.3101 | 1.6547 | 1.7838 | 1.4801 | 1.4183 | 1.7317 | 1.8029 | 1.5814 | 1.4376 | 1.3737 | 1.2643 | 1.1647
Property Taxes, General & Admin Expenses | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
| 61.4398 | 43.5193 | 35.0122 | 29.5492 | 19.347 | 16.4549 | 15.029 | 13.9758 | 13.3206 | 13.039 | 12.576 | 12.1799
(1) Based on a 99.56% (as of 12/31/2011) and 0.44% incremental weighting of capital costs
(2) Sinking Fund annuity with R1 Dispersion of Retirements
(3) Assuming MACRS Tax Depreciation
(4) @ 35% Federal Income Tax Rate

## Big Sandy Gas Fuel Case - 750MW
Big Sandy Gas Fuel Scenarios |  |  | Example of Cost Calculations:
750 MW Combined-Cycle w/ Duct Burners
Kinder Morgan - Tennessee Gas Pipeline |  |  | Assume NYMEX | 4 | $/mmBtu *
ASSUMES 15-YEAR OR 20-YEAR TERM - 100% FIRM TRANSPORTATION |  |  | Assume 750MW w/ duct burners at 7,675 btu/kwh heat rate | 7291.65 | mmBtu/hr
PIPELINE CONSTRUCTION COSTS INCLUDED IN FIRM RATE |  |  | Assume Unit CF | 75%
Base Case: 100% Firm Transportation on Lateral & Tennessee Mainline |  |  | Base Case: 100% Firm Transportation on Lateral & Tennessee Mainline
Firm Transportation Reservation Fixed Cost | 0.26 | $/mmBtu | Firm Transportation Cost
Demand Surcharge: | 0 |  | Fixed Cost
Demand Surcharge: | 0 |  | Full load | 7291.65 | mmBtu/hr
CCRM (Modernization) | 0 |  | Full Daily Load | 174999.6 | mmBtu/day
Total | 0.26 | $/mmBtu | Fixed Reservation Charge on Lateral | 1364996.88 | /month
Firm Transportation Variable Fuel Cost |  |  | Variable Cost
Fuel Supply Adjustment to NYMEX |  |  | Assume 75% CF for the month | 3937491 | mmBtu/month
Blend of Z0, 500 Leg & 800 Leg Basis* | 0.02 | $/mmBtu
|  |  | Volume Retainage Adjustment | 4016208.6903 | mmBtu/month
Pipeline Transportation Adders |  |  | Fuel Supply Cost | 16145158.9351 | /month
Commodity Price | 0.0162
EPCR | 0.019 |  | Pipeline Transportation Adders | 138599.6832 | /month
Total | 0.0352 | $/mmBtu
Retainage | 1.96%
|  |  | Total gas cost for 1 month w/ 75% CF | 17648755.4983 | /month
Interruptible Transportation Variable Fuel Cost |  |  | Interruptible Transportation Cost
Fuel Supply Adjustment to NYMEX |  |  | Variable Fuel Cost
Blend of Z0, 500 Leg & 800 Leg Basis* | 0.02 | $/mmBtu | Assume 75% CF for the month | 0 | mmBtu/month
Pipeline Transportation Adders |  |  | Volume Retainage Adjustment | 0 | mmBtu/month
IT Rate | 0 |  | Fuel Supply Cost | 0 | /month
Electric Power Recovery Cost | 0
Annual Charge Adjustment | 0 |  | Pipeline Transportation Adders | 0 | /month
Total Adjustment | 0 | $/mmBtu
|  |  | Total gas cost for 1 month w/ 75% CF | 0 | /month
Volume Adjustment
Retainage | 0% |  | Total gas cost for 1 month w/ 75% CF | 17648755.4983 | /month
*Assume blend of Tennessee Zone 0, 500 Leg & 800 Leg for Basis Differential. |  |  | *Assume blend of Tennessee Zone 0, 500 Leg & 800 Leg for Basis Differential. Please obtain from
Please obtain from Fundamentals. |  |  | Fundamentals.

## Basis Calc
|  | TGPL Zone 0 | TGPL 500 Leg | TGPL 800 Leg
|  | Basis differential | Basis differential | Basis differential
|  | to the Henry Hub | to the Henry Hub | to the Henry Hub |  | Basis Differential
|  | forecast 11/14/2012 | forecast 11/14/2012 | forecast 11/14/2012 |  | TGPL Zone 0 | 500 LEG | 800 LEG | AVG
|  |  | Eastern-most line through Mississippi | Middle leg through LA to Zone L | 2011 | -0.1 | 0.011778 | 0.10278 | 0.0048538
[5 empty] | 2012 | -0.12604 | 0.01 | 0.14048 | 0.0081469
|  | $/mmBtu | $/mmBtu | $/mmBtu | 2013 | -0.13277 | 0.010284 | 0.010284 | -0.037401
2011 | 2011-04-01 | -0.1 | 0 | 0.12 | 2014 | -0.13223 | 0.015804 | 0.015804 | -0.033539
2011 | 2011-05-01 | -0.1 | 0.01 | 0.09 | 2015 | -0.14484 | 0.025883 | 0.025883 | -0.031026
2011 | 2011-06-01 | -0.1 | 0.02 | 0.078219 | 2016 | -0.15365 | 0.033705 | 0.033705 | -0.028745
2011 | 2011-07-01 | -0.1 | 0.02 | 0.075875 | 2017 | -0.14339 | 0.03302 | 0.03302 | -0.025784
2011 | 2011-08-01 | -0.1 | 0.03 | 0.085603 | 2018 | -0.13677 | 0.03116 | 0.03116 | -0.024816
2011 | 2011-09-01 | -0.1 | 0.008 | 0.092616 | 2019 | -0.13866 | 0.031285 | 0.031285 | -0.025364
2011 | 2011-10-01 | -0.1 | 0.008 | 0.11865 | 2020 | -0.13753 | 0.037976 | 0.037976 | -0.020525
2011 | 2011-11-01 | -0.1 | 0 | 0.13416 | 2021 | -0.13656 | 0.053303 | 0.053303 | -0.0099839
2011 | 2011-12-01 | -0.1 | 0.01 | 0.12993 | 2022 | -0.1355 | 0.063242 | 0.063242 | -0.0030053
2012 | 2012-01-01 | -0.1 | 0.02 | 0.12307 | 2023 | -0.13401 | 0.050153 | 0.050153 | -0.011234
2012 | 2012-02-01 | -0.1 | 0.01 | 0.11911 | 2024 | -0.13255 | 0.0487 | 0.0487 | -0.011718
2012 | 2012-03-01 | -0.1 | 0 | 0.13517 | 2025 | -0.13362 | 0.055073 | 0.055073 | -0.0078249
2012 | 2012-04-01 | -0.1425 | 0.006 | 0.14232 | 2026 | -0.12276 | 0.060149 | 0.060149 | -0.00082007
2012 | 2012-05-01 | -0.1425 | 0.008 | 0.14315 | 2027 | -0.15684 | 0.062266 | 0.062266 | -0.01077
2012 | 2012-06-01 | -0.1425 | 0.01 | 0.14409 | 2028 | -0.16575 | 0.065559 | 0.065559 | -0.011545
2012 | 2012-07-01 | -0.1225 | 0.01 | 0.1356 | 2029 | -0.15617 | 0.068001 | 0.068001 | -0.0067233
2012 | 2012-08-01 | -0.115 | 0.02 | 0.14572 | 2030 | -0.1521 | 0.07154 | 0.07154 | -0.0030053
2012 | 2012-09-01 | -0.1075 | 0.006 | 0.14895 | 2031 | -0.14809 | 0.079746 | 0.079746 | 0.0038012
2012 | 2012-10-01 | -0.13 | 0.01 | 0.13873 | 2032 | -0.15159 | 0.079796 | 0.079796 | 0.0026689
2012 | 2012-11-01 | -0.1575 | 0.01 | 0.15931 | 2033 | -0.15478 | 0.081308 | 0.081308 | 0.0026116
2012 | 2012-12-01 | -0.1525 | 0.01 | 0.15057 | 2034 | -0.16085 | 0.082495 | 0.082495 | 0.0013807
2013 | 2013-01-01 | -0.12483 | 0.021506 | 0.021506 | 2035 | -0.16025 | 0.087805 | 0.087805 | 0.0051207
2013 | 2013-02-01 | -0.11189 | 0.028105 | 0.028105 | 2036 | -0.13539 | 0.095025 | 0.077078 | 0.012237
2013 | 2013-03-01 | -0.16504 | 0.012687 | 0.012687 | 2037 | -0.11473 | 0.10313 | 0.08286 | 0.023752
2013 | 2013-04-01 | -0.1229 | 0.0099236 | 0.0099236 | 2038 | -0.098075 | 0.11241 | 0.089064 | 0.034465
2013 | 2013-05-01 | -0.1244 | 0.0052293 | 0.0052293 | 2039 | -0.084947 | 0.12322 | 0.096009 | 0.044759
2013 | 2013-06-01 | -0.14187 | 0.0054532 | 0.0054532 | 2040 | -0.074865 | 0.13607 | 0.10401 | 0.05507
2013 | 2013-07-01 | -0.11468 | 0.0065259 | 0.0065259
2013 | 2013-08-01 | -0.12643 | 0.0057728 | 0.0057728
2013 | 2013-09-01 | -0.16363 | 0.0039064 | 0.0039064
2013 | 2013-10-01 | -0.15076 | 0.0054276 | 0.0054276
2013 | 2013-11-01 | -0.11148 | 0.011322 | 0.011322
2013 | 2013-12-01 | -0.13535 | 0.0075493 | 0.0075493
2014 | 2014-01-01 | -0.097251 | 0.010206 | 0.010206
2014 | 2014-02-01 | -0.11548 | 0.01701 | 0.01701
2014 | 2014-03-01 | -0.12988 | 0.0108 | 0.0108
2014 | 2014-04-01 | -0.12681 | 0.01458 | 0.01458
2014 | 2014-05-01 | -0.13925 | 0.01458 | 0.01458
2014 | 2014-06-01 | -0.1243 | 0.01458 | 0.01458
2014 | 2014-07-01 | -0.11376 | 0.01458 | 0.01458
2014 | 2014-08-01 | -0.092442 | 0.01458 | 0.01458
2014 | 2014-09-01 | -0.14247 | 0.021871 | 0.021871
2014 | 2014-10-01 | -0.17625 | 0.021871 | 0.021871
2014 | 2014-11-01 | -0.17594 | 0.014581 | 0.014581
2014 | 2014-12-01 | -0.15286 | 0.020413 | 0.020413
2015 | 2015-01-01 | -0.12306 | 0.020414 | 0.020414
2015 | 2015-02-01 | -0.12361 | 0.023816 | 0.023816
2015 | 2015-03-01 | -0.15525 | 0.023816 | 0.023816
2015 | 2015-04-01 | -0.14514 | 0.021872 | 0.021872
2015 | 2015-05-01 | -0.17876 | 0.029164 | 0.029164
2015 | 2015-06-01 | -0.14444 | 0.036455 | 0.036455
2015 | 2015-07-01 | -0.086702 | 0.029164 | 0.029164
2015 | 2015-08-01 | -0.13561 | 0.029164 | 0.029164
2015 | 2015-09-01 | -0.14764 | 0.029165 | 0.029165
2015 | 2015-10-01 | -0.19317 | 0.029165 | 0.029165
2015 | 2015-11-01 | -0.11983 | 0.014583 | 0.014583
2015 | 2015-12-01 | -0.18491 | 0.023819 | 0.023819
2016 | 2016-01-01 | -0.13375 | 0.023819 | 0.023819
2016 | 2016-02-01 | -0.11179 | 0.027222 | 0.027222
2016 | 2016-03-01 | -0.16304 | 0.027222 | 0.027222
2016 | 2016-04-01 | -0.12537 | 0.029167 | 0.029167
2016 | 2016-05-01 | -0.17703 | 0.036459 | 0.036459
2016 | 2016-06-01 | -0.16998 | 0.043751 | 0.043751
2016 | 2016-07-01 | -0.16348 | 0.03646 | 0.03646
2016 | 2016-08-01 | -0.14937 | 0.03646 | 0.03646
2016 | 2016-09-01 | -0.11082 | 0.043752 | 0.043752
2016 | 2016-10-01 | -0.19278 | 0.043753 | 0.043753
2016 | 2016-11-01 | -0.1251 | 0.029169 | 0.029169
2016 | 2016-12-01 | -0.22123 | 0.027224 | 0.027224
2017 | 2017-01-01 | -0.14113 | 0.027225 | 0.027225
2017 | 2017-02-01 | -0.14866 | 0.030628 | 0.030628
2017 | 2017-03-01 | -0.19355 | 0.037435 | 0.037435
2017 | 2017-04-01 | -0.17522 | 0.02917 | 0.02917
2017 | 2017-05-01 | -0.11588 | 0.036463 | 0.036463
2017 | 2017-06-01 | -0.16442 | 0.043756 | 0.043756
2017 | 2017-07-01 | -0.079341 | 0.036464 | 0.036464
2017 | 2017-08-01 | -0.07274 | 0.036464 | 0.036464
2017 | 2017-09-01 | -0.10056 | 0.036465 | 0.036465
2017 | 2017-10-01 | -0.13808 | 0.036465 | 0.036465
2017 | 2017-11-01 | -0.18925 | 0.021879 | 0.021879
2017 | 2017-12-01 | -0.20186 | 0.023824 | 0.023824
2018 | 2018-01-01 | -0.13187 | 0.023825 | 0.023825
2018 | 2018-02-01 | -0.13493 | 0.027228 | 0.027228
2018 | 2018-03-01 | -0.1743 | 0.034036 | 0.034036
2018 | 2018-04-01 | -0.15717 | 0.036467 | 0.036467
2018 | 2018-05-01 | -0.14505 | 0.036468 | 0.036468
2018 | 2018-06-01 | -0.096402 | 0.029174 | 0.029174
2018 | 2018-07-01 | -0.075852 | 0.029175 | 0.029175
2018 | 2018-08-01 | -0.07459 | 0.021881 | 0.021881
2018 | 2018-09-01 | -0.1177 | 0.036469 | 0.036469
2018 | 2018-10-01 | -0.1745 | 0.036469 | 0.036469
2018 | 2018-11-01 | -0.16904 | 0.021882 | 0.021882
2018 | 2018-12-01 | -0.1898 | 0.040846 | 0.040846
2019 | 2019-01-01 | -0.13236 | 0.040847 | 0.040847
2019 | 2019-02-01 | -0.14473 | 0.037443 | 0.037443
2019 | 2019-03-01 | -0.18185 | 0.040848 | 0.040848
2019 | 2019-04-01 | -0.16394 | 0.036472 | 0.036472
2019 | 2019-05-01 | -0.12748 | 0.029178 | 0.029178
2019 | 2019-06-01 | -0.109 | 0.029178 | 0.029178
2019 | 2019-07-01 | -0.08936 | 0.021884 | 0.021884
2019 | 2019-08-01 | -0.11955 | 0.021884 | 0.021884
2019 | 2019-09-01 | -0.10149 | 0.029179 | 0.029179
2019 | 2019-10-01 | -0.14818 | 0.029179 | 0.029179
2019 | 2019-11-01 | -0.16099 | 0.021884 | 0.021884
2019 | 2019-12-01 | -0.18504 | 0.037447 | 0.037447
2020 | 2020-01-01 | -0.1295 | 0.040852 | 0.040852
2020 | 2020-02-01 | -0.14291 | 0.034044 | 0.034044
2020 | 2020-03-01 | -0.18015 | 0.037448 | 0.037448
2020 | 2020-04-01 | -0.16269 | 0.036476 | 0.036476
2020 | 2020-05-01 | -0.12683 | 0.036476 | 0.036476
2020 | 2020-06-01 | -0.10904 | 0.036477 | 0.036477
2020 | 2020-07-01 | -0.087004 | 0.036477 | 0.036477
2020 | 2020-08-01 | -0.11752 | 0.029182 | 0.029182
2020 | 2020-09-01 | -0.10026 | 0.036478 | 0.036478
2020 | 2020-10-01 | -0.14907 | 0.043774 | 0.043774
2020 | 2020-11-01 | -0.1603 | 0.043774 | 0.043774
2020 | 2020-12-01 | -0.18504 | 0.044261 | 0.044261
2021 | 2021-01-01 | -0.12744 | 0.044261 | 0.044261
2021 | 2021-02-01 | -0.14112 | 0.044262 | 0.044262
2021 | 2021-03-01 | -0.17841 | 0.047667 | 0.047667
2021 | 2021-04-01 | -0.16265 | 0.058368 | 0.058368
2021 | 2021-05-01 | -0.12649 | 0.058369 | 0.058369
2021 | 2021-06-01 | -0.10792 | 0.05837 | 0.05837
2021 | 2021-07-01 | -0.087024 | 0.05837 | 0.05837
2021 | 2021-08-01 | -0.11692 | 0.051074 | 0.051074
2021 | 2021-09-01 | -0.10157 | 0.051075 | 0.051075
2021 | 2021-10-01 | -0.14831 | 0.058372 | 0.058372
2021 | 2021-11-01 | -0.15954 | 0.058373 | 0.058373
2021 | 2021-12-01 | -0.18131 | 0.051076 | 0.051076
2022 | 2022-01-01 | -0.12516 | 0.051077 | 0.051077
2022 | 2022-02-01 | -0.13887 | 0.051078 | 0.051078
2022 | 2022-03-01 | -0.17699 | 0.047673 | 0.047673
2022 | 2022-04-01 | -0.16141 | 0.065672 | 0.065672
2022 | 2022-05-01 | -0.12728 | 0.065673 | 0.065673
2022 | 2022-06-01 | -0.10882 | 0.072971 | 0.072971
2022 | 2022-07-01 | -0.086476 | 0.072972 | 0.072972
2022 | 2022-08-01 | -0.1167 | 0.072972 | 0.072972
2022 | 2022-09-01 | -0.099787 | 0.065676 | 0.065676
2022 | 2022-10-01 | -0.14781 | 0.065676 | 0.065676
2022 | 2022-11-01 | -0.15548 | 0.072974 | 0.072974
2022 | 2022-12-01 | -0.18121 | 0.054488 | 0.054488
2023 | 2023-01-01 | -0.12487 | 0.054489 | 0.054489
2023 | 2023-02-01 | -0.1375 | 0.054489 | 0.054489
2023 | 2023-03-01 | -0.17392 | 0.051084 | 0.051084
2023 | 2023-04-01 | -0.15878 | 0.058382 | 0.058382
2023 | 2023-05-01 | -0.1255 | 0.043787 | 0.043787
2023 | 2023-06-01 | -0.10594 | 0.065682 | 0.065682
2023 | 2023-07-01 | -0.086754 | 0.058384 | 0.058384
2023 | 2023-08-01 | -0.11711 | 0.051087 | 0.051087
2023 | 2023-09-01 | -0.099335 | 0.043789 | 0.043789
2023 | 2023-10-01 | -0.14721 | 0.043789 | 0.043789
2023 | 2023-11-01 | -0.1532 | 0.029193 | 0.029193
2023 | 2023-12-01 | -0.17798 | 0.047683 | 0.047683
2024 | 2024-01-01 | -0.12234 | 0.047683 | 0.047683
2024 | 2024-02-01 | -0.13477 | 0.05109 | 0.05109
2024 | 2024-03-01 | -0.17299 | 0.047684 | 0.047684
2024 | 2024-04-01 | -0.15821 | 0.036493 | 0.036493
2024 | 2024-05-01 | -0.12336 | 0.036494 | 0.036494
2024 | 2024-06-01 | -0.1039 | 0.065689 | 0.065689
2024 | 2024-07-01 | -0.084633 | 0.06569 | 0.06569
2024 | 2024-08-01 | -0.11522 | 0.07299 | 0.07299
2024 | 2024-09-01 | -0.097908 | 0.036495 | 0.036495
2024 | 2024-10-01 | -0.14709 | 0.036496 | 0.036496
2024 | 2024-11-01 | -0.15291 | 0.036496 | 0.036496
2024 | 2024-12-01 | -0.17733 | 0.051095 | 0.051095
2025 | 2025-01-01 | -0.12183 | 0.051095 | 0.051095
2025 | 2025-02-01 | -0.13502 | 0.051096 | 0.051096
2025 | 2025-03-01 | -0.17312 | 0.044284 | 0.044284
2025 | 2025-04-01 | -0.15965 | 0.043797 | 0.043797
2025 | 2025-05-01 | -0.12335 | 0.058397 | 0.058397
2025 | 2025-06-01 | -0.10545 | 0.065697 | 0.065697
2025 | 2025-07-01 | -0.086527 | 0.065698 | 0.065698
2025 | 2025-08-01 | -0.11722 | 0.065699 | 0.065699
2025 | 2025-09-01 | -0.099547 | 0.051099 | 0.051099
2025 | 2025-10-01 | -0.14801 | 0.0511 | 0.0511
2025 | 2025-11-01 | -0.15345 | 0.058401 | 0.058401
2025 | 2025-12-01 | -0.18027 | 0.054508 | 0.054508
2026 | 2026-01-01 | -0.17875 | 0.057915 | 0.057915
2026 | 2026-02-01 | -0.18908 | 0.057916 | 0.057916
2026 | 2026-03-01 | -0.22634 | 0.047696 | 0.047696
2026 | 2026-04-01 | -0.14247 | 0.051103 | 0.051103
2026 | 2026-05-01 | -0.081144 | 0.051104 | 0.051104
2026 | 2026-06-01 | -0.03873 | 0.080306 | 0.080306
2026 | 2026-07-01 | -0.069976 | 0.073007 | 0.073007
2026 | 2026-08-01 | -0.050059 | 0.065707 | 0.065707
2026 | 2026-09-01 | -0.070485 | 0.065707 | 0.065707
2026 | 2026-10-01 | -0.12321 | 0.051106 | 0.051106
2026 | 2026-11-01 | -0.10533 | 0.065708 | 0.065708
2026 | 2026-12-01 | -0.19754 | 0.054514 | 0.054514
2027 | 2027-01-01 | -0.19814 | 0.061329 | 0.061329
2027 | 2027-02-01 | -0.19899 | 0.057923 | 0.057923
2027 | 2027-03-01 | -0.23632 | 0.044294 | 0.044294
2027 | 2027-04-01 | -0.19151 | 0.051109 | 0.051109
2027 | 2027-05-01 | -0.15057 | 0.05111 | 0.05111
2027 | 2027-06-01 | -0.079687 | 0.080316 | 0.080316
2027 | 2027-07-01 | -0.10051 | 0.073015 | 0.073015
2027 | 2027-08-01 | -0.10929 | 0.080318 | 0.080318
2027 | 2027-09-01 | -0.11201 | 0.065715 | 0.065715
2027 | 2027-10-01 | -0.14402 | 0.058414 | 0.058414
2027 | 2027-11-01 | -0.15537 | 0.065716 | 0.065716
2027 | 2027-12-01 | -0.20567 | 0.057928 | 0.057928
2028 | 2028-01-01 | -0.20543 | 0.064744 | 0.064744
2028 | 2028-02-01 | -0.20501 | 0.061337 | 0.061337
2028 | 2028-03-01 | -0.25537 | 0.047707 | 0.047707
2028 | 2028-04-01 | -0.22932 | 0.058417 | 0.058417
2028 | 2028-05-01 | -0.15942 | 0.058418 | 0.058418
2028 | 2028-06-01 | -0.099087 | 0.080326 | 0.080326
2028 | 2028-07-01 | -0.099502 | 0.080326 | 0.080326
2028 | 2028-08-01 | -0.098945 | 0.080327 | 0.080327
2028 | 2028-09-01 | -0.15311 | 0.073025 | 0.073025
2028 | 2028-10-01 | -0.16326 | 0.058421 | 0.058421
2028 | 2028-11-01 | -0.11586 | 0.065724 | 0.065724
2028 | 2028-12-01 | -0.20474 | 0.057935 | 0.057935
2029 | 2029-01-01 | -0.17416 | 0.064752 | 0.064752
2029 | 2029-02-01 | -0.17411 | 0.061344 | 0.061344
2029 | 2029-03-01 | -0.21605 | 0.044305 | 0.044305
2029 | 2029-04-01 | -0.20968 | 0.065728 | 0.065728
2029 | 2029-05-01 | -0.13175 | 0.065728 | 0.065728
2029 | 2029-06-01 | -0.10993 | 0.073032 | 0.073032
2029 | 2029-07-01 | -0.12107 | 0.073033 | 0.073033
2029 | 2029-08-01 | -0.10022 | 0.080337 | 0.080337
2029 | 2029-09-01 | -0.153 | 0.080338 | 0.080338
2029 | 2029-10-01 | -0.13421 | 0.073035 | 0.073035
2029 | 2029-11-01 | -0.13913 | 0.073036 | 0.073036
2029 | 2029-12-01 | -0.21076 | 0.061351 | 0.061351
2030 | 2030-01-01 | -0.16988 | 0.068168 | 0.068168
2030 | 2030-02-01 | -0.17972 | 0.068169 | 0.068169
2030 | 2030-03-01 | -0.21035 | 0.051127 | 0.051127
2030 | 2030-04-01 | -0.22229 | 0.080343 | 0.080343
2030 | 2030-05-01 | -0.13997 | 0.080344 | 0.080344
2030 | 2030-06-01 | -0.096244 | 0.073041 | 0.073041
2030 | 2030-07-01 | -0.10606 | 0.073041 | 0.073041
2030 | 2030-08-01 | -0.084108 | 0.065738 | 0.065738
2030 | 2030-09-01 | -0.12817 | 0.073043 | 0.073043
2030 | 2030-10-01 | -0.14016 | 0.080348 | 0.080348
2030 | 2030-11-01 | -0.13816 | 0.080349 | 0.080349
2030 | 2030-12-01 | -0.21003 | 0.064767 | 0.064767
2031 | 2031-01-01 | -0.16925 | 0.071585 | 0.071585
2031 | 2031-02-01 | -0.17921 | 0.071586 | 0.071586
2031 | 2031-03-01 | -0.20261 | 0.051133 | 0.051133
2031 | 2031-04-01 | -0.20332 | 0.080353 | 0.080353
2031 | 2031-05-01 | -0.13853 | 0.094963 | 0.094963
2031 | 2031-06-01 | -0.085065 | 0.087659 | 0.087659
2031 | 2031-07-01 | -0.093983 | 0.080355 | 0.080355
2031 | 2031-08-01 | -0.070698 | 0.087661 | 0.087661
2031 | 2031-09-01 | -0.12709 | 0.087662 | 0.087662
2031 | 2031-10-01 | -0.13909 | 0.094968 | 0.094968
2031 | 2031-11-01 | -0.14661 | 0.087664 | 0.087664
2031 | 2031-12-01 | -0.22161 | 0.061365 | 0.061365
2032 | 2032-01-01 | -0.15793 | 0.068184 | 0.068184
2032 | 2032-02-01 | -0.1779 | 0.064776 | 0.064776
2032 | 2032-03-01 | -0.22418 | 0.051139 | 0.051139
2032 | 2032-04-01 | -0.21324 | 0.087668 | 0.087668
2032 | 2032-05-01 | -0.14695 | 0.10228 | 0.10228
2032 | 2032-06-01 | -0.10232 | 0.080364 | 0.080364
2032 | 2032-07-01 | -0.080684 | 0.087671 | 0.087671
2032 | 2032-08-01 | -0.057034 | 0.087672 | 0.087672
2032 | 2032-09-01 | -0.12312 | 0.080366 | 0.080366
2032 | 2032-10-01 | -0.15583 | 0.09498 | 0.09498
2032 | 2032-11-01 | -0.16186 | 0.087674 | 0.087674
2032 | 2032-12-01 | -0.21799 | 0.064782 | 0.064782
2033 | 2033-01-01 | -0.16754 | 0.068192 | 0.068192
2033 | 2033-02-01 | -0.17719 | 0.064784 | 0.064784
2033 | 2033-03-01 | -0.22304 | 0.051145 | 0.051145
2033 | 2033-04-01 | -0.21051 | 0.087679 | 0.087679
2033 | 2033-05-01 | -0.15302 | 0.094986 | 0.094986
2033 | 2033-06-01 | -0.10807 | 0.094987 | 0.094987
2033 | 2033-07-01 | -0.097327 | 0.094988 | 0.094988
2033 | 2033-08-01 | -0.073501 | 0.1023 | 0.1023
2033 | 2033-09-01 | -0.1117 | 0.080376 | 0.080376
2033 | 2033-10-01 | -0.15465 | 0.087684 | 0.087684
2033 | 2033-11-01 | -0.16139 | 0.080378 | 0.080378
2033 | 2033-12-01 | -0.21943 | 0.0682 | 0.0682
2034 | 2034-01-01 | -0.18673 | 0.071611 | 0.071611
2034 | 2034-02-01 | -0.1765 | 0.064791 | 0.064791
2034 | 2034-03-01 | -0.24316 | 0.054562 | 0.054562
2034 | 2034-04-01 | -0.19395 | 0.080382 | 0.080382
2034 | 2034-05-01 | -0.14455 | 0.08769 | 0.08769
2034 | 2034-06-01 | -0.11823 | 0.10961 | 0.10961
2034 | 2034-07-01 | -0.097151 | 0.094999 | 0.094999
2034 | 2034-08-01 | -0.072216 | 0.095 | 0.095
2034 | 2034-09-01 | -0.12979 | 0.080386 | 0.080386
2034 | 2034-10-01 | -0.16511 | 0.087694 | 0.087694
2034 | 2034-11-01 | -0.18077 | 0.095003 | 0.095003
2034 | 2034-12-01 | -0.22201 | 0.068208 | 0.068208
2035 | 2035-01-01 | -0.18635 | 0.07503 | 0.07503
2035 | 2035-02-01 | -0.17583 | 0.068209 | 0.068209
2035 | 2035-03-01 | -0.24307 | 0.061389 | 0.061389
2035 | 2035-04-01 | -0.19303 | 0.0877 | 0.0877
2035 | 2035-05-01 | -0.14338 | 0.095009 | 0.095009
2035 | 2035-06-01 | -0.11754 | 0.10963 | 0.10963
2035 | 2035-07-01 | -0.096748 | 0.10501 | 0.10501
2035 | 2035-08-01 | -0.071637 | 0.095012 | 0.095012
2035 | 2035-09-01 | -0.12796 | 0.095013 | 0.095013
2035 | 2035-10-01 | -0.16405 | 0.095014 | 0.095014
2035 | 2035-11-01 | -0.18203 | 0.095015 | 0.095015
2035 | 2035-12-01 | -0.22134 | 0.071627 | 0.071627