{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["LGE Section 1-4","Excel LGE Section 5","LGE Section 6-7"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"LGE Section 1-4","index":0,"n_rows":45,"n_cols":8,"rows_kept":45,"cut":false,"hidden":false,"merged":[[34,6,34,8],[30,1,30,3],[31,1,31,3],[30,6,30,8],[31,6,31,8],[34,1,34,3],[33,0,33,8],[0,0,0,8],[10,0,10,8],[11,0,11,3],[28,3,28,5],[29,6,29,8],[29,1,29,3],[1,0,1,8],[20,0,21,8],[25,2,25,6],[26,0,26,1],[26,5,26,6],[3,0,3,8],[4,0,4,3],[5,0,5,3],[4,5,4,8],[5,5,5,8],[24,0,24,8],[6,0,6,3],[7,0,7,3],[16,0,16,3],[16,5,16,8],[17,0,17,3],[18,0,18,3],[17,5,17,8],[18,5,18,8],[6,5,6,8],[7,5,7,8],[15,0,15,3],[15,5,15,8],[14,0,14,8],[11,5,11,8],[43,0,43,8],[44,3,44,5],[35,6,35,8],[36,6,36,8],[35,1,35,3],[36,1,36,3],[41,1,41,8],[38,1,38,8],[39,1,39,8],[40,1,40,8],[37,0,37,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 1: CONTACT INFORMATION"]
["UTILITY NAME",null,null,null,null,"LOUISVILLE GAS AND ELECTRIC"]
["REPORT PREPARD BY",null,null,null,null,"Tiffany Koller (Dir. Substations & Asset Mgmt)"]
["E-MAIL ADDRESS OF PREPARER",null,null,null,null,"Tiffany.Koller@lge-ku.com"]
["PHONE NUMBER OF PREPARER",null,null,null,null,"(502) 364-8633"]
[]
[]
["SECTION 2: REPORTING YEAR"]
["CALENDAR YEAR OF REPORT",null,null,null,null,2022]
[]
[]
["SECTION 3: MAJOR EVENT DAYS (MED)"]
["TMED",null,null,null,null,3.2589999999999999]
["FIRST DATE USED TO DETERMINE TMED",null,null,null,null,"2017-01-01"]
["LAST DATE USED TO DETERMINE TMED",null,null,null,null,"2021-12-31"]
["NUMBER OF MED IN REPORTING YEAR",null,null,null,null,7]
[]
["NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years.  If five years of data are not available, then utilities should use what is available until five years are accumulated.        \n"]
[]
[]
[]
["SECTION 4: SYSTEM RELIABILTIY INFORMATION AND RESULTS"]
[null,null,"System-wide Information"]
["TOTAL CUSTOMERS",null,442875,null,null,"TOTAL CIRCUITS",null,625]
[]
[null,null,null,"Excluding MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",77.489999999999995,null,null,null,"SAIDI",76.12]
["SAIFI",0.88100000000000001,null,null,null,"SAIFI",0.92100000000000004]
[]
["Including MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",186.93,null,null,null,"SAIDI",167.09]
["SAIFI",1.103,null,null,null,"SAIFI",1.1519999999999999]
["Notes:  "]
["1)","All duration indices (SAIDI) are to be reported in units of minutes."]
["2)","Reports are due on the first business day of May of each year"]
["3)","Reports cover the calendar year ending in the December before the reports are due."]
["4)","IEEE 1366 (latest version) is used to define SAIDI, SAIFI, and TMED"]
[]
["SECTION 5: CIRCUIT REPORTING"]
[null,null,null,"BEGIN ON NEXT PAGE"]

{"sheet":"Excel LGE Section 5","index":1,"n_rows":256,"n_cols":22,"rows_kept":256,"cut":false,"hidden":false,"merged":[]}
["Substation Name","Substation Location   \n(County - Road - Town)","Circuit\nNumber","Circuit Location\n (Town - Road - General Area)","Total Circuit Length (Miles)","Average 2022 OMS Custs","Date of Last Circuit Trim (VM)","Animal","Construction","Lightning","Non-Company","Other/Unknown","Overload","Planned Work","Trees","Vehicle","Utility Equipment","2018-2022 SAIDI Average","2022 SAIDI","2018-2022 SAIFI Average","2022 SAIFI","LIST OF CORRECTION ACTION, IF ANY, TAKEN OR TO BE TAKEN"]
["ASHBY","Jefferson - 5400 Vesper Ln - Lousivlle","AB1203","Louisville - Ashby Ln & Bethany Ln - W of Substation",17.387285827020204,1213,"2022-09-18",3.093783237054493E-2,0,1.2825592792642488E-3,0,1.2147817563763008E-2,0,3.6182769910950763E-2,0.35582156785051405,0,0.56362745302496298,76.869475848753595,73.620743771781775,1.0478426885993404,1.1648465076987209,"Trees Trimmed in 2022"]
["ASHBY","Jefferson - 5400 Vesper Ln - Lousivlle","AB1207","Louisville - Torrington Rd & Derring Rd - S of Substation",16.103473011363636,1646,"2022-09-18",3.7990750078241821E-3,0,0,5.7956903246745721E-5,0,0,1.212748200438154E-2,0.1480016459760522,0,0.83601384010849533,57.577264760544708,182.34045898985192,0.78560402365286852,2.0996076885653649,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1289","Louisivlle - Shelbyville rd & Upton Ln - E of Substation",41.782700284090907,2605,"2020-02-29",0,0,0,0,1.4899026704885908E-3,0,1.4145978072519393E-2,0.5507862475505676,0,0.43357787170642442,38.186818928698997,28.100404451087158,0.56113291150202826,1.0488092577403614,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1293","Louisville - New English Station Rd - NE of Substation",4.414556029040404,146,"2020-11-21",0.69419766796224325,0,0,0,7.2182121043864516E-3,0,0.29858411993337031,0,0,0,93.775740869783363,98.215184966731925,1.4938275799818146,0.76255707762557046,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1294","Louisville - Old Shelbyville Rd - W of Substation",6.6687927714646449,494,"2020-02-29",0,0.14549007028083172,0,0,5.1519835136527563E-3,0,0.55385766916489265,0.26090422171026412,0,3.4596055330358789E-2,48.351732960403638,54.825707204050303,0.54775240302940509,0.24853595498266051,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1295","Louisville - N English Station Rd & Avoca Rd - N of Substation",20.23056423611111,844,"2020-03-28",2.7365003478602135E-3,0,9.6330520719981451E-4,0,3.987726778100862E-2,0,0.46835542394348612,0.48568421428189168,0,2.3832884385536152E-3,35.928448858405659,64.131873064482903,0.45913232516061575,0.529818767644616,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1296","Louisville - ShelbyvilleRd  & N Beckley Station - NE of Substation",36.67894933712121,1592,"2020-03-08",3.1354824205924285E-4,0,0,0,0.64540651825383211,0,0.32214419669531985,1.5541343997917567E-2,0,1.6594392810871252E-2,58.439908334852177,106.15042251789663,0.43226979351897948,0.38165605676308506,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1372","Louisville - W Shipp Ave - E of Substation",1.2148083964646461,1992,"2019-02-09",0,0,0,0,0,0,0,0,0,1,18.746551673669718,55.909889557730921,0.40122004096016528,1.0015060240963856,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1373","Louisville - S 12 St - N of Substation",3.2335069444444451,987,"2019-02-09",0,0,0,1,0,0,0,0,0,0,175.92324474582358,472.71930959206799,1.2363759803106584,2.9655521783181347,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1374","Louisville - S 7th St & Algonquin Pky - SE of Substation",3.5850670770202022,451,"2019-02-09",0,0,0,0,0,0,0,0.92744504940512196,0,7.2554950594878001E-2,40.807134674340425,54.977716184035522,0.57666726694397952,1.0000000000000004,"Tree Trim Scheduled for 2023"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1377","Louisville - W Hill St & S 10th St - N of Substation",1.177578282828283,5,"2019-02-09",0,0,0,0,0.23129251700680273,0,0,0.76870748299319724,0,0,211.23733315999999,117.43666640000001,1.3199999999999998,2.4,"Tree Trim Scheduled for 2023"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1380","Louisville - S 7th St - N of Substation",2.9800303030303024,1227,"2019-02-09",0,0,0,0.17109688453183994,7.5853881069360297E-3,0,8.9711434581276651E-4,0,0,0.82042061301541125,101.39662961763653,363.320926221516,0.94184189079054614,3.4425427872860643,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1440","Louisville - S 13st - N of Substation",0.82289535984848472,1,"2019-02-09",0,0.83122362869198307,0,0,0,0,0,0,0,0.16877637130801687,94.786666400000001,473.93333200000001,0.4,2,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1441","Louisville - Bernheim Ln & 7th St Rd - SW of Substation",4.8194326073232316,48,"2019-02-09",0,0,0,0,0.96135680549592095,0,0,3.8643194504079006E-2,0,0,26.82206669650693,49.53333329787241,0.49015678982046118,1.063829787234043,"Continue to Monitor"]
["ASHBOTTOM","Jefferson - 8113 Grade Ln - Louisville","AS1418","Louisville - Outer Loop - S of Substation",9.1943494318181838,59,"2021-12-04",0,4.9423393739703456E-3,0,0,0.69007413509060955,0,2.193163097199341E-2,0.28305189456342666,0,0,75.560004516334146,110.91707835485265,0.64682477702441388,0.93248926914988561,"Continue to Monitor"]
["BRANDENBURG","Meade - Weldon Church Rd. - Brandenburg","BB1102","Brandenburg - E Broadway St - W of Substation",14.722278566919195,847,"2020-11-17",2.1556166685391339E-2,0,0.38722456416293394,0,1.2460861367422004E-2,0,7.6171960863809771E-2,0.35655843806937249,0,0.14602800885107048,84.458196929048711,194.78413543257605,1.1494035615112319,3.1779316301534513,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1217","Louisville - Robarus Ln - N of Substation",2.3255653409090908,68,"2021-05-08",1.3875748975086723E-2,0,0,0,0,0,0.96058025859350371,2.5543992431409649E-2,0,0,30.283205012864748,46.600728165387856,0.25077095386195664,0.22016197783461208,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1219","Louisivlle - Pinewood Rd & Produce Rd - SE of Substation",8.9693585858585845,961,"2021-05-08",7.1565648488725415E-3,0,0,0,3.7981768750999518E-4,0,0.12142171757556373,1.0395010395010396E-3,0,0.87000239884855268,30.818715940526829,51.963455130155332,0.28932373722928439,0.2015359491410891,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1220","Louisville - Popular Level Rd. & Gilmore Ln - W of Substation",13.656088226010096,1113,"2021-05-08",5.3817942061235424E-3,1.1826760621420036E-2,0.11602587876540157,0,0.26589195203362592,0,7.0523756541805746E-2,0.24364775209131745,0,0.28670210574030575,47.607893863191727,78.211169205231798,0.53237289695069567,0.69850836339639655,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1221","Louisville - Robards Ln - N of Substation",2.6597739898989898,64,"2021-05-08",0,0,1,0,0,0,0,0,0,0,22.375971503687424,28.132307692307698,0.14339438339438346,0.18461538461538499,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1222","Louisville - Bishop Ln - E of Substation",1.2073199179292928,44,"2021-05-08",0,0,0,0,0,0,0,0,0,1,0.21600000000000003,1.08,4.4444444444444401E-3,2.2222222222222199E-2,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1223","Louisville - Bishop Ln & Gilmore Ln - SW of Substation",8.8423478535353528,68,"2021-05-08",1.6531241244045952E-2,0,0,0.28243205379658165,0.45951246847856542,0,0,0.17960212944802464,0,6.1922107032782295E-2,23.620684943669627,52.033866328936853,0.42941014124708782,0.5232797466812813,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1224","Louisville - Popular Level Rd & Preston Hwy - W of Substation",13.720039614898987,1217,"2021-05-08",7.7485017199191457E-3,0,0,0,2.9274087733607575E-2,0,5.2945139898577964E-2,0.22711798290719529,0,0.68291428774070007,68.800667023526771,42.946488982766716,0.96225936024238035,1.1200097005448282,"Continue to Monitor"]
["BROOK","Jefferson - 913 S 1st Street - Louisivlle","BK0002","Louisville - S Brook St & S Floyd St - E of Substation",2.0708865214646464,196,"2020-02-08",0,0,0.75126779991074688,0,0,0,0.17573735242809038,8.1646314252099474E-3,0,6.4830216235952781E-2,53.502984532250068,94.308682661231018,0.32950198651814672,0.33172806432197632,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1176","Louisville - I-264 West - N of Substation",12.956057922979795,1886,"2020-07-18",4.4196425169610134E-4,0,0,0,2.1420872735462382E-4,1.5483988955973756E-2,0.9556731869093914,7.4769852619315531E-3,0,2.0709665893652564E-2,13.688847730454219,43.408684846452651,9.7809324038065665E-2,0.34128273991663705,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1179","Louisville - Breckenridge Ln - S of Substation",11.3705,2110,"2020-11-14",2.399610960083548E-2,0,0,9.766655771423105E-2,1.8184427242360707E-2,7.5057598635171439E-3,0.67377647743488767,8.8367068727727857E-2,0,9.0503599416440123E-2,56.111229267741621,72.468540206915577,0.9437915528438342,0.95311559190891304,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1182","Louisville - I - 264 East - E of Substation",5.739458806818182,225,"2020-08-01",0,0,0,0,0,0,0.9035806132542038,0,0,9.641938674579624E-2,98.399365779646018,112.2842182876106,0.84601769911504421,1.0973451327433628,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1184","Louisville - I - 264 East - E of Substation",1.2969954229797982,9,"2020-07-18",0,0,0,0,0,0,0,0,0,1,157.31777777777779,17.966666666666701,0.48888888888888893,1,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1185","Louisville - Taylorsville Rd - S of Substation",14.88382039141414,1827,"2021-01-16",1.2240831669896406E-2,3.9212186557486921E-3,1.1601561930849591E-3,0,3.3333090495825626E-2,1.2311861640901607E-3,0.62115163259656436,0.18643910363819155,0,0.14052278058659828,145.45562212880554,188.23458077891465,1.3613979728226635,2.3348753844644761,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1186","Louisville - Richland Dr & Hunsinger Ln - S of Substation",13.133689551767677,1675,"2020-09-19",9.0364770156172395E-3,0,0,0,2.3545426117028124E-3,6.4382024538748781E-5,1.2375144859555213E-2,0.63424111987932974,0,0.34192833360925629,67.619076786083696,60.148604700024876,0.81958987623099355,2.162381777404605,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1187","Louisville - Browns Ln - NE of Substation",2.0233846275252527,307,"2020-07-18",0,0,0,0,0,0,0.31383582371855495,0,0,0.6861641762814451,46.155064910899718,68.808008651508089,0.34925733621480809,1.061688311688312,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1352","Louisville - Brekenridge Ln - NW of Substation",3.4284777462121223,106,"2020-07-18",0,0,0,0,0,0,1.3761467889908258E-2,0,0,0.98623853211009171,47.517508065994306,154.24000667701259,0.58183721745581229,1.0282153983088562,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1354","Louisville - Taylorsville Rd - S of Substation",9.2731595643939411,34,"2020-09-19",5.4694277846931462E-3,0,0,0,8.6190637848440277E-2,0,2.7158537965372865E-2,0.88118139640149362,0,0,117.61851211544118,93.23823526470585,0.91625700280112066,1.1470588235294124,"Continue to Monitor"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1276","Louisville - Commonwealth Dr - SE of Substation",5.0307318497474736,142,"2021-10-23",0,0,0,0,0.18645251396648044,0,0,0.48324022346368717,0,0.33030726256983239,6.6305330584671394,9.9009750017555564,3.230098334837788E-2,6.9207674307237149E-2,"Continue to Monitor"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1279","Louisville - Watterson Way - N of Substation",13.775650726010101,868,"2021-11-13",5.0702535126756335E-2,0.22406120306015301,0,0,7.030351517575878E-2,0,0.65413270663533174,8.0004000200009997E-4,0,0,38.811282933751592,23.033721018516697,0.32178902795068404,0.68311873916202071,"Continue to Monitor"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1281","Louisville - Bluegrass Parkway - E of Substation",10.180152304292935,169,"2021-10-23",4.8135206446552094E-2,0.34804725569897071,0,1.9586869191090827E-2,1.6021298343198077E-2,0,5.9663885521405308E-3,0.26855879626328177,0,0.29368418550476599,75.530729707345373,247.43759159777099,0.94425684315002645,3.2140918097625453,"Continue to Monitor"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1283","Louisivlle - Blankenbaker Rd - S of Substation",8.0255350378787877,439,"2021-10-23",1.1205188521731387E-2,2.6417530554545521E-3,5.0460451621042008E-4,0,2.4488160345505681E-3,0,3.962629583181828E-3,0,0,0.97923700828887128,73.092488811208,306.17521759375779,0.68093069845833587,2.9043282542968272,"Continue to Monitor"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1285","Louisivlle - Moser Rd - NW of Substation",11.590669507575758,588,"2021-10-23",0,0,0,0,4.3568576669903956E-3,0,2.6923491960720837E-2,0.33790601057515918,0,0.63081363979712957,39.393580390416069,84.547485798485127,0.75587847887667559,1.1807580007213394,"Continue to Monitor"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1341","Louisville - S 20th St & W Market St - S of Substation",5.6951377840909103,1420,"2023-03-18",0,0,0,0,0.12204576578168486,0,2.3457171886734109E-2,0.65526571542165479,0,0.19923134690992622,175.61311095101593,278.61765908471034,1.7810074105313842,3.3658301794611809,"Trees Trimmed in 2023"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1343","Louisville - S 20th St & W Chestnut St - S of Substation",2.7314938446969688,2470,"2023-03-18",0,0,0,0,0,0,0,0,0,1,36.552792167611337,153.45626853036438,0.44931174089068826,2.0927125506072874,"Continue to Monitor"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1345","Louiville - S 20th St & W Broadway - S of Substation",2.7884638573232325,1031,"2023-03-18",0,0,0,0,0,0,0,0,0,1,46.102864926770124,134.66710313385062,0.9003879728419012,3.0019398642095054,"Continue to Monitor"]
["CROP","Jefferson - 116 N 26th St - Louisville","CB0002","Louisville - Duncan St - E of Substation",3.6496584595959596,604,"2023-02-18",0,3.1123368719473674E-3,7.8393910913208936E-2,0,2.6470271019829593E-2,0,0,0.88643051939047501,0,5.5929618045390816E-3,48.575588311381253,91.958093681537008,0.63042111081083685,1.4615626764834533,"Trees Trimmed in 2023"]
["CROP","Jefferson - 116 N 26th St - Louisville","CB0004","Louisville - W Market St - W of Substation",2.5368532196969698,374,"2023-02-18",0,0,0,0,0.61985879295684498,8.3979019575996707E-3,2.1276595744680851E-2,3.0391042237911895E-2,0,0.32007566710296265,90.591024444107859,271.28559630627882,0.81161673526660894,2.4309862801178133,"Continue to Monitor"]
["CENTERFIELD","Oldham - 4210 Hwy 393 - Centerfield","CF1201","Centerfield - Dawkins Rd - N of Substation",52.849264678030295,544,"2022-07-31",8.1003723333292907E-2,0,0,0,6.5358446630201447E-2,1.2310043297393666E-3,0.35828290056153206,0.48790826288916106,0,6.2156622560731569E-3,163.54768060589149,162.86682629128779,1.181264683013789,2.0377124178457575,"Trees Trimmed in 2022"]
["CENTERFIELD","Oldham - 4210 Hwy 393 - Centerfield","CF1203","Centerfield - S Camedn Ln - S of Substation",62.56318276515151,1207,"2021-01-30",0.13376428586517947,0,0,0,0,0,0.18011280816274794,0.38901493546274585,0,0.29710797050932675,117.73843756771396,118.06905406796307,1.3185373559989695,0.99621289253166301,"Continue to Monitor"]
["CENTERFIELD","Oldham - 4210 Hwy 393 - Centerfield","CF1205","Centerfield - Elder Park Rd - NE of Substation",27.318040719696967,793,"2023-03-31",8.127069652578997E-2,0,0,0,4.3537873138816061E-3,0,0.40382780490542741,0.35691434344406225,0,0.15363336781083878,117.34109135436923,128.45988927332922,1.1532449189244165,1.8757670352125289,"Trees Trimmed in 2023"]
["CAMPGROUND","Jefferson - 4300 Campground Rd. - Louisville","CG1435","Shepherdsville - Schenk Ln - N of Substation",0.20933964646464648,1,"2021-07-31",0,0.25813449023861174,0.74186550976138832,0,0,0,0,0,0,0,92.229999800000002,461.14999899999998,0.6,3,"Continue to Monitor"]
["CLARKS LANE","Jefferson - 934 Clarks Ln - Louisville","CK0001","Louisville - Clarks Ln - E of Substation",0.85711947601010097,149,"2019-09-28",0,0,0,0,0,0,0.28980540937461757,0.14808468975645575,0,0.56210990086892665,22.652933789456032,54.578847120089449,0.19967283750169657,0.60805369127516784,"Continue to Monitor"]
["CLARKS LANE","Jefferson - 934 Clarks Ln - Louisville","CK0002","Louisville - Pindell Ave - S of Substation",2.96780855429293,456,"2019-09-28",0,0,0,0,0,2.9117923319955597E-2,0.56084023567586028,0.39441550678848947,0,1.5626334215694645E-2,39.835130706785293,51.641282959137499,0.25424758915912438,0.42778126704124603,"Tree Trim Scheduled for 2023"]
["CLARKS LANE","Jefferson - 934 Clarks Ln - Louisville","CK0003","Louisville - Eastern PKY - W of Substation",1.3704869002525251,221,"2019-09-28",0,0,0,0,0,5.9574468085106386E-2,0.22251600908903119,0.7179095228258624,0,0,27.806640641861321,24.366440416289603,0.22933023521258816,0.24886877828054299,"Tree Trim Scheduled for 2023"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1227","Louisville - Frankfort Ave, Clifton Ave, & Ewing Ave - E of Substation",3.138836174242424,648,"2022-05-08",0.68158070997990627,0,0,0,0,0,0.11898861352980576,0.19943067649028801,0,0,33.957349449581372,46.046387121343983,0.48137810947826409,0.54589686521889913,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1232","Louisville - Frankfort Ave, Story Ave, & E Main St - W of Substation",13.460102904040401,1809,"2022-08-06",7.9547978313410414E-2,0,0,3.490321597317482E-2,0.11994251747338167,0,0.11421603849587388,0.1411196028479979,0,0.51027064689616131,40.800130633467589,60.792022825895884,0.67172658363693627,1.1437585601024445,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1404","Louisville - None - In Sub",2.7092136994949492,1,"2022-05-08",0,0,0,0,0,0,0,0,0,1,21.75,108.75,0.1,0.5,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1405","Louisville - Mellwood Ave, River Rd, & River Green Cir - N of Substation",5.6449458648989888,86,"2022-07-10",2.5086603981879781E-2,0,0,0,0.9177738018196353,0,0,5.0630020175872703E-2,0,6.5095740226122044E-3,146.41598320785835,286.65574710344805,1.0068486751674208,1.114942528735632,"Continue to Monitor"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1192","Louisville - Winchester Acres Rd & La Grange Rd - S of Substation",28.8663648989899,956,"2019-11-09",0.27758936755270391,0,9.436296975252062E-2,0,4.3996333638863429E-3,0,0.27031775129850288,0.28056828597616867,0,7.2761992056217542E-2,77.324567296821471,65.904134811143024,0.65717049508755088,0.69888751400569726,"Tree Trim Scheduled for 2023"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1196","Louisville - Westport Rd & Accomack Dr - NW of Substation",10.540074337121212,975,"2020-04-25",1.7854186055806465E-2,3.8129278695451095E-2,0,0,4.7944227793606291E-2,0,0.55141286163719516,0.33739101638108726,0,7.2684294368537353E-3,47.257349821812483,179.00684767213119,0.73740234891625267,2.4211065573770498,"Continue to Monitor"]
["CANE RUN","Jefferson - 5252 Cane Run Rd. - Louisville","CR1420","Louisville - Cane Run Rd - At Substation",8.1277454229797979,39,"2021-06-12",0,0,0,0,1,0,0,0,0,0,7.1923076923076916,4.9615384615384617,0.35384615384615381,0.76923076923076927,"Continue to Monitor"]
["CANE RUN","Jefferson - 5252 Cane Run Rd. - Louisville","CR1421","Louisville - Elmwood St, Lees Ln, & Campground Rd - NE of Substation",2.3017138573232323,3,"2021-06-12",0,0,1,0,0,0,0,0,0,0,134.71111099999999,149.22222199999999,0.33333333333333326,0.33333333333333298,"Continue to Monitor"]
["CANE RUN","Jefferson - 5252 Cane Run Rd. - Louisville","CR1422","Louisville - No Road - At Substation",0.52490072601010096,6,"2021-06-12",0,0,0,0,0,0,0,1,0,0,12.7083333,51.824999999999996,0.33333333333333337,1.166666666666667,"Continue to Monitor"]
["CONESTOGA","Bullitt - 1365 N Buckman St. - Shepherdsville","CS1261","Shepherdsville - I 65 S, HWY 44, & Joe B Hall Ave - S of Substation",7.1006169507575763,231,"2021-05-15",3.6229453203622947E-2,0,0,0,0.36269708151626973,0,5.3002348205300233E-3,0.5808118081180812,0,1.4961422341496142E-2,32.705125130653968,64.809182501158332,0.34348722780594354,1.0870527633568556,"Continue to Monitor"]
["CONESTOGA","Bullitt - 1365 N Buckman St. - Shepherdsville","CS1262","Shepherdsville - Buckman St & Mallard Lake Blvd - S of Substation",11.029601957070707,574,"2021-05-15",0,0.86801768035774296,0,0,1.6711039884198826E-2,0,0,0,0,0.11527127975805826,29.390221187294042,134.07060994107513,0.29604598695749057,1.2598101162047299,"Continue to Monitor"]
["CARTER","Jefferson - Opposite 2215 Carter St - Louisville","CT0003","Louisville - Portland Ave & N 20th St - SE of Substation",0.51210116792929283,45,"2019-02-23",0,0,0,0,0,0,0,0,0,1,5.1894507534090906,8.4833333333333307,0.13926767676767676,0.11111111111111099,"Continue to Monitor"]
["CRESTWOOD","Oldham - Floydsburg Rd. - Crestwood","CW1222","Crestwood - W HWY 22, Clore Ln, & Lake Ave - W of Substation",55.056928345959612,1938,"2022-02-19",4.1582840635013447E-3,0,0,0,2.078565026561472E-2,0,0.50870508495439737,0.15827252339756043,0,0.30807845731892614,98.742861432405817,254.99019567033719,0.99568173176804342,2.9174241647639727,"Reliability Improvements Scheduled for 2023"]
["CRESTWOOD","Oldham - Floydsburg Rd. - Crestwood","CW1225","Crestwood - Hwy 146, Muirs Ln, Elm Ave, & Hwy 362 - SW of Substation",35.295565340909093,1530,"2021-04-24",2.8892622321780432E-2,0,0,0,0.40298259805446662,1.8148632111671126E-3,0.10895401655155248,0.21402941115466781,0,0.2433264887063655,49.319239523101935,60.662210840946138,0.51906301459152315,1.3749605894919388,"Continue to Monitor"]
["CLAY","Jefferson - 908 Clay St. - Louisville","CY1481","Louisville - S Preston St, S Floyd St, E KY St, & 3rd St - W of Substation",5.3938478535353536,812,"2022-05-29",0,0,0,0,0.20095253867546869,0,0,0.23282375179172068,0,0.56622370953281065,150.88119635463408,510.88821613599413,1.657296953474382,5.5034146887595163,"Continue to Monitor"]
["CLAY","Jefferson - 908 Clay St. - Louisville","CY1482","Louisville - Clay St, E Broadway, Logan St, Chestnut St, & Preston St - N of Substation",3.823368055555556,35,"2022-05-29",0,0,0,0,0.11121116614137776,0,1.5608584721596878E-2,0,0,0.87318024913702541,56.519340939542488,186.47143242320266,0.22875816993464043,0.89215686274509776,"Continue to Monitor"]
["CLAY","Jefferson - 908 Clay St. - Louisville","CY1484","Louisville - Jackson St, Jacob St, Floyd St, & 1st St - NW of Substation",4.122961332070707,66,"2022-05-29",0,0,0,0,0,0,0,0,0,1,79.078393187811088,95.376923076923077,0.70250282805429864,0.84615384615384626,"Continue to Monitor"]
["CLAY","Jefferson - 908 Clay St. - Louisville","CY1487","Louisville - Clay St, Shelby St, & Bergman St - S of Substation",1.7444993686868686,1901,"2022-05-29",0,0,0,0,0,0,4.4249615028349254E-3,0.99557503849716511,0,0,47.333384183004888,142.36308454392426,0.5948266921221137,1.1647253325317506,"Trees Trimmed in 2022"]
["DAHLIA","Jefferson - 2135 Dahlia Ave. - Louisville","DA1238","Louisville - Bardstown Rd, Gold Smith Ln, & Peabody Ln - SE of Substation",10.049991950757576,1775,"2022-02-05",0,0,0,1.6994821214480824E-4,0.51943898550187251,0,6.691015610515777E-2,0.39911874127084179,0,1.4362168909983066E-2,56.558399868622871,115.96301376003272,0.38936055673017089,0.65153090895649102,"Trees Trimmed in 2022"]
["DAHLIA","Jefferson - 2135 Dahlia Ave. - Louisville","DA1240","Louisville - Eleanor Ave, Lakeside Dr, Dundee Rd, & Newburg Rd - W of Substation",11.598732323232325,1263,"2022-02-27",1.7114770520125146E-3,1.9226707812898512E-3,0,0,1.0418890644348606E-2,0,0.88487518219786887,9.1943132337683767E-2,0,9.1286469867963519E-3,68.453218954404591,103.39268682738849,0.50933945982068229,0.7408692264111717,"Continue to Monitor"]
["DEL PARK","Jefferson - 3135 Del Park Terrance - Louisville","DE1406","Louisville - River Park Dr, S 41st St, & W Broadway - W of Substation",2.3356862373737375,2115,"2023-03-18",0,0,0,0.60112716865128446,0,0,0,0.3988728313487156,0,0,232.07365615002331,535.90595744539041,2.1986436481528409,4.9914893617021274,"Trees Trimmed in 2023"]
["DIXIE","Jefferson - 1706 Bernheim Ln. - Louisville","DX1220","Louisville - Bernheim Ln, 7th Street Rd, & Taylor Blvd - SE of Substation",20.778672979797982,3126,"2019-01-09",1.9552698132179532E-2,0,1.2337365550443341E-2,3.147871659709315E-2,0.45232639629482924,0,0.19623998293671346,6.1954965111673116E-2,0,0.22610987537706817,64.818108063434352,94.181857886491102,1.0972353804545458,0.59363160031968609,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1166","Louisville - Old Shephardsville Rd, Bardstown Rd, & Bray Ave - N of Substation",5.6697219065656554,628,"2020-03-28",0.16829244548286604,3.2544781931464171E-2,0.18093847352024922,0,4.1374610591900313E-2,0,0.22954633956386294,0.23842484423676011,0,0.1088785046728972,66.63342180855193,157.74330812054728,0.70941347790040421,2.215505792144969,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1167","Louisville - Shepherdsville Rd, Bashford Ave, & Buechel Bank Rd - NE & SE of Substation",9.5383656881313108,802,"2020-04-25",0,0,0,0,0.93493453531447301,5.8753255909598327E-5,9.099222197281381E-4,7.4827544128967909E-3,0,5.6614034796992438E-2,269.91557410242757,826.31363998816084,1.5088225818971812,2.8594881727712487,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1168","Louisville - Ethel Ave, Bardstown Rd, Buechel Bank Rd, & Bradford Dr - E of Substation",12.004120422979796,1465,"2022-10-30",4.3194554868234789E-3,0,0,0,0.87507998991642266,0,1.0044794353196688E-2,2.3483100312203065E-2,0,8.7072659931354102E-2,89.949128772567931,140.93392193174995,0.65027594533741662,0.99010907097799339,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1169","Louisville - Hikes Ln, Champ Trace Ln, & Bashford Manor Ln - N of Substation",5.638110637626264,699,"2020-06-27",4.783681491040046E-3,0.10589429467693952,0,0,0.81626019771830272,0,4.1714134536992541E-2,1.5549664440401051E-3,0,2.979272513268507E-2,116.3623350657297,264.55619932904187,0.41813586483397458,0.70815450643776789,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1171","Louisville - Newburg Rd, E Indian Trl, & Poplar Level Rd - SW of Substation",18.261354008838385,1569,"2020-05-30",8.7189637461478724E-3,0,0,1.8440107233232281E-2,3.6938674951352522E-2,0,0.43457854166144699,1.0856947193479151E-3,0,0.50023801768847242,48.315755777596841,45.169114359991688,0.76058840838290398,0.99400300778719386,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1172","Louisville - Hikes Ln - NE of Substation",13.598016887626265,2025,"2020-07-11",2.4087013057068958E-2,0,0,3.6624524803888447E-3,2.0152005973488388E-2,0,0.82793571118297216,0.11237199160758951,0,1.1790825698492149E-2,32.885336444863739,33.96811952189713,0.22713717851533,0.23028100368608007,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1173","Louisville - Shepherdsville Rd, Rural Way, & Rangeland Rd - S of Substation",13.270474747474747,1750,"2020-07-11",7.5158785236865089E-2,0,0,0,0.67556884299854081,0,7.1343189848299737E-2,0.14900084703051159,0,2.8928334885782819E-2,107.51073849629888,202.44833538560133,1.1335555099779697,2.2163496429640199,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1421","Louisville - Ethel Ave, Bardstown Rd, Buechel Bank Rd, & Progress Blvd - E of Substation",3.4659584911616164,9,"2020-06-13",0,0,0,0,0.8330964127435404,0,0,0,0,0.16690358725645957,443.00851846666671,1328.6722220000001,1.5111111111111111,4,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1423","Louisville - Jennings Ln, Bishop Ln, & Robards Ln - W of Substation",5.1768268623737379,50,"2020-06-13",6.5451388888888892E-2,0,0,0,0.75468749999999996,0,0.11944444444444445,0,0,6.0416666666666667E-2,57.656429784225985,112.94836599999999,0.7468866733133932,1.1568627450980391,"Continue to Monitor"]
["EASTWOOD","Jefferson - 100 Flat Road Rd. - Louisville","EW1240","Louisville - Shelbyville Rd & Beckley Creek PKWY - W of Substation",14.574446969696968,366,"2020-02-29",4.9903447677319968E-3,2.1480179652411638E-3,0,0,0,0,4.6865846514352666E-3,0.78038143591746412,0,0.20779361669812754,24.206700603655513,52.764577651226098,0.26040417407983873,0.53678474114441432,"Continue to Monitor"]
["EASTWOOD","Jefferson - 16000 Shelbyville Rd - Middletown","EW1243","Simpsonville - Eastwood Fisherville Rd & Shakes Creek Rd - SSE of Substation",18.374521938131313,427,"2020-03-25",0,0,0,0,3.7958369808384393E-2,0,0,0,0,0.96204163019161559,26.640596354778999,95.754180558839849,0.45621495919227001,1.0507221404302056,"Continue to Monitor"]
["FARNSLEY","Jefferson - 2428 Farnsley Rd. - Louisvlle","FA1148","Louisville - Cane Run Rd & Lees Ln - SW of Substation",18.12258506944444,2583,"2021-10-16",1.952012808244635E-2,3.0776113027377287E-4,0,9.708770519510879E-3,5.0166745989435213E-2,0,0.35660938049198054,0.52050984078827212,0,4.3177372998081116E-2,88.240988897675635,158.39325705075819,1.0588600309343226,3.2938006091618806,"Continue to Monitor"]
["FARNSLEY","Jefferson - 2428 Farnsley Rd. - Louisvlle","FA1214","Louisville - Farnsley Rd, Cane Run Rd, Ralph Ave, & Campground Rd - N & E of Substation",12.96169049873737,980,"2021-10-16",7.0527382658232274E-2,0,0,0,0.5162950407157586,0,0.12503931779261174,0.1217584664313424,0,0.166379792402055,88.625867689842067,98.416917361408139,0.93016113882242824,1.417078403261119,"Continue to Monitor"]
["FARNSLEY","Jefferson - 2428 Farnsley Rd. - Louisvlle","FA1215","Louisville - Orchard Way, S Crums Ln, Dover Rd, & Burrell Dr - S of Substation",16.437021306818178,1681,"2021-10-16",1.1736770149587853E-2,0,0,0,0.7311416167640733,0,9.6060826530856999E-2,5.7720444206368876E-2,0,0.10334034234911295,61.140807714036825,126.89656441663266,0.56787190413795563,0.7913401232934183,"Continue to Monitor"]
["FARNSLEY","Jefferson - 2428 Farnsley Rd. - Louisvlle","FA1216","Louisville - Crums Ln, Hillview Ave, & Garrs Ln - SE of Substation",10.424010416666668,1330,"2021-10-16",1.1486544579141948E-2,0,0,0,0.81909265468718651,0,0.15577909609377238,6.5915799730604998E-4,0,1.298254664259307E-2,97.910719141084286,130.92408763270234,1.3879677564295523,1.3660972746305688,"Continue to Monitor"]
["FALLS CITY","Jefferson - 1048 S 43rd St - Louisville","FC0001","Louisville - Greenwood Ave & Cecil Ave - E of Substation",2.38647932449495,488,"2023-02-18",0,0,0,0,2.8240240922779703E-2,0,6.3014944030910847E-2,0.90874481504630955,0,0,55.041817464112533,36.049787832496939,0.37458937787403135,0.46485892944871238,"Trees Trimmed in 2023"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1209","Louisville - Westport Rd, Langdon Dr, & Tiverton Way - SW of Substation",13.732394570707072,1536,"2019-08-10",8.4239797170197091E-3,0,0,0,0.19884564605264696,0,8.40762247485074E-2,8.0952770410527827E-2,0,0.62770137907129808,71.54598323310671,153.54358411105278,1.4715436267382518,6.2667894921583178,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1210","Louisville - N Hurstbourne PKY, Whipps Mill Rd, & La Grange Rd - SW of Substation",17.358500789141413,1576,"2019-07-06",0.22807017543859648,0,0,3.4189473684210527E-2,0.13807719298245613,0,6.849122807017544E-3,4.7410526315789472E-2,0,0.54540350877192978,26.741342708845508,22.607250840366742,0.19862871389693004,0.20127772632332594,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1213","Louisville - Westport Rd, Blossom Ln, Goose Creek Rd & Brownsboro Rd - W of Substation",28.270854166666666,1991,"2019-07-20",1.6927915610171141E-2,0,0,0,1.9141794045809929E-2,0,0.64414973099048833,9.8773689134216913E-2,0,0.22100687021931364,70.721765145500328,91.037481100873379,0.75313653255998092,1.1626624645823773,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1214","Louisville - Freys Hill Rd, Evergreen Rd, & Park Rd - SE of Substation",26.242797032828282,722,"2019-05-04",9.1808964489604095E-4,0,0,0,1.2827752538408572E-2,0,0.80868396221259609,1.256908442417199E-3,0,0.17631328716168215,114.66066526381883,144.76807053906035,1.1096786677179049,1.5373731920300187,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1215","Louisville - Springhurst Blvd, Fischer Pard Dr, & I 265 S - NE of Substation",4.2833641098484865,79,"Underground Circuit",0,0,0,0,1,0,0,0,0,0,42.136021904803442,73.661666662499997,0.24432432432432433,1.2500000000000001E-2,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1216","Louisville - Springhurst Blvd & N Hurstbourne PKY - NW of Substation",15.742411931818179,1069,"2019-08-10",0,0,0,0,7.3284262405978707E-4,0,0,0,0,0.99926715737594018,38.204259585270329,116.15871408536583,0.4001827686858066,1.0009345794392523,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1257","Louisville - Brentlinger Ln, Seatonville Rd, Brush Run Rd, & Routt Rd - E of Substation",91.55407181186871,2033,"2019-01-05",7.135574269243967E-3,9.1999542465095172E-4,0.13040894097635541,2.3314577685978909E-4,0.44036804195310486,0,0.22916040703093232,0.11446527249870429,0,7.7308622070148422E-2,148.18164076964231,380.46131640692727,0.95166314755810133,1.6042616269567898,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1259","Louisville - Fairmount Rd & Cedar Creek Rd - W of Substation",25.828187026515153,958,"2021-08-28",1.0867000435001051E-3,0,0,0,0,1.1180008571607433E-2,0.90314725668432894,2.3778987362497131E-2,0,6.0807047338066446E-2,87.285944634120625,119.7436234625812,0.9240716455304,0.8525333166107929,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1261","Louisville - Fairmount Rd, Back Run Rd, & Dawson Hill Rd - E of Substation",34.26199305555555,836,"2021-11-20",5.6133150246714253E-4,0,0,4.3880430354151893E-3,0.1120852258152133,0,0.36248736249641628,0.51924371142732118,0,1.2343257231669962E-3,76.001782051264627,232.56284065250244,0.66307020470319977,1.4021675937314684,"Continue to Monitor"]
["FORTY FOURTH","Jefferson - 128 N 44th St - Louisville","FO0002","Louisville - N 44th St, W Market St, & Fontaine Landing Ct - SW of Substation",2.5847050189393936,352,"2023-03-23",0,0,0,0,0.23045959043301548,0,0.42816945443176491,0.16277161169298107,0,0.17859934344223855,41.871450569772108,43.986560459754386,0.61495441305717602,0.11044415060911919,"Continue to Monitor"]
["FORTY FOURTH","Jefferson - 128 N 44th St - Louisville","FO0003","Louisville - Duncan St & N Longworth Ave - W of Substation",1.4779152462121212,246,"2023-03-23",0,0.23036131583677871,0,0,0,0,0.76963868416322123,0,0,0,36.510861243996303,44.902925151593294,0.27528620051674418,0.39537351443123986,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1135","Louisville - Forest Dr, E Indian Trl, & Poplar Level Rd - N of Substation",17.001471906565655,2114,"2021-01-23",1.8730266769674854E-3,0,0,2.3723348494747326E-3,0.5382914717667312,0,0.42943980603988996,7.2933770869715343E-3,0,2.0729983579965073E-2,90.642265445201019,117.64072000728338,1.0718683112735281,0.57245265138677937,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1139","Louisville - Industrial Blvd, Grade Ln, & Knopp Ave - W of Substation",8.496988005050504,215,"2021-07-28",5.477120256333233E-2,0,4.8062481225593272E-3,0,0.23400420546710726,0,9.0117152297987391E-3,0.5253829978972665,0,0.17202363071993593,128.36784016699661,46.384174175409164,1.5850340456010386,1.7062876830318696,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1141","Louisville - Hanses Dr, Poplar Level Rd, & Rangeland Rd - NE of Substation",14.636903409090905,1432,"2021-01-23",1.679466235094737E-2,0,0,0,0.80604455165885458,0,0.10170694840985084,2.3428553979571585E-2,0,5.2025283600775608E-2,76.231841797119557,88.620500452657623,0.86670834572123812,1.7567901474410477,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1142","Louisville - Mile of Sunshine Dr, Whispering Hills Blvd, & Yellow Sands Dr - E of Substation",19.607233743686869,2201,"2021-05-01",0.31317320072814459,1.7697464813745949E-2,0,0,5.697879204960855E-3,3.0783347393035268E-4,9.3427459337862048E-2,3.5317971259009311E-2,0,0.53437819118234697,108.8645613885119,138.02103596523048,0.84871147278935821,2.3702764745741947,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1145","Louisville - Preston Hwy, Lipps Ln, & Lone Oak Ave - S of Substation",7.5585190972222227,1221,"2021-07-28",1.4323237297874088E-3,1.354346220142822E-2,1.0793728966592793E-3,1.970778954280555E-2,0.21588689157022081,0,0.24670032011819748,0.38872609373717476,0,0.1129237462037265,34.85332762778156,65.963541640870943,0.56521877227113115,1.8009045585083261,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1475","Louisville - Old/Fern Valley Rd, & Industrial Blvd - W of Substation",2.4227984532828288,11,"2021-04-03",0,0,0,0,0,0,0,1,0,0,96.12151512727273,102.06515145454543,0.83636363636363631,1.1818181818181817,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1476","Louisville - Forest Dr, E Indian Trail, Poplar Level Rd, & Taylor Ave - NNW of Substation",10.693571811868688,99,"2021-04-03",0,0,5.969346598547997E-2,0,0.38580263511696694,0,1.1815772289017786E-2,4.9936618906772177E-4,0,0.54218876041946762,162.61609282704393,261.62531143111102,2.3158456479575102,2.8161616161616161,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1477","Louisville - Preston Hwy & Outer Loop - SW of Substation",6.2204654356060596,27,"2021-04-03",3.3773411114522566E-3,0,0,0,0,0,3.9146453791832972E-2,0.95747620509671472,0,0,91.211732789417908,240.9537257248673,0.56269841269841259,0.51719576719576665,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1478","Louisville - Preston Hwy, & Standiford Ave/Ln - NW of Substation",6.7765048926767673,114,"2021-04-03",8.3307965499746325E-2,0,0.43023845763571789,0,0,0,0.35048198883815324,0.13597158802638254,0,0,19.768328149463841,46.199210396293402,0.34455379669271091,0.34157536974409847,"Continue to Monitor"]
["GRAND","Jefferson - 1038 S 34th St - Louisville","GD0002","Louisville - Louis Coleman Jr Dr, Virginia Ave, & Kirby Ave - S of Substation",4.0526425189393942,577,"2023-01-22",0,0,0,0,0.23849263644239099,0,0.11391856771585331,3.0436038117239387E-2,0,0.61715275772451628,40.017850254796087,59.963275892082336,0.45153346489794544,0.50467419380704104,"Continue to Monitor"]
["GILLIGAN","Jefferson - 35th Street & Gilligan Ave - Louisville","GI0001","Louisville - Bank ST, 33rd St, Portland Ave, & Rudd Ave - N & E of Substation",4.1134172979797983,672,"2023-03-04",0,0,0,0,0.83752447696588683,0,2.3343295887869733E-2,0.13865127623758974,0,4.8095090865368101E-4,94.021514946983146,151.87388440921694,0.83956440274569977,1.1161269642957223,"Continue to Monitor"]
["GILLIGAN","Jefferson - 35th Street & Gilligan Ave - Louisville","GI0003","Louisville - Bank St, N 39th St, & S 38th St - W of Substation",3.2909332386363634,476,"2023-03-04",0,0,0,0,0.3799303252284712,0,6.0261519005464219E-2,0.55980815576606457,0,0,50.346875694323636,166.0323188525264,0.61852663983739886,1.4654031010973112,"Trees Trimmed in 2023"]
["GOSS","Jefferson - 1260 Goss Ave - Louisville","GO0002","Louisville - Reasor Ave, E Burnett Ave, & Texas Avenue - SW of Substation",3.362231060606061,702,"2022-07-17",0,3.3310556884181754E-2,0,0,0.12196788520669628,0,0.38978476255551758,2.9039972668261018E-3,0,0.45203279808677826,26.949027237779546,27.837953874831591,0.23269328854122073,0.38362793471331985,"Continue to Monitor"]
["GOSS","Jefferson - 1260 Goss Ave - Louisville","GO0003","Louisville - Ash St & Hickory St - NW of Substation",1.6298615845959596,410,"2022-07-17",0,0,0,0,0.64830025096965549,0,0.29078256901665528,6.0917180013689252E-2,0,0,20.039247748586547,21.340877489217259,0.16177461480637115,0.16802563646074412,"Continue to Monitor"]
["GRADY","Jefferson - 1838 S 39th St. - Louisville","GR1463","Louisville - Stratton Ave, Louis Coleman Jr Dr, & Grand Ave - NE of Substation",5.0807788825757587,1790,"2019-01-26",7.1840240813479686E-2,0,0,0,0,0,0,0.92815975918652027,0,0,72.312867953022703,146.9743049463363,1.1600749942678663,2.3575418994413404,"Tree Trim Scheduled for 2023"]
["GRADY","Jefferson - 1838 S 39th St. - Louisville","GR1465","Louisville - S 41st St, Bells Ln, & Oxy Rd - SW of Substation",2.0030569760101011,2,"2019-01-26",0,0,0,0,0,0,0,0,0,1,17.9033333,58.516666499999999,0.3,1,"Continue to Monitor"]
["HALE","Jefferson - Rear 185 Hale Ave - Louisville","HA0001","Louisville - Dixie Hwy, Osage Ave, Grand Ave, & Date St - N of Substation",3.4473712121212121,659,"2022-11-26",0,0,0,0,0.73218234723569353,0,0,0.26473973488522468,0,3.0779178790817977E-3,61.241773581414762,101.25842883022788,0.44588906456936089,0.2332272848513334,"Trees Trimmed in 2022"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1143","Louisville - Hurstbourne Pky & Stone Creek Pky - N of Subsation",4.6776406249999996,402,"2019-12-14",2.3646682188591385E-4,0,0,0,0,0,7.6387878346915017E-2,0,0,0.9233756548311991,37.839637378774761,52.114949801662092,0.32151104082638216,0.26917817119731724,"Continue to Monitor"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1144","Louisville - Old Hickory Rd, Waterson Trl, & Blankenbaker Access Dr - SE of Substation",6.5383480113636372,281,"2019-11-26",0,2.7584524100006547E-2,0,0,1.6794719959054686E-2,0,0.7736997780145094,0.17939760398502638,0,2.5233739414029723E-3,81.328305297305263,99.852233229083112,0.6479329597242629,0.42974685141717744,"Continue to Monitor"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1146","Louisville - Plantside Dr, Carton Dr, & Bunsen Way - SW of Substation",3.8053197601010096,163,"2019-11-26",1.1671637919854754E-3,0,0,0,0,0,0.19815847490597849,0.80067436130203606,0,0,28.621195956517163,47.301329233128804,0.45657206384500587,1.1165644171779141,"Tree Trim Scheduled for 2023"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1148","Louisville - Old Hickory Rd, Taylorsville Rd, College Dr, & Rown Tree Rd - S of Substation",19.860262152777782,2287,"2020-07-18",2.1340424920691593E-3,5.1299098367047098E-4,2.0930032133755216E-3,0,1.4835699247750021E-3,0,0.57859432262618549,0.36367572403547432,0,5.1506346724449974E-2,52.379894305451522,59.870188015545033,0.50807695416752596,0.96446537713012204,"Continue to Monitor"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1290","Louisville - Frankfort Ave, Fenley Ave, & Breckenridge Ln - E of Substation",13.942281565656566,1673,"2018-05-26",2.1676065302014415E-2,0,0,2.1838876308038425E-2,0,0,5.2395541938635055E-3,2.6182969968769888E-2,0,0.92506253422731377,35.304643169015762,77.862011768786815,0.38461736965941029,1.1361156949761184,"Continue to Monitor"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1291","Louisville - Frankfort Ave, Birchwood Ave, & Brownsboro Rd - W of Substation",7.5719876893939384,1547,"2020-11-07",1.7377997836544805E-2,0,0,0,2.884606928333348E-2,0,0.80282656300843402,5.3470762573984011E-2,0,9.7478607297703745E-2,37.031237318504886,34.22367783312572,0.52453248556215581,1.1849041211149967,"Continue to Monitor"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1292","Louisville - Grinstead Dr, Lexington Rd, & Alta Vista Rd - S of Substation",14.427066287878787,854,"2019-12-31",8.0206350181170546E-2,0,0,0,1.6434318000368483E-2,0,0.19003869065896947,0.32030952527175582,0,0.39301111588773568,64.517198657299843,76.153724701890553,0.43595525486707143,0.63923627725069998,"Tree Trim Scheduled for 2023"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1293","Louisville - Lexington Rd, Cannons Ln, & Old Cannons Ln - SE of Substation",19.765208491161616,2310,"2021-04-10",1.3434694057067847E-2,5.7057697122248612E-2,1.226072305787305E-2,0,2.359444884260669E-2,0,0.45514551150626903,0.29237629322886005,0,0.14613063218507466,151.49257241846013,75.694879917417325,0.31766281113267664,0.41026007487769445,"Continue to Monitor"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1294","Louisville - Hillcrest Ave, Zorn Ave, & River Rd - N of Substation",20.644229797979804,1133,"2019-10-12",1.4687942224174109E-3,0,0,8.019811643000049E-3,3.3285756111843069E-2,0,0.63205362806812082,0.29194115063680282,0,3.3230859317815838E-2,137.13431912988381,198.67237489476156,1.1704311064947626,1.3685028009536513,"Tree Trim Scheduled for 2023"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1434","Louisville - Stilz Ave, Lexington Rd, & Alta Vista Rd - S & E of Substation",3.2478847853535346,7,"2021-04-10",1,0,0,0,0,0,0,0,0,0,95.853295886229091,71.642857142857139,0.78211926211926219,0.8571428571428571,"Continue to Monitor"]
["HERMAN","Jefferson - Rear 3619 Jefferson St - Louisville","HE0003","Louisville - 38th St, Amy Ave, & W Muhammad Ali Blvd - N & SW of Substation",3.0717274305555557,663,"2023-02-25",0,0,0,0,0,0,9.5526769191500216E-2,0.90447323080849973,0,0,18.324122990701362,22.351268198049311,0.154744668337126,0.27013149083900723,"Trees Trimmed in 2023"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1102","Louisville - Bardstown Rd, Baringer Ave & Highland Ave - NW of Substation",5.6543262310606055,1484,"2021-04-24",0.14702872485941537,0,0,0,5.5028116925882768E-2,0,0.54957191347079382,0.11325801712346116,0,0.13511322762044684,53.667605051608099,62.813827762791732,0.79123492019429942,0.63099261159159281,"Continue to Monitor"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1103","Louisville - Bardstown Rd, Alta Ave, & Speed Ave - E of Substation",9.1738465909090916,1865,"2021-04-24",9.9674997198251708E-2,0,0,0,9.1056819455340138E-2,0,0.24971422167432478,0.54931076992043038,0,1.0243191751653032E-2,80.146266547166292,44.051571780649589,0.79991023456451904,0.82694241406541125,"Continue to Monitor"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1104","Louisville - Fernwood Ave, Norris Pl, Dundee Rd, & Newburg Rd - S of Substation",14.727818181818179,2273,"2021-04-24",4.3984085553232292E-2,0,1.7307061482329692E-2,0,2.5181774456789704E-2,0,0.34045807364355907,7.1574761474481149E-2,0,0.50149424338960813,69.751432853419331,164.88653628057543,0.57448394984571283,1.7317857094633433,"Continue to Monitor"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1105","Louisville - Stevens Ave, Baxter Ave, Barret Ave & Winter Ave - W of Substation",14.442043402777777,2702,"2021-04-24",1.4823064582421807E-2,0,0,0,1.0378133990957664E-2,0,0.38188947668483086,0.37166713071609458,0,0.22124219402569509,78.609391681985841,74.66696746488644,0.82750366834936762,1.038479083937796,"Reliability Improvements Completed in 2022"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1473","Louisville - Eastern Pky, Poplar Level Rd, & Nightingale Rd - SW of Substation",5.6491889204545451,2766,"2021-04-24",0,0,0,0,0.89875930521091807,0,0,0,0,0.10124069478908189,108.16951787573608,130.06236554838702,0.90059289138062848,0.61290322580645129,"Continue to Monitor"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1474","Louisville - Eastern Pky & Castlewood Ave - W of Substation",2.3350377209595958,2,"2021-04-24",0,0,0,0,0,0,1,0,0,0,18.071666599999997,58.066666499999997,0.3,1,"Continue to Monitor"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1238","Louisville - Timber Bridge Dr & Fox Harbor Rd - E of Substation",10.443353377525252,428,"2023-02-11",2.4942626571708704E-2,0,0,0,0,0,0.9177647527824766,7.0033292749938046E-5,0,5.7222587353064763E-2,220.31173437276897,433.36745415721293,1.2140151307999789,3.0754503272122382,"Continue to Monitor"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1241","Louisville - River Rd, Avish Ln, & Rockledge Dr - SW of Substation",19.430770675505048,538,"2023-01-06",0.20645105918940204,0,0,0,3.2098790363294896E-2,0,0.26371190856035059,0.19339041579999594,0,0.30434782608695654,140.97600477040072,156.00529947335889,1.0812856763343954,0.79714811227572069,"Continue to Monitor"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1242","Louisville - River Rd, Shirley Ave, & Duroc Ave - N of Substation",10.436039457070706,579,"2022-07-03",3.8425719406162203E-3,0,0,0,0.62363142613418476,0,0.26528615813240047,9.533647939019714E-2,0,1.1903364402601367E-2,22.383235150701118,24.811949801581246,0.4144830264764422,0.2884253469120367,"Continue to Monitor"]
["HARMONY LANDING","Oldham - 11943 W Hwy 42 - Goshen","HL1158","Goshen - US 42 & Buckeye Ln - NE of Substation",32.114280776515159,536,"2021-12-08",1.3950058985450256E-2,3.263861580810067E-3,0,0,0,0,0.22941407786079435,0.4167322060558396,0,0.33663979551710577,167.78414770721258,183.81281315271775,1.339574160700755,1.55405693855084,"Continue to Monitor"]
["HANCOCK","Jefferson - 630 E Caldwell St - Louisville","HN1200","Louisville - Shelby St, E Broadway, Baxter Ave, & Cherokee Rd - NE of Substation",6.3644651199494939,1899,"2022-05-29",1.8821675566838834E-3,0,0,0,3.3819118399166961E-3,0,2.6352649548233711E-2,0.94370084363495632,0,2.4682427420209457E-2,91.73656933568104,228.83991176798492,1.2370381058369615,2.9902586058815346,"Trees Trimmed in 2022"]
["INTERNATIONAL","Jefferson - 5599 Cane Run Rd. - Louisville","IN1291","Louisville - Lower Hunters Trace, Terry Rd, & Mt Everest Dr - ESE of Substation",33.636002525252529,3029,"2021-11-27",1.974482435776179E-2,0,2.9477515691725659E-2,0,0.16620331890745463,0,0.39192055257802871,2.8331088246252616E-2,0,0.36432270021877655,61.106323900817266,80.72872358159627,1.4454326395710364,2.5617093879636896,"Continue to Monitor"]
["INTERNATIONAL","Jefferson - 5599 Cane Run Rd. - Louisville","IN1293","Louisville - Cane Run Rd, Port Rd, & Intermodal Rd - S of Substation",4.881780303030304,255,"2021-10-02",2.8682969148186303E-2,0,0,0,0,0,0.95206853548771897,0,0,1.924849536409478E-2,30.792030111060587,72.36191138402053,0.55591746435497646,1.1336153580736057,"Continue to Monitor"]
["INTERNATIONAL","Jefferson - 5599 Cane Run Rd. - Louisville","IN1298","Louisville - Cane Run Rd & Distribution Dr - S of Substation",2.7469678030303029,12,"2021-10-02",0,0,0,0,0.99859179721879954,0,1.4082027812004929E-3,0,0,0,64.052092944186057,132.12093020930237,0.60930232558139541,0.86046511627906996,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1120","Louisville - Taylorsville Rd & Tucker Station Rd - E of Substation",12.779702651515152,763,"2020-04-04",0.47470065662417921,0,0,0,7.0683661645422946E-2,0,0.32213209733487835,0.12514484356894554,0,7.3387408265739671E-3,1.402533655808432,3.3973541309295632,1.5447433124849252E-2,4.722233479076101E-2,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1121","Louisville - Taylorsville Rd, Neal Dr, & Watterson Trl - W of Substation",14.29680034722222,1381,"2022-12-31",1.2494457855066752E-2,5.9054633233164193E-3,0.10616286516577171,0,5.0100990196561411E-2,0,0.60262820828612251,1.756859943839598E-2,0,0.20513941573476527,19.709865066151803,47.907350690128297,0.14215288399210382,0.35790207437749605,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1122","Louisville - Chenoweth Run Rd, St Rene Rd, & Billtown Rd - W of Substation",18.476611584595961,1502,"2022-12-31",0.1286819708513737,5.449267321239262E-4,0.24820917260306546,0.1865333742854029,1.0967888953839752E-2,0,8.5206725386650288E-4,0.18294676561215087,0,0.24126383370817686,29.406734632127762,65.425469297084533,0.36122226661167423,0.67222634181260221,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1125","Louisville - Blankenbaker Pky & Chenoweth Run Rd - NW & SW of Substation",13.116521464646464,441,"2019-04-06",0.1575722028962058,0,1.3186635385486612E-2,0,0,0,2.647439527546315E-2,0.53658684572445592,0,0.26617992071838847,30.356490821141819,94.235667218695397,0.22722589013304217,0.72478031146223931,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1126","Louisville - Old Heady Rd, Easum Rd, & Valley Park Dr - SE of Substation",49.732761363636371,1487,"2019-05-18",1.4982021574111066E-4,1.2572325796456839E-5,2.7868655515479328E-4,0,4.7670068644898851E-4,0,0.96404349745340556,1.5813192001765714E-3,0,3.3457403563276512E-2,62.069160164677214,117.77291253019629,0.62577559537487693,1.8501920348630208,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1155","Louisville - Southside Dr, 3rd St, & W Southland Blvd - N of Substation",5.2852578914141422,1188,"2021-07-17",5.2802266633884768E-3,0,0.2047404961773969,0,1.7432943462938898E-2,0,0.30847177830072703,0.39996838888693759,0,6.4106166508611104E-2,32.054654415062274,39.264367083273122,0.26091229828142587,0.36140219037808652,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1158","Louisville - Inverness Ave, New Cut Rd, & Palatka Rd - W & SW of Substation",19.558025726010101,2424,"2021-07-28",5.8110260302635846E-3,0,1.2532122889400287E-3,0,1.3069213870374583E-2,0,0.52932181074256557,0.41150493638828689,0,3.9039800679569282E-2,32.072275040417381,69.007373172581978,0.24061264748952432,0.41002193053184299,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1159","Louisville - Kenwood Dr, Homestead Dr, & Southside Dr - SW of Substation",12.562955018939396,1435,"2021-07-17",0.16049657491900982,0,0,0,0.25843493170446208,0,7.8912876820733488E-2,0.3060893076472867,0,0.19606630890850787,72.597568764991081,76.259510453904966,1.0857466315241959,0.89760180563670666,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1162","Louisville - Strawberry Ln & Eiler Ave - E of Substation",2.7660367739898981,83,"2020-12-19",0,0,0,0,0,0,0.29275149737195943,9.7787556533431123E-3,0,0.69746974697469744,34.658498958205662,98.311287997131416,0.18317609757734818,0.39615605278255905,"Continue to Monitor"]
["LOGAN","Jefferson - Rear of 1130 Logan St, St Catherine St - Louisville","LG0001","Louisville - Shelby St, E Oak St, & Bergman St - N & S of Substation",2.5340347222222221,509,"2022-07-17",0,0,0,0,0.25263993597025713,0,0,0.74736006402974287,0,0,78.032376084720696,234.23924041902782,0.30629376879055736,0.53598497474199858,"Trees Trimmed in 2022"]
["LOGAN","Jefferson - Rear of 1130 Logan St, St Catherine St - Louisville","LG0003","Louisville - Logan St, E Kentucky St, & Swan St - NE of Substation",1.3846036931818184,288,"2022-07-17",0,0,0,0,6.3639668019628032E-2,0,1.6720179317865149E-2,0.7178469740110256,0,0.20179317865148119,28.393568838509658,35.9543829238754,0.25528946418759779,0.48788927335640153,"Trees Trimmed in 2022"]
["LYNN","Jefferson - Rear of 2071 S Preston St & Lynn St - Louisville","LN0003","Louisville - Barbee Ave, Crittenden Dr, Warnock St, & Floyd St - W of Substation",3.3642252209595958,436,"2022-07-17",0,6.2146657798470232E-3,0,0,0.67498752909876958,0,3.8888427003658133E-2,0.27990937811772532,0,0,34.138067909247567,81.2871510372795,0.38150986110320362,1.1124175612652276,"Trees Trimmed in 2022"]
["LYNN","Jefferson - Rear of 2071 S Preston St & Lynn St - Louisville","LN0004","Louisville - Preston St & Gernert Ct - NW of Substation",2.220891414141414,492,"2022-07-17",0,3.955408572242055E-2,0,0,0,0,0.84506888017696402,8.9358067412777329E-3,0,0.1064412273593377,27.340257707367151,47.927568979834099,0.20202319128874852,0.27588824713095994,"Continue to Monitor"]
["LOCUST","Jefferson - 2929 Preston Hwy - Louisville","LO1190","Louisville - Hess Ln, Poplar Level Rd, & Sheridan Ave - E of Substation",19.03256423611111,2259,"2019-11-09",6.1354993662018811E-2,0,0,0,1.326305957702315E-2,6.3880178797785046E-3,0.13490559743812128,0.32528854493295078,0,0.45879978651010739,113.02895996107227,130.7375199519783,1.0304347363886324,1.6541416976263519,"Tree Trim Scheduled for 2023"]
["LOCUST","Jefferson - 2929 Preston Hwy - Louisville","LO1192","Louisville - Preston Hwy, Crittenden Dr, & Boxley Ave - NW of Substation",9.256671085858585,1284,"2019-12-21",0.11911615888704401,9.3827063458534338E-3,0,0,0.19802914042620084,0,0.17354568051639271,0.37582896947427369,0,0.12409734435023531,67.667864014284447,78.912850038549152,0.84120151605269411,0.98016923347316631,"Tree Trim Scheduled for 2023"]
["LOCUST","Jefferson - 2929 Preston Hwy - Louisville","LO1193","Louisville - Preston Hwy, Belmar Dr, & Phillips Ln - SE of Substation",12.573719696969695,1290,"2020-02-08",3.564423349555855E-2,5.4804416979659055E-3,0,0,0.2264886720707214,0,0.50238288517484198,0.11060315931344941,0,0.11940060824746272,97.896815175330545,135.78805431758909,1.3165609701324172,1.0034980324767309,"Continue to Monitor"]
["LYNDON SOUTH","Jefferson - 918 Ormsby Ln. - Louisville","LS1243","Louisville - Ormsby Ln & LaGrange Rd - NE of Substation",9.5106223169191928,815,"2018-04-21",1.4517682675106646E-2,6.3800242691119252E-4,0,0,0.78783917334901232,0,4.449128688842463E-2,4.6993257190037156E-2,0,0.10552059747050803,77.908406171067782,196.19862439158484,0.65892649177755835,0.53152393685611377,"Continue to Monitor"]
["LYNDON SOUTH","Jefferson - 918 Ormsby Ln. - Bellemeade","LS1244","Lyndon - New La Grange Rd, La Grange Rd, Whipps Mill Rd - N & NE of Substation",16.894547506313131,1906,"2021-07-24",0.13088631024418027,0,5.6296718160461307E-2,0,2.0024204456467572E-2,0,0.41239837687762509,0.32228376165729339,0,5.8110628603972377E-2,98.205183032070565,124.67967618412978,0.660980977038512,0.94946575195549687,"Continue to Monitor"]
["LYNDON SOUTH","Jefferson - 918 Ormsby Ln. - Louisville","LS1246","Louisville - New La Grange Rd - NW of Substation",2.0629720643939393,387,"2021-01-23",4.7464300963043785E-2,0,0,0,0,0,0,5.4390625741259073E-2,0,0.89814507329569715,38.968593564688618,108.93664943669255,0.47455913167444663,1.2687338501291983,"Continue to Monitor"]
["LYNDON SOUTH","Jefferson - 918 Ormsby Ln. - Louisville","LS1248","Louisville - Whipps Mill Rd, Ormsby Station Rd, & Shelbyville Rd - NE of Substation",14.437793718434342,534,"2021-05-29",7.3316909470838897E-3,0,0,0,0,0,0.58917927706574902,0.38254696710744285,0,2.0942064879724186E-2,123.31737038965164,345.45363276317732,1.0067103146372713,1.7977124259016062,"Continue to Monitor"]
["LYNDON  ","Jefferson - 8407 LaGrange Rd. - Louisville","LY1163","Louisville - Railroad Ave, Lyndon Ln, & Westport Rd - W of Substation",18.516980744949493,2183,"2022-06-11",8.6619833360562001E-3,0,0,0,0.34959973860480309,0,0.32773403038719162,0.1708184937101781,0,0.14318575396177094,76.622297038857724,78.278244131043948,1.4376663933071803,2.2750137025029398,"Continue to Monitor"]
["MADISON","Jefferson - 635 E Madison - Louisville","MD1451","Louisville - Madison St, Wenzel St, Baxter Ave, & Lexington Rd - E of Substation",2.1707406881313127,24,"2022-05-29",0,0,0.65873405299313048,0,0,0,0.34126594700686946,0,0,0,43.199589738256414,55.646666639999999,0.28205128205128205,0.2,"Continue to Monitor"]
["MADISON","Jefferson - 635 E Madison - Louisville","MD1452","Louisville - Clay St, E Main St, & River Rd - N of Substation",8.9091881313131314,529,"2022-05-29",0,0,0,0,0,0,2.4744556524010056E-3,0.30595762739529264,0,0.69156791695230635,143.71955335555216,288.44472692467082,1.4313635967280975,1.5404896421845571,"Trees Trimmed in 2022"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG0407","Louisville - Chestnut St, Quest Dr, & Muhammad Ali Blvd - NE of Substation",5.1077774621212129,639,"2023-03-23",0,0,0,0,3.7325091346952333E-2,0,4.9729592260421854E-2,0.57981439960139514,0,0.33313091679123069,253.89993345350595,601.16329275052044,2.1215005783868062,3.476073281885248,"Trees Trimmed in 2023"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG0417","Louisville - 15th St, Cedar St, Chestnut St, 18th & 19th St - NW of Substation",5.0748696338383832,763,"2023-03-23",0,0,0,0,3.4230729934464993E-2,1.2818735130559164E-2,0.53651861690482094,0.15940040576241005,0,0.25703151226774479,90.50464870896073,151.60010670874183,1.0631241298326535,2.2575522114540814,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG0452","Louisville - 12th St, W Kentucky St, & W Oak St - S of Substation",2.5442492108585859,65,"2023-03-23",0,0,1.5550450609648348E-2,0,0.87877716911115034,0,0,3.8169287860045947E-2,0,6.7503092419155322E-2,136.67345365861738,86.770528314685407,0.91591193098834123,1.3034965034965038,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG0454","Louisville - W Broadway & S 9th St - SE of Substation",0.84614094065656553,4,"2023-03-23",0,0,0,1,0,0,0,0,0,0,81.739166600000004,193.9666665,0.65,1,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG1314","Louisville - Magazine St, W Chestnut St - W and E of Substation",1.8881291035353536,5,"2023-03-23",0,0,0,0,1,0,0,0,0,0,19.813333280000002,99.066666400000003,0.12000000000000002,0.60000000000000009,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG1326","Louisville - W Broadway, Dixie Hwy, & Dr W J Hodge St - SW of Substation",2.1382664141414143,117,"2023-03-23",0,0,0,0,0,0,7.4954551810935535E-2,0,0,0.92504544818906442,23.602952889787794,61.114957256410229,0.41025641025641013,1.0256410256410251,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG1329","Louisville - W Broadway, 9th St, 8th St, 7th St, & 5th St - SE of Substation",4.5300935921717169,138,"2023-03-23",0,0,0,0,5.0966989984393826E-3,3.0619703285197841E-3,8.2120068746172531E-2,0.2965765196262421,0,0.61314474230062621,184.15865569839491,366.72802364393698,2.8038124403516669,7.1498800959232618,"Trees Trimmed in 2023"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1290","Louisville - 3rd Street Rd, Chistland Rd - N of Substation",12.045075441919192,489,"2022-04-02",0,0,0,0,0.10548593839678591,0,0.34202219246221538,0.29701549646068492,0,0.25547637268031376,103.227967180519,34.760082204269914,0.4726661473494051,0.56784223206635953,"Trees Trimmed in 2022"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1292","Louisville - Outer Loop & National Tpike - NE of Substation",17.194405934343436,1345,"2021-10-30",6.3875772635288612E-3,0,0,0,6.5720460896738761E-2,0,2.6018364284632646E-3,0.38416321361214745,0,0.54112691179912176,36.772868002149572,49.051274117538192,0.33233016867340959,0.57565695122697236,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1293","Louisville - Manslick Rd and Brown Austin Rd - SE of Substation",18.580040404040407,1360,"2022-05-01",8.3005070165041821E-3,0,0,0,1.5005209604263742E-2,0,0.70002362720149347,0.24380947954310414,0,3.2861176634634379E-2,30.122514227252168,22.685513912766062,0.28984185821454533,0.32268141500163239,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1296","Louisville - 3rd St Rd, Christland Rd, & Manslick Rd - N of Substation",17.258235164141411,1740,"2022-04-02",7.8772784850892077E-2,0,3.3460720956695368E-2,0,1.7819954054576294E-2,3.0272452068617556E-3,0.44954591321897075,0.33199862593125362,0,8.5374755780750156E-2,49.516480591385275,36.817404876228053,0.41733825248487849,0.44282939374914349,"Trees Trimmed in 2022"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1299","Louisville - Arnold Town Rd, Timber Hills Rd, & St Andrews Church Rd - NW of Substation",17.78479624368687,780,"2022-02-19",0,0,0,0,0.12081711108278007,0,0.5259735802057488,0.34134491855367805,0,1.1864390157793055E-2,58.579305348947649,99.52610095496189,0.38030988000330829,0.96588127818103509,"Trees Trimmed in 2022"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1282","Louisville - Mud Ln, Blue Lick Rd, Vanguard Dr & Caven Ave - NW of Substation",29.982721906565658,2557,"2019-10-05",1.2223499780989926E-2,2.5845677537530364E-3,0,0,3.0406313463146581E-2,0,0.29275425078644524,0.62977466849838737,0,3.2256699717277904E-2,74.458199720739955,88.366235875418923,0.78090791470249799,0.90722874923278074,"Tree Trim Scheduled for 2023"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1288","Louisville - Preston Hwy, Hebron Ln, & Bells Mill Rd - S of Substation",39.15184801136364,1641,"2019-08-03",0.11158301611917854,1.8950608581230322E-2,5.9213308896094745E-3,0,0.11477865501198364,0,2.0401569622632641E-2,0.51294116264862066,0,0.21542365712674469,53.154855619338015,61.776366120501585,0.71825930455907638,1.1927148999346597,"Tree Trim Scheduled for 2023"]
["MULDRAUGH","Meade - 100 Carpenter Test Rd. - Muldraugh","MU1101","Muldraugh - Carpenter Test Rd, Main St, & Dixie Hwy - E & SE of Substation",10.299171875000001,552,"2021-11-27",6.8631235791189471E-5,0,0,0,0,0,3.7944494488053877E-2,0.74766010380474413,0,0.2143267704714108,101.72724087803233,132.03485969429809,1.3658026518295368,1.0559867972719206,"Continue to Monitor"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1264","Louisville - Six Mile Ln & Klondike Ln - W of Substation",8.6325522411616156,1217,"2021-07-24",0,0,0,0,4.0963128876636806E-2,0,0.2412129565816678,1.3675913163335631E-2,0,0.70414800137835976,25.701163276563978,38.112377068319127,0.22039445532277929,0.23473777678192584,"Continue to Monitor"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1269","Louisville - Wisteria Landing Cir, Beargrass Ave, Bardstown Rd & Fegenbush Ln - SW of Substation",22.935481218434344,2661,"2021-10-23",1.2061323839279226E-3,1.5083920656833538E-3,0,6.423018237302914E-4,0.16117125626680229,0,0.60120322604083409,0.19720119160066846,0,3.7067499818353555E-2,71.745776089825824,101.89791236505052,1.2315013248120237,1.1825971975407479,"Continue to Monitor"]
["OLD HENRY","Jefferson - 13601 Terra View Trail - Louisville","OH1170","Louisville - Old Henry Rd, Nelson Miller Pky, & Stanley Gault Pky - W of Substation",8.8888827335858576,145,"2020-11-14",0,0,0,0,0.23624401913875598,0,0.70005980861244022,6.3696172248803834E-2,0,0,7.2949817717971417,17.526559369014048,3.2948699914118605E-2,3.4484070750013127E-2,"Continue to Monitor"]
["OLD HENRY","Jefferson - 13601 Terra View Trail - Louisville","OH1172","Louisville - Eastpoint Pky & Nelson Miller Pky - NW of Substation",7.6747555239898988,96,"Underground Circuit",6.5521796565389701E-2,0,0,0,0,0,0,0,0,0.9344782034346103,49.306157560879043,78.03470789690725,0.38436242323101177,1.0309278350515465,"Continue to Monitor"]
["OLD HENRY","Jefferson - 13601 Terra View Trail - Louisville","OH1174","Louisville - Bush Farm Dr and Aiken Rd - SE of Substation",19.937237058080811,881,"2020-11-21",0,0,0,0,0,0,0,1,0,0,14.44855946552301,7.6603174603174597,0.12903260579397902,0.15079365079365101,"Continue to Monitor"]
["OKOLONA","Jefferson - 811 N 27th St. - Louisville","OK1271","Louisville - Outer Loop, Robbs Ln, & Monaco Dr - E of Substation",10.967609059343435,953,"2019-05-04",0.39206319470463347,0,0,0,0,0,5.0721243911577368E-2,0.4689724615961034,0,8.8243099787685769E-2,25.849563816029427,69.22411232995222,0.28403057733474157,0.89555986721838365,"Tree Trim Scheduled for 2023"]
["OKOLONA","Jefferson - 811 N 27th St. - Louisville","OK1272","Louisville - Outer Loop, Shepherdsville Rd, & Applegate Ln - E of Substation",18.661603693181817,1689,"2019-04-06",0,0,0,0,0.27308357160717972,0,2.1852339070025329E-3,0.56054511257759754,0,0.16418608190822018,46.306582873891202,40.366639496864536,0.7142515961232343,0.84735269783177869,"Tree Trim Scheduled for 2023"]
["OKOLONA","Jefferson - 811 N 27th St. - Louisville","OK1273","Louisville - Preston Hwy, St. Rita Dr, & High School Dr - S of Substation",9.4474234532828287,791,"2019-05-04",1.3643175290346751E-2,0,0.38437122757357534,0,4.0013736835532616E-3,0,5.161720018315781E-3,0.2642675769054656,0,0.3285549265287433,61.752427900040473,110.37841400104168,0.88828947118806367,0.84167389336852971,"Tree Trim Scheduled for 2023"]
["ORMSBY","Jefferson - Rear of 436 E Ormsby Jackson St - Louisville","OR0003","Louisville - Preston St, Woodbine St, Floyd St, & Burnett Ave- SW of Substation",3.3159938446969686,609,"2020-02-29",0,0,0,0.13907818568183483,0.16978090422803546,1.7219901809921594E-2,0.55448083827947536,0.10962116216018172,0,9.8190078405510361E-3,30.539981397001213,44.630989798365142,0.24665293220563225,0.46143836028164792,"Continue to Monitor"]
["OXMOOR","Jefferson - 8004 Shelbyville Rd - Louisville","OX1277","Louisville - Oxmoor Woods Pky, Linn Station Rd, & Hogarth Dr - SE of Substation",13.595577335858586,554,"2019-03-16",4.4389036189004579E-3,0,0,0,0,0,0.44676300679531528,3.6217098909588949E-2,0,0.51258099067619534,147.10209700716308,403.366090835092,0.9144929177877128,2.4748154026817826,"Continue to Monitor"]
["PIRTLE","Jefferson - Rear 1506 W Main St - Louisville","PI0001","Louisville - W Market St, S 12th St, & W Main St - E of Substation",3.0499728535353539,138,"2023-04-01",0,7.7319587628865982E-3,0,0,0.39484536082474225,0,0.4484536082474227,0,0,0.14896907216494845,10.742059483751319,8.4787575890414981,7.6394995771805377E-2,0.10797976263377365,"Continue to Monitor"]
["PIRTLE","Jefferson - Rear 1506 W Main St - Louisville","PI0002","Louisville - W Market St, 22nd St, 19th St, & Cedar St - W of Substation",4.6980989583333344,545,"2023-04-01",0,0,0,7.3033707865168543E-3,7.9237909135319973E-2,0.17198339032730825,0.24198827552515878,3.9106008793356128E-2,0,0.46038104543233999,65.680790597653868,59.232723019751063,0.69349201093356538,0.82373440106944051,"Continue to Monitor"]
["PLEASURE RIDGE","Jefferson - 4400 Atlas Power Rd. - Louisville","PL1276","Louisville - Dixie Hwy, Cofer Ave, and Fury Way - W of Substation",2.3507327967171716,255,"2018-10-06",0.97869138149556401,0,0,0,0,0,1.3387198986058302E-2,0,0,7.9214195183776939E-3,25.585061809789341,49.505011231050901,0.38299125752663271,0.68229166666666663,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1382","New Albany - No Road - E of Substation",0.47245138888888882,1,"2021-12-04",0,0,0,0,0.74264705882352944,0,0,0.25735294117647056,0,0,109.19999933333334,136.18333200000001,1,2,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1389","New Albany - Campground Rd & Senn Rd - S of Substation",4.7041600378787862,7,"2021-12-04",0,0,0,0,0.40831295843520782,0,0,0,0,0.59168704156479213,104.79126972380955,116.84047599999998,0.76190476190476197,1.428571428571429,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1390","New Albany - Algonquin Pky & Gibson Ln - NE of Substation",2.8430662878787873,15,"2021-12-04",0,0,0.36051502145922748,0,0,0,0,4.4842385674115734E-2,0,0.59464259286665677,230.28794011201461,400.1091451076922,2.0966666666666667,3.4000000000000004,"Continue to Monitor"]
["PLAINVIEW","Jefferson - 9900 Shelbyville Rd - Louisville","PV1257","Louisville - US 60 and Moser Rd - E of Substation",12.931390624999997,1335,"2020-02-20",0,4.8435490784397774E-2,0,0,0,0,0,2.8560471044735716E-2,0,0.92300403817086651,12.534060210785761,19.92039974006682,0.10776086183845857,0.16596906706875927,"Continue to Monitor"]
["SEVENTH","Louisville - 1231 S 7th St - Louisville","SE0001","Louisville - 7th St, oak St, & 8th St - N of Substation",1.7844717487373738,343,"2019-12-21",0,0,0,0,0,0,0.41040462427745661,0,0,0.58959537572254339,21.033351126466417,28.756866655468031,0.37515200090715795,1.0670724430122926,"Continue to Monitor"]
["SEVENTH","Louisville - 1231 S 7th St - Louisville","SE0002","Louisville - Ormsby Ave, 6th St, & 4th St - SE of Substation",1.883493213383838,406,"2019-12-21",0,0,0,0,1.7571622083528502E-2,0,0.85540124824347075,0.12702712967300073,0,0,58.06817152133452,164.22315270935923,0.28985115255669719,0.67487684729064001,"Continue to Monitor"]
["SEVENTH","Louisville - 1231 S 7th St - Louisville","SE0003","Louisville - 7th St, Hill St, 6th St, & Shipp Ave - S of Substation",3.9738620580808082,404,"2019-12-21",0,0,0,7.4187302557831444E-2,0.51635585447875265,0,0.14633649240803018,0.23417915010700091,0,2.8941200448384795E-2,12.142274498821354,48.41624753197766,0.24710586763393733,1.1186294305106188,"Continue to Monitor"]
["SEVENTH","Louisville - 1231 S 7th St - Louisville","SE0004","Louisville - Oak St, Garvin Pl, & 4th St - NE of Substation",1.9400176767676764,552,"2019-12-21",0,0,0.15462296077750781,0,0,0,0.19896520305449497,7.4843804234640751E-3,0,0.63892745574453313,42.513086125007305,140.09525176755079,0.46306743030663072,1.8242038582629103,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1281","Louisville - 7th Street Rd, Arcade Ave, Taylor Blvd, & Clara Ave - NE of Substation",12.666589804292933,1685,"2021-12-25",1.1088771096082373E-3,0,0,1.0418570645220253E-3,3.840857856577104E-2,0,0.24027295436544202,0.36494851641991105,0,0.35421921647474564,36.732554591735038,85.668045186472824,0.28144680726342458,0.54741153965655875,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1284","Louisville - Manslick Rd - S of Substation",9.1105383522727266,1315,"2022-01-01",1.9853355893965029E-3,0,7.9278059785673996E-2,0,1.4852415867644294E-2,0,9.0528294792254188E-2,0.20286520022560633,0,0.61049069373942466,89.321665308573614,89.184691892666038,1.0880524766607895,1.1617906818098405,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1285","Louisville - Nobel Pl, Dixie Hwy, & Appleton Ln - NW & SW of Substation",8.2407035984848473,1114,"2021-12-25",4.8319887842740187E-3,0,0,6.7102634077952886E-4,0.7784444770637805,0,0.17715394961910269,1.1092904196011586E-2,0,2.780565399605173E-2,145.73932517300125,246.46764036525332,1.9483987309636064,4.6348095623109362,"Continue to Monitor"]
["SKYLIGHT","Oldham - 8617 W Hwy 42 - Skylight","SK1127","Skylight - Hwy 42, Axton Ln, Shiloh Ln, & Hwy 1694 - W of Substation",26.988789614898995,268,"2018-04-21",0,0,9.4492202567917558E-2,3.3958781065740896E-3,1.9975753568082878E-2,0,0.24340111313164711,0.5787802391579876,0,5.9954813467790823E-2,161.55208552489029,186.97999949814539,1.24462283767108,1.8101824784897649,"Continue to Monitor"]
["SKYLIGHT","Oldham - 8617 W Hwy 42 - Skylight","SK1128","Skylight - Hwy 42, Hwy 393, & Hwy 524 - NE of Substation",156.81892266414144,1476,"2018-03-06",3.5259717922256624E-3,1.2925273646991153E-2,0.31782526067660311,4.2548512070919829E-3,6.6359042898148618E-2,0,0.28680347606399481,0.21577509347138338,0,9.2531030243561324E-2,409.19924788279747,239.11164336499152,2.2112481741264758,2.7684224658343255,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1231","Louisville - Crittenden Dr, Phillips Ln, & Park Blvd - N & SE of Substation",7.0055404040404037,136,"2021-10-23",1.7293316969764588E-2,0,0,0,3.1239540332477964E-3,0,3.291308713600357E-2,0.92614080107107,0,2.0528840789914092E-2,58.182927281665819,65.423055295083671,0.52425383791588664,1.0949978531558602,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1233","Louisville - Whitney Ave, 5th St, Bluegrass Ave & Taylor Ave - SW of Substation of Substation",14.469359059343436,2760,"2021-12-31",6.9791303674449218E-3,2.8434390366670541E-3,0,0,0.19490746118403221,0,0.11988422968211562,1.5267452665814845E-2,0,0.66011828706392539,62.073084776932362,128.11462339280607,0.72681520107046904,1.5917225852510655,"Reliability Improvements Scheduled for 2023"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1235","Louisville - Fairmont Ave, 3rd St, 5th St, & 4th St - NW of Substation",12.318918087121212,2261,"2022-01-01",9.6722982242954027E-3,0,0,0,0.11490141507584964,0,0.14591744737564188,0.54322155148759355,0,0.18628728783661949,55.461411014656889,69.312108906148978,0.61529227970770761,1.2767686286972451,"Trees Trimmed in 2022"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1360","Louisville - Allmond Ave, Strawbery Ln, & Crittenden Dr - S of Substation",7.8577387941919206,103,"2021-08-21",0,0,0,0.29004678860059552,0.2982773287962569,0,8.6261165461505737E-2,3.9174819225861336E-2,0,0.28623989791578053,145.64131364115914,449.85786398964194,1.1019059707984842,3.1840028094882462,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1366","Louisville - Crittenden Dr, Woodlawn Ave, Phillips Ln, & Preston Hwy - S & E of Substation",7.8606130050505048,38,"2021-08-21",0,0,0,0,0,0,0.25272507064997979,0.35607589826402908,0,0.39119903108599113,185.14402393652662,339.31240729444448,2.5039262371615307,3.7083333333333321,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1384","Louisville - Crittenden Dr - S of Substation",2.3500618686868688,1,"Underground Circuit",0,0,0,0,1,0,0,0,0,0,320.32777733333336,573.21666600000003,1.3333333333333333,2,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1397","Louisville - Crittenden Dr, Strawberry Ln, & Mclean Ave - S of Substation",2.2669280303030304,6,"2021-08-21",0,0,0,0,0,0,0,6.3118228921337727E-2,0,0.93688177107866222,161.45388871333336,353.59722200000022,1.3800000000000001,1.8333333333333339,"Continue to Monitor"]
["SHAWNEE","Jefferson - Rear of 3908 W Broadway - Louisville","SN0003","Louisville - 40th St & Garland Ave - S of Substation",1.5587244318181817,273,"2023-03-11",0,0,0,0,0,0,0,0.74914246512691518,0,0.25085753487308482,17.75319933305245,15.97890133630791,0.22594710046450223,0.30350930377765972,"Trees Trimmed in 2023"]
["SOUTHERN","Jefferson - 1475 S 3rd Street - Louisville","SO0410","Louisville - 4th St & Hill St - W of Substation",1.6467290088383839,697,"2020-02-01",0,0,0,0,0,0,2.2834276703831251E-2,0,0,0.9771657232961688,58.442678080220198,29.582760266475631,0.74705069712285821,0.79226361031518633,"Continue to Monitor"]
["SOUTHERN","Jefferson - 1475 S 3rd Street - Louisville","SO0421","Louisville - Burnett Ave, Brook St, & Lee St - E of Substation",2.9005266729797983,507,"2020-02-01",0,0,0,0,0,0.43140442828109959,0,0,0,0.56859557171890041,82.202246005186581,92.021417665039337,0.86997824000443169,1.334660494100699,"Continue to Monitor"]
["SOUTHERN","Jefferson - 1475 S 3rd Street - Louisville","SO0422","Louisville - 2nd St & 3rd St - N of Substation",1.4786437815656566,787,"2020-02-01",0,0,0,0,8.058598896059499E-2,0,1.002217886504244E-2,3.5811362916270614E-2,0,0.87358046925809196,59.539346995747465,152.4276533228259,0.39780512824017766,0.75768055064549478,"Continue to Monitor"]
["SOUTHERN","Jefferson - 1475 S 3rd Street - Louisville","SO0453","Louisville - 3rd St, Oak St, & Brook St - N of Substation",2.3091439393939392,625,"2020-02-01",0,0,0,0,0,0,0.22871622853392642,0,0,0.77128377146607363,36.118640778354973,33.9,0.42763894894628829,1,"Continue to Monitor"]
["SOUTH PARK","Jefferson - 1412 Fairdale Rd. - Louisville","SP1116","Louisville - Fairdale Rd, Mt Holly Rd, Mitchell Hill Rd, & Holsclaw Hill Rd - SW of Substation",41.915776830808085,2081,"2019-08-17",2.5674239329856539E-2,0,1.1838539116149021E-2,5.2445224753965548E-2,0.42211635889323429,0,0.4182687208465255,5.4196407818039444E-2,0,1.546050924222969E-2,103.2902321300223,173.71278224170433,0.87735911261684885,1.8609598883886387,"Continue to Monitor"]
["SOUTH PARK","Jefferson - 1412 Fairdale Rd. - Louisville","SP1117","Louisville - South Park Rd - E of Substation",8.2232858270202041,593,"2019-10-12",8.1794830630919885E-2,0,0,0,0.32766094076095681,0,0.59054422860812328,0,0,0,5.8431218171715855,11.88037231418374,0.25259190965451805,1.0438249839598921,"Continue to Monitor"]
["South Park","Jefferson - 1412 Fairdale Rd. - Louisville","SP3302","Louisville - Blue Lick Rd, Raymond Rd, & Hwy 44 - S of Substation",9.3672847222222213,1,"2019-10-12",0,0,0,0,0,0,0,0.69738863287250386,0,0.30261136712749614,310.43333319999999,394.16666599999996,2.4,3,"Tree Trim Scheduled for 2023"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1188","Louisville - Rockford Ln, Imperial Ter, & Dover Rd - W of Substation",14.106555239898986,1896,"2022-07-03",1.9557857537868057E-2,0,0,0,0.32486275779279461,0,0.14741903721388205,0.39819123538218754,0,0.10996911207326777,67.614658788696687,44.666969669703711,0.81694175137842939,0.90872152927032068,"Trees Trimmed in 2022"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1191","Louisville - Gagel Ave, Manslick Rd, & Parkwood Rd - SE of Substation",17.46952178030303,1356,"2022-07-03",2.3051631814087058E-2,0,0,0,8.7395910976161839E-2,0,0.73432319841963034,7.5602584563043307E-2,0,7.9626674227077546E-2,62.1317869906634,56.563522533061629,0.40109243558433982,0.55757042922657329,"Continue to Monitor"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1451","Louisville - Gagel Ave, Hazelwood Ave, Manslick Rd, & Brick Kiln Ln - E & SW of Substation",2.4770489267676772,37,"2023-01-15",0,0,0,0,0,0,0.69954178485708052,0.30045821514291948,0,0,420.44012744654867,247.13717946153849,2.3847735426746981,3.2051282051282048,"Trees Trimmed in 2023"]
["SMYRNA","Jefferson - 7000 Manslick Rd. - Louisville","SY1251","Louisville - Smyrna Pky, Michael Ray Dr, & Lantana Dr - NW & SW of Substation",21.782647095959597,1550,"2022-11-06",9.4364934584594939E-2,0.14276042352321666,0,0,8.3375648041926036E-3,0,0.10708442254527674,0.53517135889768619,0,0.11228129564503288,33.990978749659398,39.945305676529578,0.2940240769896888,0.30502592081170576,"Trees Trimmed in 2022"]
["SMYRNA","Jefferson - 7000 Manslick Rd. - Louisville","SY1252","Louisville - Cooper Chapel Rd, McNeely Lake Dr, & Beulah Church Rd - SW & SE of Substation",35.738808396464648,2391,"2022-10-29",1.3780291488199616E-3,5.1707534423779001E-3,8.0310173340615749E-4,0,7.2189323597895766E-3,0,0.61537535573633828,0.22736223301808145,0,0.14269159456118666,52.44152606308397,68.775952983211454,1.1289678059374584,2.1335159153365879,"Continue to Monitor"]
["SMYRNA","Jefferson - 7000 Manslick Rd. - Louisville","SY1253","Louisville - Manslick Rd, Cinderella Ln, & Shepherdsville Rd - W of Substation",19.975250946969695,1565,"2022-05-15",2.2243259998994654E-3,2.4203682914160286E-2,0,0,3.351150282334411E-5,0,0.62157973224309238,3.6841708416413932E-2,0,0.31511703892361054,52.475768583429371,68.779936490605849,0.52882368726264561,0.58648302089557003,"Continue to Monitor"]
["SMYRNA","Jefferson - 7000 Manslick Rd. - Louisville","SY1254","Louisville - Vaughn Mill Rd, Outer Loop & Smyrna Rd - NW of Substation",17.049051136363637,1211,"2022-04-17",4.0262021801898661E-2,7.9748175324063555E-3,0.33609505494809994,0,9.1596792338854927E-2,0,0.27723436209772617,0.18738881530455601,0,5.9448135976457941E-2,44.964001276679824,60.347880847657727,0.52860376060331704,0.82946565566567287,"Continue to Monitor"]
["SMYRNA","Jefferson - 7000 Manslick Rd. - Louisville","SY1255","Louisville - Manslick Rd, Beulah Church Rd, & Fegenbush Ln - NE of Substation",33.25332102272727,2952,"2022-05-01",2.3544486265716345E-2,1.7789167400763462E-2,0,0,0.57582018632711351,0,2.3133392061076855E-2,4.4633085075144819E-3,0,0.35524945943781533,35.216328788638648,62.852548838467101,0.45621764721982877,0.35382959186956076,"Continue to Monitor"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1132","Louisville - Brownsboro Rd, Country Ln, & Country Club Rd - W of Substation",9.7953666351010114,546,"2020-07-25",4.4374306651458568E-3,0,0,0,0,0,0.12602928079248762,0.24737113482601836,0,0.6221621537163482,136.49199885747612,188.77243276506553,1.112743807559287,1.2964890076407436,"Continue to Monitor"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1134","Louisville - Brownsboro Rd, Winding Bluff Trce, I264, & Blankenbaker Ln - NE of Substation",19.7130045770202,1126,"2022-10-01",0.12610327538498284,0,3.6486301177038979E-2,0,0.19703256495691335,0,0.11426295891669913,0.44280404267163598,0,8.3310856892729712E-2,211.94565593348466,315.46058985271117,1.5701169792831635,2.9633264433987612,"Trees Trimmed in 2022"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1138","Louisville - Brownsboro Rd, Chenoweth Ln, Canoe Ln, & Wampum Rd - W of Substation",11.867115372474748,572,"2022-09-04",2.5999898272324986E-2,0,0,0,7.0912666791000493E-3,0,0.58165553313779017,0.37209864193553854,0,1.3154659975246267E-2,189.58676793615115,261.52552227031703,1.1730887384701032,2.0249758967036442,"Trees Trimmed in 2022"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1172","Louisville - Chenoweth Ln, Cherrywood Rd, & Washington Sq - SW of Substation",10.73380129419192,1119,"2022-10-16",0.13827443027649222,0,5.6567327355225371E-2,0,0.24071420074433672,0,7.3334730616938473E-2,0.46361870018636742,0,2.7490610820639767E-2,138.11011095381687,130.58306920577004,1.2404206363839774,2.0491249803657743,"Trees Trimmed in 2022"]
["TERRY","Jefferson - 8408 Terry Ln. - Louisville","TE1242","Louisville - Pages Ln & Robbins Rd - E of Substation",7.9515830176767679,860,"2022-09-18",0.13263813229571986,0,0,0,4.1011673151750971E-2,0,4.8046692607003894E-2,0.38953307392996106,0,0.38877042801556422,42.785591335208508,63.569895616054716,0.47097192110456987,0.80312674826264852,"Trees Trimmed in 2022"]
["TERRY","Jefferson - 8408 Terry Ln. - Louisville","TE1243","Louisville - Terry Rd, Greenwood Rd, & Westbrook Rd - N of Substation",19.698329229797977,1790,"2020-09-05",4.071884411023171E-2,0,0,6.526266351148742E-2,1.2786733795943857E-2,0,0.37924858907231024,0.48245598189470751,0,1.9527187615319307E-2,75.849581965069291,91.464575210977543,0.57097669661855854,0.35970883682950228,"Continue to Monitor"]
["TERRY","Jefferson - 8408 Terry Ln. - Louisville","TE1244","Louisville - Terry Rd, Johnsontown Rd, & Dixie Hwy - S of Substation",19.674856691919189,1893,"2022-09-18",0.14545363320497223,0,0,0,0.59331685962645664,0,0.1352809101513992,0.10744703535993377,0,1.8501561657238187E-2,24.52213731222318,32.820732345643087,0.26482991056974348,0.47772367423420031,"Continue to Monitor"]
["TERRY","Jefferson - 8408 Terry Ln. - Louisville","TE1245","Louisville - Pages Ln, Poinsettia Dr, Greenwood Rd, & Feyhurst Dr - NE of Substation",23.72572190656566,2368,"2020-09-12",8.3883700760801067E-3,0,2.2531644069169479E-2,1.4263785197668008E-3,1.0174306616065132E-3,0,0.69927713033187999,0.22299511830841781,0,4.4363928033079335E-2,39.568725364031934,23.774389207656533,0.86605451075355655,1.3849451282268754,"Continue to Monitor"]
["TERRY","Jefferson - 8408 Terry Ln. - Louisville","TE1248","Louisville - Greenbelt Hwy, Greenwood Rd, & Cane Run Rd - NW of Substation",7.8718413825757603,310,"2020-09-19",8.8483146067415724E-2,0,0,0,4.2134831460674156E-3,0,0.11813358302122347,0,0,0.78916978776529334,67.67119535998502,19.180031577080555,0.61837418595534499,1.0459856564386492,"Continue to Monitor"]
["Tip Top","Meade - US 60 - Tip Top","TT3313","Tip Top - US 60, Baker Rd, & Eisenhower Ave - E of Substation",6.9005370896464626,2,"2020-02-15",0,0,0,0,0.55760869565217386,0,8.1521739130434784E-2,0.36086956521739133,0,0,117.42666649999998,384.16666599999996,1.3,3.5,"Continue to Monitor"]
["WESTERN","Jefferson - 2807 W Broadway - Louisville","WE0001","Louisville - 28th St, Chestnut St, 26th St, & Muhammad Ali Blvd - NE of Substation",5.0956019570707074,884,"2022-10-30",0,0,0,0,0.39744102974687445,0,2.7683685409866356E-2,4.3342366200652835E-2,0,0.53153291864260643,39.47316055969371,71.243564083908524,0.35620833270449676,0.72233566947639216,"Continue to Monitor"]
["WESTERN","Jefferson - 2807 W Broadway - Louisville","WE0002","Louisville - Broadway, Louis Coleman Jr Dr, & 35th St - W of Substation",3.0946343118686865,405,"2022-10-30",0,0,0,0,0.9505459216441875,0,4.9092345285289274E-3,4.3046235392258915E-2,0,1.4986084350246201E-3,192.30790802437156,345.9657169468648,0.66396658190191504,1.2055087447259047,"Continue to Monitor"]
["WESTERN","Jefferson - 2807 W Broadway - Louisville","WE0006","Louisville - 28th St, Chestnut St, 30th St, & 31st St  - NW of Substation",1.4620879103535356,158,"2022-10-30",0,0,0,6.1586599000267105E-2,3.0729703259943272E-2,0,0.86184352781063578,1.3813103369328806E-2,0,3.2027066559824985E-2,201.86979429904898,254.73264405557239,0.67268632661000383,1.1590247443506194,"Continue to Monitor"]
["WHAS","Jefferson - 1310 Flat Road Rd. - Louisville","WH1115","Louisville - Flat Rock Rd, Polo Fields Ln, & Glen Lakes Dr - SW of Substation",27.811253314393937,1040,"2020-10-31",1.0330110459689915E-3,3.2712016455684733E-3,0,0,2.3007149523818153E-2,0,0.16494649184011889,0.14800148608606614,0,0.65974065985845931,70.976401953558366,89.690073322955627,0.81506208098308686,0.7613605292649045,"Continue to Monitor"]
["WHAS","Jefferson - 1310 Flat Road Rd. - Louisville","WH1116","Louisville - Flat Rock Rd, Long Run Rd, & Aiken Rd - NW & SE of Substation",32.041286458333325,1131,"2020-12-26",1.1374487445936079E-2,0,0,6.7685221591866542E-3,0.46073695444587992,0,0.29433241588496323,0.20344885693422457,0,2.3338763129809582E-2,52.877772036091116,31.51998866562181,0.59938082213436972,1.05567892871131,"Continue to Monitor"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1179","Louisville - Chamberlain Ln - NW of Substation",26.132453440656565,1182,"2021-10-23",0,3.0433844161450466E-2,0,0,2.9755480867071629E-3,0,5.9480127038944217E-2,0.89892386913755362,0,8.1866115753445774E-3,72.353376656992921,45.099530317361356,0.53738523719551223,0.69530272944367644,"Continue to Monitor"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1180","Louisville - Brownsboro Rd, Norton Health Care Blvd, & Summit Plaza Dr - W of Substation",8.1160443497474795,173,"2021-10-23",2.8874484384207425E-2,0,0,0,0,0,0.97112551561579252,0,0,0,5.8153997238205983,9.751915706896547,1.7396230535052553E-2,2.8735632183908007E-2,"Continue to Monitor"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1181","Louisville - Chamberlain Ln - S of Substation",7.9919520202020209,984,"2021-09-11",7.0489767405759227E-2,0,0,0,0,0,0,0,0,0.92951023259424082,29.98482010737531,78.331557950843248,0.50106682348583764,0.97373572174306522,"Continue to Monitor"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1183","Louisville - Ballardsville Rd, Haunz Ln, & Hitt Ln - NE of Substation",32.284721748737375,1391,"2021-10-23",1.5465404530586101E-2,1.6374846592770425E-2,9.4146811329887878E-2,0,4.1687650656900756E-2,0,0.1517301401812039,2.4046430439905928E-2,0,0.656548716268745,181.0945891415607,144.18201738843248,1.5854283389966131,1.5910226061942767,"Continue to Monitor"]
["WEST POINT","Hardin - Crop St and I-C Railroad - West Point","WP1104","West Point - Main St, Dixie Hwy, 16th St, & Private Rd - W, SW & NE of Substation",23.946580176767682,687,"2019-02-09",2.1788842386849031E-2,0,0.13735599948224533,0,2.3169521508391942E-2,4.7838374250334381E-3,0.37598157656297188,0.23770871985157699,0,0.19921150278293134,96.654238106935168,115.19057770229779,1.1652099346323976,1.3352775828772905,"Continue to Monitor"]
["WATERSIDE","Jefferson - 221 North Third St. - Louisville","WS1305","Louisville - Main St, 1st St, Floyd St, & Bingham Way - E of Substation",3.5355025252525243,48,"2023-04-01",0,0,0,0,0,0,0,1,0,0,37.156190472108854,61.866666666666703,0.30340136054421774,1,"Trees Trimmed in 2023"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1151","Louisville - Hurstbourne Pky, Watterson Trl, Ferndale Rd, & Johnson School Rd - S of Substation",27.678349431818177,2667,"2021-12-04",1.738610047918135E-3,2.7724165119738615E-3,0,0,5.7306062019879143E-3,0,0.68343825027192373,5.0065162423900356E-2,0,0.25625495454229602,85.943698877163712,84.632753827949927,0.82328232356407494,1.1485880082461535,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1152","Louisville - Bardstown Rd, Seatonville Rd, & Fern Creek Rd - SE of Substation",31.882722853535356,2536,"2021-12-01",1.0110601662190149E-2,2.6666184348161613E-2,0.33170852286943336,2.8034763106251754E-3,1.1120456032146528E-2,0,9.4676108051403085E-2,0.14912685278131979,0,0.37378779794472028,38.873170688019606,81.150165365394756,0.35376132780627279,0.92359591453287837,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1154","Louisville - Walt Lee Rd, Fairground Rd, Billtown Rd, & Easum Rd - E of Substation",43.704380208333333,2870,"2021-12-31",1.5393603221317989E-2,0,0,0,4.3533021964388352E-2,0,0.57080397890564394,0.33540842831970702,0,3.4860967588942741E-2,46.670482924467493,63.980786015568249,0.53104732311311387,0.58617304956259619,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1155","Louisville - Hurstbourne Pky, Watterson Trl, & Glaser Ln - S of Substation",18.435299242424236,1800,"2021-12-04",5.553354650669232E-3,0,4.5098899233141852E-4,0,9.525594951753022E-3,0,1.6431916579416509E-2,0.8779446928322816,0,9.0093451993548207E-2,58.919867203094455,75.654787305509913,0.49777805962407057,0.33712018973765928,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1209","Louisville - Laverne Dr, Watterson Trl, & Dell Rd - NE of Substation",25.816981691919192,1525,"2021-12-18",1.5532116180229029E-3,0,0.1323618700667881,0,3.7940723796614E-2,4.363112636082518E-3,8.6810409341861877E-2,0.48584459411756398,0,0.25112607842306661,24.673503015215715,29.472392624894823,0.20876406605137671,0.23469440529233968,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1210","Louisville - Bardstown Rd, Hudson Ln, Fairground Rd & Janet Lee Dr - SE of Substation",22.316643465909095,1966,"2022-01-08",2.3128551381444248E-2,0,0,0,0.43436989578780277,0,0.28940739377487407,0.16652096896638985,0,8.6573190089489063E-2,69.51876236841062,116.07655802008343,0.86813437562354745,0.57085939470813685,"Continue to Monitor"]

{"sheet":"LGE Section 6-7","index":2,"n_rows":29,"n_cols":1,"rows_kept":29,"cut":false,"hidden":false,"merged":[[28,0,31,8],[20,0,21,8],[27,0,27,8],[16,0,16,3],[17,0,17,3],[18,0,18,3],[19,0,19,3],[15,0,15,3],[0,0,0,8],[2,0,2,8],[4,0,4,8],[5,0,10,8],[11,0,14,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
[]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 6: VEGETATION MANAGEMENT PLAN REVIEW"]
["The Companies’ Vegetation Management Plan was submitted December 19, 2007.  The Distribution Vegetation Management Program encompasses right of way maintenance for Louisville Gas and Electric Company and Kentucky Utilities Company (referred to as the “Companies”).  The program is centralized and managed by a Forestry Manager and eight company Utility Arborists.  All are certified arborists by the International Society of Arboriculture."]
[]
[]
[]
[]
[]
["The Companies’ plan is to maintain a proactive trim cycle while balancing the reactive needs of worst performing circuits. The Companies’ goal is to maintain an average trim cycle of five years or less.   The effectiveness of the plan is evaluated by the cycle and system performance as measured by system SAIDI, SAIFI, and CAIDI.  "]
[]
[]
[]
["Effectiveness of the program"]
["KU/LG&E Tree Cycle – 4.92 years"]
["LGE Tree SAIDI – 18.07 minutes"]
["LGE Tree SAIFI – 0.150"]
["LGE Tree CAIDI – 120.8 minutes"]
["The hazard tree program, mid cycle, herbicide, and worst performing circuits were completed as planned.  "]
[]
["Adjustments made to the tree plan in 2022 included"]
["No changes made to plan."]
["Changes to be implemented in 2023"]
["No changes made to plan. Continue targeted hazard tree and mid-cycle trim work."]
[]
["SECTION 7: UTILITY COMMENTS"]
["SAIDI and CAIDI improved in 2022 compared to the previous 5 year average including and excluding major events.  255 Circuits were above their previous 5 year average SAIDI and/or SAIFI in 2022.  "]