{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["KU Section 1-4","Excel KU Section 5","KU Section 6-7"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"KU Section 1-4","index":0,"n_rows":46,"n_cols":8,"rows_kept":46,"cut":false,"hidden":false,"merged":[[5,0,5,3],[5,5,5,8],[0,0,0,8],[1,0,1,8],[3,0,3,8],[4,0,4,3],[4,5,4,8],[17,0,17,3],[17,5,17,8],[6,0,6,3],[6,5,6,8],[7,0,7,3],[7,5,7,8],[10,0,10,8],[11,0,11,3],[11,5,11,8],[14,0,14,8],[15,0,15,3],[15,5,15,8],[16,0,16,3],[16,5,16,8],[35,1,35,3],[35,6,35,8],[33,3,33,5],[18,0,18,3],[18,5,18,8],[44,0,44,8],[45,2,45,6],[20,0,21,8],[24,0,24,8],[25,2,25,6],[26,0,26,1],[26,5,26,6],[28,3,28,5],[29,1,29,3],[29,6,29,8],[30,1,30,3],[30,6,30,8],[31,1,31,3],[31,6,31,8],[34,1,34,3],[34,6,34,8],[36,1,36,3],[36,6,36,8],[37,0,37,8],[41,1,41,8],[38,1,38,8],[39,1,39,8],[40,1,40,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 1: CONTACT INFORMATION"]
["UTILITY NAME",null,null,null,null,"KENTUCKY UTILITIES COMPANY"]
["REPORT PREPARD BY",null,null,null,null,"Karmen Powell (Mgr Investment Strategy & Reliability)"]
["E-MAIL ADDRESS OF PREPARER",null,null,null,null,"Karmen.Powell@lge-ku.com"]
["PHONE NUMBER OF PREPARER",null,null,null,null,"(502) 399-4805"]
[]
[]
["SECTION 2: REPORTING YEAR"]
["CALENDAR YEAR OF REPORT",null,null,null,null,2023]
[]
[]
["SECTION 3: MAJOR EVENT DAYS (MED)"]
["TMED",null,null,null,null,3.5760000000000001]
["FIRST DATE USED TO DETERMINE TMED",null,null,null,null,"2018-01-01"]
["LAST DATE USED TO DETERMINE TMED",null,null,null,null,"2022-12-31"]
["NUMBER OF MED IN REPORTING YEAR",null,null,null,null,12]
[]
["NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years.  If five years of data are not available, then utilities should use what is available until five years are accumulated.        \n"]
[]
[]
[]
["SECTION 4: SYSTEM RELIABILITY INFORMATION AND RESULTS"]
[null,null,"System-wide Information"]
["TOTAL CUSTOMERS",null,556811,null,null,"TOTAL CIRCUITS",null,1113]
[]
[null,null,null,"Excluding MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",72.556085254412125,null,null,null,"SAIDI",66.468809819182084]
["SAIFI",0.66585045349519201,null,null,null,"SAIFI",0.60708344552944105]
[]
[null,null,null,"Including MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",285.90869561471055,null,null,null,"SAIDI",894.90287784998634]
["SAIFI",0.89452330604829411,null,null,null,"SAIFI",1.2252758349952986]
["Notes:  "]
["1)","All duration indices (SAIDI) are to be reported in units of minutes."]
["2)","Reports are due on the first business day of May of each year"]
["3)","Reports cover the calendar year ending in the December before the reports are due."]
["4)","IEEE 1366 (latest version) is used to define SAIDI, SAIFI, and TMED"]
[]
[]
["SECTION 5: CIRCUIT REPORTING"]
[null,null,"BEGIN ON NEXT PAGE"]

{"sheet":"Excel KU Section 5","index":1,"n_rows":407,"n_cols":22,"rows_kept":407,"cut":false,"hidden":false,"merged":[]}
["Substation Name","Substation Location   \n(County - Road - Town)","Circuit\nNumber","Circuit Location\n (Town - Road - General Area)","Total Circuit Length (Miles)","Average 2023 OMS Custs","Date of Last Circuit Trim (VM)","Animal","Construction","Lightning","Non-Company","Other/Unknown","Overload","Planned Work","Trees","Vehicle","Utility Equipment","2019-2023 SAIDI Average","2023 SAIDI","2019-2023 SAIFI Average","2023 SAIFI","LIST OF CORRECTION ACTION, IF ANY, TAKEN OR TO BE TAKEN"]
["BUCHANAN","Fayette - 108 Buchanan St. - Lexington",5,"Lexington - W. Main St. and Jefferson St. - E of Station",5.07,616,"2023-08-05",0,0,7.1114521132868536E-2,6.751843079694432E-3,0.7400940721219601,0,3.8296026953998068E-3,0.17820996097007705,0,0,12.672183445943977,22.123108542995212,0.16695428227256856,0.49895209842140309,"Continue to Monitor"]
["LEXINGTON PLANT","Fayette - 745 N Limestone - Lexington",7,"Lexington - N. Limestone St and York St. - NE amd SE of Station ",6.4499999999999993,1223,"2023-04-21",0,0,9.912289493167116E-3,0,0,2.3112510628392598E-2,0.17398880745393824,0.69089562999291987,0,0.10209076243158224,31.331391606068838,39.245479611308177,0.25412301875612359,0.19940185122836271,"Trees Trimmed in 2023"]
["AMERICAN AVENUE","Fayette - 96 Burley Ave. - Lexington",9,"Lexington - Nicholasville Rd. - S of Station",7,846,"2019-07-20",8.6699172907341352E-4,0,0,0,3.0063116680587715E-4,0,0.82709821120489646,1.3191283123962366E-3,0,0.17041503758682808,97.995324780588675,315.80644168248,0.37035887583059474,0.64807854080073946,"Continue to Monitor"]
["LEXINGTON WATER COMPANY 4KV","Fayette - 2300 Richmond Rd. - Lexington",11,"Lexington - Richmond Rd and Holiday Rd - NW of Station",3.36,150,"2022-05-06",0,0,0,0,0.31969324550191724,0,0.32842395044735034,0.35188280405073247,0,0,36.059560153234955,109.18590212061811,0.20223904731786152,0.29165562913907284,"Continue to Monitor"]
["LEXINGTON WATER COMPANY 4KV","Fayette - 2300 Richmond Rd. - Lexington",16,"Lexington - Fontaine Rd - W of Substation",3.62,700,"2020-09-12",0,0,1.0241404535479151E-3,0,0,0,0.98220119643964521,1.6048332893920884E-2,0,7.263302128860486E-4,39.313084178177988,39.895413869411215,0.27778514070626825,0.70156235902312947,"Continue to Monitor"]
["SCOTT STREET","Fayette - 301 Scott St. - Lexington",17,"Lexingotn - Broadway Rd. - SE of Substation",4.83,990,"2019-07-20",0,0,0,0,0.53060596739464783,0,0.46939403260535223,0,0,0,1.9235373323290836,3.2794147315842586,1.575861813026469E-2,4.1372351160443993E-2,"Continue to Monitor"]
["KUNKEL","Fayette - 2000 Versailles Rd. - Lexington",19,"Lexington - Versailles Rd. - NE of Substation",2.15,204,"2020-03-28",2.3502604633165902E-3,0,0,0,1.8558459146310879E-3,0,0.99053446929255728,0,0,5.2594243294950523E-3,39.692608167210679,58.824065034146344,0.37186585143282536,0.37073170731707317,"Continue to Monitor"]
["JOYLAND","Fayette - 2375 Paris Pike - Lexington",25,"Lexington - Beverly Ave. & Bryan Station Rd. - SW of Substation",28.04,1701,"2020-04-04",2.1333378139588286E-3,0,1.3895539817358504E-3,1.3727516361284036E-3,2.2568910619922541E-2,0,0.13358312820469737,0.82082314691130875,0,1.8129170832248184E-2,40.706669744501419,60.321418881880604,0.37495771034657355,0.87013056543646661,"Continue to Monitor"]
["KUNKEL","Fayette - 2000 Versailles Rd. - Lexington",26,"Lexington - Duntreath Dr. & Pine Mt. Rd. - SE of Substation",4.67,572,"2020-03-28",0,0,0,0,0,0,0.98104585565743541,8.959989324741232E-3,0,9.9941550178233723E-3,214.88752269814216,794.16255774340675,0.96684553102408244,2.3812526091906681,"Continue to Monitor"]
["MOUNT TABOR","Fayette - 248 Old Mt. Tabor Rd - Lexington",27,"Lexington - Tates Creek Rd. & Raintree Rd. - NW of Substation",3.08,189,"2019-03-23",0,0,0,0,0,0,0.85599341943535734,0.11997396768967973,0,2.4032612874962968E-2,37.609513636963335,149.38964911578947,0.20623312207219618,0.8789473684210527,"Continue to Monitor"]
["WEST HIGH STREET","Fayette - 727 West High St - Lexington",29,"Lexington - W High St & S Mill St - SE of Substation",0.44,3,"2019-05-11",0,0,0,0,1,0,0,0,0,0,20.966666666666665,62.9,0.33333333333333331,1,"Continue to Monitor"]
["RACE STREET 4KV","Fayette - 420 Corral St - Lexington",30,"Lexington - Midland Ave. & Winchester Rd. - E of Substation",5.18,939,"2023-12-23",0,0,0,0,0.38510991289921193,0,0.51321150608729593,0,0,0.10167858101349209,33.262181595089096,52.055158836144166,0.45348338992961745,0.66282605394616201,"Continue to Monitor"]
["G E LAMP WORKS","Fayette - 1809 Edision Dr - Lexington",32,"Lexington - Edision Dr. - Rosemont Garden",2.16,284,"2020-05-09",4.9741990925054901E-2,0,0,0,0,0,0.95025800907494506,0,0,0,22.234964992342036,50.943157891228068,0.19661906949970487,0.37543859649122807,"Continue to Monitor"]
["BELT LINE","Fayette - 1090 W. New Circle Rd - Lexington",36,"Lexington - Georgetown St. & Briarwood Dr. - NW of Substation",7.06,565,"2021-09-11",1.8843779855010022E-3,9.951670007305696E-6,0,4.0099376205908249E-4,4.5830367345409588E-3,0,0.99255029691100161,5.7134293689002115E-4,0,0,55.921103776857045,120.47992457955638,0.40378100696334907,0.71850278961880787,"Continue to Monitor"]
["HUGHES LANE","Fayette - 251 Hughes Ln. - Lexington",37,"Lexington - Mir Station Rd. & US 27 - SW of Substation",138.15999999999997,1112,"2019-12-31",2.6879887446723983E-4,1.2768604712694548E-4,5.1442997131144626E-4,3.5080754184877287E-3,7.4075809707246171E-2,4.4492663844234608E-5,0.76167070216005295,0.1429141220504852,0,1.6875883106978004E-2,273.06146733183886,329.25453368131832,1.7422277940159574,2.1332723458166538,"Continue to Monitor"]
["LANSDOWNE SWITCHING","Fayette - 3200 Montavesta Rd. - Lexington",38,"Lexington - Tates Creek Rd. - S of Substation",7.98,1591,"2024-03-09",4.3270048412724473E-3,4.433621296138824E-3,0,0,7.6033395667682779E-4,0,0.88839692014944016,9.8252043512794526E-2,0,3.8300762436772567E-3,46.184127359826086,81.66807882877383,0.55912708319499738,0.73601746946338786,"Continue to Monitor"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",44,"Lexington - Nicholasville Rd . - E of Substation",14.490000000000002,1643,"2023-04-05",2.5930963988295277E-4,0,5.4153647554248615E-4,0,1.2835670207111802E-2,0,0.82399860487646537,9.717832811836323E-3,0,0.1526470459891611,92.982501396294694,97.666572690727975,0.6894778140073391,0.58779036848213739,"Continue to Monitor"]
["HALEY","Fayette - 5481 Winchester Rd - Lexington",45,"Lexington - Winchester & Cleaveland Rd - W of Substation",89.679999999999993,1130,"2021-01-16",5.7635678373133318E-4,0,9.1353898950239396E-4,1.9961186581646798E-4,0.28086573404566195,2.3228107508673075E-5,0.63603473726013238,4.042589859057838E-3,0,7.7344203088589011E-2,284.91505810499427,606.88504165006952,1.6746225261418815,2.6786511800882349,"Reliability Improvements Scheduled for 2024"]
["JOYLAND","Fayette - 2375 Paris Pike - Lexington",47,"Lexington - US 27 & 68 - NE of Substation",17.279999999999998,241,"2019-09-28",2.1192560101563076E-3,0,0,0,9.5302707677013293E-2,0,0.77521444452654276,0.12736359178628764,0,0,102.02010327503896,180.16375745748257,0.46643578797890201,0.66567098821174819,"Continue to Monitor"]
["ASHLAND AVENUE","Fayette - 448 S Ashland Ave. - Lexington",50,"Lexington - Fountaine Rd & Ridge Way Rd. - SE of Substation",4.75,991,"2019-11-23",0,0,4.0217064565633551E-2,0,1.8431502839875331E-2,0,0.90042242156723151,3.1220170761677241E-2,0,9.7088402655823979E-3,39.609034337013732,91.993690149211716,0.23986300568421473,0.44695030617543713,"Reliability Improvements Scheduled for 2024"]
["PARKERS MILL","Fayette - 2085 Parkers Mill Rd - Lexington",51,"Lexington - New Circle Rd & Viley Rd - N of Substation",13.59,1153,"2018-06-09",9.5695103681901663E-4,0,0,0,0,0,0.86833867278377541,0.10088265713404557,0,2.9821719045359966E-2,68.391086790204142,141.22733066344745,0.79373368480459328,1.000883891714383,"Continue to Monitor"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",53,"Lexington - New Circle Rd. - West of Substation",4.0299999999999994,128,"2020-05-09",0,0,0,0,0,0,9.0575916230366496E-2,0.90942408376963346,0,0,3.2332733913848499,14.9225260390625,9.386270481310803E-2,0.4453125,"Continue to Monitor"]
["HAEFLING"," Fayette - 1555 Baunmann Dr - Lexington  ",55,"Lexington - Fairman Rd & Leestown Rd - S of Substation",17.239999999999998,1354,"2022-01-14",3.1224189241748205E-3,0,0,0,0.16104711378365505,0,0.81492184120019751,5.9105270748025822E-3,0,1.4998099017170027E-2,49.323461365140773,72.811974279360214,0.48397824231360709,0.9576396114666329,"Continue to Monitor"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",56,"Lexington - Lochness Dr. & New Circle Rd. - E of Substation",9.19,1556,"2020-06-06",5.0940606015226328E-4,0,2.1700084420245271E-2,0,1.2854831240830308E-3,0,0.79188706406272191,0.16650612192541989,0,1.8111840407377549E-2,81.210303454370347,107.52995305671477,1.2159868434294583,1.4078492560769327,"Continue to Monitor"]
["PICADOME 12KV","Fayette - 1620 Harrodsburg Rd - Lexington ",62,"Lexington - Mason Headley Rd - NW of Substation",3.9699999999999998,293,"2020-04-11",2.5216856707601282E-2,0,0,0,0.9712466472908694,0,1.2567127933362362E-3,1.432534583202057E-3,0,8.4724862499100241E-4,82.714676717927588,83.301086180806095,0.8115222751742307,0.7891272549975622,"Continue to Monitor"]
["HUGHES LANE","Fayette - 251 Hughes Ln. - Lexington ",63,"Lexington - US 27 & 68 - NE of Substation",25.009999999999998,230,"2019-12-31",1.3987555781685587E-2,0,0,0,9.7192100995325464E-2,0,0.77235560360818734,1.6005766315811789E-3,0,0.11486416298322044,249.64062992379345,263.18785654557718,0.80658182706161985,0.74875549238367822,"Continue to Monitor"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",69,"Lexingotn - Lowry Ln. & Nicholasville Rd. - N of Substation",9.57,847,"2020-05-09",3.7730927631260562E-5,0,1.2078818267346589E-2,0,0,0,0.95425863238511133,2.980251140335264E-2,0,3.8223070165581356E-3,53.189374337079322,56.30245734533073,0.32006326609151381,0.35429999212540941,"Continue to Monitor"]
["WILSON DOWNING","Fayette - 680 Wilson Downing Rd - Lexington",72,"Lexington - Tates Creek Rd & Trent Blvd - NE of Substation",9.02,1338,"2023-12-30",3.6500109479864914E-3,1.4319011366124542E-2,2.62547040530742E-3,0,4.8587232260339707E-3,0,0.38197695397684761,0.56676327724735553,0,2.5806552830344408E-2,56.717627694585055,53.962014932686941,0.48570251613517268,0.64300456302719866,"Trees Trimmed in 2023"]
["WILSON DOWNING","Fayette - 680 Wilson Downing Rd - Lexington",73,"Lexington - Wilson Downing Rd - W of Substation",17.73,3085,"2023-08-12",2.6091203859402849E-3,0,6.8794513379822342E-3,0,0.10586414017028382,0,0.80609058529391198,6.3611937645254912E-2,0,1.4944765166626775E-2,80.321477351648824,95.187471687221034,0.48714579925145884,0.56957310659556404,"Continue to Monitor"]
["PARKERS MILL","Fayette - 2085 Parkers Mill Rd - Lexington",74,"Lexington - New Circle Rd - SE of Substation",10.39,1345,"2023-06-09",1.1034655188060937E-3,0,8.6674531963737891E-3,0,5.2254341189214484E-3,2.8107518570895959E-4,0.97492981634751719,7.7909714162763561E-3,0,2.0017842163962394E-3,56.8255721919219,149.80330256117375,0.49041388828668164,1.2809995826517624,"Continue to Monitor"]
["TRAFTON AVENUE 12KV","Fayette - 141 Trafton St - Lexington ",79,"Lexington - Red Mile Rd - S of Substation",7.23,1336,"2019-12-31",0.13535187474514729,0,4.1164782104970198E-3,0,0,0,0.84216930634753173,1.231059993139203E-2,0,6.0517407654319391E-3,46.810410181525711,115.94397019846255,0.45886448471949393,0.69831348729891329,"Continue to Monitor"]
["PARKERS MILL","Fayette - 2085 Parkers Mill Rd - Lexington",83,"Lexington - Versailles Rd - W of Substation",28.53,285,"2023-12-09",8.2769304769073635E-4,0,0,0,3.0031202466212943E-3,0,0.89625101899945958,9.3879131828077222E-2,0,6.0390358781510899E-3,94.75762121952701,142.36181208796941,0.83280541444473499,1.2522534042115943,"Continue to Monitor"]
["BELT LINE","Fayette - 1090 W. New Circle Rd - Lexington",86,"Lexington - New Circule Rd & New Town Rd. - E of Substation",2.74,157,"2021-09-11",0,0,0,0,0,0,0,0.46317037817894319,0,0.53682962182105676,49.521337646204081,96.674309974522288,0.36721856351319754,0.46496815286624205,"Continue to Monitor"]
["TRAFTON AVENUE 12KV","Fayette - 141 Trafton St - Lexington ",88,"Lexington - Dunkirk Dr - W of Substation",9.36,1655,"2020-04-25",4.4909665692077435E-4,0,3.2321968899128623E-3,2.4858056691957737E-3,0.42812699785380048,0,0.55851256217993739,5.0822153084431106E-3,0,2.1111254417895573E-3,42.034750647730192,61.416348972755976,0.54366210886277844,0.45042006628979947,"Reliability Improvements Scheduled for 2024"]
["AMERICAN AVENUE","Fayette - 96 Burley Ave. - Lexington",90,"Lexington - Stanley Ave. & Waller Ave. - W of Substation",1.1600000000000001,221,"2019-07-20",0,0,0,0,0.55854177754124534,0,0.44145822245875466,0,0,0,21.191463378318797,34.008672696832583,0.18654348628871084,0.1764705882352941,"Continue to Monitor"]
["LIBERTY ROAD","Fayette - 2125 Liberty Rd. - Lexington",91,"Lexington - Liberty Rd. & Winchester Rd. - W of Substation",12.559999999999999,1725,"2022-10-29",8.1033847521895823E-4,0,0,0,9.6301557066817478E-5,0,0.99553499347848406,1.4470786211980649E-3,0,2.1112878680320515E-3,70.715198634598622,48.557860251069243,0.56114448235715242,0.78391166912276777,"Continue to Monitor"]
["LIBERTY ROAD","Fayette - 2125 Liberty Rd. - Lexington",92,"Lexington - New Circule Rd. & Winchester Rd. - E of Substation",19.059999999999999,1469,"2023-01-06",2.3592567647874488E-2,0,1.317301216275108E-3,0,4.377798027019532E-3,0,0.30068143100511074,0.31647914107998892,0,0.3535517610237312,43.525795137538367,36.164781084095104,0.70303313087350017,0.91336401706468318,"Trees Trimmed in 2023"]
["G E LAMP WORKS","Fayette - 1809 Edision Dr - Lexington",94,"Lexington - Edision Dr. & Bob O Link Dr. - N of Substation",1.6,150,"2020-05-09",5.9958744316448527E-3,0,2.1303330960647307E-2,0,0.59256017664405347,0,0.32392248580020044,5.2982321067999244E-2,0,3.2358110954546116E-3,56.345385572300209,85.70353200662251,0.38927152317880787,0.82781456953642385,"Continue to Monitor"]
["STONEWALL","Fayette - 3060 Arrowhead Dr - Lexington",96,"Lexington - New Circle Rd & Southview Dr - NE of Substation",13.01,1295,"2022-09-03",1.9631770612275179E-4,2.4449383032465406E-4,2.278730674749978E-4,2.1799696201360783E-4,4.0082535335982697E-4,0,0.87623071931289287,0.12066697916912565,0,1.814794598685659E-3,155.41623620675404,160.17198626776013,0.9026770583851178,0.41149514100521206,"Continue to Monitor"]
["STONEWALL","Fayette - 3060 Arrowhead Dr - Lexington",97,"Lexington - W New Circle Rd & Harrodsburg Rd - NW of Substation",22.85,2134,"2023-01-27",4.281863952520397E-4,0,0,0,4.426103108592953E-3,0,0.98085093046841976,1.2788198266663209E-2,0,1.5065817610719913E-3,26.145273707650169,28.35755435020193,0.56371255556680677,1.1840938193414301,"Continue to Monitor"]
["PARKERS MILL","Fayette - 2085 Parkers Mill Rd - Lexington",100,"Lexington - Parkers Mill Rd & Alexandria Rd - NE of Substation",12.470000000000002,1746,"2023-09-09",4.1619234909353518E-4,0,1.2403546679584548E-4,1.0085535487701683E-3,0.45472136893168724,0,0.53160009076107217,8.7808013390931975E-3,0,3.3489576034878283E-3,58.594816512274008,74.423547843288404,0.81788113484448388,1.5776604111808592,"Reliability Improvements Scheduled for 2024"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",102,"Lexington - Mall Rd - S of Substation",5.3500000000000005,614,"2020-10-10",0.14023865174068151,0,0,0,0.18919916348874399,0,0.6705621847705745,0,0,0,2.8744941183973287,8.8780944609120525,1.540842885074987E-2,2.2801302931596091E-2,"Continue to Monitor"]
["DONERAIL","Fayette - 4601 Old Iron Works Rd - Lexington",105,"Lexington - Iron Works Rd - E of Substation",58.64,486,"2023-12-09",1.0528836900633417E-3,0,1.7717923600470231E-3,0,2.7833211620605945E-2,0,0.94679879847390669,1.4322118906866832E-2,0,8.2211949485102246E-3,251.90800808917743,263.95057711581302,1.5837390291331845,1.4688297082855619,"Continue to Monitor"]
["IBM","Fayette - 740 W New Circle Rd - Lexington ",110,"Lexington - Russell Cave Rd - NE of Substation",22.099999999999998,2098,"2023-04-07",1.8518929590853419E-3,0,0,0,0.9356172584802529,0,2.5276886234425557E-2,2.9205915611395621E-2,0,8.0480467148404747E-3,40.628652282734699,60.711649015776217,0.49657613186996308,0.39195311559992357,"Continue to Monitor"]
["PICADOME 12KV","Fayette - 1620 Harrodsburg Rd - Lexington ",112,"Lexington - Della Dr - W of Substation",11.37,1602,"2020-04-11",4.0154552334465896E-4,0,4.8777138145730359E-4,0,5.709919617537209E-2,0,0.87484984133600296,3.4106115048865529E-2,0,3.3055530534957488E-2,106.97858766613346,232.95991990830754,0.81729632982492273,1.6751970254322586,"Continue to Monitor"]
["VILEY ROAD","Fayette - 308 Alexandria Rd. - Lexington ",115,"Lexington - Alexandria Rd & Leestown Rd - NE of Substation",2.0499999999999998,21,"2021-12-17",0,0,0,0,0,0,0,0,0,1,16.333794466403162,50.086363636363643,7.1936758893280633E-2,0.27272727272727271,"Continue to Monitor"]
["VILEY ROAD","Fayette - 308 Alexandria Rd. - Lexington ",116,"Lexington - Alexandria Rd. & Old Frankfort Rd. - SW of Substation",31.099999999999998,323,"2021-12-17",5.3973740865399192E-3,0,0,0,0,0,1.2159252857879256E-2,9.5515327935959248E-3,0,0.97289184026198494,53.048429208104764,101.97714931017158,0.36748820117729958,1.0614454272378224,"Continue to Monitor"]
["LANSDOWNE SWITCHING"," Fayette - 3200 Montavesta Rd - Lexington",118,"Lexington - New Circle Rd. & Chinoe Rd. - SW of Substation",13.870000000000001,1100,"2024-03-16",2.071954086063174E-4,0,3.2682423889277036E-2,0,5.0702767225504976E-4,0,0.44978304589979379,0.41784030254772564,0,9.8980004582342143E-2,51.096219665561918,68.705166630104628,0.76160417492952082,1.1745231863076666,"Trees Trimmed in 2024"]
["VINE STREET 12KV","Fayette - Vine St. - Lexington ",125,"Lexington - Vine, Upper & Limestone St. - W of Substation",5.34,1679,"2019-05-11",0,0,0,0,8.2978870693567366E-2,0,0.80231368597558628,0,0,0.11470744333084633,54.541161380346566,84.950875737919205,0.54130628153775096,1.0688417443480125,"Continue to Monitor"]
["LOUDON AVENUE","Fayette - 811 E Loudon Ave - Lexington  ",127,"Lexington - Floyd Dr - N of Substation",10.26,1309,"2023-04-14",4.4264340179529307E-3,7.4158425468310457E-4,0,0,1.080405860822763E-2,0,0.71479987936896128,0.17429866729069607,0,9.4929376459479006E-2,76.614688160378023,54.083581099256826,0.57503052665789456,1.1292071463453905,"Continue to Monitor"]
["LEXINGTON WATER COMPANY 12KV","Fayette - 2300 Richmond Rd - Lexington ",130,"Lexington - Richmond Rd.  - E of Substation",24.76,3220,"2020-08-22",4.8259319356268852E-4,0,6.687745127586452E-3,2.618772148854832E-4,6.5889836475201496E-2,0,0.81282979166170211,9.1638674689751967E-2,0,2.2209481637309871E-2,76.272400614908562,202.60675366122925,0.65483206934795712,1.6949401020855746,"Reliability Improvements Scheduled for 2024"]
["LAKESHORE","Fayette - 3710 Richmond Rd - Lexington ",135,"Lexington - Richmond Rd & Man O War Blvd - E of Substation",28.439999999999998,2592,"2018-09-01",2.4135461738251706E-4,5.6628000823107268E-4,1.7810395703906339E-2,0,3.4107345083458203E-2,0,0.83484358321457852,0.10540720507925001,0,7.0238362931933276E-3,48.870645875092706,71.737335531282213,0.54572991785730307,0.72487367018785087,"Continue to Monitor"]
["RACE STREET 12KV","Fayette - 420 Corral St - Lexington ",139,"Lexington - Midland Ave. , Mian St. & water St. - W of Substation",2.73,15,"2024-01-06",0,0,0,0,0,0,0,0,0,1,60.187852530769234,190.4145831875,0.37788461538461537,1.25,"Continue to Monitor"]
["IBM","Fayette - 740 W New Circle Rd - Lexington ",140,"Lexington - Newtown Rd - N of Substation",26.880000000000003,987,"2023-09-30",0,0,3.8458683350553531E-2,0,7.3128190295727313E-2,0,0.8603382490166892,2.961617199154735E-3,0,2.5113260137875213E-2,87.34751210791849,113.20509299676399,1.2660084124796185,0.2739684090858161,"Continue to Monitor"]
["ASHLAND PIPE","Fayette - 448 S Ashland Ave. - Lexington",142,"Lexington - Tates Creek Rd - N of Substation",18.939999999999998,1796,"2019-08-17",9.516166016968584E-3,0,0.48061097098015237,0,0,0,0.32319294759102146,0.14232209737827714,0,4.4357818033580472E-2,17.284222579049857,29.925137133378776,0.17055976945581333,0.16027424416238931,"Continue to Monitor"]
["AMERICAN AVENUE","Fayette - 96 Burley Ave. - Lexington",144,"Lexington - Broadway - NW of Substation",5.0399999999999991,563,"2019-07-20",0.16397179147510324,0,0.19539468557624873,0,0,0,0.496454453362425,0.14417906958622301,0,0,16.561978550518752,23.29860529256899,0.13212104981043932,0.24654869241089269,"Continue to Monitor"]
["CLAYS MILL","Fayette - 4454 Clays Mill Rd - Lexington ",148,"Lexington - Weber Way - E of Substation",10.26,1104,"2023-12-23",3.2424405495800495E-4,0,0,0,3.7737648413179565E-4,0,0.9515609354032275,4.0264504131386963E-2,0,7.4729399262957845E-3,81.989977918373953,77.768215327152589,0.7497412898453325,1.8132623450718075,"Continue to Monitor"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",149,"Lexington - Man O War Blvd & Liberty Rd - NW of Substation",20.61,1407,"2022-07-15",4.5891450620951599E-3,0,0,0,2.062738644287447E-5,0,2.4658695228123198E-3,2.2869493664926043E-5,0,0.99290148853498472,10.45490251419417,12.064262103365889,0.22988136071319759,9.3807233160166648E-2,"Continue to Monitor"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",150,"Lexington - Maple Leaf Rd -  S of Substation",1.45,60,"2022-07-15",0,0,0,0,0,0,0,0,0,1,3.6666666666666667E-2,0.18333333333333332,3.3333333333333331E-3,1.6666666666666666E-2,"Continue to Monitor"]
["STANFORD","Lincoln -  746 KY Highway 78 - Hustonville ",154,"Hustonville - KY Highway 78 - SW of Substation",53.620000000000005,1107,"2018-11-10",3.5870010074297949E-3,0,6.4538471225286491E-4,0,0.20941553330814761,0,0.76378132477018013,2.1848633673340889E-2,0,7.2212252864878475E-4,70.852769525218278,77.186442987695784,1.1263623306823918,2.5980540175546127,"Continue to Monitor"]
["STANFORD","Lincoln -  746 KY Highway 78 - Stanford",155,"Stanford - KY Highway 78 & US Highway 27 - SE of Substation",18.14,296,"2018-08-11",8.8819915181861215E-4,0,3.5186351014352712E-3,0,0.1164077712545569,0,3.4361594659092574E-2,0.84482379983309663,0,0,48.888418688807626,95.156881924612222,0.41829996845138312,1.1008300880585036,"Continue to Monitor"]
["PICADOME 4KV","Fayette - 1620 Harrodsburg Rd - Lexington ",158,"Lexington - St Joseph Dr - SE of Substation",2.35,450,"2019-12-31",5.5273767720119646E-4,0,0,0,0.24489169231658503,0,0.69107021574832739,3.1177295125792981E-3,0,6.0367624745307151E-2,35.996196179900736,56.520873323738137,0.33359585954231397,0.18633531363414976,"Continue to Monitor"]
["VILEY ROAD","Fayette - 308 Alexandria Rd. - Lexington ",159,"Lexington - Leestown Rd & Masterson Station - NW of Substation",20.18,1140,"2021-12-17",2.1939619880494053E-2,0,0,0,2.653519850878874E-2,0,0.88456004041600611,6.6965141194711073E-2,0,0,40.923472859242153,29.496868369461552,0.28730191107678643,0.30178788810801976,"Continue to Monitor"]
["DANVILLE 1 12KV","Boyle - 494 S 4TH ST - Danville",161,"Danville - 2nd St - S & E of Substation",3.32,153,"2020-10-17",0,0,6.6042100393245429E-2,0,0.34154522322461256,0,0.49097848716169329,1.3532269257460098E-2,0,8.790191996298867E-2,4.8598988384821933,10.010805534334947,6.3848679256648957E-2,9.1163738222561769E-2,"Continue to Monitor"]
["DANVILLE 1 12KV","Boyle - 494 S 4TH ST - Danville",162,"Danville - 4th St - S of Substation",13.8,1293,"2020-10-17",1.3088602137291737E-3,0,7.5904834540141701E-4,0,5.8396904387082046E-2,1.1053301860302496E-2,0.8629790926564338,6.402092727084982E-2,0,1.4818652662013344E-3,35.960105120527821,95.247205843949999,0.40429424261168306,1.0897512025859064,"Reliability Improvements Scheduled for 2024"]
["GARRARD CT","Garrard - 388 Kemper Lane - Lancaster",165,"Lancaster - primary meter outside sub - W of substation",0.01,1,"No Trimming Necessary",1,0,0,0,0,0,0,0,0,0,242.72222200000002,728.16666600000008,0.66666666666666663,2,"Continue to Monitor"]
["DANVILLE WEST","Boyle - 1353 Lebanon Rd - Danville ",166,"Danville - 0.46 miles NW out of Substation",0.43,4,"2021-07-31",0,0,0,0,0.66138613861386142,0,0.10891089108910891,0.22970297029702971,0,0,30.185555533333336,126.1,0.51666666666666661,2.25,"Continue to Monitor"]
["DANVILLE WEST","Boyle - 1353 Lebanon Rd - Danville ",167,"Danville - Lebanaon Rd - SW of Substation",6.5300000000000011,22,"2021-07-31",0,0,0,0,0,0,1,0,0,0,17.614190815579711,18.559722208333334,0.15434782608695649,4.1666666666666664E-2,"Continue to Monitor"]
["DANVILLE WEST","Boyle - 1353 Lebanon Rd - Danville ",169,"Danville - Danville Bypass - N of Substation",1.39,6,"2021-07-31",0,0,0,0,0.1288244766505636,0,0,0.87117552334943649,0,0,4.4344443999999994,22.172221999999998,6.6666666666666666E-2,0.33333333333333331,"Continue to Monitor"]
["ASHLAND AVENUE","Fayette - 448 S Ashland Ave. - Lexington",187,"Lexington - High St. - NW of Substation",3.29,1003,"2019-11-23",0,0,0,9.0616606157206524E-3,0.448124206735736,0,3.2881726143038463E-2,0.3328610643761622,0,0.17707134212934267,21.529475732793127,33.545278868613089,0.16077249408714342,0.25798426120418161,"Continue to Monitor"]
["HUME ROAD","Fayette - 2319 Hume Rd. - Lexington",194,"Lexington - Winchester Rd, Sir Barton Way, Executive Dr, & Elkhorn Rd - E of Substation",8,320,"2021-04-24",1.1171870406303287E-3,0,0,0.31964289214245117,3.2917818153309422E-2,0,0.61493306677642534,0,0,3.1389035887183711E-2,126.59205747765813,123.73276165586911,0.89450496242943911,1.8845220656451722,"Continue to Monitor"]
["STONEWALL","Fayette - 3060 Arrowhead Dr - Lexington",198,"Lexington - Clays Mill Rd and Pasadena Dr - E of Substation",9.52,904,"2022-09-03",4.5401471438450113E-4,0,0,0,5.1352975185063425E-4,0,0.70826097060523963,0.29053965968734768,0,2.3182524117760421E-4,62.589543632791084,122.00922059093291,0.31331512512723741,0.45779358302455941,"Tree Trim Scheduled for 2024"]
["LONDON 2","Laurel - Near corner of Foster Heights & Substation Rd - London",205,"London - S & N on McWhorter Rd",40.519999999999996,1879,"2023-05-05",5.1009750476742385E-3,1.4595392276436461E-2,2.5605951362169227E-4,4.3968113852145847E-3,0.33356131614590001,0,0.47028361960337733,0.16315034062653722,0,8.6554854012385191E-3,91.286902104174246,97.006480724046384,1.5054383132530145,1.595114514031406,"Continue to Monitor"]
["LEBANON WEST","Marion - 2255 Saint Mary's Rd - St Mary ",218,"St Mary - Sait Mary's Rd - E of Substation",7.26,141,"2019-11-16",7.5729615200601466E-2,0,3.8069851684778895E-2,0,0,0,0,0.87253092748274208,0,1.366960563187752E-2,10.557931726755049,13.224468070921986,0.10668427761167854,0.20567375886524822,"Continue to Monitor"]
["MACKVILLE","Washington - 4685 Texas Rd - Springfield ",220,"Springfield - Texas Mackville Rd - N of Substation",6.1300000000000008,132,"2020-09-19",0,0,0,0,1.7922226306303114E-2,0,0.83907195904503362,0.14300581464866324,0,0,139.19854718401035,275.52900763104327,0.51340517624868764,1.1984732824427482,"Continue to Monitor"]
["WILLIAMSBURG SOUTH"," Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg ",226,"Williamsburg - Highway 25 - N of Substation ",32.31,1202,"2023-10-14",7.4427776059387564E-4,0,3.0447726569749461E-3,0,8.7927879162800291E-3,0,0.51720860397979174,0.43774164862356946,0,3.2467909062789978E-2,89.028377536237798,101.92428756636792,0.72634745473613227,0.72055780112173473,"Reliability Improvements Scheduled for 2024"]
["WILLIAMSBURG","Whitley -  Corner of 2nd and 3rd St - Williamsburg ",236,"Williamsburg - 2nd St - N of Substation",2.33,211,"2023-09-30",0,0,0,0,0,0,1,0,0,0,5.2851594166418776,8.9092222733957431,0.10282269771267938,5.6276571399778721E-2,"Continue to Monitor"]
["MANCHESTER SOUTH","Clay - 530 Muddy Gap Rd - Manchester ",253,"Manchester - US HWY 421 - E of Substation",17.78,564,"2019-11-30",3.7100279416330331E-3,0,7.7149953430611607E-3,0,0,3.4771809996895376E-3,0.83149642968022353,5.0232846941943493E-2,0,0.10336851909344924,56.937138401800112,28.401354104673956,0.56636683918226893,0.79956306368332331,"Continue to Monitor"]
["GARRARD","Clay - N End of Crawford Isom Rd - Manchester",257,"Manchester - End of Crawford Isom Rd - N of Substation",0.34,19,"2019-11-30",0,0,0,0,0,0,0,1,0,0,80.655087715789477,157.89473684210526,0.33684210526315789,1,"Continue to Monitor"]
["CORBIN EAST","Knox - Corner of State HWY 1232 and E Barbourville Rd - Corbin ",275,"Corbin - Barbourville Rd - E of Substation",30.44,862,"2022-10-14",3.4696014219278809E-4,0,1.0652285067322442E-3,2.1426310535414281E-3,6.4826763409705146E-3,0,0.83199824693822888,0.14792067395485867,0,1.0043583063475445E-2,75.508909302439136,94.013259556862906,0.63353381034223266,0.72276316545200003,"Continue to Monitor"]
["CORBIN EAST","Knox - Corner of State HWY 1232 and E Barbourville Rd - Corbin ",277,"Corbin - State HWY 1232 & Hancock - NW of Substation",14.580000000000002,734,"2022-05-06",1.2717390423886013E-3,0,0.23573343701651642,0.23283354798992328,1.6848517249479561E-3,0,0.50143374401594132,1.1340348148688164E-2,0,1.5702332061594292E-2,101.73149349631353,209.377962745329,0.57943447242787782,1.1609199288787235,"Continue to Monitor"]
["CORBIN US STEEL","Whitley  - S Woodbine Ave off HWY 830 - Corbin",288,"Corbin - 0.15 miles E of Substation",20.819999999999997,396,"2022-01-01",0.28086600351082502,0,3.2182562902282039E-2,0,0,0,0.31249197219883262,0.1027130400034252,0,0.27174642138463517,126.08693251189284,173.33582500946142,0.98841777311832357,1.3842985460376238,"Continue to Monitor"]
["CORBIN US STEEL","Whitley  - S Woodbine Ave off HWY 830 - Corbin",289,"Corbin - S Main St - S of Substation",0.22,5,"2022-01-01",0,0,0.59534883720930232,0,0,0,0,0,0,0.40465116279069768,8.5739999999999998,42.87,0.08,0.4,"Continue to Monitor"]
["HUME ROAD","Fayette - 2319 Hume Rd. - Lexington",295,"Lexington - Winchester Rd - E of Substation",11.48,85,"2021-04-24",0,0,6.4634982474801525E-2,0,4.5446972658127272E-3,0,0.88897290162180176,1.2381376513030163E-2,0,2.9466042124553862E-2,355.1540854103223,551.71360692339249,2.1886348200754862,7.2943912448700416,"Continue to Monitor"]
["PINEVILLE","Bell - Corner of E Park Ave and Maple St - Pineville  ",300,"Pineville - Park Ave - W of Substation",9.16,316,"2019-06-27",3.5181939109138602E-3,0,0,2.2973930556073545E-2,2.1768047837491766E-2,0,0.82891383532863405,0.12222926689789779,0,5.9672546898892332E-4,53.301706108245959,63.283725209538524,0.6387535224714409,0.67838462498590479,"Continue to Monitor"]
["CROCKETT","Bell - On HWY 66 across the street from Chaz Coal Co - Pineville ",304,"Pineville - State HWY 66 - NW of Substation",16.62,129,"2019-04-06",0,0,0,0,4.3459261112501049E-2,0,0.82072554415811849,0.13581519472938036,0,0,835.08930213861584,1471.785897376923,3.9848445164138679,6.8615384615384603,"Continue to Monitor"]
["CALLOWAY","Bell - Hwy 119 - Calloway",312,"Calloway - US HWY 119 - NW of Substation",22.8,329,"2019-06-27",2.4539107896827056E-3,0,0,0,0.12820116215877261,0,0.67337485891058069,0.19597006814096402,0,0,610.49334062682726,418.69793355406642,2.7623089228527391,2.9428641840377905,"Continue to Monitor"]
["STINKING CREEK","Knox -  Croner of New US HWY 25 E and HWY 930 - Barbourville ",313,"Barbourville - US HWY 25E - S of Substation",37.300000000000004,834,"2020-06-20",0.10363393371794676,0,3.7007564744109649E-2,0,7.7024704015996653E-3,0,7.0765809192974941E-2,0.77863559153442397,0,2.2546304089450676E-3,259.41937507283382,209.79521808613526,2.5539228412748285,2.7145125662815062,"Continue to Monitor"]
["MILL CREEK - KU"," Bell - 5539 HWY 221 Kettle Island - Pineville ",315,"Pineville - Martha Lock Branch Rd - SW of Substation",14.22,336,"2023-01-28",0,0,0,0,0.14513028993441821,0,0.39194147727934581,0.19356529639940823,0,0.26936293638682773,128.11102683352073,136.01677726799485,1.1103590656624129,1.3358597234105669,"Continue to Monitor"]
["DEER BRANCH"," Bell - HWY 66 0.5 miles S of Buffalo Hollow Rd, 7.5 miles N of HWY 221 - Pineville ",319,"Pineville - State HWY 66 - S of Substation",13.780000000000001,226,"2023-07-01",2.2716987962711557E-3,0,2.1332247262195674E-2,0,0.1980812743234682,0,0.10388270431713278,0.41660783781337674,0,0.25782423748755545,359.37912304027952,248.86957516871612,2.316635789090137,2.8730267392650926,"Trees Trimmed in 2023"]
["PUCKETT CREEK"," Harlan - 5627 E HWY 72 Pathfork - Alva",322,"Alva - E Highway 72 - NW of Substation",10.47,288,"2022-12-31",3.3196134574087328E-2,0,0,1.4316392269148174E-3,0,0,0.35916249105225484,0.27040085898353616,0,0.33580887616320687,75.301538329729482,38.79837973921979,0.75670596506699128,1.2146565607605624,"Continue to Monitor"]
["BRUSH CREEK","Knox - HWY 225 Kay Jay Road - Barbourville",323,"Trosper - State HWY 225 - N of Substation",3.0100000000000002,32,"2020-05-09",0,0,0,0,0,0,0.98915031086187977,0,0,1.08496891381202E-2,328.65627279226192,512.70572912499995,1.2214842549923195,1.03125,"Continue to Monitor"]
["BEAR TRACK","Lee Ky - 584 New Yellow Rock Rd - Beattyville ",333,"Beattyville - New Yellow Rock Rd - S of Substation",9.98,77,"2020-10-31",0,0,1.3822139254081106E-2,0,0,0,0.98020018270643838,3.912300909560313E-3,0,2.0653771299201651E-3,311.11445551878529,437.57713674358973,1.2202151835093011,1.1153846153846154,"Continue to Monitor"]
["OKONITE","Madison - 1742 Berea Rd - Richmond",334,"Richmond - Battlefield Memorial Rd & Berea Rd - S of Substation",28.590000000000003,1252,"2019-09-28",0.18230767863806799,0,0,0,0.22511684111385566,0,0,0.59257548024807627,0,0,64.817773799103037,34.738587015029694,0.54072375807627548,0.64510004172144964,"Continue to Monitor"]
["OKONITE","Madison - 1742 Berea Rd - Richmond",335,"Richmond - Industry Rd - N of Substation",0.2,1,"2019-09-28",0,0,0,1,0,0,0,0,0,0,14.283333333333333,42.85,0.33333333333333331,1,"Continue to Monitor"]
["DARK HOLLOW","Estill - 37 Dark Hollow Rd - Red Lick",337,"Red Lick - Richmond Rd - E of Substation",17.150000000000002,537,"2023-07-28",7.2227544945703277E-4,0,0,0,0,0,0.32494386421814797,0.66589198793340243,0,8.4418723989926701E-3,61.846116176020118,133.63278023363117,0.30907046540192573,0.54521584837593551,"Trees Trimmed in 2023"]
["MIDDLESBORO 2 4KV","Bell - Intersection of Cumberland Ace and S 38th St - Middlesborough",350,"Middlesborough - Dorchester Ave - E of Substation",5.59,448,"2022-02-25",2.474047575266211E-3,0,1.3590545126293442E-2,9.526754818541984E-2,0.65843098577422643,0,0.11703248023269421,0.11320439310609985,0,0,39.392464276124187,133.238754969448,0.39443545189510865,1.2985117280022624,"Continue to Monitor"]
["MIDDLESBORO 2 4KV","Bell - Intersection of Cumberland Ace and S 38th St - Middlesborough",351,"Middlesborough - Dorchester Ave - E of Substation",7.88,654,"2022-02-11",2.773781693939939E-2,0,0,0.17532817838518253,0.15446862075166337,0,0.14772522927531018,0.16283042618234131,0,0.33190972846610323,29.806094300389816,30.905428380049759,0.61346709472336625,0.36309466909169347,"Continue to Monitor"]
["MIDDLESBORO 1 12KV","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",365,"Middlesborough - N 12th St - NE of Substation",3.39,477,"2021-12-31",1.1402620315614075E-2,0,0,1.5225275263828535E-2,2.1841408828045875E-2,0,0.1812657235272977,0.32110301565001464,0,0.44916195641519913,41.718291740776138,85.235252223090015,0.41452191636810926,0.80540429299173344,"Continue to Monitor"]
["MIDDLESBORO 1 12KV","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",367,"Middlesborough - N 19th St - N & S of Substation",4.3599999999999994,518,"2021-12-31",3.7153204170544941E-3,0,0,2.2096379322481992E-3,0.58244491548623767,0,0.27342802837722624,0.10102933929870395,0,3.7172758488529439E-2,73.484704254979164,123.85669003628206,0.70774887189651525,0.74280783560812202,"Continue to Monitor"]
["MIDDLESBORO 1 4KV","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",370,"Middlesborough - N 19th St - SW of Substation",1.63,690,"2021-12-31",2.6226946792779217E-3,0,0,0,3.196060377779638E-2,0,0.72111548226890987,2.7705700175776345E-2,0,0.21659551909823946,52.911869029424373,81.291082475608476,0.50892170992458963,0.45027812722128852,"Continue to Monitor"]
["MIDDLESBORO 1 4KV","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",371,"Middlesborough - N 19th St - S of Substation",13,163,"2021-12-31",0,0,0,0,0.73815562544384705,0,5.4073247438368673E-2,0.18971289438977376,0,1.8058232728010552E-2,40.393026113066519,60.408435574667067,0.27608013985008217,0.56224749364058058,"Continue to Monitor"]
["MIDDLESBORO 1 4KV","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",372,"Middlesborough - Lynnwood Dr - E of Substation",8.69,498,"2022-02-11",5.2149041606155003E-3,0,2.9555558019134618E-3,0,5.6275290178818889E-2,0,0.91709588372892259,1.7292107801292641E-2,0,1.16625832843697E-3,57.88648060666327,110.77042763395022,0.35738488223469633,0.76711604636874164,"Continue to Monitor"]
["TRAFTON AVENUE 12KV","Fayette - 141 Trafton St - Lexington ",404,"Lexington - Old Frankfort Rd - N of Substation",5.3599999999999994,154,"2019-12-31",6.676238334529792E-3,0,0,0,1.457286432160804E-2,0,0.56460875807609479,0.16604450825556352,0,0.24809763101220389,38.095645165182475,46.786804470538286,0.45559320133585252,1.1623790117167601,"Continue to Monitor"]
["FORKS OF ELKHORN","Franklin - 3286 Georgetown Rd - Frankfort ",405,"Frankfort - Switzer Rd - N of Substation",55.5,687,"2018-01-27",2.8573090217635916E-4,0,1.5539602949237391E-3,0,2.3136617300121121E-2,0,0.80061686407946753,0.16359569161628446,0,1.0811135807026844E-2,103.8494780542707,81.177956289004314,1.2532573957442155,2.1864876123506805,"Continue to Monitor"]
["FORKS OF ELKHORN","Franklin - 3286 Georgetown Rd - Frankfort ",407,"Frankfort - Old Grand Dad Rd - N of Substation",0.88,3,"2017-12-23",0,0,0,0,0,0,1,0,0,0,108.13555553333329,134.63333333333333,0.73333333333333339,1,"Continue to Monitor"]
["HARLAN 4KV"," Harlan - Corner of River St and Rain St - Harlan ",409,"Harlan - Clover St - NW of Substation",1.83,259,"2023-11-11",0,0,0,0,0.92865499987553213,0,7.13450001244679E-2,0,0,0,62.196272741601604,154.47588194085202,0.48871793790038581,0.85728049003911067,"Reliability Improvements Completed in 2023"]
["HOOVER 1","Scott Ky - 3 Quality Dr - Georgetown",410,"Georgetown - Showalter Dr & McClelland Blvd - SW of Substation",22.68,1316,"2018-10-06",1.6002989942919273E-2,0,0,0,0,0,3.1802120141342753E-2,0.4484914378907312,0,0.50370345202500677,30.599675342938333,64.323897321398746,1.1526265859356222,4.3698792701864768,"Continue to Monitor"]
["HOOVER 1","Scott Ky - 3 Quality Dr - Georgetown",412,"Georgetown - Old Lemons Mill Rd - N of Substation",3.5999999999999996,329,"2019-01-12",0.25406334793004326,0.35410901861752142,0,0,0,0,0.26728098218843188,0,0,0.12454665126400344,50.09515024401469,117.81037402607741,0.46575278877355608,0.93325223992353745,"Continue to Monitor"]
["HARLAN WYE 12KV","Harlan - Sunshine Pike Rd just W of US HWY 421 - Harlan",413,"Harlan - US HWY 421 Bypass - NW of Substation",12.530000000000001,639,"2023-11-18",1.1724747592239335E-3,0,0,1.3716093611873634E-2,3.554645698599544E-3,0,0.32311915507374495,0.64452612478481375,0,1.3911506071744288E-2,73.241213235947242,84.134594524535231,0.77564227305405531,0.41095848020502929,"Trees Trimmed in 2023"]
["KENTENIA"," Harlan - Near HWY 219 on Meadow Creek Ln (Wilson Ln) - Wallins Creek ",422,"Wallins Creek - HWY 219 - N of Substation",44.82,1064,"2020-03-07",4.6609430760089518E-4,0,1.6277721047893859E-3,0,6.0378781679291541E-3,0,0.70544085049758232,0.28575139027748619,0,6.7601464461198538E-4,196.18383403471506,227.14261586310553,1.6435451856844565,1.3268827457722001,"Reliability Improvements Scheduled for 2024"]
["GEORGETOWN 12KV","Scott Ky - 207 W Clinton St - Georgetown ",426,"Georgetown - N Broadway St - N of Substation ",24.049999999999997,1704,"2024-02-11",1.8560144065678018E-3,0,2.1715909668915168E-2,0,3.6968776751228052E-3,4.1557407120818419E-4,0.38542005989028411,0.58600056492100305,0,8.9499936689887592E-4,43.076055741337704,73.541937231813023,0.44344876412759932,0.36839018812945012,"Trees Trimmed in 2024"]
["NEWTOWN","Scott Ky - 5849 Paris Pike - Georgetown ",430,"Georgetown - US 460 Pike - E of Substation",68.75,806,"2021-01-16",2.2513447918317622E-3,0,1.0597933498444681E-3,0,0.30603394775887122,0,0.63276919228470441,1.1810489853672137E-2,0,4.6075231961075984E-2,68.823777533810869,216.83707106894667,0.39609589626232328,1.0439932838031969,"Continue to Monitor"]
["LEMONS MILL","Scott Ky - 125 Carley Ct - Georgetown ",442,"Georgetown - Holmes Dr - N of Substation",1.53,57,"2018-11-10",1,0,0,0,0,0,0,0,0,0,0.90724137931034488,1.1362068965517242,1.3914095583787053E-2,3.4482758620689655E-2,"Continue to Monitor"]
["ADAMS 12KV","Scott - 900 W Main St - Georgetown",452,"Georgetown - Paynes Depot Rd - SW of Substation",43.599999999999994,1548,"2019-01-26",3.4084745379140777E-3,0,2.502224743232875E-2,0,1.5373541506518006E-2,0,0.9096735996893025,4.4443033067824191E-2,0,2.0791037661125069E-3,31.381840880203129,26.929023394772738,0.19241206026837615,0.30804429198972116,"Continue to Monitor"]
["ADAMS 12KV","Scott - 900 W Main St - Georgetown",453,"Georgetown Rd - Frankfort Rd - E of Substation",45.34,1628,"2019-04-20",2.5248166322809381E-3,6.8497466963671688E-5,0.11777317474799782,0,0.40669138055274717,0,0.23285987884168041,0.11989933612255019,0,0.12018291563577979,105.81126568984737,272.79885944176669,0.6685014184448187,1.0154989782177464,"Continue to Monitor"]
["BLACK MOUNTAIN","Harlan - Black Mountain Rd - Lynch",467,"Lynch - Radar Station Rd - SW of Substation",3.65,10,"2023-11-25",0,0,0,0,0,0,1,0,0,0,616.88799992000008,1104.5899999000001,2.02,1.1000000000000001,"Continue to Monitor"]
["TOTZ"," Harlan - HWY 119 about 1/4 miles S on unnamed Rd on W side of Loop Dione ",468,"Poor Fork - N US HWY 119 - E of Substation",3.16,66,"2020-12-31",3.0019604287034398E-2,0,0,0,0,0,0.82544411914570215,0.14453627656726342,0,0,309.54781221460433,306.70570408467023,1.9843133564220696,2.0601604278074865,"Continue to Monitor"]
["SHADRACK","Franklin - 74 Bethel Ln - Frankfort ",475,"Frankfort  - US HWY 127 - N of Substation",47.82,580,"2018-03-09",1.5751349455258828E-3,3.9784625091546664E-5,1.3336254608152263E-4,0,1.1789697351072419E-2,0,0.11843434612287621,0.78553901723010477,0,8.2488657179247665E-2,54.57055088147424,99.270649044771915,0.41769730751844902,0.6086888272756461,"Continue to Monitor"]
["SHADRACK","Franklin - 74 Bethel Ln - Frankfort ",476,"Frankfort - S on US HWY 127 & N on Peaks Mill Rd",57.269999999999996,699,"2018-09-29",6.9356015287399869E-4,0,2.6587897845687571E-3,0,1.9583881012101811E-4,0,0.95686757105998399,3.4825955740428911E-2,0,4.7582844520233395E-3,119.63051483047968,153.36221214529115,0.98104939033334304,1.718640574490147,"Continue to Monitor"]
["HIGHSPLINT","Harlan - Gano St South of KY 38 - Highsplint",483,"Highsplint -  Gano St - E of Substation",0.06,1,"2022-12-06",0,0,0,4.9036777583187391E-2,0.27145359019264448,0,0,0.67950963222416805,0,0,203.66999959999998,401.16666599999996,1.4,3,"Continue to Monitor"]
["ROBBINS","Harlan - E of 15537 HwY 38 - Upper Clover ",487,"Upper Clover - Highway 38 - E of Substation",8.98,220,"2023-04-14",2.9746662700444974E-4,0,5.7653325646223248E-4,0,5.0368459950872004E-2,0,0.85964635204715312,8.9111188118508253E-2,0,0,262.92149228956964,430.23391132554769,1.6410803143936181,3.2642395879704504,"Continue to Monitor"]
["HOLMES MILL"," Harlan - 1/4 mile E of 25511 HWY 38 - Upper Clover ",491,"Upper Clover - Highway 38 - W of Substation",8.8899999999999988,189,"2023-05-13",3.8680591679671346E-4,0,0,0,0.53471916556627053,0,0.45122910914595921,1.366491937097355E-2,0,0,304.24506682344276,771.83226862397657,1.5320272817713083,2.6242829295460872,"Continue to Monitor"]
["DAYS BRANCH","Harlan - Off of State Route 38 - Holmes Mill",493,"Holmes Mill - Off of State Route 38 - S of Substation",0,1,"No Trimming Necessary",0,0,0,0,0.38554216867469882,0,0,0,0,0.61445783132530118,288.63333320000004,664.45,0.6,2,"Continue to Monitor"]
["BAILEY CREEK","Harlan - Tyree Ln - Evarts",495,"Evarts - Tyree Ln, Hwy 38, & Bailey Creek Rd – W of Substation",7.01,286,"2021-10-16",8.7623823760384668E-3,0,0,0.78737445407326789,8.5281677527795762E-3,0,2.2608599809872836E-2,5.8181667883664218E-2,0,0.11454472810437706,246.31370955057599,252.59164105147954,1.5079235285079535,2.2901982057309405,"Continue to Monitor"]
["ALEXANDER","Woodford - 2915 Troy Pike - Versailles",501,"Woodford South - Troy Pike - N of Substation",60.839999999999996,2150,"2020-03-21",2.1447589506212706E-4,1.1672591463604238E-4,8.8274929713299144E-2,4.8269036011379819E-4,4.5016018718244214E-4,0,0.67255622258356229,7.1809081052912394E-2,0,0.16609571429323175,67.866365095137098,164.2654541071515,0.62827322616102221,1.6069384012473298,"Continue to Monitor"]
["MIDWAY 12KV","Woodford - 860 Weisenburger Rd - Midway ",503,"Midway - Weisenberger Mill Rd - W of Substation",45.64,803,"2023-08-05",2.9438524723960605E-3,5.17374265278864E-4,4.5907207612569709E-2,3.8040138023247066E-4,8.1248341066741989E-2,0,0.81874016172736286,4.8554403784709849E-2,0,1.7082576907081286E-3,150.39085294980356,136.83518339329288,1.0149311754813641,1.5615992244139318,"Continue to Monitor"]
["VERSAILLES BYPASS","Woodford - 350 Markham Dr - Versailles ",507,"Versailles - Big Sink Rd & Lexington Rd - E of Substation",51.79,1093,"2020-06-20",2.0850235508526691E-4,0,1.2036853750627984E-3,0,0.34611422923043123,0,0.59467078213646474,3.0961000785721299E-2,0,2.6841800117234606E-2,103.46728323331972,131.60507971834008,1.04531054270109,1.18538673510229,"Continue to Monitor"]
["VERSAILLES BYPASS","Woodford - 350 Markham Dr - Versailles ",509,"Versailles - Frankfort Rd - N of Substation",136.46,2004,"2021-01-23",2.7285004349158625E-3,6.9384691648473041E-6,1.1334865450117068E-2,1.2962321939782918E-3,0.24984656521596826,1.1829038642857859E-3,0.68581938800319064,4.3642130020324105E-2,0,4.1424763480552001E-3,174.20896366426598,355.14297170073235,0.93030022735302409,1.937538840652518,"Continue to Monitor"]
["VERSAILLES BYPASS","Woodford - 350 Markham Dr - Versailles ",510,"Versailles - Kuhlman Blvd - N of Substation",2.4000000000000004,35,"2020-05-02",0,2.3416370721759945E-3,0,0,0,0,0.9621276926666148,0,0,3.5530670261209187E-2,13.895092200380825,28.503703694444447,6.7674731182795697E-2,8.3333333333333329E-2,"Continue to Monitor"]
["VERSAILLES BYPASS","Woodford - 350 Markham Dr - Versailles ",511,"Versailles - 0.28 miles E of Substation",0.3,4,"2020-05-02",1,0,0,0,0,0,0,0,0,0,19.307500000000001,9.7125000000000004,0.15,0.25,"Continue to Monitor"]
["VERSAILLES WEST","Woodford - 115 Rutter Rd - Versailles",512,"Versailles - Tyrone Pike - W of Substation",34.300000000000004,1119,"2021-04-03",5.2789344106986399E-4,0,4.4074035289323379E-3,0,2.2220045271699289E-2,0,0.95372502678621607,4.5950375559792762E-3,0,1.4524593416103177E-2,74.46517051151784,87.948245179115261,0.72213985100983469,0.44851402686878444,"Continue to Monitor"]
["VERSAILLES WEST","Woodford - 115 Rutter Rd - Versailles",513,"Versailles - Clifton Rd - N of Substation",27.1,943,"2020-08-22",2.6220999574470636E-3,0,0,4.2153378363529937E-4,7.3059196528639323E-3,0,0.88389541167468777,2.4196238959710563E-2,0,8.1558795971655343E-2,63.45223357479,53.477851705655922,0.53896414949836036,0.64690867114339334,"Continue to Monitor"]
["ALEXANDER","Woodford - 2915 Troy Pike - Versailles",515,"Versailles - N & S on McCowans Ferry Rd - E of Substation",50.01,1546,"2021-10-23",6.6051764098945824E-4,4.1774303066167463E-4,4.0048801490029172E-2,0,8.6564321995000366E-3,0,0.80830384001153177,0.10321856542965417,0,3.8694100197633703E-2,105.13500398190158,126.02853150741997,1.34525400264971,1.6171599143135247,"Continue to Monitor"]
["MIDWAY 12KV","Woodford - 860 Weisenburger Rd - Midway ",516,"Midway - State HWY 341 - N of Substation",39.35,575,"2023-05-13",4.8558623227308643E-4,0.12935594978857395,0,9.0481906634736604E-4,1.5665434102027399E-2,0,0.81704558478456257,5.4560589700746176E-3,0,3.1086567056141007E-2,49.89043260266191,15.194868840492566,0.2612764772881494,0.26565826499774953,"Continue to Monitor"]
["PAYNES MILL","Woodford - 221 Paynes Mill Rd - Versailles",517,"Versailles - Lexington Rd,  Crossfield Dr, Kroger Way - W of Substation",0.89000000000000012,107,"2020-06-20",0.9242700729927007,0,0,0,0,0,0,0,0,7.5729927007299275E-2,6.2289719532710244,10.241121485981306,7.0093457943925228E-2,0.12149532710280374,"Continue to Monitor"]
["PAYNES MILL","Woodford - 221 Paynes Mill Rd - Versailles",519,"Versailles - Lexington Rd, Methodist Home, Paynes Mill Rd - E of Substation",1.8599999999999999,140,"2020-06-20",1.6252787542049363E-3,0,1.2930614323539884E-4,0,2.2877240726262873E-4,0,0.9683100482809246,2.5544925927473181E-2,0,4.1616684868992981E-3,113.37666395159951,221.41842112487336,0.47913050291892822,0.90805471124620052,"Continue to Monitor"]
["SOMERSET 1","Pulaski - 144 Railroad Dr - Somerset ",521,"Somerset - S Main St - N of Substation",4.05,391,"2020-08-15",0,0,0,0,0,0,0.99096660579180806,0,0,9.0333942081920159E-3,25.103581352120909,76.704249365838621,0.21457438323694067,0.61588382050447321,"Continue to Monitor"]
["SCIENCE HILL","Pulaski - 45 E HWY 635 neat the intersection of E hWY 635 and Maple Ln - Science Hill",528,"Science Hill - E on HWY 635 and S on HWY 1247",14.84,583,"2023-02-25",6.7775402742297061E-4,3.362702674521662E-3,2.3356446483499296E-2,0,2.7761847661748607E-3,0,0.9343490954590481,1.480631875293259E-2,0,2.0671497836400606E-2,35.30638086715733,35.437203263478274,0.3626206551913404,0.28446473588869009,"Continue to Monitor"]
["DENHAM STREET","Pulaski - 114 Adams St - Somerset ",531,"Somerset - Monticello St - S of Substation",5.33,199,"2020-10-24",4.7619047619047616E-2,0,1.8264840182648401E-2,0,0.14742335290280495,0,0,0.7051532941943901,0,8.1539465101108932E-2,6.7695111784723734,15.08433815762894,0.13466701387814412,0.21035475886897173,"Continue to Monitor"]
["WAITSBORO"," Pulaski - 676 Old Monticello Rd at W Summitt Dr just W of HWY 27 - Somerset ",534,"Somerset - Old Monticello Rd - N of Substation",11.430000000000001,477,"2021-01-09",2.0536100302637268E-3,0,6.803033578325407E-2,8.0973483210837298E-3,0,0,0.8335224816255945,6.1788442138636691E-2,0,2.6507782101167315E-2,40.210894542477973,40.548248397834193,0.28297032773255582,0.36454307519697443,"Continue to Monitor"]
["SOMERSET SOUTH"," Pulaski - 3084 S HWY 27 S of Monticello Rd - Somerset ",542,"Somerset - HWY 27 - S of Substation",3.6500000000000004,280,"2020-11-14",0.41413046499346839,0,0,0,0,0,0.58586953500653161,0,0,0,31.010603192928933,114.44517856785714,0.36296500127087272,1.1892857142857143,"Continue to Monitor"]
["SOMERSET SOUTH"," Pulaski - 3084 S HWY 27 S of Monticello Rd - Somerset ",543,"Somerset - Monticello St - N of Substation",6.02,216,"2020-11-14",0,0,0.99749342410645214,0,0,0,2.5065758935478881E-3,0,0,0,50.623635647562757,148.91434172641948,0.47211573869739076,1.0967530545808144,"Continue to Monitor"]
["BURNSIDE","Pulaski - S Hwy 27 - Burnside",545,"Burnside - HWY 27 & Old 27 - SE of Substation",8.4499999999999993,201,"2021-04-03",7.8498327995716443E-3,0,0,0,0,0,0.98976591940030112,0,0,2.3842478001272946E-3,118.68874921642092,342.04561698178196,0.59700969380895019,1.0593608074047112,"Continue to Monitor"]
["WAYNESBURG","Lincoln - On Old Somerset Rd (HWY 1247) just S of Clear Fork Rd - Waynesburg ",546,"Waynesburg - KY HWY 1247 - S of Substation",10.030000000000001,265,"2023-03-04",0,0,1.0549093859886394E-3,0,7.3951852853665137E-2,0,3.3757100351636461E-2,0,0,0.89123613740870977,162.07681617762969,128.58478154061262,0.80535087937975491,1.0377645455197646,"Continue to Monitor"]
["WINCHESTER WATER","Clark -  335 Waterworks Rd - Winchester ",555,"Winchester - Boonesboro Rd - SW of Substation",19.73,269,"2022-08-12",2.4901222089497382E-2,0,0.43807773591840488,0,1.8083249104107323E-2,0,0.42196085638151243,9.207020123127814E-2,0,4.9067352751998531E-3,50.654364339196675,109.73105678643162,0.51568125817966626,0.84741996915256179,"Continue to Monitor"]
["DANIEL BOONE","Hopkins - 500 Daniel Boone Rd - Nortonville",557,"Nortonville - Dan Boone Rd, Squire Rd, Hwy 62 - NW&SE of Subst.",10.209999999999999,133,"2022-06-03",0,0,4.1396863913909294E-2,0,1.4150632360504834E-2,0,5.1089981141282131E-2,2.0045630184498927E-3,0,0.89135795956585384,127.62198556622964,551.62383446009653,0.46357163247769728,1.4722873254295086,"Continue to Monitor"]
["SHUN PIKE","Jessamine - 1201 Short Shun Rd Nicholasville ",580,"Nicholasville - N & S on Nicholasville Bypass ",32.79,1405,"2020-11-07",1.2400322935368874E-3,0,1.5064004522083237E-3,4.8415603492675289E-3,8.029332609843929E-3,0,0.86464668754520946,0.10770907327347529,0,1.2026913476458531E-2,90.285267583650267,68.294924262343329,0.91413582208048294,1.3318471464848727,"Continue to Monitor"]
["WILMORE 4KV","Jessamine - 210 W Linden St - Wilmore ",588,"Wilmore - Main St - SE of Substation",1.21,48,"2021-01-16",0,0,0,0,0,0,1,0,0,0,6.3556944375000075,18.719097208333334,0.1041666666666666,0.22916666666666666,"Continue to Monitor"]
["INNOVATION DRIVE","Fayette - 2350 Innovation Dr - Lexington ",592,"Lexington - Georgetown Rd - E of Substation",13.27,942,"2019-11-09",2.9036199957398624E-2,0,0,0,8.268029910649223E-2,0,3.3767194699492145E-2,0.15700848664222694,0,0.69750781959439012,52.597491553005611,89.531909060290317,0.26170896981997788,0.51769548838843527,"Continue to Monitor"]
["INNOVATION DRIVE","Fayette - 2350 Innovation Dr - Lexington ",594,"Lexington - Greendale Rd - W of Substation",28.650000000000002,2771,"2019-11-09",5.049761188377133E-4,0,0,0,0,0,1.3195506914866436E-3,0,0,0.99817547318967559,0.88490536243920181,0.33183280977224078,8.3021788155460512E-3,9.5093486601664327E-3,"Continue to Monitor"]
["MOUNT STERLING 12KV","Montgomery 346 Calk Ave - Mount Sterling ",601,"Mount Sterling - 686 Bypass - N of Substation",18.16,1359,"2019-01-12",7.6827442721944536E-3,0,1.7100956537183163E-3,0,4.2412401999340321E-2,0,0.86157359246948972,8.3317687057569839E-2,0,3.3034785476873112E-3,19.053834439936555,18.875803501653191,0.23368754737634229,0.31590584124318594,"Continue to Monitor"]
["MOUNT STERLING 12KV","Montgomery 346 Calk Ave - Mount Sterling ",602,"Mount Sterling - Richmond Ave - N of Substation",4.03,384,"2019-01-12",0,1.5139751552795032E-2,2.9114906832298135E-3,0,0,0,2.1642080745341616E-2,0,0,0.96030667701863359,10.231313720462307,26.695626805827334,7.3749268675165694E-2,0.18145481461543639,"Continue to Monitor"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",604,"Mount Sterling - US 460 HWY - S of Substation",24.240000000000002,636,"2023-08-05",3.9208785237737994E-4,6.1128657299780497E-4,0.23421537663588624,0,1.0160323796645334E-2,0,0.74792455859243545,6.8846922110358838E-4,0,6.0078973285541837E-3,47.086340530850507,120.87795421646696,0.54962840452895034,1.0329798171050535,"Continue to Monitor"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",605,"Mount Sterling - 686 Bypass & Spencer Rd - E of Substation",38.96,1326,"2019-06-01",4.3317458709089063E-3,0,4.9397102036680511E-3,0,0.1013527206403891,0,0.48782804742121794,5.4590130712331543E-3,0,0.39608876279258282,29.165192431578895,31.143485783158731,0.51005017821175269,0.79084138007323501,"Continue to Monitor"]
["A O SMITH","Montgomery - 1871 Owingsville Rd - Mt. Sterling",606,"Mount Sterling - Owingsville Rd - E of Substation",1.54,25,"2023-04-21",0,0,0,0,0.54584404455869751,0,0,0.3667523564695801,0,8.7403598971722368E-2,25.013358858051781,41.600127653895271,0.38362939742250091,0.46360153256704983,"Trees Trimmed in 2023"]
["OWINGSVILLE","Montgomery - 69 W Paul Lewis Dr - Owingsville ",610,"Owingsville - Slate Ave - S of Substation",8.64,474,"2023-03-24",0,1.5944001555512346E-3,2.3060470542484932E-2,0,0.14540151662453821,0,0.36492319657787287,5.0787478125607619E-2,0,0.41423293797394517,34.741642934192853,34.269596406284997,0.50880492637444219,0.59487363932439219,"Reliability Improvements Scheduled for 2024"]
["OWINGSVILLE","Montgomery - 69 W Paul Lewis Dr - Owingsville ",611,"Owingsville - W Main St - SW of Substation",25.25,722,"2023-03-24",4.7048860241360657E-3,0,7.131823064919586E-3,0,4.08344899511476E-2,0.36025900397562871,0.32631913241901717,5.1855685462686332E-2,0,0.20889497910246457,56.295860265877607,110.72102103089112,0.49663274240907607,0.91808729915392484,"Continue to Monitor"]
["SALT LICK","Bath - 11457 US HWY 60 E - Salt Lick ",613,"Salt Lick - US HWY 60 - NE of Substation",10.199999999999999,247,"2023-03-03",0,0,0,0,8.9526256890620475E-3,0,0.34766029759190947,0.64338707671902851,0,0,49.790542896601984,98.170953513401102,0.46005718287234953,0.44777507842630321,"Reliability Improvements Scheduled for 2024"]
["FARMERS"," Rowan - 6901 US 60 W - Morehead ",614,"Morehead - US HWY 60 - SW of Substation",5.22,139,"2022-11-18",0.24086378737541528,0,0.48172757475083056,0,0.24916943521594684,0,2.823920265780731E-2,0,0,0,6.0038382991089509,6.4864230433944368,5.9706356652787174E-2,5.7402012841953211E-2,"Continue to Monitor"]
["FARMERS"," Rowan - 6901 US 60 W - Morehead ",615,"Morehead - US HWY 60 - NE of Substation",22.299999999999997,616,"2022-11-18",2.1740263802721444E-2,0,0,0,0.14167665919399405,0,0.76307283249048541,3.6833324644179134E-2,0,3.6676919868619991E-2,37.128649552996137,49.644520669734341,0.29719979115505046,0.21043810548165789,"Continue to Monitor"]
["MOREHEAD WEST","Rowan - 133 Gregory Ct - Morehead ",616,"Morehead - US HWY 60 - SW of Substation",8.0399999999999991,370,"2022-09-09",5.5063171789553082E-3,0,2.6173863850650576E-2,0,9.5493117103526301E-2,0,0.7230247029983029,3.7073354704884029E-2,0,0.11272864416368093,27.582754753919875,63.561687073698764,0.19232341817774029,0.33906122643567072,"Continue to Monitor"]
["ROCKWELL","Clark - 5835 Rockwell Rd - Winchester  ",627,"Winchester - N & S on Van Meter Rd",27.8,1132,"2022-03-25",0,0,0.25150117483247758,0,0,0,0.4404316421547298,0.23931772691671743,0,6.874945609607519E-2,6.569554003748431,6.341259683831554,8.816129851464044E-2,0.12408280229674247,"Continue to Monitor"]
["WINCHESTER","Clark - 2 Almond St - Winchester ",632,"Winchester - 1st St - S of Substation",0.6,74,"2021-07-03",0,0,0,0,0,0,0,1,0,0,11.489503499991459,12.490690672792791,0.12710863460863461,0.2147747747747748,"Continue to Monitor"]
["WINCHESTER SOUTH","Clark - 105 Hood Ave - Winchester",636,"Winchester - Boone Ave & S Main St - E of Substation",2.66,301,"2021-07-03",3.2346868547832072E-2,0,0,0,0.24971323698095893,0,0.71793989447120898,0,0,0,16.722394279679321,28.835098136568121,0.12505380093415119,0.13541260452291307,"Continue to Monitor"]
["BOONE AVENUE","Clark - 660 Boone Ave. - Winchester",640,"Winchester - Main St, Hughes Ave, Muddy Creek Rd - E of Subs.",9.2200000000000006,439,"2021-09-11",0.15578558225508318,0,0,0,0,0,0.75763401109057305,0,0,8.6580406654343814E-2,23.064784459063894,30.223221600826154,0.31273644411689971,0.269844346803573,"Continue to Monitor"]
["WINCHESTER WATER","Clark -  335 Waterworks Rd - Winchester ",641,"Winchester - Old Boonesboro Rd - N of Substation",23.39,1093,"2022-07-15",1.165845097973464E-2,0,9.3446452723472267E-3,0,0.19241474128969518,0,0.74182622983803359,3.4427640477068732E-3,0,4.1313168572482475E-2,39.323488148274876,56.596249630999857,0.23072140255506463,0.31032366984784127,"Reliability Improvements Scheduled for 2024"]
["WINCHESTER INDUSTRIAL","Clark - 705 Tech Dr - Winchester",644,"Winchester - Rolling Hills Ln - E of Substation",0.9,12,"2021-10-23",0,0,0,0,0,0,0,1,0,0,3.8991830009803925,5.3194444166666672,4.0196078431372552E-2,8.3333333333333329E-2,"Continue to Monitor"]
["WINCHESTER INDUSTRIAL","Clark - 705 Tech Dr - Winchester",649,"Wnchester - Enterprise Dr - N NW of Substation",0.88,5,"2021-10-23",0.31972789115646261,0,0,0,0.68027210884353739,0,0,0,0,0,5.8479999600000001,29.2399998,0.12000000000000002,0.60000000000000009,"Continue to Monitor"]
["STRINGTOWN","Muhlenberg - 5995 Paradise Rd - Greenville",652,"Greenville - Paradise Rd - S of Substation",0.90999999999999992,7,"2023-09-29",0,0,0.74223163841807904,0,0,0.23163841807909605,0,0,0,2.6129943502824857E-2,47.773809507142857,201.66488091071429,0.27142857142857146,1.1071428571428572,"Continue to Monitor"]
["MUHLENBERG PRISON","Muhlenberg - 1200 River Rd - Central City",657,"Central City - Hwy 431, S R 81, & S Carrolton St - NW of Substation",48.54,702,"2018-10-26",1.4345754942687078E-2,0,3.0751788266775573E-2,0,6.315850428665909E-2,0,0.65565311739015153,0.23300651303979444,0,3.0843220739322974E-3,54.463239549455849,60.373004009694611,0.71594467829180586,1.1802105868867347,"Continue to Monitor"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",659,"Mt Sterling - US Hwy 460 - SE of Substation",47.64,1057,"2023-12-09",9.1195198315730224E-4,0,0.34546202410042837,0,0.19206737079101688,0,0.36004513756403284,9.0610683098038908E-2,0,1.090283246332573E-2,111.27857853256111,133.59714656495692,1.343411541706524,1.1710248933438241,"Continue to Monitor"]
["SIMMONS","Ohio - 5798 US HWY 62 W - Centertown",698,"Centertown - US HWY 62 - E of Substation",2.1100000000000003,27,"2023-09-29",0,0,0,0,1.3854190324778561E-2,0,0.98614580967522147,0,0,0,32.556049373015874,162.78024686507936,0.1693121693121693,0.84656084656084651,"Continue to Monitor"]
["SIMMONS","Ohio - 5798 US HWY 62 W - Centertown",699,"Centertown - Midway Rd & US HWY 62 - W of Substation",3.7800000000000002,15,"2023-09-29",0,0,0.10518518518518519,0,0.4177777777777778,0,0.47703703703703704,0,0,0,135.61573609333334,42.500902733333334,0.50416666666666665,1.2541666666666667,"Continue to Monitor"]
["CAMPBELLSBURG","Henry - 379 Turners Station Rd. - Campbellsburg",703,"Campbellsburg - Hwy 193 & Webb Ln - W & E of Sub.",52.14,945,"2023-09-09",2.9565097635902825E-3,0,4.7979422158940722E-4,0,5.1533453429973368E-4,0,0.90596033256847619,8.545668191197997E-2,0,4.6313470000644164E-3,47.484559430877582,50.525971061335667,0.85950713298798365,0.25824135188413505,"Continue to Monitor"]
["CARROLLTON 4KV","Carroll - 802 Mason St - Carrollton ",704,"Carrolton - 4th St - N of Substation",6.7399999999999993,504,"2019-11-23",0,0,0,0,0,0,1,0,0,0,7.448102397545485,10.531304656987288,7.1708400836062253E-2,5.3532238797677587E-2,"Continue to Monitor"]
["CARROLLTON 12KV","Carroll - 802 Mason St - Carrollton ",708,"Carrollton - 11th St - N of Substation",15.65,793,"2019-11-30",1.0545305212519434E-2,0,8.9026429262855297E-3,0,0,0,6.2127834325775129E-2,0.12456366783021912,0,0.79386054970520081,81.108064153834178,85.322204131337656,0.75078889523101899,0.69506450951666632,"Continue to Monitor"]
["DAYTON-WALTHER","Carroll - 5220 Highway 42 E - Carrollton",710,"Carrollton - D Rd & US HWY 42 - SW of Substation",5.39,49,"2021-08-07",0,0,0,0,0,0,0,1,0,0,77.703421547344462,130.15034012244897,0.72363636363636374,1,"Continue to Monitor"]
["GHENT","Carroll - 402 Liberty - Ghent",717,"Ghent - US HWY 42 - NE & SW of Substation",8.6999999999999993,290,"2021-07-31",0,0,0,5.0369155045118949E-2,0.92258681979764834,0,2.7044025157232705E-2,0,0,0,81.412438057037832,125.9788301131502,0.77749601382823919,1.0813559322033899,"Continue to Monitor"]
["HUNTERS BOTTOM","Trimble - 400 Hunter Heights Rd - Milton",719,"Milton - N Spillman Lan, HWY 421 N - SE of Substation",25.59,495,"2020-03-21",1.2388389882459553E-2,0,0.9072576561208987,0,7.7294170953383617E-4,0,9.8190250273194925E-3,2.7996481782563504E-2,0,4.1765505477224872E-2,129.4273648390072,251.2813438401225,0.93356979614316749,0.84767316497977685,"Continue to Monitor"]
["LAWRENCE","Henry - 9255 HWY 55 - Campbellsburg",720,"Campbellsburg - HWY 55, HWY 316 - N & S of Substation",10.709999999999999,107,"2020-03-28",0,0,0,0,0,0,0,0,0,1,28.197022758299351,23.656422018348625,0.30097558744347735,0.3577981651376147,"Continue to Monitor"]
["SCHOLLS","Owen - 970 HWY 127 N - Owenton",724,"Owenton - HWY 127 N, State HWY 845 - NE of Substation",12.73,183,"2022-01-15",0,0,0,9.4114515500375506E-4,0.92928102214067743,0,6.2571893032673895E-2,1.4259775075814471E-3,0,5.7799621640634655E-3,6.2904681257924775,7.1367753586956528,4.965322318647164E-2,5.9782608695652162E-2,"Continue to Monitor"]
["SPARTA","Owen - RR 1 Box 136C - Sparta",730,"Sparta - State HWY 467 - NE & SE of Substation",28.589999999999996,379,"2023-09-16",5.3365115224177952E-4,0,0,4.9362731582364605E-4,2.4343386728095846E-2,0,0.83452811896863011,0.13840687342684088,0,1.69434240836765E-3,169.58829244986094,483.93331079731541,0.74724318198362449,1.8711708544301238,"Continue to Monitor"]
["GHENT PLANT","Carroll - 9486 HWY 42 E - Ghent",733,"Ghent - US HWY 42 - NE of Substation",2.2799999999999998,5,"2021-07-31",0,0,0,1,0,0,0,0,0,0,48.237333280000001,226.63333320000001,0.28999999999999998,1,"Continue to Monitor"]
["WARSAW","Gallatin - RR 1 Box 51 - Warsaw",734,"Warsaw - Smith Ave, Center Ave, E Main St - NE of Substation",3.38,446,"2020-03-28",0,0,0,0,0,0,7.627155642872735E-2,0.91918795022920752,0,4.5404933420650512E-3,21.346751350880336,94.312805677496229,0.1684072352543543,0.72485227876927394,"Continue to Monitor"]
["MORGANFIELD 4KV","Union - 307 Rhea St - Morganfield",746,"Morganfield - Morton St, Brady St, SR 947, & Spring St - SE of Substation",7.4099999999999993,565,"2019-12-20",0,0,0,0,0.34299335089700161,0,0.63843934261698654,0,0,1.8567306486011792E-2,9.2144011281494222,14.060767181738926,0.10029131926431982,8.2926747618159685E-2,"Continue to Monitor"]
["STANFORD NORTH","Lincoln - 300 Lee Dr - Stanford",767,"Stanford - US Hwy 27, E Main St - SE of Substation",15.47,585,"2018-06-16",0,0,0,0.35105043669840269,6.8848847273585648E-3,0,0.63742229915807691,0,0,4.6423794161617755E-3,44.475274068799102,45.179074715475494,0.3949585890204913,0.27667805316984634,"Continue to Monitor"]
["STANFORD NORTH","Lincoln - 300 Lee Dr - Stanford",768,"Stanford - Danville Ave, Lancaster St - SW of Substation",11.27,633,"2018-06-16",5.8070780271582356E-2,0,0,0,0.87794272848800392,0,6.1459227467811156E-2,2.5272637726025471E-3,0,0,29.245889591573189,35.318057901440746,0.26216085017168528,0.65401348543065163,"Continue to Monitor"]
["BOONE AVENUE","Clark - 660 Boone Ave. - Winchester",769,"Winchester - Boone Ave, Harkins Ave, Skylark Dr- NW of Subst.",16.79,1458,"2021-08-14",3.4677960550608951E-3,0,7.3209027829063342E-3,0,0,0,0.76739757960679045,4.8211997932166059E-2,0,0.17360172362307624,42.873273253877755,43.021858746373681,0.82678778147959398,0.50502832469594605,"Continue to Monitor"]
["PARIS 12KV","Bourbon - 520 Scott Ave - Paris",795,"Paris - Clintonville Rd - SW of Substation",16.89,1037,"2021-08-28",3.5817956509192144E-3,0,0,0,0.83311548320290618,0,0.15164551620780722,5.84436528010515E-4,0,1.1072768410356894E-2,130.98851987184585,326.42304088491522,1.2153864851945586,1.0491018580537557,"Continue to Monitor"]
["HANSON","Hopkins - 235 Fowler Rd - Hanson",809,"Hanson - Hanson Rd, N Main, Hwy 1069, & University Circle Dr - SW of Substation",1.36,42,"2019-06-22",0,0,0,0,0,0,0.68853087840429605,0.28116609129267356,0,3.0303030303030304E-2,16.742380938095238,34.589285666666669,0.26555924695459565,0.52380952380952372,"Continue to Monitor"]
["HANSON","Hopkins - 235 Fowler Rd - Hanson",811,"Hanson - US HWY 41 & City of Hanson - N of Substation",17.71,618,"2019-08-03",7.4275167061866779E-2,0,0.11418139685277,0,0.10341668463030826,0,0.28140493640870878,6.8562729036430264E-2,0,0.35815908600991592,88.569824675664151,99.857201702764726,1.048176820493578,1.1208878020140871,"Continue to Monitor"]
["CROSSROADS","Hopkins - 1340 Amanda Ln - Nortonville",812,"Nortonville - Wells Rd - W of Substation",5.99,72,"2023-01-13",4.7548742889400317E-3,0,1.5589039906205219E-2,8.1267098006860911E-2,0,0,0.89838898779799381,0,0,0,63.871378752563906,107.46952054794521,0.67907870812412996,1.2492389649923894,"Continue to Monitor"]
["DOZIER HEIGHTS","Hopkins - 200 Claire Ln - Madisonville",815,"Madisonville - Country Club Ln, US 41A - NW of Substation",13.780000000000001,658,"2019-07-27",0.14776168704677287,0,2.0066249494484869E-4,2.0745414861990511E-3,0.19142893306207881,0,0.57056065101087594,3.9978143223627543E-3,0,8.3975710576765755E-2,43.095628311772188,137.99559146610895,0.70992020148762225,2.3490628004215401,"Continue to Monitor"]
["DOZIER HEIGHTS","Hopkins - 200 Claire Ln - Madisonville",816,"Madisonville - Sandcut Ln, Mcleod Ln, Grapvine Rd - N&E of Subs.",21.52,818,"2019-09-07",2.422078410446131E-2,0,4.3692675746625457E-4,2.0134444512092484E-2,0.16937358312173423,0,0.78497473345677116,0,0,8.5952804747459915E-4,63.732559742282568,97.812088998596252,1.0858601373805814,1.6115487271765268,"Continue to Monitor"]
["NORTONVILLE","Hopkins - 55 Holly Ln - Nortonville ",819,"Nortonville - City of Nortonville, US 41, & Red Hill Rd - S of Substation",34.410000000000004,889,"2022-11-25",2.4091143632931727E-2,0,1.2137097469514663E-3,8.7843403587009719E-2,0.81022885392638422,0,7.4647792043104608E-2,1.1487132686994206E-3,0,8.2638379491886715E-4,60.635743903928798,110.2455051496019,0.87314094186470881,1.3344879329171799,"Continue to Monitor"]
["ONTON","Webster - 6294 S R 370 - Onton",832,"Onton - KY 147, Harry Ashby Rd, Hwy 41 & Main St - SW of Substation",17.459999999999997,326,"2019-09-21",2.4170177532084843E-3,0,5.1627986265007425E-3,0,0.75919319095049076,0,0.1255753354601466,9.9274285853444708E-2,0,8.3773713562087532E-3,53.335435908189154,63.649247483648296,0.65271750707933673,0.57105797130833269,"Continue to Monitor"]
["CYNTHIANA 12KV","Harrison - 208 McIlvain Blvd - Cynthiana",853,"Cynthiana/Berry - River Rd, Poplar St, US 27, City of Berry - N of Subst.",76.260000000000005,905,"2022-10-07",1.9495021505340014E-3,0,8.7507982147020172E-3,0,1.9359874042564694E-3,0,0.55965577941231126,0.40009730617319822,0,2.7610626644998023E-2,51.166161628400971,70.176909937584554,0.52916594909805659,0.29754792105391892,"Continue to Monitor"]
["WEST HICKMAN","Fayette - 3172 Ashgrove Rd - Lexington",864,"Lexington - Lauderdale Dr, Whitfield Dr, Ridgewater Dr - NW of Subst",27.200000000000003,2194,"2023-12-09",1.6530096159621207E-3,0,0,0,0,0,0.98450527591545267,6.9939159564731375E-3,0,6.8477985121120606E-3,18.485727738063225,24.766962030128962,0.13164470466588568,0.22998246824121998,"Continue to Monitor"]
["WEST HICKMAN","Fayette - 3172 Ashgrove Rd - Lexington",865,"Lexington - Saron Dr, Tates Creek Rd, Kenesaw Dr - NE of Subst",24.5,1293,"2019-02-16",1.5400041945289301E-2,0,0,0,1.4394165104219642E-2,0,0.73554485220586319,0.23457317967795738,0,8.7761066670507157E-5,48.158667176365306,72.77879880240431,0.81593991461106152,2.4699689392074844,"Continue to Monitor"]
["SHANNON RUN","Woodford - 2770 Shannon Run Rd - Versailles",868,"Versailles - Shannon Run, Lexington Rd, Pisgah Rd - N of Subst",65.930000000000007,1123,"2021-08-07",1.4221029475964839E-3,0,2.3615964288957531E-2,0,3.4546965798784267E-2,0,0.85430442109888327,8.3134111150928391E-2,0,2.9764347148500941E-3,143.20089201370797,130.89333365559568,0.99624488604641803,1.7468812935944318,"Continue to Monitor"]
["WARSAW EAST","Gallatin - 101 Brown St - Warsaw",872,"Warsaw - Hwy 42, Riverview Dr, Dorman Ln, - S & E of Subst",6.0500000000000007,224,"2021-10-16",6.2716858201244409E-4,0,0,0,6.0325495982060271E-3,0,0.99169791229566262,1.218241130527769E-3,0,4.2412839359114927E-4,254.23350377379984,985.08474808852964,0.45096214266202406,1.0934724001708309,"Continue to Monitor"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",874,"Lexington - Todds Rd - S of Substation",29.830000000000002,2415,"2022-09-03",7.602716533672368E-4,0,1.1773562564820079E-2,0,5.3240311860450753E-6,0,0.92684142266631742,2.2554725716561357E-2,0,3.806469336774787E-2,11.75350113487286,28.037596136809128,8.6910712481740343E-2,0.20781539220928802,"Continue to Monitor"]
["CARLISLE 4KV","Nicholas - 104 S Elm St - Carlisle",876,"Carlisle - Main St, Eastern Ave - ENE of Substation",7.27,386,"2019-06-15",7.1478839227807752E-3,0,0,0,2.4341442547848046E-2,0,0.83239730091487396,0.12631607997902553,0,9.7972926354717195E-3,16.068493499132124,31.11282090542084,0.14229238114885862,0.14963123551419338,"Continue to Monitor"]
["CYNTHIANA SOUTH","Harrison - 460 Education Dr - Cynthiana",880,"Cynthiana - New Lair Rd, Old Lair Rd, Ruddles Mill Pike, & Lake Rd - SE of Subst.",21,223,"2020-10-03",4.5389350914574762E-3,0,1.5051085153727653E-4,9.3936478518264928E-3,0,0,0.77404484633137172,1.1621798693211666E-2,0,0.2002502611805953,69.421482688522389,41.134805247811023,0.52921447770740926,0.60163967378653471,"Continue to Monitor"]
["CYNTHIANA SOUTH","Harrison - 460 Education Dr - Cynthiana",881,"Cynthiana - New Lair Rd, Hwy 27 - S of Substation",35.380000000000003,502,"2020-11-07",2.02785283269118E-3,0,1.852470966080051E-3,0,7.3989224976570074E-5,0,0.97479159701631601,1.6362580086485182E-2,0,4.8915098734510221E-3,204.77888375560858,220.44072807118332,0.72869289714029362,0.90261646156274,"Continue to Monitor"]
["MAYSVILLE WEST","Mason - 210 Cox Alley - Maysville",900,"Maysville - Maddox Aly, 4th St, Hwy 62 - SE of Substation",1.5500000000000003,166,"2019-09-07",0,0,0,0,0,0,0,0,0,1,3.7677797572966427,8.1274096385542176,7.1859627860554637E-2,0.19879518072289157,"Continue to Monitor"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",905,"Lexington - Todds Rd - SE of Substation",15.930000000000001,1369,"2022-06-20",0,0,0,0,0,0,0,0.84123698788579782,0,0.15876301211420224,8.3881477619085132,31.889613141557529,6.0558068519748973E-2,0.19285265597204407,"Continue to Monitor"]
["MAYSVILLE MID","Mason - 314 Lexington St - Maysville",906,"Maysville - E Reynolds dr, Elizabeth St, Center St, Union St - E of Subst.",1.25,74,"2019-10-12",0,0,0,0,0,0,0,0,0,1,5.3674146479374114,7.8506756756756761,0.11166429587482218,0.12162162162162163,"Continue to Monitor"]
["MAYSVILLE MID","Mason - 314 Lexington St - Maysville",907,"Maysville - Buckley Pl, Hwy 11, Bank St - W & S of Subst.",6.7799999999999994,220,"2019-10-12",0,0,0,0,0,0,0.91546783973368206,0,0,8.4532160266317921E-2,6.4324738669488806,9.6931818181818183,6.2406059533942196E-2,0.11363636363636363,"Continue to Monitor"]
["MAYSVILLE EAST","Mason - 1107 Forest Ave - Maysville",913,"Maysville - Bryant ln, Hwy 10, Buckner St - E of Substation",10.219999999999999,817,"2019-10-12",0,0,0,0,0,0,0.81466803911477093,0.13026248069994853,0,5.5069480185280496E-2,23.08338346003001,23.821423825153893,0.22935629849812439,0.13332429347828156,"Continue to Monitor"]
["BEAVER DAM NORTH","Ohio - 129 Raines Ave. - Beaver Dam",918,"Beaver Dam - State Hwy 273, Hope St - S of Substation",2.29,35,"2019-06-08",0,0,0,0,0,0,1,0,0,0,5.9671916508538896,22.061764705882354,2.4098671726755221E-2,8.8235294117647065E-2,"Continue to Monitor"]
["BEAVER DAM NORTH","Ohio - 129 Raines Ave. - Beaver Dam",919,"Beaver Dam - US Hwy 231 - NE & SE of Substation",17.029999999999998,803,"2024-02-10",0.10615685940560333,0,0.28846121093417354,9.0266541769564845E-3,4.8812058247466573E-2,0,4.5831559226773393E-2,0.50171165800902662,0,0,59.857204450619903,61.993344366595366,0.64491873206885852,0.59085649311974531,"Trees Trimmed in 2024"]
["KENTON","Mason - 801 Kenton Station Rd - Maysville",920,"Maysville - Lexington Rd, Duke of York St, Hwy 2515 - S of Subst.",55.67,1313,"2021-06-25",1.1088040060015701E-2,0,2.6059448988976991E-3,3.5349805134779842E-3,0.14103689664943306,0,0.30562484612847635,0.19596148218341949,0,0.34014780956627971,58.208664243065094,78.083532410561389,1.1033710320778489,1.6247911278162714,"Continue to Monitor"]
["KENTON","Mason - 801 Kenton Station Rd - Maysville",922,"Maysville - Parker Rd, Hwy 10, Martha Comer Dr - W of Subst.",4.2700000000000005,118,"2021-01-23",0,0,0,0,0.26247030878859856,0,2.2862232779097387E-2,0,0,0.71466745843230406,6.9703992339044376,11.69501423931624,0.14023313579377653,0.21367521367521367,"Continue to Monitor"]
["AUGUSTA","Bracken - 318 E 4th St. - Augusta",929,"Augusta - 5th Street, Old August-Brooksville Rd - W&SW of Subst.",22.33,659,"2022-10-21",3.5897236882955603E-4,0,5.7387069233157402E-2,0.10869101210804098,1.3131597330021732E-2,0,3.0100318224153988E-2,0.7300430766842595,0,6.0287954051536786E-2,88.008571561304322,73.54858186359769,0.80133534832949738,0.98491738354684732,"Tree Trim Scheduled for 2024"]
["AUGUSTA","Bracken - 318 E 4th St. - Augusta",931,"Augusta - Hamilton Ave, E 2nd St - N of Substation",2.9400000000000004,284,"2022-10-21",0.17212989785028204,0,0,0,0.19835340753163591,0,0.51516999542613207,6.2509528891599329E-3,0,0.10809574630279006,15.810267893488398,22.060611097317281,0.39136253671443444,0.52036344395689227,"Continue to Monitor"]
["SHARON","Bracken - 3061 Asbury Rd - Augusta",935,"Augusta - Mt Zion Rd, City of Brooksville, Hwy 10&19 - NW&SW of Subst",78.34,1201,"2019-01-19",4.3322618351841029E-2,4.6269238262224818E-4,9.7652444963958699E-3,3.1414377556984218E-3,5.9395090590298072E-2,0,1.6096824469121373E-2,5.5766608221313073E-3,0,0.86223943113189172,39.068419851800307,31.638957536635555,0.33127606515250513,0.39526196054506979,"Continue to Monitor"]
["SHARON","Bracken - 3061 Asbury Rd - Augusta",936,"Augusta - Dutch Ridge Rd, KY 1235, City of Dover - N&NE of Subst",53.499999999999993,622,"2019-02-16",3.3270271046849076E-3,0,7.4858109855410427E-3,0,4.572847526884647E-2,0,0.16493888099980189,7.8235042366665619E-2,0,0.7002847632744601,121.92370334073107,189.80502635819389,1.5374610900557149,4.4951822808060315,"Continue to Monitor"]
["PARKERS MILL","Fayette - 2085 Parkers Mill Rd - Lexington",939,"Lexington - Parkers Mill Rd - SW out of Substation",62.610000000000007,1369,"2023-11-04",2.8796107966285907E-3,0,2.9585378205062213E-4,0,3.5735558192992747E-2,0,0.80017417870548901,0.12474783796331021,0,3.6166960559528873E-2,92.619937811079723,111.5415304217623,0.86491934356118771,1.0807090082525623,"Continue to Monitor"]
["SARDIS","Mason - 4000 Blue Lick Rd - Mays Lick",941,"Mays Lick - Hwy 62 - NE of Substation",5.67,45,"2019-11-30",0,0,3.1345194472650216E-3,0,0,0,1.4171559754536224E-2,0,0,0.98269392079819873,6.3636910095282158,11.457970978260867,8.2814266625552468E-2,0.10869565217391304,"Continue to Monitor"]
["CARNTOWN","Pendleton - 15125 Hwy 8 - Foster",947,"Foster - Hwy 8 - NNW of Substation",48.45,667,"2023-10-28",6.3288435039895747E-3,0,5.5560302929960802E-2,0,1.4751279120691312E-2,0,0.45712408805904786,0.42169858682532391,0,4.4536899560986554E-2,78.787968198501019,191.73132562272241,0.56287659226605447,1.6103852939712149,"Trees Trimmed in 2023"]
["CARNTOWN","Pendleton - 15125 Hwy 8 - Foster",948,"Foster - Hwy 8 - S&SE of Substation",23.72,232,"2022-10-28",1.7190919839998658E-3,0,3.0188932401948865E-3,1.0062977467316288E-3,0,0,4.8386149988679152E-3,3.2872393059899876E-2,0,0.95654470897030586,237.87474198235591,499.60524478020375,1.5665717321244448,3.0988825810862219,"Continue to Monitor"]
["BUTLER","Pendleton - 11095 Hwy 27 N - Burnside Butler",950,"Butler - City of Butler, Flour Creek Rd, Hwy 10 - ESE of Substation",58.760000000000005,938,"2023-12-23",7.5734912658711974E-4,0,6.4993177546618E-2,0,6.9411047451709527E-3,0,0.74187017268822331,7.6234763082259474E-2,0,0.10920343281114112,141.47345400263856,151.55461268516569,1.5373072737430353,1.6347122579528308,"Continue to Monitor"]
["FLEMINGSBURG","Fleming - 523 Fountain Ave - Flemingsburg",960,"Flemingsburg - City of Flemingsburg - S of Substation",10.63,958,"2019-05-11",7.7807606263982101E-2,0,0,6.3087248322147649E-3,1.1483967188665176E-3,0,0.45912005965697239,0.34068605518269945,0,0.11492915734526472,22.379819462116362,23.401505712673494,0.22726899427192229,0.29668126657863425,"Tree Trim Scheduled for 2024"]
["FLEMINGSBURG","Fleming - 523 Fountain Ave - Flemingsburg",961,"Flemingsburg - Water St - Fountain Ave - SW of Substation",7.84,439,"2019-06-01",1.399551198771702E-2,0,0.21022794378174087,0,1.1515294673438054E-2,0,0.1668831935750561,0,0,0.59737805598204796,12.268213680293684,17.393448170858356,0.19047072757214606,0.26821288051356384,"Continue to Monitor"]
["EWINGTON","Montgomery - 4006 Old Owingsville Rd - Mt Sterling",969,"Mt Sterling - Woodland Ln, Clarence Dr - N of Substation",5.08,178,"2023-04-14",7.7290836653386458E-2,0,0,0.82782715292675457,9.4882010419859025E-2,0,0,0,0,0,53.446112147049632,91.145623832402222,0.82692210795349186,1.1340782122905027,"Continue to Monitor"]
["WEST HIGH STREET","Lexington - 727 West High St - Lexington",1102,"Lexington - West High St - SE of Substation",1.93,26,"2019-05-11",0,0,0,0,0,0,0,0,0,1,136.12760388806367,219.31494251724138,0.49230769230769245,1,"Continue to Monitor"]
["VINE STREET 12KV","Fayette - 112 E Vine St. - Lexington",1202,"Lexington - Water St - E of Substation, Ayers Aly - E of Subst.",1.02,20,"2019-05-11",0,0,0,0,0,0,0,0,0,1,11.898195507012987,19.4241666,0.17861471861471861,0.8,"Continue to Monitor"]
["BARLOW","Ballard - 433 Oscar Rd. - Barlow",1310,"Barlow - US Hwy 60 - S of Substation",14.17,211,"2022-11-18",2.597046991174674E-2,1.0320786907344608E-3,1.5902436969479957E-2,0,5.7375150072666768E-2,0,0.85561429744929129,3.8397539861406579E-2,0,5.7080270446742635E-3,222.90228918190056,206.14765359095875,0.46705562248875265,0.56727505634120667,"Continue to Monitor"]
["BARLOW","Ballard - 433 Oscar Rd. - Barlow",1312,"Barlow - N 6th St - City of Barlow",6.33,325,"2023-03-10",0.1817308154341454,0,0.57618567103935414,0,1.5472586612848975E-2,0,0.20340204699437797,1.8163471241170535E-2,0,5.0454086781029266E-3,99.725230111538934,63.88960616049819,0.59767391072334586,1.2397640973686448,"Continue to Monitor"]
["CLINTON 12KV","Hickman - 318 Moss Drive - Clinton",1316,"Clinton - City of Clinton, Hwy 58, ",27.070000000000004,655,"2021-12-04",5.5520096884001044E-3,0,7.8145456925896831E-4,0,7.0780963603037442E-4,1.4606245090337784E-3,0.76452441738675048,0.22531258182770358,0,1.6611023828227284E-3,76.743106132346341,162.74481250106192,0.61762986937004583,1.34690940162172,"Continue to Monitor"]
["FORESTDALE","McCracken - 4250 Rice Springs Rd - Kevil",1320,"Kevil - SR 1154, SR 996, & Cairo Rd - E of Substation",41.39,932,"2019-12-20",2.5499399358490098E-2,0,1.2235748696546001E-2,0.22714156563092128,0.21759322327764499,0,0.10213382540527821,0.40937743817107758,0,6.0187994600418588E-3,87.512732523550781,80.791324813135844,0.94683286654133147,1.3206229008442563,"Continue to Monitor"]
["FORESTDALE","McCracken - 4250 Rice Springs Rd - Kevil",1322,"Kevil - Clarkline Rd, Kevil Rd, Woodville Rd, & Hwy 473 - NW of Substation",26.080000000000002,605,"2019-12-20",9.230048284114778E-3,0,5.020878486372499E-4,0,1.6401536388816829E-3,0,0.62892360733382979,6.7614496949816319E-2,0,0.29208960594472011,110.94401500998568,188.63503541570878,0.98555085328248138,2.5907864949322157,"Continue to Monitor"]
["CRUTCHFIELD","Fulton - 200 Crutchfield St - Fulton",1323,"Fulton - Depot St, Hwy 924 - SW of Substation",1.2,42,"2021-07-24",0,0,0,0,0,0,0.86031680724130832,0.13968319275869162,0,0,106.80639758188154,347.22500000000002,0.72032520325203264,2.1428571428571428,"Continue to Monitor"]
["WICKLIFFE CITY","Ballard - Mayola Ave - Wickliffe",1324,"Wickliffe - Hwy 1290, Hwy 286, Hwy 21/Court St, & Beech Grove Rd - S of Substation",11.799999999999999,284,"2023-12-09",4.1867617813061089E-4,0,1.9162486614439499E-2,0,1.4009549037447364E-3,0,0.22692248854679109,8.0893068493812448E-2,0,0.67120232526308166,152.58769468363442,430.4221217221891,1.1156129929431553,2.7312577217692118,"Continue to Monitor"]
["WICKLIFFE CITY","Ballard - Mayola Ave - Wickliffe",1325,"Wickliffe - 4th St, Greene St, US 60, & County Farm Rd - N & S of Substation",14.29,312,"2023-12-09",5.3553521517420892E-3,1.6855490836160361E-3,1.1329450169621712E-2,0,0,0,0.93360216774413796,4.8027480850882244E-2,0,0,104.69879291799502,149.3027469618327,0.69194893814093217,0.57066518670860811,"Continue to Monitor"]
["GREENVILLE NORTH","Muhlenberg - 501 HWY 189 Bypass - Greenville",1327,"Greenville - HWY 601, S R 181, & Luzerne Depoy Rd - NW of Substation",43.82,798,"2022-01-01",1.1217424490240976E-2,0,3.0207311089303239E-2,0.14626949078617382,3.7209682695453061E-3,0,0.67048985933922145,6.5866590339112418E-3,0,0.13150828699160397,64.074449777652092,118.68182245396217,0.69292775066169243,1.1004302288582932,"Continue to Monitor"]
["CABIN","Livingston - 900 Three Rivers Rock Rd - Burna",1330,"Burna - 900 Three Rivers Rock Rd - S of Substation",1.24,1,"2022-04-23",0,0,0,0,0,0,1,0,0,0,57.493333200000009,65.283332999999999,0.6,1,"Continue to Monitor"]
["CLAY - KU","Webster - 62 W College St - Clay",1407,"Clay – Main St, Taylor St, & Lisman St- NE & SW of Substation",10.98,434,"2019-08-17",0,0,0.68533214444939816,0,4.6723138653588944E-2,0,0.25180561747659386,0,0,1.6139099420419082E-2,13.022212217011335,25.458928783312238,0.19032448869632645,0.21148370768744068,"Continue to Monitor"]
["DIAMOND","Webster - 830 Bill Dorris Rd - Providence",1410,"Providence - Bill Dorris Rd, S R 109 - SW of Substation",6.6099999999999994,123,"2019-06-29",1.533128916144514E-2,0,0,0,0.73363551526463133,0,0.25103319557392345,0,0,0,19.200285732562243,60.496908596774198,0.27136689116121249,0.67741935483870974,"Continue to Monitor"]
["DIXON","Webster - 818 S R 1340 - Dixon",1427,"Dixon - City of Dixon, Clay-Dixon Rd - NE of Substation",13.330000000000002,457,"2020-03-28",5.1270100209741317E-3,0,1.953146674656812E-3,0,0.16012473504899513,0,0.83074208476212674,7.4352742728412736E-4,0,1.3094960659630899E-3,10.959082210968736,16.025200973365997,0.11722820913331185,0.11158310341546951,"Continue to Monitor"]
["CORYDON","Henderson - 5430 Greenlick Rd - Corydon",1431,"Corydon - City of Corydon - E of Substation",14.48,422,"2020-09-05",4.4448036204945852E-3,0,9.1051128710737568E-3,1.236463552610312E-2,0.40135229782878074,0,0.5493507892893702,2.3382360864177578E-2,0,0,31.784511004130117,46.464730589343809,0.27478161574047361,0.26078170908804355,"Continue to Monitor"]
["SPENCER CHEMICAL 12KV","Henderson - 1413 Hwy 136 W - Henderson",1437,"Henderson - Hwy 136 & Hwy 60 - S of Substation",4.29,84,"2020-03-28",0,5.7786483839373161E-2,0.63467189030362392,0,0.29431929480901076,0,1.3222331047992164E-2,0,0,0,5.3484918691027143,13.669542479691877,5.6670598752249557E-2,0.14257703081232492,"Continue to Monitor"]
["TUNNEL HILL","Henderson - 12990 HWY 416 W - Corydon",1443,"Corydon - US HWY 41 A & S R 416 - N & E of Substation",23.2,374,"2020-10-17",1.8475837127813068E-2,0,0,0,0,0,0.93017220379635357,4.3528772462383118E-2,0,7.8231866134502587E-3,49.495371195726037,57.989319324908067,0.505715973600666,0.507530329314275,"Continue to Monitor"]
["MANITOU","Hopkins - 7615 Nebo Rd - Nebo",1450,"Nebo - US 41 ALT & City of Nebo & State HWY 1034- W of Substation",15.1,273,"2019-01-26",0,0,0.21012477354494655,1.6789569033706719E-2,0,0,0.62496491541425325,6.1034421168125332E-2,0,8.7086320838968126E-2,62.112533107565753,72.657280391048062,0.68019366689323257,0.6539679459655845,"Continue to Monitor"]
["SENTRY","Hopkins - 1000 John Hardy Rd - Madisonville",1454,"Madisonville - Pleasant View Rd & Austin Powder Rd - SE of Substation",6.08,65,"2019-01-26",0,0,0,0,0.38344402277039846,0,0.33002846299810246,0,0,0.28652751423149903,95.32575299974971,213.5625681880864,0.6681909577947257,2.0611292713602851,"Continue to Monitor"]
["SENTRY","Hopkins - 1000 John Hardy Rd - Madisonville",1455,"Madisonville - Manitou-Richland Rd - W of Substation",0.89,4,"2019-01-26",0,0,0,0,1,0,0,0,0,0,23.80666665,119.03333325,0.2,1,"Continue to Monitor"]
["ZION","Henderson - 7485 HWY 351 - Henderson",1468,"Henderson - HWY 351/Zion Rd, Adams Ln, & Spring Garden Rd - W of Substation",12.649999999999999,721,"2020-08-29",1.3033035397881639E-2,0,0,0,1.0683676549723721E-2,0,0.84672730374978677,2.0002362483757922E-2,0,0.10955362181884999,93.712608616904106,105.41908550371056,0.45650292127919989,1.0315986429623709,"Continue to Monitor"]
["SEBREE","Webster - 199 N Railroad St - Sebree",1473,"Sebree - Railroad St, Dixon St, State St, & Church St - S of Substation",5.58,326,"2020-03-28",0,0,0.93847587974831037,0,0,0,6.152412025168958E-2,0,0,0,8.1496760871594098,13.122680935779817,5.0301777176170001E-2,9.480122324159021E-2,"Continue to Monitor"]
["EARLINGTON 12KV","Hopkins - 310-A McEuen - Madisonville",1476,"Madisonville - Railroad St - SE of Substation",32.51,944,"2020-03-28",1.6788850022203351E-2,0,1.0673190037317213E-3,0,0.20433315934215754,0,0.76652981092093275,3.3499793547783949E-3,0,7.9308813561962937E-3,29.612457139840462,43.736430736363012,0.4946967221255707,1.1450625782156676,"Continue to Monitor"]
["EARLINGTON 12KV","Hopkins - 310-A McEuen - Madisonville",1478,"Madisonville - Hwy 1337 - W of Substation",14.23,145,"2019-11-02",5.2116660937623946E-2,0,1.2877125254501706E-2,0,0,0,0.93172743858906903,0,0,3.2787752188053625E-3,24.98577156762541,22.381924212556399,0.59296345585685062,0.72940317164455082,"Continue to Monitor"]
["CROFTON","Christian - 13770 Madisonville Rd - Crofton",1491,"Crofton - Madisonville Rd, W Princeton St, W Mill St - S of Subst",6.3800000000000008,266,"2023-12-09",7.2451104606288317E-4,0,0,0,9.902864549201217E-4,0,9.5023810564026385E-3,0.98802190280629698,0,7.6091863631729938E-4,210.07780625927498,1023.7623077068688,0.27802770908831109,1.0713867560569859,"Trees Trimmed in 2023"]
["CROFTON","Christian - 13770 Madisonville Rd - Crofton",1492,"Crofton - City of Crofton, Madisonville Rd - N&S of Substation",26.990000000000002,466,"2023-12-16",1.1934252433909841E-3,0,7.9059716439150373E-5,4.7304063669424976E-3,3.093305524391805E-2,0,0.89583129409461559,6.5884979406826236E-2,0,1.3477799278674206E-3,390.9416336768777,1083.081972000645,1.8008337660575457,1.4097995280918334,"Continue to Monitor"]
["KUTTAWA","Lyon - 3487 Lake Barkley Dr - Kuttawa",1501,"Kuttawa - Hwy 295, Lake Shore Dr, & Holley St - SW & SE of Substation",11.2,430,"2021-02-13",1.5686274509803921E-3,0,4.950632735363649E-4,0,2.7923793630927549E-3,0,0.90410791266861357,2.3473786677791686E-3,0,8.8688638575997777E-2,116.52520948388981,319.28804159564453,1.0291437669916172,1.5598815872784186,"Continue to Monitor"]
["KUTTAWA","Lyon - 3487 Lake Barkley Dr - Kuttawa",1502,"Kuttawa - Mary Blue Rd, State HWY 93, & US HWY 62 - NE of Substation",7.2700000000000005,133,"2021-02-13",3.4565234164030553E-2,0,2.2220507676876784E-2,0,4.8453051462078546E-2,0,0.55481830105701724,0.29966823547565774,0,4.0274670164339173E-2,74.888000606557071,88.769584393782964,0.60673200534307414,1.0972393670744023,"Continue to Monitor"]
["EDDYVILLE PRISON","Lyon - 328 Water St - Eddyville ",1503,"Eddyville - HWY 93, HWY 1055, Perry Springs Rd, E of Substation",60.05,932,"2021-08-14",8.4706869225402381E-2,0,0.1413649727174838,3.0448336633583507E-3,8.2162114203443284E-2,0,0.56259653735869752,0.10189102318509766,0,2.4233649646516992E-2,53.717099440474882,124.77897646561014,0.54880526644528538,0.97988050236717239,"Continue to Monitor"]
["EDDYVILLE","Lyon - 1765 S R 3305 - Eddyville",1506,"Eddyville - City of Eddyville - NW of Substation",27.29,1028,"2021-03-06",7.6086370498166921E-3,1.3478542160879879E-3,0.58670072244985982,0,2.589227949105025E-2,0,0.15718675868018114,0.21726736036230321,0,3.996387750700884E-3,75.571458478058304,144.10175167385515,1.5141616726653149,1.7535049064021599,"Continue to Monitor"]
["FREDONIA","Caldwell - 150 Wigginton Ln - Fredonia",1509,"Fredonia - Hwy 91, Princeton Fredonia Rd, & Marion Rd - SE of Substation",34.18,199,"2021-11-06",6.026701259391384E-3,0,4.2781471271823142E-2,0,0,0,0.25755364574887846,9.4589481649640561E-4,0,0.69269228690341067,138.70928270473578,137.9367194084102,1.0516724815190404,1.1352281307032677,"Continue to Monitor"]
["FREDONIA QUARRY 12KV","Caldwell - 181 Fredonia Quarry Rd - Fredonia",1513,"Fredonia - Beck Rd & New Bethel Church Rd - S of Substation",11.85,71,"2021-11-13",6.8380397619349116E-3,0,0,0,7.4711915917437003E-3,0,0,0,0,0.98569076864632144,53.30539831331005,109.70521646537559,0.47705373714690608,0.93094679186228479,"Continue to Monitor"]
["CEDAR BLUFF","Caldwell - 10195 Hopkinsville Rd - Princeton",1514,"Princeton - Hopkinsville Rd - SSW of Substation",0.23,5,"2023-01-06",0,0,5.0501406824904403E-4,0,0,0,3.8958228122069113E-3,0.995599163119544,0,0,119.19399997333332,12.303333199999999,0.31333333333333335,0.4,"Trees Trimmed in 2023"]
["CLAXTON","Caldwell - 1600 Jones-Keeney Rd - Princeton",1519,"Princeton - Mt Hebron Rd, Dearing Cem. Rd - W & E of Subst.",12.45,56,"2023-12-16",0,0,0,0,3.121387283236994E-2,0,0.94936416184971095,0,0,1.9421965317919076E-2,64.776723699630196,76.913403246553884,0.43112775028862427,0.51535087719298245,"Continue to Monitor"]
["SUNSET 2 2.4KV","Hopkins - 1515 Olney Rd - Dawson Springs",1523,"Dawson Springs - Hwy 1220, Purdy Ln, & Walnut Grove Rd - S of Substation",2.25,27,"2022-12-31",0,0,4.2606516290726815E-2,0,0,0,0.95739348370927313,0,0,0,15.506860650529106,42.733333321428567,0.10846560846560842,0.3214285714285714,"Continue to Monitor"]
["SUNSET 2 2.4KV","Hopkins - 1515 Olney Rd - Dawson Springs",1524,"Dawson Springs - Olney Rd, Walton Calvert Rd. & McClearn Ln - NW of Substation",5.45,59,"2022-12-31",2.8527131782945738E-3,0,0.39280620155038759,0,0,8.8682170542635653E-3,0.553984496124031,0,0,4.1488372093023258E-2,17.165443004593808,76.881666622033904,0.28469316189362948,1.3053672316384182,"Continue to Monitor"]
["DAWSON 12KV","Hopkins - 203 Parker St - Dawson Springs",1529,"Dawson Springs - Mill Dam Rd, Mt Hebron Rd, Hwy 672 - W & SW",35.1,595,"2022-07-08",3.2475081473575883E-2,0,6.1310056983857747E-2,6.2091440986449656E-2,9.4051952507099162E-2,0.16132720931562197,0.53421890186960419,5.0141983190714869E-2,0,4.3833736730765566E-3,26.359857696633025,44.263127587885911,0.40907651680508783,0.82518073766527444,"Continue to Monitor"]
["DAWSON 12KV","Hopkins - 203 Parker St - Dawson Springs",1530,"Dawson Springs - Hospital Dr, Saddle Club Rd - NE & SE of Subst",12.4,296,"2022-09-09",1.5150609014612363E-3,0,0.10590475051332655,0,0.24846998783964278,0,0.613529892550286,2.6867412236110281E-2,0,3.7128959591730959E-3,63.208772584167605,105.8683795414164,0.81083278466389452,2.4355378105378107,"Continue to Monitor"]
["SIXTH VEIN","Hopkins - 2395 Sixth Vein Rd - Dawson Springs",1541,"Dawson Springs - Charleston Rd, Hwy 70, Campbell Rd, & High Glory Rd - N of Substation",40.58,464,"2022-11-25",2.3694552179385096E-3,0,6.1901214907661879E-3,3.5240027739963528E-2,1.7465902961497958E-3,0,0.83892841548300934,7.0582796085582933E-2,0,4.4942593686589781E-2,58.415389244491202,130.80729962156789,0.80800760883554257,1.5958658969128967,"Continue to Monitor"]
["SIXTH VEIN","Hopkins - 2395 Sixth Vein Rd - Dawson Springs",1544,"Dawson Springs - Fergusontown Rd, Hwy 109, Niles Rd & Fox Rd - W & S of Substation",26.72,357,"2023-04-01",2.0710996320752418E-3,4.2640286542725567E-5,5.8076070271192222E-2,0,1.9614531809653761E-3,0,0.874704563728954,5.8429375502546239E-2,0,4.7147973977242274E-3,55.4596280649763,57.0814467208751,0.76950426971403629,0.62036651798674669,"Continue to Monitor"]
["ST CHARLES","Hopkins - 660 St. Charles Rd - St. Charles",1553,"St. Charles - City of St. Charles & Mc Gregor Rd - SE of Substation",12.520000000000001,213,"2022-10-14",1.0516554012065355E-2,0,3.8433224662275207E-3,0,1.6348461236937962E-3,0,0.81605590982532961,0.16794936757268372,0,0,37.659315138381359,136.80705910042244,1.1202394450728803,5.042237947273609,"Continue to Monitor"]
["ST CHARLES","Hopkins - 660 St. Charles Rd - St. Charles",1554,"St. Charles - Ilsley Rd, Union Temple Rd, & Hwy 112 - SW/NW of Substation",68.47,618,"2022-11-04",2.5405782098903255E-3,0,3.2066765448136345E-2,0,0.10568940670225505,0,0.67782017713006004,0.17003606200228688,0,1.1847010507371398E-2,105.94432830916189,95.405548805734355,0.68612878030552782,0.68620715480842132,"Continue to Monitor"]
["GRAHAM","Muhlenberg - 5230 S R 175 S - Greenville",1603,"Greenville - S R 175, Landfill Rd, & S R 70 - NW of Substation",19.52,269,"2023-11-20",1.7078124616801218E-3,0,6.1244919480878523E-3,0,4.193058611856143E-2,0,0.92797757994502006,2.2047725109079274E-2,0,2.1180441757129447E-4,85.933955372082011,66.088886616221629,0.69764682021257485,0.89262094231846911,"Continue to Monitor"]
["CALHOUN","McLean - 530 W First St - Calhoun",1606,"Calhoun - High St, W 7th St, S R 81 - N of Subst.",6.28,324,"2023-10-07",0,0,2.8741206986987417E-4,2.7304146637638046E-4,0.98717064373118357,0,7.0775222205456522E-3,0,0,5.1913805120246022E-3,20.54594149357542,74.15268679479,0.26822984967257596,1.0922133081642285,"Continue to Monitor"]
["GREENVILLE 12KV","Muhlenberg - 200 N Boggess Ave - Greenville",1614,"Greenville - Outer York, Lake Rd, & Rogers Ave - N of Substation",2.67,67,"2021-05-08",0.32832467350091277,0,0,0,0,0,2.064316809436877E-2,0.6510321584047184,0,0,26.724937573408177,36.587478036215977,0.73179302991418871,0.45610184372256363,"Continue to Monitor"]
["POWDERLY","Muhlenberg - Opportunity Way - Greenville",1625,"Greenville - Opportunity Way & N Main St - E of Substation",1.24,34,"2021-05-22",0,0,0.65079365079365081,0.34920634920634919,0,0,0,0,0,0,1.1113725411764706,5.5568627058823532,1.7647058823529412E-2,8.8235294117647051E-2,"Continue to Monitor"]
["POWDERLY","Muhlenberg - Opportunity Way - Greenville",1626,"Greenville - Main St - NE of Substation",24.6,833,"2021-05-22",4.7346314609032519E-2,0,3.2052196961973698E-3,0,4.9509634009583033E-2,0,0.57739626873279637,0.2672076664287899,0,5.5334896523600775E-2,93.602775835793722,129.40654115214056,1.2621163227113508,2.0717876704423412,"Continue to Monitor"]
["ISLAND","McLean - 499 E Main St - Island",1638,"Island - City of Island, Hwy 85, 1412, & Old Island Rd - W & E of Substation",37.979999999999997,615,"2020-11-14",2.0130892221025598E-2,0,9.9063872090133384E-2,2.4355894292105045E-3,3.1132466241405022E-2,0,0.63626874326899185,0.20447353160467235,0,6.4949051445613451E-3,110.7303640432295,27.06985683831499,1.2014174122194194,1.2307202818658229,"Continue to Monitor"]
["LIVERMORE","McLean - 190 Main St - Livermore",1642,"Livermore - Hill St, Hwy 431, & Comy Dock Rd - NE of Substation",6.35,341,"2023-01-20",0,0,0,0,1.7213107328253958E-3,0,0.9620224495157681,3.6256239751406495E-2,0,0,94.408247917488936,47.322386990155017,1.0186641167965171,1.5068296123119582,"Continue to Monitor"]
["CENTRAL CITY","Muhlenberg - 106 Pendleton St - Central City",1645,"Central City - Hwy 70, S Cherry Hill Rd - W of Substation",12.4,413,"2024-03-01",1.0947322217054831E-3,0,3.3361899138322944E-2,0,1.336670655428461E-2,0,0.80521604631840771,0.14440536967461109,0,2.555246092668168E-3,66.82156796666716,41.285514654123716,0.73163714446888706,0.80770163586940591,"Continue to Monitor"]
["CENTRAL CITY","Muhlenberg - 106 Pendleton St - Central City",1648,"Central City - E Reservoir St, N 2nd St, Whitmer St - N of Subst.",12.530000000000001,741,"2020-12-05",3.945107025675746E-3,0,0.36789750533826365,0,0,0,0.44157856361647829,0.17006926722566534,0,1.6509556793916982E-2,20.641390237558173,40.588236471314708,0.26559037381479733,0.38422088343640171,"Continue to Monitor"]
["CENTRAL CITY SOUTH","Muhlenberg - 500 E Second Ave - Central City",1649,"Central City - Everly Borthers Blvd, S Stroud Ln - SW of Subst.",8.91,307,"2020-12-12",0,0,4.8127212214063075E-2,2.3371546304611971E-2,0,0,0.92850124148132496,0,0,0,23.624684897546203,24.398250940743836,0.18642609121404152,0.33360943984039498,"Continue to Monitor"]
["CENTRAL CITY SOUTH","Muhlenberg - 500 E Second Ave - Central City",1650,"Central City - Everly Borthers Blvd, S R 604, US 431 - E of Subst.",18.569999999999997,786,"2020-12-12",4.3771055851149704E-3,0,8.7900890848620317E-4,8.4671878531732223E-4,0,0,0.42485550169881925,0.56855731317472902,0,4.8435184753321396E-4,73.639968702523092,46.911771758722566,0.32711085899421077,0.40809687308625037,"Tree Trim Scheduled for 2024"]
["CENTRAL CITY SOUTH","Muhlenberg - 500 E Second Ave - Central City",1651,"Central City - W 2nd Ave, Center St, W Reservoir St - W of Subst.",5.53,410,"2020-12-05",7.1768596242596024E-4,0,2.3165812711217705E-4,3.906391947381809E-4,2.0258730331770775E-3,0,0.75740397543515392,0.23851248228496674,0,7.1768596242596024E-4,31.115937783117971,96.698653169739273,0.41052983516278874,1.2244272720242242,"Continue to Monitor"]
["BEECH CREEK 1","Muhlenberg - 169 Beech Creek Browder Rd - Beech Creek",1671,"Beech Creek - Beech Creek Browder Rd - NE of Substation",5.120000000000001,116,"2023-06-23",0,0,0.11049779205138499,5.2187876354877561E-3,2.9355680449618627E-3,0,0.81541047771979125,6.5937374548374145E-2,0,0,69.874770941832679,62.888981098038343,0.50004526233393753,0.8888177054454085,"Continue to Monitor"]
["DRAKESBORO","Muhlenberg - 201 S Mine St - Drakesboro",1674,"Drakesboro - Broad St, SR 2107, & Big Springs Rd - NE of Substation",13.62,376,"2023-09-09",0,0,0,0,2.885794984451228E-2,3.9799149810276456E-3,0.95308265099426548,1.3708596045761889E-2,0,3.7088813443268378E-4,48.564053695325335,18.524228351647228,0.38929945394203513,0.42034222777354857,"Continue to Monitor"]
["SALEM","Livingston - 266 W Main St - Salem",1703,"Salem - Hwy 60, College St, & Levias Rd - ENE of Substation",19.52,390,"2022-05-06",1.0705428060151321E-2,0,0,0,2.2603836373340032E-3,0,0.31441308510972277,0.66122500235456627,0,1.1396100838225599E-2,14.12096110539969,29.574701081986412,0.12767176412234085,0.17451737269952466,"Continue to Monitor"]
["SALEM","Livingston - 266 W Main St - Salem",1704,"Salem - Hayden Ave, Hwy 723, & Jayna Ln - NE/SE of Substation",13.24,307,"2022-05-06",1.6741019018548957E-2,0,0.42383188541911249,0,0,0,0.30338107536980513,0.25604602019253347,0,0,56.02647753263566,101.21233738815995,0.55630309831204117,1.0622074129869588,"Continue to Monitor"]
["DYCUSBURG","Crittenden - 9315 S R 70 - Dycusburg",1707,"Dycusburg - City of Dycusburg, S R 70 - N & SW of Substation",6.7299999999999995,88,"2021-08-28",0,0,0.16897959183673469,0,0,0,0.42040816326530611,0.41061224489795917,0,0,10.460915141658949,13.778040928115423,9.4617505702356539E-2,0.10125127681307457,"Continue to Monitor"]
["MEXICO","Crittenden - 2747 S R 70 - Crayne",1708,"Crayne - S R 70 & Ken Spar - NE of Substation",8.9499999999999993,117,"2021-09-11",0,0,0,0,0,0,0.80947099922368859,0.19052900077631141,0,0,7.2473049104011125,11.959742118354338,9.5301371300072615E-2,0.13631754309720409,"Continue to Monitor"]
["MEXICO","Crittenden - 2747 S R 70 - Crayne",1709,"Crayne - S R 70 & Marion Rd - W of Substation",11.28,121,"2021-09-11",9.1906826816071218E-3,0,4.9694923059211788E-3,0,5.4683602594113355E-3,0,0.93696995279941675,4.3401511953643654E-2,0,0,126.70756011095857,425.15940239012895,0.79063224014224387,2.5022399855484796,"Continue to Monitor"]
["MARION SOUTH","Crittenden - 505 Chappell Hill Rd - Marion",1711,"Marion - HWY 641 - S of Substation",15.59,365,"2021-11-20",9.2136338455258478E-3,0,5.8605708954135929E-3,0,1.2654168003032335E-2,0,0.28104498935766975,0.67107910312855357,0,2.014753476980494E-2,50.129741323050403,88.362975383696394,0.48786169527362561,1.2323003218803796,"Continue to Monitor"]
["MARION","Crittenden - 106 Sparmill Rd - Marion",1715,"Marion - Gum St, Mill Rd, Sturgis Rd/Main St - N of Substation",9.3199999999999985,309,"2022-04-15",1.4637040944155074E-2,0,0,0,0,0,0.45658337179402653,0,0,0.5287795872618184,9.4502249036406418,14.138003680436576,0.10599741026499773,0.18820991179643379,"Continue to Monitor"]
["SUNOCO","Union - 2823 S R 130 S - Morganfield",1731,"Morganfield - S R 130 & Adamson Rd - SW of Substation",23.099999999999998,180,"2020-01-18",6.6308891067650552E-3,0,2.0124877444656587E-3,0,1.0114040972186388E-2,0,0.9399091800402497,3.9501522266370812E-2,0,1.8318798699623303E-3,113.22242971261406,211.96711222363413,0.72808646300439772,1.1271332105586251,"Continue to Monitor"]
["SUNOCO","Union - 2823 S R 130 S - Morganfield",1732,"Morganfield - S R 130 - NE of Substation",4.09,29,"2020-01-18",0,0,0.16061452513966482,0,6.5642458100558659E-2,0,0,0.5027932960893855,0,0.27094972067039108,61.777937962819806,24.703448241379313,0.71864571746384864,1.3793103448275861,"Continue to Monitor"]
["MORGANFIELD","Union - 305 Rhea St - Morganfield",1750,"Morganfield - S R 947, N Chapman St, & Hedge Rd - NW of Substation",9.2900000000000009,284,"2019-12-20",0,0,0,0,4.3782837127845885E-2,0,0.95621716287215408,0,0,0,3.5590961504672194,4.020685068322214,3.4019027708840459E-2,7.0410180380528778E-2,"Continue to Monitor"]
["WAVERLY","Union - 178 Blessed Martin Rd - Waverly",1764,"Waverly - E Main St, S Maple St, & E Market St - S of Substation",3.8600000000000003,162,"2019-12-06",0,0,0.29939175489975217,0,0,0,2.0725388601036267E-2,0.67988285649921154,0,0,13.271484425046513,45.044580766871164,7.1280080973332494E-2,0.20858895705521471,"Tree Trim Scheduled for 2024"]
["MANNINGTON","Christian - 2535 Mannington Loop - Mannington",1801,"Mannington - HWY 407 & US 41- E of Substation",3.27,23,"2023-05-12",0,0,2.3154942438769854E-3,0,0,0,0.99768450575612311,0,0,0,327.60313268888899,1277.6041665833336,1.1722222222222221,2.4166666666666665,"Continue to Monitor"]
["MANNINGTON","Christian - 2535 Mannington Loop - Mannington",1802,"Mannington - HWY 407, Daniel Boone Rd, & Possum Pocket Rd- NW & SW of Substation",15.38,147,"2023-05-29",3.5464136891568402E-4,0,4.5972029303884964E-4,0,0,0,0.91149399244088491,0,0,8.7691645897160567E-2,355.18793050379088,1094.0322377183843,1.9727588455431035,3.3712053432743057,"Continue to Monitor"]
["ECHOLS","Ohio - 5590 S R 1245 - Rockport",1903,"Rockport - Hwy 1245, Hwy 62, & City of Rockport - NW & SE of Substation",13.68,322,"2020-12-05",6.836108676599474E-3,0,7.9851981692472488E-3,0,0.4998247151621385,0,0.31994351933002241,0.15080338884019864,0,1.4607069821793748E-2,178.84405780701243,279.46779950171629,0.94685238633429081,2.3073309981865697,"Continue to Monitor"]
["RIVERVIEW","Ohio - 25 Riverview Rd - McHenry",1907,"McHenry - Watts Rd, City of McHenry, & HWY 62 - E & S of Substation",23.93,514,"2023-09-16",0,0,1.3181097593559075E-4,0,6.7508594431876876E-4,0,0.89526192978393693,1.1139808695961952E-2,0,9.2791364599846812E-2,211.44077099735469,898.94803602647494,0.6430119707320483,1.4627105331034902,"Continue to Monitor"]
["HARTFORD","Ohio - 425 Walnut St - Hartford",1911,"Hartford - US HWY 231, Old Main St, HWY 1543- E of Substation",8.7799999999999994,396,"2023-03-03",4.9834403136709065E-3,0,0.28992189296166726,6.2106590941571956E-2,2.4718361057085868E-2,0,0.60519595111008928,7.8914827909751274E-3,0,5.1822808249395707E-3,22.109696902214573,46.410504208725065,0.32712248260486743,0.77603053651153342,"Continue to Monitor"]
["HARTFORD","Ohio - 425 Walnut St - Hartford",1913,"Hartford - US HWY 231, Washington St, Union St- N & NE of Substation",9.08,567,"2024-02-17",8.992926397951094E-2,0,0,0,0.13981035428989572,0,4.8935910726263798E-3,0.75115860723214833,0,1.4208183425818647E-2,31.088413322897715,25.226960365609482,0.21924752403464937,0.25046063554933884,"Trees Trimmed in 2024"]
["BEAVER DAM","Ohio - 310 Ridgecrest Dr. - Beaver Dam",1914,"Beaver Dam - Ridge Crest Rd & US Hwy 62 - City of Beaver Dam",13.36,533,"2019-05-25",9.7692727995231474E-2,0,0.20287353467117028,0,2.3258990661633221E-2,0,2.5916451420623883E-2,0.64936419630439113,0,8.9409894695012917E-4,44.696408454617213,54.929489587928003,0.49795724850856332,0.6432020048352568,"Continue to Monitor"]
["BEAVER DAM","Ohio - 310 Ridgecrest Dr. - Beaver Dam",1916,"Beaver Dam - Main St. - S of Substation",33.32,928,"2019-05-25",0.24141902692954051,0,0,0,5.0334057466081897E-3,3.0741484608763371E-4,0.25321555929007666,0.33270074189449522,0,0.16732385129319177,55.37359414734361,118.58227612328835,0.93175919828000442,2.3427750037041646,"Continue to Monitor"]
["BUENA VISTA","Garrard - 164 High Bridge Rd. - Lancaster",2105,"Lancaster - Rock Quarry Rd, Lexington Rd, & US 27 - E of Substation",20.350000000000001,343,"2022-10-15",2.0406959598938366E-4,0,1.613447360660572E-2,0,0.23775759363019758,0,4.250663521085226E-2,0.67311943379534067,0,3.0277794161014449E-2,126.34944708665709,194.96900563703014,1.0315584040436083,2.7834315968873784,"Continue to Monitor"]
["RICHMOND 3 12KV","Madison - 950 Vickers Dr - Richmond",2109,"Richmond - Lancaster Rd - SW of Substation",60.469999999999992,1357,"2020-03-14",1.3738391202840607E-3,0,2.4377756999695976E-2,7.7009562379179593E-4,0.6482140091436307,0,0.12326836039901566,0.19319935294758761,0,8.7965857659941839E-3,31.242318021451382,23.532689962613933,0.25342691279807206,0.32235653380859414,"Continue to Monitor"]
["DANVILLE E 4KV","Boyle - 805 East Dr - Danville",2111,"Danville - E Walnut St, Alta Ave, & E Main St - W of Substation",2.5299999999999998,347,"2021-04-16",0,0,0,0,0,0,0.96496299058985535,3.5037009410144593E-2,0,0,10.246446853084777,8.4381364063400568,6.9473376459124922E-2,7.492795389048991E-2,"Continue to Monitor"]
["DANVILLE E 12KV","Boyle - 805 East Dr - Danville",2113,"Danville - Lexington Ave, Fork Church Rd, & Lancaster Rd - NW & E of Substation",46.53,1331,"2021-04-10",3.9282533428492225E-4,0,5.9572610754920642E-5,0,6.7181389752331299E-4,0,0.71282167735238078,0.28512159300700124,0,9.3251779805474783E-4,43.829177174924027,38.432897153493769,0.73228777240668297,1.1554591961023188,"Continue to Monitor"]
["HARRODSBURG 2 12KV","Mercer - 709 E Office St - Harrodsburg ",2130,"Harrodsburg - Beaumont Ave, S College St, & Perryville St - SW of Substation",20.119999999999997,1097,"2021-09-11",4.6816014305583152E-3,0,9.262368368766144E-2,9.190343731372938E-2,0.21436518974766539,0,0.36505563282336578,0.23137045499701969,0,0,33.275886170212523,78.372460515431058,0.44272947440867966,1.3626555857727671,"Continue to Monitor"]
["HARRODSBURG 3","Mercer - 1020 N College St - Harrodsburg",2135,"Harrodsburg - Crosses over N College St - E of Substation",0.2,3,"2022-03-05",0,0,1,0,0,0,0,0,0,0,4.6755555333333323,23.377777666666663,6.6666666666666666E-2,0.33333333333333331,"Continue to Monitor"]
["LANCASTER 1","Garrard - 104 Hamilton Ave - Lancaster",2139,"Lancaster - Maple St & Lexington Rd - NW of Substation",8.09,466,"2023-11-24",0,0,0.39561096064999202,0,0.26131113589294247,0,0.27819818384578621,0,0,6.487971961127928E-2,35.048527748134958,37.748979969431176,0.41099557953609739,0.40241402661102871,"Continue to Monitor"]
["LANCASTER 1","Garrard - 104 Hamilton Ave - Lancaster",2141,"Lancaster - Richmond St, Cowden Ct, & Hamilton Ave - N/E/SE of Substation",5.25,369,"2023-11-24",0,0,0.76418211859739305,0,0.23187075454378558,0,2.6084694939110214E-3,1.3386573649103483E-3,0,0,27.948655760891722,85.398775386681052,0.44742527050561504,0.95886596916430256,"Continue to Monitor"]
["LANCASTER 2","Garrard - 183 Industry Rd - Lancaster",2143,"Lancaster - Crab Orchard St & Richmond St - NE of Substation",3.91,107,"2023-12-16",0,0,0,0,0,0,5.5658056580565808E-2,0.94434194341943423,0,0,2.1406160665054212,1.6475757545454544,1.2810675562969142E-2,1.8181818181818181E-2,"Trees Trimmed in 2023"]
["PINE HILL","Rockcastle - 501 Flat Rock Rd - Mt. Vernon",2148,"Mt. Vernon - Mullins Station Rd, Skyline Rd, & Honeycomb Rd - NE of Substation",4.74,51,"2020-07-25",0,0,0,0,0,0,0.88034038073515219,9.9394683744188084E-2,0,2.0264935520659708E-2,65.90893241786469,219.30424207503771,0.35091645889124884,0.92420814479638014,"Continue to Monitor"]
["SHAKERTOWN","Mercer - 3499 Lexington Rd - Harrodsburg",2151,"Harrodsburg - Shakertown Rd, HWY 342, & Handy Pike - S of the Substation",32.06,320,"2022-04-09",3.3212226124938358E-4,0,3.592959008061513E-3,0,3.398046852722228E-2,0,0.64255593240808773,0.31922652415602365,0,3.1199363935548153E-4,86.615981834385877,134.13016753257364,0.80687166800591326,1.3153919044619575,"Continue to Monitor"]
["WEST CLIFF","Mercer - 815 Dix Dam Rd - Burgin",2159,"Burgin - Dix Dam Rd - S of Substation",1.1200000000000001,4,"2022-04-09",0,0,0,0,0,0,0.69938650306748462,0,0,0.30061349693251532,8.1233333000000005,40.616666500000001,0.25,1.25,"Continue to Monitor"]
["MOUNT VERNON","Rockcastle - 56 Old Somerset Rd - Mt. Vernon",2166,"Mt. Vernon - Richmond St and Williams St - NE of Substation",12.840000000000002,841,"2020-10-03",1.812411784272653E-2,0,0,0,0.19104042864977122,0,0.65384373342443336,0.12122301834887128,0,1.5768701734197584E-2,31.020507938344927,48.763161573866711,0.21775996661438687,0.23272601723966591,"Continue to Monitor"]
["RICHMOND NORTH","Madison - 2236 Lexington Rd - Richmond",2170,"Richmond - Lexington Rd - N of Substation",34.890000000000008,828,"2023-02-17",7.1237622463097032E-4,0,2.9259916089579435E-2,0,6.6997109252267414E-2,0,0.86145782170347907,3.3702894122146276E-2,0,7.8698826078968786E-3,51.371904075413894,32.061244718143342,0.39627701623917205,0.65025094013381957,"Continue to Monitor"]
["RICHMOND NORTH","Madison - 2236 Lexington Rd - Richmond",2171,"Richmond - Jacks Creek Rd, N Keeneland Dr, and Foxhaven Dr - SE of Substation",19.380000000000003,2075,"2023-04-21",1.1471410019282988E-2,2.7875067228103316E-5,1.4560623352091614E-3,0,0.3093476578384689,0,0.54689078220718057,6.5785158658323822E-2,0,6.50210538743064E-2,45.73252519345791,48.971949923635968,0.51541441807567112,0.46156291146554534,"Reliability Improvements Scheduled for 2024"]
["CAMPBELLSVILLE 1","Taylor - 101 Old Greensburg Rd. - Campbellsville",2204,"Campbellsville - New Columbia Rd - S of Substation",15.149999999999999,200,"2023-07-08",1.6838483809616107E-3,0,0,0,0.72094150141128299,0,6.5912367200087224E-2,0.20929387394153776,0,2.1684090661304193E-3,44.81779588515942,48.863633979294242,0.37262015762899919,0.23982709847339417,"Continue to Monitor"]
["COLUMBIA","Adair - 114 Lindsey Wilson St - Columbia",2210,"Columbia - Guthrie St, Miller Ave, & Adair Ave - S & SE of Substation",2.13,149,"2019-03-23",0,0,0,0,0,0,0.4217767963308986,0.5782232036691014,0,0,26.686504694425061,30.08563981655481,0.36051006711409395,0.38671140939597315,"Continue to Monitor"]
["COLUMBIA","Adair - 114 Lindsey Wilson St - Columbia",2211,"Columbia - Burkesville Rd & Greensburg St  - W of Substation",4.3600000000000003,457,"2019-03-23",5.9638062384765531E-3,0,0,0,1.8367225559478558E-2,0,0.96712607259298511,1.5761101709119811E-3,0,6.9667854381478137E-3,36.515454798986774,34.977429477278577,0.47945376793439154,0.6816993774962179,"Continue to Monitor"]
["GREENSBURG","Green - 424 Old Hodgenville Rd - Greensburg",2212,"Greensburg - City of Greensburg - SE of Substation",8.66,678,"2019-11-09",6.7153420301359118E-4,0,0,0,0,0,0.9880941223642894,1.0221337347325802E-2,0,1.0130060853712304E-3,11.933190812183714,10.477430865779532,0.16769076101285377,0.19199313298736836,"Continue to Monitor"]
["GREENSBURG","Green - 424 Old Hodgenville Rd - Greensburg",2214,"Greensburg - Buckner Hill Rd, Hawthorne Rd, HWY 1464, & HWY 88 - SW of Substation",20.07,210,"2019-11-23",4.9180732253310063E-4,0,0.14652466436848241,0,0,0,0.81887769260654797,3.1434042317013758E-2,0,2.6717933854227692E-3,73.43820024407367,13.992950794831867,0.41399126474839321,0.64251861882193639,"Continue to Monitor"]
["LEBANON SOUTH","Marion - 1157 Bradfordsville - Bradfordsville",2218,"Bradfordsville - Bradfordsville Rd, Hwy 49, & Central Ave - SE of Substation",29.850000000000005,385,"2020-04-11",2.9575983675308906E-4,0,2.7385170069730468E-4,0,1.0062093917049537E-3,0,0.90551490379198529,1.4415553524706118E-2,0,7.8493721754153159E-2,136.69750011618547,208.64478183283418,1.1674047142515049,1.5692015780339676,"Continue to Monitor"]
["LEBANON SOUTH","Marion - 1157 Bradfordsville - Bradfordsville",2219,"Lebanon - Mulberry St, Old Calvary Pike, & Hwy 208 - NW & S of Substation",15.150000000000002,543,"2019-10-26",0,0,0,0,0.39706298018860653,0,7.9849423131279393E-2,0.52308759668011406,0,0,40.253143180287864,83.072665967084333,0.65935682913808613,2.0753580125782216,"Continue to Monitor"]
["RUSSELL SPRINGS","Russell - 1183 HWY 1870 - Russell Springs",2222,"Russell Springs - Old Columbia Rd, KY 80, Lakeway Dr, & Maple St - E of Substation",19.939999999999998,1012,"2019-01-26",2.4713767104160848E-2,0,6.1253839709578331E-2,0,1.615470538955599E-2,0,0.44695615749790557,4.0938285395141022E-2,0,0.40998324490365817,33.094473232242798,13.034716176599924,0.50425993470647623,0.59324952150396337,"Continue to Monitor"]
["RED HOUSE","Madison - 3858 Boonesboro Rd - Richmond",2224,"Richmond - Hwy 627, Simpson Ln, Hwy 25, & Hwy 2328 - W & NW of Substation",35.949999999999996,604,"2021-03-20",2.3269741849351816E-3,0,0.13632450372440641,0,0,0,0.24825632899547082,0.60747127153854796,0,5.6209215566396745E-3,33.320121547159502,47.919777995646015,0.21454283669573221,0.41060366570019946,"Continue to Monitor"]
["SPRINGFIELD","Washinton - 107 Commercial Ave - Springfield ",2225,"Springfield - State HWY 55 - N of Substation",11.71,276,"2020-06-20",0,0,2.3013642818197615E-2,0,0.47832547438301748,0,2.1353976309309113E-2,0.47558732422214367,0,1.7195822673321309E-3,18.939607607563161,64.118506094378532,0.19520254849984214,0.64825908147207789,"Continue to Monitor"]
["SPRINGFIELD","Washinton - 107 Commercial Ave - Springfield ",2226,"Springfield - State HWY 55 & Bloomfield Rd - S & N of Substation",37.970000000000006,391,"2020-06-27",1.2371659701181386E-2,0,0,1.0001000100010001E-4,3.0472061290636107E-2,0,0.93496110174397729,2.150919317283841E-2,0,5.8597409036678313E-4,63.14994065441779,129.39997760265055,0.46741539563883372,1.1297607185107625,"Continue to Monitor"]
["SPRINGFIELD","Washinton - 107 Commercial Ave - Springfield ",2227,"Springfield - Main St - SE of Substation",5.8500000000000005,622,"2020-06-20",2.5807305452620433E-2,0,0,0,0.65861566966649021,0,0.23067760719957647,7.0837744838538913E-2,0,1.4061672842773954E-2,5.870710684804,4.4177717376446317,0.12113241145954408,0.19529023946807955,"Continue to Monitor"]
["UNION UNDERWEAR","Russell - 101 Fruit Of The Loom Dr - Jamestown",2229,"Jamestown - N Main St & Progress Dr - N & S of Substation",15.91,551,"2023-10-14",3.2024865401253932E-3,0,2.4602969578428117E-5,0,0,0,0.97656567147654727,1.8620347475940345E-2,0,1.5868915378086134E-3,15.802422771883807,17.966040013366268,0.18621211517646538,0.19201671697315595,"Continue to Monitor"]
["WOODLAWN","Nelson – 285 Spencer Mattingly Ln. – Bardstown ",2231,"Bardstown - Poplar Flat Rd, Ashleigh Way, Ed Piler Rd, & Old US 150 - SE of Substation",51.069999999999993,1186,"2018-09-15",2.9481399048344461E-4,0,2.227036287611004E-3,0,0.44712750889556774,0,0.30361916874528977,0.24658423278432196,0,1.4723929672608895E-4,22.675949862358191,21.358891789143669,0.1663947883070544,0.17032516966714822,"Continue to Monitor"]
["UNION UNDERWEAR","Russell - 101 Fruit Of The Loom Dr - Jamestown",2233,"Jamestown - Fruit of the Loom Dr, N Main St, Airport Rd - N of Substation",1.36,1,"2023-11-30",0,0,0,0,1,0,0,0,0,0,35.673333200000002,178.36666600000001,0.2,1,"Continue to Monitor"]
["LEBANON WEST","Marion - 2255 Saint Mary's Rd - St Mary ",2235,"St Mary  - Warehouse Rd & Campbellsville Rd - E of Substation",7.03,222,"2019-11-16",0.11945377290421429,0,2.3783860824329018E-3,6.360178512573378E-3,1.6523993194430837E-2,0,0.85515005211070627,1.3361719564229787E-4,0,0,21.191488052211078,98.261627919562414,0.29284915242561921,1.319779601029601,"Continue to Monitor"]
["BEATTYVILLE 4KV","Lee - 950 W Main St. - Beattyville",2301,"Beattyville - W Main St, Lee Ave, & Grand Ave - E of Substation",8.1599999999999984,227,"2020-11-21",0,0,0,0,0.40154610269967156,0,0.52411279339902273,5.2251061443563243E-2,0,2.2090042457742529E-2,33.545291842284698,35.806182117546989,0.20120305233418412,0.21522604054595701,"Continue to Monitor"]
["ESTILL STONE CO","Estill - 598 Tipton Ridge Rd - Ravenna",2302,"Ravenna - Tipton Ridge Rd - S of Substation",0.4,2,"2021-01-23",0,0,0,0,0,0,1,0,0,0,13.040000000000001,65.2,0.2,1,"Continue to Monitor"]
["IRVINE","Estill - 83 River Dr - Irvine",2305,"Irvine - Kirkland Ave - SE of Substation",3.7199999999999993,80,"2021-01-23",0,0,0,0,0.80231465162730586,0,5.9628715779579372E-2,0,0,0.13805663259311479,35.781097904087403,31.502546275617284,0.25833401744803447,0.28549382716049382,"Continue to Monitor"]
["OKONITE","Madison - 1742 Berea Rd - Richmond ",2306,"Richmond - Berea Rd - N of Substation",2.42,23,"2019-09-28",0.13381995133819952,0,0,0,0,0,0.81021897810218979,5.5961070559610707E-2,0,0,30.79649720961698,35.760869521739124,0.61966196040815014,1.2173913043478259,"Continue to Monitor"]
["RICHMOND EAST","Madison - 1799 Irvine Rd - Richmond",2319,"Richmond - Irvine Rd, Reba Rd, & Charlie Norris Rd - E of Substation",38.28,1442,"2023-09-09",2.3106658233801934E-3,0,2.519356392804057E-2,0,3.5922633793715991E-2,0,0.29104799654770086,0.4423326765136345,0,0.20319246339352784,31.169426371636185,68.029723716191782,0.28157060708947079,0.57431335733328681,"Trees Trimmed in 2023"]
["RICHMOND EAST","Madison - 1799 Irvine Rd - Richmond",2320,"Richmond - DR Martin BYP, Commercial Dr, & Berea Rd - SE of Substation",20.439999999999998,1494,"2023-12-09",8.2718367195196759E-3,0,1.3569529899436772E-3,0,5.8646392921538379E-2,0,0,0.72089521720542038,0,0.21082960016357791,13.731687153105474,27.735067030818666,0.18071606064983764,0.46809284973796517,"Trees Trimmed in 2023"]
["RICHMOND SOUTH","Madison - 464 Eastern Bypass - Richmond",2321,"Richmond - Lake Shore Dr, Willis Branch Rd, & Barnes Mill Rd - W of Substation",25.92,1831,"2024-02-10",2.2221189264444622E-4,0,0.32171860491745846,2.0588612093995632E-3,0.28711930624540127,0,0.38380075302621985,2.7606426458634007E-3,0,2.3196200630129439E-3,9.662897069379806,35.775351632988453,7.1632143811307281E-2,0.19505871215245141,"Continue to Monitor"]
["RICHMOND SOUTH","Madison - 464 Eastern Bypass - Richmond",2323,"Richmond - S Killarney Dr, Barnes Mill Rd, & Martin Dr - NW of Substation",5.36,660,"2019-12-07",2.0604680671920119E-4,0,9.9557666423561078E-2,0,1.0672928117829127E-3,0,1.9356541022585102E-2,0.87909203028739824,0,7.2042264795346602E-4,17.067371487375969,32.91497870662937,0.22836165017621807,0.36973119597574389,"Tree Trim Scheduled for 2024"]
["RICHMOND 1","Madison - 315 Clay Dr - Richmond",2326,"Richmond - Third St, New Richmond Byp, & Red House Rd - N of Substation",25.24,984,"2019-08-03",4.9654347248072319E-3,0,4.4801914384472216E-2,0,3.6812018080297791E-2,0,0.69679163343082517,0.17476734910927944,0,4.1861650270318178E-2,47.834873464929565,40.284170517019952,0.3554827976430549,0.38503071359652313,"Continue to Monitor"]
["RICHMOND 1","Madison - 315 Clay Dr - Richmond",2327,"Richmond - Moberly Ave, 5th, 4th, 3rd, 2nd, 1st St, & Irvine St - SE of Substation",5.6100000000000012,921,"2023-12-23",1.9657375145180024E-3,0,0,0,0,0,0.97675667828106849,8.3594657375145182E-3,0,1.2918118466898955E-2,7.1515508314581338,23.246006774181531,0.17841406293625178,0.65974318572468227,"Continue to Monitor"]
["RICHMOND 1","Madison - 315 Clay Dr - Richmond",2328,"Richmond - Georgia St, N 2nd St, & Golfview Dr - E of Substation",7.24,723,"2024-02-03",4.2214905991534079E-3,0,0,0.15961364183864271,0.11145652897112637,0,0.10940887660170007,0.32097094283780531,0,0.29432851915157215,20.897481237462134,48.187244954164086,0.18534064810834702,0.29715384757017926,"Trees Trimmed in 2024"]
["RICHMOND 1","Madison - 315 Clay Dr - Richmond",2329,"Richmond - Sunset Ave, Barnes Mill Rd, & Kirksville Rd - SW of Substation",41.47,1477,"2019-07-13",8.9408278321967741E-4,0,0.28890089424074838,7.4919714209439686E-2,2.2724867348760211E-2,0,0.10768010792179461,0.49320670846424697,0,1.1673625031790487E-2,75.826839886632129,89.72354723514826,0.8910623745157249,1.0832739325836536,"Tree Trim Scheduled for 2024"]
["ELIZABETHTOWN 3","Hardin - 100 Crucible Steel Rd - Elizabethtown",2331,"Elizabethtown - Mulberry St - NE of Substation",2.3699999999999997,67,"2021-01-23",0,0,0,0,1,0,0,0,0,0,20.764946246395375,44.278431367647059,0.11466967649545808,0.20588235294117646,"Continue to Monitor"]
["ELIZABETHTOWN 3","Hardin - 100 Crucible Steel Rd - Elizabethtown",2332,"Elizabethtown - Leitchfield Rd, Blackbranch Rd, & Nicholas St - SW of Substation",19.07,926,"2021-01-23",4.4435042344874638E-4,0,0,0,0.18344384736613562,0,0.56377238326691703,0.25233941894349871,0,0,26.021100014940231,91.227937660501055,0.18866278937423964,0.51919302021370062,"Continue to Monitor"]
["NEW HAVEN","Nelson - 256 Lyons Station Rd - New Haven",2333,"New Haven - Center St, First St, & Depot St - SE of substation",1.4900000000000002,153,"2022-07-08",0.67440780306548997,0,0,0,0,0,0,0.32559219693450997,0,0,10.094536941727176,13.980303025974026,0.1631926428751595,0.20779220779220778,"Continue to Monitor"]
["RINEYVILLE","Hardin - Rineyville Big Springs Rd - Radcliff",2334,"Radcliff - Rineyville Big Springs Rd & Rineyville Rd - SW of Substation",27.05,758,"2019-06-22",2.5900554941858564E-4,0,4.8206080175698904E-5,8.4891724241612145E-3,1.3076103510709921E-2,0,0.97249557157704147,2.1243357365562228E-5,0,5.6106975011275323E-3,71.804450745263338,38.088345981116561,0.77357578009966799,0.93792726407773641,"Continue to Monitor"]
["BOSTON","Nelson - 1100 Old Nelsonville Rd. - Boston",2403,"Boston - Lebanon Junction Rd, Boston Rd, KY 52 & Nelsonville Rd - SE of Substation",30.18,353,"2021-07-03",1.0347977505637863E-4,0,1.0868944649025148E-3,0,1.4287345493991035E-3,0,0.99456124575376093,2.5805714938197596E-3,0,2.3907396306128856E-4,260.22086878930787,582.37437804348588,1.6118582401167347,2.4125975201711003,"Continue to Monitor"]
["CLARKSON","Grayson - 405 Peonia Rd - Clarkson",2404,"Clarkson - City of Clarkson - N/S/E/W of Substation",13.380000000000003,607,"2021-09-11",9.9168201412640916E-5,0,1.0523972394810871E-3,0,2.8738540001214307E-4,0,0.2822853210823501,0.57409483718200405,0,0.14218089089474004,44.856867391108587,126.77298714215138,0.60585167761333691,2.1397082132559708,"Continue to Monitor"]
["EASTVIEW","Hardin - 12540 Sonora - Hardin Springs",2407,"Sonora - KY 84, Main St, & White Mills Rd - SE of Substation",14.9,266,"2019-09-21",1.8945122824892936E-3,0,0.16850015124257717,0,4.457675958798338E-3,0,0.48722398229665831,0.33792367821947689,0,0,61.166079131451752,84.483875251666902,0.39388608759669502,0.28950205702936582,"Continue to Monitor"]
["ELIZABETHTOWN 2","Hardin - 1011 Woodland Dr - Elizabethtown",2411,"Elizabethtown - Dixie Ave, Miles St, & Helm St - SE of Substation",15.000000000000002,629,"2024-02-16",1.136316082574448E-3,0,1.4749575893360116E-2,0,0,0,0.29802384010455396,0.27466658941004918,0,0.41142367850946232,34.695080808578737,92.836100203558502,0.39392088800068004,1.0636130084758437,"Trees Trimmed in 2024"]
["ELIZABETHTOWN 2","Hardin - 1011 Woodland Dr - Elizabethtown",2415,"Elizabethtown - Woodland Dr, Saint John Rd, & Westport Rd - S of Substation",7.99,1352,"2021-04-03",5.8217209902896683E-4,0,6.2266291489091741E-3,0,0.12443742023122681,0,0.59593337861338547,0.22502444376441436,0,4.7795956143035209E-2,31.256888298104609,53.247049602170776,0.48925064292670839,0.69605414598157134,"Continue to Monitor"]
["ELIZABETHTOWN 4","Hardin - 201 Sportsman Lake Rd - Elizabethtown",2419,"Elizabethtown - Sportsman Lake Rd & Hodenville Rd - SE of Substation",23.930000000000003,773,"2020-05-16",0,0,0,0,5.8296290898491589E-4,0,0.49828377729811768,0.49183726288863144,0,9.295996904265932E-3,15.36322105020442,14.857352644189653,0.16163975355749552,0.2233464520905892,"Continue to Monitor"]
["ELIZABETHTOWN WEST","Hardin - 300 College Street Rd - Elizabethtown",2426,"Elizabethtown - College Street Rd & Peters Dr - NE of Substation",6.61,370,"2021-02-06",1.7780887188701928E-2,0,1.8724852094875965E-2,0,1.2551621279896545E-3,0,0.9592055019668817,3.0335966215507531E-3,0,0,37.370544553652493,55.181311763699284,0.62718451794745878,1.261455525606469,"Continue to Monitor"]
["HODGENVILLE 12KV","Larue - 500 W High Ave - Hodgenville",2430,"Hodgenville - S Lincoln Blvd/Hwy 61, Greensburg Rd, & L & N Tpke - SE of Substation",35.819999999999993,1539,"2022-03-18",1.6280419034398993E-3,0,2.4691742940181321E-2,6.2424087971196807E-3,0.36044657962087362,7.6318700386066886E-4,0.29435973625992279,5.064416778727281E-3,0,0.30680388669587472,58.746666081684495,131.67227773249039,0.58909520691905959,1.6767501751111256,"Continue to Monitor"]
["HORSE CAVE","Hart - 501 Shewey Ave - Horse Cave",2433,"Horse Cave - W Main St, KY 335, New St, US 31 - N & NW of Substation",23.31,883,"2023-04-05",5.9744810845386534E-4,0,0.55553521689654439,0,3.5429435531027127E-2,0,0.24141022159985925,0.16594464427176922,0,1.0830335923461558E-3,63.510083298880204,135.87522774142909,0.61076441009230098,1.7284255860199749,"Continue to Monitor"]
["HORSE CAVE","Hart - 501 Shewey Ave - Horse Cave",2435,"Horse Cave - E Main St, KY 218, & US HWY 31 E - E of Substation",18.43,394,"2023-07-14",1.7870841509770063E-3,0,0.10317394189965322,0,0.10707851965074285,0,0.16533688834746432,0.45913984364450244,0,0.1634837223066602,67.99765608613383,240.2688480192497,0.46867625255196826,1.2512544572202806,"Trees Trimmed in 2023"]
["HORSE CAVE","Hart - 501 Shewey Ave - Horse Cave",2436,"Hiseville - Old Glasgow Rd & Hiseville Main St - SE of Substation",28.060000000000002,347,"2023-09-09",3.7477607129739981E-3,0,0,0,2.5559728062482669E-2,0,0.67224333460757202,0.29844917661697135,0,0,161.43059428506251,258.80817999502614,1.0006910175212169,1.925196933762692,"Trees Trimmed in 2023"]
["MILLWOOD","Grayson - 6649 Beaver Dam Rd - Millwood",2440,"Caneyville - US 62, Hwy 79, & River Park Dr - W of Substation",22.25,425,"2021-10-16",0,0,0.33702477236442746,0,4.7804786048878056E-2,0,0.56153046544676222,8.3554097440305972E-4,0,5.2804435165529219E-2,127.6132863486029,486.13158765844486,0.87500379177610144,2.8968960935423862,"Continue to Monitor"]
["MILLWOOD","Grayson - 6649 Beaver Dam Rd - Millwood",2441,"Millwood - US HWY 62, School House Rd, & Rock Quarry Rd - NE of Substation",11.760000000000002,171,"2021-10-02",0,0,6.5594691168963756E-2,0,3.318019397651863E-4,0,0.88300153139356818,5.1071975497702912E-2,0,0,9.0931043183744578,16.86191859883721,8.1860463729006933E-2,0.16860465116279069,"Continue to Monitor"]
["MUNFORDVILLE","Hart - 75 Gorin Mill Rd - Munfordville",2442,"Munfordville - Mill St, KY 88, US 31 W, & HWY 571 - SE of Substation",25.11,499,"2023-10-27",2.9989757682130527E-3,0,5.1744880017441739E-3,0,0.17019187484609075,0,0.79969602431805453,1.9305122256886114E-2,0,2.6335148090113575E-3,69.147714290768135,94.223704086408873,0.4374223386643023,0.55681898669763363,"Continue to Monitor"]
["MUNFORDVILLE","Hart - 75 Gorin Mill Rd - Munfordville",2443,"Munfordville - City of Munfordville & US 31 - E & N of Substation",16.259999999999998,978,"2024-02-09",0.64664365122364043,0,1.6085610728220378E-3,1.0359749294067083E-4,1.4853640541898886E-3,0,0.30730096331668771,4.1333299734146428E-2,0,1.5245631055728452E-3,63.388641802854025,74.093985811607226,0.64997627914948075,0.41014451906550647,"Continue to Monitor"]
["NEW HAVEN","Nelson - 256 Lyons Station Rd - New Haven",2444,"New Haven - 3rd St, Center St, New Hope Rd, & Rogers Rd - ESE of Substation",25.05,587,"2022-06-10",0,0,1.2179333493167107E-2,1.9659554063773677E-4,5.9985614960441141E-3,0,0.93429872932150559,1.8873171901222726E-2,0,2.8453608247422681E-2,109.2053397788147,187.56194623396919,0.97318460655381467,1.1719200783858383,"Continue to Monitor"]
["NEW HAVEN","Nelson - 256 Lyons Station Rd - New Haven",2445,"New Haven - KY 52, Clark Rd, & Lyons Station Rd - NW of Substation",13.719999999999999,204,"2022-06-24",1.5672038895813743E-4,0,7.8967637847123513E-5,0,1.2266711374498555E-2,0,0.98731901224848806,0,0,1.785883502081101E-4,137.24805009208629,83.684478027059498,1.107007238118437,1.3301932134961068,"Continue to Monitor"]
["NEW HAVEN","Nelson - 256 Lyons Station Rd - New Haven",2446,"New Haven - Cissal Hill Rd & US 31 - SSW of Substation",7.97,48,"2022-07-08",6.5001870557426116E-4,0,0,0,0,0,0.22557519640852974,0.77377478488589602,0,0,57.342657521023931,79.082143295845995,0.44769182992345868,0.51929548415110727,"Continue to Monitor"]
["RADCLIFF","Hardin - 677 N Wilson Rd - Radcliff",2447,"Radcliff - N Dixie Blvd, E Lincoln Trail, & New St - SE/E/NE of Substation",10.3,760,"2019-03-23",9.5917471466198424E-3,0,3.7862159789288849E-2,0,3.2462686567164181E-2,3.0728709394205444E-4,0.69047410008779631,0.15245829675153644,0,7.6843722563652322E-2,13.186095233905665,18.904733938186411,0.19837684223085281,0.24924230660452865,"Continue to Monitor"]
["RIO","Hart - 301 Glen Lily Rd E - Munfordville",2450,"Munfordville - E US 31, Eve Rd, & Pikeview Rd - N of Substation",14.120000000000001,171,"2020-03-14",5.2797756619824682E-4,0,0,0,4.1638548656104786E-2,0,0.84950191785228513,1.7521162809400099E-2,0,9.0810393116011703E-2,426.90580785461646,377.92104851190066,1.8343650325832936,2.4770242183515205,"Continue to Monitor"]
["ROGERSVILLE","Hardin - 180 Rogersville Rd - Radcliff",2454,"Radcliff - Parkside Mobile Home Park, 1st, 2nd, & 3rd St - S of Substation",3.0700000000000003,303,"2020-08-01",0,0,0,0,0,0,0.5197245302792125,0.4802754697207875,0,0,17.818408236467512,25.608694573994491,0.38801366455545239,0.24693719074248943,"Tree Trim Scheduled for 2024"]
["SONORA","Hardin - 1340 Old Sonora Rd - Sonora",2456,"Sonora - US 31 W, S Dixie Hwy, & Sonora Rd - E of Substation",12.730000000000002,199,"2022-08-12",2.0037997981357239E-3,0,6.6540996259573715E-2,0,7.7183399631894551E-4,0,0.9275663480377605,7.4214807338360148E-4,0,2.3748738348275248E-3,27.64352719873856,24.025744806970174,0.28922417886270124,0.29880747018675469,"Continue to Monitor"]
["LEITCHFIELD EAST","Grayson - 705 Wallace Ave - Leitchfield",2466,"Leitchfield - Wallace Ave, Bobby Bland Way, Clinton St, & White Oak St - S & W of Substation",4.3899999999999997,226,"2021-08-28",0,0,0,0,0.10013351134846461,0,0.8998664886515354,0,0,0,7.5591104454833893,13.238515346258973,4.4001617419701031E-2,0.1633673367726621,"Continue to Monitor"]
["HODGENVILLE 12KV","Larue - 500 W High Ave - Hodgenville",2467,"Hodgenville - Hwy 61, Glendale Rd, & Railroad Dr - NW of Substation",7.54,42,"2023-03-04",0,0,1,0,0,0,0,0,0,0,189.82637848210004,338.355038744186,0.66359530670584332,1.6046511627906976,"Continue to Monitor"]
["HORSE CAVE INDUSTRIAL","Hart - 400 Cherry St - Horse Cave",2469,"Horse Cave - Hatcher Valley Rd, N Toohey Ridge Rd, & Park Ridge Rd - W of Substation",20.47,110,"2023-02-10",0,0,0,0,1.9178390704286811E-3,0,0.4082885837550233,0,0,0.58979357717454794,81.039670920077668,51.741239244318919,0.34272602705195709,0.36480997409896498,"Continue to Monitor"]
["HORSE CAVE INDUSTRIAL","Hart - 400 Cherry St - Horse Cave",2473,"Horse Cave - Old Dixie Hwy - W of Substation",0.38,3,"2023-01-28",0,0,0,0,0,0,0,0,0,1,42.432777716666671,78.258333250000007,0.25,0.25,"Continue to Monitor"]
["HORSE CAVE INDUSTRIAL","Hart - 400 Cherry St - Horse Cave",2474,"Horse Cave - Butler Rd & Top Quality Dr - S of Substation",2.56,29,"2023-01-28",0,0,0.11661706349206349,0,0.88338293650793653,0,0,0,0,0,66.895637641105623,81.045976999999993,0.60931399379675233,1,"Continue to Monitor"]
["HORSE CAVE INDUSTRIAL","Hart - 400 Cherry St - Horse Cave",2476,"Horse Cave - S Dixie St and Bluegrass Ave - SW of Substation",1.24,11,"2023-01-28",0,0,0.23248407643312102,0,0,0,0.76751592356687903,0,0,0,34.028671328671344,28.109090909090909,0.27505827505827513,0.36363636363636365,"Continue to Monitor"]
["BLACK BRANCH ROAD","Hardin - 1220 N Black Branch Rd - Elizabethtown",2479,"Elizabethtown - N BlackBranch Rd - E of Substation",5.8800000000000008,33,"2021-03-13",7.7949783928669112E-4,0,0,0,1.6820742847765439E-3,0,0.99753842787593683,0,0,0,54.493363566354255,78.960407120085478,0.48074474057232663,0.35178062678062683,"Continue to Monitor"]
["EMINENCE","Henry - 1257 Ballardsville Rd - Eminence",2501,"Eminence - City of Eminence, Hwy 22, & Castle Hwy - E of Substation",20.38,1022,"2021-11-20",1.0910903034594906E-2,0,3.5276837936370549E-2,0,0,0,0,5.7177328402444466E-3,0,0.94809452618879009,17.527823028359748,35.988592634196273,0.17832395497180847,0.38843488224840411,"Continue to Monitor"]
["FAIRFIELD","Nelson - 5729 High Grove Rd - Coxs Creek",2503,"Bloomfield - KY 48, US 62, & Lawrenceburg Rd - E of Substation",55.54,1258,"2020-11-14",1.4580720799602276E-3,0,4.3740307345269985E-2,0,0.27502096210496635,0,0.16217805545868055,0.47065861820772142,0,4.6943984803401423E-2,68.066506975732395,148.51560011892335,0.44435867318780248,1.1257590998680622,"Continue to Monitor"]
["LA GRANGE E 12KV","Oldham - 1810 E Highway 146 - La Grange",2508,"La Grange - Fort Pickens Rd, Hwy 146, & Covey Trace Rd - N & NE of Substation",20.740000000000002,381,"2021-02-06",3.8537812638745006E-2,0,6.7367174781707857E-3,0,1.6575403285481725E-3,0,0.65778303981056674,0.17790735533520793,0,0.11737753440876128,145.92734045549363,383.60344571804183,0.98153834380598182,2.1870649595723117,"Continue to Monitor"]
["LA GRANGE E 12KV","Oldham - 1810 E Highway 146 - La Grange",2511,"La Grange - Waterworks Rd, Hwy 53/1st St, & Fendley Mill Rd - W of Substation",18.14,1286,"2021-04-10",4.3259190506182252E-2,5.8010408724765471E-3,0.62694334869227963,0,2.45301156893294E-3,0,0.21271588159246857,0.10882752676766003,0,0,14.616708466816458,19.785632202177549,0.11955546322817474,0.11120477710415466,"Continue to Monitor"]
["LAGRANGE PENAL","Oldham - 3011 W Highway 146 - La Grange",2512,"La Grange - W Highway 146 - W of Substation",0.01,1,"2021-03-27",0,0,0.10044642857142858,0.15848214285714285,0.7410714285714286,0,0,0,0,0,61.329999799999996,115.983333,0.8,2,"Continue to Monitor"]
["LAGRANGE PENAL","Oldham - 3011 W Highway 146 - La Grange",2513,"La Grange - HWY 146, Jefferson St, & Allen Ln - NE of Substation",24.189999999999998,1516,"2021-03-27",3.3157464966086458E-3,0,7.1497502192626725E-2,0,0.11738457435547772,0,0.75836016265303707,3.018264099483392E-2,0,1.9259373307415891E-2,42.122669376189876,69.352341826236966,0.33323553650281995,0.55902440282917509,"Continue to Monitor"]
["LAGRANGE PENAL","Oldham - 3011 W Highway 146 - La Grange",2514,"La Grange - Dawkins Rd & Fendley Mill Rd - N of Substation",8.74,172,"2020-12-19",5.815628375945265E-2,0,7.9732325051014283E-2,0,0,0,0.85124834953787065,8.8824870963869883E-3,0,1.9805545552754773E-3,130.42106594320924,189.77309656055354,0.95812048044583042,1.4367945056439548,"Continue to Monitor"]
["LAWRENCEBURG 12KV","Anderson - 108 E Broadway st - Lawrenceburg ",2517,"Lawrenceburg - Industry Rd & Tyron Rd - NE of Substation",11.620000000000001,183,"2022-06-03",0,0,7.1452986831407639E-5,0,1.6492121825411386E-3,0,0.98568429753023723,9.9203781987281369E-3,0,2.6746591016621512E-3,58.732808791586834,18.443017921323417,0.74417409222616304,1.2644340098010804,"Continue to Monitor"]
["SIMPSONVILLE","Shelby - 6801 Shelbyville Rd - Simpsonville",2527,"Simpsonville - Main St, 3rd St, & Grand Central Dr - NW of Substation",7.0400000000000009,315,"2023-12-23",0,0,5.3416149068322982E-2,0,0,0,0.76645962732919259,0,0,0.18012422360248448,4.3572876935682334,2.5480485221518987,4.2899595474654946E-2,4.7468354430379743E-2,"Continue to Monitor"]
["SHELBYVILLE SOUTH","Shelby - 614 Mack Walters Rd - Shelbyville",2537,"Shelby - Old Finchville Rd, Hwy 55, & Gordon Ln - SW of Substation",12.940000000000001,505,"2023-01-06",0,0,0,0,1.9360372503369683E-2,0,0.33363558387452519,0.42779071192255852,0,0.21921333169954663,29.542933348963679,34.75951020102751,0.30472014151712867,0.13025547473708007,"Trees Trimmed in 2023"]
["MID VALLEY CLARKSON","Grayson - 1960 Peonia Rd - Clarkson",2538,"Clarkson - No Road - W of Substation",0.01,1,"No Trimming Necessary",0,0,0,0.19450800915331809,0,0,0.80549199084668188,0,0,0,304.97999960000004,436.66666600000002,1.4,2,"Continue to Monitor"]
["SIMPSONVILLE","Shelby - 6801 Shelbyville Rd - Simpsonville",2540,"Simpsonville - Buck Creek Rd, Kingbrook Pky, & Rolling Ridge Way - S of Substation",5.15,332,"2023-11-11",0,0,2.5594014431456072E-3,0,2.2808178008085788E-3,0,0.99499372843721434,1.6605231883143082E-4,0,0,10.098814312270759,14.71005794851478,0.12470396012217096,0.11427692752993958,"Continue to Monitor"]
["SIMPSONVILLE","Shelby - 6801 Shelbyville - Simpsonville",2541,"Simpsonville - Shelbyville Rd, Champions Way, & Conner Station Rd - SW of Substation",60.22,1180,"2019-05-18",1.9388065947894217E-3,0,8.2562982744336603E-4,0,0,0,6.877211762662741E-2,2.4603768857812309E-2,0,0.90385967709332748,66.801195600772957,192.98354616507615,0.35090239463917461,0.68287755430560027,"Continue to Monitor"]
["SHELBYVILLE EAST","Shelby - 183 Boone Station Rd - Shelbyville ",2542,"Shelbyville - KY 60 - E of Substation",46.8,1155,"2022-10-21",2.8906347205447466E-4,0,0.23995535854553315,0,0.34335210570171415,0,0.32996972374329658,2.1953742303685058E-2,0,6.4480006233716608E-2,100.04950219163972,296.11053304456283,0.89180820491011836,2.6679917669422162,"Continue to Monitor"]
["Frankfort to Adams","Scott - 900 W Main St - Georgetown",3401,"Georgetown - Frankfort Rd - W of Substation",12.38,1799,"2019-04-20",0,0,0,0,0,0,0,0,0,1,74.373724074302089,42.594774874930529,1.0624571714217939,1.3418565869927737,"Continue to Monitor"]
["GREEN RIVER","Muhlenberg - 811 Power Plant Dr - South Carrollton",3412,"Muhlenberg - HWY 431 & 138 - N of Substation",7.7299999999999995,642,"2021-09-24",0,0,0,0,1,0,0,0,0,0,509.06110917402594,1525.55,1.9009740259740262,1,"Continue to Monitor"]
["Salem - Three Rivers Rock","Livingston - 271 W Main St - Salem",3425,"Salem - Phillips Ln & Three Rivers Rock Rd - SW of Substation",9.86,2,"2021-09-21",0,0,8.7991145545102373E-2,0,0,0,0,0,0,0.91200885445489766,439.50888860000003,1249.5666660000002,1.9333333333333331,3,"Continue to Monitor"]
["West Cliff - High Bridge","Garrard - 815 Dix Dam Rd - Burgin",3427,"Burgin - Dix Dr, High Bridge Rd, & Blake Ln - N of Substation",4.03,138,"2021-07-10",0.21906005221932115,0,0,0,0.3926892950391645,0,0,3.2375979112271538E-2,0,0.3558746736292428,849.6713293454701,3830.0833320000002,1.4044439673679689,4,"Continue to Monitor"]
["SHAWNEE GAS 4KV","Harlan - Ball Park Rd - Harlan",4400,"Harlan - Memorial Hospital Rd & Hwy 115 - E of Substation",1.2000000000000002,36,"2020-02-15",0,0,0,0,0,0,0.91066997518610426,8.9330024813895778E-2,0,0,5.3293299489864872,21.791441432432435,3.412162162162162E-2,0.10810810810810811,"Continue to Monitor"]
["SHAWNEE GAS 12KV","Harlan - Ball Park Rd - Harlan",4402,"Harlan - Hwy 421 & Hwy 990 - E of Substation",16.990000000000002,478,"2020-03-21",2.8822428569725722E-2,0,1.263514238375073E-3,0,1.4232415100187143E-2,0,0.28381390580858951,0.54757846304220847,0,0.12428927324091402,68.008643944109707,76.810886790816809,0.54086543421573863,0.35557428743634317,"Tree Trim Scheduled for 2024"]
["HARLAN WYE 4KV","Harlan - Sunshine Pike Rd just W of US HWY 421 - Harlan",4411,"Harlan - US HWY 421 - E of Substation",4.82,380,"2023-11-18",1.8659720577788301E-2,0,0,0,2.6521430262846316E-3,0,0.88998342410608577,5.5789722945773147E-2,0,3.2914989344068196E-2,34.384738364476462,62.415859712421167,0.36481923750459477,0.45831424626007483,"Continue to Monitor"]
["HARLAN WYE 12KV","Harlan - Sunshine Pike Rd just W of US HWY 421 - Harlan",4412,"Harlan - US HWY 421 - E of Substation",19.63,883,"2023-11-25",2.9877269373460671E-3,0,0,2.0264582705477674E-4,2.9305704220229248E-3,0,0.95280950253047481,3.996799235141904E-2,0,1.101561931682376E-3,40.81648983319112,72.57871849608982,0.43913203491310543,0.67338748800247716,"Continue to Monitor"]
["EVARTS","Harlan - 1600 Block of Hwy 215 - Evarts",4475,"Evarts - Hwy 215 & City of Evarts - W of Substation",10.99,594,"2023-04-14",1.5461712399926664E-2,0,0,0,0.47744301167267617,0,0.38833954653792091,0.11875572938947626,0,0,63.689782068413294,74.738947866939412,0.62019642702492173,0.30685968352801113,"Continue to Monitor"]
["EVARTS","Harlan - 1600 Block of Hwy 215 - Evarts",4476,"Evarts - Hwy 215 - E of Substation",14.729999999999999,450,"2023-04-07",1.2921566093810569E-3,0,0,1.5687738390930017E-2,1.0815829397041439E-3,0,0.92892660071882194,4.2124305465822458E-2,0,1.0887615875340387E-2,150.77423150921908,460.83919015962368,0.89928010148288851,1.4964045811013218,"Continue to Monitor"]
["SOMERSET 3","Pulaski - 125 Young St. - Somerset",4501,"Somerset - E Mt. Vernon St & Eller St - E & SW of Substation",8.83,728,"2020-10-10",7.8129684996873106E-3,0,0,0.14610765105500775,3.3839063129128153E-3,0,0.46583111309100567,0.26321651003606644,0,0.11364785100532002,36.654656515669146,115.10043834850136,0.62980851182864295,1.4261186639202528,"Continue to Monitor"]
["SOMERSET 2","Pulaski - 105 Tandy Ave - Somerset ",4508,"Somerset - Clifty Rd, W Columbia St, & Ogden St - S & W of Substation",6.65,547,"2020-07-25",0,0,0,0,0,0,0.98766196093598912,1.0645909882034423E-2,0,1.6921291819764069E-3,32.68770061393996,112.70947840668823,0.21192855565884816,0.47384264363095374,"Continue to Monitor"]
["MCKEE ROAD","Pulaski - 140 McKee Rd - Somerset",4511,"Somerset - Hwy 2227, Hwy 27, & Hwy 80 - N & SW of Substation",23.699999999999996,941,"2020-06-20",1.5255134001746225E-4,0,1.4411232971862393E-3,0,0.42191481143680643,0,0.46269470581934674,0.11043743285306709,0,3.3593752535760308E-3,67.280699596745393,161.93126861486431,0.67641979844305489,0.81119274763457261,"Continue to Monitor"]

{"sheet":"KU Section 6-7","index":2,"n_rows":30,"n_cols":1,"rows_kept":30,"cut":false,"hidden":false,"merged":[[0,0,0,8],[2,0,2,8],[4,0,4,8],[5,0,10,8],[11,0,14,8],[29,0,32,8],[28,0,28,8],[20,0,21,8],[15,0,15,5],[16,0,16,6],[17,0,17,6],[18,0,18,6],[19,0,19,6],[25,0,26,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
[]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 6: VEGETATION MANAGEMENT PLAN REVIEW"]
["The Companies’ Vegetation Management Plan was submitted December 19, 2007.  The Distribution Vegetation Management Program encompasses right of way maintenance for Louisville Gas and Electric Company and Kentucky Utilities Company (referred to as the “Companies”).  The program is centralized and managed by a Forestry Manager and eight company Utility Arborists.  All are certified arborists by the International Society of Arboriculture."]
[]
[]
[]
[]
[]
["The Companies’ plan is to maintain a proactive trim cycle while balancing the reactive needs of worst performing circuits. The Companies’ goal is to maintain an average trim cycle of five years or less.   The effectiveness of the plan is evaluated by the cycle and system performance as measured by system SAIDI, SAIFI, and CAIDI.  "]
[]
[]
[]
["Effectiveness of the program"]
["KU/LG&E Tree Cycle – 4.91 years"]
["KU (Kentucky) Tree SAIDI – 27.02 minutes"]
["KU (Kentucky) Tree SAIFI – 0.169"]
["KU (Kentucky) Tree CAIDI – 159.4 minutes"]
["The hazard tree program, mid cycle, herbicide, and worst performing circuits were completed as planned.  "]
[]
["Adjustments made to the tree plan in 2023 included"]
["No changes made to plan."]
["Changes to be implemented in 2024"]
["The routine trimming cycle plan is a proactive plan to trim work areas based on clearance thresholds and risk mitigation. Danger trees are prioritized and mitigated based on reliability disruption potential."]
[]
[]
["SECTION 7: UTILITY COMMENTS"]
["SAIDI and SAIFI improved in 2023 compared to the previous 5 year average excluding major events.  406 Circuits were above their previous 5 year average SAIDI and/or SAIFI in 2023.  "]