{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["LGE Section 1-4","Excel LGE Section 5","LGE Section 6-7"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"LGE Section 1-4","index":0,"n_rows":45,"n_cols":8,"rows_kept":45,"cut":false,"hidden":false,"merged":[[43,0,43,8],[44,3,44,5],[35,6,35,8],[36,6,36,8],[35,1,35,3],[36,1,36,3],[41,1,41,8],[38,1,38,8],[39,1,39,8],[40,1,40,8],[37,0,37,8],[24,0,24,8],[6,0,6,3],[7,0,7,3],[16,0,16,3],[16,5,16,8],[17,0,17,3],[18,0,18,3],[17,5,17,8],[18,5,18,8],[6,5,6,8],[7,5,7,8],[15,0,15,3],[15,5,15,8],[14,0,14,8],[11,5,11,8],[0,0,0,8],[10,0,10,8],[11,0,11,3],[28,3,28,5],[29,6,29,8],[29,1,29,3],[1,0,1,8],[20,0,21,8],[25,2,25,6],[26,0,26,1],[26,5,26,6],[3,0,3,8],[4,0,4,3],[5,0,5,3],[4,5,4,8],[5,5,5,8],[34,6,34,8],[30,1,30,3],[31,1,31,3],[30,6,30,8],[31,6,31,8],[34,1,34,3],[33,0,33,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 1: CONTACT INFORMATION"]
["UTILITY NAME",null,null,null,null,"LOUISVILLE GAS AND ELECTRIC"]
["REPORT PREPARD BY",null,null,null,null,"Karmen Powell (Mgr Investment Strategy & Reliability)"]
["E-MAIL ADDRESS OF PREPARER",null,null,null,null,"Karmen.Powell@lge-ku.com"]
["PHONE NUMBER OF PREPARER",null,null,null,null,"(502) 399-4805"]
[]
[]
["SECTION 2: REPORTING YEAR"]
["CALENDAR YEAR OF REPORT",null,null,null,null,2024]
[]
[]
["SECTION 3: MAJOR EVENT DAYS (MED)"]
["TMED",null,null,null,null,3.3119999999999998]
["FIRST DATE USED TO DETERMINE TMED",null,null,null,null,"2019-01-01"]
["LAST DATE USED TO DETERMINE TMED",null,null,null,null,"2023-12-31"]
["NUMBER OF MED IN REPORTING YEAR",null,null,null,null,8]
[]
["NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years.  If five years of data are not available, then utilities should use what is available until five years are accumulated.        \n"]
[]
[]
[]
["SECTION 4: SYSTEM RELIABILITY INFORMATION AND RESULTS"]
[null,null,"System-wide Information"]
["TOTAL CUSTOMERS",null,449149,null,null,"TOTAL CIRCUITS",null,630]
[]
[null,null,null,"Excluding MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",74.498118035915908,null,null,null,"SAIDI",82.429660907405534]
["SAIFI",0.79636949091418596,null,null,null,"SAIFI",0.82164918399509945]
[]
["Including MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",393.22426539685836,null,null,null,"SAIDI",433.30756120757468]
["SAIFI",1.1226088858237682,null,null,null,"SAIFI",1.2738656539904116]
["Notes:  "]
["1)","All duration indices (SAIDI) are to be reported in units of minutes."]
["2)","Reports are due on the first business day of May of each year"]
["3)","Reports cover the calendar year ending in the December before the reports are due."]
["4)","IEEE 1366 (latest version) is used to define SAIDI, SAIFI, and TMED"]
[]
["SECTION 5: CIRCUIT REPORTING"]
[null,null,null,"BEGIN ON NEXT PAGE"]

{"sheet":"Excel LGE Section 5","index":1,"n_rows":252,"n_cols":22,"rows_kept":252,"cut":false,"hidden":false,"merged":[]}
["Substation Name","Substation Location   \n(County - Road - Town)","Circuit\nNumber","Circuit Location\n (Town - Road - General Area)","Total Circuit Length (Miles)","Average 2024 OMS Custs","Date of Last Circuit Trim (VM)","Animal","Construction","Lightning","Non-Company","Other/Unknown","Overload","Planned Work","Trees","Vehicle","Utility Equipment","2020-2024 SAIDI Average","2024 SAIDI","2020-2024 SAIFI Average","2024 SAIFI","LIST OF CORRECTION ACTION, IF ANY, TAKEN OR TO BE TAKEN"]
["ASHBY","Jefferson - 5400 Vesper Ln - Lousivlle","AB1204","Louisville - Dixie Hwy - N of Substation",14.6578467529013,1242,"2020-10-24",2.0503198789150714E-2,0,6.3592556951986734E-2,0,6.5281411239041191E-4,0,0.45460040522831568,0.46065102491815646,0,0,82.264573263486312,85.215807832528171,0.8995571658615138,1.3647342995169087,"Reliability Improvements Scheduled for 2025"]
["ASHBY","Jefferson - 5400 Vesper Ln - Lousivlle","AB1205","Louisville - Valley Station Rd & Dodge Ln - E of Substation",24.595542328533501,2219,"2020-09-12",1.9374223234696892E-3,1.224195424170408E-4,0,0,4.695853969453663E-3,0,0.862921604476652,0.12392938344018431,0,6.3933162478232832E-3,79.765784132492101,83.018514342045961,0.70493465525011234,0.36863452005407848,"Continue to Monitor"]
["ASHBY","Jefferson - 5400 Vesper Ln - Lousivlle","AB1206","Louisville - Valley Station Rd & 3rd St - E of Substation",25.0485282192701,1416,"2021-01-30",7.4033551678945094E-3,0,5.6511024660134017E-2,0,3.4543373342476799E-2,0,0.50785123806239763,0.36697359500237881,0,2.6717413764718236E-2,93.510396062146896,136.03396892019774,0.89247881355932224,0.87076271186440668,"Tree Trim Scheduled for 2025"]
["ASHBY","Jefferson - 5400 Vesper Ln - Lousivlle","AB1207","Louisville - Torrington Rd & Derring Rd - S of Substation",16.0826026445806,1658,"2024-01-01",1.349595217696832E-3,0,0,0,0,0,0.92763044322298482,8.0077266411892872E-3,0,6.3012234918129045E-2,86.922931742159207,118.43075994993967,0.76040410132689984,0.562726176115802,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1289","Louisivlle - Shelbyville rd & Upton Ln - E of Substation",46.5669936026909,2858,"2023-06-16",2.52818228029782E-2,2.1628841112739088E-3,0,0,4.8475515553827904E-2,0,0.160731194370521,0.30917780502147935,0,0.45417077813991968,42.531169813418465,67.574148583624904,0.77781665500349884,1.7382785164450663,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1291","Louisville - Shelbyville Rd & Bellewood Rd -  SW of Substation",21.9249138644272,1765,"2024-01-01",6.8324406798488059E-4,2.4715201446968418E-3,0,0,5.1678192043979124E-3,0,0.92764686341720548,9.834732481653534E-4,0,6.3047079917549625E-2,46.735054292492919,68.339697822662899,0.51416430594900853,1.3569405099150142,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1293","Louisville - New English Station Rd - NE of Substation",4.6376814233631798,156,"2020-11-21",3.0700864787122232E-3,0,0,1.3368244426824995E-3,0,0,0.92772389504545194,2.9041358582412922E-4,0,6.7578780447329123E-2,96.417307677884594,103.86720084615382,1.3173076923076921,1.0769230769230769,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1294","Louisville - Old Shelbyville Rd - W of Substation",6.70150348559745,496,"2023-08-05",4.9300630417651696E-2,6.5011820330969263E-4,0.1763888888888889,0,8.6780929866036253E-3,0,0.3762608353033885,0.38027974783293933,0,8.4416863672182822E-3,89.862970423891142,140.40131047580647,0.41582661290322587,0.60483870967741948,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1373","Louisville - S 12 St - N of Substation",3.1790394072027843,1154,"2023-05-12",0,0,8.8308884855026242E-5,0,0.5548839719373988,0,2.1635676789481429E-3,0.41647941912377962,0,2.6384732375018399E-2,108.72461727166377,171.96904968024265,1.0922876949740037,2.5571923743500875,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1441","Louisville - Bernheim Ln & 7th St Rd - SW of Substation",4.8194324669370596,49,"2023-05-12",3.6615134255492267E-2,0,0,0,0.427786818551668,0,0,0.53559804719283965,0,0,48.848299306122449,100.30680271428571,0.6071428571428571,1.2653061224489797,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1442","Louisville - S 4th St & S 3rd St - E of Substation",7.1283552748627699,1276,"2023-05-12",9.8656710992953828E-5,0,0,0,2.5635167482748057E-2,0,5.036684719113959E-4,2.1652551833716712E-3,0,0.97159725215097592,50.966914835815039,150.92771681818181,0.60560344827586199,2.0070532915360499,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1444","Louisville - S 15th St - N of Substation",3.3188375427468899,33,"2023-05-12",0,0,0,0,0,0,0,0.31391585760517798,0,0.68608414239482196,16.999873712121211,18.704040393939394,0.19696969696969696,0.12121212121212122,"Continue to Monitor"]
["ASHBOTTOM","Fayette - 96 Burley Ave. - Lexington","AS1414","Lexington - Burley Ave - E of Substation",4.1685901090401902,7,"Underground",0,0,0,0,0,0,0,0,0,1,16.158333321428572,64.633333285714286,0.25,1,"Continue to Monitor"]
["ASHBOTTOM","Jefferson - 8113 Grade Ln - Louisville","AS1417","Louisville - Grade Ln - N of Substation",1.93309479558856,25,"2021-10-30",0,0,0,0.39912436398059403,0.26754230268607265,0,0,0.33333333333333331,0,0,80.64349996,112.70133328,0.58000000000000007,1.04,"Continue to Monitor"]
["ASHBOTTOM","Jefferson - 8113 Grade Ln - Louisville","AS1419","Louisville - Outer Loop & National Turnpike - W of Substation",1.8626032088684601,4,"2021-10-30",0,0,0,0,0,0,0,1,0,0,8.1458333125000006,32.583333250000003,0.25,1,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1218","Louisivlle - Bishop Ln - N of Substation",2.97025051601371,136,"2021-05-08",8.993220495318914E-3,0,0,0,7.4251717935710004E-2,0,0,0.15818844255868653,0,0.75856661901028455,9.1462316102941177,23.560416647058823,3.4926470588235295E-2,5.8823529411764705E-2,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1219","Louisivlle - Pinewood Rd & Produce Rd - SE of Substation",8.9693585972727696,963,"2021-05-08",0.17735842721152392,0,4.8150697580712859E-2,0,7.3753840471433602E-2,0,2.2446821013045012E-2,0.64941322633178322,0,2.8876987391501435E-2,13.740853233904463,32.891588781931461,0.23805815160955349,0.71235721703011423,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1221","Louisville - Robards Ln - N of Substation",2.6654198344553501,65,"2021-05-08",2.5183842046942683E-3,0,0,0,0,0,0.83912561700413013,0,0,0.1583559987911756,94.843333323076905,305.45230766153838,0.37307692307692303,1.0769230769230769,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1224","Louisville - Popular Level Rd & Preston Hwy - W of Substation",13.6178092811466,1224,"2021-05-08",3.9633152366507435E-3,0,0,0,3.5740711865848297E-2,0,0.63764298977986311,0.15158972032829179,0,0.17106326278934611,70.97186137622549,87.541557729575175,0.87009803921568607,0.43382352941176461,"Continue to Monitor"]
["BROOK","Jefferson - 913 S 1st Street - Louisivlle","BK0003","Louisville - S 2nd St - W of Substation",1.0930210672698899,141,"2020-02-01",0,0,0,0,4.771255868184468E-2,0,0.26090024853487159,0.69138719278328375,0,0,57.798167845744679,231.1424349787234,0.27482269503546097,1.0921985815602837,"Tree Trim Scheduled for 2025"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1180","Louisville - Dutchmans Ln - W of Substation",8.7059721729908208,549,"2020-07-18",1.8074162114509705E-2,0,0,0,7.8081954567636915E-3,0,0.1667309478456622,0.71323182154495224,0,9.415487303811218E-2,111.63038857468123,127.59893745355188,1.2085610200364298,1.2823315118397083,"Tree Trim Scheduled for 2025"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1182","Louisville - I - 264 East - E of Substation",6.0938857399071198,226,"2020-08-01",0,0,0,0,0,0,3.2765549566027945E-2,0.228259626968703,0,0.73897482346526899,105.88515855088495,82.848230084070792,1.0564159292035398,1.5088495575221239,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1186","Louisville - Richland Dr & Hunsinger Ln - S of Substation",13.131097534359499,1676,"2020-09-19",5.5034912957241763E-2,0,0,3.2197095379593924E-4,3.0137464392716085E-2,0,0.46673007774000969,0.43654591527002545,0,1.1229658686211041E-2,86.017221056682587,138.15531025477333,1.089797136038186,0.77983293556085875,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1354","Louisville - Taylorsville Rd - S of Substation",9.29274654127261,37,"2020-09-19",8.0109207170312891E-2,0,7.4972159356252469E-2,0,0,0,1.9147178216043396E-2,0.66501418974745841,0,0.16075726550993283,106.45608103378379,277.76936929729737,1.5067567567567568,2.9459459459459461,"Tree Trim Scheduled for 2025"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1276","Louisville - Commonwealth Dr - SE of Substation",5.0302658988568698,145,"2021-10-23",0,0,0,0,2.3933722000613684E-2,0,0.91735706249360749,0,0,5.8709215505778865E-2,20.015775855172414,67.424712634482759,0.52586206896551724,2.0206896551724141,"Continue to Monitor"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1277","Louisville - Blankenship Rd & Plantside Dr. - S of Substation",11.0650725601177,116,"2021-10-23",0,0,0,0,1,0,0,0,0,0,2.0985632176724138,3.8668103448275861,1.0775862068965518E-2,2.5862068965517241E-2,"Continue to Monitor"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1278","Louisville - Ellinsgworth Ln - NE of Substation",21.826582494447599,1964,"2021-11-13",1.075002639901813E-3,0,0,1.0455742262491063E-3,4.4587508850162633E-2,0,0.26054878798212833,0.68879625670578337,0,3.9468695957747719E-3,58.877439746435847,173.02781737627291,0.52367617107942976,1.7795315682281059,"Continue to Monitor"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1281","Louisville - Bluegrass Parkway - E of Substation",10.556301529004401,175,"2021-10-23",0,0,0,0,0,0,0.97231256775915276,0,0,2.7687432240847302E-2,81.136309515714288,68.515142857142848,1.3185714285714287,2.0114285714285716,"Continue to Monitor"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1283","Louisivlle - Blankenbaker Rd - S of Substation",8.1487089801929606,451,"2021-10-23",1.7564894190995745E-2,0,0,0,2.16713626281398E-2,0,0.93525568011510107,7.5834782087404835E-3,0,1.792458485702296E-2,99.274630441241698,73.969844780487804,1.2555432372505542,2.0399113082039912,"Continue to Monitor"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1284","Louisville - Watterson Trail - SW of Substation",7.84625754004123,328,"2021-10-23",1.0613369267737146E-3,0,0.20619152957731363,0,0,0,0.12744390715090662,0.66530322634500605,0,0,66.067670217987796,65.708739835365847,0.85746951219512157,2.0060975609756095,"Continue to Monitor"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1285","Louisivlle - Moser Rd - NW of Substation",11.5918216154275,627,"2021-10-23",0,0,0,0,0,0,0.84772172333984608,3.9152543451558906E-2,0,0.11312573320859506,47.311848745349891,85.882961187141234,0.87759170653907503,2.1419457735247209,"Continue to Monitor"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1306","Louisville - Portland Ave - W of Substation",3.50328644769486,1322,"2023-03-31",0,0,0,0,0,0,4.0007094854259866E-3,0.77639384324313676,0,0.2196054472714373,4.483815556796209,8.5830559757942506,0.50397125567322243,1.0052950075642966,"Continue to Monitor"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1342","Louisville - Portland Ave - W of Substation",4.1226442916868802,1138,"2023-03-31",0,0,3.3801661639413665E-2,0,1.150976345451659E-3,0,5.8666719585119334E-2,0.86077155103984759,0,4.560909139016775E-2,32.029170324694689,44.94128587170475,0.42948154657293497,0.50175746924428821,"Continue to Monitor"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1346","Louisivlle - Northwestern PKY & W Market St - W fo Substation",5.2882257014253797,2184,"2024-03-01",0,0,0,0,0.71370029177457961,0,2.6500125670699058E-2,0,0,0.25979958255472141,58.027146290407508,81.661187422161163,0.86446886446886451,1.4487179487179487,"Continue to Monitor"]
["CROP","Jefferson - 116 N 26th St - Louisville","CB0003","Louisville - N 26th St - S of Substation",2.4695826512645702,398,"2023-02-24",0,1.1538072264768395E-2,0,8.3499207179244958E-2,0.23703653722883844,0,0.43844674606119899,0.1394689787793934,0,9.0010458486555783E-2,46.659034751884427,74.473785587939702,0.31218592964824121,0.58040201005025116,"Continue to Monitor"]
["CENTERFIELD","Oldham - 4210 Hwy 393 - Centerfield","CF1201","Centerfield - Dawkins Rd - N of Substation",53.116700841550902,562,"2022-08-19",1.2457939949205641E-2,0,0,0,8.2512902712900141E-2,0,0.40270000816491408,0.46187414859284154,0,4.0455000580138629E-2,212.92145609197485,252.7505931032029,2.1948398576512456,1.3185053380782918,"Continue to Monitor"]
["CENTERFIELD","Oldham - 4210 Hwy 393 - Centerfield","CF1202","Centerfield - W HWY 22 & Payton Way - SE of Substation",57.368535153823998,1012,"2024-01-01",1.2829837774135931E-2,0,0,6.9358768973919876E-4,0.72685841604213086,0,6.0116559559541122E-2,0.1364081364587745,0,6.3093462475678402E-2,178.19416994540518,518.8896738903162,0.89550395256916959,1.8814229249011851,"Continue to Monitor"]
["CENTERFIELD","Oldham - 4210 Hwy 393 - Centerfield","CF1203","Centerfield - S Camedn Ln - S of Substation",63.300401973478998,1229,"2024-01-01",6.8037532011965482E-2,0,1.7862138722103858E-3,0,0.11215486259065573,0,5.3220565132244387E-2,0.65570189596918249,0,0.10909893042374158,57.075359364117176,62.07381338974777,0.493287225386493,0.53620829943043102,"Trees Trimmed in 2024"]
["CENTERFIELD","Oldham - 4210 Hwy 393 - Centerfield","CF1204","Centerfield - S Hwy 393 - N of Substation",77.393192860514802,2041,"2021-04-10",1.6936168504321461E-2,0,0.64551836499988025,1.1092626996980449E-3,8.5768735887335693E-3,0,0.11681255014508482,5.009813704736675E-2,0,0.16094864301491515,75.438224719622738,81.675943155805953,1.4083782459578633,1.1509064184223412,"Continue to Monitor"]
["CAMPGROUND","Jefferson - 4300 Campground Rd. - Louisville","CG1438","Shepherdsville - Campground Rd - SE of Substation",0.45843918318601701,1,"2021-07-31",0,0,0,0,0,0,0,1,0,0,10.4625,41.85,0.25,1,"Continue to Monitor"]
["CLARKS LANE","Jefferson - 934 Clarks Ln - Louisville","CK0001","Louisville - Clarks Ln - E of Substation",3.7419974191804199E-2,151,"2023-05-12",0,0,0,0,1,0,0,0,0,0,131.05091058609273,151.03333333112582,0.89238410596026485,1,"Continue to Monitor"]
["CLARKS LANE","Jefferson - 934 Clarks Ln - Louisville","CK0002","Louisville - Pindell Ave - S of Substation",2.56509433592257E-2,702,"2023-05-12",0,0,0,0,7.971297744025016E-2,0,0.92028702255974981,0,0,0,38.694456309829064,51.018589733618242,0.30876068376068377,0.3931623931623931,"Continue to Monitor"]
["CLARKS LANE","Jefferson - 934 Clarks Ln - Louisville","CK0003","Louisville - Eastern PKY - W of Substation",0.26422801893724102,221,"2023-05-12",0,0,0,0,3.7403669428949151E-3,0,0.99625963305710508,0,0,0,53.375245090497721,140.32488685520357,0.39140271493212669,0.99095022624434392,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1229","Louisville - Brownsboro Rd, Hite Ave, Birchwood Ave, & Cleveland Blvd - NE of Substation",10.5932435549429,2695,"2024-01-01",2.8088543935374015E-2,0,0,2.7418524531738803E-3,4.2927176969072986E-2,0,0.26347443868055281,0.18659961192729579,0,0.47616837603453055,62.671912489795929,134.01698206233769,0.53283858998144717,0.81743970315398895,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1230","Louisville - Mellwood Ave, Shiloh Ave, & River Rd - N of Substation",16.0907930631328,2118,"2022-07-22",5.8041910530044942E-3,0,0,0,4.1559349132944915E-4,0,0.69306523582504131,9.8938604223524004E-2,0,0.20177637540710075,104.92232254839472,170.07374094617563,1.0105051935788478,1.346081208687441,"Reliability Improvements Scheduled for 2025"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1231","Louisville - Payne St, Grindstead Dr, & Lexington Rd - SE of Substation",5.2559332493623696,673,"2022-05-13",9.1715406437151963E-3,2.2764683220677338E-3,0,1.5541274121808567E-3,0.18504622981823277,0,0.6895072321647463,2.7011172206072918E-3,0,0.1097432844184499,50.164629764115894,125.79333828231798,0.81686478454680522,2.1872213967310543,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1232","Louisville - Frankfort Ave, Story Ave, & E Main St - W of Substation",13.4655717465454,1932,"2022-08-12",6.0270729389248785E-3,0,0,3.4599283739157979E-2,1.4458195737113759E-2,0,2.3876230543688128E-2,0.80629537741887958,0,0.11474383962223564,44.438666748706005,56.061602823498966,0.74961180124223603,1.3964803312629399,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1402","Louisville - Mellwood Ave & Zorn Ave - N of Substation",3.7014465620580799,12,"2022-08-12",0.19967532467532467,0,0,0,0,0,0.77922077922077926,0,0,2.1103896103896104E-2,41.192708270833329,51.37638883333333,0.375,0.49999999999999994,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1403","Louisville - Payne St, Spring St, & Story Ave - W of Substation",1.4678055485024599,4,"2018-07-28",0,0,0,1,0,0,0,0,0,0,426.47916662499995,11.583333250000001,0.375,0.5,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1404","Louisville - None - In Sub",2.7097808997916699,2,"2022-05-13",0,0,0,0,0,0,0,0,0,1,68.820833249999993,46.2,0.625,1,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1405","Louisville - Mellwood Ave, River Rd, & River Green Cir - N of Substation",5.5454116706590897,88,"2022-07-22",0,0,0,0,0,0,0,0.87504611978846403,0,0.1249538802115361,263.78115528125005,699.11780301136378,2.0369318181818183,5.1022727272727275,"Continue to Monitor"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1192","Louisville - Winchester Acres Rd & La Grange Rd - S of Substation",28.889675475829101,1115,"2024-01-01",4.2167300002976513E-2,2.8772981178501624E-4,0,0,0,0,0.75626875381808956,0.17422819667112199,0,2.704801969602692E-2,93.4285799632287,182.04886396860985,0.77735426008968611,1.0807174887892381,"Continue to Monitor"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1193","Louisville - Westport Rd, Rollington Rd, Collins Ln - NE of Substation",6.74603034910277,296,"2023-12-16",0,0.70438957475994513,0,0,8.23045267489712E-3,0,0.21742112482853224,0,0,6.9958847736625515E-2,1.5143862592905406,4.9243806250000004,1.0135135135135136E-2,2.7027027027027029E-2,"Continue to Monitor"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1195","Louisville - Collins Ln, Westport Rd, & Northumberland Dr - N of Substation",16.578114128165002,1156,"2020-04-25",1.2557734348033335E-3,0,5.0382156182711751E-3,0,9.9600585150972244E-3,0,0.87312283239369481,8.0173572872663912E-2,0,3.0449547165469517E-2,114.7650627125865,167.20037485121105,1.2610294117647058,1.6704152249134945,"Continue to Monitor"]
["CONESTOGA","Bullitt - 1365 N Buckman St. - Shepherdsville","CS1260","Shepherdsville - Buckman St & N Preston Hwy - N of Substation",8.6336827229824706,249,"2021-05-15",1.308139534883721E-2,0,0,0,0,0,4.7549833887043189E-2,2.0071982281284605E-3,0,0.93736157253599117,47.245147245983929,58.028246301204817,0.32730923694779113,0.52610441767068261,"Continue to Monitor"]
["CARTER","Jefferson - Opposite 2215 Carter St - Louisville","CT0001","Louisville - N 22nd St & Griffiths Ave - S of Substation",2.3977344222855099,369,"2023-04-07",0,0,0,0,0.16052179883281842,0,0.66852042567799519,0.12509440439409544,0,4.586337109509097E-2,35.152213184959351,34.735094842818427,0.27168021680216803,0.33333333333333337,"Continue to Monitor"]
["CARTER","Jefferson - Opposite 2215 Carter St - Louisville","CT0004","Louisville - Portland Ave, Bank St, & N 28th St - W of Substation",3.4551365432299499,471,"2023-04-07",0,0,0,7.2586284732979842E-4,0.30240154378634848,0,0.2014357921199621,3.2752347989271394E-3,0,0.49216156644743247,46.44697451963907,92.857961777070074,0.29405520169851379,0.62208067940552014,"Continue to Monitor"]
["CRESTWOOD","Oldham - Floydsburg Rd. - Crestwood","CW1224","Crestwood - W HWY 146, Glenarm Rd, & Fox Run Rd - N of Substation",49.494097732452197,1970,"2023-04-04",0.18530554975622338,0,5.8027435617178573E-4,0,4.6974590737715993E-3,0,0.61724458717624375,0.11285415157134612,0,7.9317978066243383E-2,47.396755494923859,107.29237732081219,0.77893401015228414,1.6005076142131975,"Continue to Monitor"]
["CRESTWOOD","Oldham - Floydsburg Rd. - Crestwood","CW1225","Crestwood - Hwy 146, Muirs Ln, Elm Ave, & Hwy 362 - SW of Substation",35.406087301511803,1534,"2024-01-01",3.8475291425302152E-3,3.1625704228150053E-4,4.5091261611321681E-2,1.1369361208451532E-2,0.19069505033890358,0,0.36294865988064873,0.37258575889770912,0,1.3146121878153632E-2,74.677034434485023,129.60335722685795,1.1724250325945245,1.6003911342894397,"Reliability Improvements Scheduled for 2025"]
["CRESTWOOD","Oldham - Floydsburg Rd. - Crestwood","CW1227","Crestwood - HWY 22, Carriage Hill Dr, & Mary Clayton Ln - NE of Substation",31.274300271542099,990,"2022-12-17",2.7892089620484683E-2,0,6.2538969946377351E-2,0,1.3073118011389617E-2,0,0.54584944091116927,0.33162904767843038,0,1.9017333832148646E-2,38.97295874823233,21.123282819191921,0.24267676767676774,0.27171717171717175,"Continue to Monitor"]
["CRESTWOOD","Oldham - Floydsburg Rd. - Crestwood","CW1228","Crestwood - HWY 329, I 71, Covered Bridge Rd, & Halls Hill Rd - N of Substation",78.933845205862397,1511,"2023-12-16",6.9534897489681308E-3,0,7.6566623249204949E-2,0,0.26440176940253063,0,6.1345490222613167E-2,0.51557636680424923,0,7.5156260572433853E-2,102.03399237971541,207.62859032825941,0.9424222369291857,2.0714758438120446,"Continue to Monitor"]
["CLAY LGE","Jefferson - 908 Clay St. - Louisville","CY1481","Louisville - S Preston St, S Floyd St, E KY St, & 3rd St - W of Substation",5.3934845702344099,801,"2022-06-17",0,0,0,0,0,0,0.24995888496011842,0.75004111503988158,0,0,89.292192048689131,60.729567207240962,1.2025593008739077,1.7927590511860176,"Continue to Monitor"]
["CLAY LGE","Jefferson - 908 Clay St. - Louisville","CY1482","Louisville - Clay St, E Broadway, Logan St, Chestnut St, & Preston St - N of Substation",3.9721658228190901,129,"2022-06-17",0,0,0,0,0,0,0.72045743329097844,0,0,0.27954256670902161,32.333494825581397,12.200904387596898,0.21124031007751939,0.26356589147286824,"Continue to Monitor"]
["DAHLIA","Jefferson - 2135 Dahlia Ave. - Louisville","DA1237","Louisville - Bardstown Rd, Landor Ave, & Wood Creek Rd - NE of Substation",7.6207413766641103,952,"2024-03-01",5.0285079223457499E-3,0,0,0,8.1602704828541581E-2,0,0.60879773658444969,0.29869206617542515,0,5.8789844892379499E-3,63.05244659978991,102.09422268592438,0.43907563025210089,0.78886554621848748,"Trees Trimmed in 2024"]
["DAHLIA","Jefferson - 2135 Dahlia Ave. - Louisville","DA1238","Louisville - Bardstown Rd, Gold Smith Ln, & Peabody Ln - SE of Substation",10.013889800138401,1779,"2022-02-11",2.0180126554432642E-2,0,9.2690122801796088E-2,0,2.5617567515107596E-2,0,0.2891186480156317,0.46557797072943491,0,0.1068155643835971,64.785808971753795,40.906782831365938,0.59822934232715019,1.1613265879707704,"Continue to Monitor"]
["DAHLIA","Jefferson - 2135 Dahlia Ave. - Louisville","DA1239","Louisville - Gardiner Ln, I 265 E, & Newburg Rd - SW of Substation",14.4517250769215,1421,"2024-03-01",6.627036573595757E-3,0,0,0,1.4911125470407016E-2,0,0.50831047508030192,0.42918006987061386,0,4.0971293005081393E-2,64.277680031667842,122.34467510204084,0.43859957776213926,0.88458831808585492,"Reliability Improvements Completed in 2024"]
["DAHLIA","Jefferson - 2135 Dahlia Ave. - Louisville","DA1241","Louisville - Bardstown Rd, & Village Dr - NW of Substation",7.20759582543291,1397,"2022-03-18",1.5771892835108159E-2,0,0,0,0,0,0.83468429970755753,0.13944943952638766,0,1.0094367930946719E-2,50.921265802970652,52.550035788117391,0.54509663564781674,0.51539012168933429,"Continue to Monitor"]
["DAHLIA","Jefferson - 2135 Dahlia Ave. - Louisville","DA1242","Louisville - Bardstown Rd, Doup Ave, Taylorsville Rd, & Millvale Rd - N of Substation",11.1188904809826,1285,"2024-03-01",9.7626246770275288E-3,0,4.2520721443693246E-2,0,2.4444336250648464E-3,0,0.47820072224955046,0.34171033125769135,0,0.12536116674697259,104.11104084980548,152.33396886459144,1.0461089494163422,1.673151750972762,"Trees Trimmed in 2024"]
["DUMESNIL","Jefferson - 1309 Dumesnil St - Louisville","DU0003","Louisville - S 15th St, Wilson Ave, & W Kentucky St -  W & N of Substation",2.70758719590214,387,"2022-11-18",3.5640125344508625E-2,0,0,0,0.33144561482991658,0.115037565598218,0.11583040736965304,0.37897836674595087,0,2.3067920111752935E-2,21.323417306201549,29.638544346253234,0.2099483204134367,0.3152454780361757,"Continue to Monitor"]
["DIXIE","Jefferson - 1706 Bernheim Ln. - Louisville","DX1220","Louisville - Bernheim Ln, 7th Street Rd, & Taylor Blvd - SE of Substation",20.711213962004901,3136,"2023-08-19",4.648020316308682E-2,0,0,0,0.13993959376488191,0,0.49546680070039906,0.27671045526851817,0,4.1402947103114006E-2,73.710224006138404,112.55871597576532,0.78635204081632648,0.50701530612244872,"Reliability Improvements Scheduled for 2025"]
["DIXIE","Jefferson - 1706 Bernheim Ln. - Louisville","DX1223","Louisville - Dixie Hwy, S 2nd St, & Hale Ave - NW of Substation",17.490481502994101,2708,"2023-07-14",1.7309655920783758E-2,0,9.2473611454531243E-3,2.7544785900144388E-4,5.1723983309140895E-2,0,0.2799767342645606,0.56260545489253044,0,7.8861362608529662E-2,42.621721131093061,73.080212945347142,0.40823485967503703,0.29948301329394394,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1169","Louisville - Hikes Ln, Champ Trace Ln, & Bashford Manor Ln - N of Substation",5.6381108160222899,700,"2020-05-30",3.0446301724027593E-2,0,3.5194737044195006E-2,0,3.8397051106475021E-5,0,0.62700336614148033,0.30217711279773712,0,5.1400852414534562E-3,143.26072023250001,56.034499994285717,0.62714285714285722,0.69285714285714284,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1171","Louisville - Newburg Rd, E Indian Trl, & Poplar Level Rd - SW of Substation",18.2526550618729,1574,"2020-05-30",1.5932047962874622E-2,0,0,0,0.15565240346985185,0,0.69113594575693438,6.0537150849632029E-2,0,7.6742451960707128E-2,36.34238140263659,52.532856837357045,0.41677255400254132,0.27763659466327828,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1172","Louisville - Hikes Ln - NE of Substation",13.592291069864499,2030,"2020-07-11",1.3587752224759449E-2,0,0,2.1991528742626814E-2,1.7563097612262234E-2,0,0.35822212046537688,0.47627023672525048,0,0.11236526422972411,53.903360010837417,88.379334969950719,0.39162561576354671,0.65467980295566508,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1422","Louisville - Bardstown Rd, Goldsmith Ln, & Shepherdsville Rd - N of Substation",6.15853816703759,280,"2020-05-02",0,2.6366271150528194E-2,0.85448323092290457,0,0,0,6.7273057481006149E-2,0,0,5.1877440445561036E-2,56.495773807142861,208.36898809285714,0.45982142857142849,1.6749999999999998,"Continue to Monitor"]
["EASTWOOD WEST","Jefferson - 100 Flat Road Rd. - Louisville","EW1240","Louisville - Shelbyville Rd & Beckley Creek PKWY - W of Substation",14.278118733499999,368,"2020-02-22",4.5128477625536116E-2,3.4539036702470869E-3,0,0,0.90455586341265926,0,6.7433357371490749E-3,1.9863109019369694E-2,0,2.0255310535038776E-2,102.12955162160326,207.65443839130435,0.54347826086956519,1.1114130434782605,"Continue to Monitor"]
["EASTWOOD WEST","Jefferson - 100 Flat Road Rd. - Louisville","EW1241","Louisville - Gilliland Rd, Shelbyville Rd, & Long Run Rd - E & SW of Substation",83.625149839215894,2262,"2020-10-24",1.3783034972993647E-2,0,1.6325083724357957E-4,0,4.1090235734208981E-2,0,0.62920604121383994,0.14706101849865202,0,0.16869641874306185,49.746776445623347,126.30494399381082,0.31774977895667544,0.72634836427939853,"Continue to Monitor"]
["FARNSLEY","Jefferson - 2428 Farnsley Rd. - Louisvlle","FA1123","Louisville - Kramers Ln, Campground Rd, & Lees Ln - SW of Substation",19.293962866426501,918,"2021-10-30",1.3309327393932809E-2,0,0,1.9401351886199432E-5,6.1374236556803276E-2,0,0.11947740518559333,0.80561009491141333,0,2.0953460037095384E-4,179.18292029003271,168.73576614923749,0.87581699346405217,1.2886710239651409,"Continue to Monitor"]
["FARNSLEY","Jefferson - 2428 Farnsley Rd. - Louisvlle","FA1215","Louisville - Orchard Way, S Crums Ln, Dover Rd, & Burrell Dr - S of Substation",16.564288355213002,1685,"2021-10-16",4.3777189202541547E-2,0,0,0,3.43081420082614E-4,0,8.9663185533857562E-2,0.86621654384351832,0,0,63.788120668100895,69.063392670623188,0.64228486646884309,1.1970326409495562,"Continue to Monitor"]
["FARNSLEY","Jefferson - 2428 Farnsley Rd. - Louisvlle","FA1216","Louisville - Crums Ln, Hillview Ave, & Garrs Ln - SE of Substation",10.4202590494183,1335,"2024-01-01",0,0,0,9.2051269672685135E-2,3.7335859804962825E-2,0,3.4922033407357347E-2,0.60577990730906628,0,0.22991092980592837,113.48254368876404,105.13348314157304,1.4344569288389515,1.7812734082397008,"Trees Trimmed in 2024"]
["FALLS CITY","Jefferson - 1048 S 43rd St - Louisville","FC0001","Louisville - Greenwood Ave & Cecil Ave - E of Substation",2.3864795303466999,491,"2023-02-10",0,0,0,0,0.2617139752818145,0,0.22094255059079179,0.51734347412739368,0,0,31.048302780040732,59.667786820773927,0.19653767820773932,0.2219959266802444,"Continue to Monitor"]
["FALLS CITY","Jefferson - 1048 S 43rd St - Louisville","FC0004","Louisville - Greenwood Ave, S 45th St, & Garland Ave - NW of Substation",3.6272695399672901,416,"2023-02-10",0,0,0.16542321035550417,0,0,1.5182601559294214E-2,0.11209758645130004,0.70403252881709999,0,3.2640728168015815E-3,103.47428885576923,99.088221146634638,0.54326923076923073,0.69711538461538458,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1210","Louisville - N Hurstbourne PKY, Whipps Mill Rd, & La Grange Rd - SW of Substation",16.965270898002899,1586,"2024-01-01",1.694574489473533E-3,0,0,0,7.861404667713745E-2,0,0.51163602777227701,0.17666808259123265,0,0.23138726846987936,45.666900481242116,73.477522066204315,0.55453972257250939,0.79760403530895319,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1213","Louisville - Westport Rd, Blossom Ln, Goose Creek Rd & Brownsboro Rd - W of Substation",29.334881978662199,2396,"2024-01-01",1.5401109857758003E-2,0,0,0,1.1447809096084068E-2,0,0.5124553420198853,9.1938688915042463E-2,0,0.36875705011123022,87.38105174916528,98.651001663188666,1.2360183639398996,2.0317195325542565,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1214","Louisville - Freys Hill Rd, Evergreen Rd, & Park Rd - SE of Substation",26.288833000003599,727,"2024-01-01",3.0912027310388196E-2,0,0,0,5.7188271396982709E-2,0,0.83944938206571562,7.1797981530369953E-2,0,6.5233769654352903E-4,147.21699907427785,280.94520860797797,1.0997248968363134,2.3906464924346622,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1215","Louisville - Springhurst Blvd, Fischer Pard Dr, & I 265 S - NE of Substation",4.3969953537064397,81,"Underground",0,0,0,0,0,0,1,0,0,0,51.422942382716052,7.2172839506172846,0.51543209876543206,0.97530864197530864,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1216","Louisville - Springhurst Blvd & N Hurstbourne PKY - NW of Substation",15.791450105377001,1070,"2019-08-10",0,0,0,0,0,0,1,0,0,0,60.793368378971962,6.5932710261682246,0.76612149532710272,1.0056074766355141,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1217","Louisville - Westport Rd & Chamberlain Ln - NE of Substation",8.2908193572297808,556,"2024-01-01",7.2505180081668102E-3,0,0,0,1.4845842685150008E-3,0,1.5436483738215115E-2,0.34733844370871497,0,0.62848997027638809,231.61320443435253,563.34790167266192,1.6740107913669062,6.5215827338129486,"Trees Trimmed in 2024"]
["FLOYD","Jefferson - 1806 S Floyd St. - Louisville","FL1495","Louisville - Floyd St, Burnett Ave, & Shelby St - E of Substation",3.9526390303711398,1056,"2024-03-01",0,0,0,0,0.97601732719422807,0,2.3982672805771908E-2,0,0,0,13.818532985256352,55.253424870949651,0.25260416666666674,1.0085227272727275,"Continue to Monitor"]
["FLOYD","Jefferson - 1806 S Floyd St. - Louisville","FL1497","Louisville - S Floyd St & Crittenden Dr - S of Substation",3.7356342023114499,428,"2019-12-07",0,0,0,0,1,0,0,0,0,0,35.200700933411213,90.220482864485987,0.47137850467289721,0.86214953271028028,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1256","Louisville - Bardstown Rd, Lands Ln, & HWY 44 -  S of Substation",38.053999669270503,2068,"2023-06-16",2.8360985229586538E-3,0,1.4902450719603055E-4,1.3049296225973658E-3,8.7121425631751948E-3,0,8.3808911974389416E-2,0.80153178661852587,0,0.10165710619115752,25.598067776353972,60.480722110735016,0.38237427466150858,0.32350096711798831,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1260","Louisville - Thixton Ln & Independence School Rd - SW of Substation",47.358921813577702,1832,"2021-07-24",6.6964642668670945E-3,0,0,0,1.3400924311963283E-2,0,0.8762333487918379,5.879695520765036E-2,0,4.487230742168135E-2,12.252838424536026,21.008624449235807,7.7101528384279472E-2,0.16593886462882096,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1261","Louisville - Fairmount Rd, Back Run Rd, & Dawson Hill Rd - E of Substation",34.418323528200197,866,"2021-11-20",5.7603962598273634E-2,1.8820630833326203E-3,1.1104172191662461E-2,0,2.8953829570632972E-2,0,8.6929927369474649E-2,0.81158837569401077,0,1.9376694926129024E-3,138.42203136143186,231.91389528637413,1.2271939953810618,1.814087759815241,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1262","Louisville - Bardstown Rd & Stone Breaker Rd - NNW of Substation",33.944624363622097,2226,"2021-08-28",6.3508507659225258E-4,0,4.7843737316904479E-2,0,3.2169043770261946E-2,0,6.9353275004738332E-3,0.17427826054166803,0,0.73813854579409943,31.392505238993706,27.788814013477094,0.39330637915543565,0.59254267744833766,"Continue to Monitor"]
["FORTY FOURTH STREET","Jefferson - 128 N 44th St - Louisville","FO0002","Louisville - N 44th St, W Market St, & Fontaine Landing Ct - SW of Substation",2.5847046152038602,359,"2023-03-17",0,0,0,0,4.0881145929967455E-4,0,0.12557849442077182,0.54060598437082341,0,0.33340670974910508,123.31881383008357,182.46225626740949,0.48119777158774368,1.1253481894150417,"Continue to Monitor"]
["FORTY FOURTH STREET","Jefferson - 128 N 44th St - Louisville","FO0003","Louisville - Duncan St & N Longworth Ave - W of Substation",1.47791506141954,248,"2023-03-17",0,0,0,3.655624811500955E-2,0,0,0.50717553031064644,0.16386850306625114,0,0.29239971850809288,70.48881048084678,207.92540321774197,0.33266129032258068,0.73790322580645162,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1134","Louisville - Preston Hwy, Loretta St, & Ulrich Ave - NW of Substation",15.5462235483102,1841,"2021-01-23",4.5306074769809945E-3,0,2.7201388755398948E-2,0,0.23694603934116923,0,0.6962555948714233,2.0809151117347761E-2,0,1.4257218437679749E-2,55.403648376018474,105.30757740032593,0.50135795763172175,0.98804997284084728,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1138","Louisville - Fern Valley Rd & Shepherdsville Rd - E of Substation",11.1031699946343,1565,"2021-05-01",0,0,0.10058727653739684,0,0,0,0.21716296277132435,0.16614493053579282,0,0.51610483015548603,9.0382454720447285,18.794110753993611,7.1884984025559123E-2,0.11309904153354633,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1139","Louisville - Industrial Blvd, Grade Ln, & Knopp Ave - W of Substation",8.4566765635393804,219,"2021-06-12",7.1346102608129307E-3,0,0,0,0.82607537227271388,0,1.7229639716983925E-2,5.447171319458835E-2,0,9.5088664554900976E-2,80.338698611872147,151.90509892237444,0.67465753424657526,0.52054794520547942,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1140","Louisville - Preston Hwy, Minor Ln, & Rossmoor Dr - SE of Substation",11.278558955418401,1341,"2021-05-01",4.2558443553891996E-2,0,0,0,0.93813207323800341,0,7.9419254572337516E-3,4.0251179450236391E-3,0,7.3424398058472519E-3,165.4301640551827,296.05389012900821,1.0288963460104399,0.97240865026099921,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1141","Louisville - Hanses Dr, Poplar Level Rd, & Rangeland Rd - NE of Substation",14.7992274295326,1437,"2021-01-23",4.4393212883112165E-3,0,1.1968511086952684E-2,7.2524889206143417E-2,0.54463661885147696,0,4.7485603735083502E-2,1.7595855288215369E-2,0,0.30134920054381686,98.262355016875446,266.89851541892835,1.0480167014613779,1.9095337508698682,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1144","Louisville - Preston Hwy & Oaklawn Dr - S of Substation",1.2451292196381201,31,"2021-05-01",0,0,0,0,0,0,0.22740631888317414,0,0,0.77259368111682591,27.128225798387099,87.782795677419358,0.23387096774193544,0.87096774193548376,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1477","Louisville - Preston Hwy & Outer Loop - SW of Substation",6.2330343589383901,29,"2021-02-27",0,0,0.2869980031062791,0,1.2480585755491456E-2,0,0,0,0,0.70052141113822941,251.87183905172415,443.2218390344828,0.8793103448275863,1.1379310344827587,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1478","Louisville - Preston Hwy, & Standiford Ave/Ln - NW of Substation",7.0617543258687201,117,"2021-02-27",4.0494491221099924E-3,0,1.8337128100120718E-4,0,0.99494200883238337,0,0,8.2517076450543234E-4,0,0,165.47236465598289,559.34173786324789,0.73717948717948723,1.8803418803418803,"Continue to Monitor"]
["GRAND","Jefferson - 1038 S 34th St - Louisville","GD0002","Louisville - Louis Coleman Jr Dr, Virginia Ave, & Kirby Ave - S of Substation",4.05264262725413,585,"2023-01-13",0,0,0,4.6314613189169601E-2,0.76827592455565463,0,7.0113710152368586E-2,1.7668111324202292E-3,0,0.11352894097038704,64.761531334188049,108.97421651794873,0.56880341880341878,0.41538461538461541,"Continue to Monitor"]
["GRAND","Jefferson - 1038 S 34th St - Louisville","GD0003","Louisville - Louisville Coleman Jr Dr - N of Substation",1.11062591963041,156,"2023-01-13",0,0,0,0.88925348646431501,0.11074651353568499,0,0,0,0,0,4.9026442243589745,7.8192307564102563,6.0897435897435896E-2,7.0512820512820512E-2,"Continue to Monitor"]
["GRAND","Jefferson - 1038 S 34th St - Louisville","GD0004","Louisville - Greenwood Ave & S 38th St - W of Substation",1.31584553236697,230,"2023-01-13",0.45873965969466673,0,0,0,4.8422893267872757E-3,0,0.32349182863676107,0.21238819019436411,0,5.3803214742080845E-4,31.537717388043475,64.647028978260863,0.29456521739130431,0.50869565217391299,"Continue to Monitor"]
["GILLIGAN","Jefferson - 35th Street & Gilligan Ave - Louisville","GI0001","Louisville - Bank ST, 33rd St, Portland Ave, & Rudd Ave - N & E of Substation",4.1134172840229004,674,"2023-03-10",0,0,0,0,0.95435136909019835,0,4.5648630909801549E-2,0,0,0,133.19426310126113,201.18904549851629,0.92581602373887295,1.0756676557863505,"Continue to Monitor"]
["GILLIGAN","Jefferson - 35th Street & Gilligan Ave - Louisville","GI0002","Louisville - S 32nd St - S of Substation",2.3506066230106999,173,"2023-03-10",0,0,0,0,0.83293404390553949,0,6.5679036490164438E-3,0,0,0.16049805244544402,147.84819363439306,354.68381501734103,0.83526011560693636,1.8554913294797686,"Continue to Monitor"]
["GILLIGAN","Jefferson - 35th Street & Gilligan Ave - Louisville","GI0003","Louisville - Bank St, N 39th St, & S 38th St - W of Substation",3.2909331911178601,480,"2023-03-10",3.1934216081583844E-3,0,0,0,0.465755016108786,0,0.50239577459600526,4.9983990388566017E-3,0,2.3657388648193747E-2,223.73381075913414,688.97972221361988,1.2244791666666668,3.0770833333333334,"Continue to Monitor"]
["GOSS","Jefferson - 1260 Goss Ave - Louisville","GO0001","Louisville - Goss Ave - E of Substation",0.37058428706596602,42,"2022-07-15",0,0,0,0,0,0,0.85235521858364249,0,0,0.14764478141635748,42.270337297619051,87.177777761904764,0.23214285714285715,0.38095238095238093,"Continue to Monitor"]
["GOSS","Jefferson - 1260 Goss Ave - Louisville","GO0002","Louisville - Reasor Ave, E Burnett Ave, & Texas Avenue - SW of Substation",3.3612764793200798,704,"2022-07-15",0,0,0,0,0,0,0.17903007190608561,6.2785729054193759E-2,0,0.75818419903972067,36.539044741122161,47.682410035511367,0.4140625,0.62073863636363635,"Continue to Monitor"]
["GOSS","Jefferson - 1260 Goss Ave - Louisville","GO0003","Louisville - Ash St & Hickory St - NW of Substation",1.6298616245153701,411,"2022-07-15",0,0,0,0,0,0,0.90315229775921002,1.2533232054690467E-2,0,8.4314470186099499E-2,31.087956200729927,32.028183289537715,0.24878345498783455,0.1508515815085158,"Continue to Monitor"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1141","Louisville - Embassy Square Blvd, Doral Ct, & Bunsen Pky - NW of Substation",7.1444664314294499,932,"2023-09-09",2.9834058853588346E-3,0,0,0,1.7289538292485198E-5,0,0,8.1068723993652815E-4,0,0.99618861733641217,140.8794751408262,556.86090843562238,0.5080472103004291,2.0128755364806863,"Continue to Monitor"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1143","Louisville - Hurstbourne Pky & Stone Creek Pky - N of Subsation",9.6104304524787505,404,"2023-11-18",0,0,0,0,0,0,5.6829527265811954E-2,0,0,0.94317047273418808,64.830631183168322,149.27929042326733,0.57673267326732669,1.6782178217821782,"Continue to Monitor"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1144","Louisville - Old Hickory Rd, Waterson Trl, & Blankenbaker Access Dr - SE of Substation",6.5848580672180699,282,"2023-09-16",7.7477084242688786E-3,0,0,0,1.6668485377564383E-2,2.9463116542994324E-3,0.96993670886075944,6.2745525971191621E-4,0,2.0733304233958969E-3,91.288578593971636,129.9868794219858,0.72517730496453892,1.0425531914893615,"Continue to Monitor"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1147","Louisville - I 64 W, Linn Station Rd, & Timberwood Cir - NNW of Substation",15.5017913608827,528,"2024-01-01",2.5521542964386463E-3,0,0,1.7798103003242533E-5,1.9034602790836226E-3,0,0.89517994584692984,3.1255342358220549E-2,0,6.9091299116324181E-2,107.95460068844699,285.04756943371223,1.1728219696969697,2.7897727272727271,"Continue to Monitor"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1150","Louisville - Bunsen Way & Production Dr - E of Substation",2.7849690302686199,327,"2023-11-18",1.599427070899976E-2,0,2.5125328240630223E-2,0,0,0,0.83605872523275249,0,0,0.12282167581761758,136.66766054663611,49.952956165137614,0.22629969418960244,0.27217125382262997,"Continue to Monitor"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1291","Louisville - Frankfort Ave, Birchwood Ave, & Brownsboro Rd - W of Substation",7.5659558126167497,1549,"2024-01-01",2.5558649363946175E-2,0,0,0,2.6958246713079262E-3,0,0.41710134036468288,0.53781291994073444,0,1.6831265659328489E-2,38.462890033408655,62.444383468689473,0.55196901226597817,0.42285345384118789,"Trees Trimmed in 2024"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1292","Louisville - Grinstead Dr, Lexington Rd, & Alta Vista Rd - S of Substation",14.5469070704931,855,"2024-01-01",0,0,0,1.0904109713517234E-4,9.4275115231451086E-4,0,0.42664600943659831,0.32079890777167702,0,0.25150329054227499,152.49109160730995,192.56426899415206,1.0154970760233915,1.0596491228070177,"Trees Trimmed in 2024"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1293","Louisville - Lexington Rd, Cannons Ln, & Old Cannons Ln - SE of Substation",19.715445110997699,2324,"2024-01-01",4.6241330580999729E-4,0,1.0756424455551517E-3,0,5.7137276292614606E-5,0,0.61275543186147263,5.741166809620589E-2,0,0.3282377070146637,72.511429642211709,60.18675415490533,0.30496987951807231,0.31282271944922546,"Continue to Monitor"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1294","Louisville - Hillcrest Ave, Zorn Ave, & River Rd - N of Substation",20.693850786275799,1135,"2024-01-01",2.1249596581556459E-3,0,0.13405406906061051,0,9.2908279708081215E-2,0,0.52280716771912128,0.21441039599207393,0,3.3695127861957441E-2,183.32353890088103,239.31778265814981,1.0951541850220263,1.421145374449339,"Continue to Monitor"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1434","Louisville - Stilz Ave, Lexington Rd, & Alta Vista Rd - S & E of Substation",3.2478849249125901,7,"2021-04-10",0,0,0,0,0,0,0.69,0.31,0,0,74.888095214285713,83.538095142857145,1.2142857142857142,1.1428571428571428,"Tree Trim Scheduled for 2025"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1435","Louisville - Hillcrest Ave, Zorn Ave, & Frankfort Ave - N & W of Substation",2.8425244694632501,40,"2023-05-19",0,0,0,0,0,0,0.50410787640650112,0.49589212359349882,0,0,63.202916662499995,138.82374999999999,0.75,0.97499999999999998,"Continue to Monitor"]
["HERMAN","Jefferson - Rear 3619 Jefferson St - Louisville","HE0001","Louisville - W Market St, 37th, 36th, 35th & 34th St - NE of Substation",3.5890908928857801,683,"2023-02-17",0,0,0,0,0.93630281801255955,0,1.9517813752406198E-2,4.4179368235034239E-2,0,0,124.88139336054172,92.408735966325025,0.74304538799414344,1.0556368960468521,"Continue to Monitor"]
["HERMAN","Jefferson - Rear 3619 Jefferson St - Louisville","HE0003","Louisville - 38th St, Amy Ave, & W Muhammad Ali Blvd - N & SW of Substation",3.0717279975581899,669,"2023-02-17",0,0,0,0,0.96842846904192115,0,1.2609176273368885E-2,1.8962354684709855E-2,0,0,40.17387892189835,123.04890383408069,0.31539611360239161,0.81315396113602378,"Continue to Monitor"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1105","Louisville - Stevens Ave, Baxter Ave, Barret Ave & Winter Ave - W of Substation",14.367654216480799,2704,"2024-01-01",0.10134833196330154,0,0,0,2.0870457517061035E-2,0,0.45417657411136425,3.625986836660948E-2,0,0.38734476804166368,61.064728176127957,93.249235694526604,0.87805103550295882,1.7714497041420127,"Reliability Improvements Scheduled for 2025"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1472","Louisville - Bardstown Rd, Grinstead Dr, Baxter Ave,  & Payne St - NW of Substation",5.7664592625321696,350,"2021-04-24",0,0,0,0,0,0,0,0.99924222741837709,0,7.5777258162293241E-4,84.481904760952375,131.96590476,0.99071428571428577,1.382857142857143,"Tree Trim Scheduled for 2025"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1475","Louisville - Cherokee Pky, Bardstown Rd, & Richmond Dr - N & SE of Substation",4.6473210026078098,21,"2021-04-10",0,0,7.02000702000702E-2,0,0,0,0,8.4240084240084237E-2,0,0.84555984555984554,72.37996028571429,133.39365071428571,0.70238095238095233,2.0952380952380949,"Continue to Monitor"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1233","Louisville - US 42, Hunting Creek Dr, & Westover Dr - NE of Substation",29.565573289187,1222,"2024-01-01",1.0190370805293347E-4,0,0,2.7127275190822457E-4,0.36373554717492435,0,0.54492062237477978,7.3836999232193667E-2,0,1.7133654758141006E-2,71.30142184533554,173.45424167430448,0.43044189852700487,0.92062193126022929,"Continue to Monitor"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1234","Louisville - HWY 42, Wolf Pen Branch Rd, & Barbour Ln - SE of Substation",54.669662139637602,2334,"2024-01-01",1.2366571588202429E-2,0,3.1021554385861735E-2,0,0,0,0.33099214867527271,0.53671302967036194,0,8.8906695680301115E-2,75.845399525814059,98.433811765638367,0.7226863753213365,0.6838046272493572,"Trees Trimmed in 2024"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1235","Louisville - US 42, Marina Dr, & Seminary Dr - S of Substation",23.7788682493408,1471,"2024-01-01",0,8.9875803222049175E-3,0,0,0,0,0.31270039653976522,0.43383151640470613,0,0.24448050673332375,46.984435187967371,73.616168135961942,0.42946974847042824,0.5791978246091094,"Trees Trimmed in 2024"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1241","Louisville - River Rd, Avish Ln, & Rockledge Dr - SW of Substation",19.702179709104101,541,"2023-01-28",1.534435412187092E-3,0,2.2629197971963035E-2,0,1.3239843676288752E-2,0,0.94050263932822509,1.5644289069754739E-2,0,6.4495945415812134E-3,135.94680374445471,135.49254465804069,1.561460258780037,2.0018484288354901,"Continue to Monitor"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1242","Louisville - River Rd, Shirley Ave, & Duroc Ave - N of Substation",10.5495794238557,583,"2022-07-15",9.6580756013745703E-3,0,0,0,0.19959450171821305,0,0.64780240549828183,0.1429450171821306,0,0,25.073956542452834,38.78907946826758,0.49656946826758142,0.30188679245283029,"Continue to Monitor"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1243","Louisville - US 42, Covered Bridge Rd, Rose Island Rd, & River Bluff Rd - NNE of Substation",53.081332644914099,1524,"2022-11-18",8.166863797861787E-4,0,0,9.5979328236658581E-5,0.37304521143613811,0,0.39195198964572708,0.21405689102840411,0,2.0033242181707836E-2,140.73489445767717,90.402241898293966,1.1174540682414698,1.2919947506561682,"Continue to Monitor"]
["HARMONY LANDING","Oldham - 11943 W Hwy 42 - Goshen","HL1155","Goshen - Goshen Ln - NW of Substation",15.089176307132499,389,"2021-12-24",9.2465559272067576E-3,0,0,0,5.1760303872101596E-3,0,0.26239582742785872,0.71522195135778666,0,7.9596348999376385E-3,104.71630247236506,203.76413880462727,0.4080976863753214,0.81233933161953742,"Continue to Monitor"]
["HARMONY LANDING","Oldham - 11943 W Hwy 42 - Goshen","HL1156","Goshen - US 42, Harmony Landing Rd, & Hwy 1793 - W & SW of Substation",51.3750822355642,1292,"2022-01-07",0,2.7603821965325608E-4,3.8689694240556777E-4,0,7.1143585326296027E-2,0,0.22328831360602364,0.68792826110333249,0,1.6976904802289011E-2,47.852267148993818,67.469491732972145,0.66137770897832837,0.79411764705882404,"Continue to Monitor"]
["HARMONY LANDING","Oldham - 11943 W Hwy 42 - Goshen","HL1157","Goshen - Meadowridge Trl, Hwy 1793, & Rose Island Rd - W of Substation",30.1684307541605,1345,"2024-01-01",1.5145077106997787E-2,0,0,0,0.19066874725306809,0,0.6546527226363873,0.13020939506759213,0,9.3240579359547115E-3,259.62822489535313,477.95623294646839,2.9979553903345719,5.3085501858736013,"Reliability Improvements Scheduled for 2025"]
["HANCOCK","Jefferson - 630 E Caldwell St - Louisville","HN1200","Louisville - Shelby St, E Broadway, Baxter Ave, & Cherokee Rd - NE of Substation",6.4522218830939,1913,"2022-06-10",0.57087367877989403,0,0.32225192613532194,2.2810899772743747E-3,1.6202134418023595E-4,0,8.037964159173179E-2,9.9088843124965353E-3,0,1.4142757859101122E-2,112.42335554652379,121.39312597699947,1.178254051228437,0.92838473601672777,"Continue to Monitor"]
["HANCOCK","Jefferson - 630 E Caldwell St - Louisville","HN1201","Louisville - Shelby St, Logan St, & Barrett Ave - E & S of Substation",6.4313224243460096,918,"2022-06-10",0.37966493887285468,0,0,0,2.0842121970269696E-3,0,0.47137027554204136,2.6748085991504435E-2,0,0.12013248739657253,63.928576611655757,144.87389251198255,0.67156862745098023,1.3681917211328973,"Continue to Monitor"]
["HANCOCK","Jefferson - 630 E Caldwell St - Louisville","HN1204","Louisville - S Preston St, E Broadway, S Shelby St, & E Madison St - N of Substation",8.5677761693166108,1246,"2022-06-10",6.2846789718038728E-3,2.1798210848148567E-3,4.0829181293171785E-2,0,6.9018231230891181E-2,0,0.14277828105537313,0.73847808855169295,0,4.3171781225229307E-4,94.483333326243979,113.39985285714282,0.71187800963081893,1.1958266452648481,"Continue to Monitor"]
["INTERNATIONAL","Jefferson - 5599 Cane Run Rd. - Louisville","IN1290","Louisville - Cane Run Rd, Greenbelt Hwy, & Rockaway Dr - ENE of Substation",13.798252309754099,1164,"2021-11-20",1.5515374713349189E-2,0,0,0,0.37767150030263508,0,0.56394124617443719,5.5326803236063872E-3,0,3.7339198485972225E-2,47.376510592353952,50.061383157216504,0.41151202749140892,0.60309278350515449,"Continue to Monitor"]
["INTERNATIONAL","Jefferson - 5599 Cane Run Rd. - Louisville","IN1296","Louisville - Greenwood Rd - S of Substation",0.75706332995217895,640,"2021-10-02",5.240695819118162E-4,0,9.3190987040952661E-3,0,0,0,0.14840509022039461,0.70603588060553379,0,0.13571586088806445,36.854348955859379,137.41302082968753,0.35039062499999996,1.1921874999999997,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1121","Louisville - Taylorsville Rd, Neal Dr, & Watterson Trl - W of Substation",14.3307930024698,1559,"2022-12-23",4.6868503609630721E-3,0,1.945042899799675E-2,0,1.5254941981328192E-2,0,0.39389197565861583,0.52855576973957741,0,3.8160033261518692E-2,22.197436923829375,24.591137479794742,0.15923669018601666,0.13277742142398974,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1123","Louisville - Taylorsville Rd, I 265 S, & Eastwood Fisherville Rd - E of Substation",68.779889448576895,1432,"2020-08-01",3.8446115574002596E-3,0,1.8054280669946844E-4,0,5.5569175451499553E-3,2.4287758627570596E-3,0.84561309486479241,0.10886731243977946,0,3.3508744923421346E-2,54.789004299057254,120.80804235195528,0.59898743016759792,1.6962290502793302,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1125","Louisville - Blankenbaker Pky & Chenoweth Run Rd - NW & SW of Substation",13.1966890074197,470,"2019-04-06",0,0,1.3221913885100001E-3,0,0,0,0.93375977925152465,3.5850723024421348E-2,0,2.9067306335543955E-2,37.528608149468084,47.889645385106391,0.22925531914893613,0.10212765957446809,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1155","Louisville - Southside Dr, 3rd St, & W Southland Blvd - N of Substation",5.2020716563391201,1264,"2021-07-17",7.3087660020417569E-2,0,0.4185510755359611,0,7.1009766101419292E-2,0,0.29442853400066854,8.4443802003812476E-2,0,5.8479162337721005E-2,38.339464659810133,76.031724678797488,0.31289556962025311,0.51503164556962022,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1156","Louisville - Strawberry Ln, Southside Dr, & National TPke - S of Substation",12.782144656164499,1268,"2020-12-19",2.9124542722615206E-4,0,0,0.44463468556525881,0.16720576489433528,0,9.0903875770586857E-3,0.37877791653612103,0,0,104.24697685804416,178.71670609463723,1.1614747634069396,1.4787066246056779,"Tree Trim Scheduled for 2025"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1158","Louisville - Inverness Ave, New Cut Rd, & Palatka Rd - W & SW of Substation",19.558025682530801,2433,"2021-07-10",1.2003109299970052E-2,0,0,0.11772491668713735,2.571902561807432E-2,0,0.13796340851961653,0.6637244971784112,0,4.2865042696790534E-2,68.14069050113028,127.24178653925192,0.70263049732840133,1.9313604603370331,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1159","Louisville - Kenwood Dr, Homestead Dr, & Southside Dr - SW of Substation",12.562941793802599,1452,"2024-01-01",1.4502469941797777E-2,0,4.4568994693925106E-2,0,7.4597605700747732E-3,0,0.58069062198886257,0.30301312555367937,0,4.9765027251660342E-2,109.33386420402891,87.028730480716234,1.0203168044077133,1.2300275482093666,"Trees Trimmed in 2024"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1161","Louisville - Southside Dr, 3rd St, & W Kenwood Way - N of Substation",6.04231392518171,740,"2021-07-17",0,0,0,0,0,0,0.39031516248209303,0.46504373067933352,0,0.14464110683857348,69.159611483445957,75.879932427027029,0.6425675675675675,0.92837837837837833,"Continue to Monitor"]
["LOGAN","Jefferson - Rear of 1130 Logan St, St Catherine St - Louisville","LG0003","Louisville - Logan St, E Kentucky St, & Swan St - NE of Substation",1.3529922125198,293,"2022-07-22",0,0,0,0,0,0,0.24850085272597239,0.63005446443307478,0,0.12144468284095285,31.336291236348121,49.077133098976105,0.3011945392491468,0.33447098976109213,"Continue to Monitor"]
["LOGAN","Jefferson - Rear of 1130 Logan St, St Catherine St - Louisville","LG0004","Louisville - Logan St, Goss Ave, & Charles St - SE of Substation",3.0035613718917,740,"2022-07-22",0,0,0,0,0,0,0.3737304853990599,0.59818797340412577,0,2.8081541196814341E-2,24.677725221959463,55.483851348648649,0.21993243243243243,0.39459459459459456,"Continue to Monitor"]
["LYNN","Jefferson - Rear of 2071 S Preston St & Lynn St - Louisville","LN0001","Louisville - Shelby St - NE & SE of Substation",3.338800558984,585,"2022-07-15",0,0,0,0,0.23065072713827953,1.4789253142716292E-2,8.5038205570618676E-3,0.52119792950456001,0,0.22485826965738231,8.9816239294871778,13.281111107692306,6.4529914529914537E-2,5.6410256410256411E-2,"Continue to Monitor"]
["LYNN","Jefferson - Rear of 2071 S Preston St & Lynn St - Louisville","LN0003","Louisville - Barbee Ave, Crittenden Dr, Warnock St, & Floyd St - W of Substation",3.3767206119054798,451,"2022-07-15",0,0,0,0,0,0,0.15446552924791088,0.23581128133704735,0,0.60972318941504178,40.649002215077601,44.929526973392463,0.42294900221729487,0.38802660753880258,"Continue to Monitor"]
["LOCUST","Jefferson - 2929 Preston Hwy - Louisville","LO1190","Louisville - Hess Ln, Poplar Level Rd, & Sheridan Ave - E of Substation",18.930667816873701,2902,"2024-01-01",1.4700624129721307E-2,3.9244300128779444E-4,1.4302367158044065E-3,0,0.12627943685882809,0,0.74745130073052535,5.0536484117686388E-2,0,5.9209474446146645E-2,97.024112676257744,158.22173213094422,0.65799448656099258,0.78807718814610639,"Reliability Improvements Completed in 2024"]
["LYNDON SOUTH","Jefferson - 918 Ormsby Ln. - Bellemeade","LS1241","Bellemeade - Old Whipps Mill Rd, Dorchester Rd, & Shelbyville Rd - S & SE of Substation",5.8001470801752797,534,"2024-01-01",4.9790613472754236E-2,0,0,0,1.2325026864419034E-2,0,0.53479048588448441,0.39554631879488628,0,7.5475549834560542E-3,111.77866728604869,88.317665411985018,1.2504681647940075,2.0992509363295881,"Trees Trimmed in 2024"]
["LYNDON SOUTH","Jefferson - 918 Ormsby Ln. - Bellemeade","LS1244","Lyndon - New La Grange Rd, La Grange Rd, Whipps Mill Rd - N & NE of Substation",16.760157503873099,1910,"2021-07-24",1.2100958457648024E-2,0,0,0,3.0202096066258295E-2,5.1953779051740179E-4,7.5492837406720914E-2,0.63978667254649313,0,0.24189789773236225,110.16811954188482,160.03750435706812,0.7858638743455495,1.284816753926701,"Continue to Monitor"]
["LYNDON SOUTH","Jefferson - 918 Ormsby Ln. - Louisville","LS1245","Louisville - Ormsby Ln, Westport Rd, & Colonel Dr - N of Substation",21.006213562700601,1931,"2020-12-26",8.9089383130507765E-2,0,0,0,7.867184221569451E-2,0,0.28569030633655057,0.45142152748636177,0,9.5126940830885437E-2,22.593287153029515,27.020800960642145,0.41170378042465039,0.16002071465561893,"Continue to Monitor"]
["MILL CREEK SWITCHING","Jefferson - 14660 Dixie Hwy - Louisville","MC1261","Louisville - Dixie Hwy, Pendleton Rd, & Blevins Gap Rd - NE of Substation",67.760564639337304,3042,"2024-01-13",3.2812737675045243E-3,4.0130671476304156E-2,2.0633427601400259E-2,0,1.6551237436529444E-2,0,0.82019012968843941,6.7563610249660344E-2,0,3.1649649780161902E-2,56.507877212689024,75.4126670950033,0.70636094674556182,1.3579881656804722,"Continue to Monitor"]
["MILL CREEK SWITCHING","Jefferson - 14660 Dixie Hwy - Louisville","MC1262","Louisville - Watson Ln, Galston Blvd, & Dixie Hwy - NE & S of Substation",19.594210388439102,1304,"2024-01-13",1.3119771401219145E-2,0,0.35859257996787142,0,4.7395083530661752E-3,0,0.18442018080480985,0.40520076731443577,0,3.3927192158597658E-2,68.576060830713175,48.506186087423316,1.0523389570552144,1.16180981595092,"Trees Trimmed in 2024"]
["MADISON","Jefferson - 635 E Madison - Louisville","MD1451","Louisville - Madison St, Wenzel St, Baxter Ave, & Lexington Rd - E of Substation",2.1707406700223801,25,"2022-06-03",0,0,0,0,0,0,0,0,0,1,47.946833320000003,35.066666640000001,0.47000000000000003,0.8,"Continue to Monitor"]
["MADISON","Jefferson - 635 E Madison - Louisville","MD1452","Louisville - Clay St, E Main St, & River Rd - N of Substation",9.0630650380114393,537,"2022-06-03",0,0.13662327072432717,0.33499882083484894,0,0.21113051959212878,0,7.230880536580101E-3,9.3118072404737448E-2,0,0.21689843590737759,172.03994413081935,301.9128491582868,1.5656424581005588,3.0055865921787714,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG0407","Louisville - Chestnut St, Quest Dr, & Muhammad Ali Blvd - NE of Substation",5.9321016744383899,661,"2023-03-17",0,0,0,0,0,0,0,0.51581655338880772,0,0.48418344661119228,196.99062027080183,190.5351739773071,1.350226928895613,1.913767019667171,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG0411","Louisville - W Broadway, 15th St, Garland Ave, & 16th St  - SW of Substation",4.0379483830736298,387,"2023-03-17",0,0,0,0,6.8613773071381197E-3,0,4.3409647096493836E-3,3.732589255083137E-3,0,0.98506506872812938,168.4148148113695,564.89388457622738,0.62403100775193798,1.1343669250645996,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG0451","Louisville - W Broadway - S of Substation",0.78512353722081796,33,"2023-03-17",0,0,0,0.5535714285714286,0,0,0,0,0,0.44642857142857145,15.609090901515152,50.922222212121213,0.18939393939393939,0.69696969696969691,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG0454","Louisville - W Broadway & S 9th St - SE of Substation",0.84614115676283996,4,"2023-03-17",0,0,0,0,0,0,0.35195530726256985,0,0,0.64804469273743015,59.659374937500004,44.670833250000001,0.5,1,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG1328","Louisville - 15th St, 13th St, 12th St, 11th St & W Kentucky St - S of Substation",5.6674838380630002,1288,"2023-03-17",1.6341717891666982E-4,0,0,0,2.228758909378889E-2,1.6341717891666982E-4,3.5951779361667359E-3,0.13552312353081672,0,0.83826727508139431,38.520733047166146,60.387163559006204,1.2901785714285716,1.0225155279503104,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1292","Louisville - Outer Loop & National Tpike - NE of Substation",17.188371343219,1389,"2021-10-30",2.8895744829321619E-3,0,0,3.1549543567762793E-3,0.41558488243988773,0,6.7085071694857551E-3,0.45502709835126148,0,0.11663498319965659,73.4152387773578,115.94540436069111,0.73920086393088569,1.0525557955363571,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1293","Louisville - Manslick Rd and Brown Austin Rd - SE of Substation",20.137766958768399,1646,"2022-05-06",8.682723907400965E-3,0,1.5115298263705513E-2,0,8.5200323380780867E-3,0,0.79408503512886419,0.1656976089345204,0,7.8993014274308E-3,88.374374742861491,214.2388821318348,0.69441069258809229,1.7582017010935602,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1295","Louisville - Outer Loop, New Cut Rd, & Scottsdale Blvd - NE of Substation",19.413683306947,1802,"2022-03-25",0.41437845397892181,0,0,1.2995934129179584E-4,8.1688728811985965E-4,0,5.975035429391852E-2,0.28294005161242408,0,0.24198429348532388,38.427108765399559,89.672308541620424,0.56132075471698117,0.72142064372918979,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1297","Louisville - Outer Loop & National Tpke - NE of Substation",8.2712388879625092,622,"2022-03-25",1.2940827135685331E-2,0,0,0,1.3410398237727276E-2,0,1.8551511259348261E-2,0.81771664146174727,0,0.13738062190549191,55.477264198151126,142.64370310289391,0.55546623794212213,1.0385852090032153,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1299","Louisville - Arnold Town Rd, Timber Hills Rd, & St Andrews Church Rd - NW of Substation",17.784795511386701,788,"2024-01-01",0.27035636483209341,1.4351870881115815E-2,0,5.622919149985614E-2,2.1579185334374613E-3,0,0.32730486250976204,0.189437845095702,0,0.14016194664803322,83.349661583439087,104.02313873730964,0.62531725888324863,0.97461928934010134,"Continue to Monitor"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1282","Louisville - Mud Ln, Blue Lick Rd, Vanguard Dr & Caven Ave - NW of Substation",30.28652927572,2623,"2019-10-05",0.13433398211952485,0,0,0,2.487706495632892E-2,0,0.22140777567539727,0.16161824263880681,0,0.45776293460994216,67.985973433568432,111.37985765764392,0.93528402592451332,1.844071673656116,"Continue to Monitor"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1284","Louisville - Christman Dr, Mount Washington Rd, & Cedar Creek Rd- E of Substation",58.035700116635098,3110,"2019-08-24",1.5794306183745332E-2,0,4.2584075253559165E-4,0,3.1621151694096378E-2,0,9.4089585010405513E-2,0.54073570002702176,0,0.31733341633219542,40.224744101286177,89.60991960836013,0.70426045016077166,1.4855305466237942,"Continue to Monitor"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1286","Louisville - Overdale Dr, Blossom Rd, Summers Dr, & Summit Dr - SW of Substation",27.0563279469938,2652,"2023-10-07",2.9373243532425555E-2,0,0.1691965719376603,0,0.3135129055506965,0,8.103984360316523E-3,0.46655034578085208,0,1.3262948838049064E-2,40.925282802507539,54.561601305429861,0.77347285067873295,0.44758672699849156,"Continue to Monitor"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1288","Louisville - Preston Hwy, Hebron Ln, & Bells Mill Rd - S of Substation",39.1598250750977,1682,"2019-08-03",6.9724924720995334E-3,0,0.42314513353979727,0,1.0040243119923402E-3,1.8254987490769821E-5,0.19297164726617871,7.3081104171173361E-2,0,0.30280734325126801,97.645885348246139,103.01767736385256,1.2932520808561239,0.92984542211652776,"Continue to Monitor"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1289","Louisville - Holgate Dr, 1st, 2nd, & 3rd St - SE of Substation",6.3246632429217602,803,"2023-11-04",0.16135464938419877,0,0.56423707497252407,0,0,0,1.9828006208998518E-3,0.26396741408808166,0,8.4580609342956529E-3,102.88209318804483,191.46448733374842,1.1158156911581569,1.1594022415940224,"Continue to Monitor"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1264","Louisville - Six Mile Ln & Klondike Ln - W of Substation",8.6537210565208902,1225,"2021-07-24",7.9218833416570518E-4,0,0,2.3541770713141716E-2,0.49065734410250228,1.8633647338419414E-2,0.34883841080131572,0,0,0.11753663871045517,26.320435372857144,46.412571426938769,0.2385714285714286,0.56816326530612249,"Continue to Monitor"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1267","Louisville - Breckenridge Ln & Bardstown Rd - S of Substation",12.8903409707573,1419,"2021-09-11",2.3951612903225807E-2,0,0,0,0.84071774193548399,0,8.0834677419354836E-2,2.0161290322580645E-2,0,3.4334677419354837E-2,119.50186457293871,322.97746065116286,0.90662438336856954,1.9492600422832984,"Continue to Monitor"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1268","Louisville - Breckenridge Ln, Manner Dale Dr, & Klondike Ln - NW of Substation",14.768371792981499,1947,"2021-07-24",1.267574064197989E-3,1.6463004614278758E-3,3.4858286765444696E-3,0,2.9702970297029702E-2,0,0.76195886567579474,0.13569998686051274,0,6.6238473964492464E-2,53.084041682973812,114.76020372316384,0.32909604519774011,0.6456086286594761,"Reliability Improvements Scheduled for 2025"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1269","Louisville - Wisteria Landing Cir, Beargrass Ave, Bardstown Rd & Fegenbush Ln - SW of Substation",22.8253891265276,2815,"2024-01-01",7.1055435268240711E-3,0,7.7041161173545952E-4,0,0.15952675533560162,0,0.2659065653962035,0.48216310959892772,0,8.4527614530707632E-2,57.211079038632327,75.577033745293065,0.78552397868561263,0.50657193605683837,"Trees Trimmed in 2024"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1271","Louisville - Nachand Ln, Watterson Trl, & Hurstbourne Pky - SE of Substation",21.523364282462701,1569,"2021-08-14",0.23347667570346825,0,3.2766196129756009E-2,0,2.7881649060484247E-2,0,1.4606899130597364E-2,0.58586519584930363,0,0.10540338412639058,11.091833968769917,14.539451877629062,0.17288081580624598,0.23326959847036327,"Continue to Monitor"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1272","Louisville - Six Mile Ln, Raintree Dr, & Stony Brook dr - NE of Substation",19.876424476,1393,"2021-07-24",7.0467541204170869E-2,0,0,0,0.80606410071596757,0,2.2872519340733265E-2,6.7680553553409253E-2,0,3.2915285185719088E-2,11.667166186468057,29.879444839913862,0.1035534816941852,0.17157214644651828,"Continue to Monitor"]
["OLD HENRY","Jefferson - 13601 Terra View Trail - Louisville","OH1170","Louisville - Old Henry Rd, Nelson Miller Pky, & Stanley Gault Pky - W of Substation",8.8888814753199004,149,"2020-11-14",1.4260078956813017E-2,0,0,0,6.199306137097739E-2,0,2.8950831439167363E-3,0.23457351357817921,0,0.68627826295011363,163.08914987751675,280.51085010067106,0.53859060402684567,1.0872483221476512,"Continue to Monitor"]
["OLD HENRY","Jefferson - 13601 Terra View Trail - Louisville","OH1173","Louisville - Old Henry Rd and Factory Ln - NW of Substation",45.658589516487503,2696,"2020-11-21",3.7375352746832433E-3,0,4.833497471667314E-2,0,0,0,0.35025915786493672,0.59171116471959451,0,5.957167424112373E-3,35.741063920623141,44.33986770326409,0.18870548961424333,0.22106824925816024,"Continue to Monitor"]
["OKOLONA","Jefferson - 811 N 27th St. - Louisville","OK1272","Louisville - Outer Loop, Shepherdsville Rd, & Applegate Ln - E of Substation",18.5665494814079,1690,"2023-11-04",8.9070821590458538E-2,0,0.142961240476216,0.19076501034087379,7.2332536782434443E-3,0,3.0186778683869309E-2,0.20043078044128204,0,0.33935211478905691,43.242147432248522,44.358382640828395,0.6868343195266271,0.90887573964497037,"Continue to Monitor"]
["OKOLONA","Jefferson - 811 N 27th St. - Louisville","OK1274","Louisville - Preston Hwy, Miles Ln, & Cooper Ave - S of Substation",13.5341588026732,1546,"2023-11-11",5.2919365086941091E-3,0,0,0.1671255596953706,0.19712016036894403,3.2813586017832691E-4,3.3341586447392366E-2,0.59088020952966203,0,5.9124115897585816E-3,40.772536650064687,90.294663644890051,0.64003880983182415,0.59249676584734801,"Continue to Monitor"]
["ORMSBY","Jefferson - Rear of 436 E Ormsby Jackson St - Louisville","OR0001","Louisville - Jackson St, Oak St, & Preston St - N of Substation",2.4576837641146798,589,"2020-02-29",0,1.0675425990556354E-2,0.22175771262201152,0,0.52365577350180104,0,7.0920662175024728E-3,0.23681902166812863,0,0,33.39115732640068,70.793718162988128,0.23853989813242782,0.23938879456706283,"Continue to Monitor"]
["ORMSBY","Jefferson - Rear of 436 E Ormsby Jackson St - Louisville","OR0002","Louisville - E Ormsby Ave - E of Substation",0.388605961654992,137,"2020-02-29",0,0,0,0,0,0,0,0,0,1,4.6223540145985407,18.489416058394163,7.1167883211678828E-2,0.28467153284671531,"Continue to Monitor"]
["OXMOOR","Jefferson - 8004 Shelbyville Rd - Louisville","OX1273","Louisville - Shelbyville Rd, Lyndon Rd, & Hurstbourne Club Ln - E of Substation",25.615972860564899,1981,"2024-01-01",0.2010047393364929,0,0.17338388625592416,0,6.1232227488151655E-3,0,0.16663507109004738,5.7251184834123225E-2,0,0.39560189573459714,33.791841238011102,26.628377918727914,0.30716809692074715,0.37607269056032311,"Continue to Monitor"]
["PIRTLE","Jefferson - Rear 1506 W Main St - Louisville","PI0003","Louisville - Main St, 15th St, Rowan St, & Portland Ave - NW of Substation",5.211806488193,560,"2023-03-24",0,0,0,0,8.1623390408702604E-2,0,0.76221239650666539,0.15578354794550631,0,3.8066513912578785E-4,76.130282731250006,48.751785705357143,0.38258928571428574,0.42142857142857149,"Continue to Monitor"]
["PLEASURE RIDGE","Jefferson - 4400 Atlas Power Rd. - Louisville","PL1276","Louisville - Dixie Hwy, Cofer Ave, and Fury Way - W of Substation",2.83456642769006,1896,"2023-09-09",3.8026169629403417E-2,0,8.7791421543128873E-3,0,0.20240352508062648,0,0.44375945955923068,0.23713416046097208,0,6.9897543115454444E-2,31.121112428401897,68.936014414556965,0.27109704641350213,0.41877637130801693,"Continue to Monitor"]
["PLEASURE RIDGE","Jefferson - 4400 Atlas Power Rd. - Louisville","PL1277","Louisville - Dixie Hwy, Lower Hunters Trace, & Upper Hunters Trace - N of Substation",2.2435214470361098,723,"2023-09-09",0.14695100722911306,0,0,0,5.938931401929129E-4,0,0.49979179608303581,0.34273777911270997,0,9.9255244349482213E-3,59.653838170816037,202.56521437621021,0.44813278008298757,1.5753803596127247,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1380","New Albany - Bells Ln & Algonquin Pky - NE of Substation",2.2529705026469,2,"2021-11-13",0,0,0,0,0,0,0,0,0,1,83.07916625,183.691666,1.125,1.5,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1389","New Albany - Campground Rd & Senn Rd - S of Substation",4.7041595968532102,7,"2021-11-13",0,5.6721750781598926E-2,0,0,0,0,0,0.94327824921840109,0,0,147.91726174999999,319.81666642857147,1.214285714285714,1.8571428571428568,"Continue to Monitor"]
["PLAINVIEW","Jefferson - 9900 Shelbyville Rd - Louisville","PV1254","Louisville - Hurstbourne Pky & Whittington Pky - W of Substation",6.8851301554014901,931,"2024-01-01",4.4563506349576107E-2,0,0.89496904625766782,0,0,0,4.3765838645235524E-3,1.6496897566760552E-2,0,3.9593965961471946E-2,9.323097921589687,15.981614750805582,0.10848549946294307,0.17185821697099893,"Continue to Monitor"]
["PLAINVIEW","Jefferson - 9900 Shelbyville Rd - Louisville","PV1257","Louisville - US 60 and Moser Rd - E of Substation",1.84419464133546,1341,"2020-01-18",4.22106583654695E-2,0,0,2.318450030200251E-2,0.14730753147795381,0,0.10642103795939228,9.9289132555870463E-2,0,0.58158713933931139,17.842303626771066,32.098558287844888,0.18158090976882924,0.31096196868008946,"Continue to Monitor"]
["SEVENTH STREET","Louisville - 1231 S 7th St - Louisville","SE0003","Louisville - 7th St, Hill St, 6th St, & Shipp Ave - S of Substation",3.9738621847696098,409,"2019-12-21",1.0328413615543514E-2,0,2.9338682154297518E-3,0,5.1791755231566025E-3,0,0.23761338801904019,0.31317546328174117,0,0.43076969134508875,52.979839033618589,76.669030146699271,0.47860635696821519,0.38386308068459662,"Tree Trim Scheduled for 2025"]
["SEVENTH STREET","Louisville - 1231 S 7th St - Louisville","SE0004","Louisville - Oak St, Garvin Pl, & 4th St - NE of Substation",1.90848963860736,559,"2019-12-21",0,0,0,0,2.3073921103125304E-2,0,0.41836482487235355,0.55856125402452117,0,0,100.85105843515208,140.51753130411453,0.80456171735241488,0.52415026833631484,"Tree Trim Scheduled for 2025"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1282","Louisville - Berry Blvd, Powell Ave, Wheeler Ave & Southgate Ave - E of Substation",10.3142812643905,2108,"2022-01-01",8.6761956061895944E-3,1.2354838113673607E-2,1.3786026653932358E-4,2.0797476636001048E-3,3.2684726835329941E-2,0,0.74749257757482479,0.15072343477669717,0,4.5850619163145548E-2,49.067443464302663,116.11888835341557,0.73885199240986743,2.2594876660341563,"Reliability Improvements Completed in 2024"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1284","Louisville - Manslick Rd - S of Substation",9.8476909808145692,1538,"2022-01-01",0.58388289520336323,0,0,0,1.1832041736311603E-2,0,0.12716405814719139,2.725016461530669E-3,0,0.27439598845160312,65.314293452698308,60.777481576072816,0.68758127438231476,0.76527958387516248,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1456","Louisville - Dixie Hwy, Ralph Ave, & Fitzgerald Rd - N of Substation of Substation",3.4481732116846202,23,"2021-08-07",1.8745739604635311E-2,0,0,0,0.33588957055214724,0,4.5671438309475121E-2,0.54618268575323792,0,5.3510565780504428E-2,102.43768111956523,115.82681152173915,0.66304347826086951,0.60869565217391308,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1458","Louisville - 7th Street Rd, Arcade Ave, Taylor Blvd, & Berry Blvd - NE of Substation",5.2027839591014997,15,"2021-08-07",0,0,0,0,0,0,0.22285174693106705,0.65155807365439089,0,0.12559017941454201,25.687222200000001,70.5566666,0.16666666666666669,0.2,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1232","Louisville - Tug Rd, Crittenden Dr, Woodlawn Ave, & 1st St - S of Substation",11.3417157730316,1483,"2022-01-14",0.1681309820145146,0,2.3752760929775969E-2,0,2.5979034463415487E-3,0,0.42265189496196054,0.37662588086807136,0,6.2405777793359749E-3,46.755945152730959,117.63481680849631,0.53691840863115303,1.0161834120026974,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1234","Louisville - Whitney Ave, Taylor Blvd, & Ashland Ave - W of Substation",13.6670935414597,2325,"2022-02-04",9.443261553582407E-3,0,0,2.1607543901079517E-4,2.9263880695762915E-2,0,0.87187682552673174,8.6473199474917564E-2,0,2.7267573099946365E-3,37.473374547419354,37.007254476129027,0.56172043010752692,0.91655913978494619,"Reliability Improvements Completed in 2024"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1235","Louisville - Fairmont Ave, 3rd St, 5th St, & 4th St - NW of Substation",12.5106283151162,2267,"2022-01-01",6.8968413575299134E-2,0,2.403419262871432E-2,5.351597559863498E-3,3.3326293862701528E-2,0,0.19830188769804513,0.55199928965341805,0,0.11801832502195835,44.021987571901207,52.736766649757399,0.57862814292015874,0.46493162770180857,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1380","Louisville - Dakota St & Crittenden Dr - S of Substation",2.2580743412406399,1,"2021-08-21",0,0,0,0,0,0,0,0,0,1,325.04583300000002,851.28333299999997,1,1,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1381","Louisville - Dakota St & Crittenden Dr - S of Substation",2.23713117477035,1,"2021-08-21",0,0,0,0,0,0,0,0,0,1,383.79166624999999,852.23333300000002,1,1,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1382","Louisville - Dakota St & Crittenden Dr - S of Substation",2.2361823639936902,1,"2021-08-21",0,0,0,0,0,0,0,0,0,1,622.14166625000007,940.31666600000005,1.5,1,"Continue to Monitor"]
["SHAWNEE","Jefferson - Rear of 3908 W Broadway - Louisville","SN0002","Louisville - Broadway, 37th St, & Lindell Ave - E of Substation",2.43875442436982,541,"2023-03-03",0,0,0,0,0.36521104327050702,0,0.24694717281656489,0.38731085744624372,0,5.3092646668436425E-4,26.859149720887245,27.854805913123844,0.20240295748613679,0.24214417744916819,"Continue to Monitor"]
["SOUTHERN","Jefferson - 1475 S 3rd Street - Louisville","SO0405","Louisville - 3rd St & Ormsby Ave - N of Substation",2.60784401337762,681,"2019-12-31",0,0,0,0,0,0,0.58550422780402889,4.5138025366824173E-2,0,0.36935774682914696,36.43215858773862,94.470925104258441,0.36013215859030834,0.56681350954478704,"Continue to Monitor"]
["SOUTHERN","Jefferson - 1475 S 3rd Street - Louisville","SO0409","Louisville - 3rd St - S of Substation",1.9709796082868101,177,"2019-12-31",0,0,0,0,2.5885039969547011E-2,0.26456033498287018,0,2.7027027027027029E-2,0,0.68252759802055574,18.419161956214687,14.455367231638418,0.1115819209039548,0.1807909604519774,"Continue to Monitor"]
["SOUTHERN","Jefferson - 1475 S 3rd Street - Louisville","SO0451","Louisville - 3rd St & Lee St - S of Substation",2.5418888270352298,540,"2019-12-31",0,0,0,0,0.115611529033894,0,0,0.26934325078184429,0,0.61504522018426167,44.413441356944439,80.041358022222227,0.21481481481481479,0.39814814814814814,"Tree Trim Scheduled for 2025"]
["SOUTH PARK","Jefferson - 1412 Fairdale Rd. - Louisville","SP1115","Louisville - National Tpke, Glengarry Dr, & Grange Rd - NW & S of Substation",22.666816789869699,1527,"2019-10-05",9.9768317405154929E-3,3.0553142195192586E-3,1.6217781639154358E-3,0.22732044598899509,7.7414567043150889E-2,0,0.21220315667535478,0.41613090066608749,0,5.2277005502461629E-2,78.597817065487874,79.614079888670602,0.43925998690242302,0.50163719711853305,"Tree Trim Scheduled for 2025"]
["SOUTH PARK","Jefferson - 1412 Fairdale Rd. - Louisville","SP1117","Louisville - South Park Rd - E of Substation",8.2331780884570094,602,"2019-10-12",2.6803284250525888E-2,0,0,0,5.2181583768745335E-2,0,0.19474791341521341,0,0,0.72626721856551535,10.768646175249168,24.482641189368767,0.33513289036544841,0.21262458471760798,"Continue to Monitor"]
["SOUTHERN BAPTIST SEMINARY","Jefferson - 2845 Seminary Rd - Louisville","SS0002","Louisville - Seminary Rd - N of Substation",0.55606043922354897,6,"No Trimming Required",0,0,0,0,0,0,0,1,0,0,19.775000000000002,79.100000000000009,0.25,1,"Continue to Monitor"]
["SHEPHERDSVILLE","Bullitt - 1706 4th St. - Shepardsville","SV1122","Shepherdsville - HWY 44, Preston Hwy, & Old Preston Hwy - SE of Substation",18.021839984311299,935,"2021-05-15",2.9280207540538423E-3,0,0,5.9167258760673498E-4,5.5207603751305345E-2,9.0419708259901026E-3,8.9231306054024268E-2,0.83340371034339766,0,9.5957156836220473E-3,38.16685382700534,43.620213895187156,0.34197860962566856,0.5679144385026742,"Tree Trim Scheduled for 2025"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1184","Louisville - Romania Dr, Meyers Ln, & Blanton Ln - SW of Substation",16.1043526583748,1450,"2022-09-02",2.0213211216978114E-2,0,1.0545666428671081E-3,0,2.7984998071415089E-3,0,0.82193416549720555,0.15224741692723079,0,1.7521399085768685E-3,32.42774999396552,49.743195398620692,0.56137931034482769,0.39999999999999997,"Continue to Monitor"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1186","Louisville - Gagel Ave, Hazelwood Ave, Bluegrass Ave, & Lonsdale Ave - E of Substation",13.970643921857899,2082,"2022-05-13",8.2960778834982873E-3,0,0,0,5.1188252768423065E-2,0,0.79194363152399294,0.10315776702598567,0,4.5414270798099975E-2,54.399371593900085,53.883149212776175,0.85218539865513931,1.1950048030739673,"Continue to Monitor"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1187","Louisville - San Jose Ave, Dixie Hwy, Sadie Ln, & Estate Dr - NE of Substation",14.275962726860101,1533,"2022-05-13",6.6399596239984857E-3,0,0,4.4161251656046939E-4,5.4859840598910688E-3,0,7.3134187117532015E-2,2.5566210333732887E-2,0,0.88873204634828507,93.814144375407693,237.42332028180041,0.87899543378995437,1.8030006523157212,"Continue to Monitor"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1190","Louisville - Dixie Hwy, Upper Hunters Trace, & Graston Ave - SW of Substation",15.0998004423293,1596,"2022-07-08",4.530188196334272E-2,0,0,2.9564009213942093E-3,0.1773370453750085,0,0.6838583643685785,4.2873036683398709E-2,0,4.7673270688277293E-2,38.524313383928558,111.06343984523807,0.68828320802005005,2.2186716791979948,"Reliability Improvements Scheduled for 2025"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1191","Louisville - Gagel Ave, Manslick Rd, & Parkwood Rd - SE of Substation",17.4759563258255,1362,"2022-07-08",8.5659135229070611E-3,0,0,7.7691830895026872E-4,0.29858428219257949,0,0.36079859843371004,0.30132826142947305,0,2.9946026112380029E-2,77.420955695668127,184.75775819089574,0.63436123348017603,1.4140969162995589,"Reliability Improvements Scheduled for 2025"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1130","Louisville - Hubbards Ln, Shelbyville Rd, & Browns Ln - S of Substation",14.2611881165324,1729,"2024-01-01",9.7809805271041658E-3,0,0,0,6.5818918402019179E-3,5.5812343211010583E-4,0.83258530647230522,0.11857177358448423,0,3.1921924143794266E-2,77.578884707779082,127.89227876749571,0.46833429728166576,0.81781376518218618,"Reliability Improvements Scheduled for 2025"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1133","Louisville - US 42 & Lime Kiln Ln - N of Substation",28.283175832659399,1295,"2024-01-01",1.4916918942854244E-3,5.7265107122294245E-4,5.6646970528102473E-3,0,1.825213519541475E-2,0,0.23664523663551751,0.59268064070052373,0,0.14469294745022543,154.26645107779922,87.944620315830122,2.1895752895752896,3.9081081081081068,"Trees Trimmed in 2024"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1138","Louisville - Brownsboro Rd, Chenoweth Ln, Canoe Ln, & Wampum Rd - W of Substation",11.84810984189,574,"2024-01-01",4.9480091284081918E-5,0,5.7035834953137673E-3,0,7.1470648610445248E-2,0,0.54319377941641567,0.37399794457026203,0,5.5845638162790841E-3,174.77808506358886,186.58455283797909,1.2108013937282232,1.1864111498257841,"Trees Trimmed in 2024"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1172","Louisville - Chenoweth Ln, Cherrywood Rd, & Washington Sq - SW of Substation",10.7348998802021,1126,"2024-01-01",8.602235816050596E-4,0,0,0,0,0,0.92810193562480481,4.1596488701608508E-2,0,2.9441352091981659E-2,94.698590135435168,107.26537891207813,1.2775310834813496,1.3383658969804615,"Reliability Improvements Scheduled for 2025"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1173","Louisville - Hubbards Ln, Rudy Ln, Massie Ave, & Westport Rd - S of Substation",25.952916420356601,2041,"2024-01-01",5.6770035850228447E-4,0,0,0,3.2182805418734355E-3,0,0.93822101696582849,3.4276753924769865E-2,0,2.3716248209025896E-2,66.325206184958347,89.573558707496332,0.6718520333170015,1.2077413032827045,"Continue to Monitor"]
["TERRY","Jefferson - 8408 Terry Ln. - Louisville","TE1243","Louisville - Terry Rd, Greenwood Rd, & Westbrook Rd - N of Substation",19.7002270791155,1799,"2020-09-05",0.12476812185502516,0,4.3059975520195838E-2,4.9770161838705293E-2,1.8057935536515708E-2,9.3023255813953494E-4,0.50328029375764993,5.0746634026927785E-2,0,0.20938664490684075,91.369582635214016,178.027987766537,0.60366870483601986,1.036131183991106,"Continue to Monitor"]
["TERRY","Jefferson - 8408 Terry Ln. - Louisville","TE1245","Louisville - Pages Ln, Poinsettia Dr, Greenwood Rd, & Feyhurst Dr - NE of Substation",23.0110354053093,2374,"2020-09-12",2.0813361294188138E-2,0,0,0,0.11900838825644099,0,9.4600059916117446E-2,6.8506590772917916E-2,0,0.6970715997603355,46.211383737784331,51.578124120050553,0.92175652906486905,0.63816343723673119,"Continue to Monitor"]
["TERRY","Jefferson - 8408 Terry Ln. - Louisville","TE1246","Louisville - Trade Port Dr - SW of Substation",2.5947378043646601,28,"2020-09-19",0,0,0,0,0,0,0,0,0,1,46.344494026785711,101.47797617857142,0.75892857142857151,1.0714285714285716,"Continue to Monitor"]
["TIP TOP","Meade - US 60 - Tip Top","TT3313","Tip Top - US 60, Baker Rd, & Eisenhower Ave - E of Substation",6.9005368970346099,2,"2020-02-15",0,0,0,0,0.44367816091954021,0,0.55632183908045973,0,0,0,219.58333299999998,217.64999949999998,1.375,2,"Continue to Monitor"]
["VERMONT","Jefferson - Rear 529 Southwestern Pkwy - Louisville","VE0001","Louisville - Southwestern Pky - N of Substation",2.1237478391733702,264,"2023-02-03",0,0,0,0.1217136990137208,0,0,0,0.80977567592794242,0,6.8510625058336702E-2,27.343639514204547,42.493181814393942,0.19981060606060605,0.32196969696969691,"Continue to Monitor"]
["VERMONT","Jefferson - Rear 529 Southwestern Pkwy - Louisville","VE0002","Louisville - River Park Dr, 44th, 43rd, & 42nd St - SE of Substation",1.2005798226870801,314,"2023-02-03",0,0,0,0.65036122210114222,0,0,0,0.34963877789885783,0,0,27.678463374203822,102.63566878980892,0.15207006369426751,0.39490445859872614,"Continue to Monitor"]
["WESTERN","Jefferson - 2807 W Broadway - Louisville","WE0001","Louisville - 28th St, Chestnut St, 26th St, & Muhammad Ali Blvd - NE of Substation",5.1123030636287803,893,"2022-11-04",0,0,0,0.71012769704975787,7.597240569499486E-2,3.8896227799794509E-3,0.17218552766769413,1.6439160428592396E-3,0,3.6180830764714518E-2,55.656275657614771,76.2918066394177,0.55599104143337075,0.77827547592385227,"Continue to Monitor"]
["WESTERN","Jefferson - 2807 W Broadway - Louisville","WE0002","Louisville - Broadway, Louis Coleman Jr Dr, & 35th St - W of Substation",2.85957507387399,429,"2022-11-04",0,0,9.5350875843932148E-4,0,0.83122894975624007,0,5.2765944358150192E-2,0.11505159712717039,0,0,210.34725135606061,139.6322843776224,0.91724941724941744,0.94172494172494181,"Continue to Monitor"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1177","Louisville - Ballardsville Rd, Murphy Ln, & Tazwell Dr - E of Substation",27.068253765300302,2393,"2021-08-28",0.1161823093718775,9.4580520325031319E-3,0,0,1.242393643173972E-3,0.49054459135822703,0.14768095331243292,6.8728158984092077E-4,0,0.23420441869194453,26.063511629857921,78.557034402841623,0.26243209360635184,0.82156289176765551,"Continue to Monitor"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1178","Louisville - Chamberlain Rd, Sweet Water Dr, & Shenandoa Dr - E of Substation",11.7747356299417,713,"2024-01-01",0.18058743517810083,0,0,0,0,0,3.6130238884638274E-2,0.78328232593726088,0,0,34.255078303997195,65.993571755960744,0.61430575035063106,1.2636746143057505,"Trees Trimmed in 2024"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1180","Louisville - Brownsboro Rd, Norton Health Care Blvd, & Summit Plaza Dr - W of Substation",8.3664679265457806,179,"2021-10-02",0,0,5.1158591634065604E-3,0,0.35359614805898287,0,0,0,0,0.64128799277761062,11.653514892458102,18.564711346368718,0.31983240223463688,1.2011173184357542,"Continue to Monitor"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1181","Louisville - Chamberlain Ln - S of Substation",7.9919518359917401,989,"2021-08-28",0.93769440891794165,0,0,0,3.7768619834841234E-2,0,2.4536971247217092E-2,0,0,0,49.987693796258846,64.036029658240636,0.50808897876643078,0.52881698685540945,"Continue to Monitor"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1182","Louisville - Brownsboro Rd, Park Plaza Ave, & Ten Broeck Way - W of Substation",18.558771258037101,1024,"2024-01-01",0,0,1.0333489901362142E-3,0,0.41957726632221704,0,0.24334429309534994,0.33454830123688745,0,1.4967903554094254E-3,42.005521643066409,107.10275064648438,0.626220703125,1.943359375,"Trees Trimmed in 2024"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1183","Louisville - Ballardsville Rd, Haunz Ln, & Hitt Ln - NE of Substation",34.312313679499198,1409,"2021-10-23",5.3490411488353096E-2,1.3381020910407185E-3,0,0,0,0,0.65413135360592156,0.16487789452417589,0,0.12616223829050871,85.104415062455629,89.616879580553572,0.73119233498935421,0.3286018452803407,"Continue to Monitor"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1184","Louisville - Brownsboro Rd & Worthington Ln - N of Substation",45.625924534929801,2947,"2021-10-23",9.5568223997119384E-3,0,0,0,9.3923217405994783E-2,0,0.20530150849817311,0.24785464751356145,0,0.44336380418255872,30.61982241711911,88.905678088564656,0.12792670512385479,0.32100441126569396,"Continue to Monitor"]
["WEST POINT","Hardin - Crop St and I-C Railroad - West Point","WP1104","West Point - Main St, Dixie Hwy, 16th St, & Private Rd - W, SW & NE of Substation",24.3820815975178,700,"2019-02-09",6.3866748416104631E-4,2.5060095568985822E-4,6.2127139840199314E-3,5.8818234017498274E-3,7.33822856753574E-2,0,0.64398849668622815,0.2687257306356019,0,9.1968117719190676E-4,126.11336903642855,186.67045236714281,1.4324999999999994,3.0671428571428554,"Continue to Monitor"]
["WATERSIDE WEST","Jefferson - 221 North Third St. - Louisville","WS1319","Louisville - 3rd St, Jefferson St, 8th St, & Broadway - SW of Substation",2.4256124451162799,18,"2023-03-24",0,0,0,0,5.6052344601962921E-2,0,0,0,0,0.94394765539803704,76.650462944444442,254.75740733333333,0.31944444444444442,1.0555555555555556,"Continue to Monitor"]
["WATERSIDE WEST","Jefferson - 221 North Third St. - Louisville","WS1322","Louisville - Main St, 13th St, Market St, 10th St, & Portland Ave - W of Substation",5.7386083958586402,181,"2023-03-24",0,0,0,0,1.2317256532645416E-2,0,0,0.92446915811457864,0,6.3213585352775978E-2,57.097490781767952,135.69438304972374,0.67403314917127066,1.4419889502762431,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1152","Louisville - Bardstown Rd, Seatonville Rd, & Fern Creek Rd - SE of Substation",28.986880446659999,2628,"2021-11-13",8.0998979109085933E-3,0,0,0,6.7480889420084164E-2,0,0.36881053758621546,0.16934214785488408,0,0.38626652722790766,80.824946089707026,70.023795025114168,1.1396499238964992,1.4764079147640792,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1153","Louisville - Bardstown Rd, Watterson Trl, & Woodhaven Rd - W of Substation",19.496095354306998,1099,"2021-09-18",4.455349018588327E-3,0,4.439100480956714E-2,0,3.7433380995710391E-2,0,0.24659430651241387,0.631577408033277,0,3.5548550630443258E-2,40.141719739080983,46.020548976342127,0.28275705186533207,0.37761601455868965,"Reliability Improvements Scheduled for 2025"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1154","Louisville - Walt Lee Rd, Fairground Rd, Billtown Rd, & Easum Rd - E of Substation",44.461616195064799,2891,"2021-12-25",4.6272407454021882E-3,1.7215475875302258E-5,6.0430973153628581E-3,3.9549066200018703E-5,6.0142497611934331E-3,0,0.33471258763026185,0.16942028978764012,0,0.47912577021806424,50.934365267208591,87.684549746800457,0.5749740574195783,1.1432030439294365,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1210","Louisville - Bardstown Rd, Hudson Ln, Fairground Rd & Janet Lee Dr - SE of Substation",22.312724959679102,1971,"2024-01-01",1.3924294784216026E-3,6.9436631037531139E-5,4.0898497146990278E-3,0,1.2560636502451176E-2,0,0.9399611026279836,2.9752632001928798E-2,0,1.2173913043478261E-2,89.317897002156286,129.39353965296806,0.6798579401319127,0.80263825469304939,"Reliability Improvements Scheduled for 2025"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1212","Louisville - Stony Brook Dr, Guttenberg Rd, & Billtown Rd - NE of Substation",25.03257207011,1439,"2021-09-25",1.2340293266006119E-2,0,0,0,9.5126047670721928E-2,0,6.2546691896195397E-3,2.451426795286368E-2,0,0.86176472192078868,23.228283527797082,36.705374099374566,0.26737317581653924,0.33425990271021544,"Continue to Monitor"]

{"sheet":"LGE Section 6-7","index":2,"n_rows":31,"n_cols":1,"rows_kept":31,"cut":false,"hidden":false,"merged":[[15,0,15,3],[0,0,0,8],[2,0,2,8],[4,0,4,8],[5,0,10,8],[11,0,14,8],[30,0,33,8],[20,0,21,8],[29,0,29,8],[16,0,16,3],[17,0,17,3],[18,0,18,3],[19,0,19,3],[26,0,27,8],[23,0,24,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
[]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 6: VEGETATION MANAGEMENT PLAN REVIEW"]
["The Companies’ Vegetation Management Plan went into effect January 1, 2024 and is reflected in this reporting period (see attached).  The Distribution Vegetation Management Program encompasses right of way maintenance for Louisville Gas and Electric Company and Kentucky Utilities Company (referred to as the “Companies”).  The program is centralized and managed by a Forestry Manager and eight company Utility Arborists.  All are certified arborists by the International Society of Arboriculture."]
[]
[]
[]
[]
[]
["The Companies’ plan is to maintain a proactive trim cycle while balancing the reactive needs of worst performing circuits. The Companies’ goal is to maintain an average trim cycle of five years or less.   The effectiveness of the plan is evaluated by the cycle and system performance as measured by system SAIDI, SAIFI, and CAIDI.  "]
[]
[]
[]
["Effectiveness of the program"]
["KU/LG&E Tree Cycle – 5.03 years"]
["LGE Tree SAIDI – 22.24 minutes"]
["LGE Tree SAIFI – 0.172"]
["LGE Tree CAIDI – 128.9 minutes"]
["The hazard tree program, mid cycle, herbicide, and worst performing circuits were completed as planned.  "]
[]
["Adjustments made to the tree plan in 2024 included"]
["Our vegetation management approach leverages unit-based, target pricing, and time-and-expense models to drive efficiency and accountability in contractor operations. The target price strategy deploys prescriptive tree management techniques. Maintenance work is prescribed ensuring that each work segment is clearly defined, mapped, and costed in advance. All work areas are inspected post-completion to verify standards have been met.\nContractor performance is systematically evaluated on a quarterly and annual basis, with a focus on safety, productivity, quality, and customer satisfaction. Compliance with OSHA and internal safety standards is mandatory, and contractors are held to the highest operational standards."]
[]
["Changes to be implemented in 2025"]
["The routine trimming cycle plan is a proactive plan to trim work areas based on time since trim and clearance thresholds. Danger trees are prioritized and mitigated based on reliability disruption potential."]
[]
[]
["SECTION 7: UTILITY COMMENTS"]
["Rolling average SAIDI and SAIFI improved in 2024 compared to the previous 5 year average excluding major events.  251 Circuits were above their previous 5 year average SAIDI and/or SAIFI in 2024.  "]