{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["KU Section 1-4","Excel KU Section 5","KU Section 6-7"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"KU Section 1-4","index":0,"n_rows":46,"n_cols":8,"rows_kept":46,"cut":false,"hidden":false,"merged":[[36,1,36,3],[36,6,36,8],[37,0,37,8],[41,1,41,8],[38,1,38,8],[39,1,39,8],[40,1,40,8],[44,0,44,8],[45,2,45,6],[20,0,21,8],[24,0,24,8],[25,2,25,6],[26,0,26,1],[26,5,26,6],[28,3,28,5],[29,1,29,3],[29,6,29,8],[30,1,30,3],[30,6,30,8],[31,1,31,3],[31,6,31,8],[34,1,34,3],[34,6,34,8],[35,1,35,3],[35,6,35,8],[33,3,33,5],[18,0,18,3],[18,5,18,8],[17,0,17,3],[17,5,17,8],[6,0,6,3],[6,5,6,8],[7,0,7,3],[7,5,7,8],[10,0,10,8],[11,0,11,3],[11,5,11,8],[14,0,14,8],[15,0,15,3],[15,5,15,8],[16,0,16,3],[16,5,16,8],[5,0,5,3],[5,5,5,8],[0,0,0,8],[1,0,1,8],[3,0,3,8],[4,0,4,3],[4,5,4,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 1: CONTACT INFORMATION"]
["UTILITY NAME",null,null,null,null,"KENTUCKY UTILITIES COMPANY"]
["REPORT PREPARD BY",null,null,null,null,"Karmen Powell (Mgr Investment Strategy & Reliability)"]
["E-MAIL ADDRESS OF PREPARER",null,null,null,null,"Karmen.Powell@lge-ku.com"]
["PHONE NUMBER OF PREPARER",null,null,null,null,"(502) 399-4805"]
[]
[]
["SECTION 2: REPORTING YEAR"]
["CALENDAR YEAR OF REPORT",null,null,null,null,2024]
[]
[]
["SECTION 3: MAJOR EVENT DAYS (MED)"]
["TMED",null,null,null,null,3.585]
["FIRST DATE USED TO DETERMINE TMED",null,null,null,null,"2019-01-01"]
["LAST DATE USED TO DETERMINE TMED",null,null,null,null,"2023-12-31"]
["NUMBER OF MED IN REPORTING YEAR",null,null,null,null,9]
[]
["NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years.  If five years of data are not available, then utilities should use what is available until five years are accumulated.        \n"]
[]
[]
[]
["SECTION 4: SYSTEM RELIABILITY INFORMATION AND RESULTS"]
[null,null,"System-wide Information"]
["TOTAL CUSTOMERS",null,559358,null,null,"TOTAL CIRCUITS",null,1122]
[]
[null,null,null,"Excluding MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",69.881682684460841,null,null,null,"SAIDI",76.927584047431722]
["SAIFI",0.63432964275779347,null,null,null,"SAIFI",0.67517533721736656]
[]
[null,null,null,"Including MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",378.98362836381602,null,null,null,"SAIDI",564.24411682224684]
["SAIFI",0.94287455445347335,null,null,null,"SAIFI",1.1232514265234352]
["Notes:  "]
["1)","All duration indices (SAIDI) are to be reported in units of minutes."]
["2)","Reports are due on the first business day of May of each year"]
["3)","Reports cover the calendar year ending in the December before the reports are due."]
["4)","IEEE 1366 (latest version) is used to define SAIDI, SAIFI, and TMED"]
[]
[]
["SECTION 5: CIRCUIT REPORTING"]
[null,null,"BEGIN ON NEXT PAGE"]

{"sheet":"Excel KU Section 5","index":1,"n_rows":495,"n_cols":22,"rows_kept":495,"cut":false,"hidden":false,"merged":[]}
["Substation Name","Substation Location   \n(County - Road - Town)","Circuit\nNumber","Circuit Location\n (Town - Road - General Area)","Total Circuit Length (Miles)","Average 2024 OMS Custs","Date of Last Circuit Trim (VM)","Animal","Construction","Lightning","Non-Company","Other/Unknown","Overload","Planned Work","Trees","Vehicle","Utility Equipment","2020-2024 SAIDI Average","2024 SAIDI","2020-2024 SAIFI Average","2024 SAIFI","LIST OF CORRECTION ACTION, IF ANY, TAKEN OR TO BE TAKEN"]
["LEXINGTON PLANT","Fayette - 745 N Limestone - Lexington",1,"Lexington - N. Broadway - SW of Station",2.98674212691901,529,"2023-04-01",0,0,2.5062083110851195E-2,0,0.71937162568757573,8.9247120445472804E-3,1.5929721070965443E-2,0.20659055658674261,0,2.412130149931772E-2,114.32202267958412,357.22599243289221,0.52930056710775053,1.2438563327032139,"Continue to Monitor"]
["LEXINGTON PLANT","Fayette - 745 N Limestone - Lexington",3,"Lexington - N. Upper St. and 6th St. - W of Station ",4.2188198292764696,580,"2023-04-01",0,0,0,0,0,1.52484742907506E-3,2.8538892802191553E-2,0.96723703850957943,0,2.6992212591539682E-3,39.879353445689652,46.230977008620691,0.30129310344827587,5.1724137931034482E-2,"Continue to Monitor"]
["LEXINGTON PLANT","Fayette - 745 N Limestone - Lexington",4,"Lexington - Loudon Ave and Bryan Ave. - E of Station",4.06736010631111,652,"2023-04-01",0,0,0,0,9.6562169762804252E-5,0,0.88578865253459416,0.11313614397961995,0,9.7864131602302734E-4,28.348383177147237,36.710046009202458,0.17983128834355827,0.1303680981595092,"Continue to Monitor"]
["BUCHANAN","Fayette - 108 Buchanan St. - Lexington",5,"Lexington - W. Main St. and Jefferson St. - E of Station",5.0756541404112996,622,"2023-08-05",0,0,0,0,0,0,0.50928293496386878,0.49071706503613116,0,0,17.599310019694535,28.920953909967846,0.19332797427652734,7.2347266881028938E-2,"Continue to Monitor"]
["AMERICAN AVENUE","Fayette - 96 Burley Ave. - Lexington",8,"Lexington - University Dr. - University of Kentucky Campus",5.19566823254178,753,"2019-07-20",9.1889914967541366E-3,0,0,0,6.4002925848038767E-5,0,3.3967267075066289E-2,5.8937551430922559E-2,0,0.89784218707140895,10.078458386454184,29.696325803452854,0.32536520584329343,1.1766268260292163,"Continue to Monitor"]
["AMERICAN AVENUE","Fayette - 96 Burley Ave. - Lexington",9,"Lexington - Nicholasville Rd. - S of Station",7.3978492595189804,896,"2019-07-20",2.4372315198995802E-3,3.0917185412754193E-3,0,0,0.29327368058591241,0,0.61215294482527882,8.9044424527633767E-2,0,0,130.52812964481024,175.55016740290176,0.3875558035714286,0.5569196428571429,"Continue to Monitor"]
["BUCHANAN","Fayette - 108 Buchanan St. - Lexington",10,"Lexington - Manchester St. - S of Station",4.0812507303677403,442,"2023-08-05",0,0,0,2.5655021834061136E-2,0.8973799126637555,0,7.6965065502183405E-2,0,0,0,9.3421851419683257,12.432692305429866,0.1165158371040724,0.28054298642533937,"Continue to Monitor"]
["LEXINGTON WATER COMPANY","Fayette - 2300 Richmond Rd. - Lexington",11,"Lexington - Richmond Rd and Holiday Rd - NW of Station",3.3606982676313599,154,"2022-05-06",0,0,0,0,0.23991621461947474,0,7.250657930071433E-2,0.68757720607981099,0,0,68.047727266233764,8.7666666623376628,0.55844155844155852,1,"Continue to Monitor"]
["RACE STREET","Fayette - 420 Corral St - Lexington",14,"Lexington - Race St. and E Third St. and Chestnut Street - N of Station",6.1028224689655097,947,"2023-12-23",0,0,0,0,0.26275855403054321,0,0.58732843611057417,0.14302629035375991,0,6.886719505122753E-3,25.723710838437171,43.699683209081307,0.16552270327349519,0.22492080253431887,"Continue to Monitor"]
["RACE STREET","Fayette - 420 Corral St - Lexington",15,"Lexington - Coral St & Forrest Ave. - SE of Substation",3.09902190653,520,"2023-12-23",0,0,0,0,0,0,0.99979127740741391,0,0,2.0872259258607293E-4,27.962916663942309,76.048076917307696,0.13317307692307692,0.35576923076923073,"Reliability Improvements Completed in 2024"]
["LEXINGTON WATER COMPANY","Fayette - 2300 Richmond Rd. - Lexington",16,"Lexington - Fontaine Rd - W of Substation",3.6940523008116899,702,"2024-01-01",0,0,0,0,0.71325391078030476,0,8.2723961254281039E-2,0.20247959533701043,0,1.5425326284037265E-3,51.635392923789169,160.01498100427347,0.45370370370370378,1.0897435897435899,"Continue to Monitor"]
["SCOTT STREET","Fayette - 301 Scott St. - Lexington",18,"Lexington - Limestone St. - SE of Substation",3.2111416429463699,886,"2019-07-20",0,0,0,0,0.58851674641148322,0,0.37562915553346177,0,0,3.5854098055054996E-2,12.627135063487586,18.16337471670429,9.5654627539503378E-2,0.14334085778781039,"Continue to Monitor"]
["HIGBY MILL DISTRIBUTION","Fayette - 308 Waveland Museum Ln. - Lexington",23,"Lexington - Nicholasville Rd - S of Substation",58.218248382889001,1783,"2019-01-19",3.0519052896222035E-3,4.6271269829924631E-3,1.472173049552866E-2,1.6446147195099187E-4,7.7890896120721656E-2,0,0.26349295348516061,8.9690486285509283E-2,0,0.54636043986851413,156.12756355328099,243.31148811665727,2.0267807066741454,2.8928771733034226,"Continue to Monitor"]
["LANSDOWNE","Fayette - 3200 Montavesta Rd. - Lexington",24,"Lexington - Old Mt. Tabor Rd & Turkeyfoot Rd. - N of Substation",23.756755072880001,1888,"2024-01-01",7.0662683229759625E-3,0,0,5.5787330582485204E-3,2.244761678959927E-3,4.2687449563554813E-5,0.26692407833174181,0.7164982370355224,0,1.6452341229877081E-3,220.40340968670554,171.12071856514837,1.4576271186440681,1.8771186440677965,"Trees Trimmed in 2024"]
["JOYLAND","Fayette - 2375 Paris Pike - Lexington",25,"Lexington - Beverly Ave. & Bryan Station Rd. - SW of Substation",28.441641824761302,1706,"2020-04-04",3.1911922669494333E-3,0,0,6.3113749417747838E-4,6.115303679939631E-4,0,0.71052038902658043,0.25527047500647831,0,2.9775275837820452E-2,69.59880567980656,158.69848572919108,0.75952520515826505,1.8294255568581479,"Continue to Monitor"]
["RACE STREET","Fayette - 420 Corral St - Lexington",31,"Lexington - Corral St. & MLK Blvd. - NE of Substation",2.8423651249409199,588,"2023-12-23",0,0,0,0,5.5065180977350518E-2,1.2205957322846114E-2,0.9318257956448911,9.030660549122424E-4,0,0,65.712280323129235,233.51927435544212,0.54846938775510201,1.9234693877551021,"Reliability Improvements Completed in 2024"]
["GE LAMP WORKS","Fayette - 1809 Edision Dr - Lexington",32,"Lexington - Edision Dr. - Rosemont Garden",2.1472830905308555,285,"2020-05-09",8.6814806140273829E-2,0,0,0,0.79915293107318164,0,5.8055449834587346E-2,3.6683549492051409E-2,0,1.929326345990573E-2,33.577748531578948,46.01140350175438,0.26403508771929823,0.42105263157894735,"Continue to Monitor"]
["BELT LINE","Fayette - 1090 W. New Circle Rd - Lexington",36,"Lexington - Georgetown St. & Briarwood Dr. - NW of Substation",7.0585487731349001,566,"2024-01-01",4.9918265696826075E-4,0,0,0,7.3684297139847942E-3,0,1.6953011003960548E-2,0.97242290096435513,0,2.7564756607313299E-3,48.519662832597177,54.86843344699647,0.31492932862190809,0.43816254416961137,"Trees Trimmed in 2024"]
["HUGHES LANE","Fayette - 251 Hughes Ln. - Lexington",37,"Lexington - Mir Station Rd. & US 27 - SW of Substation",139.46108901641301,1119,"2019-12-31",1.8041173635080978E-3,1.4443494446027775E-3,4.486103634271721E-3,0,0.27100596036043645,4.0902709606595098E-5,0.51723279535274846,6.3851768580385701E-2,0,0.1401340025544402,314.49618332596071,523.61359841912451,2.0328418230562999,3.6988382484361018,"Reliability Improvements Scheduled for 2025"]
["LANSDOWNE","Fayette - 3200 Montavesta Rd. - Lexington",38,"Lexington - Tates Creek Rd. - S of Substation",7.96812627408654,1605,"2024-03-01",1.866600734453107E-3,0,0,0,9.1053694363566201E-6,0,0.13827133860837737,0.26801584894612351,0,0.59183710634160969,60.288284006697815,98.488722740809962,0.63208722741433021,0.29158878504672897,"Reliability Improvements Scheduled for 2025"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",40,"Lexington - Reynolds Rd. - W of Substation",12.991262988164801,1112,"2024-01-01",1.0833047221738838E-3,0,6.004424147505029E-4,0,5.5577765131384009E-2,1.3981058628576983E-2,0.88307520580438115,3.6965618008882782E-2,0,8.7166052898506423E-3,42.770990702113309,49.728447237410059,0.36982913669064743,0.48920863309352508,"Continue to Monitor"]
["VILEY ROAD","Fayette - 308 Alexandria Rd. - Lexington ",41,"Lexington - Leestown Rd. & Adams Ln. - NE of Substation",63.597618223680499,1133,"2022-05-20",5.4831022209356267E-3,0,7.5881302404883395E-3,2.7580767771075067E-4,6.9521770001470216E-4,0,0.61459182173250537,0.31638331796636288,0,5.4982602461982416E-2,112.02992790953223,147.14970578111215,0.45851721094439524,0.62930273609885223,"Continue to Monitor"]
["KENTUCKY RIVER","Fayette - 6300 Kentucky American Ave - Lexington",43,"Lexington - Old Richmond Rd - N of Substation",48.211002658126297,426,"2023-12-16",1.9078607840815082E-3,0,0,0,2.074701351062809E-3,0,0.85008899604337163,0.13584020650194115,0,1.0088235319542909E-2,167.44550075586855,181.47672140375587,0.77230046948356834,1.1079812206572774,"Continue to Monitor"]
["JOYLAND","Fayette - 2375 Paris Pike - Lexington",47,"Lexington - US 27 & 68 - NE of Substation",18.204652305706698,244,"2019-09-28",5.8314900462497481E-4,0,5.9795623640385353E-3,0,7.1061916165475386E-2,0,0.79910425388004314,0.1169131491874303,0,6.3579693983876568E-3,105.73611678381148,159.25539614754098,1.0327868852459015,2.8237704918032778,"Continue to Monitor"]
["ASHLAND AVENUE","Fayette - 448 S Ashland Ave. - Lexington",50,"Lexington - Fountaine Rd & Ridge Way Rd. - SE of Substation",4.7555119451099097,993,"2024-01-01",0,0,0,0,0,0,0.69822661727162449,0.28260598258036546,0,1.9167400148009966E-2,337.99753692044317,141.44629069587108,0.94889224572004016,1.1883182275931521,"Reliability Improvements Completed in 2024"]
["AMERICAN AVENUE","Fayette - 96 Burley Ave. - Lexington",52,"Lexington - Waller Ave. & St. Joseph Dr. - SE of Substation",0.45888056337939997,88,"2019-07-20",0,0,0,0,0.89469890570735866,0,0,5.2126335102548979E-2,0,5.3174759190092395E-2,89.681060602272723,346.83863635227272,0.36363636363636359,1.2272727272727271,"Continue to Monitor"]
["WEST HIGH STREET","Fayette - 727 West High St - Lexington",54,"Lexington - West High St & Broadway - S of Substation",3.3679584559281501,748,"2019-05-11",7.0084178885973037E-3,0,0,0,0.20237974722972812,0,0.78234968890411705,8.2621459775574883E-3,0,0,53.665519160872009,151.40432263636364,0.45053475935828879,0.29946524064171121,"Continue to Monitor"]
["HAEFLING"," Fayette - 1555 Baunmann Dr - Lexington  ",60,"Lexington - Mercer Rd - W of Substation",16.875452376424501,966,"2024-01-01",8.476943272910091E-3,3.5541714381476411E-3,0,0,0.53374717202469069,0,1.8224729771248219E-3,0.44885903415914868,0,3.5402061279781022E-3,44.403877670548646,148.25263974430641,0.50595238095238093,1.1832298136645962,"Trees Trimmed in 2024"]
["PICADOME","Fayette - 1620 Harrodsburg Rd - Lexington ",62,"Lexington - Mason Headley Rd - NW of Substation",3.9781531997333701,294,"2020-04-11",1.1484390469275955E-2,0,0.15989043627483335,0,4.7521615734934988E-3,0.66980727344729718,8.6957956570523406E-3,0.11593294172001849,0,2.9437000858029173E-2,106.61128117006801,173.17290248299318,0.89540816326530603,1.1088435374149659,"Continue to Monitor"]
["HUGHES LANE","Fayette - 251 Hughes Ln. - Lexington ",63,"Lexington - US 27 & 68 - NE of Substation",25.0186998417295,234,"2019-12-31",8.9954497213921483E-3,0,5.8393052394626088E-5,0,0,0,0.91012287358050148,7.9034996416126407E-2,0,1.788287229585424E-3,153.56967590811965,71.157193713675227,0.64850427350427353,1.0128205128205128,"Continue to Monitor"]
["PARKERS MILL","Fayette - 2085 Parkers Mill Rd - Lexington",64,"Lexington - New Circle Rd - S of Substation",17.684752816772999,1376,"2021-07-03",4.7174675190760984E-3,0,0,0,0,0,1.1162095277376779E-3,0,0,0.99416632295318619,2.4678385403343022,1.6451065886627907,1.835029069767442E-2,2.5436046511627907E-2,"Continue to Monitor"]
["RACE STREET","Fayette - 420 Corral St - Lexington",67,"Lexington - Eastern Ave. & Main St. - SW of Substation",2.0863131273921498,481,"2023-12-23",0,0,0,0,2.0361508214710274E-2,0,0.25012954552382111,0.72950894626146856,0,0,14.050675673596674,19.591268189189186,0.11642411642411643,0.11226611226611227,"Reliability Improvements Completed in 2024"]
["PROCTOR AND GAMBLE","Fayette - 120 Zesta Pl - Lexington",68,"Lexington - Delware Rd - SE of Substation",3.4138127211202698,393,"2023-04-07",0,0,6.9017458443268564E-2,0,3.3672978528009796E-3,0,6.5207990165352296E-3,0.88984125595836783,0,3.125318872902727E-2,28.050879977099235,29.438210338422387,0.2410941475826972,0.37150127226463098,"Continue to Monitor"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",69,"Lexingotn - Lowry Ln. & Nicholasville Rd. - N of Substation",9.6118131320554507,853,"2020-05-09",1.2096664950827667E-2,0,0,0,7.1794316057543822E-4,0,0.53882311506055103,0.44836227682804586,0,0,35.823202418229776,60.969577953106679,0.20691676436107856,0.25205158264947247,"Tree Trim Scheduled for 2025"]
["LOUDON AVENUE","Fayette - 811 E Loudon Ave - Lexington  ",75,"Lexington - Floyd Dr - NE of Substation",11.7966054663917,1269,"2024-01-01",2.2021044001093195E-2,0,0,0,9.5654550423613012E-4,0,0.81953265919650176,0.15400245968843945,0,3.4872916097294345E-3,70.823299179866041,146.19289465957448,0.47005516154452331,0.73601260835303395,"Continue to Monitor"]
["TRAFTON AVENUE","Fayette - 141 Trafton St - Lexington ",77,"Lexington - Versailles Rd - E of Substation",6.1070799375803801,968,"2023-12-30",1.3665626241677175E-3,0,0,0,0.9715846843929361,0,2.2707907000245754E-2,4.0422692748490465E-3,0,2.9857670780135002E-4,11.544821792355371,12.781163905991738,0.11466942148760328,0.18285123966942152,"Continue to Monitor"]
["TRAFTON AVENUE","Fayette - 141 Trafton St - Lexington ",78,"Lexington - Versailles Rd - W of Substation",5.2952327105171602,542,"2023-12-30",1.383699131521559E-3,0,0,0,0.19285705176437581,1.574993942330991E-3,0.66318085011413919,0.12210347773966052,0,1.8899927307971891E-2,8.8333102675276756,10.873800732472324,9.1789667896678973E-2,0.14760147601476015,"Continue to Monitor"]
["TRAFTON AVENUE","Fayette - 141 Trafton St - Lexington ",79,"Lexington - Red Mile Rd - S of Substation",7.2095917431036103,1346,"2019-12-31",1.3528252957740209E-2,0,0,0,4.2293180781088273E-4,0,0.97699195316586718,8.7786174581798351E-3,0,2.7824461040189654E-4,117.66924219595097,265.30094105720656,0.43499257057949481,0.42421991084695387,"Continue to Monitor"]
["PARKERS MILL","Fayette - 2085 Parkers Mill Rd - Lexington",83,"Lexington - Versailles Rd - W of Substation",29.26108730437581,294,"2023-12-09",7.5292776631429329E-3,0,0,0,4.0753545764480896E-3,9.2699724990815864E-5,0.12988261468157644,0.82926427318265628,0,2.9155780171185492E-2,80.179620163265312,110.95221086054421,0.60204081632653061,0.41156462585034009,"Continue to Monitor"]
["PROCTOR AND GAMBLE","Fayette - 120 Zesta Pl - Lexington",84,"Lexington - Magnolia Ave - NE of Substation",2.3417458078729001,255,"2023-04-07",0,0,0,0,0,0,5.7877813504823147E-3,0,0,0.9942122186495177,10.651650325490195,12.195555552941176,7.8431372549019607E-2,9.8039215686274508E-2,"Continue to Monitor"]
["TRAFTON AVENUE","Fayette - 141 Trafton St - Lexington ",88,"Lexington - Dunkirk Dr - W of Substation",9.3615193028635009,1664,"2024-01-01",3.2112927378324697E-3,0,1.8233173836976456E-3,0,0,0,0.91750505138713645,7.6692897601274027E-2,0,7.6744089005936051E-4,54.709512716045666,97.920953519831741,0.65790264423076916,1.3293269230769225,"Reliability Improvements Scheduled for 2025"]
["HAEFLING"," Fayette - 1555 Baunmann Dr - Lexington  ",89,"Lexington - Baumann Dr - W of Substation",0.58302070229452096,4,"2021-10-30",0,0,0,0,0,0,1,0,0,0,21.188541624999999,8.6208332500000004,0.1875,0.25,"Continue to Monitor"]
["LIBERTY ROAD","Fayette - 2125 Liberty Rd. - Lexington",92,"Lexington - New Circule Rd. & Winchester Rd. - E of Substation",19.090086815866499,1472,"2024-01-01",0,0,0.20944342719698364,0,1.8505476884405778E-2,0,6.4292447208468315E-2,6.3100642491088543E-2,0,0.64465800621905367,39.831717049082876,61.343331065896734,0.57438858695652173,0.48165760869565233,"Continue to Monitor"]
["GE LAMP WORKS","Fayette - 1809 Edision Dr - Lexington",94,"Lexington - Edision Dr. & Bob O Link Dr. - N of Substation",1.6018428769411801,151,"2020-05-09",0,0,0,0,0,0,0.18388422902231211,0.81611577097768784,0,0,157.35836092384108,446.73399558278146,0.7185430463576159,1.1523178807947021,"Tree Trim Scheduled for 2025"]
["STONEWALL","Fayette - 3060 Arrowhead Dr - Lexington",98,"Lexington - Chelsea Dr & Clays Mill Dr - S of Substation",5.7504283799920399,477,"2024-01-01",7.716913037841103E-4,0,2.7834718230919841E-4,0,0.67122306999217141,0,0.30817956675654962,1.118804682666159E-2,0,8.3592779385240051E-3,119.7716718998952,157.93361285115307,0.87211740041928731,1.3542976939203355,"Continue to Monitor"]
["JOYLAND","Fayette - 2375 Paris Pike - Lexington",99,"Lexington - I-64 & I-75 - NW of Substation",16.066493728878601,2265,"2024-01-01",1.7063612222713579E-2,0,0.16348108145788992,3.3417057512629424E-3,1.6187884900674659E-2,2.8301023642459268E-2,0.34709299919180386,5.9424198393628537E-2,0,0.36510749443956719,75.554403968653403,210.17752022825601,0.73940397350993337,2.1262693156732877,"Reliability Improvements Completed in 2024"]
["PARKERS MILL","Fayette - 2085 Parkers Mill Rd - Lexington",100,"Lexington - Parkers Mill Rd & Alexandria Rd - NE of Substation",12.711215928970001,1762,"2024-01-01",1.1513719834322057E-3,0,0,0,9.9934066250299422E-2,2.3577592907480871E-3,0.85183498675541347,3.2311487171413925E-2,0,1.2410328548692935E-2,126.24934259804199,267.80172152043133,1.2779511918274689,1.9619750283768445,"Reliability Improvements Scheduled for 2025"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",101,"Lexington - Shilito Park Rd. & Tiverton Way - SE of Substation",18.075796596131099,1958,"2024-01-01",2.4627787380376382E-4,0,1.1685247832014644E-2,0,0.27866608667336568,0,0.69650959702525927,1.2746421775733364E-2,0,1.4636881982327198E-4,49.264364144024512,52.032056516853928,0.5842696629213483,0.19050051072522983,"Continue to Monitor"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",102,"Lexington - Mall Rd - S of Substation",5.4175561819148301,615,"2020-10-10",0,0,0,0,0,0,0,1,0,0,8.6310094841463414,19.384146341463413,3.1300813008130084E-2,5.0406504065040651E-2,"Tree Trim Scheduled for 2025"]
["DONERAIL","Fayette - 4601 Old Iron Works Rd - Lexington",104,"Lexington - Georgetown Rd - N and S on Georgetown Rd from Substation",33.833703332976199,428,"2019-07-20",1.5600481609047935E-2,0,0,0,1.3002457390429009E-3,0,7.4642000651356497E-2,0.83927284928992274,0,6.9184422710629939E-2,87.807749207359791,136.45027257009343,0.77803738317756987,0.83177570093457942,"Tree Trim Scheduled for 2025"]
["DONERAIL","Fayette - 4601 Old Iron Works Rd - Lexington",105,"Lexington - Iron Works Rd - E of Substation",58.811395632616602,490,"2023-12-09",1.3566855696429726E-3,0,1.4239919549073614E-3,2.665860749687553E-4,2.768667953846296E-2,0,0.8950073179197312,4.8890830362834203E-2,0,2.536790857945255E-2,263.90152209234691,213.47557821428575,1.7224489795918374,2.0857142857142867,"Continue to Monitor"]
["LEXINGTON WATER COMPANY","Fayette - 2300 Richmond Rd - Lexington ",109,"Lexington - Lakeshore Dr. - SE of Substation",14.6794370979324,1114,"2024-01-01",9.7823741305755208E-3,0,0,0,1.812165579367319E-3,0,0.52409045887905803,0.46426686143988311,0,4.8139971116017327E-5,43.745930576526028,85.219225009874322,0.30498204667863554,0.39766606822262118,"Reliability Improvements Scheduled for 2025"]
["IBM","Fayette - 740 W New Circle Rd - Lexington ",110,"Lexington - Russell Cave Rd - NE of Substation",22.024671255774098,2105,"2024-01-01",4.7987756637225525E-3,0,0,0,3.1706505151118204E-2,0,0.89724135247655723,4.0832825354828392E-3,0,6.2170084173119075E-2,46.582119947030876,48.709612028503564,0.27577197149643706,0.23277909738717339,"Continue to Monitor"]
["ASHLAND AVENUE","Fayette - 448 S Ashland Ave. - Lexington",111,"Lexington - Ashland Dr & Preston Ave. - E of Substation",5.3403714366431201,989,"2024-01-01",0,0,0,0,0.4750965017512388,0,0.2501834330808671,0.27391436920906032,0,8.0569595883383301E-4,61.383329116531854,125.01046511122347,0.32077856420626893,0.60465116279069753,"Trees Trimmed in 2024"]
["PICADOME","Fayette - 1620 Harrodsburg Rd - Lexington ",112,"Lexington - Della Dr - W of Substation",11.414142221237899,1604,"2024-01-01",1.0819049587310608E-3,0,0,0,0.57457471680078531,0,0.11512522765729342,0.30762112659683027,0,1.5970239863599375E-3,92.011681727088529,97.849636318578533,0.59304862842892758,0.32356608478803006,"Trees Trimmed in 2024"]
["LANSDOWNE"," Fayette - 3200 Montavesta Rd - Lexington",118,"Lexington - New Circle Rd. & Chinoe Rd. - SW of Substation",13.8655647235051,1101,"2024-03-01",8.8111627595473447E-4,0,2.3327605728720832E-3,0,0.89600358306666139,0,2.1416357787623769E-2,7.6880639091843297E-2,0,2.485543205044757E-3,56.73443460081743,74.415470779291553,0.47320617620345123,0.54132606721162579,"Continue to Monitor"]
["FMC","Fayette - 2641 Palumbo Dr - Lexington ",120,"Lexington - Palumbo Dr & Man O War Blvd - S of Substation",7.08796060222104,276,"2022-06-03",0,0,0,0,0.94767993411016205,0,6.2321916540650129E-3,9.5366870682856812E-3,0,3.6551187167487231E-2,22.294897339673913,40.640821250000002,0.15217391304347827,0.29710144927536236,"Continue to Monitor"]
["FMC","Fayette - 2641 Palumbo Dr - Lexington ",121,"Lexington - Palumbo Dr - S of Substation",0.73377143979232695,6,"2022-06-03",0,0,0,0,0,0,0,0,0,1,334.09722220833333,1336.3888888333333,0.20833333333333334,0.83333333333333337,"Continue to Monitor"]
["FMC","Fayette - 2641 Palumbo Dr - Lexington ",123,"Lexington - Palumbo Dr - W of Substation",4.6765019885400898,367,"2022-06-03",0,0,0,0,0,0,0,1,0,0,1.3023274291553135,1.8783378746594006,2.7929155313351498E-2,8.9918256130790186E-2,"Continue to Monitor"]
["VINE STREET","Fayette - Vine St. - Lexington ",125,"Lexington - Vine, Upper & Limestone St. - W of Substation",5.3412956333674897,306,"2019-05-11",0.21357966580371851,0,0,0,0,0,0.22308517036688372,0.56223686619073765,0,1.0982976386600769E-3,88.622031585784313,249.94270151960785,0.85457516339869277,2.2320261437908497,"Tree Trim Scheduled for 2025"]
["LOUDON AVENUE","Fayette - 811 E Loudon Ave - Lexington  ",127,"Lexington - Floyd Dr - N of Substation",10.3318648381345,1323,"2024-01-01",1.4176810577008451E-2,0,0,0,0.17671474013408706,0,0.43384789278672486,0.34204321397414372,0,3.3217342528035806E-2,98.204487900982599,128.20658855479971,0.66156462585034004,0.77173091458805743,"Trees Trimmed in 2024"]
["BELT LINE","Fayette - 1090 W. New Circle Rd - Lexington",129,"Lexington - Georgtown Rd, Price Rd, & Main St - S of Substation",16.658675720984,2010,"2024-01-01",2.4181295434889321E-2,0,0,0,0.26670718309529928,5.4229681400621774E-2,1.8933638764872256E-3,0.20397489539748953,0,0.44901358079521281,67.476774458333324,64.302429516417902,0.76243781094527352,0.77412935323383048,"Continue to Monitor"]
["LAKESHORE","Fayette - 3710 Richmond Rd - Lexington ",133,"Lexington - Richmond Rd - N of Substation",8.3922420041299208,1335,"2024-01-01",0,0,0,0.10345375990669813,6.2157075834283142E-2,0.18299891324515599,0,0,0,0.65139025101386272,7.2128089876404502,18.409013731086144,9.0636704119850184E-2,0.26666666666666666,"Reliability Improvements Scheduled for 2025"]
["LAKESHORE","Fayette - 3710 Richmond Rd - Lexington ",134,"Lexington - Richmond Rd & Yorkshire Blvd - N of Substation",7.3904075321837199,1061,"2023-12-09",2.9808226792662592E-2,0,0,0,0.34130072262367983,5.5725403001667596E-2,1.9246803779877711E-2,2.6473040578098943E-2,0,0.52744580322401335,25.804889253770028,27.130474392082945,0.43850141376060325,0.83129123468426025,"Continue to Monitor"]
["LAKESHORE","Fayette - 3710 Richmond Rd - Lexington ",135,"Lexington - Richmond Rd & Man O War Blvd - E of Substation",28.433281479809899,2654,"2024-01-01",1.5297441751628154E-3,2.0666308013278924E-4,3.4421430852064228E-2,0,5.6663954897149579E-2,0,0.13616089978262105,0.35293570919333606,0,0.41808159801953348,112.55674767360588,297.83752197663904,0.74717407686510928,1.5090429540316503,"Trees Trimmed in 2024"]
["WILSON DOWNING","Fayette - 680 Wilson Downing Rd - Lexington",137,"Lexington - Man O War Blvd - E of Substation",8.2198259083641698,1458,"2021-06-26",0.11049453239758446,0.34258201403623306,0,0,9.7927207442467757E-4,0,2.2523257711767587E-2,1.7953321364452424E-3,0,0.52162559164354494,2.7241455181755829,3.794364425240055,9.5850480109739372E-2,0.29972565157750342,"Continue to Monitor"]
["IBM","Fayette - 740 W New Circle Rd - Lexington ",140,"Lexington - Newtown Rd - N of Substation",26.963034314864252,991,"2023-09-30",2.9001568287678362E-2,0,0,0,0.25196707603340757,1.1115700675337584E-3,0.65973194706105576,7.8750205690835753E-3,0,5.0312817981240994E-2,76.4267995229566,103.71089807669019,0.85393541876891987,0.84964682139253223,"Continue to Monitor"]
["ASHLAND PIPE","Fayette - 448 S Ashland Ave. - Lexington",142,"Lexington - Tates Creek Rd - N of Substation",18.949759617920002,1799,"2024-01-01",1.590382417035914E-3,0,2.2840378100036952E-2,0,1.5523928261838074E-3,8.6875287080430876E-3,0.14815595072404705,0.80591290713617192,0,1.126046008848121E-2,28.084417266259038,65.117935888271276,0.16759310728182322,0.35853251806559194,"Trees Trimmed in 2024"]
["AMERICAN AVENUE","Fayette - 96 Burley Ave. - Lexington",144,"Lexington - Broadway - NW of Substation",5.0749992014132399,570,"2019-07-20",1.3859486636676369E-2,0,0.10564964276263562,0,2.6131251653876688E-3,2.5866631383964011E-2,0.51893688806562588,0.16348571050542471,0,0.16958851548028578,29.144466370175437,80.545029231578951,0.21403508771929824,0.512280701754386,"Continue to Monitor"]
["CLAYS MILL","Fayette - 4454 Clays Mill Rd - Lexington ",145,"Lexington - Glenview Dr - NW of Substation",32.257734703636899,1999,"2024-01-01",1.6028922907301241E-3,0,0,0,0.833239425394109,0,5.4573611832178944E-4,0.15819760960938356,0,6.4143365874555968E-3,34.776490324162083,23.901442383191593,0.25350175087543775,0.42721360680340176,"Continue to Monitor"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",149,"Lexington - Man O War Blvd & Liberty Rd - NW of Substation",20.6199455236065,1426,"2022-07-15",0,0,0,0,0,0,0,0.65814042272585294,0,0.34185957727414706,28.596587188814865,40.410144926367458,0.15708274894810659,0.12201963534361851,"Continue to Monitor"]
["DANVILLE CENTRAL","Boyle - 494 S 4TH ST - Danville",162,"Danville - 4th St - S of Substation",13.7854609205096,1313,"2024-01-01",1.530529244396636E-3,0,3.5175612460699264E-3,0,0.2386214612736261,0,0.36131446233935255,0.30138312035404691,0,9.3632865542507882E-2,79.107574888613868,129.972353385377,0.75133282559025116,0.71820258948971816,"Reliability Improvements Scheduled for 2025"]
["DANVILLE CENTRAL","Boyle - 494 S 4TH ST - Danville",163,"Danville - Russel St - W of Substation",2.5734733691310132,108,"2020-10-17",0,0,0,0,5.4329555929078781E-2,0,6.5011115328308847E-2,0,0,0.88065932874261232,68.704783942129623,170.76111110185184,0.68981481481481488,1.5092592592592593,"Continue to Monitor"]
["DANVILLE WEST","Boyle - 1353 Lebanon Rd - Danville ",167,"Danville - Lebanaon Rd - SW of Substation",6.5213313166738596,24,"2021-07-31",3.3200199700449323E-2,0,0,0,0,0,0.32126809785322019,0.33824263604593108,0,0.30728906640039938,53.655034697916669,166.98541658333335,0.29166666666666669,0.79166666666666674,"Continue to Monitor"]
["AMERICAN AVENUE","Fayette - 2300 Richmond Rd - Lexington ",178,"Lexington - SW of Substation",4.3855054380759801,1515,"2019-07-20",4.2780047630492257E-2,0,0,0,3.4958159452904802E-4,0,5.5496078131486376E-3,0.30079311324258778,0,0.65052764971924226,14.540979096864687,30.211815180858082,0.14537953795379535,0.3003300330033003,"Tree Trim Scheduled for 2025"]
["VILEY ROAD","Fayette - 308 Alexandria Rd. - Lexington ",189,"Lexington - Leestown Rd and Masterson Station Dr - N of Substation",5.4537846163878303,1323,"2021-12-11",0.53194726166328599,0,5.8823529411764705E-2,0,0,0,4.8554766734279921E-2,0,0,0.36067444219066935,3.2773337095616024,5.9619551496598646,3.4013605442176867E-2,5.8956916099773243E-2,"Continue to Monitor"]
["VILEY ROAD","Fayette - 308 Alexandria Rd. - Lexington ",190,"Lexington - W New Cir Rd - SE of Substation",2.5575025186859199,510,"2021-12-11",0,0,0,0,0.10321578653748574,0,0.85580122733096164,3.1678483021174123E-4,0,4.0666201301340868E-2,34.918913393627449,45.260424831372546,0.46225490196078434,1.0450980392156863,"Continue to Monitor"]
["HUME ROAD","Fayette - 2319 Hume Rd. - Lexington",194,"Lexington - Winchester Rd, Sir Barton Way, Executive Dr, & Elkhorn Rd - E of Substation",8.0135814653725301,323,"2024-01-01",3.1820161641581573E-3,0,0,0,1.4518704931520108E-4,0,4.1741276678120311E-2,0.91983255093645644,0,3.5098969171949865E-2,119.8741356989164,255.89102166563467,1.0580495356037152,1.4303405572755417,"Trees Trimmed in 2024"]
["LAKESHORE","Fayette - 3710 Richmond Rd - Lexington ",195,"Lexington - Hays Blvd & Chilesburg Rd - E of Substation",12.953077950245399,1092,"2023-12-09",0,0,0,0,0,0,0.97462547877524197,2.4057747659950592E-2,0,1.3167735648074699E-3,135.93686660370881,400.5399420009158,0.31478937728937723,0.35347985347985345,"Continue to Monitor"]
["STONEWALL","Fayette - 3060 Arrowhead Dr - Lexington",198,"Lexington - Clays Mill Rd and Pasadena Dr - E of Substation",9.5257949384021003,908,"2024-01-01",7.7938412600819275E-4,0,0,0,0.57359139964466188,0,0.41267707210025562,1.1823602335904928E-2,0,1.1285417931694325E-3,125.08885370044055,227.29263949118945,0.8152533039647577,1.8568281938325988,"Continue to Monitor"]
["STONEWALL","Fayette - 3060 Arrowhead Dr - Lexington",199,"Lexington - Harrodsburg Rd and Man O War Blvd - W of Substation",16.760993645862701,1151,"2021-10-09",7.6830144140031285E-5,0,0,0,0.88462450658901992,0,9.7736851188918644E-2,1.4558755574361001E-2,0,3.0030565035603536E-3,71.719950040834064,90.021618879235447,0.5449609035621199,0.82797567332754129,"Continue to Monitor"]
["LONDON","Laurel - Near corner of Foster Heights & Substation Rd - London",205,"London - S & N on McWhorter Rd",40.868132521663902,1895,"2023-05-05",9.2380188263478467E-3,0,1.2430361723526156E-3,2.2984868859683816E-2,1.582611053981671E-2,0,0.60215497270970586,0.34234911235916965,0,6.2038805329235084E-3,49.13628407229551,36.430272636939314,0.82981530343007881,1.2358839050131927,"Continue to Monitor"]
["CAMPBELLSVILLE INDUSTRIAL","Taylor - 620 Clem Haskins Blvd. - Campbellsville",206,"Campbellsville - Broadway St & Airport Rd - N of Substation",15.2274337798173,879,"2023-02-18",2.5757477454097191E-2,0,0,0,1.9853370531369624E-2,0,2.1994420294556543E-2,0.81950301693375727,0,0.11289171478621943,10.044738335324231,17.533314372013649,0.12969283276450511,0.15585893060295788,"Continue to Monitor"]
["CAMPBELLSVILLE INDUSTRIAL","Taylor - 620 Clem Haskins Blvd. - Campbellsville",208,"Campbellsville - Industrial Rd - SE of Substation",1.88775560854913,12,"2023-02-18",0,0,0.35164835164835168,0,0,0,0,0,0,0.64835164835164838,3.798263875,15.1930555,0.10416666666666666,0.41666666666666663,"Continue to Monitor"]
["COLUMBIA","Taylor - 114 Lindsey Wilson St - Columbia ",209,"Columbia - KY HWY 3491 & KY 55 - N of Substation",43.566927684797697,931,"2019-03-30",4.0572120737541448E-2,2.7651686630531867E-3,9.2620914952710725E-3,0,5.8117482962401046E-2,0,0.23937061824766614,0.2243579547540101,0,0.42555456314005702,59.862661105800207,76.951790175080546,0.8901718582169712,1.4758324382384536,"Continue to Monitor"]
["CARON","Laurel - 1136 South Laurel Rd - London ",210,"London - S Laurel Rd - N of Substation",15.0781929759601,742,"2023-12-16",2.3296387520525451E-2,1.4932266009852218E-2,0,0,8.220443349753695E-2,9.2364532019704429E-4,0.10704022988505747,0.73706896551724133,0,3.4534072249589494E-2,19.974707989892181,25.940813110512128,0.13477088948787058,0.14285714285714282,"Continue to Monitor"]
["CARON","Laurel - 1136 South Laurel Rd - London ",211,"London - 0.32 miles S of Substation",0.34513480336382441,2,"2023-12-16",0,0,0,0,0,0,0,0,0,1,11.34583325,45.383333,0.125,0.5,"Continue to Monitor"]
["FARISTON","Laurel - 57 Rocky Branch Rd - North Corbin ",216,"North Corbin - S Laurel Rd - S of Substation",3.1673785135469399,95,"2019-03-26",0.14053254437869822,0,0,0,8.8757396449704144E-3,0,0.58727810650887569,0.26331360946745563,0,0,20.31517542631579,7.1126315578947361,9.4736842105263161E-2,0.12631578947368421,"Tree Trim Scheduled for 2025"]
["LEBANON WEST","Marion - 2255 Saint Mary's Rd - St Mary ",218,"St Mary - Sait Mary's Rd - E of Substation",7.2621865189286403,143,"2019-11-16",5.9405940594059407E-3,0,0,0,0,0,0,0,0,0.99405940594059405,26.265530295454543,63.57132866433566,0.39860139860139859,1.0419580419580421,"Continue to Monitor"]
["LEBANON WEST","Marion - 2255 Saint Mary's Rd - St Mary ",219,"St Mary - Sait Mary's Rd - W of Substation",41.963625906043013,841,"2020-05-16",3.5972657028621007E-2,0,2.4857246708173577E-3,0,2.2160469942664181E-3,0,0.91006835742844749,3.4530467714892071E-2,0,1.4726746162955667E-2,49.395327972948863,57.942330548156946,0.42122473246135572,0.36860879904875138,"Continue to Monitor"]
["MACKVILLE","Washington - 4685 Texas Rd - Springfield ",220,"Springfield - Texas Mackville Rd - N of Substation",6.1290535785773299,134,"2020-09-19",0,0,0.13048943819168685,0,7.6652411945769397E-2,0,0.79285814986254377,0,0,0,240.44443407089554,684.16119400746265,1.4365671641791042,4.4776119402985071,"Continue to Monitor"]
["EAST BERNSTADT","Laurel - 440 State HWY 490 - East Bernstadt ",221,"East Bernstadt - US HWY 25 - N & S of Substation",28.8638089074846,787,"2019-05-11",8.8775528278158596E-3,0,0,0,1.8739925961351116E-3,0,0.22152434596241385,0.76292753777210975,0,4.7965708415254084E-3,93.942545519695059,126.04015246505719,0.95648030495552749,1.6391359593392638,"Continue to Monitor"]
["SPRINGFIELD","Washinton - 107 Commercial Ave - Springfield ",224,"Springfield - High St - E of Substation",7.3544028457168542,651,"2020-06-20",7.7718936942237915E-3,0,0,0,1.1277826811807393E-3,0,0.37118760419731295,0.53917818966362652,0,8.0734529763655971E-2,26.22958268740399,59.646518170506909,0.46774193548387089,1.3594470046082947,"Continue to Monitor"]
["WILLIAMSBURG SOUTH"," Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg ",225,"Williamsburg - I75 - NW of Substation",15.5567082019137,636,"2024-01-01",0.21852731591448932,0,3.9106337567558262E-2,0,9.2946400908809255E-4,0,7.0535990911907473E-2,8.3100967331061315E-2,0,0.58779992426589556,44.594247895440255,30.460822836477988,0.27594339622641523,0.57232704402515766,"Reliability Improvements Completed in 2024"]
["WILLIAMSBURG SOUTH"," Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg ",227,"Williamsburg - Savoy Clear Creek Rd - N of Substation",8.85445594295172,188,"2023-10-07",0,0,0,0,0.98641325327042684,0,1.1422903710057903E-2,4.2033025948959898E-4,0,1.7435127600257344E-3,455.76274377792555,665.55345743085104,2.0558510638297869,2.4946808510638299,"Continue to Monitor"]
["PICADOME","Fayette - 1620 Harrodsburg Rd - Lexington ",232,"Lexington - Harrodsburg Rd - SW of Substation",10.971419261854599,1071,"2024-01-01",2.1810059077510182E-3,0,1.4440659515393176E-3,0,2.7390620986582188E-3,0,0.77354691341414195,0.21969066868891962,0,3.9828393898993359E-4,55.966553836367879,100.28664798412697,0.40056022408963576,0.42296918767506997,"Continue to Monitor"]
["WILLIAMSBURG","Whitley -  Corner of 2nd and 3rd St - Williamsburg ",235,"Williamsburg - 5th St - W of Substation",3.3258950866362298,286,"2023-09-30",0,0,0,0,7.2115384615384619E-3,0,0.36598557692307693,0.28485576923076922,0,0.34194711538461536,3.1865093225524475,5.7747668951048947,4.2832167832167832E-2,4.8951048951048952E-2,"Continue to Monitor"]
["MANCHESTER SOUTH","Clay - 530 Muddy Gap Rd - Manchester ",254,"Manchester - State HWY 80 - S of Substation",20.4642910835097,409,"2024-01-01",1.4558797214023005E-3,0,0,5.7609751266945453E-3,5.359652673658827E-3,0,0.24703047444653115,0.70211797490257943,0,3.8275043129133754E-2,214.19229827444994,148.48504480929094,0.73594132029339865,0.88997555012224949,"Trees Trimmed in 2024"]
["GARRARD","Clay - N End of Crawford Isom Rd - Manchester",257,"Manchester - End of Crawford Isom Rd - N of Substation",0.33819724516076399,2,"2019-11-30",0,0,0,0,0,0,0,0,0,1,288.53749998481777,637.59999999999991,1,2,"Continue to Monitor"]
["CORBIN EAST","Knox - Corner of State HWY 1232 and E Barbourville Rd - Corbin ",275,"Corbin - Barbourville Rd - E of Substation",30.2381987803012,870,"2022-10-14",3.9442648579825707E-3,0,1.1291759541502678E-2,3.8640483074307832E-3,0.17539946135439674,0,0.54987762709203059,0.20323631113098509,0,5.2386527715671587E-2,91.608654200000018,162.84149423678159,0.69367816091954027,1.2896551724137928,"Continue to Monitor"]
["VAKSDAHL AVENUE","Boyle - 1120 Old Lebanon Rd - Danville",281,"Danville - Old Lebanon Rd - N of Substation",7.5458425452774994E-2,5,"2020-10-24",0,0,0,0,0,0,0,0,0,1,3.7458333000000001,14.983333200000001,0.25,1,"Continue to Monitor"]
["HOPEWELL","Laurel - Corner of American Greeting Rd and Hopewell Church Rd - North Corbin",286,"North Corbin - Robinson Creek Rd & US HWY 25 - NW of Substation",70.839012243904605,2105,"2024-01-01",7.1545895845249091E-2,0,1.8038629064191121E-3,3.6297241409652864E-4,4.4168976491120004E-2,1.4656386114655286E-2,0.35055069148078077,0.12227037411823369,0,0.39464084062944549,76.163145279216138,110.11248613254153,1.3323040380047488,3.8593824228028444,"Reliability Improvements Completed in 2024"]
["CORBIN US STEEL","Whitley  - S Woodbine Ave off HWY 830 - Corbin",288,"Corbin - 0.15 miles E of Substation",20.795713263619799,399,"2022-01-01",0.10441168298339232,0,0,0,1.8162325102908546E-4,0,0.65684997512845777,0.22464356436985544,0,1.3913154267265391E-2,238.19366121867171,389.57949037092737,1.5958646616541352,2.0426065162907263,"Continue to Monitor"]
["HUME ROAD","Fayette - 2319 Hume Rd. - Lexington",293,"Lexington - Winchester Rd, Man O War Blvd, and Blackford Pkwy - SE of Sub",26.4485103820221,1658,"2021-04-24",0,0,0,0.46129447602298779,0,0,0.53870552397701221,0,0,0,5.8992611574185769,19.205418173100121,3.8449939686369117E-2,0.12303980699638119,"Continue to Monitor"]
["WHITE SULPHUR","Scott Ky - 4283 Frankfort Rd - Georgetown",296,"Georgetown - Frankfort Pike - E of Substation",7.5274992809992103,1107,"2023-11-04",3.849088481347249E-3,0,1.5209008910810147E-2,0,3.4914298171512658E-3,3.6498215112952009E-2,2.3554377742049756E-2,0.74971387306864323,0,0.16768400686704635,40.417355459123762,83.772252321589875,0.60298102981029811,0.35953026196928606,"Continue to Monitor"]
["PINEVILLE","Bell - Corner of E Park Ave and Maple St - Pineville  ",303,"Pineville - US HWY 25E - S of Substation",25.808921248555102,537,"2024-01-01",3.0619027382781426E-3,0,8.8588146840574023E-3,0,1.0057424296906498E-2,0,0.17162455188345155,0.8042316367559087,0,2.1656696413977967E-3,74.69069674348232,118.70037240409681,0.62988826815642485,1.1899441340782138,"Trees Trimmed in 2024"]
["CROCKETT","Bell - On HWY 66 across the street from Chaz Coal Co - Pineville ",305,"Pineville - State HWY 66 - SW of Substation",1.81823306342903,10,"2019-01-22",0,0,0,0,0,0,1,0,0,0,241.17916663409093,786.58333330000005,1.05,2,"Continue to Monitor"]
["KU PARK - GREASY CREEK"," Bell - US HWY 25 at HWY 3085 - Pineville US HWY 25 AT HWY 3085 PINEVILLE ",310,"Pineville - Mocking Bird - E of Substation",5.7206772656245297,199,"2020-08-29",7.0129786341788625E-2,0,0,0,9.8925794901020452E-4,0,0.32368089979462145,0.20743233798212884,0,0.39776771793245086,173.45374788819095,357.13484083417086,1.7776381909547736,3.5929648241206023,"Continue to Monitor"]
["CALLOWAY","Bell - Hwy 119 - Calloway",311,"Calloway - US HWY 119 - S of Substation",67.750801227721297,915,"2019-09-28",8.9314349974220627E-4,3.8342018928327038E-5,2.4572723307301359E-2,3.3831193172053272E-5,9.087284027301322E-2,0,0.5430768071833999,0.28629218693403236,0,5.4220125590410707E-2,679.22860197021862,1355.3134790043716,5.5240437158469966,10.853551912568312,"Reliability Improvements Completed in 2024"]
["CALLOWAY","Bell - Hwy 119 - Calloway",312,"Calloway - US HWY 119 - NW of Substation",22.747178194244199,332,"2019-06-27",1.4039148431354851E-3,0,8.6491470129334246E-3,0,0.32111771608360951,0,0.52373599308841934,0.14483372232466379,0,2.595066472385914E-4,738.06303962902825,841.77389554322133,3.4947289156626513,4.0090361445783138,"Continue to Monitor"]
["MILL CREEK KU"," Bell - 5539 HWY 221 Kettle Island - Pineville ",316,"Pineville - State HWY 221 - NE of Substation",30.809090850587801,337,"2022-11-18",7.3761014313623863E-4,0,0,0,0.24388979705753361,0,0.49137295163669709,0.20663550097683503,0,5.7364140185798017E-2,287.21483677522258,554.70182984866494,1.398367952522255,2.7537091988130564,"Continue to Monitor"]
["STRAIGHT CREEK","Bell - 3582 HWY 66 Arjay - Pineville",317,"Pineville - State HWY 66 - NE of Substation",8.1132945178767297,220,"2023-06-09",2.5941422594142258E-2,0,0,0,3.4030683403068342E-2,0,0.72329149232914924,0.17629009762900977,0,4.0446304044630406E-2,155.60549241022724,115.2290151409091,0.83977272727272723,1.1318181818181821,"Continue to Monitor"]
["CALLOWAY","Bell - Hwy 119 - Calloway",318,"Tejay - State HWY 2012 - S of Substation",3.8905063363852501,7,"2019-09-28",0,0,0,0,0,0,5.9211962453612748E-3,0.99407880375463875,0,0,58.034523714285712,62.026190428571432,0.64285714285714279,0.14285714285714285,"Continue to Monitor"]
["DEER BRANCH"," Bell - HWY 66 0.5 miles S of Buffalo Hollow Rd, 7.5 miles N of HWY 221 - Pineville ",319,"Pineville - State HWY 66 - S of Substation",13.787073317546501,230,"2023-07-01",4.1059330732909051E-4,0,0,0,0,0,0.85058361139074878,0.13374458622830471,0,1.5261209073617402E-2,341.03811591739128,765.48702895652173,2.2826086956521738,3.4434782608695649,"Continue to Monitor"]
["DEER BRANCH","Bell - Hwy 66 0.5 miles S of Buffalo Hollow Rd - Pineville",320,"Pineville - Hwy 66 & Buffalo Hollow Rd - N of Substation",2.1830643185537499,28,"2023-07-01",0,0,0,0,0,0,0,0,0,1,19.516815473214283,63.758928571428569,0.28571428571428575,1.0357142857142858,"Continue to Monitor"]
["PUCKETT CREEK"," Harlan - 5627 E HWY 72 Pathfork - Alva",321,"Alva - E Highway 72 - SE of Substation",2.79994115396044,63,"2022-12-31",0,0,0,0,0,0,0.98282087118565098,3.1009783368273936E-3,0,1.4078150477521546E-2,110.02043648015872,201.20343914285715,1.0198412698412698,1.3333333333333333,"Continue to Monitor"]
["PUCKETT CREEK"," Harlan - 5627 E HWY 72 Pathfork - Alva",322,"Alva - E Highway 72 - NW of Substation",10.472577880820699,295,"2022-12-31",1.2234910277324632E-3,0,0,0,1.3686306496497457E-2,0,0.73966829798803702,0.10376883216581902,0,0.1416530723219141,121.96271184745761,298.02299432881352,0.98898305084745763,1.593220338983051,"Continue to Monitor"]
["BRUSH CREEK","Knox - HWY 225 Kay Jay Road - Barbourville",324,"Trosper - State HWY 225 - N of Substation",1.03630415579847,37,"2020-05-02",0,0,0,0,0.89950870924519877,0,0.10049129075480125,0,0,0,62.219369358108104,121.03558556756757,0.43918918918918914,0.70270270270270263,"Continue to Monitor"]
["WACO","Madison - 3761 New Irvine Rd - Madison East ",331,"Madison East - Irvine Rd - E & W of Substation",45.143787395915297,1083,"2019-04-06",1.1423719655744664E-2,0,0.13835822623596156,4.0060206090077571E-2,2.9639921268959129E-2,0.42638261742117245,0.16240206861950521,0.14379993053143453,0,4.793331017714484E-2,17.637946282779314,21.443582629732219,0.41712834718374858,1.1763619575253916,"Continue to Monitor"]
["DARK HOLLOW","Estill - 37 Dark Hollow Rd - Red Lick",336,"Red Lick - Wisemantown Rd - S of Substation",12.0130292013542,532,"2023-07-14",1.2788510556014554E-3,0,0,0.22128517939072195,0,0,0.73147204106386343,2.1261448134020075E-2,0,2.4702480355793064E-2,139.41560932847744,170.69179197556389,0.6546052631578948,1.0601503759398496,"Continue to Monitor"]
["DARK HOLLOW","Estill - 37 Dark Hollow Rd - Red Lick",337,"Red Lick - Richmond Rd - E of Substation",17.1710156906076,540,"2023-07-28",1.3726522731262068E-2,0,7.6180445848692295E-3,1.412439295535662E-2,3.3257269908138785E-2,0,0.14565560821484994,0.16530337604587211,0,0.62031478555965125,72.160563262500006,116.32632714814817,0.77083333333333326,2.2722222222222217,"Continue to Monitor"]
["RICHMOND INDUSTRIAL","Madison - 110 Mikron Way - Richmond",343,"Richmond - Pavilion Way - NW of Substation",9.6706908217733005,590,"2024-01-01",0,0,0,0,0,0,0,0,0,1,30.703919490677968,63.818474576271193,0.26567796610169486,0.36949152542372876,"Continue to Monitor"]
["RICHMOND INDUSTRIAL","Madison - 110 Mikron Way - Richmond",344,"Richmond - 1.51 miles S of Substation",5.1112903705024433,9,"2019-09-07",0,0,0,0,0,0,0.70322580645161292,0.29677419354838708,0,0,4.5597221944444444,17.194444333333333,0.1111111111111111,0.33333333333333331,"Continue to Monitor"]
["MIDDLESBORO 2","Bell - Intersection of Cumberland Ace and S 38th St - Middlesborough",350,"Middlesborough - Dorchester Ave - E of Substation",5.6089654441152303,451,"2024-01-01",3.7509472088911339E-2,0,0.1581207375599899,0,0,0,0.54773932811315984,0.10019365159552075,0,0.15643681064241813,97.551820009423508,44.469807815964529,1.1092017738359199,1.1862527716186253,"Continue to Monitor"]
["MIDDLESBORO 2","Bell - Intersection of Cumberland Ace and S 38th St - Middlesborough",361,"Middlesborough - Glenboro Rd - SW of Substation",9.0538718656397208,136,"2020-11-28",1.3647753713978879E-3,0,3.1233219974941828E-2,0,3.1926794344012889E-2,0,0.72080275639878288,0.16976910685519958,0,4.4903347055664934E-2,79.822058805147066,138.49313722058824,0.43198529411764702,1.0735294117647056,"Continue to Monitor"]
["MIDDLESBORO 1","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",365,"Middlesborough - N 12th St - NE of Substation",3.9847673845174101,480,"2021-12-31",2.2294009041184597E-3,0,2.7187815903883654E-4,4.6713610962127375E-4,0,0,1.8722518679265339E-2,0.71987157464414853,0,0.25843749150380751,90.609201376041653,203.07385415416664,0.92395833333333321,2.3874999999999997,"Continue to Monitor"]
["MIDDLESBORO 1","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",372,"Middlesborough - Lynnwood Dr - E of Substation",8.8026237121917301,500,"2024-01-01",1.1759662506454662E-2,0,0.11150732177827141,3.0008086594764173E-3,0,0,0.76875261840041309,7.8771227311255951E-2,0,2.6208361344128451E-2,92.02569165349999,178.73293331799997,0.59050000000000014,0.92200000000000015,"Continue to Monitor"]
["APOLLO","Bell - Intersection of Delta Gas Rd Spur and Delta Gas Rd - Middlesboro",380,"Middlesboro - Delta Gas Rd - NE of Substation",0.39405490591276598,6,"2020-11-21",0,0,0,0,0,0,1,0,0,0,123.00972220833333,492.03888883333332,0.58333333333333337,2.3333333333333335,"Continue to Monitor"]
["MELDRUM","Bell - HWY 25/Wilderness Rd S of HWY 2486 Middlesborough",390,"Middlesborough - S of Substation on US HWY 25E and E of Substation Colmar Rd",16.6475759131255,296,"2022-02-04",2.833846563065874E-3,0,8.0718589828843845E-3,0,0,0,0.95387070702937171,3.1827063746201929E-2,0,3.3965236784760659E-3,169.00447632939188,121.81593466216216,1.6782094594594597,1.7668918918918919,"Continue to Monitor"]
["HOOVER 1","Scott Ky - 3 Quality Dr - Georgetown",397,"Georgetown - Quality Dr - SW of Substation",2.6578890309121102,1605,"2019-01-12",5.6910986696800038E-2,0,0,0,1.263547177564333E-2,0.41679079562381222,0.4067491910216241,0,0,0.10691355488212029,4.7489745580996878,14.392191069158878,8.1619937694704048E-2,0.16822429906542052,"Continue to Monitor"]
["HOOVER 1","Scott Ky - 3 Quality Dr - Georgetown",400,"Georgetown - Quality Dr - SW of Substation",3.2604508906082001,1267,"2019-01-12",1.5240289664252797E-2,0.22340355497037526,0,0,9.3153390388413422E-3,0,0.39545753785385124,2.4358130348913758E-2,0,0.33222514812376563,9.2876907383583269,23.977374371744279,5.5248618784530391E-2,0.12470402525651145,"Continue to Monitor"]
["DELAPLAIN","Scott Ky -  413 Triport Cir - Sadieville ",401,"Sadieville - I75 - N of Substation",10.7315577544954,109,"2019-09-28",3.3454722865954591E-3,0,0,0,0,0,0.92320224425432551,7.3121221097384614E-2,0,3.3106236169434231E-4,137.17178896911759,74.580886807339439,0.65596330275229353,0.83486238532110058,"Continue to Monitor"]
["DELAPLAIN","Scott Ky -  413 Triport Cir - Sadieville ",402,"Sadieville - Triport Rd & Cincinnati Rd - S of Substation",25.4647651835147,593,"2019-09-21",8.5622480135114157E-3,0,0,0,8.3820644426776308E-2,4.0929427317334786E-4,0.86352623482200408,1.18789429857782E-2,0,3.180263547875669E-2,21.022428319983138,24.44825743676223,0.13069139966273188,0.14165261382799324,"Continue to Monitor"]
["DELAPLAIN","Scott Ky -  413 Triport Cir - Sadieville ",403,"Sadieville - 0.41 Miles N of Substation",0.121897429900309,1,"2019-09-28",0,0,0,0,1,0,0,0,0,0,224.25,145.15,0.5,1,"Continue to Monitor"]
["FORKS OF ELKHORN","Franklin - 3286 Georgetown Rd - Frankfort ",405,"Frankfort - Switzer Rd - N of Substation",55.760310667111099,699,"2018-01-27",2.1568207735763794E-3,0,9.5047824339903938E-3,0,0.10751933064700868,0,0.64700867860616551,0.22934653212511313,0,4.4638554141458904E-3,142.52920241523606,210.43650451502143,1.4148783977110151,1.2074391988555071,"Continue to Monitor"]
["FORKS OF ELKHORN","Franklin - 3286 Georgetown Rd - Frankfort ",406,"Frankfort - Steadmantown Ln - N of Substation",22.370465118265201,802,"2017-12-23",2.7658823641617945E-2,0,0.16619137998454922,0,1.8884300279449493E-3,0,0.206754475483791,0.57867027820961581,0,1.8836612652481186E-2,31.923207599438904,34.740149613466336,0.33790523690773061,0.55985037406483773,"Continue to Monitor"]
["FORKS OF ELKHORN","Franklin - 3286 Georgetown Rd - Frankfort ",407,"Frankfort - Old Grand Dad Rd - N of Substation",0.87465175949138596,3,"2017-12-23",2.8358902835890282E-2,0,0,0,0.97164109716410973,0,0,0,0,0,539.59999991666666,1434.1055553333335,1.5833333333333333,1.6666666666666665,"Continue to Monitor"]
["HOOVER 1","Scott Ky - 3 Quality Dr - Georgetown",411,"Georgetown - Pocaontas Trl - E of Substation",20.028086984154299,1777,"2024-03-01",1.7235790023358386E-2,0,0,0,1.209098730796796E-4,0,0.8679594093289853,7.8612445305805606E-2,0,3.6071445468771085E-2,40.155646217782774,53.620258859313445,0.44850872256612284,0.55768148564997166,"Continue to Monitor"]
["HOOVER 1","Scott Ky - 3 Quality Dr - Georgetown",412,"Georgetown - Old Lemons Mill Rd - N of Substation",3.4731680196066201,901,"2019-01-12",7.9466428399166591E-3,0,0,0,9.7413585201057973E-2,0,5.7514321748103288E-2,0.57952968525759374,0,0.25759576495332831,60.468863295504988,201.5610247780244,0.63540510543840178,2.1931187569367374,"Tree Trim Scheduled for 2025"]
["HARLAN Y","Harlan - Sunshine Pike Rd just W of US HWY 421 - Harlan",413,"Harlan - US HWY 421 Bypass - NW of Substation",12.6343443174023,646,"2023-11-18",0,0,0,0,0.366597473282746,0,0.28682312979222119,0.29388979381033731,0,5.2689603114695484E-2,71.162422588235287,97.797523208978319,0.51780185758513941,0.72600619195046467,"Continue to Monitor"]
["CAWOOD","Bell - Off Slack Hollow Rd just N of S Old US HWY 421 - Cawood ",418,"Cawood - US HWY 421 Bypass - W of Substation",32.448653092786856,700,"2021-01-09",1.3211740569014105E-3,0,0,2.8889469296891304E-2,1.2509351959548274E-2,0,0.9311976488593966,2.559477242242908E-2,0,4.8758340483336121E-4,191.67364283750007,305.68980948428595,1.385714285714285,2.8385714285714263,"Continue to Monitor"]
["CAWOOD","Bell - Off Slack Hollow Rd just N of S Old US HWY 421 - Cawood ",419,"Cawood - US HWY 421 Bypass - E of Substation",21.882241262898901,302,"2020-12-19",3.9182408064920421E-5,0,0,0,5.8739797142475285E-2,0,0.88455306022658164,5.6612138710018509E-2,0,5.5821512859612654E-5,904.31988131705282,969.23907282119194,3.1274834437086083,4.5430463576158928,"Continue to Monitor"]
["GEORGETOWN","Scott Ky - 207 W Clinton St - Georgetown ",420,"Georgetown - W & E on Clinton St",3.9351436871380301,460,"2018-10-20",0,0,0,0,1.6392954010312658E-4,0,4.2189502548359216E-2,0.15740216386992936,0,0.80024440404160835,46.846458329891298,173.03065216521736,0.72119565217391313,2.6804347826086956,"Continue to Monitor"]
["GEORGETOWN","Scott Ky - 207 W Clinton St - Georgetown ",421,"Georgetown - Water St - N of Substation",2.7936740662203601,321,"2018-10-20",0,0,0.10859700760363011,0,0,0,0.38974736325729703,0.5016556291390728,0,0,31.561928864485978,108.72071650778814,0.36915887850467283,1.3489096573208721,"Tree Trim Scheduled for 2025"]
["KENTENIA"," Harlan - Near HWY 219 on Meadow Creek Ln (Wilson Ln) - Wallins Creek ",422,"Wallins Creek - HWY 219 - N of Substation",44.704480409783081,1101,"2024-03-01",4.6311367578921077E-3,0,0,0,2.782695557943838E-2,9.8553801010510924E-4,0.84579228783061233,9.6408806517929213E-2,0,2.4355275304022869E-2,251.45479865508634,202.37853464486835,1.2611262488646684,1.3079019073569476,"Reliability Improvements Completed in 2024"]
["GEORGETOWN","Scott Ky - 207 W Clinton St - Georgetown ",427,"Georgetown - S Broadway St - S of Substation",7.6917578443416703,757,"2024-03-01",0.10350138617927919,0,0,0,0,0,0.16480131430331657,0,0,0.73169729951740425,13.581010565389697,10.745794803170408,0.18758256274768823,0.38705416116248348,"Continue to Monitor"]
["NEWTOWN","Scott Ky - 5849 Paris Pike - Georgetown ",431,"Georgetown - US 460 Pike - W of Substation",45.3367303102901,1383,"2019-04-20",5.0054852085308936E-3,0,7.225600119001134E-3,0,0.14525761886167979,2.7876015693274577E-2,0.45324185121139432,0.35540990312563914,0,5.9835257804800954E-3,98.835162080260318,176.6369004454086,1.1097252349963849,2.0766449746926976,"Tree Trim Scheduled for 2025"]
["TURTLE CREEK","Harlan - HWY 990 - Cawood",432,"Cawood - HWY 990 - SW of Substation",3.8355649780115799,88,"2019-07-06",2.4627164162047882E-2,0,0,0,2.4855722530141137E-3,0,0.71370207416719045,0.25918518941774754,0,0,314.06297346022728,361.54999997727271,2.3153409090909092,2.8409090909090908,"Tree Trim Scheduled for 2025"]
["LEMONS MILL","Scott Ky - 125 Carley Ct - Georgetown ",440,"Georgetown - McClelland Blvd - N of Substation",20.7656730997609,1544,"2019-01-19",4.6306221326587486E-3,3.8374137117866483E-3,1.3505981220254685E-3,0,9.8400720318998405E-3,5.0015006645800282E-2,0,0.40138489902671182,0,0.52894138832911719,16.2898397007772,14.405731863341968,0.22716968911917099,0.36463730569948188,"Continue to Monitor"]
["LEMONS MILL","Scott Ky - 125 Carley Ct - Georgetown ",441,"Georgetown - Lemons Mill Rd - SE of Substation",28.637326318459301,1538,"2018-11-10",6.8244891094104781E-2,0,0,0,4.6894710285089562E-2,0,1.1374148515684131E-2,0.32294382305945668,0,0.55054242704566481,16.544099476430429,34.513545725617682,0.32038361508452545,1.0136540962288689,"Tree Trim Scheduled for 2025"]
["LEMONS MILL","Scott Ky - 125 Carley Ct - Georgetown ",442,"Georgetown - Holmes Dr - N of Substation",1.5243471988097299,58,"2018-11-10",0,0,0,0,0,0,1,0,0,0,0.56645114655172413,1.1295976896551725,1.2931034482758621E-2,1.7241379310344827E-2,"Continue to Monitor"]
["CUMBERLAND"," Harlan - Russel Dr just S of E Main St - Cumberland",454,"Cumberland - Raymond D Hatfield Blvd - N of Substation",10.093194460413001,542,"2024-01-01",1.9942941029831318E-3,0,0,1.0386948453037144E-2,7.686341855247486E-2,0,0.90720992715286819,3.5454117386366783E-3,0,0,34.758694643450184,66.613837627306268,0.1780442804428044,0.34317343173431725,"Continue to Monitor"]
["OXFORD","Scott Ky - 1827 Oxford Dr - Georgetown ",470,"Georgetown - Oxford Rd - N of Substation",38.598179691695002,1234,"2019-08-31",2.6965431265096228E-2,0,2.1723956574812353E-2,0,3.4250577877048544E-4,0,0.25115250759681063,0.66867841466898681,0,3.1137184115523464E-2,21.616474197528358,46.305578057536451,0.18314424635332258,0.41977309562398724,"Tree Trim Scheduled for 2025"]
["OXFORD","Scott Ky - 1827 Oxford Dr - Georgetown ",471,"Georgetown - Oxford Rd - S & E of Substation ",13.8462406134642,652,"2019-08-31",0,0,7.7561327561327567E-2,0,0,0,0.54365079365079361,0.37878787878787878,0,0,2.4484598661809813,2.4256134969325154,1.4570552147239263E-2,1.5337423312883436E-2,"Continue to Monitor"]
["SHADRACK","Franklin - 74 Bethel Ln - Frankfort ",475,"Frankfort  - US HWY 127 - N of Substation",47.946781578752997,584,"2018-03-09",2.0886695093082823E-2,0,0,0,8.2516260557227456E-3,0,0.10083038987999671,0.83090140613682018,0,3.9129882834377544E-2,96.634902950342479,107.82214609246577,0.70248287671232845,1.4623287671232867,"Tree Trim Scheduled for 2025"]
["SHADRACK","Franklin - 74 Bethel Ln - Frankfort ",476,"Frankfort - S on US HWY 127 & N on Peaks Mill Rd",61.236400572278697,705,"2018-09-29",1.5263034524327763E-2,0,9.3024813314134553E-3,0,0.17726283360680439,0,7.472122693634263E-2,0.23771891638482404,0,0.48573150721628772,137.47489951134753,155.62096923971635,1.3382978723404244,1.2595744680851046,"Continue to Monitor"]
["STAMPING GROUND","Scott Ky - 3540 Main St - Stamping Ground ",480,"Stamping Ground - Owenton/HWY 227 N of Substation",55.913472900080002,498,"2017-09-23",2.2676797684285637E-3,0,5.6227706327091863E-2,0,4.8802591075479244E-4,3.262791829371061E-2,0.85246676501657126,2.8374622373369841E-2,0,2.7547282310073092E-2,218.35749662637136,388.6632864432367,2.0145582329317278,4.124497991967873,"Continue to Monitor"]
["STAMPING GROUND","Scott Ky - 3540 Main St - Stamping Ground ",481,"Stamping Ground - SE on Main St & N on Locust Fork Rd ",102.51828333092401,1327,"2023-12-23",6.2630643684800542E-3,1.5821653930692149E-3,2.1229996524327263E-2,0,9.7710461774942856E-4,0,0.92510561639342659,2.5886418931157201E-2,0,1.8955633771790267E-2,93.922164639035415,89.650037660135609,0.76281085154483819,0.80030143180105595,"Continue to Monitor"]
["ALEXANDER","Woodford - 2915 Troy Pike - Versailles",500,"Woodford South - Troy Pike - S of Substation",95.947680446347604,1001,"2022-03-11",6.2628648850519804E-3,1.1811810073042149E-4,2.9764024353173121E-3,4.8810568095953585E-4,1.1038831325615127E-3,4.6639279479585542E-4,0.52676851457803175,0.41577137199385089,0,4.6044346398700704E-2,142.41242089610387,198.46003993706293,0.985764235764236,0.55044955044955068,"Continue to Monitor"]
["MIDWAY","Woodford - 860 Weisenburger Rd - Midway ",504,"Midway - Weisenberger Mill Rd - E of Substation",63.579633520221101,558,"2023-07-14",1.3003540189960988E-3,0,1.1247758645966256E-2,4.9984255219850046E-3,1.071339034996786E-2,1.8911085799943266E-4,0.54173494465037486,0.42148386094973556,0,8.3321550049750039E-3,197.74490738127238,380.82724010573469,1.5022401433691759,1.4802867383512557,"Continue to Monitor"]
["VERSAILLES BYPASS","Woodford - 350 Markham Dr - Versailles ",509,"Versailles - Frankfort Rd - N of Substation",137.05717378185136,2011,"2021-01-23",1.1471228481712526E-3,0,3.9139152690537207E-2,3.8250407033929679E-2,5.9750025058993461E-2,0,0.72815824185303168,0.11770358984557669,0,1.5851460669760006E-2,236.86354009845846,345.76030165638991,1.2642963699651906,1.6190949776230714,"Continue to Monitor"]
["VERSAILLES WEST","Woodford - 115 Rutter Rd - Versailles",512,"Versailles - Tyrone Pike - W of Substation",34.349129690149503,1125,"2021-04-03",9.738203010722965E-3,0,0.10990751298619029,0,4.5494857353466247E-4,0,0.39421005954643357,0.35055803185791778,0,0.13513124402520069,69.515685175777776,81.323896289777764,0.75488888888888916,0.45511111111111097,"Continue to Monitor"]
["VERSAILLES WEST","Woodford - 115 Rutter Rd - Versailles",513,"Versailles - Clifton Rd - N of Substation",26.859557695303899,948,"2020-08-22",1.7143926360092925E-3,0,5.9535959719670686E-4,0,6.439603806413359E-5,8.407935535920839E-4,0.7392531517608063,0.24589930889685943,0,1.1632597517471982E-2,98.630617080959937,233.05305906118147,0.88027426160337563,1.0411392405063293,"Continue to Monitor"]
["MIDWAY","Woodford - 860 Weisenburger Rd - Midway ",516,"Midway - State HWY 341 - N of Substation",39.480262578088897,819,"2023-05-13",1.2672017944454583E-3,0,0,5.3256935736891943E-5,4.1466789993021773E-2,0,0.66498411298615556,0.22287949286866135,0,6.934914542197898E-2,86.318798323565318,126.37724866666665,0.84768009768009744,1.4407814407814405,"Continue to Monitor"]
["PAYNES MILL","Woodford - 221 Paynes Mill Rd - Versailles",517,"Versailles - Lexington Rd,  Crossfield Dr, Kroger Way - W of Substation",0.92685799541638603,107,"2020-06-20",0.41763005780346824,0,0,0,0,0,0.14920520231213874,0.12427745664739884,0,0.30888728323699421,10.587149521028037,25.870716485981305,9.3457943925233641E-2,0.19626168224299065,"Continue to Monitor"]
["PAYNES MILL","Woodford - 221 Paynes Mill Rd - Versailles",518,"Versailles - Lexington Rd, Gleneagles Way, and Bryanwood St - W of Substation",3.85254388485393,2888,"2020-06-20",8.2826552876916447E-3,0,1.5505788666502175E-3,3.7494496775473279E-4,6.1636114699294134E-3,0,0.21786479726362745,0.61059667048868627,0,0.15516674165566022,41.815557188105956,52.877977835872578,0.3398545706371191,0.65096952908587258,"Continue to Monitor"]
["PAYNES MILL","Woodford - 221 Paynes Mill Rd - Versailles",519,"Versailles - Lexington Rd, Methodist Home, Paynes Mill Rd - E of Substation",1.8511360168688,141,"2020-06-20",3.9563915284730701E-3,0,0,0,0,0,0.46963138884220446,0.51952710651674994,0,6.8851131125725641E-3,67.621867602836886,42.630969262411355,0.32801418439716312,0.34751773049645385,"Continue to Monitor"]
["SOMERSET 1","Pulaski - 144 Railroad Dr - Somerset ",522,"Somerset - Langdon St - N of Substation",3.2105037017106,290,"2024-02-01",0,0,0,2.4056130972268625E-2,1.2028065486134313E-2,0,0.88239224858002008,8.1523554961577011E-2,0,0,6.7063218362068975,20.634367810344834,7.4137931034482768E-2,0.20689655172413796,"Continue to Monitor"]
["SOMERSET 1","Pulaski - 144 Railroad Dr - Somerset ",523,"Somerset - S Main St - N of Substation",1.82835299145727,70,"2020-08-15",0,0,0,0,0,0,1,0,0,0,3.5177380892857144,8.105714271428571,4.642857142857143E-2,0.11428571428571428,"Continue to Monitor"]
["SCIENCE HILL","Pulaski - 45 E HWY 635 neat the intersection of E hWY 635 and Maple Ln - Science Hill",527,"Science Hill - N Highway 27 - NW of Substation",5.45660793360243,192,"2023-03-04",3.6732108929702342E-2,0,0,0,0.14914502849905004,0,0.22751741608613044,0.58660544648511714,0,0,26.313932276041669,65.796440947916665,0.25,0.60416666666666663,"Continue to Monitor"]
["WAITSBORO"," Pulaski - 676 Old Monticello Rd at W Summitt Dr just W of HWY 27 - Somerset ",533,"Somerset - N & S on HWY 27",24.009213184824802,1131,"2024-01-01",1.9418760839383835E-3,0,6.1830176844594256E-2,2.3645462462828339E-3,1.2935812797730518E-4,0,0.81636861651482129,0.1082110823815734,0,9.1543438008125488E-3,54.901234151414684,90.630106091069877,0.72745358090185686,1.7621573828470383,"Continue to Monitor"]
["FERGUSON SOUTH"," Pulaski - 140 McKee Rd - Somerset ",539,"Somerset - Crane Rd - N of Substation",16.506815346736602,754,"2024-01-01",4.4674519438168562E-3,0,8.1891099461127318E-4,2.7711363121220764E-3,0.32251200947597009,0,0.53695701448448818,0.12878106560793173,0,3.6924111810597584E-3,22.342722139920426,22.732051271883289,0.44893899204244064,0.34084880636604781,"Continue to Monitor"]
["FERGUSON SOUTH"," Pulaski - 140 McKee Rd - Somerset ",540,"Somerset - McKee Rd - N of Substation",0.75421439367202203,5,"2020-11-14",0,0,0,0,0,0,1,0,0,0,16.6958333,66.783333200000001,0.25,1,"Continue to Monitor"]
["BURNSIDE","Pulaski - S Hwy 27 - Burnside",544,"Burnside - City of Burnside - NW of Substation",13.910586965554799,496,"2024-02-01",4.0684960087783689E-2,0,0.22668438825738549,1.6691265677039463E-3,2.7741501750264664E-3,0,0.35393983416918456,4.6519175636934064E-3,0,0.36959562317922245,91.895094065400855,200.90557793095829,1.1441532258064517,2.9233870967741935,"Continue to Monitor"]
["WAYNESBURG","Lincoln - On Old Somerset Rd (HWY 1247) just S of Clear Fork Rd - Waynesburg ",547,"Waynesburg - KY HWY 1247 - N of Substation",14.995488603085301,361,"2023-03-04",2.446744983644329E-3,0,0,0,0.23953263471629913,0,0.67006991454888465,8.6407618202091627E-2,0,1.5430875490802247E-3,282.10992611011079,372.74542934349029,0.91828254847645396,0.83933518005540153,"Continue to Monitor"]
["LIBERTY","Casey - 1351 E KY HWY 70 - Liberty ",551,"Liberty - E KY 70 - SW of Substation",23.057739935390298,719,"2023-01-20",4.5772179023579372E-3,0,6.3576847628276333E-3,3.4112484539087552E-3,2.4217500571167467E-2,0,0.77158028251124611,0.1627157634342527,0,2.7140302364239401E-2,75.864354420723231,153.77579971210014,0.48991655076495122,0.95132127955493728,"Continue to Monitor"]
["LIBERTY","Casey - 1351 E KY HWY 70 - Liberty ",552,"Liberty - E KY 70 - NE of Substation",30.333631159501,525,"2023-02-17",5.1473426843392101E-4,0,0,0,0.7313967585286727,0,0.2262494158443335,2.0663871749893325E-2,0,2.1175219608666501E-2,153.23363490761906,446.74349205142863,0.68809523809523776,1.2152380952380948,"Continue to Monitor"]
["DANIEL BOONE","Hopkins - 500 Daniel Boone Rd - Nortonville",557,"Nortonville - Dan Boone Rd, Squire Rd, Hwy 62 - NW&SE of Subst.",10.3430431185212,136,"2022-06-03",0,0,0,0,8.9161567990515131E-5,5.0846191475672142E-4,2.3663962099104291E-3,0.99703598030734231,0,0,146.43158698345593,38.354901926470589,0.54044117647058809,0.58823529411764697,"Continue to Monitor"]
["WHITLEY CITY"," McCreary - Corner of US HWY 27 & Hicks Rd - Stearns-Whitley City ",575,"Stearns-Whitley City - Tunnel Ridge Rd - SW of Substation",11.5697716134855,613,"2024-01-01",4.5742985985472419E-2,0,0.13204439283881944,0,0,0,0.67175222099208809,0.13509572543407233,0,1.53646747495477E-2,27.874619351957588,51.61068514518761,0.24836867862969003,0.48450244698205541,"Continue to Monitor"]
["WHITLEY CITY"," McCreary - Corner of US HWY 27 & Hicks Rd - Stearns-Whitley City ",576,"Stearns-Whitley City - US HWY 27 - N of Substation",39.778856623722596,757,"2024-01-01",2.5478802959511865E-3,2.3635253209194681E-4,6.1073494292559051E-4,7.6124423536174232E-3,1.3160108986879597E-2,5.1713934021717963E-4,0.56897806837584219,0.36034117960712536,0,4.5996093565349581E-2,257.38208937087182,258.55797004227213,1.3992734478203435,0.97225891677675058,"Trees Trimmed in 2024"]
["WILMORE","Jessamine - 210 W Linden St - Wilmore ",585,"Wilmore - College St - E & S of Substation",22.235292029683201,893,"2021-01-16",2.2538641220615278E-2,0,6.9934041903625915E-4,0,4.9532471405141748E-2,0,0.65297095429792618,5.4857398453641189E-2,0,0.2194011942036394,45.398628213605825,114.60307950167974,0.46164613661814125,1.4400895856662941,"Continue to Monitor"]
["INNOVATION DRIVE","Fayette - 2350 Innovation Dr - Lexington ",594,"Lexington - Greendale Rd - W of Substation",28.65806092570525,2908,"2024-01-01",0,0,0,0,6.4371373307543514E-2,0,0.17686653771760155,1.2998065764023211E-2,0,0.74576402321083168,1.5534445204607981,4.4444922049518576,1.1519944979367262E-2,2.6478679504814303E-2,"Continue to Monitor"]
["INNOVATION DRIVE","Fayette - 2350 Innovation Dr - Lexington ",595,"Lexington - Drummond Dr and Georgetown Rd - NW of Substation",21.7132300023843,1539,"2019-11-09",2.5376698366739053E-3,0,0,0,3.3126159631913073E-2,2.248791486741715E-2,2.2015325861767716E-3,0.93942041284976163,0,2.2631022805747614E-4,9.7449940423976606,23.828319254710852,8.4470435347628325E-2,0.23066926575698504,"Tree Trim Scheduled for 2025"]
["INNOVATION DRIVE","Fayette - 2350 Innovation Dr - Lexington ",596,"Lexington - Spurr Rd and Kearney Rd - NW of Substation",26.843193373965399,894,"2019-11-09",1.5387622149837134E-2,0.45019543973941367,6.0586319218241041E-3,0,0,0,0.51182410423452762,1.6078175895765472E-2,0,4.560260586319218E-4,19.571420578299776,28.649776281879195,0.12332214765100671,0.14988814317673377,"Continue to Monitor"]
["JOYLAND","Fayette - 2375 Paris Pike - Lexington",599,"Lexington - US 27 & US 68 - SW of Substation",15.670846326806201,1168,"2024-01-01",5.5172916740283184E-2,0,2.9471667727997558E-4,0,6.7181869511183823E-2,0,0.61537969958446459,0.25967997678354338,0,2.2908207032451165E-3,75.290011406678076,197.69925797859591,0.7264554794520548,1.8467465753424659,"Trees Trimmed in 2024"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",603,"Mount Sterling - S Queen St - N of Substation",15.660593889673599,1303,"2023-07-14",0,0,9.7016612046558939E-2,0,0,0,0.1964063736015369,0.23946208611142503,0,0.46711492824047918,8.2097691208749044,13.582450752877975,0.15080583269378361,0.12893323100537221,"Continue to Monitor"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",605,"Mount Sterling - 686 Bypass & Spencer Rd - E of Substation",39.633163870095402,1337,"2019-06-01",1.2648589195820466E-2,0,0,0,0.189977367908964,0,0.12372562291129066,0.11303354625830196,0,0.56061487372562291,39.614304407068069,98.222538010471226,0.48784592370979796,0.89528795811518302,"Continue to Monitor"]
["A O SMITH","Montgomery - 1871 Owingsville Rd - Mt. Sterling",607,"Mount Sterling - Maysville Rd - W of Substation",36.847741414422401,1095,"2023-06-14",7.6154746444775782E-4,0,2.0040722748625205E-4,3.2906866753242589E-3,1.466980905199365E-3,0,0.29075080563705447,0.59650810446827951,0,0.10702146762220832,17.039988579223746,19.423363767123291,0.25068493150684934,0.14246575342465756,"Continue to Monitor"]
["A O SMITH","Montgomery - 1871 Owingsville Rd - Mt. Sterling",608,"Mount Sterling - 6 miles W of Substation",6.3003784778135898,216,"2023-06-14",0.11593735209328342,0,7.9278000086054817E-2,0,1.8716922679746998E-3,0,0,0.79080074007142553,0,1.2112215481261564E-2,37.170833321759254,50.928858009259258,0.44097222222222227,0.6342592592592593,"Continue to Monitor"]
["OWINGSVILLE","Montgomery - 69 W Paul Lewis Dr - Owingsville ",610,"Owingsville - Slate Ave - S of Substation",8.6332782881402306,478,"2023-03-24",0,0,3.9955183349474926E-2,0,2.9599245459782122E-2,0,0.35021553770485575,0.5802300334858872,0,0,53.100331233263603,127.48622732008369,0.75889121338912113,1.8263598326359827,"Reliability Improvements Completed in 2024"]
["OWINGSVILLE","Montgomery - 69 W Paul Lewis Dr - Owingsville ",611,"Owingsville - W Main St - SW of Substation",25.3443913494566,729,"2023-03-24",6.2628274779669201E-4,0,0,0,2.4432572739345647E-2,0,0.94580013280212483,2.7941265242062058E-2,0,1.1997464686707715E-3,60.556647225651574,30.998033825788752,0.75445816186556913,1.0397805212620026,"Continue to Monitor"]
["SALT LICK","Bath - 11457 US HWY 60 E - Salt Lick ",613,"Salt Lick - US HWY 60 - NE of Substation",10.213285203138501,257,"2023-03-03",2.635707561970505E-3,0,0,0,0,0,0.81568481330404774,3.0322403514276751E-2,0,0.15135707561970504,126.92746431809337,191.35324252529185,1.1439688715953304,1.7042801556420231,"Reliability Improvements Completed in 2024"]
["FARMERS"," Rowan - 6901 US 60 W - Morehead ",614,"Morehead - US HWY 60 - SW of Substation",5.2856710889703091,142,"2022-11-18",0,0,0,0,1.8152978498413817E-2,0,0.9818470215015862,0,0,0,14.55173121302817,8.5766431901408442,0.14964788732394366,0.23943661971830982,"Continue to Monitor"]
["FARMERS"," Rowan - 6901 US 60 W - Morehead ",615,"Morehead - US HWY 60 - NE of Substation",22.338095806862199,629,"2024-01-01",8.5837217512225983E-4,0,2.4012916798827309E-4,0,1.863689064983612E-4,0,0.96142342836355554,3.074190952864795E-2,0,6.5497918581875984E-3,48.313626116454685,67.177159496025439,0.32472178060413365,0.39586645468998422,"Continue to Monitor"]
["MOREHEAD WEST","Rowan - 133 Gregory Ct - Morehead ",616,"Morehead - US HWY 60 - SW of Substation",8.0444666322824894,373,"2022-09-09",1.7609533168000249E-2,0,0,0,2.9346622369878183E-2,0,0.90304618408123161,4.1910376990625928E-2,0,8.0872833902640648E-3,40.927066568364616,32.283958887399464,0.3130026809651475,0.34048257372654162,"Continue to Monitor"]
["MOREHEAD WEST","Rowan - 133 Gregory Ct - Morehead ",617,"Morehead - Clearfield Rd - S of Substation",27.818578479642099,1472,"2024-01-01",4.6692758533403433E-3,0,2.2742761454134781E-3,0,2.5795899293183013E-2,0,0.6937282162120062,0.25549778997994432,0,1.8034542516112702E-2,38.830497051970113,38.950430249320654,0.33203124999999994,0.43478260869565211,"Reliability Improvements Completed in 2024"]
["MOREHEAD","Rowan - 100 E Wilkinson Blvd - Morehead ",618,"Morehead - Wilkinson Blvd - SW of Substation",1.2048380696102099,111,"2022-07-15",0,0,0,0,0,0,0,1,0,0,2.8995495495495494,4.7319819819819822,4.0540540540540543E-2,9.90990990990991E-2,"Continue to Monitor"]
["MOREHEAD","Rowan - 100 E Wilkinson Blvd - Morehead ",619,"Morehead - Wilkinson Blvd - N of Substation",2.3139357986268698,204,"2022-07-15",0,0,0,0,0.95825771324863884,0,1.8148820326678767E-2,0,0,2.3593466424682397E-2,3.458169933823529,8.093464049019607,4.1666666666666664E-2,6.8627450980392149E-2,"Continue to Monitor"]
["RODBURN"," Rowan - 1974 US HWY 60 E - Morehead ",622,"Morehead - Midland Trail - NE of Substation",5.6183327727111303,234,"2024-01-01",1.1624120618236617E-3,0,0,0,7.1940811643809684E-4,0,0.83151461913019775,0.16447941356879434,0,2.1241471227461703E-3,11.358279911324786,15.006196572649573,8.5470085470085472E-2,0.12820512820512819,"Continue to Monitor"]
["RODBURN"," Rowan - 1974 US HWY 60 E - Morehead ",623,"Morehead - Rodburn Hollow Rd - NW of Substation",4.4060758165570499,307,"2024-01-01",3.7204726892081067E-4,0,0,0,2.3760578123620587E-2,0,0.33261656430111869,0.6432508103063399,0,0,29.294991854234524,52.346959820846905,0.36563517915309446,0.57328990228013033,"Trees Trimmed in 2024"]
["ROCKWELL","Clark - 5835 Rockwell Rd - Winchester  ",626,"Winchester - Lexington Rd - E of Substation",16.918581775838799,596,"2022-03-04",5.3975623911781775E-2,0,0,0,0,0,2.6842716192687173E-3,0.50007254788160183,0,0.44326755658734762,12.541687634228186,11.561884781879193,0.15729865771812079,0.17785234899328858,"Continue to Monitor"]
["PARKER SEAL","Clark - 390 Mt Sterling Rd - Winchester ",629,"Winchester - Mt Sterling Rd - NE & S of Substation",16.617708904252702,468,"2021-04-17",1.2174423234080004E-2,0,5.1757014437482972E-3,0,1.9089327996982586E-2,0,0.69773484483372794,0.26582570249146115,0,0,44.770566224893159,101.96737890384614,0.36698717948717946,0.54700854700854695,"Continue to Monitor"]
["PARKER SEAL","Clark - 390 Mt Sterling Rd - Winchester ",630,"Winchester - Cherry St - SW of Substation",18.130271627842902,1414,"2024-01-01",2.6634963908423435E-2,0,4.5798610035420349E-3,0,3.7777399134628291E-2,0,0.63758687278622839,0.29075921393682169,0,2.6616892303561656E-3,24.332349122171152,35.390393675388971,0.45615275813295614,1.2765205091937761,"Trees Trimmed in 2024"]
["PARKER SEAL","Clark - 390 Mt Sterling Rd - Winchester ",631,"Winchester - Rolling Hills Ln - N of Substation",19.164328021687702,383,"2021-04-17",1.7856677354604938E-3,0,6.5691718151247363E-3,0,0,0,0.98974218607439846,1.3034071061755429E-3,0,5.9956726884074975E-4,46.555548295039166,159.53507396866843,0.19386422976501305,0.60574412532637079,"Continue to Monitor"]
["WINCHESTER","Clark - 2 Almond St - Winchester ",632,"Winchester - 1st St - S of Substation",0.60306306672596299,76,"2021-07-03",0,0,0,0,0,0,1,0,0,0,10.024451749999999,18.994736842105262,0.13157894736842105,0.22368421052631576,"Continue to Monitor"]
["WINCHESTER","Clark - 2 Almond St - Winchester ",634,"Winchester - Maple St - S of Substation",1.6720964614407301,261,"2021-07-03",0,0,0,0,1.1644154634373545E-3,0,0.9038192827200745,0,0,9.5016301816488125E-2,8.4629948869731795,16.448339704980842,0.34003831417624519,0.15708812260536398,"Continue to Monitor"]
["WINCHESTER SOUTH","Clark - 105 Hood Ave - Winchester",637,"Winchester - Belmont Ave & S Burns Ave - NE of Substation",2.9621533034513501,374,"2024-01-01",0,0,0,0,2.2165660132806115E-3,0,0.94688694574109389,4.4472203698659729E-2,0,6.4242845469658404E-3,10.294652403074865,16.369652403743313,6.7513368983957225E-2,8.5561497326203204E-2,"Continue to Monitor"]
["WINCHESTER WATER","Clark -  335 Waterworks Rd - Winchester ",642,"Winchester - Waterworks Rd - E of Substation",25.12538568178212,233,"2022-12-02",2.2473174626062554E-3,0,2.180495816613268E-4,0,5.1843046504348685E-2,0,0.93036129408909785,8.3667734640692978E-3,0,6.9635188982165655E-3,20.40094775643777,24.671959909871244,0.44742489270386282,1.2017167381974256,"Continue to Monitor"]
["EWINGTON","Montgomery - 4006 Old Owingsville Rd - Mt Sterling",647,"Mt. Sterling - Owingsville Rd, Quisenberry Rd - N of Substation",9.4442927532176704,61,"2023-04-14",1.8097299599020615E-2,0,1.6713388453213157E-2,0,0.87956424541357647,0,1.0822894858237821E-2,7.2637592704304324E-2,0,2.164578971647564E-3,32.203142045081961,55.957650213114761,0.34426229508196726,0.78688524590163944,"Continue to Monitor"]
["MUHLENBERG PRISON","Muhlenberg - 1200 River Rd - Central City",657,"Central City - Hwy 431, S R 81, & S Carrolton St - NW of Substation",44.957719624264399,714,"2018-10-26",4.5745803402516311E-4,8.3734394500643952E-5,1.9400280492097249E-3,0,1.7478376770701517E-2,0,0.97843241238790557,1.2904521403562445E-3,0,3.1753822330114333E-4,57.019736214986004,85.326610620448193,0.85714285714285687,1.225490196078431,"Continue to Monitor"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",658,"Mt Sterling - US 460 Hwy, By-Pass, Burley Dr - SW of Substation",4.8768455632387901,348,"2023-07-14",0,0,0,0,0,0,1,0,0,0,2.3098778714080463,2.6019157068965519,2.8017241379310345E-2,2.2988505747126436E-2,"Continue to Monitor"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",663,"Mt Sterling - S Queen St - NW of Substation",1.1705916049043701,1094,"2023-07-15",3.3021885844519987E-4,0,2.3675512797454957E-3,0,2.9483826646892848E-4,0,0.99015829866526717,4.2486194198172594E-3,0,2.6004735102559489E-3,7.2486822038391221,14.735268122486289,7.7010968921389394E-2,0.11882998171846437,"Continue to Monitor"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",664,"Mt Sterling - S Queen St - NW of Substation",0.50811145468914698,94,"2023-07-15",0,0,0,0,0,0,0,1,0,0,0.65385637765957438,1.5028368723404253,1.329787234042553E-2,2.1276595744680851E-2,"Continue to Monitor"]
["BEDFORD","Trimble - 660 Cutshaw - Bedford",700,"Bedford - City of Bedford/Highway 421N - W of Substation",33.690918348933401,897,"2020-03-21",1.0984932828620203E-2,0,0,0,0.60058079121205377,0,4.8151859274103764E-3,0.37310732576263639,0,1.05117642692793E-2,72.391471563545139,80.174526191750275,0.61900780379041243,0.48717948717948717,"Continue to Monitor"]
["BROMLEY","Owen - 7205 Hwy 127 - New Liberty",701,"Bromley - State Hwy 36, St Hwy 227, & Alexander Rd - W of Subst.",77.366666347367399,959,"2018-12-08",8.4508352801603102E-3,0,5.3403430181744472E-3,0,0.15821306207359506,0,0.1279489028536108,0.32938318539663758,0,0.3706636713778218,109.17350102867572,308.84169271220026,0.96063607924921857,3.0145985401459883,"Continue to Monitor"]
["CAMPBELLSBURG","Henry - 379 Turners Station Rd. - Campbellsburg",703,"Campbellsburg - Hwy 193 & Webb Ln - W & E of Sub.",52.2989854761109,949,"2023-09-09",9.0136407373167561E-3,0,0.11605946833198121,0,6.250589589268532E-2,0,0.12067713148312359,5.8982510423938261E-2,0,0.63276135313095483,95.854614494731294,201.88159464699677,1.2378819810326664,1.5047418335089562,"Continue to Monitor"]
["CARROLLTON","Carroll - 802 Mason St - Carrollton ",705,"Carrollton - 9th St - N of Substation",5.3476921642894402,500,"2024-01-01",7.810947251262074E-3,0,0,0,0.13674126485669993,0,0.82287236156934451,0,0,3.2575426322693488E-2,33.924183329999998,100.62773332800001,0.26150000000000001,0.58000000000000007,"Continue to Monitor"]
["CARROLLTON","Carroll - 802 Mason St - Carrollton ",707,"Carrollton - HWY 227 - SE of Substation",32.327407308131832,754,"2019-12-31",4.1857494258184637E-3,0,1.0464373564546159E-3,0,9.8636913417501332E-2,0,0.18157726648818343,0.69817756818830434,0,1.6376065123737821E-2,48.889732530172431,97.49292660212204,0.84515915119363405,2.0596816976127315,"Tree Trim Scheduled for 2025"]
["CARROLLTON","Carroll - 802 Mason St - Carrollton ",708,"Carrollton - 11th St - N of Substation",15.6697820977377,795,"2024-01-01",1.8112979710947033E-3,0,1.3836303945862316E-3,0,0.92549779248059783,0,3.6880039244789373E-2,3.4427239908931963E-2,0,0,49.686991609119502,99.078364776100628,0.41572327044025154,0.79622641509433956,"Continue to Monitor"]
["CARROLLTON","Carroll - 802 Mason St - Carrollton ",709,"Carrollton - KY 36 - NW of Substation",22.607459669714,389,"2021-10-02",7.2086217971593751E-3,0,1.9801901680425699E-2,3.7510210231643392E-3,0.79769863361327209,0,1.070587395617729E-2,0.13444198605857302,0,2.6391961871228161E-2,140.93065551542412,324.15586973007703,0.6053984575835476,0.87146529562982022,"Continue to Monitor"]
["DAYTON-WALTHER","Carroll - 5220 Highway 42 E - Carrollton",710,"Carrollton - D Rd & US HWY 42 - SW of Substation",5.4048627491988901,50,"2021-08-07",0.21898989898989898,0,0,0,0,0,0,7.5959595959595963E-2,0,0.70505050505050504,53.311666649999999,49.497999999999998,0.55000000000000004,0.87999999999999989,"Continue to Monitor"]
["DOW CORNING","Carroll - 4790 Highway 42 E - Carrollton",712,"Carrollton - US HWY 42 - NE of Substation",1.58657888924688,6,"2023-11-10",0,0,0,0,1,0,0,0,0,0,37.204166666666666,148.81666666666666,0.125,0.5,"Continue to Monitor"]
["OWENTON","Owen - 327 Gayle Avenue - Owenton",715,"Owenton - Madison St - S of Substation",1.4125595374148201,163,"2022-01-14",0,0,0,0,0.96299902629016554,0,3.7000973709834468E-2,0,0,0,1.9694018374233131,6.2946830184049087,1.8404907975460124E-2,4.9079754601226995E-2,"Continue to Monitor"]
["OWENTON","Owen - 327 Gayle Avenue - Owenton",716,"Owenton - Gratz Rd- SW of Substation",19.175694815361201,490,"2022-03-04",1.8216693155039185E-2,0,1.3700882336822491E-3,0,1.4906559982462871E-3,0,0.54097659889296867,3.1599715021647393E-2,0,0.40634624869841618,67.73769557040815,85.146632640816279,0.31122448979591832,0.25510204081632643,"Continue to Monitor"]
["GHENT CITY","Carroll - 402 Liberty - Ghent",717,"Ghent - US HWY 42 - NE & SW of Substation",8.7250359574426692,299,"2021-07-31",0,0,0,0,0,0,0.95708451282494544,3.997666227283532E-2,0,2.9388249022192451E-3,105.62540411956522,154.77525083277592,0.9205685618729097,1.2842809364548493,"Continue to Monitor"]
["HUNTERS BOTTOM","Trimble - 400 Hunter Heights Rd - Milton",719,"Milton - N Spillman Lan, HWY 421 N - SE of Substation",25.573878665880901,506,"2020-03-21",8.8859219031208977E-4,0,4.314137637066473E-2,0,0.91339699322053769,0,2.387020239153086E-2,1.6591865547431427E-2,0,2.110970279523137E-3,440.46960637697646,1400.285375482214,1.1669960474308301,2.1818181818181817,"Continue to Monitor"]
["LAWRENCE","Henry - 9255 HWY 55 - Campbellsburg",720,"Campbellsburg - HWY 55, HWY 316 - N & S of Substation",11.288065366430287,109,"2020-03-28",1.3611963190184049E-2,0.4866756134969325,0.30952837423312884,0,0,0,0.19018404907975461,0,0,0,28.569495394495416,59.042660513761469,0.30275229357798167,0.47706422018348627,"Continue to Monitor"]
["LAWRENCE","Henry - 9255 HWY 55 - Campbellsburg",720,"Campbellsburg - HWY 55, HWY 316 - N & S of Substation",11.288065366430287,109,"2020-03-28",1.3611963190184049E-2,0.4866756134969325,0.30952837423312884,0,0,0,0.19018404907975461,0,0,0,28.569495394495416,59.042660513761469,0.30275229357798167,0.47706422018348627,"Continue to Monitor"]
["METAL AND THERMIT","Carroll - 2318 Highland Ave - Carrollton",722,"Carrollton - Easterday Rd, Highland Ave - NE and SE of Subst.",16.054682024719401,438,"2024-01-01",1.9094167481264256E-2,0,1.2381883349625285E-3,0,0.70824372759856635,0,0.13913326816552624,0.13229064841968069,0,0,14.42590372431507,28.909665139269411,0.27111872146118715,0.1095890410958904,"Continue to Monitor"]
["SCHOLLS","Owen - 970 HWY 127 N - Owenton",724,"Owenton - HWY 127 N, State HWY 845 - NE of Substation",12.894151038336,185,"2022-01-15",0,0,0.8682227084852906,0,0,0,4.9963530269876003E-2,0,0,8.1813761244833458E-2,31.421599091891892,44.462612605405411,0.34054054054054056,0.22162162162162163,"Continue to Monitor"]
["WARSAW","Gallatin - RR 1 Box 51 - Warsaw",728,"Warsaw - Dry Creek Rd - S & E of Substation",9.8429519203549898,99,"2018-12-22",4.1179994010182687E-3,0,0,0,0,0,0,0,0,0.99588200059898169,87.91607743686869,134.90925925252526,0.4267676767676768,0.67676767676767668,"Continue to Monitor"]
["MARKLAND DAM","Gallatin - RR 2 Box 26B - Warsaw",729,"Warsaw - US HWY 42 - N of Substation",0.25894373743928301,2,"2021-08-07",0,0,0,0,0,0,1,0,0,0,115.55,462.2,0.25,1,"Continue to Monitor"]
["SPARTA","Owen - RR 1 Box 136C - Sparta",730,"Sparta - State HWY 467 - NE & SE of Substation",28.600471392161101,382,"2023-09-16",3.4966000165628422E-4,0,0,0,0.78263570028616913,0,5.017160944818131E-2,0.12597881796516283,0,4.0864212298830478E-2,467.027192396597,568.98965967277502,1.7316753926701574,2.93455497382199,"Continue to Monitor"]
["SPARTA","Owen - RR 1 Box 136C - Sparta",731,"Sparta - State HWY 467 - SW of Substation",6.2323898124998296,110,"2023-10-07",5.9414524683802528E-3,0,0,0,0.89955630354957161,0,5.1382088943288454E-2,4.312015503875969E-2,0,0,243.14662878409086,356.50393939090907,0.76590909090909098,1.9818181818181819,"Continue to Monitor"]
["STANFORD NORTH","Lincoln - 300 Lee Dr - Stanford",767,"Stanford - US Hwy 27, E Main St - SE of Substation",15.628448243815599,596,"2018-06-16",1.9070018752185107E-4,0,8.9120554301878402E-2,0,0,0,4.3924609859199694E-2,0.84837216201040377,0,1.8391973640996304E-2,22.489142893875837,31.050727063758391,0.21644295302013422,0.3741610738255034,"Tree Trim Scheduled for 2025"]
["HARRODSBURG NORTH","Mercer - 1000 Warwick Rd - Harrodsburg",773,"Harrodsburg - Warwick Rd, N Greenville St - S of Substation",4.1400611298111398,197,"2021-11-13",0.54796083277878127,0,0,0,0,0,0,0,0,0.45203916722121873,14.426015225888325,53.398815563451777,0.18401015228426396,0.6649746192893401,"Continue to Monitor"]
["MOREHEAD","Rowan - 100 E Wilkinson Blvd - Morehead ",780,"Morehead - 2nd St - E of Substation",15.285039131670199,1359,"2024-01-01",1.5697009062509665E-2,0,0,0,7.1989731217716749E-2,0,0.41012753497675092,0.43657274236285093,0,6.5612982380171769E-2,24.672688246320824,40.921510908756439,0.27612214863870499,0.42457689477557037,"Trees Trimmed in 2024"]
["DETROIT HARVESTER","Bourbon - 115 W 20th St - Paris",801,"Paris - Bypass Rd, S Main, US 27/66, Bethlehem Rd - SW of Sub",74.482798661354806,1210,"2020-07-30",1.6325089214908804E-2,0,0,1.6232157018239493E-3,2.2539155432196669E-2,0,0.34816737708168116,0.58162544607454403,0,2.9719716494845359E-2,22.671446271280992,48.393209353719023,0.22272727272727272,0.4024793388429751,"Continue to Monitor"]
["PARIS 12KV","Bourbon - 520 Scott Ave - Paris",806,"Paris - Cane Ridge Rd/KY 537, US HWY 68, & Bypass Rd - NE of Substation",115.26989821338063,1054,"2021-12-11",2.8889698610171256E-2,0,0.25149453638340213,6.4065859703775485E-5,3.6037046083373706E-3,9.4577225387698551E-3,0.49223401656903298,1.30974641931906E-2,0,0.20115879123739203,40.54366697201138,49.214294732447804,0.4475806451612907,0.54743833017077836,"Continue to Monitor"]
["MILLERSBURG","Bourbon - Vimont Ln. – Millersburg",808,"Millersburg - Old US Hwy 68/Vimont St/HWY 68/HWY 1879 - NE/NW/SW of Subst.",36.119983221019098,625,"2022-01-15",2.8073840729919857E-3,0,3.5513952590029434E-3,0,0.11938999243747314,5.8759201527739237E-4,0.52820441673331486,0.33807487445661338,0,7.384345025326304E-3,88.806246654133346,236.89917331200002,1.1512000000000002,2.5599999999999996,"Continue to Monitor"]
["HANSON","Hopkins - 235 Fowler Rd - Hanson",809,"Hanson - Hanson Rd, N Main, Hwy 1069, & University Circle Dr - SW of Substation",1.36616401539456,42,"2019-06-22",0,0,0,0,0,0,1,0,0,0,32.519841255952386,51.847619047619048,0.39285714285714279,0.2857142857142857,"Continue to Monitor"]
["HANSON","Hopkins - 235 Fowler Rd - Hanson",810,"Hanson - Hanson Rd & Hwy 1069 - SW of Substation",22.067079243696,891,"2019-08-03",4.3317055525411464E-2,0,0.43196479170434676,2.9224694037499246E-2,6.0001808645324652E-2,0,0.10979984325073852,0.12111894857418461,0,0.20457285826249472,55.883548437149273,65.627235306397296,0.92283950617283983,1.7272727272727282,"Continue to Monitor"]
["HANSON","Hopkins - 235 Fowler Rd - Hanson",811,"Hanson - US HWY 41 & City of Hanson - N of Substation",17.651724777286201,624,"2019-08-03",1.7639365565959148E-2,0,1.2899436873146514E-2,0,0.476056695878178,0,0.46845531638399251,2.4949185298723801E-2,0,0,63.768803400641033,75.427483948717935,0.7716346153846152,0.88141025641025594,"Continue to Monitor"]
["NORTONVILLE","Hopkins - 55 Holly Ln - Nortonville ",818,"Nortonville - Mockingbird St, US 41, & Wells Rd - N of Substation",18.023211056191901,368,"2022-11-04",1.9024649187592318E-2,0,1.0140094165435746E-2,0,1.2093796159527326E-3,0,0.96950586225997049,0,0,1.2001477104874446E-4,27.415670275815216,59.404664842391298,0.46942934782608697,1.1114130434782608,"Continue to Monitor"]
["EAST DIAMOND","Hopkins - 550 East Diamond Rd - Madisonville",825,"Madisonville - Randall Dr, Meadowlark Ln - W of Substation",9.5234332486690594,306,"2019-11-16",0,0,0,0,5.5583184623935876E-4,4.0741499185755099E-2,2.2525816926542435E-3,0.9564500872753513,0,0,23.556127443627449,72.098638336601311,0.23529411764705885,0.62418300653594772,"Continue to Monitor"]
["EAST DIAMOND","Hopkins - 550 East Diamond Rd - Madisonville",827,"Madisonville - Hwy 85, Hwy 892, & Hwy 1221 - NE & SE of Substation",22.601325614161802,366,"2020-03-28",7.7890285968621343E-4,0,0.25017618040873857,4.2283298097251587E-3,0,0,0.69856459330143539,0,0,4.6251993620414676E-2,54.552868845628417,110.46785062841531,0.76844262295081966,1.0601092896174864,"Continue to Monitor"]
["WHITE PLAINS","Hopkins - 336 NW Railroad - White Plains",837,"White Plains - City of White Plains, HWY 813, White Plains Rd - W/SE of Substation",41.522912531166,493,"2022-07-22",4.6252915489401319E-4,0,4.2782450937803291E-4,9.3941885276015621E-5,2.3270063174421957E-3,0,0.98991830047760776,5.6903651527064243E-4,0,6.2013611401313751E-3,66.739934059837736,63.393509107505082,1.0780933062880327,1.2576064908722109,"Continue to Monitor"]
["WHITE PLAINS","Hopkins - 336 NW Railroad - White Plains",839,"White Plains - US 62, Main St/Hwy 813, & Concord Church Rd - NE of Substation",22.259457443647101,351,"2022-09-09",4.9420178808120456E-4,0,1.2925277534431502E-3,0,0.56637552408621239,0,0.42970549797377267,1.9607561540794455E-3,0,1.7149224441108466E-4,74.205650498575494,81.644207005698021,1.0819088319088315,0.91452991452991406,"Continue to Monitor"]
["ASHBYBURG PUMP","Hopkins - 250 High Banks Ferry - Ashbyburg",843,"Ashbyburg - Highbanks Ferry Rd - S of Substation",6.3191873605345599,81,"2023-09-09",0,0,0,0,0,0,1,0,0,0,19.560802453703705,27.430452666666664,0.16049382716049382,0.1728395061728395,"Continue to Monitor"]
["SYLVANIA","Clark - 439 E Washington St - Winchester",847,"Winchester - E Washington, E Broadway St, Hickman St - SW of Subst.",14.299599092506313,1508,"2024-01-01",6.8073126691011463E-3,0,0.74901207432662409,0,3.4036563345505731E-3,3.9228581482955759E-4,0.11560893719388726,0.10902661197740895,0,1.5749121683598415E-2,24.985297850132632,26.587643675066317,0.32078912466843496,0.38660477453580905,"Continue to Monitor"]
["CYNTHIANA","Harrison - 208 McIlvain Blvd - Cynthiana",851,"Cynthiana - S Walnut St, Oddvill Rd - NNE of Subst.",3.20438227450544,456,"2020-06-13",0,0,0,0,2.1300631533101046E-2,0,0.91064623257839727,6.5820993031358882E-2,0,2.232142857142857E-3,1.0374086249999999,1.7570906425438597,1.425438596491228E-2,3.0701754385964911E-2,"Continue to Monitor"]
["CYNTHIANA","Harrison - 208 McIlvain Blvd - Cynthiana",853,"Cynthiana/Berry - River Rd, Poplar St, US 27, City of Berry - N of Subst.",76.589389506246803,922,"2022-10-07",6.5055073857813654E-4,1.8561000876690776E-3,3.6628315758377333E-5,0,2.1439508734658906E-2,0,0.52398955615240239,0.42420924642017932,0,2.7818409550753709E-2,37.660231372017364,62.58179680585684,0.29338394793926231,0.67678958785249421,"Continue to Monitor"]
["CYNTHIANA","Harrison - 208 McIlvain Blvd - Cynthiana",854,"Cynthiana - Water Works Ave, Ney Lair Rd - S of Substation",1.1791328439426001,38,"2020-06-13",0,0,0,0,0,0,1,0,0,0,22.022807013157895,50.535087710526312,0.3289473684210526,0.52631578947368418,"Continue to Monitor"]
["CYNTHIANA","Harrison - 208 McIlvain Blvd - Cynthiana",855,"Cynthiana - City of Cynthiana (Eastern) - E of Substation",14.5325127033099,1316,"2024-01-01",3.1730979648406155E-2,0,0.17559892875379052,5.9606306597334386E-3,0,0,3.7931286016485523E-2,3.8806623386096722E-2,0,0.70997155153548763,25.769253415083586,72.626950349544074,0.25265957446808507,0.61474164133738596,"Reliability Improvements Completed in 2024"]
["KAWNEER","Harrison - RR 7 Box 729 White Oak Pike - Cynthiana",856,"Cynthiana - Western Ave, Ladish Rd, Hwy 27 - S of Substation",13.9033715430021,448,"2020-11-21",0.3021285389543294,0,0,0,0,0,0.53296135565199421,0.13184542260797685,0,3.3064682785699524E-2,6.3224702327008933,6.6130208258928578,0.1021205357142857,0.11607142857142858,"Continue to Monitor"]
["ASHLAND PIPE","Fayette - 900 Forest Lake Dr - Lexington",862,"Lexington - No Road - NE of Substation",5.0065439041293699E-3,1,"No Trimming Required",0,0,0,0,1,0,0,0,0,0,210.70416650000001,497.03333300000003,0.5,1,"Continue to Monitor"]
["WEST HICKMAN","Fayette - 3172 Ashgrove Rd - Lexington",864,"Lexington - Lauderdale Dr, Whitfield Dr, Ridgewater Dr - NW of Subst",27.196824010191001,2196,"2023-12-09",7.2587171104158456E-4,0,0,0,0.84335002798862013,0,0.15190225085251505,9.3571247441272666E-4,0,3.0861369734105151E-3,21.574749543602,38.956071644353358,0.14093806921675775,0.19763205828779606,"Continue to Monitor"]
["WEST HICKMAN","Fayette - 3172 Ashgrove Rd - Lexington",865,"Lexington - Saron Dr, Tates Creek Rd, Kenesaw Dr - NE of Subst",24.498527162918958,1296,"2024-01-01",1.0178829623274067E-4,0,0,0,0.57959149625816297,0,0.40557273543384653,3.9622956289622957E-3,0,1.0771684382795493E-2,46.466017229938281,94.679179524691364,0.78722993827160503,0.3603395061728395,"Continue to Monitor"]
["MACKVILLE","Washington - 4685 Texas Rd - Springfield ",866,"Springfield - Texas Mackville Rd - S of Substation",9.8419141174571401,48,"2020-09-19",0.31506849315068491,0,0,0,0,0,0,0,0,0.68493150684931503,202.75729165624998,235.21874999999997,1.0520833333333333,1.0416666666666665,"Continue to Monitor"]
["SHANNON RUN","Woodford - 2770 Shannon Run Rd - Versailles",868,"Versailles - Shannon Run, Lexington Rd, Pisgah Rd - N of Subst",66.207411624902406,1129,"2021-08-07",3.8309332407346535E-3,0,1.2985166792809893E-3,0,5.9301363189664903E-3,1.7643195036530965E-4,0.93299125762829382,3.9638190887008817E-2,0,1.6134533295349893E-2,101.43045096988489,110.94087685916746,0.88108945969884844,0.74136403897254199,"Continue to Monitor"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",873,"Lexington - Bryant Rd & I75 - E of Substation",32.839418711284203,2076,"2022-09-03",3.7678475658500549E-2,0,0.3095736822399644,0,0,0,0.63503435435070776,9.3804073950396159E-3,0,8.3330803557876195E-3,63.069960258309251,95.124068720134872,0.62825144508670516,0.62957610789980745,"Continue to Monitor"]
["CARLISLE","Nicholas - 104 S Elm St - Carlisle",877,"Carlisle/Sharpsburg - S Upper Jackstown, Hwy 1285, Hwy 11 - SSE of Subst",45.137553870639302,695,"2019-12-31",7.9147252186123705E-3,0,1.0440507344828529E-3,0,3.3104158878078577E-2,0,3.3085922184026478E-2,9.3102882309494928E-2,0,0.83174826067530483,43.971768575539571,94.030815335251802,0.65863309352517962,1.7827338129496391,"Continue to Monitor"]
["CARLISLE","Nicholas - 104 S Elm St - Carlisle",879,"Carlisle - City of Carlisle, Hwy 36 - E of Substation",35.405077260962202,1091,"2019-10-21",1.1372372109723482E-2,4.0278589742999584E-4,2.117503003631978E-4,0,0,0,0.94442014942205976,3.0818875237643678E-2,0,1.2774067032779867E-2,19.43900854560037,15.796959968835926,0.24014665444546279,0.25206232813932161,"Continue to Monitor"]
["DETROIT HARVESTER","Bourbon - 115 W 20th St - Paris",883,"Paris - Lexington Rd and Hutchison Rd - SW of Sub",16.392179154317901,746,"2020-07-20",6.8568970694454584E-2,1.1540428018406252E-2,3.1650962919679593E-4,4.2038971262548797E-3,2.3373018771455701E-3,0,0.77505092558777466,6.3569741679448788E-2,0,7.4412225387318509E-2,66.444275007037518,97.342269860589795,0.62801608579088486,0.8351206434316355,"Continue to Monitor"]
["MAYSVILLE WEST","Mason - 210 Cox Alley - Maysville",900,"Maysville - Maddox Aly, 4th St, Hwy 62 - SE of Substation",1.5420754475669001,169,"2019-09-07",0,0,0,0,0,0,1,0,0,0,3.3439349112426036,4.9559171597633132,7.2485207100591711E-2,4.142011834319527E-2,"Continue to Monitor"]
["MAYSVILLE WEST","Mason - 210 Cox Alley - Maysville",902,"Maysville - Washington St, E 6th, Edgemont Rd - SW of Subst.",3.98561851336075,166,"2024-01-01",0,0,0,0,0.77754361692714824,0,0.14771438453680391,5.1214195510010371E-2,0,2.3527803026037436E-2,99.976656617469871,112.75863451204819,0.81174698795180711,1.1746987951807228,"Continue to Monitor"]
["MAYSVILLE WEST","Mason - 210 Cox Alley - Maysville",903,"Maysville - W 2nd St, W Mcdonald Pkwy - NW of Subst.",3.3284126886857299,351,"2024-01-01",0,0.12570668440305952,0,0,1.0364704578206407E-2,0,0.75684513911983153,0.10708347189890256,0,0,37.107514240740741,38.441642917378914,0.40028490028490032,0.36467236467236469,"Continue to Monitor"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",904,"Lexington - Bryant Rd - NE of Substation",18.6571180267896,1195,"2024-01-01",0,0,0,0,7.7836777344166509E-3,0,4.7896274497259715E-2,1.755059390527371E-2,0,0.92676945386304987,21.055223150627615,39.24218967615063,0.1893305439330544,0.10962343096234307,"Continue to Monitor"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",905,"Lexington - Todds Rd - SE of Substation",15.9410199565104,1400,"2022-06-20",0,0,0,0,0,0,5.3781289423013084E-3,4.1497908505411327E-3,0,0.9904720802071576,15.322741070357143,21.516749997857143,9.3035714285714277E-2,0.09,"Continue to Monitor"]
["MAYSVILLE MID","Mason - 314 Lexington St - Maysville",906,"Maysville - E Reynolds dr, Elizabeth St, Center St, Union St - E of Subst.",1.28690847399704,75,"2019-10-12",0,0,0,0,0,0,0.14772727272727273,0.85227272727272729,0,0,3.4011666633333335,5.8586666533333336,5.6666666666666671E-2,0.10666666666666667,"Tree Trim Scheduled for 2025"]
["MAYSVILLE MID","Mason - 314 Lexington St - Maysville",907,"Maysville - Buckley Pl, Hwy 11, Bank St - W & S of Subst.",6.7718751728661601,222,"2019-10-12",0,0,0,0,0,0,0.38265048052604955,0.54931714719271618,0,6.8032372281234196E-2,9.4290728164414421,16.597822806306304,0.12387387387387389,0.2747747747747748,"Tree Trim Scheduled for 2025"]
["MAYSVILLE MID","Mason - 314 Lexington St - Maysville",909,"Maysville - E 2nd St, Lexington St - NW & NE of Substation",3.3314897213816801,494,"2019-10-12",0,0,0,0,3.5878596443040582E-2,0,0.11010780745725468,0,0,0.85401359609970473,35.678103910425108,114.83903508299595,0.36589068825910936,1.1477732793522268,"Continue to Monitor"]
["MAYSVILLE EAST","Mason - 1107 Forest Ave - Maysville",913,"Maysville - Bryant ln, Hwy 10, Buckner St - E of Substation",10.2991370339968,835,"2024-01-01",0,0,6.8948972680063225E-2,0,2.3707383156468731E-3,0.5041205689771957,0.30424475050801536,0.11410589297809889,0,6.209076540979905E-3,22.663278439520958,38.142115760479037,0.2251497005988024,0.44311377245508982,"Continue to Monitor"]
["BEAVER DAM NORTH","Ohio - 129 Raines Ave. - Beaver Dam",918,"Beaver Dam - State Hwy 273, Hope St - S of Substation",2.29724017484302,36,"2019-06-08",0,0,0,0,0,0,1,0,0,0,9.1256944375,15.666666638888888,5.5555555555555552E-2,0.1388888888888889,"Continue to Monitor"]
["KENTON","Mason - 801 Kenton Station Rd - Maysville",921,"Maysville - W Maple Leaf Rd, Jersey Ridge Rd - E&NE of Subst.",20.650917154983802,893,"2024-01-01",8.0761428443843382E-3,0,0.1313489582668827,0,6.5068449457124995E-4,0,0.25981449112644966,0.41981908419347019,0,0.18029063907424184,26.453508764277718,58.629619247480413,0.60358342665173603,1.5632698768197097,"Trees Trimmed in 2024"]
["KENTON","Mason - 801 Kenton Station Rd - Maysville",922,"Maysville - Parker Rd, Hwy 10, Martha Comer Dr - W of Subst.",4.2670988584359604,120,"2021-01-23",0,0,3.9715174004613378E-2,0,0.81436164878146622,0,0.14592317721392037,0,0,0,9.6356944395833324,15.075277766666666,0.10416666666666667,0.11666666666666667,"Continue to Monitor"]
["KENTON","Mason - 801 Kenton Station Rd - Maysville",923,"Maysville - Hwy 10, Market Square Dr - SE of Substation",19.801575623987301,376,"2021-01-23",9.3100331425128052E-2,0,0,0,0,6.0379632419403438E-2,0.34239228683338352,2.8984633925881291E-2,0,0.47514311539620369,22.825808948138295,29.417686164893617,0.37765957446808512,0.17553191489361702,"Continue to Monitor"]
["AUGUSTA","Bracken - 318 E 4th St. - Augusta",930,"Augusta - E Fourth St - N of Substation",0.106011479882906,1,"2022-10-21",0,0,0,0,0,0,1,0,0,0,100.41666650000001,401.66666600000002,0.25,1,"Continue to Monitor"]
["AUGUSTA","Bracken - 318 E 4th St. - Augusta",931,"Augusta - Hamilton Ave, E 2nd St - N of Substation",2.9777600442290599,287,"2022-10-21",4.1388387851606298E-2,0,0,0,0,7.3124360161848584E-3,0.2197630770730756,0,0,0.73153609905913319,37.589895462543552,62.410569094076649,0.55052264808362372,0.4006968641114983,"Continue to Monitor"]
["SHARON","Bracken - 3061 Asbury Rd - Augusta",935,"Augusta - Mt Zion Rd, City of Brooksville, Hwy 10&19 - NW&SW of Subst",78.708351542109298,1210,"2019-01-19",5.6140071296678024E-3,0,6.1544484207681884E-3,6.6178075405417577E-2,0.28622082569729052,0,0.59573778897153329,3.2480175158408189E-2,0,7.6146792169144266E-3,76.580805775000002,189.15168042975208,0.49669421487603288,0.69338842975206549,"Continue to Monitor"]
["PARKERS MILL","Fayette - 2085 Parkers Mill Rd - Lexington",939,"Lexington - Parkers Mill Rd - SW out of Substation",62.828950315309399,1376,"2023-11-04",7.5507862982270176E-4,7.4002545970251826E-2,2.0003130026798838E-2,0,9.9676832800099396E-2,0,4.0937201013870536E-2,0.68338972221818872,0,8.1235489340968012E-2,141.67756782194766,155.43132266715116,1.9736555232558137,3.9069767441860468,"Continue to Monitor"]
["SARDIS","Mason - 4000 Blue Lick Rd - Mays Lick",940,"Mays Lick/Mt Olivet - Hwy 62, Brierly Ridge Rd - W&NW of Subst.",22.205473622507998,480,"2019-11-30",5.6028495900353956E-2,0,3.2035485460818135E-3,0,1.0954791881356691E-2,0,0.13943277028540707,0.50008960974954075,0,0.29029078363725974,89.238229152083335,58.662986089583342,1.5760416666666668,2.2666666666666675,"Continue to Monitor"]
["SARDIS","Mason - 4000 Blue Lick Rd - Mays Lick",941,"Mays Lick - Hwy 62 - NE of Substation",5.6707131253200096,46,"2019-11-30",0,0,0,0,0.30451127819548873,0,0,0.69548872180451127,0,0,5.7023550543478256,5.7688405652173911,5.9782608695652176E-2,6.5217391304347824E-2,"Continue to Monitor"]
["FLEMINGSBURG","Fleming - 523 Fountain Ave - Flemingsburg",960,"Flemingsburg - City of Flemingsburg - S of Substation",10.634236937691901,963,"2024-01-01",9.5542263241941167E-3,0,0,0,0.80515332773973536,0,8.3362654613365096E-3,0.10555660811432593,0,7.1399572360408156E-2,26.769734333592936,34.741294560747662,0.26194184839044654,0.17133956386292837,"Continue to Monitor"]
["WEDONIA","Mason - 6964 KY Hwy 11 - Maysville ",965,"Maysville - Hwy 11 - N of Substation",32.772035626116597,390,"2022-03-18",1.0356366478591143E-2,0,1.3311838987811729E-2,0,0.24276397743093719,0,0.65855743631078867,6.8537651742751768E-2,0,6.4727290491194646E-3,21.236655970512821,40.423589720512823,0.25128205128205128,0.36923076923076914,"Continue to Monitor"]
["WEDONIA","Mason - 6964 KY Hwy 11 - Maysville ",966,"Flemingsburg - Hwy 170, City of Ewing - SW of Substation",28.226490331350401,537,"2022-01-14",3.2438249461924772E-2,0,6.8668648150046118E-3,0,4.3558470841447164E-2,0,6.5286461002357271E-2,0.83601516859690483,0,1.5834785282361381E-2,29.335086895716948,36.091526996275611,0.44227188081936686,0.47486033519553073,"Continue to Monitor"]
["EWINGTON","Montgomery - 4006 Old Owingsville Rd - Mt Sterling",968,"Mt Sterling - Owinsville Rd - W of Substation",1.5398381655192199,16,"2023-04-14",0,0,0,0,0,0,0,1,0,0,14.71249996875,11.51145825,0.25,0.375,"Continue to Monitor"]
["EWINGTON","Montgomery - 4006 Old Owingsville Rd - Mt Sterling",970,"Mt Sterling - Woodland Ln, Clarence Dr - N of Substation",2.9149290659227098,6,"2023-04-14",0,0,1,0,0,0,0,0,0,0,3.997222166666667,10.636111,8.3333333333333329E-2,0.16666666666666666,"Continue to Monitor"]
["WEST HIGH STREET","Fayette - 727 West High St - Lexington",1105,"Lexington - West High St - N of Substation",0.193435952250502,2,"Underground",0,0,0,0,0,0,0,1,0,0,2.4500000000000002,9.8000000000000007,0.25,1,"Continue to Monitor"]
["VINE STREET","Fayette - 112 E Vine St. - Lexington",1201,"Lexington - Water St, N MLK Blvd, E Short St - E of Substation",1.1179838407207701,3,"Underground",0,0,0,0,0,0,0,0,0,1,13.700000000000001,54.800000000000004,0.25,1,"Continue to Monitor"]
["BARLOW","Ballard - 433 Oscar Rd. - Barlow",1311,"Barlow - US Hwy 60 - E of Substation",25.403969108470701,682,"2023-03-10",4.937500342501411E-3,4.4771784459751978E-3,1.6494867958855991E-3,0,0.60570689551240953,5.9255484132594627E-2,0.28119091850658429,4.2289334232057038E-2,0,4.9320203199237184E-4,45.852572081011729,98.720601159824028,0.45637829912023448,1.1085043988269792,"Continue to Monitor"]
["BARDWELL","Carlisle - US Hwy 62 - Bardwell",1313,"Bardwell - US Hwy 62 - N of Substation",5.9529765238910999,27,"2021-11-13",1.1039086066362877E-2,0,0,0,0,0,0,0,0,0.98896091393363716,318.58842590740738,577.09753085185184,1.2314814814814814,1.1481481481481481,"Continue to Monitor"]
["BARDWELL","Carlisle - US Hwy 62 - Bardwell",1315,"Bardwell - US Hwy 62 - W of Substation to Primary Meter",9.5344605943263397E-3,1,"2024-01-01",0,0,0,0,0,0,0,0,0,1,8.8000000000000007,35.200000000000003,0.25,1,"Continue to Monitor"]
["CLINTON 12KV","Hickman - 318 Moss Drive - Clinton",1316,"Clinton - City of Clinton, Hwy 58, ",27.090749549897499,661,"2021-12-04",3.3083461731558267E-2,0,2.5942212142721119E-2,0.1046863909422987,0.37941242663989061,0,0.4025154510672922,5.3742591855224509E-2,0,6.1746562101460561E-4,305.08542611232974,393.98436710590016,1.973903177004539,3.6202723146747355,"Continue to Monitor"]
["GREENVILLE NORTH","Muhlenberg - 501 HWY 189 Bypass - Greenville",1327,"Greenville - HWY 601, S R 181, & Luzerne Depoy Rd - NW of Substation",44.059032403517499,804,"2022-01-01",5.8147276493451339E-4,0,2.4228031872271393E-4,0,0.19664849498617623,0,0.76551165269845123,2.6499163640460736E-2,0,1.0516935591254587E-2,79.920786679415414,127.95980512189051,0.64241293532338317,0.3196517412935323,"Continue to Monitor"]
["GREENVILLE NORTH","Muhlenberg - 501 HWY 189 Bypass - Greenville",1328,"Greenville - S R 176 & Paradise Rd/St - SE of Substation",43.7193825121171,987,"2022-02-11",4.3061950340161594E-4,0,5.2147141154662856E-5,7.8800124411490541E-5,6.3225511586631235E-3,0,0.90773849668830886,8.2312755839668628E-2,0,3.0646295443915866E-3,32.39756837740628,55.461938525835869,0.35992907801418433,0.39716312056737579,"Reliability Improvements Scheduled for 2025"]
["CHRISTIAN","Webster - 1678 S R 493 - Wheatcroft",1404,"Wheatcroft - City of Wheatcroft - NW of Substation",10.8606633760853,200,"2019-09-21",0,0,0,0,0,0,0.67966751918158563,0.1221227621483376,0,0.19820971867007672,7.5730208300000008,7.8157500000000004,0.11000000000000001,8.4999999999999992E-2,"Continue to Monitor"]
["DIXON","Webster - 818 S R 1340 - Dixon",1427,"Dixon - City of Dixon, Clay-Dixon Rd - NE of Substation",13.3209913166405,462,"2020-03-28",7.8243737686462145E-2,0,0,3.5575569940895016E-2,3.6082184069800169E-2,0,0.81396003377427528,2.8764424430059103E-2,0,7.3740500985083031E-3,17.779067451839826,38.121608930735931,0.25432900432900429,0.72077922077922074,"Continue to Monitor"]
["CORYDON","Henderson - 5430 Greenlick Rd - Corydon",1428,"Corydon - Hwy 266, Hwy 136 - NW of Substation",12.7241371878214,218,"2020-09-05",0.59049990423290555,0,0.1277533039647577,0,0.1013215859030837,0,0,0.13024324841984294,0,5.0181957479410073E-2,4.9752293486238521,12.028746160550458,5.2752293577981654E-2,0.11467889908256881,"Continue to Monitor"]
["CORYDON","Henderson - 5430 Greenlick Rd - Corydon",1429,"Corydon - King Mill Rd - W of Substation",6.6091542211311296,56,"2020-09-05",5.9322033898305086E-2,0,0.19242273180458624,0,2.7417746759720838E-2,0,0.67073778664007977,5.0099700897308079E-2,0,0,60.28303569196428,68.069940446428575,0.46428571428571425,0.3571428571428571,"Continue to Monitor"]
["CORYDON","Henderson - 5430 Greenlick Rd - Corydon",1431,"Corydon - City of Corydon - E of Substation",14.4669869675395,426,"2024-01-01",0,0,0,0,0.86102526813306668,0,0.11788765678967461,2.1087075077258679E-2,0,0,19.859663533450703,22.953442875586855,0.10328638497652583,5.1643192488262907E-2,"Continue to Monitor"]
["MANITOU","Hopkins - 7615 Nebo Rd - Nebo",1451,"Nebo - US 41 ALT & Happy Ln - E of Substation",8.4875854523842307,135,"2019-01-26",0.10520336287207453,0,8.929788684389911E-2,0,9.3160645307884572E-3,0,7.9754601226993863E-2,0,0,0.71642808452624407,8.5525308462962961,9.2371604740740736,0.12407407407407409,0.12592592592592591,"Continue to Monitor"]
["ZION","Henderson - 7485 HWY 351 - Henderson",1467,"Henderson - HWY 351, Larue Rd, & Elm St - E of Substation",3.3121938101701298,117,"2020-08-29",0.83750934928945397,0,0,0,5.5721765145848916E-2,0,2.7112939416604337E-2,7.9655946148092752E-2,0,0,80.874537027777777,79.013817641025639,1.0619658119658117,1.4017094017094014,"Continue to Monitor"]
["SEBREE","Webster - 199 N Railroad St - Sebree",1472,"Sebree - SR 56, College St, Jefferson St, & Old Beech Grove Rd - W/E of Substation",12.238937226607399,430,"2020-03-28",0,0,0.29997810378804468,0,0.22246551346617036,0,8.0797022115174075E-2,0,0,0.3967593606306109,7.02090115872093,10.620116272093023,7.5581395348837205E-2,0.13488372093023254,"Continue to Monitor"]
["EARLINGTON","Hopkins - 310-A McEuen - Madisonville",1478,"Madisonville - Hwy 1337 - W of Substation",14.2072046757621,149,"2019-11-02",0,0,1.2072081116353779E-2,8.3826925007529363E-3,2.3943379178797311E-2,0,0.76490814175283606,0.19069370545125991,0,0,56.488898196308718,102.71991048993289,0.83557046979865768,0.77181208053691275,"Continue to Monitor"]
["PERDUE","McLean - S R 2110 - Island",1498,"Island - Old Island-Livermore Rd & Hwy 138 - NE & NW of Substation",8.8263221401182594,25,"2020-09-26",1.9213973799126639E-2,0,2.5036390101892285E-2,0,0,0,0,8.7336244541484712E-3,0,0.94701601164483262,42.82883331,133.94999995999999,0.24000000000000002,0.68,"Continue to Monitor"]
["EDDYVILLE PRISON","Lyon - 328 Water St - Eddyville ",1503,"Eddyville - HWY 93, HWY 1055, Perry Springs Rd, E of Substation",60.199749588307597,966,"2021-08-14",2.2593196644920783E-2,0,1.3513513513513514E-4,0,7.4603914259086671E-3,0,0.89678937558247906,3.9514212488350416E-2,0,3.3507688723205961E-2,92.006422513716345,160.26413041200829,0.78105590062111807,1.1459627329192532,"Reliability Improvements Scheduled for 2025"]
["FREDONIA","Caldwell - 150 Wigginton Ln - Fredonia",1507,"Fredonia - City of Fredonia & Hwy 641 - S of Substation",11.013961307678899,253,"2021-10-16",5.1141774404031776E-3,0,5.1423935917985053E-2,0,0.32689978955453752,0,0.52621162897328477,7.5344962045357455E-2,0,1.5005506068432005E-2,10.75706520750988,33.464953869565214,0.11857707509881422,0.34387351778656128,"Continue to Monitor"]
["FREDONIA","Caldwell - 150 Wigginton Ln - Fredonia",1509,"Fredonia - Hwy 91, Princeton Fredonia Rd, & Marion Rd - SE of Substation",33.727373261958199,203,"2021-11-06",8.0007748118765185E-4,0,0.15501922291421907,0,0.16034394909822847,0,0.6801500776917343,0,0,3.6866728146304696E-3,100.56028323399013,121.54515596551722,0.81896551724137923,0.69950738916256139,"Continue to Monitor"]
["FREDONIA QUARRY","Caldwell - 181 Fredonia Quarry Rd - Fredonia",1513,"Fredonia - Beck Rd & New Bethel Church Rd - S of Substation",11.9451785050976,72,"2021-11-13",3.6900971507878196E-3,0,0,0,0.87060168176994035,0,0.12570822107927176,0,0,0,78.480092565972228,60.890509222222221,0.91666666666666652,1.25,"Continue to Monitor"]
["CEDAR BLUFF","Caldwell - 10195 Hopkinsville Rd - Princeton",1514,"Princeton - Hopkinsville Rd - SSW of Substation",0.244058440720543,6,"2023-01-06",0,0,0,0.13876651982378854,0.86123348017621149,0,0,0,0,0,82.790972166666663,226.94444433333334,0.58333333333333326,1,"Continue to Monitor"]
["CEDAR BLUFF","Caldwell - 10195 Hopkinsville Rd - Princeton",1515,"Princeton - Hopkinsville Rd, Sandlick Rd, Hwy 91 - E/NW of Subs",8.9388444336627906,82,"2023-01-06",0,0,0.5683355450135118,0,0.10357110238377934,4.3603229948477699E-2,0.1532183975974169,0,0,0.13127172505681423,109.91285568292683,373.24166664634146,0.67987804878048785,2.1341463414634148,"Continue to Monitor"]
["CLAXTON","Caldwell - 1600 Jones-Keeney Rd - Princeton",1518,"Princeton - Hwy 62, Lewistown Rd - NW of Substation",15.376984105485599,152,"2023-12-09",0,0,0,0,1.8927571834162255E-3,0,0.98389142822624487,0,0,1.4215814590338884E-2,66.581661171052644,214.69265348684212,0.43585526315789469,1.0723684210526314,"Continue to Monitor"]
["BARNHILL","Webster - 7390 Rabbit Ridge Rd - Providence",1520,"Providence - Hwy 109 - S of Substation",5.3146606799200704,30,"2022-12-09",0,0,3.5631804684922469E-2,0,0,0,0.96436819531507756,0,0,0,79.730833308333331,101.04,1.0499999999999998,2,"Continue to Monitor"]
["SUNSET","Hopkins - 1515 Olney Rd - Dawson Springs",1523,"Dawson Springs - Hwy 1220, Purdy Ln, & Walnut Grove Rd - S of Substation",2.2482232792177799,28,"2022-12-31",0,0,0,0,3.7348879127660094E-4,0,0.99962651120872337,0,0,0,73.924999973214284,192.06607142857143,0.75,2.1785714285714288,"Continue to Monitor"]
["DAWSON SPRINGS 4KV","Hopkins - 205 Munn St - Dawson Springs",1525,"Dawson Springs - N Trim St, Sycamore St - NW of Substation",2.2929214764221499,151,"2022-10-01",0,0,0,0,0.72264280798348246,0,0.27735719201651754,0,0,0,5.79655076986755,9.6245033112582785,0.37582781456953646,1.0331125827814569,"Continue to Monitor"]
["DAWSON SPRINGS 4KV","Hopkins - 205 Munn St - Dawson Springs",1526,"Dawson Springs - E Walnut St, E Keigan St E Ramsey St - NE of Subst.",15.8205416786698,738,"2022-10-01",0,0,1.0437786876048672E-4,0,6.1556848101497041E-3,0,0.94861347048585287,0,0,4.5126466835236925E-2,27.551004964092147,103.86032067886181,0.55555555555555547,2.1043360433604335,"Continue to Monitor"]
["DAWSON SPRINGS 12KV","Hopkins - 203 Parker St - Dawson Springs",1529,"Dawson Springs - Mill Dam Rd, Mt Hebron Rd, Hwy 672 - W & SW",36.067383336131797,610,"2022-07-08",1.8058606694716461E-3,0,0.54255873701455859,0,0.10912735351429174,3.8357473532660634E-2,0.21899318613396879,7.972471484777402E-2,0,9.4326742872745777E-3,52.510423480737707,110.0195901442623,0.66639344262295064,1.0754098360655735,"Continue to Monitor"]
["SIXTH VEIN","Hopkins - 2395 Sixth Vein Rd - Dawson Springs",1541,"Dawson Springs - Charleston Rd, Hwy 70, Campbell Rd, & High Glory Rd - N of Substation",40.936313037205601,467,"2022-11-25",8.0515054529026772E-4,0,1.8136496924627191E-4,0,4.3060990016408035E-2,1.2832945551213482E-4,0.83427693496499511,9.5766199670190553E-4,0,0.1205895680518462,159.84160419271947,385.73408276659524,1.5513918629550325,2.8736616702355464,"Continue to Monitor"]
["ST CHARLES KU","Hopkins - 660 St. Charles Rd - St. Charles",1553,"St. Charles - City of St. Charles & Mc Gregor Rd - SE of Substation",12.863994438982999,219,"2022-10-14",8.2793245093564588E-2,0,0,0,0.14879050661798265,0,0.52761296211775444,4.6462802373345505E-2,0,0.1943404837973528,38.519748831050237,50.020852301369878,0.7374429223744291,0.58904109589041076,"Continue to Monitor"]
["ST CHARLES KU","Hopkins - 660 St. Charles Rd - St. Charles",1554,"St. Charles - Ilsley Rd, Union Temple Rd, & Hwy 112 - SW/NW of Substation",68.284454265268295,625,"2022-11-04",4.4842620339655945E-4,0,2.0627605356241735E-5,0,0.13573861176813853,0,0.84971713275089744,4.5222287858531695E-3,0,9.5529728863580372E-3,145.33283331399997,154.36058664160001,0.7884000000000001,1.0192000000000003,"Continue to Monitor"]
["GRAHAM","Muhlenberg - 5230 S R 175 S - Greenville",1602,"Greenville - Ford Ln, US HWY 62 McNary Rd - SW & SE of Substation",33.226591346587497,467,"2023-11-03",4.751026400986628E-4,0,1.9622163656110611E-3,0,0.43733127251075943,0,0.54077437484135715,1.4785741447916579E-2,0,4.6712921942570615E-3,61.040176645074943,91.213775858672392,0.6643468950749466,1.3940042826552463,"Continue to Monitor"]
["GRAHAM","Muhlenberg - 5230 S R 175 S - Greenville",1603,"Greenville - S R 175, Landfill Rd, & S R 70 - NW of Substation",19.600577879666002,276,"2023-11-20",5.4010333098849447E-5,0,0,0.11272219982769387,0.42570483484693999,0,0.12062088171210121,0.32171057311550044,0,1.9187500164665649E-2,111.84974334510868,152.09384056884056,0.89130434782608692,1.181159420289855,"Continue to Monitor"]
["CALHOUN","McLean - 530 W First St - Calhoun",1607,"Calhoun - State Hwy 81, W 2nd St, Walnut St - NE & S of Subst.",19.563107917301,355,"2023-10-21",0,0,0,0,4.5036160420775809E-2,0,0.16798159105851412,0.78698224852071008,0,0,7.512276991549296,8.569999997183098,7.5352112676056349E-2,0.11830985915492957,"Continue to Monitor"]
["SHAVERS CHAPEL","Muhlenberg - 7870 S R 181 N - Bremen",1609,"Bremen - S R 181, Buttermilk Rd, S R 175, & S R 81 - NW of Substation",92.723449448143796,1759,"2019-08-03",1.3427440497419472E-3,0,7.7108525839037781E-2,0,3.0630655068596774E-2,0,0.14632950926650601,0.13516895117078589,0,0.60941961460533156,65.579133492183075,112.84654157987499,0.77942012507106218,1.4457077885161982,"Continue to Monitor"]
["SHAVERS CHAPEL","Muhlenberg - 7870 S R 181 N - Bremen",1612,"Bremen - S R 181, HWY 70, & New Harmony Rd- S of Substation",44.245841382536902,803,"2019-08-03",1.2767676893382703E-3,0,1.0488317945100157E-2,5.7674276067275502E-4,6.0279924412863812E-5,0,0.94591490730308792,3.3593418521181778E-2,0,8.0895658562063245E-3,62.853642576587809,136.36770442341225,0.79763387297633881,1.6849315068493151,"Continue to Monitor"]
["GREENVILLE 12KV","Muhlenberg - 200 N Boggess Ave - Greenville",1615,"Greenville - Hwy 181, 62, 171, SR 189, & Bards Hill Rd - W&S of Substation",85.711088469062503,1862,"2021-10-23",9.2781650065875256E-4,0,3.1527454456385814E-2,1.4679311536883047E-3,0.11184346835915837,2.6537425148850831E-5,0.76772799337898334,8.3367250149432668E-3,0,7.8142073711033266E-2,73.336983068206195,188.33555314661641,0.55397422126745421,0.51664876476906507,"Continue to Monitor"]
["GREENVILLE WEST","Muhlenberg - S Walton St - Greenville",1618,"Greenville - Campbell St, Main St, & Chatham Ln - E of Substation",3.3326547856011901,288,"2021-05-08",0,0,0,0,1.5872218246466439E-3,0,0.99841277817535334,0,0,0,64.407826961805554,226.83871527430554,0.33593750000000006,1.0104166666666667,"Continue to Monitor"]
["GREENVILLE","Muhlenberg - 117 E Depot St - Greenville",1622,"Greenville - W Depot St, N Cherry St, & Short St - SE of Substation",4.8364843768186301,415,"2021-10-30",0,4.9825756398946038E-4,0,0,4.8820448490426126E-2,0,0.81792496241086321,0.12332753986793243,0,9.428791666788788E-3,5.1575903578313254,9.3079518024096384,0.30180722891566258,1.0457831325301201,"Continue to Monitor"]
["GREENVILLE","Muhlenberg - 117 E Depot St - Greenville",1623,"Greenville - N Main St & Broad St - N & S of Substation",2.23737301734131,154,"2021-10-30",0,0,0,0,0,0,1,0,0,0,39.499404753801571,58.50281383988164,0.43506493506493504,1.0649350649350648,"Continue to Monitor"]
["POWDERLY","Muhlenberg - Opportunity Way - Greenville",1625,"Greenville - Opportunity Way & N Main St - E of Substation",1.24723126492879,34,"2021-05-22",1.4150034411562285E-2,0,0,0,0,2.0646937370956643E-3,0.9211286992429456,5.5058499655884381E-4,0,6.2105987611837575E-2,23.860171536764703,84.254411676470582,0.63970588235294124,2.3823529411764706,"Continue to Monitor"]
["LIVERMORE","McLean - 190 Main St - Livermore",1642,"Livermore - Hill St, Hwy 431, & Comy Dock Rd - NE of Substation",6.3526388939275202,347,"2023-01-20",0,5.9553285204201308E-3,2.4694414761917173E-3,0,3.4011832468920223E-3,0,0.4862454064479137,8.346581875993641E-3,0,0.49358205843258879,126.01163543083574,442.29812678097983,0.85014409221902032,1.7146974063400584,"Continue to Monitor"]
["LIVERMORE","McLean - 190 Main St - Livermore",1643,"Livermore - Main St, 2nd St, 3rd St, & Broadway St - N of Substation",6.8414949197489499,422,"2024-01-01",0,0,1.0710209650245594E-3,0,2.3725503792145098E-3,0,0.90569205945243936,1.4261539009338404E-3,0,8.9438215302387727E-2,133.13010465284361,485.29020535545027,0.89336492890995278,2.3056872037914693,"Continue to Monitor"]
["CENTRAL CITY SOUTH","Muhlenberg - 500 E Second Ave - Central City",1649,"Central City - Everly Borthers Blvd, S Stroud Ln - SW of Subst.",8.9138629536116998,312,"2024-01-01",2.3502633971461549E-2,0,3.3464655778295042E-3,0,0,0,0.68587069360173836,2.417966457969295E-3,0,0.28486224039100128,50.038982365384619,157.4938034070513,0.45112179487179493,1.2243589743589745,"Continue to Monitor"]
["CENTRAL CITY SOUTH","Muhlenberg - 500 E Second Ave - Central City",1650,"Central City - Everly Borthers Blvd, S R 604, US 431 - E of Subst.",18.6603044557537,792,"2024-01-01",5.4172842029948383E-2,0,3.023523806540637E-3,0,4.2039180516241135E-4,0,0.90384402969449873,3.6504846045926569E-2,0,2.0343666179231984E-3,60.651131097222219,45.655702857323227,1.018939393939394,1.0719696969696977,"Continue to Monitor"]
["CENTRAL CITY SOUTH","Muhlenberg - 500 E Second Ave - Central City",1651,"Central City - W 2nd Ave, Center St, W Reservoir St - W of Subst.",5.5425647731741998,414,"2024-01-01",1.9718910975869996E-3,0,7.4926459266942733E-2,0,0.7536702836011594,5.9426854995772589E-5,6.5547821060337158E-2,8.4839939168510251E-2,0,1.8984178950467716E-2,55.433786227053147,87.196859898550741,0.75181159420289856,1.2149758454106281,"Continue to Monitor"]
["BEVIER","Muhlenberg - 2665 S Route 2107 - Bevier",1666,"Bevier - Robertson St, Main St, Holts Rd - W of Substation",7.5854081269943299,183,"2024-01-01",1.7624599328618066E-4,0,0,0,2.2954805256413212E-2,0,0.97317931300300109,3.6896357472994833E-3,0,0,116.05607921994535,390.85428049180325,0.83333333333333326,1.540983606557377,"Continue to Monitor"]
["BEECH CREEK","Muhlenberg - 169 Beech Creek Browder Rd - Beech Creek",1668,"Beech Creek - Arnold Hill Rd, State Route 1163 - SW of Subst.",21.609417831330902,284,"2023-06-01",2.8913217203943787E-4,0,2.971171139844023E-3,0,0.22398148523783856,0,0.77199127065540274,6.9224295087393257E-4,0,7.4697844001280167E-5,228.49392603961266,270.51660795070421,1.28080985915493,1.6232394366197198,"Continue to Monitor"]
["DRAKESBORO","Muhlenberg - 201 S Mine St - Drakesboro",1673,"Drakesboro - Simmons St, S R 176, Merle Travis Hwy - SW of Subs",20.311030583021001,303,"2023-09-01",3.4966273485849034E-4,0,2.7016126991837829E-2,0,1.8068100739301384E-2,0,0.88513756268374999,6.9057631098224354E-2,0,3.7091575202789204E-4,75.078699107260732,155.26952693729373,0.721947194719472,1.2574257425742574,"Continue to Monitor"]
["DRAKESBORO","Muhlenberg - 201 S Mine St - Drakesboro",1674,"Drakesboro - Broad St, SR 2107, & Big Springs Rd - NE of Substation",13.560634130009101,382,"2024-01-01",0,0,5.0941094549243199E-2,0,0.156515410914079,0,0.79239899267543101,0,0,1.4450186124679977E-4,67.168728178010468,191.69214659162304,0.83507853403141363,2.3403141361256545,"Continue to Monitor"]
["GREEN RIVER STEEL","Daviess - 4575 US 60 E - Owensboro",1676,"Owensboro - Ellis Smeathers Rd & US 60 - NE of Substation",2.4467325053262101,16,"2017-10-04",0,0,0,0,1,0,0,0,0,0,12.76510415625,19.03125,0.203125,0.1875,"Continue to Monitor"]
["NELSON","Muhlenberg - 2030 S R 1379 - Central City",1690,"Central City - S R 1379, US 62, & SR 2590 - NW/S/SE of Substation",30.752322927505499,319,"2019-10-26",3.7385791926772223E-4,0,3.5229930507647521E-5,0,1.0831889081455805E-4,0,0.98976596809745765,9.6614140768285922E-3,0,5.5211085123925226E-5,171.47199580329152,462.56671888714737,0.82288401253918508,0.91222570532915404,"Continue to Monitor"]
["REED MINERALS","Muhlenberg - 4661 S R 176 Drakesboro - Drakesboro",1693,"Drakesboro - S R 176 & P&M Haul Rd - NNE of Substation",5.6338772932166297,11,"2020-03-28",1.2930337805075158E-2,0,0,1.519314692096331E-2,0,0,2.5375787942459996E-2,0.71407790528527559,0,0.23242282204622597,145.32196961363636,160.89848472727272,0.45454545454545453,0.45454545454545453,"Continue to Monitor"]
["SALEM 12KV","Livingston - 266 W Main St - Salem",1703,"Salem - Hwy 60, College St, & Levias Rd - ENE of Substation",19.493928390697299,395,"2022-05-06",0.13074604370761114,0,2.5872896257221802E-2,0,1.8211504647073599E-2,0,0.44385832705350414,0.13551871389098216,0,0.24579251444360714,18.799135007594934,10.931350202531647,0.17151898734177221,0.18227848101265823,"Continue to Monitor"]
["DYCUSBURG","Crittenden - 9315 S R 70 - Dycusburg",1707,"Dycusburg - City of Dycusburg, S R 70 - N & SW of Substation",6.7302621575804302,89,"2021-08-28",0.13712374581939799,0,5.2396878483835008E-2,0,0,0,0.68729096989966554,0.12318840579710146,0,0,13.546161033707865,20.154681629213481,0.11797752808988762,0.19101123595505617,"Continue to Monitor"]
["MARION 4KV","Crittenden - 106 Sparmill Rd - Marion",1715,"Marion - Gum St, Mill Rd, Sturgis Rd/Main St - N of Substation",8.8544016793367604,374,"2022-04-15",0,0,4.5524617015126695E-2,0,0.89485981308411211,0,5.9615569900761153E-2,0,0,0,22.346468356951871,34.553163989304814,0.19385026737967914,0.20588235294117649,"Continue to Monitor"]
["SUNOCO","Union - 2823 S R 130 S - Morganfield",1731,"Morganfield - S R 130 & Adamson Rd - SW of Substation",23.121863128724701,182,"2020-01-18",6.3347875455686369E-3,0,0.17546166258291998,0,0.74099085639156159,0,3.4602282914002268E-2,2.1813183529552381E-2,0,2.0797227036395149E-2,140.15963826236265,79.124908406593406,0.85027472527472525,1.1428571428571428,"Continue to Monitor"]
["UNIONTOWN","Union - 5668 S R 130 N - Uniontown",1742,"Uniontown - City of Uniontown, S R 130, & KY 268 - NW & S of Substation",13.747634827503701,619,"2020-03-15",0.13034360380706564,0,0.21436925310533958,0,8.3723181158251336E-2,0,0.25859009517664139,0.31138086788191643,0,1.5929988707856105E-3,23.005385022617123,56.691680116316633,0.22051696284329561,0.53473344103392562,"Continue to Monitor"]
["MORGANFIELD","Union - 305 Rhea St - Morganfield",1750,"Morganfield - S R 947, N Chapman St, & Hedge Rd - NW of Substation",9.3061723232692994,290,"2019-12-20",0,0,1.0314224034540657E-2,0,0,0,0.42576157351882948,5.9126888942192375E-2,0,0.50479731350443746,10.585948272413793,27.053620686206898,0.32758620689655166,1.1724137931034482,"Continue to Monitor"]
["MORGANFIELD","Union - 305 Rhea St - Morganfield",1751,"Morganfield - Hwy 60, Jim Veatch Rd, & Townsend St - SW of Substation",9.5301026122933692,447,"2024-01-01",2.0205871139916128E-2,0,0,0,0,8.7685855890202058E-2,0.74050069894522819,0.1131020460033041,0,3.85055280213496E-2,8.7843400408277397,7.3250186353467566,7.7181208053691275E-2,0.13646532438478748,"Continue to Monitor"]
["CAMP BRECKINRIDGE","Union - 1820 S Route 2091 - Morganfield",1759,"Morganfield - Marshall Rd, Headquarters Rd, & Patton Rd - NE of Substation",19.471316045255399,258,"2019-12-20",1.6695605716575398E-2,0,0,0,2.1904634700146922E-2,0,0.93114732202484296,0,0,3.0252437558434622E-2,44.705943140503877,58.034496108527136,0.39244186046511631,0.31395348837209308,"Continue to Monitor"]
["MORGANFIELD INDUSTRIAL","Union - 3324 U S HWY 60 E - Morganfield",1762,"Morganfield - US HWY 60, Blessed Martin Rd, & King Mill Rd - NE of Substation",22.380511868652999,230,"2020-01-18",8.0442958629335565E-2,0.20901239726981474,7.4731856804568883E-2,0,6.1986349073687143E-2,0,6.8951107396573339E-3,0.5669313274829364,0,0,50.6931159283466,27.79666665193114,0.98043478260869565,1.3043478260869565,"Continue to Monitor"]
["WAVERLY","Union - 178 Blessed Martin Rd - Waverly",1764,"Waverly - E Main St, S Maple St, & E Market St - S of Substation",3.85116311007204,164,"2024-12-06",0,0,0,0,0,0,0.24914371120752288,0.75085628879247712,0,0,87.170147350609753,293.73963414024388,0.53048780487804881,1.8109756097560976,"Trees Trimmed in 2024"]
["MANNINGTON","Christian - 2535 Mannington Loop - Mannington",1802,"Mannington - HWY 407, Daniel Boone Rd, & Possum Pocket Rd- NW & SW of Substation",15.784632558392699,151,"2023-05-29",0,0,0,0,1.2082326472793933E-2,0,9.5408715940338312E-2,2.3664694608782601E-2,0,0.86884426297808515,377.93416110099326,172.24227370860928,1.8029801324503312,2.0596026490066226,"Continue to Monitor"]
["BORG-WARNER","Hopkins - 1000 Island Ford Rd - Madisonville",1807,"Madisonville - Whittington Dr/St Malo Dr/Pin Oak St - NW of Subst.",13.3338070691944,503,"2023-01-27",0.2780239619235188,3.0362711308058427E-2,8.3046118496635485E-2,0,9.8473658296405718E-3,0,6.1463975053339899E-2,3.6107008042015427E-3,0,0.53364516658460526,15.7031229194831,24.067064272365805,0.27385685884691846,0.41153081510934397,"Continue to Monitor"]
["HARTFORD","Ohio - 425 Walnut St - Hartford",1912,"Hartford - HWY 69, Frederica St, & Mulberry Ct- NE of Substation",11.581834643933499,506,"2023-06-09",5.6496927129060577E-2,0,0.13156277436347674,0,0.11071115013169447,0,9.6707638279192279E-2,0.60452151009657595,0,0,26.159749662549405,40.568972320158103,0.26185770750988141,0.36956521739130432,"Continue to Monitor"]
["HARTFORD","Ohio - 425 Walnut St - Hartford",1913,"Hartford - US HWY 231, Washington St, Union St- N & NE of Substation",9.1172962776277409,578,"2024-02-01",0.20525696752748657,0,7.7985170033239584E-2,0,4.0143185885962669E-2,7.8854512912298648E-3,9.208897980056252E-2,0.56999232932753774,0,6.6479161339810791E-3,35.630911182958485,97.665253742214574,0.37846020761245674,1.0916955017301038,"Trees Trimmed in 2024"]
["BEAVER DAM","Ohio - 310 Ridgecrest Dr. - Beaver Dam",1914,"Beaver Dam - Ridge Crest Rd & US Hwy 62 - City of Beaver Dam",13.441822497686401,537,"2019-05-25",1.5120852456081904E-2,0,0,0,2.5343960857826198E-2,3.6397448200762754E-3,0.18633802886934209,0.68462008920358208,0,8.4937323793091449E-2,41.311646482309122,69.080633128491613,0.5018621973929237,0.80074487895716961,"Tree Trim Scheduled for 2025"]
["ATOKA","Boyle - 20 Parksville Cross Pike - Danville",2100,"Danville - Parksville Cross Pike & Lebanon Rd - S of Substation",15.4231289010591,284,"2020-10-10",0.13345548938769278,0,0.39578561612459917,0,0,0,6.7338524965643604E-2,0.35257291189494577,0,5.0847457627118647E-2,12.582731798415491,23.059448341549292,0.15933098591549294,0.25704225352112675,"Continue to Monitor"]
["ATOKA","Boyle - 20 Parksville Cross Pike - Danville",2101,"Perryville - City of Perryville & Perryville Rd - W of Substation",30.895358829243801,603,"2020-10-10",3.7896836389827694E-2,0,0.1644412432821763,0,0,0,0.23306000332428389,0.5612222283783036,0,3.3796886254086099E-3,17.096144271558874,23.524295182421227,0.20522388059701493,0.30182421227197342,"Continue to Monitor"]
["ATOKA","Boyle - 20 Parksville Cross Pike - Danville",2102,"Danville – Parksville Cross Pike & Lebanon Rd - S of Substation",13.4872944430785,214,"2020-10-10",2.5655549261986471E-3,0,4.7112917735647887E-2,0,0.21500683037350482,0,0.58304734615000164,0.14950188251757573,0,2.7654682970712692E-3,60.505607455607468,140.24314638317753,0.63317757009345776,1.1168224299065415,"Continue to Monitor"]
["BRODHEAD","Rockcastle - 77 Cass St. - Brodhead",2103,"Brodhead - Hwy 1505, City of Brodhead, & Hwy 150 - W of Substation",22.223839846219001,789,"2020-05-30",6.2524043815424493E-2,0,0,0,3.1585980683957967E-3,0,0.18329992508453299,0.59537548846909227,0,0.15564194456255442,54.832145115335862,47.205133073510773,0.36692015209125478,0.38403041825095063,"Continue to Monitor"]
["BUENA VISTA","Garrard - 164 High Bridge Rd. - Lancaster",2104,"Lancaster - High Bridge Rd, Pine Crest Rd, & Camp Dix Rd - NW & SE of Substation",35.4223822587619,643,"2022-11-04",3.4178417709090714E-3,0,0,0,0,0,0.77857267955610521,0.12865732951922004,0,8.9352149153765728E-2,58.643792112363926,178.99551580248834,0.56726283048211501,1.7402799377916016,"Continue to Monitor"]
["BUENA VISTA","Garrard - 164 High Bridge Rd. - Lancaster",2105,"Lancaster - Rock Quarry Rd, Lexington Rd, & US 27 - E of Substation",20.506525393921802,354,"2022-10-15",9.4461962118699667E-5,0,6.3659148384341078E-5,0,0.20229850596085783,1.2937181768430607E-4,0.72103021037295023,7.0634958934715483E-2,0,5.7488318032891247E-3,168.87196326694911,400.16977399717507,1.1850282485875707,1.3672316384180792,"Continue to Monitor"]
["BUENA VISTA","Garrard - 164 High Bridge Rd. - Lancaster",2106,"Lancaster - Kennedy Bridge Rd, Ashley Camp Rd, & Chminey Rock Rd - W of Substation",30.719371030758001,1209,"2022-09-09",4.9205546536076434E-3,0,1.1992654299630054E-2,0,1.8094908577968222E-2,0,0.43867990312192268,0.48675804434035075,0,3.9553935006520637E-2,190.08735524338292,452.37980423738617,1.1515715467328369,1.8751033912324222,"Continue to Monitor"]
["CRAB ORCHARD","Lincoln - 635 KY HWY 39 N - Crab Orchard",2107,"Crab Orchard - City of Crab Orchard - S of Substation",10.810610817553901,499,"2018-12-08",0.54626974928323069,0,1.2261331055938511E-2,0,0,0,0.23430732629781004,0.20716159336302079,0,0,18.202705406312624,32.849465589178351,0.15280561122244493,0.26653306613226463,"Continue to Monitor"]
["CRAB ORCHARD","Lincoln - 635 KY HWY 39 N - Crab Orchard",2108,"Crab Orchard - KY 39 - NNW of Substation",9.1598589575208695,131,"2018-12-08",4.5876288659793818E-3,0,3.9690721649484539E-3,0,0,0,0.67905498281786936,0.31238831615120277,0,0,52.582283702290077,196.69631041984735,0.29198473282442744,1.0152671755725189,"Tree Trim Scheduled for 2025"]
["RICHMOND 3","Madison - 950 Vickers Dr - Richmond",2109,"Richmond - Lancaster Rd - SW of Substation",61.115856416061298,1387,"2020-03-14",5.3888169378906468E-2,0,5.349400304071175E-4,7.3108470822306057E-3,6.7364904180040153E-2,0,0.13986335566942584,0.59294817651144016,0,0.13808960714754959,36.053226378875273,37.645457809661146,0.46971881759192485,0.9142033165104535,"Tree Trim Scheduled for 2025"]
["DANVILLE CENTRAL","Boyle - 494 S 4TH ST - Danville",2110,"Danville - S 3rd St, MLK Blvd, & E Walnut St - N of Substation",1.5518780339287701,142,"2020-10-17",0,0,0,0,0.45329249617151607,0,0,0,0,0.54670750382848388,2.0202464771126758,4.6044600915492957,3.1690140845070422E-2,9.8591549295774655E-2,"Continue to Monitor"]
["DANVILLE EAST","Boyle - 805 East Dr - Danville",2111,"Danville - E Walnut St, Alta Ave, & E Main St - W of Substation",2.5406173377101999,349,"2021-04-16",0,0,0,0,0,0,0.98280069479225496,0,0,1.7199305207745017E-2,5.4771251181948424,6.7677650401146128,5.8022922636103161E-2,8.3094555873925502E-2,"Continue to Monitor"]
["DANVILLE EAST","Boyle - 805 East Dr - Danville",2114,"Danville - Hill N Dale St, Lexington St, Shakertown Rd, & 4th St - N of Substation",31.639386758360299,1843,"2024-01-01",5.9383297901662788E-3,0,0,0,1.5023210245802099E-3,0,0.75372578343107743,0.23639382915840002,0,2.4397365957760354E-3,22.379616563619098,26.64190630982095,0.23331524688008692,0.16440586001085192,"Reliability Improvements Scheduled for 2025"]
["DANVILLE EAST","Boyle - 805 East Dr - Danville",2115,"Danville - Stanford Rd, Baughman Ave, & Danville Bypass - S of Substation",16.4893569758854,732,"2021-07-17",4.8432805406276357E-3,0,6.956884377339892E-3,0,2.8073966656240817E-2,0,0.20155060801652969,0.75848047996815382,0,9.4780441108172921E-5,23.526553957308746,24.430009101092899,0.60894808743169393,0.35792349726775963,"Continue to Monitor"]
["DANVILLE NORTH","Boyle - 514 N Danville Bypass - Danville",2123,"Danville - Harrodsburg Rd, Maple Ave, Lexington Ave, & Springhill Rd - N & E of Substation",23.178183396172201,1212,"2020-12-26",4.2958847549220518E-3,0,9.8308210756409675E-3,0,0.16826244364497472,0,0.57032993305706092,0.24505897354160028,0,2.2219439258011143E-3,49.950030935231027,113.34973871947196,0.5884900990099009,0.82013201320132012,"Continue to Monitor"]
["DANVILLE NORTH","Boyle - 514 N Danville Bypass - Danville",2124,"Danville - Whirlaway Dr, War Admiral Dr, & Bluegrass Pike - W of Substation",6.73380822351589,425,"2024-01-01",0,0,3.7840191595906812E-2,0,0,0,0.95657449742361567,4.8131214166485239E-3,0,7.7218956382901522E-4,18.368647057647056,35.196549018823525,0.24176470588235296,0.44000000000000011,"Continue to Monitor"]
["HARRODSBURG EAST","Mercer - 709 E Office St - Harrodsburg ",2129,"Harrodsburg - Cane Run St, N East St, & Cogar Ave - W of Substation",3.7292550290863802,421,"2021-11-06",0,0,0,0,2.1561956603916233E-2,0,0.89758826642473732,8.0849776971346488E-2,0,0,7.9448931086698336,15.522684080760094,8.9667458432304045E-2,0.21377672209026127,"Continue to Monitor"]
["HARRODSBURG EAST","Mercer - 709 E Office St - Harrodsburg ",2130,"Harrodsburg - Beaumont Ave, S College St, & Perryville St - SW of Substation",20.124017206989301,1106,"2021-09-11",1.2479443733857466E-2,0,0.17392206150336062,9.1855027087356107E-4,0,0,0.42074047004093967,0.29334841204387313,0,9.8591062407095559E-2,41.528198457278478,51.312989748643766,0.66591320072332738,0.84358047016274862,"Continue to Monitor"]
["HARRODSBURG EAST","Mercer - 709 E Office St - Harrodsburg ",2131,"Harrodsburg - Lexington Rd, Burgin Rd, & City of Burgin - NE/SE of Substation",43.178133269150599,850,"2021-10-23",1.2949086104597022E-2,0,2.3889503732125531E-4,0,0.16503259210866311,0,0.58312815987440947,0.23222060250303495,0,6.4306643719741997E-3,42.743622540588234,81.95437253764706,0.65500000000000003,1.1811764705882353,"Continue to Monitor"]
["KENTUCKY STATE HOSPITAL","Boyle - 4180 Shakertown Rd - Danville",2138,"Danville - Shakertown Rd, Faulkner Ln, & Curdsville Rd - N of Substation",34.101755688580702,637,"2022-06-10",1.2612965203159467E-2,0,6.337614744182737E-4,0,0.34147512986550915,0,0.16797347541450222,0.46226117199174555,0,1.5043496050665338E-2,20.626576391679748,23.72671375510204,0.18956043956043958,0.27158555729984302,"Continue to Monitor"]
["MOUNT VERNON","Rockcastle - 56 Old Somerset Rd - Mt. Vernon",2144,"Mt. Vernon - Hysinger Hollow Rd, W Main St, Williams St, Richmond St - ENE of Sub",2.3274268582266799,79,"2020-08-08",0,0,0,0,0,0,1,0,0,0,9.7365506297468354,22.29789029113924,0.15822784810126583,0.39240506329113928,"Continue to Monitor"]
["MOUNT VERNON","Rockcastle - 56 Old Somerset Rd - Mt. Vernon",2145,"Mt. Vernon - W Main St & N Hwy 461 - NW of Substation",5.4794342125642501,255,"2020-08-08",0.51176559890693796,0,0.19644754820100196,0,0,0,0.21724609078487933,7.4540762107180802E-2,0,0,8.1448692745098032,21.897777760784312,9.509803921568627E-2,0.26274509803921564,"Continue to Monitor"]
["MOUNT VERNON","Rockcastle - 56 Old Somerset Rd - Mt. Vernon",2146,"Mt. Vernon - Poplar St, South City of Mt Vernon, & Mchargue Branch Rd - E of Sub",20.801741422499902,698,"2024-01-01",3.46147076155418E-2,0,7.1709000742345048E-3,0,1.8734646085086518E-2,0,0.84098509952780731,8.4106928298652309E-2,0,1.4387718398677555E-2,60.234951041189106,70.51430275071634,0.44305157593123196,0.5100286532951287,"Continue to Monitor"]
["PINE HILL","Rockcastle - 501 Flat Rock Rd - Mt. Vernon",2148,"Mt. Vernon - Mullins Station Rd, Skyline Rd, & Honeycomb Rd - NE of Substation",4.7449872963717796,52,"2020-07-25",1.4852267340812134E-2,0,0,0,0,0,0.978669616053089,6.4781166060989097E-3,0,0,109.67716344711539,121.70576921153847,0.49519230769230771,0.32692307692307693,"Continue to Monitor"]
["SHAKERTOWN","Mercer - 3499 Lexington Rd - Harrodsburg",2152,"Harrodsburg - Lexington Rd & Sexton Rd - SW of the Substation",12.966337378084599,71,"2022-04-09",5.7344508160564623E-3,0,6.5505072783414206E-2,0,0,0.11149095721217468,3.4186149095721216E-3,0.4027716512277606,0,0.41107925305102189,138.49014082746481,383.16924878873243,0.97887323943661975,2.295774647887324,"Continue to Monitor"]
["RICHMOND 2","Madison - 200 Fairview St - Richmond",2154,"Richmond - Big Hill Ave, Boggs Ln, & Richmond East - SE of the Substation",8.3207367735846596,961,"2019-11-22",6.4547840910279333E-2,0,0,0,0,0,9.0076240077808803E-2,0.81028875014379986,0,3.5087168868111987E-2,12.325593998439127,25.736593825182105,0.16675338189386057,0.29656607700312176,"Tree Trim Scheduled for 2025"]
["WEST CLIFF","Mercer - 815 Dix Dam Rd - Burgin",2159,"Burgin - Dix Dam Rd - S of Substation",1.1246549250528599,4,"2022-04-09",0,0,0,0,1,0,0,0,0,0,41.145833250000003,123.9666665,0.5625,1,"Continue to Monitor"]
["MOUNT VERNON TAP","Rockcastle - 56 Old Somerset Rd - Mt. Vernon",2166,"Mt. Vernon - Richmond St and Williams St - NE of Substation",12.9020608453538,848,"2020-10-03",7.5588599752168528E-2,0,0,5.6106292165771718E-3,0.27629767313782183,0,0.55380008261049163,1.0704942861076689E-2,0,7.799807242186424E-2,24.399498815153304,25.055621061320764,0.2193396226415095,0.29599056603773605,"Continue to Monitor"]
["RICHMOND NORTH","Madison - 2236 Lexington Rd - Richmond",2171,"Richmond - Jacks Creek Rd, N Keeneland Dr, and Foxhaven Dr - SE of Substation",21.565195644513398,2089,"2024-01-01",4.3735474329178112E-3,0,0,0,0,0.10792309317557575,0.23905204591872667,0.17500528206211705,0,0.47364603141066275,41.898025366682631,35.651475977979899,0.53662039253231208,0.61704164672091899,"Reliability Improvements Completed in 2024"]
["LANCASTER 2","Garrard - 183 Industry Rd - Lancaster",2176,"Lancaster - Stanford Rd - SW of Substation",11.3413488509369,313,"2023-12-16",0,0,0,0,6.3526052819414702E-2,0.65988579586009988,0.27658815132048536,0,0,0,10.716813094249201,17.90260915654952,0.22124600638977635,0.33226837060702874,"Continue to Monitor"]
["BARTON","Nelson - 500 Cathedral Manor - Bardstown",2201,"Bardstown - New Haven Rd - E of Substation",0.78303737164142895,5,"2023-09-16",0,0,1,0,0,0,0,0,0,0,17.787500000000001,71.150000000000006,0.25,1,"Continue to Monitor"]
["BARTON","Nelson - 500 Cathedral Manor - Bardstown",2202,"Bardstown - New Haven Rd - W/N/S of Substation",1.1637684741188199,7,"2023-09-16",0,0,0.77449455676516332,0,0,0,0.22550544323483671,0,0,0,27.945238071428573,91.909523714285726,0.39285714285714279,1.2857142857142856,"Continue to Monitor"]
["COLUMBIA","Adair - 114 Lindsey Wilson St - Columbia",2210,"Columbia - Guthrie St, Miller Ave, & Adair Ave - S & SE of Substation",2.1682409294518998,150,"2019-03-23",0.91879494173072151,0,0,0,0,0,2.1572030746342674E-2,0,0,5.9633027522935783E-2,28.493055551666668,53.786888880000006,0.42333333333333339,0.88666666666666671,"Continue to Monitor"]
["GREENSBURG","Green - 424 Old Hodgenville Rd - Greensburg",2214,"Greensburg - Buckner Hill Rd, Hawthorne Rd, HWY 1464, & HWY 88 - SW of Substation",20.068362340952199,214,"2019-11-23",5.7472259248359794E-4,0,0,0,0,0,0.99284712725258362,5.6814444232866513E-3,0,8.9670573164609552E-4,154.59135513200937,296.53917444859815,1.0665887850467286,2.0186915887850461,"Continue to Monitor"]
["LEBANON CITY","Marion - 351 E Water St - Lebanon",2215,"Lebanon - E Main St, Woodlawn Ave, Harrison Ave, & Highland Dr - S/SE/E of Substation",6.4073128713838496,342,"2019-09-21",0,0,0.13406896551724137,0,3.8068965517241378E-2,0,0.65765517241379312,0.12082758620689656,0,4.9379310344827586E-2,8.4080774817251474,8.831140347953216,6.6520467836257313E-2,6.4327485380116955E-2,"Continue to Monitor"]
["LEBANON CITY","Marion - 351 E Water St - Lebanon",2216,"Lebanon - MLK Ave, Spalding Ave, Walnut St, & W Main St - SW of Substation",6.2198999884159196,643,"2019-09-21",1.6100906442033951E-3,0,0.49230889226877927,0,0.362359534912225,0,0.12022752976439192,6.5573587827937587E-3,0,1.6936593627606647E-2,36.885063500777605,112.61604457698289,0.22628304821150858,0.54432348367029548,"Continue to Monitor"]
["LEBANON CITY","Marion - 351 E Water St - Lebanon",2217,"Lebanon - Woodlawn Ave, Hood Ave, & Danville Hwy - E of Substation",3.40905364221637,258,"2019-09-21",7.0097835137385517E-2,0,0,0,0.92074313072439629,0,0,9.1590341382181521E-3,0,0,25.142393403100776,73.800129193798455,0.13468992248062014,0.27906976744186046,"Continue to Monitor"]
["LEBANON SOUTH","Marion - 1157 Bradfordsville - Bradfordsville",2220,"Lebanon - Metts Dr, Hill Creek Rd, & Hamilton Hts - W of Substation",5.5988198954243877,163,"2019-09-07",0,0,0.18885656746475721,0,0,0,0.62004922801521589,0.15887223092414413,0,3.2221973595882747E-2,17.687346616564415,22.224642116564414,0.21165644171779144,0.19631901840490801,"Continue to Monitor"]
["RUSSELL SPRINGS","Russell - 1183 HWY 1870 - Russell Springs",2221,"Russell Springs - Old Columbia Rd & Providence Rd - W of Substation",12.359493788299901,151,"2019-01-19",0.12873796249366448,0,1.6218955904713634E-2,0,5.2204764318297008E-2,0,0.77318803852002027,0,0,2.9650278763304613E-2,15.32069534602649,26.127373039735097,0.14238410596026491,0.21854304635761596,"Continue to Monitor"]
["RUSSELL SPRINGS","Russell - 1183 HWY 1870 - Russell Springs",2222,"Russell Springs - Old Columbia Rd, KY 80, Lakeway Dr, & Maple St - E of Substation",20.0735119491485,1027,"2019-01-26",5.7014734144778985E-3,0,4.6444586803331197E-4,0.2614509929532351,0.46795323510570147,0,6.7392696989109546E-2,0.18526585522101216,0,1.1771300448430493E-2,14.604495289435249,32.812122681596883,0.27069133398247325,0.35929892891918208,"Continue to Monitor"]
["RED HOUSE","Madison - 3858 Boonesboro Rd - Richmond",2224,"Richmond - Hwy 627, Simpson Ln, Hwy 25, & Hwy 2328 - W & NW of Substation",35.958550017921198,617,"2021-03-20",4.9787567429439529E-3,0,1.6848584578490537E-4,0,5.8941965050419388E-3,0,0.17329892477949416,0.81445777042680267,0,1.2018656999323249E-3,27.541247960696921,39.594165294975689,0.38654781199351718,0.90761750405186425,"Continue to Monitor"]
["SPRINGFIELD","Washinton - 107 Commercial Ave - Springfield ",2227,"Springfield - Main St - SE of Substation",5.8619205498093798,629,"2020-06-20",0,0,0,0,0.17819659180679381,5.8571267351314751E-2,0.54677801602527931,0.17785802956776889,0,3.8596095248843248E-2,8.8144011617647067,13.80092739109698,0.12360890302066772,0.16375198728139903,"Continue to Monitor"]
["UNION UNDERWEAR","Russell - 101 Fruit Of The Loom Dr - Jamestown",2228,"Jamestown - City of Jamestown - SSE of Substation",26.387630774367199,793,"2024-01-01",4.3140198138697086E-2,0,2.5217652356649654E-3,0,0,0,0.86772740918643043,7.163014109876914E-2,0,1.4980486340438307E-2,30.485119788461546,69.213808307692361,0.30895334174022709,0.77049180327868894,"Continue to Monitor"]
["UNION UNDERWEAR","Russell - 101 Fruit Of The Loom Dr - Jamestown",2229,"Jamestown - N Main St & Progress Dr - N & S of Substation",16.080689350017501,556,"2023-10-14",9.2126730172096202E-2,0,0.46042313562444082,0,0.17346455449713172,0,0.17225409188990054,1.8525340771538341E-2,0,8.3206147044892376E-2,21.786203528327341,38.781774564748204,0.21267985611510787,0.32194244604316535,"Continue to Monitor"]
["UNION UNDERWEAR","Russell - 101 Fruit Of The Loom Dr - Jamestown",2230,"Jamestown - Geneva Dr, Shawnee Ave, & Comanche Way - N of Substation",5.7857711446613198,183,"2023-10-07",0,0,0,0,0,0,0.77659473333967111,0.22340526666032892,0,0,49.233970848360656,97.267941710382516,0.41803278688524592,0.71038251366120231,"Continue to Monitor"]
["WOODLAWN","Nelson – 285 Spencer Mattingly Ln. – Bardstown ",2231,"Bardstown - Poplar Flat Rd, Ashleigh Way, Ed Piler Rd, & Old US 150 - SE of Substation",51.342252527897898,1217,"2018-09-15",3.733694257111521E-3,0,0.13926679579025972,0,2.0675331948755045E-2,0,0.38571395234872707,0.23984318484120132,0,0.21076704081394534,23.88861954847987,32.672897829909608,0.18919474116680363,0.28759244042728027,"Continue to Monitor"]
["WOODLAWN","Nelson – 285 Spencer Mattingly Ln. – Bardstown ",2232,"Bardstown - My Old KY Home St Park &  Gilkey Run Rd - SW of Substation",6.7014612721962701,135,"2018-10-13",1.7435658087745033E-2,0,1.1201493532470996E-2,0,0.90812108281104142,0,5.310708094412589E-2,1.0134684624616615E-2,0,0,218.49808640740741,222.19604936296298,1.7814814814814814,1.8740740740740738,"Continue to Monitor"]
["LEBANON EAST","Marion - 541 Corporate Dr. - Lebanon",2240,"Lebanon - Danville Hwy and Spalding Ave - W & E of Sub.",17.910415126203699,935,"2019-10-05",1.5741214434693635E-2,0,8.7009562787769071E-2,0,0,0,2.097516823422927E-2,0.49399866199677306,0,0.38227539254653498,19.449754896256685,37.891176464171124,0.36256684491978619,0.85454545454545472,"Tree Trim Scheduled for 2025"]
["LEBANON EAST","Marion - 541 Corporate Dr. - Lebanon",2241,"Lebanon - Corporate Dr - SW of Substation",0.152996084079498,1,"2019-10-05",0,0,0,0,0,0,1,0,0,0,4.9249999999999998,19.7,0.25,1,"Continue to Monitor"]
["BEATTYVILLE CITY","Lee - 950 W Main St. - Beattyville",2301,"Beattyville - W Main St, Lee Ave, & Grand Ave - E of Substation",8.1621696253115594,230,"2024-01-01",0,0,0,0,0.60019911304190421,0,0.38026970766585211,1.9531179292243642E-2,0,0,153.38177535000003,462.10224636521747,0.74239130434782596,2.1130434782608694,"Continue to Monitor"]
["IRVINE","Estill - 83 River Dr - Irvine",2304,"Irvine - City of Irvine/Ravenna & Cow Creek Rd - E of Substation",18.839051842772299,1115,"2021-01-23",2.2977270964238617E-2,0,0,2.2527344659064464E-2,0,0,0.13215421611977349,0.81359087735629509,0,8.7502909006283453E-3,15.508019426457398,19.902899847533632,0.14058295964125561,0.16591928251121074,"Continue to Monitor"]
["IRVINE","Estill - 83 River Dr - Irvine",2305,"Irvine - Kirkland Ave - SE of Substation",3.7212418103419602,81,"2021-01-23",5.3175210405508801E-2,0,3.5577658760520277E-2,0,3.2517214996174444E-2,0,0.67903596021423107,0.19969395562356543,0,0,22.210185175925925,32.271604925925928,0.16975308641975306,0.2839506172839506,"Continue to Monitor"]
["PAINT LICK","Garrard - 11811 HWY 52 E - Paint Lick",2310,"Paint Lick - HWY 52, White Lick Rd, & Noe Rd - S of Substation",10.8635854175541,146,"2020-04-18",4.5743169855459939E-3,0,1.8589690032584177E-2,0,1.2323502381151308E-3,0,0,0.12643077951374382,0,0.84917286323001084,7.646318481164383,8.2858447397260271,8.3904109589041098E-2,6.8493150684931503E-2,"Continue to Monitor"]
["RED HOUSE","Madison - 3858 Boonesboro Rd - Richmond",2311,"Richmond - Lost Fork Rd, Red House Rd, & Boonesboro Rd - S of Substation",9.3815420460277306,96,"2021-01-23",2.891566265060241E-2,0,0,0,0,0,0.73627844712182067,0.16760374832663991,0,6.7202141900937082E-2,19.360677072916666,38.892187479166665,0.38281250000000011,1.1562500000000004,"Continue to Monitor"]
["RICHMOND 2","Madison - 200 Fairview St - Richmond",2313,"Richmond - Four Mile Rd, Dr Robert R Martin Byp - N of Substation",28.6494561349005,3240,"2019-11-22",9.0579710144927537E-4,0,3.8975155279503106E-2,0,0.24940476190476191,0.32937370600414079,5.5124223602484465E-2,0.17437888198757764,0,0.1518374741200828,7.9174074050925931,8.5486162543209883,0.12824074074074074,0.11265432098765432,"Continue to Monitor"]
["RICHMOND 3","Madison - 950 Vickers Dr - Richmond",2314,"Richmond - Lancaster Ave, Barnes Mill Rd, Water St, & Crabbe St - N of Substation",8.9598604043970997,1175,"2024-01-01",3.7710018668326073E-2,0,0,0,0,0,0.44247044181705042,0.26313005600497819,0,0.25668948350964532,28.924624110851063,22.544936166808508,0.2719148936170212,0.37617021276595741,"Trees Trimmed in 2024"]
["RICHMOND","Madison - 315 Clay Dr - Richmond",2325,"Richmond - US 25, Keeneland Dr, & Jacks Creek Rd  - NW of Substation",4.2990866201935001,371,"2024-01-01",7.9033994770035379E-2,0,0,0,4.0609137055837565E-3,0,0.25740655283802494,0.63494846946623595,0,2.4550069220119982E-2,7.9992362964959574,17.952470797843667,0.1017520215633423,0.17520215633423181,"Trees Trimmed in 2024"]
["RICHMOND","Madison - 315 Clay Dr - Richmond",2326,"Richmond - Third St, New Richmond Byp, & Red House Rd - N of Substation",25.235711080203199,1019,"2019-08-03",5.4918029509110132E-4,0,1.9450579771770268E-2,0,0,0,0.54251815160841854,0.40411671947417321,0,3.3365368850546979E-2,38.81936129784102,36.4718678390579,0.38076545632973496,0.39548577036310101,"Tree Trim Scheduled for 2025"]
["RICHMOND","Madison - 315 Clay Dr - Richmond",2328,"Richmond - Georgia St, N 2nd St, & Golfview Dr - E of Substation",7.16891178890973,733,"2024-02-03",4.3256185155626493E-2,0,0.57581803671189147,0,0,0,0.25163607342378291,0.12354349561053472,0,5.7462090981644058E-3,18.29373578717599,17.094747611186904,0.15620736698499318,0.20190995907230558,"Continue to Monitor"]
["ELIZABETHTOWN 3","Hardin - 100 Crucible Steel Rd - Elizabethtown",2332,"Elizabethtown - Leitchfield Rd, Blackbranch Rd, & Nicholas St - SW of Substation",19.171449912409301,954,"2021-01-23",4.6327837580051774E-3,0,0.55762365444883499,0,2.1147295271835401E-2,0,5.6410955171004223E-2,1.7986101648725987E-2,0,0.34219920970159423,34.928756110587003,38.464744929769395,0.3139412997903564,0.59329140461215935,"Continue to Monitor"]
["NEW HAVEN","Nelson - 256 Lyons Station Rd - New Haven",2333,"New Haven - Center St, First St, & Depot St - SE of substation",1.4849144161874499,155,"2022-07-08",0.12397568067671161,0,0,0,0,0,0.45678033306899285,0,0,0.41924398625429554,13.52341397580645,24.405268812903223,0.13387096774193549,0.16129032258064516,"Continue to Monitor"]
["BONNIEVILLE","Hart - 8074 N Dixie Hwy - Bonnieville",2400,"Bonnieville - US 31, Olive Ave, & Waldeck Rd - N & S of Substation",8.3904229002649195,229,"2023-01-06",3.6831575118224809E-3,0,0,0,0,0,1.8643142961076754E-3,0.95291469625318304,0,4.1537831938886868E-2,36.146579322052403,91.110189209607,0.28056768558951967,0.67685589519650668,"Continue to Monitor"]
["LEBANON JUNCTION","Nelson - 1100 Old Nelsonville Rd. - Boston",2402,"Lebanon Junction - City of Lebanon Junction - NW of Substation",15.4304741812805,721,"2021-06-12",0,0,0.56406651476220493,0,2.4046153100305424E-2,0,0.28011829155960632,4.4068453968100066E-2,0,8.770058660978329E-2,17.536332633841887,21.921474796116506,0.16678224687933424,0.19694868238557556,"Continue to Monitor"]
["EASTVIEW","Hardin - 12540 Sonora - Hardin Springs",2406,"Sonora - Hwy 62, KY 1375, & Church Ln - NE of Substation",24.070473245265099,388,"2019-09-21",0,0,0.12326611764994662,0,0.25239877759913598,0,0.36709090685943618,0.19995336221603111,0,5.7290835675450118E-2,69.861898615335036,252.69454465979379,0.53350515463917514,1.7319587628865976,"Continue to Monitor"]
["EASTVIEW","Hardin - 12540 Sonora - Hardin Springs",2407,"Sonora - KY 84, Main St, & White Mills Rd - SE of Substation",14.879249605147701,268,"2019-09-21",7.4462868454986287E-4,0,0.30370558713669082,0,3.8484589818564861E-2,0,0.64210602786000981,1.4365885109242478E-2,0,5.9328139094216718E-4,68.754819640858216,80.997761171641798,0.65858208955223874,1.0074626865671641,"Continue to Monitor"]
["EASTVIEW","Hardin - 12540 Sonora - Hardin Springs",2408,"Sonora - W Main St, Skees St, & St. Paul Rd - SW of Substation",39.760155797554503,610,"2019-09-21",2.8066887997229974E-3,0,0.18747377640181681,1.1617817789274294E-2,4.8801352424791746E-3,4.6846039472880219E-4,0.78063832820742618,1.0884575432307473E-2,0,1.2302177322443327E-3,17.071810098360654,22.990983595081957,0.18483606557377047,0.2262295081967213,"Continue to Monitor"]
["ELIZABETHTOWN 2","Hardin - 1011 Woodland Dr - Elizabethtown",2409,"Elizabethtown - Woodland Dr - N of Substation",1.70085059645286E-2,1,"2021-02-13",0,0,0,0,0,0,1,0,0,0,46.612499999999997,186.45,0.25,1,"Continue to Monitor"]
["ELIZABETHTOWN 2","Hardin - 1011 Woodland Dr - Elizabethtown",2411,"Elizabethtown - Dixie Ave, Miles St, & Helm St - SE of Substation",14.896695423316199,1453,"2024-02-01",1.3217823358919643E-3,0,0.18269261394400738,0,9.5550530305443199E-5,0,0.1207758703060802,1.0829060101283563E-3,0,0.69403127687358668,35.459259575361322,31.414728146593252,0.4772883688919477,0.64211975223675155,"Continue to Monitor"]
["ELIZABETHTOWN 2","Hardin - 1011 Woodland Dr - Elizabethtown",2412,"Elizabethtown - Layman Ln - N of Substation",0.218476620889267,8,"2021-03-20",0,0,0,0,0,0,0,0,0,1,28.958333312499999,115.83333325,0.25,1,"Continue to Monitor"]
["ELIZABETHTOWN 2","Hardin - 1011 Woodland Dr - Elizabethtown",2414,"Elizabethtown - Woodland Dr, Ring Rd, & N Dixie HWY - N of Substation",17.510510146953788,1346,"2021-03-20",4.006398001580383E-2,0,9.983813820703015E-2,2.9950804210955623E-3,1.1470520761642578E-4,0,9.0241135836455877E-2,0.76404501542147785,0,2.7019448905202517E-3,35.353033675705795,85.985314508915309,0.30627786032689452,0.45913818722139671,"Continue to Monitor"]
["ELIZABETHTOWN 2","Hardin - 1011 Woodland Dr - Elizabethtown",2415,"Elizabethtown - Woodland Dr, Saint John Rd, & Westport Rd - S of Substation",8.1005963740198208,1449,"2024-03-01",9.6696862826452755E-3,0,5.1967360486826639E-2,0,0.33101675771615607,0,0.2007814120738538,0.39879676370928702,0,7.768019731231127E-3,18.477918678053829,22.297849089026908,0.23119392684610077,0.20013802622498272,"Trees Trimmed in 2024"]
["ELIZABETHTOWN 4","Hardin - 201 Sportsman Lake Rd - Elizabethtown",2418,"Elizabethtown - Dixie Hwy, New Glendale Rd, & Nicholas St - W & SW of Substation",21.017053477668199,709,"2020-05-16",2.4081515931427882E-3,0,0.62648063695609635,0,1.0227118797128279E-2,0,1.5901325988470973E-2,0.17363525533932361,0,0.17134751132583795,45.898213443229899,155.77959566854724,0.32933709449929477,1.0324400564174894,"Continue to Monitor"]
["ELIZABETHTOWN 5","Hardin - 800 N Mulberry St - Elizabethtown",2423,"Elizabethtown - Brooks Str, N Main St, & Guthrie St - S & E of Substation",5.5900065016199996,567,"2024-01-01",1.3110614742157911E-3,0,6.2979508594736333E-2,0,0.41468388851121685,0,0.14251723803049432,0.36602894046809747,0,1.2479362921239195E-2,41.807965892416227,64.330158721340382,0.65784832451499109,0.37213403880070545,"Trees Trimmed in 2024"]
["HODGENVILLE","Larue - 500 W High Ave - Hodgenville",2429,"Hodgenville - Tonieville Rd, N Lincoln Blvd, & Phillips Ln - NE of Substation",7.4722371700612102,383,"2022-03-22",0,0,0,0,0,0,0.40817009877783361,0.59182990122216639,0,0,11.634323319190599,22.702436892950388,0.12402088772845954,0.24020887728459533,"Continue to Monitor"]
["HODGENVILLE","Larue - 500 W High Ave - Hodgenville",2430,"Hodgenville - S Lincoln Blvd/Hwy 61, Greensburg Rd, & L & N Tpke - SE of Substation",35.955726217769197,1572,"2022-03-18",1.7100458697714308E-3,0,1.6112894213651779E-2,0,1.0590329664617905E-2,3.3785100770560185E-4,0.83739230999129388,3.3961822836129266E-2,0,9.9894746416830174E-2,59.207206843352402,91.955226877862557,0.82363231552162874,1.4866412213740463,"Continue to Monitor"]
["HODGENVILLE","Larue - 500 W High Ave - Hodgenville",2431,"Hodgenville - Hwy 61, New Jackson Hwy, BF Brown Rd, & L & N Tpke - S of Substation",24.925177037372901,471,"2022-04-15",0,0,6.0063412673603357E-2,0,0.2666458268208815,0,0.39356048765239138,0.27973027285312374,0,0,27.329493976645431,31.887933469214435,0.32802547770700635,0.22505307855626328,"Continue to Monitor"]
["HORSE CAVE","Hart - 501 Shewey Ave - Horse Cave",2432,"Horse Cave - Maple St, US 31 W, 3rd Street & Owen Street - SW of Substation",17.175273837655499,717,"2023-02-10",7.8926765272223278E-3,0,0,0,0.33585137222539624,0,0.54737721915402349,9.7208997228041216E-2,0,1.166973486531666E-2,12.960332398535565,24.924872147838215,0.13493723849372385,0.26778242677824271,"Continue to Monitor"]
["HORSE CAVE","Hart - 501 Shewey Ave - Horse Cave",2433,"Horse Cave - W Main St, KY 335, New St, US 31 - N & NW of Substation",23.948704478575198,905,"2023-04-05",1.2773795168749254E-3,0,5.6581022168629999E-4,0.11662846012164257,0.30476499662103967,0,0.35457749744921624,0.22213285277008496,0,5.3003299455391101E-5,142.18379833701658,333.7222467712707,1.3544198895027626,3.1535911602209943,"Continue to Monitor"]
["HORSE CAVE","Hart - 501 Shewey Ave - Horse Cave",2436,"Hiseville - Old Glasgow Rd & Hiseville Main St - SE of Substation",28.110531474016991,354,"2023-09-09",1.1475369639310498E-3,0,0,0,0,0,0.32056003727043131,0.42235245077605865,0,0.25593997498957899,205.25666194844632,332.68187381638415,1.067090395480226,1.562146892655367,"Continue to Monitor"]
["LEITCHFIELD CITY","Grayson - 205 Mulberry St - Leitchfield",2439,"Leitchfield - Conklin St, Floyd St, Brandenburg Rd, & Lilac Rd - NE of Substation",7.4933927595179597,663,"2019-03-09",2.0455737513841134E-2,0,0.40471472696544086,0,4.3009499388076231E-2,0,0.44789906171688332,8.3920974415758492E-2,0,0,36.582308942684762,46.119482143288074,0.47096530920060331,0.47511312217194562,"Continue to Monitor"]
["MILLWOOD","Grayson - 6649 Beaver Dam Rd - Millwood",2441,"Millwood - US HWY 62, School House Rd, & Rock Quarry Rd - NE of Substation",11.7460764295021,174,"2021-10-02",6.6970911249628973E-3,0,4.0293855743544077E-2,2.5100178094390028E-2,0.83732190560997333,0,3.3541110121697831E-2,5.7045859305431879E-2,0,0,87.63316569971262,309.78850572413785,0.64511494252873569,2.2701149425287359,"Continue to Monitor"]
["NEW HAVEN","Nelson - 256 Lyons Station Rd - New Haven",2445,"New Haven - KY 52, Clark Rd, & Lyons Station Rd - NW of Substation",13.7090178368609,206,"2022-06-24",0,0,0,0,0,0,0.99512948225477404,0,0,4.8705177452259734E-3,104.26057846723303,264.12006471359228,0.72208737864077666,1.0776699029126213,"Continue to Monitor"]
["RADCLIFF","Hardin - 677 N Wilson Rd - Radcliff",2448,"Radcliff - N Dixie Blvd & N Wilson Rd - NW of Substation'Town - Road - General Area",8.2045250705601394,604,"2024-01-01",6.0000960015360247E-4,0,0.23539576633226131,0,0.42586281380502089,0,0.25002400038400618,6.2232995727931645E-2,0,2.5884414150626409E-2,25.436610095198674,66.447213014900669,0.2429635761589404,0.71357615894039739,"Continue to Monitor"]
["ROGERSVILLE CITY","Hardin - 180 Rogersville Rd - Radcliff",2452,"Radcliff - Dixie Blvd, Yarwood Dr, Logan St & Vine St - N & S of Substation",10.6354217497144,693,"2024-01-01",1.3714335157585066E-2,0,0,0,7.0951134569209803E-3,0,0.69516969867399259,0.2679270587726319,0,1.609379393886954E-2,13.219666901515151,13.009716204906207,0.14033189033189034,0.17893217893217894,"Trees Trimmed in 2024"]
["SONORA","Hardin - 1340 Old Sonora Rd - Sonora",2456,"Sonora - US 31 W, S Dixie Hwy, & Sonora Rd - E of Substation",12.8099402582219,201,"2022-08-12",0,0,7.604887635648979E-3,0,0,0,0.81208237204135691,0.17718533709305306,0,3.1274032299410406E-3,56.899647582089557,65.021973447761198,0.58582089552238803,0.78606965174129351,"Continue to Monitor"]
["SONORA","Hardin - 1340 Old Sonora Rd - Sonora",2457,"Sonora - Sonora Hardin Springs Rd, Nolin Rd, Gilead Church Rd, & KY 222 - N of Substation",27.418720331961499,505,"2022-10-07",1.4585232452142207E-3,0,0.27486326344576117,0,2.677757520510483E-2,0,0.36893801276207844,0.31403828623518687,0,1.3924339106654512E-2,22.765726064851485,56.950396027722775,0.28168316831683171,0.73069306930693068,"Continue to Monitor"]
["SONORA","Hardin - 1340 Old Sonora Rd - Sonora",2458,"Sonora - Maple St, US 31, & City of Upton - S of Substation",17.751993476728799,519,"2022-10-28",0.28431212170783576,0,5.1938491738917061E-3,0,0.20358252903647964,0,3.108130214297399E-3,0.4856862424341567,0,1.8117127433338785E-2,17.420022473988439,25.088503526011557,0.34537572254335264,0.98265895953757232,"Continue to Monitor"]
["VINE GROVE","Hardin - 108 Crutcher St - Vine Grove",2459,"Vine Grove - Park St, Edgebrook Dr, Brown St, & 1st St - W of Substation",8.3158713939159199,550,"2024-01-01",0,0,0,0,1.4442171139728006E-3,0,0.62317968467926343,0.18485979058851848,0,0.19051630761824528,7.5853030281818175,12.463636360000001,7.0000000000000007E-2,0.1,"Continue to Monitor"]
["VINE GROVE","Hardin - 108 Crutcher St - Vine Grove",2460,"Vine Grove - Main St, Highland Ave, Central Ave, & Cheryl Ave - E of Substation",8.6519357570054805,682,"2020-10-03",0,0,0,0,8.5740992522093815E-2,0,0.66255948334466352,0.2516995241332427,0,0,11.220307916055717,24.41502932404692,0.11253665689149558,0.20821114369501467,"Continue to Monitor"]
["ELIZABETHTOWN INDUSTRIAL","Hardin - 111 Ring Rd - Elizabethtown",2462,"Elizabethtown - N Blackbranch Rd - NW of Substation",3.1979654027677502,8,"2020-10-24",1,0,0,0,0,0,0,0,0,0,16.595833312500002,66.383333250000007,0.21875,0.875,"Continue to Monitor"]
["LEITCHFIELD EAST","Grayson - 705 Wallace Ave - Leitchfield",2466,"Leitchfield - Wallace Ave, Bobby Bland Way, Clinton St, & White Oak St - S & W of Substation",4.4031261166948799,232,"2021-08-28",0,0,0,0,0.84521767540635473,0,0.14479022026191837,0,0,9.9921043317269739E-3,19.293049565732762,25.768318965517246,0.14978448275862069,0.16379310344827586,"Continue to Monitor"]
["HORSE CAVE INDUSTRIAL","Hart - 400 Cherry St - Horse Cave",2469,"Horse Cave - Hatcher Valley Rd, N Toohey Ridge Rd, & Park Ridge Rd - W of Substation",20.3032465825838,115,"2023-02-10",0,0,0,0,0,0,0.22083007047768208,5.7288067928816008E-2,0,0.72188186159350187,182.39793475652175,566.31724634782609,0.70652173913043481,1.7391304347826084,"Continue to Monitor"]
["RADCLIFF SOUTH","Hardin - 100 Energy Dr - Radcliff",2471,"Hardin - S Wilson Rd & Medical Center Dr  - SE of Substation",3.1349913677747399,109,"2019-04-06",0,0,0,0,0,0,1,0,0,0,2.8509556536697245,5.1620795045871555,3.8990825688073397E-2,3.669724770642202E-2,"Continue to Monitor"]
["HORSE CAVE INDUSTRIAL","Hart - 400 Cherry St - Horse Cave",2476,"Horse Cave - S Dixie St and Bluegrass Ave - SW of Substation",1.2317011945740599,13,"2023-01-28",0,0,0,0,0,0,0,1,0,0,28.933974346153846,73.211538461538467,0.23076923076923078,0.30769230769230771,"Continue to Monitor"]
["BLACK BRANCH ROAD","Hardin - 1220 N Black Branch Rd - Elizabethtown",2477,"Elizabethtown - City of Elizabethtown, W Main St, & St. Paul Rd- NE & SW of Substation",24.004345244569901,701,"2019-05-18",2.6308913173427638E-3,0,1.6107497861282227E-4,0,3.7508993352972551E-2,0,4.6740379349471853E-2,0.59370805339098631,0,0.31925060761061375,23.477639078815976,36.824060853067046,0.28780313837375182,0.30242510699001424,"Tree Trim Scheduled for 2025"]
["BLACK BRANCH ROAD","Hardin - 1220 N Black Branch Rd - Elizabethtown",2479,"Elizabethtown - N BlackBranch Rd - E of Substation",6.3233603466137396,77,"2021-03-13",1.5151515151515152E-2,0,0,0,0,0.4647562582345191,0,0.5200922266139657,0,0,38.506872279220779,39.431818168831171,0.30844155844155841,0.53246753246753242,"Continue to Monitor"]
["EMINENCE","Henry - 1257 Ballardsville Rd - Eminence",2502,"New Castle - Jackson Rd, Eminence Rd, & City of New Castle - N of Substation",27.799011707272602,925,"2022-07-08",1.0535667429869883E-3,0,2.1311084561051593E-3,0,0.61182658637715559,0,4.2679442661861022E-2,0.2019784678129366,0,0.14033082794895463,102.89611260783784,267.93801801081082,0.87270270270270267,2.0345945945945947,"Continue to Monitor"]
["FINCHVILLE","Shelby - 198 Parent Ln - Finchville",2504,"Simpsonville - Hwy 55, Buck Creek Rd, & Finchville Rd - NE & SW of Substation",45.571268305937302,560,"2022-07-08",1.3833763631459288E-2,0,2.4469191938653618E-3,4.7242880813841467E-2,0.6522484682671188,0,4.4121613810643133E-2,0.23018380794574389,0,9.9225463373280413E-3,51.428578858035713,71.76449404107143,0.59241071428571412,1.1660714285714284,"Continue to Monitor"]
["FLORIDA TILE","Anderson - 1247 Alton Rd - Lawrenceburg",2507,"Lawrenceburg - Alton Rd - SE of Substation",0.72414454896214697,1,"2022-04-30",0,0,0,0,0,0,0,0,0,1,204.375,817.5,0.25,1,"Continue to Monitor"]
["LAGRANGE EAST","Oldham - 1810 E Highway 146 - La Grange",2509,"La Grange - Grange Dr, Hwy 53, & Hwy 22 - S of Substation",72.936499821762496,2186,"2021-07-24",1.0892214729563471E-2,0,0,0,1.3598916073569948E-2,0,0.47990219744280577,0.31629783058977434,0,0.1793088411642865,36.97831083737421,76.629155225526105,0.41434126258005527,1.1770356816102487,"Continue to Monitor"]
["LAGRANGE EAST","Oldham - 1810 E Highway 146 - La Grange",2510,"La Grange - Jefferson St, Jericho Rd, & Walnut Aly - SW of Substation",7.8162096278884503,724,"2024-01-01",8.203510905083973E-2,0,1.9758340299414847E-3,0,0.77758568280264462,0,5.9635990576791552E-2,6.9667147959571393E-2,0,9.1002355802112626E-3,28.345862103591159,65.810750457182323,0.20441988950276241,0.26933701657458559,"Continue to Monitor"]
["LAGRANGE EAST","Oldham - 1810 E Highway 146 - La Grange",2511,"La Grange - Waterworks Rd, Hwy 53/1st St, & Fendley Mill Rd - W of Substation",18.137722434765699,1292,"2024-01-01",0.11819274393450012,0,0,0,0,0,0.55068980194797057,0.33111745411752924,0,0,16.788822235874612,36.447510316563466,0.13138544891640869,0.22678018575851394,"Trees Trimmed in 2024"]
["LAGRANGE PENAL","Oldham - 3011 W Highway 146 - La Grange",2512,"La Grange - W Highway 146 - W of Substation",9.3291225575972397E-3,1,"2024-01-01",0,0,0,0,1,0,0,0,0,0,114.25416650000001,341.03333300000003,0.75,1,"Continue to Monitor"]
["LAGRANGE PENAL","Oldham - 3011 W Highway 146 - La Grange",2513,"La Grange - HWY 146, Jefferson St, & Allen Ln - NE of Substation",24.300708856665999,1541,"2024-01-01",1.7900559441659913E-2,0,7.5143007766088864E-3,0,7.1492080477767894E-2,0,2.8090108662297095E-2,0.85018608713441546,0,2.4816863507250712E-2,37.538113775470478,59.245511567813111,0.48069435431537977,1.1440622972096046,"Trees Trimmed in 2024"]
["LAWRENCEBURG","Anderson - 108 E Broadway st - Lawrenceburg ",2518,"Lawrenceburg - Waterfill Rd - N of Substation",13.4863690180484,1184,"2024-01-01",2.6112217253647553E-4,3.0328252331059396E-4,1.974056424149449E-2,0,0,0,0.80805208299333042,0.15114485752521462,0,2.0498090544113327E-2,58.954057570312493,36.538527585304053,0.72888513513513509,1.1984797297297298,"Continue to Monitor"]
["SHELBYVILLE","Shelby - 1201 Willow St - Shelbyville",2519,"Shelbyville - Smithfield Rd, Bayberry Dr, & La Grange Rd - NW of Substation",42.729414170907411,2274,"2023-06-03",5.7728484088415112E-2,0,5.7218999843235618E-3,9.9741338767831943E-3,3.6839630036055808E-3,0,0.18288524847154727,0.33533861106756546,0,0.40466765950775985,15.483045658531223,18.435143649076515,0.2222955145118734,0.14423922603342135,"Continue to Monitor"]
["SHELBYVILLE","Shelby - 1201 Willow St - Shelbyville",2520,"Shelbyville - KY 43, KY 12 & Washington St - E of Substation",4.4058089665866298,238,"2022-08-12",5.2688953488372091E-3,0,0,0,4.923691860465116E-2,0,8.7209302325581394E-3,0.31413517441860467,0,0.62263808139534882,20.202485990546222,22.926820722689076,0.22478991596638659,0.27731092436974791,"Continue to Monitor"]
["SHELBYVILLE SOUTH","Shelby - 614 Mack Walters Rd - Shelbyville",2526,"Shelbyville - Kentucky St, Old KY 53, Osprey Cove, & Zaring Mill Rd - S & SE of Substation",29.8513215104403,1285,"2022-09-09",1.315128409728995E-2,0,0,0,0.63386234004196584,0,7.0829762291771334E-2,1.7998049472470967E-2,0,0.26415856409650185,69.426789877820994,76.157159528404662,0.94571984435797662,1.0412451361867703,"Continue to Monitor"]
["TAYLORSVILLE","Spencer - 1604 Elk Creek Rd - Taylorsville",2529,"Taylorsville - Elk Creek Rd, KY 55, & Hwy 1633 - N of Substation",51.266053069545997,1098,"2020-07-18",8.2234382943093803E-3,0,2.108190544541132E-3,0.4007281480816961,0,0,1.8360694955294399E-2,0.55839388774259147,0,1.2185640381567537E-2,35.211839704234976,110.45887977686705,0.40664845173041886,1.3533697632058284,"Continue to Monitor"]
["TAYLORSVILLE","Spencer - 1604 Elk Creek Rd - Taylorsville",2530,"Taylorsville - Elk Creek Rd, City of Taylorsville, & Bloomfield Rd - SE of Substation",27.2685856388402,827,"2020-05-02",2.6396766019066008E-2,0.13662966091468565,0.12058042717509351,0,2.7150959333896462E-4,0,0.16746108362495477,0.53221913840955715,0,1.644141426330397E-2,31.510111841596135,26.495667065296246,0.47128174123337369,1.120918984280532,"Continue to Monitor"]
["LOCKPORT","Henry - 88 Sawmill Rd - Bethlehem",2532,"Bethlehem - KY 22, Hwy 1360, Sewell Rd, & Bethlehem Rd - SW of Substation",50.546975938061799,957,"2022-05-13",1.4983905654807922E-2,1.7710807809622872E-3,3.0347328619822048E-2,3.1907566450669776E-3,1.1793149009740945E-2,0,0.83713084913484115,8.9819096748801706E-3,0,9.1801020479878551E-2,24.712286648380356,26.889150108672933,0.30721003134796226,0.23197492163009395,"Continue to Monitor"]
["SHELBYVILLE EAST","Shelby - 183 Boone Station Rd - Shelbyville ",2533,"Shelbyville - KY 53, KY 44, & Mill St - S of Substation",53.721687754608297,1492,"2019-12-13",7.2069042815512217E-3,0,0,0,0.57350369872225959,9.2449376074123887E-2,0.30211462302921616,2.4725397892849135E-2,0,0,47.411260049765403,123.82369302211792,0.38505361930294901,0.83646112600536171,"Continue to Monitor"]
["SHELBYVILLE SOUTH","Shelby - 614 Mack Walters Rd - Shelbyville",2534,"Shelbyville - Main St/US 60, Sunset Way, Old KY 55, & Haven Hill Rd - NW of Substation",11.5433807509846,920,"No Trimming Necessary",0.12748042963772074,2.5213908610959401E-2,0.41156926997997451,0,9.0569816129619524E-3,0,0.15665392317494992,1.7613326051338068E-2,0,0.2524121609320954,20.41536231548913,23.882192025000005,0.20923913043478257,0.3380434782608695,"Continue to Monitor"]
["EMINENCE","Henry - 1257 Ballardsville Rd - Eminence",2535,"Eminence - Giltner Rd, Smithfield Rd, & Hwy 22 - W of Substation",14.624965580264501,240,"2021-12-04",0,0,0,0,6.047411707789066E-3,0,0,0.99395258829221089,0,0,68.856684017301831,54.405138881707309,0.7270833333333333,1.0125,"Continue to Monitor"]
["SHELBYVILLE SOUTH","Shelby - 614 Mack Walters Rd - Shelbyville",2537,"Shelby - Old Finchville Rd, Hwy 55, & Gordon Ln - SW of Substation",13.3258221409136,508,"2023-01-06",5.1803530314658477E-3,0,0,0,0,0,1.2087490406753646E-2,0.95644666155026858,0,2.6285495011511895E-2,37.423720468503937,41.042913379921252,0.4114173228346456,0.37007874015748032,"Continue to Monitor"]
["SIMPSONVILLE","Shelby - 6801 Shelbyville Rd - Simpsonville",2540,"Simpsonville - Buck Creek Rd, Kingbrook Pky, & Rolling Ridge Way - S of Substation",5.1369487791908703,333,"2023-11-11",0.74300313552432939,0,0,0,0,0,0,0.25699686447567066,0,0,11.388788788288288,25.858258258258257,0.10435435435435435,0.24624624624624625,"Continue to Monitor"]
["SIMPSONVILLE","Shelby - 6801 Shelbyville - Simpsonville",2541,"Simpsonville - Shelbyville Rd, Champions Way, & Conner Station Rd - SW of Substation",60.659447520527699,1197,"2019-05-18",3.3530882327232042E-3,0,0,0,2.744707260362581E-4,0,0.42694533312354677,0.31608538312267265,0,0.25334172479502104,130.54144388053467,275.67971316374269,0.62698412698412709,1.4218880534670013,"Tree Trim Scheduled for 2025"]
["WEST SHELBY","Shelby - 3900 HWY 60 - Shelbyville",2544,"Shelbyville - 3900 HWY 60 - E of Substation",3.0135464912219398,973,"2023-12-16",0.28986387943607195,0,0,0,9.4676713660670875E-2,0.22927807486631016,0.22131745260087504,4.436071949440934E-2,0,0.12050315994166262,3.7941418281089421,13.395906128468656,4.6505652620760542E-2,0.16957862281603292,"Continue to Monitor"]
["WEST SHELBY","Shelby - 3900 HWY 60 - Shelbyville",2545,"Shelbyville - 3900 HWY 60 - E of Substation",1.4808294193043601,134,"2023-12-16",0.10996705107084019,0,0,0,0,0,0.55271828665568368,0.33731466227347612,0,0,4.5304415373134326,18.12176614925373,5.5970149253731324E-2,0.2238805970149253,"Continue to Monitor"]
["GREEN RIVER","Muhlenberg - 811 Power Plant Dr - South Carrollton",3412,"Muhlenberg - HWY 431 & 138 - N of Substation",7.7293736042792203,618,"2021-09-24",0,0,0,0,0.10516252390057361,0,0,0,0,0.89483747609942643,8.0051847350323619,11.003182305825241,0.50121359223300965,1.0016181229773462,"Continue to Monitor"]
["RUMSEY","McLean - 1/8 SE of HWY 138 - Earlington",3424,"Earlington - HWY 138 - SE of Substation",9.6833712296831607,783,"2017-10-31",0,0,0,0,0,0,0.98577744693329727,0,0,1.4222553066702759E-2,28.308450404214561,113.23380161685824,0.25159642401021709,1.0063856960408684,"Continue to Monitor"]
["ALVA","Harlan - Rockhouse Branch Rd - Pathfork",4331,"Alva - Hwy 72 & Alva Rd - NW of Substation",2.07835258190959,9,"2022-12-02",0,0,0,0,0.91607004863857444,0,5.5553661530069548E-2,2.1194145188417654E-2,0,7.1821446429383151E-3,241.80046294444446,742.38518511111113,0.80555555555555558,2.4444444444444446,"Continue to Monitor"]
["FOURMILE","Bell - Hwy 2014 - Pineville",4340,"Pineville - Hwy 2014 & 2015, US 25, & Hwy 92 - SW & N of Substation",16.012038269970301,176,"2022-12-02",6.067567965597479E-3,0,0,0,8.9344447389865791E-4,0,0.86947856224166198,1.8919423090139709E-2,0,0.10464100222870215,175.95089960085227,238.64554923295455,1.0539772727272729,1.0965909090909094,"Continue to Monitor"]
["DANIEL BRANCH","Harlan - Gilbert Rd/Bandana Branch - Smith",4421,"Rose Hill - Hwy 987 - E of Substation",20.688521431407398,234,"2021-10-16",1.4063518318780705E-3,0,2.8351900480598824E-2,0,2.8119414134407598E-2,0,0.86364104108148076,7.722739070283291E-2,0,1.2539017688018568E-3,211.07459043162396,396.69537034188045,1.7200854700854697,2.7606837606837602,"Continue to Monitor"]
["CATRONS CREEK","Harlan - Near 6872 Hwy 72 - Gulston",4427,"Gulston - Hwy 72 & Bardo Hollow Rd - SW of Substation",3.11208244069954,90,"2020-02-15",0,0,0,0,0.10140023172351428,0,0.62696753044903497,0,0,0.27163223782745077,408.52819443333328,1572.7475925777776,1.4555555555555555,5.5444444444444443,"Continue to Monitor"]
["CATRONS CREEK","Harlan - Near 6872 Hwy 72 - Gulston",4428,"Gulston - Hwy 1216, Hwy 72, & Hwy 2425 - N of Substation",8.9807473614754407,318,"2024-01-01",9.2774450123821253E-3,0,0,0,0,0,0.51266270601295549,0.43713173849926196,0,4.0928110475400438E-2,184.19144390644655,303.5074423333333,0.85534591194968557,1.4937106918238994,"Trees Trimmed in 2024"]
["LYNCH","Harlan - Hwy 160 (W Main St) - Lynch",4451,"Lynch - W Main St, Mountain St, & 1st, 2nd, & 3rd St - W of Substation",4.5939906059969404,513,"2024-02-01",0,0,0,0,4.7771912370247818E-3,0,0.94907993269656243,4.0599079509936277E-2,0,5.5437965564765464E-3,339.22604774951265,475.46520467056541,1.6924951267056532,0.86744639376218347,"Continue to Monitor"]
["EVARTS","Harlan - 1600 Block of Hwy 215 - Evarts",4475,"Evarts - Hwy 215 & City of Evarts - W of Substation",10.9854544242398,603,"2024-01-01",1.8763519469806666E-4,0,0,0,2.4215560976127847E-3,0,0.96657615333689728,2.5475903038628067E-2,0,5.3387523321638585E-3,116.90693061318407,260.28150910945277,0.81301824212271978,1.9784411276948592,"Continue to Monitor"]
["EVARTS","Harlan - 1600 Block of Hwy 215 - Evarts",4476,"Evarts - Hwy 215 - E of Substation",14.7278887062084,457,"2023-04-07",2.8757480166494956E-4,0,0,0,7.674652519433342E-2,0,0.91653277030166191,5.4116965624637558E-3,0,1.0214331398759767E-3,259.80212434682716,296.47359590590804,1.6012035010940922,2.3916849015317285,"Continue to Monitor"]
["VERDA","Harlan - Corner of School St - Evarts ",4479,"Evarts - Hwy 38, Nolan Ln, & Ages Creek Rd - W of Substation",13.6253858498953,492,"2021-11-13",0.14081993461872039,0,0,3.677696977783708E-3,0.16561311628527586,0,0.55273867502835416,0.13700880645806923,0,1.4177063179665088E-4,61.231741181402427,107.71222898373982,0.47357723577235766,0.89837398373983735,"Continue to Monitor"]
["VERDA","Harlan - Corner of School St - Evarts ",4480,"Evarts - Hwy 38, Hill St, & Hwy 1601 - NE & SE of Substation",10.234010356408501,378,"2024-01-01",0,0,0,3.4614739749439763E-4,6.1089607104675335E-2,0,0.21576340825381257,0.61514358807017411,0,0.10765724917384352,302.25690033862435,179.37398588624342,2.072089947089947,2.5317460317460321,"Trees Trimmed in 2024"]
["SOMERSET 3","Pulaski - 125 Young St. - Somerset",4501,"Somerset - E Mt. Vernon St & Eller St - E & SW of Substation",8.8950304921674519,760,"2020-10-10",3.4582569293951836E-2,3.5006895297558611E-3,3.1218270265355296E-3,0,0,0,0.18670344158697924,0.70750299301377551,0,6.458847954900207E-2,68.67837718388158,61.00096490526316,0.75460526315789433,0.92105263157894735,"Continue to Monitor"]
["SOMERSET 3","Pulaski - 125 Young St. - Somerset",4502,"Somerset - Pumphouse Rd, Speedway Dr, & College St - W of Substation",13.1970166360978,912,"2020-10-10",0,2.5785462113839617E-3,0.19182821057417049,0,0.13407729955887682,0,0.51032483999516964,9.0192289933724967E-2,0,7.0998813726674104E-2,43.691534169407902,62.581213445175436,0.43064692982456143,0.79276315789473684,"Continue to Monitor"]
["SOMERSET 2","Pulaski - 105 Tandy Ave - Somerset ",4506,"Somerset - N Main St, Robin Dr, & Elliott Dr - NW of Substation",1.71795064618335,103,"2024-02-01",0,0,0,0,0,0,0.62452350698856418,0.37547649301143582,0,0,16.07220873300971,30.567152097087376,0.10436893203883493,0.16504854368932037,"Trees Trimmed in 2024"]
["MCKEE ROAD","Pulaski - 140 McKee Rd - Somerset",4512,"Somerset - Hwy 1247, Crab Orchard Rd, & Oak Leaf Ln - N & E of Substation",33.970085003498099,1307,"2024-01-01",9.1703939554746927E-2,0,0.20430596618906829,0,0,0,0.56250473807899326,4.6951204103808153E-2,0,9.4534152073383365E-2,18.414524348890591,23.909334346595259,0.1228003060443764,0.13848508033664875,"Continue to Monitor"]
["AISIN","Laurel - Farriston Rd/Greta Ln - Lily",4618,"Lily - Greta Ln & S Laurel Rd - S of Substation",1.04307349341317,155,"2023-12-01",1.5622760498781712E-2,0,0.49935502364913287,0,7.8830442883760926E-3,0,3.0098896373799626E-3,0.45979647412928193,0,1.4332807797047441E-2,17.569542996774196,20.538494606451614,0.18548387096774194,0.21290322580645157,"Continue to Monitor"]

{"sheet":"KU Section 6-7","index":2,"n_rows":31,"n_cols":1,"rows_kept":31,"cut":false,"hidden":false,"merged":[[30,0,33,8],[29,0,29,8],[20,0,21,8],[15,0,15,5],[16,0,16,6],[17,0,17,6],[18,0,18,6],[19,0,19,6],[26,0,27,8],[23,0,24,8],[0,0,0,8],[2,0,2,8],[4,0,4,8],[5,0,10,8],[11,0,14,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
[]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 6: VEGETATION MANAGEMENT PLAN REVIEW"]
["The Companies’ Vegetation Management Plan went into effect January 1, 2024 and is reflected in this reporting period (see attached).  The Distribution Vegetation Management Program encompasses right of way maintenance for Louisville Gas and Electric Company and Kentucky Utilities Company (referred to as the “Companies”).  The program is centralized and managed by a Forestry Manager and eight company Utility Arborists.  All are certified arborists by the International Society of Arboriculture."]
[]
[]
[]
[]
[]
["The Companies’ plan is to maintain a proactive trim cycle while balancing the reactive needs of worst performing circuits. The Companies’ goal is to maintain an average trim cycle of five years or less.   The effectiveness of the plan is evaluated by the cycle and system performance as measured by system SAIDI, SAIFI, and CAIDI.  "]
[]
[]
[]
["Effectiveness of the program"]
["KU/LG&E Tree Cycle – 5.03 years"]
["KU (Kentucky) Tree SAIDI – 26.84 minutes"]
["KU (Kentucky) Tree SAIFI – 0.162"]
["KU (Kentucky) Tree CAIDI – 166.2 minutes"]
["The hazard tree program, mid cycle, herbicide, and worst performing circuits were completed as planned.  "]
[]
["Adjustments made to the tree plan in 2024 included"]
["Our vegetation management approach leverages unit-based, target pricing, and time-and-expense models to drive efficiency and accountability in contractor operations. The target price strategy deploys prescriptive tree management techniques. Maintenance work is prescribed ensuring that each work segment is clearly defined, mapped, and costed in advance. All work areas are inspected post-completion to verify standards have been met.\nContractor performance is systematically evaluated on a quarterly and annual basis, with a focus on safety, productivity, quality, and customer satisfaction. Compliance with OSHA and internal safety standards is mandatory, and contractors are held to the highest operational standards."]
[]
["Changes to be implemented in 2025"]
["The routine trimming cycle plan is a proactive plan to trim work areas based on time since trim and clearance thresholds. Danger trees are prioritized and mitigated based on reliability disruption potential."]
[]
[]
["SECTION 7: UTILITY COMMENTS"]
["Rolling average SAIDI and SAIFI improved in 2024 compared to the previous 5 year average excluding major events.  494 Circuits were above their previous 5 year average SAIDI and/or SAIFI in 2024.  "]