{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["KU Section 1-4","Excel KU Section 5","KU Section 6-7"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"KU Section 1-4","index":0,"n_rows":46,"n_cols":8,"rows_kept":46,"cut":false,"hidden":false,"merged":[[45,2,45,6],[37,0,37,8],[38,1,38,8],[39,1,39,8],[40,1,40,8],[41,1,41,8],[44,0,44,8],[36,1,36,3],[36,6,36,8],[28,3,28,5],[29,1,29,3],[29,6,29,8],[30,1,30,3],[30,6,30,8],[31,1,31,3],[31,6,31,8],[33,3,33,5],[34,1,34,3],[34,6,34,8],[35,1,35,3],[35,6,35,8],[26,0,26,1],[26,5,26,6],[14,0,14,8],[15,0,15,3],[15,5,15,8],[16,0,16,3],[16,5,16,8],[17,0,17,3],[17,5,17,8],[18,0,18,3],[18,5,18,8],[20,0,21,8],[24,0,24,8],[25,2,25,6],[11,0,11,3],[11,5,11,8],[0,0,0,8],[1,0,1,8],[3,0,3,8],[4,0,4,3],[4,5,4,8],[5,0,5,3],[5,5,5,8],[6,0,6,3],[6,5,6,8],[7,0,7,3],[7,5,7,8],[10,0,10,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 1: CONTACT INFORMATION"]
["UTILITY NAME",null,null,null,null,"KENTUCKY UTILITIES COMPANY"]
["REPORT PREPARD BY",null,null,null,null,"Karmen Powell (Mgr Investment Strategy & Reliability)"]
["E-MAIL ADDRESS OF PREPARER",null,null,null,null,"Karmen.Powell@lge-ku.com"]
["PHONE NUMBER OF PREPARER",null,null,null,null,"(502) 399-4805"]
[]
[]
["SECTION 2: REPORTING YEAR"]
["CALENDAR YEAR OF REPORT",null,null,null,null,2025]
[]
[]
["SECTION 3: MAJOR EVENT DAYS (MED)"]
["TMED",null,null,null,null,3.78071038983142]
["FIRST DATE USED TO DETERMINE TMED",null,null,null,null,"2020-01-01"]
["LAST DATE USED TO DETERMINE TMED",null,null,null,null,"2024-12-31"]
["NUMBER OF MED IN REPORTING YEAR",null,null,null,null,9]
[]
["NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years.  If five years of data are not available, then utilities should use what is available until five years are accumulated.        \n"]
[]
[]
[]
["SECTION 4: SYSTEM RELIABILITY INFORMATION AND RESULTS"]
[null,null,"System-wide Information"]
["TOTAL CUSTOMERS",null,562321,null,null,"TOTAL CIRCUITS",null,1123]
[]
[null,null,null,"Excluding MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",75.02436446052657,null,null,null,"SAIDI",84.418269520095549]
["SAIFI",0.66622525016858303,null,null,null,"SAIFI",0.74747662219318345]
[]
[null,null,null,"Including MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",400.51656374911744,null,null,null,"SAIDI",185.12062239778885]
["SAIFI",1.0068486204260811,null,null,null,"SAIFI",0.99804077513753753]
["Notes:  "]
["1)","All duration indices (SAIDI) are to be reported in units of minutes."]
["2)","Reports are due on the first business day of May of each year"]
["3)","Reports cover the calendar year ending in the December before the reports are due."]
["4)","IEEE 1366 (latest version) is used to define SAIDI, SAIFI, and TMED"]
[]
[]
["SECTION 5: CIRCUIT REPORTING"]
[null,null,"BEGIN ON NEXT PAGE"]

{"sheet":"Excel KU Section 5","index":1,"n_rows":517,"n_cols":22,"rows_kept":517,"cut":false,"hidden":false,"merged":[]}
["Substation Name","Substation Location   \n(County - Road - Town)","Circuit\nNumber","Circuit Location\n (Town - Road - General Area)","Total Circuit Length (Miles)","Average 2025 OMS Custs","Date of Last Circuit Trim (VM)","Animal","Construction","Lightning","Non-Company","Other/Unknown","Overload","Planned Work","Trees","Vehicle","Utility Equipment","2021-2025 SAIDI Average","2025 SAIDI","2021-2025 SAIFI Average","2025 SAIFI","LIST OF CORRECTION ACTION, IF ANY, TAKEN OR TO BE TAKEN"]
["LEXINGTON PLANT","Fayette - 745 N Limestone - Lexington",1,"Lexington - N. Broadway - SW of Station",2.9852013300113498,529,"2023-04-01",0,0,0,3.2630038199278857E-2,0,4.9623362250544433E-3,0.17132555067651994,0.50979972153796727,0.24829531255578166,3.2987040805397883E-2,109.99021423667295,92.662980465028355,0.65482041587901707,1.1568998109640831,"Reliability Improvements Scheduled for 2026"]
["LEXINGTON PLANT","Fayette - 745 N Limestone - Lexington",3,"Lexington - N. Upper St. and 6th St. - W of Station ",4.6785128485170198,580,"2023-04-01",0,0,0,0,0,0.1474867724867725,0.85251322751322745,0,0,0,47.752022986206889,79.242701148275856,0.47724137931034483,1.1810344827586208,"Continue to Monitor"]
["LEXINGTON PLANT","Fayette - 745 N Limestone - Lexington",4,"Lexington - Loudon Ave and Bryan Ave. - E of Station",4.06736010631111,653,"2023-04-01",0,0,0,0,0,2.3720403899721448E-2,0.20007834261838439,9.1399721448467974E-3,8.4435933147632314E-2,0.682625348189415,32.958223580704441,51.571235321592653,0.3635528330781011,1.0995405819295561,"Reliability Improvements Scheduled for 2026"]
["BUCHANAN","Fayette - 108 Buchanan St. - Lexington",5,"Lexington - W. Main St. and Jefferson St. - E of Station",5.0719209606267803,674,"2023-08-05",0,0,0,0,4.2302237041829446E-3,4.5910369024809015E-2,0.72289546370716895,0.20558887202329112,0,2.1375071540547939E-2,48.767952519881305,178.87376359495551,0.31869436201780416,0.87982195845697331,"Continue to Monitor"]
["LEXINGTON PLANT","Fayette - 745 N Limestone - Lexington",6,"Lexington - N. Limestone St. SW of Station",2.6201319048720699,382,"2023-04-21",0,0,0,0.13379740175644503,0,5.2490995183941076E-2,3.1972155894613298E-3,6.4227609373102915E-2,2.4565947630418066E-2,0.7217208304666316,37.572268758638742,64.683333329842938,0.47329842931937172,1.1047120418848169,"Continue to Monitor"]
["LEXINGTON PLANT","Fayette - 745 N Limestone - Lexington",7,"Lexington - N. Limestone St and York St. - NE amd SE of Station ",6.4644899987533604,1250,"2023-04-21",1.0294766476878795E-3,0,0,0.59566079094620805,0,4.8133285711284328E-2,0.2683432429214726,1.046284429690947E-2,2.1429922053910959E-3,7.4227367271046493E-2,40.51550666416,112.12751999599999,0.16016000000000002,0.37040000000000006,"Reliability Improvements Scheduled for 2026"]
["AMERICAN AVENUE","Fayette - 96 Burley Ave. - Lexington",8,"Lexington - University Dr. - University of Kentucky Campus",6.3722672590473604,753,"2025-01-01",0.74590517241379306,0,0,0,1.6487068965517243E-2,0,0.21594827586206897,0,0,2.1659482758620691E-2,10.527184593094288,12.322089419654715,0.29030544488711812,0.15006640106241698,"Continue to Monitor"]
["BUCHANAN","Fayette - 108 Buchanan St. - Lexington",10,"Lexington - Manchester St. - S of Station",4.04907049922413,444,"2023-08-05",0,0,0,0,0.285387501143746,0,3.1841888553390062E-2,0,2.6534907127825053E-2,0.65623570317503888,12.362980478378379,24.614489484234234,0.12657657657657656,0.16891891891891891,"Continue to Monitor"]
["LEXINGTON WATER COMPANY","Fayette - 2300 Richmond Rd. - Lexington",11,"Lexington - Richmond Rd and Holiday Rd - NW of Station",3.35470422029627,154,"2022-05-06",0,0,0,0,0,3.0530571829358857E-3,2.6817394174436834E-2,0.94764419506559949,0,2.2485353577027807E-2,85.916580077922063,157.3919913246753,0.52727272727272734,0.40259740259740256,"Tree Trim Scheduled for 2026"]
["RACE STREET","Fayette - 420 Corral St - Lexington",15,"Lexington - Coral St & Forrest Ave. - SE of Substation",3.1616794651269999,520,"2023-12-23",0,0,0,0,0,4.1379655141765177E-2,0.47139698693449467,5.2978624122300241E-2,0.43363367700648831,6.1105679495155989E-4,88.482897430769228,330.56282049807692,0.48615384615384605,1.8980769230769226,"Continue to Monitor"]
["SCOTT STREET","Fayette - 301 Scott St. - Lexington",17,"Lexingotn - Broadway Rd. - SE of Substation",4.8218629427544197,992,"2025-01-01",0,0,0,0,0,0.11735330836454431,0,0.1523096129837703,0,0.7303370786516854,4.54304099375,7.0678259395161298,0.22903225806451616,1.0181451612903227,"Continue to Monitor"]
["SCOTT STREET","Fayette - 301 Scott St. - Lexington",18,"Lexington - Limestone St. - SE of Substation",3.20909726092551,886,"2025-01-01",0,0,0,0.12460169212174486,0,1.3915730010276827E-2,4.2328897276963748E-2,0,0,0.81915368059101457,46.189939803160271,180.44115876185103,0.46659142212189619,1.9503386004514676,"Continue to Monitor"]
["JOYLAND","Fayette - 2375 Paris Pike - Lexington",25,"Lexington - Beverly Ave. & Bryan Station Rd. - SW of Substation",28.187540937041899,1706,"2020-04-04",0.85492335555420695,0,0,7.1262245703023934E-3,1.0793147836419447E-2,2.7214447933203221E-3,1.4188565460010414E-2,3.4717586219012421E-2,3.4893266340646947E-2,4.0636409226081152E-2,92.361193819343512,183.41074637749128,0.84478311840562748,1.1858147713950768,"Reliability Improvements Scheduled for 2026"]
["KUNKEL","Fayette - 2000 Versailles Rd. - Lexington",26,"Lexington - Duntreath Dr. & Pine Mt. Rd. - SE of Substation",4.6641109297998797,584,"2024-01-01",0,0,0,0,7.8062263058621397E-3,0,0,0.99219377369413786,0,0,273.39336757636988,532.7526255702054,0.92397260273972603,1.0136986301369861,"Continue to Monitor"]
["RACE STREET","Fayette - 420 Corral St - Lexington",30,"Lexington - Midland Ave. & Winchester Rd. - E of Substation",5.2054042072919398,941,"2023-12-23",0,0,0,0,0,5.2022035808188309E-2,0.57584199323901342,0.27272442719419054,2.1534994365844499E-2,7.7876549392763242E-2,30.777127166206164,33.951983701381508,0.32794899043570669,0.49415515409139216,"Continue to Monitor"]
["RACE STREET","Fayette - 420 Corral St - Lexington",31,"Lexington - Corral St. & MLK Blvd. - NE of Substation",2.8423645081899598,588,"2023-12-23",0,0,0,0,0,7.6733882515456278E-3,0.93467933491686461,0,0,5.7647276831589767E-2,92.951014732993201,201.90595237244904,0.58163265306122447,0.7142857142857143,"Continue to Monitor"]
["HUGHES LANE","Fayette - 251 Hughes Ln. - Lexington",37,"Lexington - Mir Station Rd. & US 27 - SW of Substation",139.662861538915,1129,"2025-01-01",1.3239522435558509E-2,1.588692337517813E-3,0,0,3.457608854379101E-2,2.3554692810852457E-2,0.15439521428463523,0.58103463903198027,0.15922927020861974,3.2381880347044929E-2,312.13403894827275,313.82793028875096,2.0317094774136422,2.0992028343667015,"Reliability Improvements Scheduled for 2026"]
["LEXINGTON WATER COMPANY","Fayette - 2300 Richmond Rd. - Lexington",39,"Lexington - St. Phillip Dr. & Richmond Rd.  - E of Substation",13.9004463929134,2051,"2024-01-01",5.0665838986683219E-2,0,0,0,9.4784138104317239E-2,1.0434679791306405E-2,4.6852599062948024E-2,0.79726274405474518,0,0,58.956138465724038,32.606874692832761,0.48600682593856659,0.62554851292052671,"Reliability Improvements Completed in 2025"]
["KENTUCKY RIVER","Fayette - 6300 Kentucky American Ave - Lexington",43,"Lexington - Old Richmond Rd - N of Substation",48.508788710334599,426,"2023-12-16",3.0607449541956312E-3,0,0,0,8.8587663031205553E-3,9.6003027177462182E-3,4.6442151004888653E-2,0.80601041202570667,0,0.12602762299434236,181.20230826619721,236.22953830751177,0.90845070422535235,1.4530516431924883,"Reliability Improvements Scheduled for 2026"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",44,"Lexington - Nicholasville Rd . - E of Substation",14.461806758574999,1648,"2024-01-01",1.3501253768348688E-2,1.0114670498408137E-2,0,0,0.37314400022539657,8.9516242639393687E-2,7.0346265460795088E-2,0.35948496886710057,0,8.3892598540557292E-2,74.630204282645636,69.629945382888337,0.6930825242718448,0.91747572815534029,"Continue to Monitor"]
["HALEY","Fayette - 5481 Winchester Rd - Lexington",45,"Lexington - Winchester & Cleaveland Rd - W of Substation",89.997481624950694,1138,"2021-01-16",2.2483938024994298E-3,1.4134914936081914E-3,0,0,4.4263014958509317E-2,2.6969417698044294E-3,5.6043995393902382E-2,0.80612550673670036,0,8.7208655844975794E-2,280.54129172390157,187.47379904745168,1.8537785588752214,2.2056239015817241,"Continue to Monitor"]
["HALEY","Fayette - 5481 Winchester Rd - Lexington",46,"Lexington - Winchester & Haley Rd - W of Substation",46.345172129678197,407,"2021-08-17",2.5800979595536461E-3,0,0,1.734201351233235E-2,2.8908751290858296E-2,2.1981010220036711E-3,1.6613629521241294E-2,0.43175689455913341,0,0.50060051213487733,271.37721537100737,672.1592137272728,1.2702702702702704,2.7272727272727284,"Tree Trim Scheduled for 2026"]
["ASHLAND AVENUE","Fayette - 448 S Ashland Ave. - Lexington",50,"Lexington - Fountaine Rd & Ridge Way Rd. - SE of Substation",4.7483748985439798,993,"2024-01-01",1.7268984690298882E-3,0,0,2.3302469464810713E-3,3.1340009252764636E-3,0,0.95319039162219721,2.9105701110118561E-2,0,1.0512760926896764E-2,364.0089660892246,468.05468276435056,1.0710976837865052,1.559919436052366,"Reliability Improvements Scheduled for 2026"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",53,"Lexington - New Circle Rd. - West of Substation",4.0634292460019203,130,"2025-01-01",0.52221031320709776,0,0,0,0,0,0.47778968679290224,0,0,0,74.012615378461547,64.596410246153852,0.52615384615384619,0.70000000000000007,"Continue to Monitor"]
["HAEFLING"," Fayette - 1555 Baunmann Dr - Lexington  ",55,"Lexington - Fairman Rd & Leestown Rd - S of Substation",17.818239406922,1364,"2024-01-01",1.1006871206925556E-2,3.4524256266256033E-3,0,0,6.602052303989441E-3,1.2386288642451377E-2,0.70589163938456756,0.18790098215556619,1.531334515198178E-2,5.7446395527892442E-2,97.656368517448669,239.63212364736069,0.63973607038123159,0.73387096774193539,"Reliability Improvements Completed in 2025"]
["HUGHES LANE","Fayette - 251 Hughes Ln. - Lexington ",63,"Lexington - US 27 & 68 - NE of Substation",25.2766726943881,237,"2025-01-01",5.1014117502003577E-3,0,0,0,0.21447506318969237,0.223321620122064,3.9285494112570124E-2,0.29748474200110969,0,0.22033166882436347,176.05441628607596,273.76905759071735,0.91729957805907136,2.0253164556962022,"Trees Trimmed in 2025"]
["PARKERS MILL","Fayette - 2085 Parkers Mill Rd - Lexington",64,"Lexington - New Circle Rd - S of Substation",17.6848317309144,1376,"2021-07-03",1.7386091127098321E-2,0,0,0,0.81813120931825967,0,1.879924631723193E-2,0,0,0.14568345323741008,5.3497747077034878,16.877519377180235,0.11540697674418603,0.50363372093023251,"Reliability Improvements Scheduled for 2026"]
["PROCTOR AND GAMBLE","Fayette - 120 Zesta Pl - Lexington",66,"Lexington - Zesta Pl - W of Substation",0.38246253006880998,5,"2023-04-07",0,0,0,0,0,4.5871559633027525E-2,0,0,0,0.95412844036697253,26.159333319999995,130.79666659999998,0.2,1,"Continue to Monitor"]
["RACE STREET","Fayette - 420 Corral St - Lexington",67,"Lexington - Eastern Ave. & Main St. - SW of Substation",2.1177953443237501,481,"2023-12-23",0,0,0,0,0,0,0,0,1,0,42.087110185446981,154.23284823284823,0.12806652806652807,0.17463617463617465,"Continue to Monitor"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",69,"Lexingotn - Lowry Ln. & Nicholasville Rd. - N of Substation",9.5871401151152291,855,"2025-01-01",0.10796374302538429,0,0,0,1.7475685331804248E-2,5.2929889949937144E-3,0.37890743885495004,0.44796771276713054,2.9737776503539686E-2,1.2654654522197472E-2,58.90998050128654,151.59228069239762,0.49380116959064324,1.6432748538011694,"Trees Trimmed in 2025"]
["JOYLAND","Fayette - 2375 Paris Pike - Lexington",71,"Lexington - Kingston Rd. & Parkside Dr. - NW of Substation",15.0880379731875,858,"2024-01-01",1.0375932379012512E-2,0,0,1.3044434823956907E-2,3.0183885367948162E-2,1.2136008459720518E-3,0.64912741389466511,0.15771133332860193,7.0999198029850316E-2,6.734420132999297E-2,95.009693078554776,160.59211343356642,0.42727272727272725,0.66666666666666663,"Continue to Monitor"]
["LOUDON AVENUE","Fayette - 811 E Loudon Ave - Lexington  ",76,"Lexington - Eastland Dr & Winchester Rd - SE of Substation",6.1885425881135303,538,"2023-09-09",1.7858219301947074E-3,0,0,0,1.9817348845620592E-3,0.11944662125504853,7.4416782205075666E-2,0.20290553981554041,0,0.59946349990957859,58.786840144237921,246.67716851858737,0.40817843866171011,1.684014869888476,"Continue to Monitor"]
["TRAFTON AVENUE","Fayette - 141 Trafton St - Lexington ",78,"Lexington - Versailles Rd - W of Substation",5.2740021728575801,543,"2023-12-30",0,0,0,0.34144486692015208,0,1.2167300380228136E-2,1.3434727503168568E-2,0.6329531051964512,0,0,9.9595088983425413,14.529373847145489,0.11233885819521179,0.19521178637200734,"Continue to Monitor"]
["PICADOME","Fayette - 1620 Harrodsburg Rd - Lexington ",80,"Lexington - Lafayette Pky - S of Substation",7.2877364582710902,857,"2024-01-01",0.11460155089919155,0,0,0,2.5771324863883848E-2,4.1148325358851677E-2,0.10661606995545289,0.54057086289391187,0,0.17129186602870813,32.425768179229877,35.359393228704782,0.18459743290548428,0.24854142357059511,"Continue to Monitor"]
["WILSON DOWNING","Fayette - 680 Wilson Downing Rd - Lexington",81,"Lexington - Tates Creek Rd & Armstrong Mill Rd - NE of Substation",18.9346792618155,2325,"2024-01-01",7.4121458492395945E-2,0,0,0,0.14058727636656282,1.5022389137657084E-2,0.18981242648727842,0.2313097129650647,0,0.34914673655104106,44.158623652129037,33.266688168172045,0.48877419354838708,0.70623655913978489,"Reliability Improvements Scheduled for 2026"]
["SPINDLETOP","Fayette - 2500 Research Park Dr - Lexington ",82,"Lexington - Berea Rd - W of Substation",5.6709293812173298,108,"2023-02-10",1.4727540500736377E-3,0,0,0,1.4247294614842799E-2,0.27793430236280975,4.1205097009668949E-2,0.65857719152205929,0,6.5633604405455591E-3,39.634012322222226,98.739351824074078,0.24259259259259264,0.57407407407407418,"Continue to Monitor"]
["PARKERS MILL","Fayette - 2085 Parkers Mill Rd - Lexington",83,"Lexington - Versailles Rd - W of Substation",29.399718247602099,302,"2023-12-09",8.6322898418259835E-3,0,0,0,2.0184324777210754E-2,2.2088506359966486E-3,1.3633940132531039E-2,0.16365805976591261,0,0.79168253484652296,98.453785852317878,180.04630240066223,0.79602649006622517,1.6357615894039736,"Continue to Monitor"]
["TRAFTON AVENUE","Fayette - 141 Trafton St - Lexington ",88,"Lexington - Dunkirk Dr - W of Substation",9.5193289799110108,1665,"2024-01-01",6.4389349862783406E-3,0,0,0,1.1480696908633594E-2,4.9643204592278766E-3,1.0199686039401572E-2,0.70642909346700589,0,0.26048726813945272,70.464764760360367,133.6172072024024,0.82078078078078076,1.4738738738738739,"Reliability Improvements Completed in 2025"]
["AMERICAN AVENUE","Fayette - 96 Burley Ave. - Lexington",90,"Lexington - Stanley Ave. & Waller Ave. - W of Substation",1.1548864747801799,222,"2019-07-20",0,0,0,0,0,0,0,1,0,0,19.752087085585586,34.744594594594595,0.14324324324324325,6.3063063063063057E-2,"Continue to Monitor"]
["LIBERTY ROAD","Fayette - 2125 Liberty Rd. - Lexington ",95,"Lexington - Liberty Rd. - SE  of Substation",18.407772729281898,1717,"2022-09-23",0.10285881966756523,0,0,0,1.6754367641158781E-2,8.7319665907365229E-3,5.2806265397406439E-2,0.70360717921171911,8.4173041151485606E-2,3.1068360339928314E-2,54.348272176587066,101.01702581013393,0.89784507862550933,2.4071054164239936,"Continue to Monitor"]
["JOYLAND","Fayette - 2375 Paris Pike - Lexington",99,"Lexington - I-64 & I-75 - NW of Substation",16.049307101410498,2271,"2024-01-01",5.5317113557733352E-3,0,0,0,1.9379221442191577E-2,2.5738866331632422E-5,1.5728592234155046E-2,0.64043661696920551,0,0.31889811913234284,83.645963594804044,116.8106634359313,0.72681638044914176,0.68428005284015847,"Reliability Improvements Scheduled for 2026"]
["DONERAIL","Fayette - 4601 Old Iron Works Rd - Lexington",104,"Lexington - Georgetown Rd - N and S on Georgetown Rd from Substation",33.858414727626702,430,"2025-01-01",1.1439291212544478E-2,0,0,0,0.14999541204897893,2.1695910606323216E-2,0.66867856815146354,0.1365476178338754,0,1.1643200146814433E-2,103.06045735116281,165.70492246976744,0.83720930232558144,1.0883720930232559,"Continue to Monitor"]
["LEXINGTON WATER COMPANY","Fayette - 2300 Richmond Rd - Lexington ",109,"Lexington - Lakeshore Dr. - SE of Substation",14.5811923424891,1117,"2024-01-01",1.0731508317299496E-2,1.5252441608417156E-3,0,0,2.4842300104727343E-3,6.0979322438442238E-3,0.2739168026498453,0.47015879587910081,0,0.23508548673859567,77.04698596866605,210.72117277170992,0.4358102059086838,0.96239928379588124,"Reliability Improvements Completed in 2025"]
["ASHLAND AVENUE","Fayette - 448 S Ashland Ave. - Lexington",111,"Lexington - Ashland Dr & Preston Ave. - E of Substation",5.3346885834827402,989,"2024-01-01",5.7729128895064132E-2,0,0,4.3546774658149344E-2,0.10900249080773336,1.2742091261839809E-2,0.17198434349424743,7.9146686547943809E-2,9.1837944998898625E-3,0.51666468983513225,58.522477244893835,47.07906975834176,0.38584428715874625,0.64610717896865533,"Continue to Monitor"]
["PICADOME","Fayette - 1620 Harrodsburg Rd - Lexington ",112,"Lexington - Della Dr - W of Substation",11.414142221237899,1605,"2024-01-01",9.6646892869900799E-3,0,0,0,6.6662728783953686E-4,7.0319334160288702E-5,4.0315480660776719E-2,0.93084515401340562,0,1.8437729416827697E-2,109.03636344174454,177.36440290280376,0.69819314641744523,1.1202492211838,"Continue to Monitor"]
["WILSON DOWNING","Fayette - 680 Wilson Downing Rd - Lexington",114,"Lexington - Wilson Downing Rd , Bellueau Wood Dr, & Spangler Dr, W of Substation",4.6410545635426699,820,"2024-01-01",0,0,0,1.332529797776885E-3,0,7.4681933842239187E-2,4.5198875050220971E-4,0,0,0.9235335476094817,77.940443087560993,364.24211381585371,0.31121951219512195,1.3292682926829269,"Continue to Monitor"]
["DONERAIL","Fayette - 4601 Old Iron Works Rd - Lexington",117,"Lexington - Lisle Rd - N of Substation",7.6990080498145002,479,"2019-07-06",0,0,0,0,0.30989810771470161,0,0.26986899563318778,0,0,0.42023289665211061,13.071322194989563,14.341858035490604,0.1081419624217119,0.11273486430062631,"Continue to Monitor"]
["FMC","Fayette - 2641 Palumbo Dr - Lexington ",123,"Lexington - Palumbo Dr - W of Substation",4.68770112815755,367,"2022-06-03",0.19169976171564734,0,0,0,4.2494042891183482E-3,7.2200158856235111E-2,0,0.6191818903891978,0,0.11266878474980142,5.4066939128065403,21.824159847411444,5.3405994550408731E-2,0.15531335149863765,"Continue to Monitor"]
["LANSDOWNE","Fayette - 3200 Montavesta Rd. - Lexington",126,"Lexington - Alumni Dr. & Shady Brook Ln - E of Substation",30.771505667816399,2513,"2024-03-01",5.0563870202661072E-3,0,0,0,2.8700500810219386E-3,2.5533016198593561E-3,3.5462307898818178E-2,0.92224984114292119,0,3.1808112237113266E-2,52.4523252367688,54.757680059689612,0.66152009550338264,0.55471547950656597,"Reliability Improvements Completed in 2025"]
["LAKESHORE","Fayette - 3710 Richmond Rd - Lexington ",134,"Lexington - Richmond Rd & Yorkshire Blvd - N of Substation",7.3853574966996502,1063,"2023-12-09",0,5.5196652896045861E-2,0,0,0,0,0,0,0.94480334710395408,0,70.699727185512714,178.52873941486359,0.5525870178739416,0.68203198494825956,"Reliability Improvements Scheduled for 2026"]
["LAKESHORE","Fayette - 3710 Richmond Rd - Lexington ",135,"Lexington - Richmond Rd & Man O War Blvd - E of Substation",28.465303186393601,2698,"2024-01-01",1.4526803881498162E-2,0,0,0,3.281718923855078E-2,3.4665732790148192E-3,2.0613255431481984E-3,0.82597536161856167,0,0.12115274643922636,114.71943167449963,83.254528040770936,1.092142327650111,1.7946627131208299,"Reliability Improvements Scheduled for 2026"]
["RACE STREET","Fayette - 420 Corral St - Lexington ",138,"Lexington - Midland Ave & Main St. - W of Substation",2.7585475933481698,51,"-",0,0,0,0,0,0,1,0,0,0,15.170196077356104,25.818627450980394,0.22352941176470589,5.8823529411764705E-2,"Continue to Monitor"]
["IBM","Fayette - 740 W New Circle Rd - Lexington ",140,"Lexington - Newtown Rd - N of Substation",27.025205945783298,992,"2023-09-30",3.7701633012050379E-3,0,0,0,7.2193458884546688E-2,3.9895907949259659E-4,6.3706511193522353E-3,0.80476574754957519,6.8929248234152708E-3,0.10560809524241298,82.619485881048391,107.69840389213709,0.99455645161290318,1.5604838709677422,"Continue to Monitor"]
["ASHLAND PIPE","Fayette - 448 S Ashland Ave. - Lexington",142,"Lexington - Tates Creek Rd - N of Substation",18.947180864513602,1799,"2024-01-01",3.3851183504305408E-3,0,0,0,2.7634407218153502E-2,6.3377653070418191E-2,0.87629516172628164,0,0,2.9307659634716127E-2,31.10495089627571,43.187085416342413,0.17998888271261809,0.22957198443579765,"Continue to Monitor"]
["AMERICAN AVENUE","Fayette - 96 Burley Ave. - Lexington",144,"Lexington - Broadway - NW of Substation",5.0654225148011101,585,"2025-01-01",6.0196642365059191E-3,0,0,0.14801685505986223,0.47648986689853523,0,8.4275299311082873E-3,0,0,0.36104608387398834,26.665150993846151,19.737065526495726,0.2088888888888889,0.21025641025641026,"Continue to Monitor"]
["SHELBY CITY","Boyle - 401 Grubbs Ln - Junction City ",153,"Junction City - Shelby St - W of Substation",10.2884041964285,591,"2024-01-01",0.11223244981701232,0,0,0,1.1201064655650439E-2,0,7.1420649883553289E-2,0.24797604524786512,0,0.55716979039591885,9.0401409986463612,13.782966715736041,0.28561759729272423,1.0558375634517767,"Continue to Monitor"]
["STANFORD","Lincoln -  746 KY Highway 78 - Hustonville ",154,"Hustonville - KY Highway 78 - SW of Substation",53.919653653695903,1118,"2025-01-01",1.366627298802092E-2,0,0,0,6.7112835798511525E-3,4.4532553474682712E-2,0.28563260409050861,0.12728005548994245,0.51994638471776988,2.2308456592242654E-3,55.449868804114487,83.370259381932016,0.88783542039355967,0.40876565295169959,"Continue to Monitor"]
["VILEY ROAD","Fayette - 308 Alexandria Rd. - Lexington ",159,"Lexington - Leestown Rd & Masterson Station - NW of Substation",12.6530434420749,1218,"2024-01-01",2.1632179921320933E-3,0,0,0.9272629359523179,0,0,7.0573846055549977E-2,0,0,0,31.532101804597705,89.950779964696224,0.18193760262725775,0.3423645320197044,"Reliability Improvements Completed in 2025"]
["LAWRENCEBURG","Anderson - 108 E Broadway st - Lawrenceburg ",160,"Lawrenceburg - US HWY 127 - S of Substation",26.910308747983201,832,"2022-05-06",7.2200242989467044E-3,0,0,0,0.2486810753001002,1.677979540532733E-3,2.2694724506081905E-2,0.60628125723487825,1.6550328117733108E-2,9.6894611001727152E-2,110.23647835384614,103.97920671634614,0.71995192307692302,1.0132211538461542,"Continue to Monitor"]
["DANVILLE CENTRAL","Boyle - 494 S 4TH ST - Danville",163,"Danville - Russel St - W of Substation",2.5633596734564099,110,"2020-10-17",5.2570934754428925E-3,0,0,0,2.3260838254356906E-2,0,0,0,0.96341639060924678,8.065677660953478E-3,79.211484839999997,126.23499999090909,0.74727272727272731,1.0272727272727271,"Continue to Monitor"]
["DANVILLE WEST","Boyle - 1353 Lebanon Rd - Danville ",168,"Danville - S Danville Bypass - S of Substation",2.2439060620779299,20,"2021-07-31",0,0,0,0,7.9782411604714415E-2,0,0,0,0,0.92021758839528556,42.521999970000003,110.29583325,0.32,1.05,"Continue to Monitor"]
["CORNING HARRODSBURG","Taylor - 620 Clem Haskins Blvd. - Campbellsville",172,"Campbellsville - Martin Luther King - SW of Substation",3.7379532584997599E-2,3,"0/0/00",0,0,0,0,0,0,0,0,0,0,1.9144444,9.572222,6.6666666666666666E-2,0.33333333333333331,"Continue to Monitor"]
["EASTLAND","Fayette - 1159 Industry Rd - Lexington",182,"Lexington - Eastland Pky - E of Substation",17.950889495352499,2389,"2024-01-01",1.0578631396820604E-2,1.2866216890973909E-3,0,0,0.15430635066247081,0,0.43757446264965105,0.2634764332245666,0,0.13277750037739355,106.52163666395981,159.18762382754292,0.94709083298451235,0.81707827542904954,"Continue to Monitor"]
["ASHLAND AVENUE","Fayette - 448 S Ashland Ave. - Lexington",187,"Lexington - High St. - NW of Substation",3.8337813784244101,1045,"2025-01-01",0,0,0,0,0,5.0352373887240356E-2,0.15343100890207714,1.9380563798219585E-3,2.9553041543026706E-2,0.76472551928783383,31.414995213014361,103.19566187942586,0.28956937799043059,0.97703349282296648,"Reliability Improvements Scheduled for 2026"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",188,"Lexington - Regency Rd. - N of Substation",6.5974849211442299,743,"2024-01-01",0,0,0,0,0,7.3446327683615822E-2,0.77536723163841803,0.14526553672316384,0,5.9209039548022598E-3,21.411982949663525,29.778196500672948,0.15370121130551814,0.12113055181695825,"Continue to Monitor"]
["VILEY ROAD","Fayette - 308 Alexandria Rd. - Lexington ",189,"Lexington - Leestown Rd and Masterson Station Dr - N of Substation",12.933406385886,1409,"-",2.2467725918570009E-2,0,0,0,6.0824230387288977E-3,0,2.6688182720953327E-3,0,0,0.96878103277060579,4.7488786357700494,11.43520226969482,3.5628105039034783E-2,5.0390347764371894E-2,"Reliability Improvements Scheduled for 2026"]
["LONDON","Laurel - Near corner of Foster Heights & Substation Rd - London",200,"London - Main St - W of Substation",10.704064700737201,508,"2024-01-01",1.2147922140294375E-3,0,0,0,0,0,2.1984913975760658E-2,0.93549735853320903,4.0167245811791957E-2,1.1356894652089159E-3,101.64042650039369,257.61594487204724,0.71496062992125986,1.3799212598425197,"Continue to Monitor"]
["LONDON","Laurel - Near corner of Foster Heights & Substation Rd - London",201,"London - Waterworks Rd & Daniel Boone PKWY - W & SW of Substation",25.221381582024499,591,"2024-01-01",1.7084144459971406E-3,0,0,0,7.1809949999596129E-3,5.533162626515562E-4,2.3556329211059865E-2,0.96599528267595058,0,1.0056624043812954E-3,85.569289326565155,152.93965029610828,0.93062605752961058,0.80372250423011837,"Continue to Monitor"]
["LONDON","Laurel - Near corner of Foster Heights & Substation Rd - London",203,"London - Locus St - SW of Substation",1.72326078624884,97,"2023-02-10",0.24656516895655403,0,0,0,0.19717786854808764,0,0,0,0.55625696249535839,0,53.988213053608249,233.46168384536082,0.46597938144329898,1.195876288659794,"Continue to Monitor"]
["LONDON","Laurel - Near corner of Foster Heights & Substation Rd - London",205,"London - S & N on McWhorter Rd",40.9002259919843,1895,"2023-05-05",5.0769043754335028E-4,0,0,0,0.26898297449391839,1.8341210877446388E-3,3.1087101087601626E-2,0.31898333202239559,0.35175439223734173,2.6850388633454656E-2,55.288211072401054,79.895919072823247,0.98881266490765152,1.6248021108179411,"Reliability Improvements Scheduled for 2026"]
["CAMPBELLSVILLE INDUSTRIAL","Taylor - 620 Clem Haskins Blvd. - Campbellsville",208,"Campbellsville - Industrial Rd - SE of Substation",1.8340845904868199,14,"2023-02-18",0,0,0,0,0,0,5.5274688237276708E-2,0.94472531176272334,0,0,87.392857114285718,423.94166657142858,0.32857142857142857,1.2857142857142856,"Continue to Monitor"]
["CARON","Laurel - 1136 South Laurel Rd - London ",210,"London - S Laurel Rd - N of Substation",15.078192976528801,743,"2023-12-16",0,8.1408748259470878E-2,0,0,6.4399577471551353E-2,2.136649541460604E-2,0.15395880347625679,0.54646612570221342,0.11198204254093244,2.041820713496903E-2,25.616527584925979,48.291341405114395,0.32786002691790034,1.1009421265141317,"Continue to Monitor"]
["CARON","Laurel - 1136 South Laurel Rd - London ",212,"London - S Laurel Rd - NW of Substation",17.037659991139101,726,"2023-12-23",1.2399170633253197E-2,0,0,0,0.56385917297531873,2.504632467917146E-2,2.8414766034538578E-2,0.36734953950857957,0,2.9310261691384643E-3,100.48415517713502,343.98014231129491,0.9650137741046827,3.4545454545454528,"Continue to Monitor"]
["CARON","Laurel - 1136 South Laurel Rd - London ",213,"London - S Laurel Rd - S of Substation",3.5079467366700201,164,"2023-12-16",4.8524205191490894E-4,0,0,0,0,0.88567906929376317,5.3616251415289319E-4,0.11140498541278523,0,1.8945407273838265E-3,85.063536573170737,310.74806908536584,0.35,0.60365853658536595,"Continue to Monitor"]
["FARISTON","Laurel - 57 Rocky Branch Rd - North Corbin ",216,"North Corbin - S Laurel Rd - S of Substation",3.1667533595993,95,"2025-01-01",0,0,0,0,0,0,9.3621019428878228E-3,0.98815475990738566,0,2.4831381497265191E-3,107.39252630105264,313.69228068421052,0.4757894736842106,1.0631578947368423,"Trees Trimmed in 2025"]
["FARISTON","Laurel - 57 Rocky Branch Rd - North Corbin ",217,"North Corbin - S Laurel Rd - N of Substation",29.495929206565499,879,"2024-02-01",4.2286144523192676E-4,0,0,0,4.3263889070436816E-2,7.9164629698859915E-2,1.1962338534899468E-2,0.85175079016922295,1.2862307947703738E-3,1.2149260286578496E-2,107.01114143913537,162.75919604209335,0.53788395904436859,0.5551763367463024,"Continue to Monitor"]
["LEBANON WEST","Marion - 2255 Saint Mary's Rd - St Mary ",218,"St Mary - Sait Mary's Rd - E of Substation",7.2621865189286403,143,"2025-01-01",0,0,0,0,0.59171597633136097,0,2.1038790269559501E-2,6.0924830155599387E-2,0,0.32632040324348016,27.004405586013984,29.959906748251747,0.39160839160839161,0.36363636363636365,"Continue to Monitor"]
["LEBANON WEST","Marion - 2255 Saint Mary's Rd - St Mary ",219,"St Mary - Sait Mary's Rd - W of Substation",41.417049867933002,841,"2025-01-01",8.5735063344432965E-4,0,0,0,1.3118995674972251E-2,0,6.1805794771692124E-3,0.11884104566157615,9.127722279634095E-3,0.85187430627320393,44.978489883234239,27.311137524375738,0.4273483947681333,0.45184304399524372,"Continue to Monitor"]
["EAST BERNSTADT","Laurel - 440 State HWY 490 - East Bernstadt ",221,"East Bernstadt - US HWY 25 - N & S of Substation",30.069864049845201,797,"2019-05-11",8.1988398139107466E-2,0,0,0,0.10174602262937224,1.8379185572339326E-3,7.1362931480098785E-2,0.7263894472842839,0,1.6675281909903701E-2,98.985696350062724,123.87310747678794,0.9304893350062734,0.87452948557089083,"Tree Trim Scheduled for 2026"]
["WILLIAMSBURG SOUTH"," Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg ",225,"Williamsburg - I75 - NW of Substation",15.5567082019137,636,"2024-01-01",3.0347271206181002E-3,0,0,2.5294860648611407E-2,2.5770574629681273E-2,0,3.5580124997949505E-2,0.64560948803333285,0,0.26471022456980692,54.144030389622642,92.343160366352194,0.27798742138364785,0.28616352201257861,"Continue to Monitor"]
["WILLIAMSBURG SOUTH"," Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg ",226,"Williamsburg - Highway 25 - N of Substation ",31.039175485547801,1303,"2024-01-01",2.6686147957181413E-3,0,0,0,0.40532756944737941,2.3244721636911411E-3,0.20671500763755141,0.34947986161843636,0,3.3484474337223555E-2,72.235745706062929,83.373458676131989,0.59953952417498113,0.42747505755947834,"Reliability Improvements Scheduled for 2026"]
["WILLIAMSBURG SOUTH"," Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg ",227,"Williamsburg - Savoy Clear Creek Rd - N of Substation",10.816530642945599,188,"2023-10-07",0,0,0,0,0.20954307817960954,0,3.1343153635349768E-3,0.78281599164182558,0,4.5066148150297884E-3,608.42744678936174,1219.0862588351065,2.4851063829787234,4.2021276595744688,"Reliability Improvements Scheduled for 2026"]
["WILLIAMSBURG SOUTH"," Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg ",230,"Williamsburg - Highway 92 - N of Substation",24.517044074948899,663,"2023-11-17",3.9723103961550189E-2,0,0,0,0.20201395240400996,5.469772780258604E-4,0.26363408116784137,0.44071124979824611,0,5.3370635390326569E-2,92.078632470286578,134.41525891402716,0.54962292609351426,0.44494720965309187,"Continue to Monitor"]
["PICADOME","Fayette - 1620 Harrodsburg Rd - Lexington ",232,"Lexington - Harrodsburg Rd - SW of Substation",10.8718701488154,1072,"2024-01-01",2.9826906717130505E-2,0,0,0,8.9411274501293423E-4,9.2189100505217104E-3,2.8581225368495982E-2,0.31933280091668259,1.6146113647806386E-3,0.61053143283737565,82.491138052238796,188.79830534048503,0.51604477611940291,0.97947761194029836,"Continue to Monitor"]
["WILLIAMSBURG","Whitley -  Corner of 2nd and 3rd St - Williamsburg ",235,"Williamsburg - 5th St - W of Substation",3.3258950866362298,286,"2023-09-30",0,0,0,0,2.8917197452229298E-2,0,4.8280254777070063E-2,0.92280254777070059,0,0,4.9231934713286716,11.869930066433568,5.454545454545455E-2,0.10139860139860139,"Continue to Monitor"]
["MANCHESTER","Clay - 1195 HWY 687 (Town Branch Rd) - Manchester ",250,"Manchester - Town Branch Rd - NE of Substation",24.217931019481,1072,"2025-01-01",1.4805922368947579E-3,0,0,0,4.4977991196478592E-2,2.5152918310181215E-4,4.1387983764934544E-3,0.9167809981135312,2.0945521065569083E-2,1.1424569827931172E-2,91.721337052985078,166.62313431529853,0.94197761194029861,1.5998134328358211,"Reliability Improvements Scheduled for 2026"]
["MANCHESTER","Clay - 1195 HWY 687 (Town Branch Rd) - Manchester ",251,"Manchester - Town Branch Rd - NW of Substation",3.7961000040145398,65,"2025-01-01",0,0,0,0,3.7921084532773305E-2,0,8.2603425020061808E-2,0.87947549044716489,0,0,288.82999997538457,376.11999995384616,1.1723076923076923,1.7846153846153849,"Trees Trimmed in 2025"]
["MANCHESTER SOUTH","Clay - 530 Muddy Gap Rd - Manchester ",253,"Manchester - US HWY 421 - E of Substation",17.164201119368599,581,"2025-01-01",1.9179847958938042E-3,0,0,0,2.5958798269931121E-2,0,6.7579844852889787E-2,0.57009962649769763,0.19522289778771712,0.13922084779587052,70.659661491222025,208.31296614285714,0.76282271944922542,2.3201376936316698,"Trees Trimmed in 2025"]
["MANCHESTER SOUTH","Clay - 530 Muddy Gap Rd - Manchester ",254,"Manchester - State HWY 80 - S of Substation",20.8013832020997,412,"2025-01-01",1.2130391657507438E-3,0,0,0,7.5306722426257047E-3,2.7254286965302165E-4,1.7949852111983845E-2,0.83184775129792954,0,0.14118614231205712,361.3802427033981,956.37063104854371,1.3859223300970878,4.0072815533980588,"Trees Trimmed in 2025"]
["CORBIN EAST","Knox - Corner of State HWY 1232 and E Barbourville Rd - Corbin ",275,"Corbin - Barbourville Rd - E of Substation",30.284815012687101,870,"2022-10-14",4.6056961099736768E-2,0,0,8.0707078093009647E-3,5.4968558057911669E-2,4.0600321731500438E-2,2.0574363849078677E-2,0.71708650190114065,4.7939821585258849E-2,6.4702763966071955E-2,96.973704966666673,118.43390803333337,0.66735632183908056,0.56206896551724161,"Continue to Monitor"]
["CORBIN EAST","Knox - Corner of State HWY 1232 and E Barbourville Rd - Corbin ",277,"Corbin - State HWY 1232 & Hancock - NW of Substation",14.5732857555286,747,"2024-01-01",2.5678034681015397E-3,0,0,2.780343123429686E-2,2.5303832165563415E-2,1.9723974952395173E-4,2.4350813936555161E-3,0.93313388154923527,0,8.5587304396234371E-3,145.54144130414994,167.61561800669344,1.1081659973226241,1.5073627844712185,"Continue to Monitor"]
["CORBIN EAST","Knox - Corner of State HWY 1232 and E Barbourville Rd - Corbin ",278,"Corbin - Commonwealth Ave - N of Substation",17.773652951988499,759,"2024-01-01",0,0,0,0,6.7677325475938077E-2,5.0868841423843862E-3,4.377461314286406E-3,0.91717891563108389,0,5.6794134363071314E-3,117.84101887193674,311.94378567193661,0.74967061923583656,1.3359683794466404,"Continue to Monitor"]
["CORBIN EAST","Knox - Corner of State HWY 1232 and E Barbourville Rd - Corbin ",279,"Corbin - Pennington Rd - S of Substation",9.2370964367304893,399,"2024-01-01",1.5934654525977504E-2,0,0,0,0.97596411355115154,0,0,8.1012319228709155E-3,0,0,23.327786123308272,36.860609854636593,0.11929824561403508,0.13283208020050125,"Continue to Monitor"]
["HOPEWELL","Laurel - Corner of American Greeting Rd and Hopewell Church Rd - North Corbin",285,"North Corbin - American Greeting Rd and I75 - S of Substation",22.127362219626999,1167,"2024-01-01",4.1429261226460651E-3,0,0,0,1.78786415580235E-2,3.9916304522774823E-3,0.74912924513117662,8.1686785771768869E-2,7.5548044422984059E-2,6.7622726541123446E-2,95.65139387694947,244.69934303170524,0.69528706083976011,0.71893744644387303,"Reliability Improvements Scheduled for 2026"]
["CORBIN US STEEL","Whitley  - S Woodbine Ave off HWY 830 - Corbin",288,"Corbin - 0.15 miles E of Substation",20.795143683872499,400,"2022-01-01",3.3749252695118893E-3,0,0,0,0.21850551880636929,2.4074466922518146E-3,8.2701740175753248E-3,0.1287775056409465,0.11992877300574059,0.51873565656760456,292.73926664900006,513.30362498250008,1.6539999999999995,1.902499999999999,"Continue to Monitor"]
["CORBIN US STEEL","Whitley  - S Woodbine Ave off HWY 830 - Corbin",289,"Corbin - S Main St - S of Substation",0.79373234248720903,5,"2022-01-01",0,0,0,0,1,0,0,0,0,0,19.533333280000001,23.143333200000001,0.2,0.2,"Continue to Monitor"]
["HUME ROAD","Fayette - 2319 Hume Rd. - Lexington",293,"Lexington - Winchester Rd, Man O War Blvd, and Blackford Pkwy - SE of Sub",27.239914457032999,1747,"-",0.1357150757659551,0,0,0,0,8.5167569959075318E-2,0.15086826678464771,0,0,0.62824908749032182,5.5140583851173437,5.1753863755008593,4.1442472810532337E-2,6.1247853463079566E-2,"Reliability Improvements Scheduled for 2026"]
["WHITE SULPHUR","Scott Ky - 4283 Frankfort Rd - Georgetown",296,"Georgetown - Frankfort Pike - E of Substation",60.379475251180402,1112,"2023-11-04",4.6517066000785028E-3,0,0,0,7.7208307931285027E-3,2.185550479785537E-2,1.9208124201401357E-4,0.34932061699835476,0.47445319481213621,0.14180606475643262,64.678642079316546,162.45071941366908,0.7526978417266188,1.3624100719424466,"Continue to Monitor"]
["WHITE SULPHUR","Scott Ky - 4283 Frankfort Rd - Georgetown",298,"Georgetown - Frankfort Pike - W and S of Substation",54.416734619167599,574,"2023-09-02",3.3921088005060489E-2,0,0,0,0.70862655175140343,9.9971007617089686E-2,4.1683139611502072E-2,3.2076118183495428E-2,0,8.3722094831448823E-2,55.905017412891979,54.396428564459931,0.83832752613240447,0.96341463414634143,"Continue to Monitor"]
["PINEVILLE","Bell - Corner of E Park Ave and Maple St - Pineville  ",300,"Pineville - Park Ave - W of Substation",9.1655248348114498,322,"2024-03-01",3.9136415104376442E-3,0,0,0,3.4850407702654435E-2,1.195370504061828E-2,0.13168833734829891,0.80536662841683704,0,1.2227279981153727E-2,159.79425463043478,414.06884054037272,1.0739130434782607,2.1086956521739126,"Continue to Monitor"]
["PINEVILLE","Bell - Corner of E Park Ave and Maple St - Pineville  ",301,"Pineville - US HWY 25E  & KY HWY 66 - N of Substation",25.275556349058999,1141,"2022-09-09",9.966704002148349E-3,0,0,0,1.5320578082429266E-2,4.9420506867405782E-2,5.1291813331656354E-2,0.85945995557134347,0,1.4540442145016904E-2,129.69220273444347,61.503739400525852,1.1512708150744959,1.5801928133216483,"Continue to Monitor"]
["PINEVILLE","Bell - Corner of E Park Ave and Maple St - Pineville  ",302,"Pineville - US HWY 25E - S of Substation",33.6913701027363,631,"2024-01-01",3.0528363927057722E-3,0,0,0,6.5718939953845465E-2,1.0859892306067966E-3,1.5942925232658109E-3,0.89415828293036104,0,3.4389658969215219E-2,291.50903325610147,426.66629685736939,2.4954041204437387,5.1933438985736897,"Continue to Monitor"]
["PINEVILLE","Bell - Corner of E Park Ave and Maple St - Pineville  ",303,"Pineville - US HWY 25E - S of Substation",25.9385490798423,537,"2024-01-01",2.6477317037921734E-3,0,0,0,3.3959681399616609E-2,0,1.734250631938025E-3,0.87802982583869837,0,8.3628510425954858E-2,90.934109218994436,155.90775912104286,0.92811918063314758,2.1210428305400391,"Continue to Monitor"]
["CROCKETT","Bell - On HWY 66 across the street from Chaz Coal Co - Pineville ",304,"Pineville - State HWY 66 - NW of Substation",21.435347687830198,131,"2025-01-01",0,0,0,0,0.1449599037500533,2.2807258534367201E-3,3.3109602732134314E-3,0.78345419838288721,0,6.5994211740409342E-2,1562.9133332900765,3005.7782442137409,6.1236641221374057,11.160305343511455,"Reliability Improvements Scheduled for 2026"]
["CROCKETT","Bell - On HWY 66 across the street from Chaz Coal Co - Pineville ",305,"Pineville - State HWY 66 - SW of Substation",1.80148786760683,11,"2025-01-01",0,0,0,0,0,0,3.8869257950530034E-2,0.96113074204946991,0,0,260.77757572727273,257.19848481818178,1.290909090909091,1.7272727272727275,"Trees Trimmed in 2025"]
["CROCKETT","Bell - On HWY 66 across the street from Chaz Coal Co - Pineville ",306,"Pineville - 0.05 Miles S of Substation",8.6742941579285499E-2,2,"2025-01-01",0,0,0,0,1,0,0,0,0,0,222.55333330000002,266,0.4,1,"Continue to Monitor"]
["CALLOWAY","Bell - Hwy 119 - Calloway",311,"Calloway - US HWY 119 - S of Substation",68.302106276025597,917,"2025-01-01",1.7148530677624414E-3,0,0,0,0.20894790630096566,5.2161979737421523E-4,0.13126461458901173,0.62548370162004363,0,3.2067304624842308E-2,733.97244271210479,943.76417661941116,6.2067611777535481,7.9901853871319641,"Reliability Improvements Scheduled for 2026"]
["STINKING CREEK","Knox -  Croner of New US HWY 25 E and HWY 930 - Barbourville ",313,"Barbourville - US HWY 25E - S of Substation",37.220099381601301,844,"2025-01-01",2.4178767603778763E-3,0,0,0,0.37977717823800006,7.2568189947511005E-2,2.7501961752073357E-2,0.40442732089827449,0,0.11330747240376324,221.16079381066348,322.83621639218018,2.5734597156398116,5.2784360189573469,"Trees Trimmed in 2025"]
["STINKING CREEK","Knox -  Croner of New US HWY 25 E and HWY 930 - Barbourville ",314,"Barbourville - US HWY 25E & Stinking Creek Rd - NW of Substation",27.2253131339804,407,"2020-08-22",1.905806001702566E-2,0,0,0,0.31516948699987118,2.8538400404595043E-2,1.1321122185818442E-2,0.53542562581869235,0,9.0487304573997229E-2,320.258624054054,593.90405402211309,2.2029484029484023,3.4054054054054053,"Tree Trim Scheduled for 2026"]
["MILL CREEK KU"," Bell - 5539 HWY 221 Kettle Island - Pineville ",316,"Pineville - State HWY 221 - NE of Substation",30.796657060226199,339,"2022-11-18",1.3256345881019643E-3,0,0,0,6.9187371520984739E-2,0,8.4584172626162772E-4,0.92264787753700817,0,5.9932746276435142E-3,387.28412977168136,794.33923300884942,1.9569321533923301,4.2241887905604711,"Continue to Monitor"]
["STRAIGHT CREEK","Bell - 3582 HWY 66 Arjay - Pineville",317,"Pineville - State HWY 66 - NE of Substation",8.0913278795745107,222,"2023-06-09",4.1739436078250459E-4,0,0,0,4.2906492679122596E-2,1.1780406629979898E-3,2.6196988170165089E-3,0.91966531562702514,0,3.3213057853055214E-2,203.1247146981982,398.809008981982,1.3018018018018018,3.1801801801801797,"Continue to Monitor"]
["CALLOWAY","Bell - Hwy 119 - Calloway",318,"Tejay - State HWY 2012 - S of Substation",3.8905063363852501,7,"2019-09-28",0,0,0,0,0,0,0,1,0,0,175.4919046857143,302.7714285714286,1.0571428571428569,1.7142857142857142,"Continue to Monitor"]
["DEER BRANCH"," Bell - HWY 66 0.5 miles S of Buffalo Hollow Rd, 7.5 miles N of HWY 221 - Pineville ",319,"Pineville - State HWY 66 - S of Substation",13.715218966411401,232,"2023-07-01",2.5841708517547322E-4,0,0,0,2.4459477596841302E-2,0,7.5822377316989622E-3,0.96769986758628423,0,0,357.39943963017237,377.03929595258626,2.544827586206897,2.6939655172413794,"Continue to Monitor"]
["DEER BRANCH","Bell - Hwy 66 0.5 miles S of Buffalo Hollow Rd - Pineville",320,"Pineville - Hwy 66 & Buffalo Hollow Rd - N of Substation",2.5122950191128299,28,"2023-07-01",0,0,0,0,0,0,0,1,0,0,529.82011904285707,2571.0333333214285,0.42857142857142855,1,"Continue to Monitor"]
["PUCKETT CREEK"," Harlan - 5627 E HWY 72 Pathfork - Alva",322,"Alva - E Highway 72 - NW of Substation",10.4660739062601,298,"2022-12-31",1.8849693494479732E-3,0,0,0,6.1681265939079057E-2,0,2.676973277787458E-3,0.52048914162614246,0,0.41326764980754305,137.2264093785235,203.19244964429529,1.288590604026846,2.5268456375838926,"Continue to Monitor"]
["CHUNKLICK BRANCH","Harlan - Off HWY 72 between Alva and Liggett - Alva",325,"Alva - 0.12 miles N of Substation",0.13741257926658301,4,"2023-10-07",0,0,0,0,0,0,1,0,0,0,80.127500000000012,400.63750000000005,0.3,1.5,"Continue to Monitor"]
["WACO","Madison - 3761 New Irvine Rd - Madison East ",331,"Madison East - Irvine Rd - E & W of Substation",45.492692597298102,1112,"2025-01-01",7.3794958726415092E-3,0,0,0.41467054834905659,0.10254827535377359,0,6.9704451650943397E-2,0.23590433372641512,0.15949292452830188,1.0299970518867925E-2,31.788483205215822,90.230560543165439,0.64568345323741083,1.6034172661870518,"Reliability Improvements Scheduled for 2026"]
["BEAR TRACK","Lee Ky - 584 New Yellow Rock Rd - Beattyville ",333,"Beattyville - New Yellow Rock Rd - S of Substation",10.9354483618724,78,"2020-10-31",3.142366667636533E-3,0,0,0,0,5.0801594460123953E-3,0,0.99177747388635107,0,0,187.17132477179487,135.82628202564101,0.82820512820512826,1.0897435897435896,"Continue to Monitor"]
["OKONITE","Madison - 1742 Berea Rd - Richmond",334,"Richmond - Battlefield Memorial Rd & Berea Rd - S of Substation",28.928969198756,1275,"2025-01-01",2.8090087399284592E-4,0,0,0,1.0546227750161785E-2,0.1226256764733073,1.0773793015168648E-2,0.53102354589351364,0.32149638384571078,3.2534721481449875E-3,37.925801304156863,83.311045746666665,0.46509803921568621,0.90901960784313707,"Trees Trimmed in 2025"]
["OKONITE","Madison - 1742 Berea Rd - Richmond",335,"Richmond - Industry Rd - N of Substation",0.187017107193334,1,"2025-01-01",0,0,0,0,0,0,1,0,0,0,12.183333200000002,18.066666000000001,0.4,1,"Continue to Monitor"]
["DARK HOLLOW","Estill - 37 Dark Hollow Rd - Red Lick",336,"Red Lick - Wisemantown Rd - S of Substation",12.289239097966901,546,"2023-07-14",0.60309831034865236,0,0,0,0.22239065330720598,0,0.13199245757385292,7.505453469885754E-3,0,3.5013125300403E-2,120.53123320402933,59.292765560439562,0.83589743589743581,1.6282051282051282,"Continue to Monitor"]
["DARK HOLLOW","Estill - 37 Dark Hollow Rd - Red Lick",337,"Red Lick - Richmond Rd - E of Substation",17.1710156906076,541,"2023-07-28",4.2863912462844092E-3,0,0,0,0.49416275362943179,0,5.6003101710248567E-4,0.22455089820359281,0,0.27643992590358851,78.925871833641395,106.52064078188539,0.68465804066543434,0.34565619223659882,"Reliability Improvements Scheduled for 2026"]
["RICHMOND INDUSTRIAL","Madison - 110 Mikron Way - Richmond",344,"Richmond - 1.51 miles S of Substation",5.1002694570632503,9,"-",0,0,0,0,0.16236162361623616,0,0.83763837638376382,0,0,0,21.71851848888889,90.353703666666661,0.2,0.55555555555555558,"Continue to Monitor"]
["MIDDLESBORO 2","Bell - Intersection of Cumberland Ace and S 38th St - Middlesborough",360,"Middlesborough - State HWY 74 - E of Substation",30.0585804234995,399,"2021-12-31",2.6970552696053886E-3,0,0,0,4.2909214716308507E-2,5.8170274979471671E-2,7.0597424445735116E-3,0.88916371259004101,0,0,232.12101083859648,230.50250623809521,0.92481203007518764,1.3458646616541348,"Continue to Monitor"]
["MIDDLESBORO 2","Bell - Intersection of Cumberland Ace and S 38th St - Middlesborough",361,"Middlesborough - Glenboro Rd - SW of Substation",7.4929600157169798,144,"2020-11-28",1.0414568888633159E-2,0,0,0,2.0066745303374666E-2,0,1.7060329698783048E-2,0.95245835610920904,0,0,141.91824072222224,408.04120368055561,0.77083333333333348,2.2222222222222232,"Tree Trim Scheduled for 2026"]
["MIDDLESBORO 1","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",364,"Middlesborough - Nutwood Rd - N of Substation",26.081445340934099,1492,"2024-01-01",4.312852237116175E-2,0,0,0,9.695942353522527E-2,3.4152535481732148E-3,0.14780041408385511,0.57732797067635788,0,0.13136841578522684,47.813699723190354,54.361662184986592,0.47372654155495963,0.74329758713136751,"Continue to Monitor"]
["MIDDLESBORO 1","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",365,"Middlesborough - N 12th St - NE of Substation",16.067493091355399,483,"2021-12-31",6.8996550172491374E-4,0,0,0,1.4659267036648167E-2,0,4.0247987600619973E-3,0.97343132843357838,0,7.1946402679866003E-3,96.628109028157354,122.95489991925467,0.8231884057971014,0.44306418219461707,"Continue to Monitor"]
["MIDDLESBORO 1","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",366,"Middlesborough - Asbury Rd & N 12th St - E of Substation",10.8040698279886,447,"2021-12-31",2.2351626374919123E-3,0,0,9.6857047624649528E-2,9.971962433582339E-2,1.1509126914103092E-2,0.24700507813265887,0.50759759229849222,0,3.5076368056780972E-2,82.907076791051438,110.82636089932883,0.88814317673378063,1.2281879194630871,"Continue to Monitor"]
["MIDDLESBORO 1","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",370,"Middlesborough - N 19th St - SW of Substation",4.8443522526860097,695,"2021-12-31",1.1389122511914775E-3,0,0,0,5.1321138211382115E-2,0,0.69635723296888141,0.24878223997757218,0,2.4004765909728062E-3,66.306978408920855,123.3743405179856,0.60086330935251797,1.2201438848920863,"Reliability Improvements Scheduled for 2026"]
["MELDRUM","Bell - HWY 25/Wilderness Rd S of HWY 2486 Middlesborough",390,"Middlesborough - S of Substation on US HWY 25E and E of Substation Colmar Rd",13.751679709392301,369,"2022-02-04",7.6590630114566289E-3,0,0,0,0.13239054828150573,0.15255472585924715,7.927577741407529E-3,0.41783449263502459,0,0.28163359247135844,162.23487803035226,203.32737125203252,1.7962059620596205,2.617886178861788,"Continue to Monitor"]
["HOOVER 1","Scott Ky - 3 Quality Dr - Georgetown",397,"Georgetown - Quality Dr - SW of Substation",20.136272226761498,1608,"2019-01-12",1.6063130908508253E-2,0,0,0.37321743310366928,0.1702852107034129,0,0,3.7253645249158793E-2,0,0.40318058003525076,5.6451057207711433,9.2650704800995012,7.5995024875621889E-2,5.4104477611940288E-2,"Continue to Monitor"]
["HOOVER 1","Scott Ky - 3 Quality Dr - Georgetown",400,"Georgetown - Quality Dr - SW of Substation",19.570183067323001,1269,"2019-01-12",4.701366562300812E-2,0.2076600334811266,0,0,4.6033046852563965E-2,5.7240118514782827E-2,0.60860703103658409,1.6460386503883951E-3,0,3.1800065841546016E-2,27.595224584869975,100.88391121276595,0.19653270291568165,0.76201733648542169,"Continue to Monitor"]
["DELAPLAIN","Scott Ky -  413 Triport Cir - Sadieville ",401,"Sadieville - I75 - N of Substation",10.7315577544954,109,"2025-01-01",7.2049634192443684E-3,0,0,0,0.12017167381974249,0,0.54181769663545998,0.33080566612555318,0,0,182.728256856028,364.9541284036697,0.81467889908256874,1.4495412844036693,"Trees Trimmed in 2025"]
["DELAPLAIN","Scott Ky -  413 Triport Cir - Sadieville ",402,"Sadieville - Triport Rd & Cincinnati Rd - S of Substation",27.241879166893298,723,"2025-01-01",1.0027851569786514E-2,2.4635453182990604E-3,0,0,0.89821634173168574,1.0909067519151975E-2,6.0360076414930498E-2,0,0,1.8023117446146129E-2,56.468169653941914,213.37100044813278,0.29183955739972334,1.0304287690179805,"Continue to Monitor"]
["TRAFTON AVENUE","Fayette - 141 Trafton St - Lexington ",404,"Lexington - Old Frankfort Rd - N of Substation",5.47739860794265,159,"2019-12-31",4.1385135135135136E-2,0,0,0,0.12820945945945947,0,0.69949324324324325,0,0,0.13091216216216217,23.885492647798742,34.801991597484275,0.31320754716981131,0.20754716981132074,"Continue to Monitor"]
["FORKS OF ELKHORN","Franklin - 3286 Georgetown Rd - Frankfort ",405,"Frankfort - Switzer Rd - N of Substation",55.741320097255901,701,"2018-01-27",1.6418207408826629E-2,0,0,0,2.2814528787130719E-2,3.6601991112945181E-2,6.8237253413704927E-3,0.88880127926427566,1.6359255138058849E-3,2.690434257164543E-2,181.50230620970038,339.02130287018531,1.328102710413694,0.99714693295292434,"Continue to Monitor"]
["FORKS OF ELKHORN","Franklin - 3286 Georgetown Rd - Frankfort ",406,"Frankfort - Steadmantown Ln - N of Substation",22.879897987835999,802,"2017-12-23",9.3199710532663755E-3,0,0,0,2.4253854082147322E-2,4.2323633253656722E-3,0.43551676498322406,0.52667704655599656,0,0,30.920839560598505,26.911367405236906,0.36109725685785526,0.45386533665835399,"Continue to Monitor"]
["FORKS OF ELKHORN","Franklin - 3286 Georgetown Rd - Frankfort ",407,"Frankfort - Old Grand Dad Rd - N of Substation",0.11530564764507099,3,"2017-12-23",0,0,0,0,2.2708840227088401E-2,0,0.97729115977291159,0,0,0,513.87999993333335,411,1.6666666666666665,2,"Continue to Monitor"]
["HARLAN Y","Harlan - Sunshine Pike Rd just W of US HWY 421 - Harlan",413,"Harlan - US HWY 421 Bypass - NW of Substation",12.58329786857,647,"2023-11-18",3.7178608777180773E-2,0,0,0,0.25686055317154088,4.4426814756049184E-2,0.11131946197396415,0.45155241426562331,0,9.8662147055641705E-2,73.767434298299861,84.627434292117485,0.7103554868624421,1.4837712519319937,"Continue to Monitor"]
["DAYHOIT","Harlan - Dayhoit Dr (Keith Tremont Rd) - Harlan",414,"Harlan - US HWY 119 - N of Substation",15.2006115141041,577,"2024-01-01",6.2352090920685306E-4,0,0,0,3.2005044850992675E-2,3.4293650006376919E-3,8.1135658310541758E-2,0.85018493063329881,0,3.2621480295322178E-2,154.32259963778159,152.30742344020788,1.4294627383015595,1.7175043327556323,"Tree Trim Scheduled for 2026"]
["DAYHOIT","Harlan - Dayhoit Dr (Keith Tremont Rd) - Harlan",415,"Harlan - S US HWY 119 - S of Substation",14.100062892761001,401,"2024-01-01",5.1312454002780273E-3,0,0,0,0.52663750102216045,4.5056832120369615E-2,5.2130182353422195E-3,0.41309591953553032,0,4.8654836863194044E-3,124.47255193566085,129.19854528927684,1.5745635910224436,2.3266832917705731,"Continue to Monitor"]
["CAWOOD","Bell - Off Slack Hollow Rd just N of S Old US HWY 421 - Cawood ",418,"Cawood - US HWY 421 Bypass - W of Substation",31.7643418346311,704,"2021-01-09",1.1147743924005862E-3,0,0,0,4.5244681926128037E-2,3.7264413117073415E-4,0.12707164872922036,0.82415302410186453,1.5158405335758679E-4,1.8916426658582184E-3,198.23062024573863,227.19543085227278,1.6380681818181819,2.6519886363636376,"Tree Trim Scheduled for 2026"]
["CAWOOD","Bell - Off Slack Hollow Rd just N of S Old US HWY 421 - Cawood ",419,"Cawood - US HWY 421 Bypass - E of Substation",21.210717764388601,311,"2020-12-19",7.4238540995664472E-4,0,0,0,1.728958513219029E-2,5.0043629419477452E-2,0.1481984019297452,0.78372599810863042,0,0,996.14513394790993,1350.8534833601288,3.8790996784565919,6.2990353697749191,"Tree Trim Scheduled for 2026"]
["GEORGETOWN","Scott Ky - 207 W Clinton St - Georgetown ",420,"Georgetown - W & E on Clinton St",4.0188332167191101,460,"2025-01-01",0,0,0,0,7.8886396234048028E-2,4.6669853995807434E-2,0.24644183737266007,3.405538597329999E-2,5.6195064543415101E-2,0.53775146188076939,48.896905793478254,57.098695647826077,0.63782608695652177,0.30434782608695649,"Continue to Monitor"]
["GEORGETOWN","Scott Ky - 207 W Clinton St - Georgetown ",421,"Georgetown - Water St - N of Substation",2.7582859501269699,321,"2025-01-01",0,0,0,0,0,0.15729646697388633,0.20276497695852536,0.26712749615975423,0,0.37281105990783409,36.492502591900305,56.214797501557626,0.37445482866043606,0.39563862928348908,"Trees Trimmed in 2025"]
["GEORGETOWN","Scott Ky - 207 W Clinton St - Georgetown ",426,"Georgetown - N Broadway St - N of Substation ",23.9407090844355,1708,"2024-02-01",1.6259351620947632E-2,0,0,0,0,5.8753117206982543E-2,0.14342144638403989,0.45093266832917706,0,0.33063341645885286,34.999998044730688,29.346809128220137,0.37892271662763466,0.74531615925058525,"Reliability Improvements Scheduled for 2026"]
["NEWTOWN","Scott Ky - 5849 Paris Pike - Georgetown ",430,"Georgetown - US 460 Pike - E of Substation",70.435770268767698,814,"2021-01-16",2.2415714008913002E-2,3.4876961829102887E-3,0,7.9926370858360784E-4,0.21984596008525481,1.0111896919201705E-2,8.4818833559387713E-2,0.51451995737260225,7.4719046696376676E-2,6.9281631466770008E-2,76.527846013759216,67.665888595823077,0.56093366093366115,0.77272727272727282,"Continue to Monitor"]
["TURTLE CREEK","Harlan - HWY 990 - Cawood",432,"Cawood - HWY 990 - SW of Substation",3.5212533526041301,89,"2025-01-01",0,0,0,0,0.17433380419948763,0,0,0.8211698230660569,0,4.4963727344554316E-3,392.01558050112357,697.43932583146079,2.1797752808988764,1.7303370786516854,"Trees Trimmed in 2025"]
["SPENCER CHEMICAL","Henderson - 1413 KY-136 W - Henderson",437,"Somerset - S Main St - N of Substation",1.17656337519766E-2,1,"2025-01-01",0,0,0,0,0,0,0,0,0,1,4.2733331999999997,21.366665999999999,0.2,1,"Continue to Monitor"]
["ROGERS GAP","Scott Ky - 192 Harbor Village Dr - Stamping Ground ",450,"Stamping Ground - Cincinnati Rd - S of Substation",12.9485757311248,567,"2019-11-02",6.7747458160092242E-2,0,0,1.442996401243842E-2,0.73557877083260537,1.0901086614723455E-2,6.0095733901680583E-3,0.13559973446071066,0,2.9733412529261732E-2,27.359635503350965,50.480158726631387,0.19259259259259257,0.27160493827160492,"Continue to Monitor"]
["ROGERS GAP","Scott Ky - 192 Harbor Village Dr - Stamping Ground ",451,"Stamping Ground - Cincinnati Rd - N of Substation",72.198700823435303,1219,"2019-12-31",8.1642955011383654E-3,0,0,1.5499284014463937E-2,8.8880074998197153E-2,6.9077151304741985E-2,5.5810814987277092E-3,0.21149646128012031,1.3171043278492618E-2,0.58813060812411788,141.31201529844137,251.8695925471699,0.87793273174733366,0.89253486464315024,"Continue to Monitor"]
["ADAMS","Scott - 900 W Main St - Georgetown",452,"Georgetown - Paynes Depot Rd - SW of Substation",35.346959743543302,1592,"2019-01-26",2.4020608209829045E-2,0,0,0,0.27959921046468839,0,3.2066508313539195E-2,0.58780234853300328,0,7.6511324478940143E-2,33.803509208668345,33.090839612437186,0.25904522613065317,0.38316582914572861,"Reliability Improvements Scheduled for 2026"]
["CUMBERLAND"," Harlan - Russel Dr just S of E Main St - Cumberland",454,"Cumberland - Raymond D Hatfield Blvd - N of Substation",10.093716669735899,744,"2024-01-01",5.708268676568388E-3,0,0,0,0.29533362890711595,0.60463311904234096,3.9348259809354913E-2,5.4976723564619821E-2,0,0,25.107562719623651,24.251724905913981,0.13225806451612904,0.14247311827956988,"Continue to Monitor"]
["CUMBERLAND"," Harlan - Russel Dr just S of E Main St - Cumberland",455,"Cumberland - N US HWY 119 - S & E of Substation",5.6868105475450497,229,"2024-01-01",0,0,0,0,3.5362228133312468E-2,0,0,1.7837584102644344E-2,0,0.94680018776404318,19.823071318777288,27.907933034934494,0.12489082969432315,5.2401746724890827E-2,"Continue to Monitor"]
["CLOVERLICK","Harlan - HWY 179 1/4 miles W from intersection of HWY 2006 and HWY 179 - Cumberland ",458,"Cumberland - State Hwy 2006 - S of Substation",8.7793404527006302,148,"2021-07-10",0,0,0,0,8.549896681657955E-2,0,0,0.43470280782788379,0,0.47979822535553662,279.20067566081082,555.87060809459456,1.5243243243243243,2.5540540540540539,"Continue to Monitor"]
["CLOVERLICK","Harlan - HWY 179 1/4 miles W from intersection of HWY 2006 and HWY 179 - Cumberland ",459,"Cumberland - State Hwy 2006 - N of Substation",7.1894062331340196,494,"2024-01-01",0,0,0,0,3.2745646563875695E-3,7.9153384078242575E-4,0.94171925487389663,2.7226595537050289E-2,2.6988051091882983E-2,0,61.266390006477728,186.69392711538458,0.40647773279352234,1.1781376518218623,"Continue to Monitor"]
["BLACK MOUNTAIN","Harlan - Black Mountain Rd - Lynch",467,"Lynch - Radar Station Rd - SW of Substation",3.6448302839327602,10,"2025-01-01",0.86460032626427408,0,0,0,0.13539967373572595,0,0,0,0,0,375.99866660000004,514.86833319999994,0.8,1.7999999999999998,"Continue to Monitor"]
["OXFORD","Scott Ky - 1827 Oxford Dr - Georgetown ",470,"Georgetown - Oxford Rd - N of Substation",41.268222551041802,1296,"2025-01-01",1.1298759130394327E-3,0,0,7.4724675825307896E-2,0.38405146917100341,5.7324586764500626E-2,0.23797845260170544,2.6984095334941743E-3,0,0.24209253019094903,33.083168719290121,83.086432609567879,0.2450617283950618,0.5277777777777779,"Continue to Monitor"]
["OXFORD","Scott Ky - 1827 Oxford Dr - Georgetown ",471,"Georgetown - Oxford Rd - S & E of Substation ",13.8021310217656,654,"2019-08-31",2.0974974685375378E-2,0,0,0,2.5025314624620279E-2,0,0,0,0,0.95399971069000433,4.0667227308868501,10.569724769113149,1.9266055045871561E-2,3.82262996941896E-2,"Continue to Monitor"]
["SHADRACK","Franklin - 74 Bethel Ln - Frankfort ",475,"Frankfort  - US HWY 127 - N of Substation",48.4198587622449,585,"2025-01-01",1.6079165552286709E-2,0,0,0,3.3174645627173038E-2,2.3000802353570471E-3,0.15829901043059641,0.2578443434073282,0,0.53230275474725863,101.01845582222222,119.21341878290599,0.83111111111111102,1.3504273504273503,"Trees Trimmed in 2025"]
["STAMPING GROUND","Scott Ky - 3540 Main St - Stamping Ground ",480,"Stamping Ground - Owenton/HWY 227 N of Substation",56.465186416130003,498,"2025-01-01",2.2725098991908488E-3,0,0,0.27913805306348871,1.9740995083880102E-2,1.4767488570499455E-3,1.5934349714023376E-3,0.13699906268531095,1.6554125141075425E-2,0.54222507029860167,384.41191429708101,1048.6295849799196,2.3301204819277119,3.5923694779116482,"Reliability Improvements Scheduled for 2026"]
["STAMPING GROUND","Scott Ky - 3540 Main St - Stamping Ground ",481,"Stamping Ground - SE on Main St & N on Locust Fork Rd ",103.201333709689,1336,"2023-12-23",7.1815429012722027E-3,0,0,1.5242043653213022E-4,0.62235042474494984,0.19170172336706906,8.1824371011665238E-3,0.11088586757712475,0,5.9545583871885542E-2,105.18017213727543,152.74303890194611,0.99955089820359222,1.9670658682634723,"Continue to Monitor"]
["HOLMES MILL"," Harlan - 1/4 mile E of 25511 HWY 38 - Upper Clover ",490,"Upper Clover - Highway 38 - NE of Substation",1.05833657340009,18,"2023-05-13",0,0,0,0,0,0,0,1,0,0,436.45074072222224,929.24444438888895,0.57777777777777772,1.7777777777777777,"Continue to Monitor"]
["HOLMES MILL"," Harlan - 1/4 mile E of 25511 HWY 38 - Upper Clover ",491,"Upper Clover - Highway 38 - W of Substation",8.8876821773032297,197,"2023-05-13",1.3188742511432001E-4,0,0,0,0.39757306035801632,4.3406789353625007E-3,0,0.59790161831146116,0,5.2754970045728006E-5,455.25978002233495,680.51548221827409,2.3847715736040609,3.639593908629442,"Continue to Monitor"]
["MIDWAY","Woodford - 860 Weisenburger Rd - Midway ",504,"Midway - Weisenberger Mill Rd - E of Substation",63.709620436822497,558,"2023-07-14",2.2834846868624594E-3,0,0,0,8.0347835962247469E-3,2.2713169176607058E-4,3.852315729275247E-2,0.80370549131424074,0,0.14722595141815351,202.69799280609317,222.51033450537631,1.3491039426523299,0.73655913978494636,"Continue to Monitor"]
["VERSAILLES BYPASS","Woodford - 350 Markham Dr - Versailles ",508,"Versailles - US 60 Bypass - SE of Substation",4.0837043998317997,345,"2020-05-02",0,0,0,0,9.060562708631377E-3,1.3198126174647256E-2,0.95483744284552163,0,0,2.2903868271199754E-2,62.820724634782607,206.65806762898552,0.63072463768115949,1.9072463768115941,"Continue to Monitor"]
["VERSAILLES BYPASS","Woodford - 350 Markham Dr - Versailles ",510,"Versailles - Kuhlman Blvd - N of Substation",2.3614735109872198,37,"2020-05-02",0.11328125,0,0,4.98046875E-2,0,0,0,0,0.2587890625,0.578125,12.1908108,27.69279278378378,5.4054054054054057E-2,0.13513513513513514,"Continue to Monitor"]
["ALEXANDER","Woodford - 2915 Troy Pike - Versailles",515,"Versailles - N & S on McCowans Ferry Rd - E of Substation",50.4233901887483,1557,"2021-10-23",3.1085326122606647E-2,0,0,0,0.86496650947865572,1.2900592552640977E-3,9.7811272348272259E-3,2.7761783634468636E-2,0,6.5115194274177682E-2,67.443943473988455,87.121633477841996,0.75465639049454103,0.50995504174694939,"Continue to Monitor"]
["MIDWAY","Woodford - 860 Weisenburger Rd - Midway ",516,"Midway - State HWY 341 - N of Substation",25.7677941614674,819,"2023-05-13",4.3255996854109323E-3,0,0,0,8.0613448682658281E-2,1.6606672918116096E-2,0,0.30003932363350372,0.20983695816570375,0.3885779969146072,77.128445250793646,40.367032959706968,0.89035409035409008,1.0610500610500608,"Continue to Monitor"]
["PAYNES MILL","Woodford - 221 Paynes Mill Rd - Versailles",517,"Versailles - Lexington Rd,  Crossfield Dr, Kroger Way - W of Substation",3.95987063147258,392,"2020-06-20",9.0383776711731353E-2,0,0,0,0.89184474487570864,0,1.7771478412559966E-2,0,0,0,6.9910374112244913,23.395748293367351,7.9081632653061243E-2,0.29336734693877553,"Continue to Monitor"]
["PAYNES MILL","Woodford - 221 Paynes Mill Rd - Versailles",518,"Versailles - Lexington Rd, Gleneagles Way, and Bryanwood St - W of Substation",53.514341899459403,2936,"2020-06-20",1.6694864389517557E-2,0,0,0,9.8839118223397068E-2,3.1264965880406798E-3,2.7994169449841164E-2,0.5585031296335411,5.3558245899479476E-3,0.28948639712571445,54.929745682152586,110.12103200851499,0.48385558583106275,1.0820844686648503,"Reliability Improvements Scheduled for 2026"]
["SOMERSET 1","Pulaski - 144 Railroad Dr - Somerset ",522,"Somerset - Langdon St - N of Substation",3.2105036993698302,290,"2024-02-01",0,0,0,0,0,0,1.8850096848868521E-2,0.98114990315113149,0,0,19.962885055172414,72.989137931034492,0.26965517241379311,1.0517241379310345,"Tree Trim Scheduled for 2026"]
["SOMERSET 1","Pulaski - 144 Railroad Dr - Somerset ",523,"Somerset - S Main St - N of Substation",2.0001400189596499,121,"2025-01-01",0.25747508305647843,0,0,0,0.36710963455149503,0,0.13953488372093023,0,0,0.23588039867109634,2.6226721719008266,4.9731404876033061,3.1404958677685953E-2,4.9586776859504134E-2,"Continue to Monitor"]
["WOODLAKE","Franklin - 1635 Woodlake Rd - Frankfort",525,"Frankfort - Woodlake Rd - N of Substation",3.5017671110965402E-3,1,"-",0,0,0,0,0,0,1,0,0,0,66.183333200000007,330.91666600000002,0.2,1,"Continue to Monitor"]
["SCIENCE HILL","Pulaski - 45 E HWY 635 neat the intersection of E hWY 635 and Maple Ln - Science Hill",528,"Science Hill - E on HWY 635 and S on HWY 1247",14.988579892092201,589,"2023-02-25",4.724301624977177E-3,0,0,0,3.8798612379039622E-3,0,0.10633102063173269,0.21193171444221287,0,0.67313310206317323,33.495263147707981,73.928890764006795,0.57996604414261455,1.1629881154499149,"Continue to Monitor"]
["DENHAM STREET","Pulaski - 114 Adams St - Somerset ",529,"Somerset - HWY 27 - W of Substation",8.0695212517894301,336,"2025-01-01",0,0,0,0,0,0,0,0.99180809399477798,0,8.1919060052219328E-3,46.824890869047621,49.319146818452388,0.76428571428571446,0.39583333333333326,"Trees Trimmed in 2025"]
["DENHAM STREET","Pulaski - 114 Adams St - Somerset ",530,"Somerset - HWY 27 - SW of Substation",6.8780340202594497,356,"2025-01-01",2.3074977873308888E-3,0,0,0,0,0,2.6330762422556581E-2,2.2074008513507819E-2,0.87851392927888061,7.0773801997724109E-2,91.847106729775277,266.59330523876406,0.9539325842696631,1.6769662921348316,"Continue to Monitor"]
["DENHAM STREET","Pulaski - 114 Adams St - Somerset ",531,"Somerset - Monticello St - S of Substation",5.3713830728978502,201,"2025-01-01",0,0,0,0,0.83837024348464451,3.670622782332069E-3,2.2513153064970023E-2,0.13348831518414292,1.9576654839104368E-3,0,12.921243775124378,14.858872298507464,0.17412935323383083,0.15422885572139303,"Continue to Monitor"]
["WAITSBORO"," Pulaski - 676 Old Monticello Rd at W Summitt Dr just W of HWY 27 - Somerset ",533,"Somerset - N & S on HWY 27",23.9926111140907,1131,"2024-01-01",5.7216075722589174E-4,0,0,0,3.4303399527258736E-3,7.309432411279651E-2,0.22723338227319995,0.69354754892105697,0,2.1222439829947522E-3,62.43480989513705,92.569112870026515,0.7386383731211319,0.78337754199823151,"Continue to Monitor"]
["WAITSBORO"," Pulaski - 676 Old Monticello Rd at W Summitt Dr just W of HWY 27 - Somerset ",534,"Somerset - Old Monticello Rd - N of Substation",11.6213107363136,481,"2025-01-01",3.1096254011972056E-4,0,0,0,0.46309263351954066,0.26803027442444166,4.7699432493364278E-3,0.2389608298257499,1.8452295014604134E-2,6.3830614262074788E-3,64.799875250311842,206.74577268399167,0.45031185031185039,0.9293139293139292,"Continue to Monitor"]
["FERGUSON SOUTH"," Pulaski - 140 McKee Rd - Somerset ",539,"Somerset - Crane Rd - N of Substation",16.530613770131801,754,"2024-01-01",5.0207599963895656E-2,0,0,4.4002166260492821E-3,2.459608267894214E-3,0,0.35037006950085747,0.52087282245690047,0,7.1689683184402928E-2,29.629186551193641,58.77504419628648,0.63846153846153864,1.3965517241379313,"Continue to Monitor"]
["FERGUSON SOUTH"," Pulaski - 140 McKee Rd - Somerset ",540,"Somerset - McKee Rd - N of Substation",0.75421439367202203,5,"2020-11-14",0,0,0,0,0,0,1,0,0,0,32.34599996,94.9466666,0.24,0.2,"Continue to Monitor"]
["SOMERSET SOUTH"," Pulaski - 3084 S HWY 27 S of Monticello Rd - Somerset ",541,"Somerset - HWY 27 - S of Substation",5.1016127830808502,346,"2025-01-01",0,0,0,0,0.1878301304560642,0,0.74671731681882991,6.5452552725105875E-2,0,0,45.047899802890178,154.39677263583818,0.30289017341040469,0.76589595375722552,"Continue to Monitor"]
["LIBERTY","Casey - 1351 E KY HWY 70 - Liberty ",551,"Liberty - E KY 70 - SW of Substation",23.6593936029597,719,"2023-01-20",3.4470843060741166E-3,0,0,0,6.9700213230398395E-3,6.0850730293044303E-3,0.24064693934311551,0.72595258362761383,0,1.6898298370852331E-2,90.678052842837275,149.93284653129345,0.71515994436717656,1.6161335187760775,"Continue to Monitor"]
["LIBERTY","Casey - 1351 E KY HWY 70 - Liberty ",552,"Liberty - E KY 70 - NE of Substation",30.490766348052698,525,"2023-02-17",4.3808547327212565E-4,0,0,0,0.32421121312392226,0.50830032157337934,2.6676609032017521E-2,0.11180500535955631,1.5267744791909401E-2,1.3301020645943049E-2,201.85737776495239,396.35234919428569,0.87619047619047596,1.6285714285714286,"Continue to Monitor"]
["SHELBY CITY","Boyle - 401 Grubbs Ln - Junction City ",553,"Junction City - Hustonville Rd & Hwy 127 - SE & NE of Substation",21.660540643630199,965,"2022-12-02",8.735299130731209E-3,0,0,0,0,0,0.3638571672064087,0.44865348559740925,0,0.17875404806545084,15.416103623419687,10.429119167875648,0.24435233160621758,0.55647668393782379,"Continue to Monitor"]
["WINCHESTER WATER","Clark -  335 Waterworks Rd - Winchester ",555,"Winchester - Boonesboro Rd - SW of Substation",20.145738980176802,273,"2022-08-12",3.9678512715390392E-3,0,0,0,0.38409003267642222,0,8.9850013192344383E-2,0.4869700229343833,0,3.5122079925311037E-2,96.203504246153855,184.94981682051284,0.91721611721611696,1.7326007326007327,"Continue to Monitor"]
["EDDYVILLE","Lyon - 1765 S R 3305 - Eddyville",560,"Eddyville - US HWY 62 & Riley Rd - NE of Substation",49.438085413449301,537,"2021-05-08",2.2457505762123187E-3,0,0,0,8.1060685272149519E-2,3.1004086902364403E-3,0,0.90811970668860897,0,5.4734487727927774E-3,30.617380494972071,38.601272484171325,0.47858472998137797,0.32960893854748607,"Reliability Improvements Scheduled for 2026"]
["WHITLEY CITY"," McCreary - Corner of US HWY 27 & Hicks Rd - Stearns-Whitley City ",575,"Stearns-Whitley City - Tunnel Ridge Rd - SW of Substation",11.5697716134855,613,"2024-01-01",5.7649667405764967E-3,0,0,0,9.0022172949002222E-2,0.38680709534368068,5.7039911308203989E-2,0.40726164079822613,0,5.3104212860310418E-2,28.185377916476348,29.428412174551386,0.24959216965742251,0.25448613376835238,"Continue to Monitor"]
["WHITLEY CITY"," McCreary - Corner of US HWY 27 & Hicks Rd - Stearns-Whitley City ",576,"Stearns-Whitley City - US HWY 27 - N of Substation",39.730332487903198,757,"2024-01-01",1.8271380321491131E-3,0,0,0.13909088269735123,0.4110712177371747,5.385992586929382E-2,2.4077963050778564E-3,0.36333143006454982,0,2.8411609294403423E-2,310.58231614266833,523.38322322985448,1.4055482166446502,1.430647291941876,"Continue to Monitor"]
["SHUN PIKE","Jessamine - 1201 Short Shun Rd Nicholasville ",580,"Nicholasville - N & S on Nicholasville Bypass ",34.965114499782999,1435,"2025-01-01",3.7758292032024398E-3,6.9111704155547082E-3,0,0,0.42505223027068245,2.3484559664506291E-4,0.18692489515821581,0.32989706443004196,0,4.7203964925657642E-2,110.78654354787457,174.0445876815331,1.1237630662020905,1.4968641114982573,"Reliability Improvements Scheduled for 2026"]
["WILMORE","Jessamine - 210 W Linden St - Wilmore ",585,"Wilmore - College St - E & S of Substation",21.853038982902198,893,"2025-01-01",0,0,0,0,0.13279569584095718,2.9252680061717419E-3,6.3782314173783869E-3,0.84593014918866838,0,1.1970655546824364E-2,56.301978344456892,99.915378867861151,0.44904815229563277,0.39865621500559906,"Trees Trimmed in 2025"]
["WILMORE","Jessamine - 210 W Linden St - Wilmore ",586,"Wilmore - Lexington Rd - N of Substation",52.053763775373803,1345,"2021-04-10",3.6931070244670158E-3,0,0,0,6.0913720350779715E-2,4.2312911910888339E-3,4.0043811100266618E-3,0.75813276276114649,0,0.16902473756249117,49.950731095167285,101.28115240966542,0.4802973977695168,1.2059479553903352,"Reliability Improvements Scheduled for 2026"]
["WILMORE","Jessamine - 210 W Linden St - Wilmore ",588,"Wilmore - Main St - SE of Substation",1.1853178274318401,48,"2021-01-16",0,0,0,0,0,0,0.44801714898177919,0,0,0.55198285101822075,18.436944433333334,58.319097208333332,0.19999999999999998,0.45833333333333331,"Continue to Monitor"]
["HIGH BRIDGE","Jessamie - 200 Crusher Ln - Wilmore ",590,"Wilmore - High Bridge Road - S of Substation",7.3162314001222102,140,"2024-01-01",0,0,0,0,0,0,0.26692696371152963,0.73307303628847043,0,0,93.989357134285711,155.50642856428573,0.72857142857142843,0.88571428571428568,"Continue to Monitor"]
["INNOVATION DRIVE","Fayette - 2350 Innovation Dr - Lexington ",592,"Lexington - Georgetown Rd - E of Substation",14.635354895986501,960,"2025-01-01",7.4917945195023275E-2,0,0,0,0,0,0,9.4076788031447978E-2,0,0.83100526677352871,49.588913191250001,24.775659718750003,0.27583333333333326,0.44791666666666669,"Reliability Improvements Scheduled for 2026"]
["INNOVATION DRIVE","Fayette - 2350 Innovation Dr - Lexington ",594,"Lexington - Greendale Rd - W of Substation",29.0418144226004,2921,"2024-01-01",3.8768718801996671E-2,0,0,0,0.39373266777592902,1.9966722129783694E-3,0,0,0,0.56550194120909592,1.7735684122560766,2.6817185891817865,1.4447107155083874E-2,2.636083533036631E-2,"Reliability Improvements Scheduled for 2026"]
["INNOVATION DRIVE","Fayette - 2350 Innovation Dr - Lexington ",595,"Lexington - Drummond Dr and Georgetown Rd - NW of Substation",21.323092717064299,1660,"2025-01-01",1.6342480046410927E-2,4.096343423706676E-4,0,5.7675872001063763E-2,0,1.9187401277587317E-2,2.1918654340461899E-3,0.6930058689234444,0,0.21118687797507665,41.912769074337362,173.42518071807231,0.51686746987951826,2.2710843373493983,"Trees Trimmed in 2025"]
["INNOVATION DRIVE","Fayette - 2350 Innovation Dr - Lexington ",596,"Lexington - Spurr Rd and Kearney Rd - NW of Substation",27.481711585087801,905,"2025-01-01",0,0,0,0,9.7331222307017635E-3,5.6633216771268778E-2,7.7397970225416609E-3,2.7735696467827732E-2,0,0.89815816750766009,50.695502759116025,176.14337016243095,0.30121546961325962,1.0187845303867402,"Continue to Monitor"]
["MOUNT STERLING","Montgomery 346 Calk Ave - Mount Sterling ",601,"Mount Sterling - 686 Bypass - N of Substation",18.323462043224499,1366,"2025-01-01",2.0530776002849443E-2,0,0,0,9.374936996391154E-3,3.9031995752716715E-2,1.3286201033595204E-2,0.57482140577012242,0,0.34295468444432498,48.086073689897503,105.27468276793557,0.54275256222547574,1.1954612005856513,"Reliability Improvements Scheduled for 2026"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",604,"Mount Sterling - US 460 HWY - S of Substation",24.8547895278328,641,"2023-08-05",0,1.4045946911082014E-2,0,0,0.20336864658969173,6.0707058683490058E-4,9.4869658374003088E-3,1.1760504701821212E-2,0,0.76073086537316981,82.570249601248037,129.75161205460216,0.882371294851794,1.1809672386895476,"Continue to Monitor"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",605,"Mount Sterling - 686 Bypass & Spencer Rd - E of Substation",39.751879347446199,1349,"2025-01-01",7.8458473921704137E-3,0,0,0,2.8219304307763185E-3,6.3688225808637212E-4,6.4569020420884322E-3,0.28369716926162308,0.16672764475520685,0.53181362386004849,74.035470712972568,213.12968865085242,0.76456634544106705,1.888806523350629,"Reliability Improvements Scheduled for 2026"]
["A O SMITH","Montgomery - 1871 Owingsville Rd - Mt. Sterling",607,"Mount Sterling - Maysville Rd - W of Substation",36.999061512303498,1099,"2023-06-14",5.7282327156804147E-4,0,0,0,1.123231719466029E-2,4.7527727967058512E-3,2.8060038520289566E-3,1.2157966394368069E-2,0,0.96847811649066884,56.755232023839859,215.8642857088262,0.41856232939035476,1.0937215650591441,"Continue to Monitor"]
["OWINGSVILLE","Montgomery - 69 W Paul Lewis Dr - Owingsville ",611,"Owingsville - W Main St - SW of Substation",25.493381578613299,729,"2023-03-24",1.8405162671193383E-3,0,0,0,9.1979685128720817E-2,0,8.7210026431474214E-2,0.80366442637243007,0,1.5305345800255551E-2,101.89271146721538,267.23696843347057,0.93635116598079515,1.6639231824417,"Continue to Monitor"]
["MOREHEAD WEST","Rowan - 133 Gregory Ct - Morehead ",616,"Morehead - US HWY 60 - SW of Substation",7.8874938384014204,373,"2022-09-09",2.8113493610569633E-2,0,0,0,5.2567875753290272E-3,0.9008243193313713,0,0,0,6.5805399482730065E-2,44.471403030026806,58.648748876675604,0.74906166219839143,2.4932975871313672,"Continue to Monitor"]
["MOREHEAD WEST","Rowan - 133 Gregory Ct - Morehead ",617,"Morehead - Clearfield Rd - S of Substation",27.866096980235099,1478,"2024-01-01",7.5636112220387776E-3,0,0,0,0.10434684134297312,3.2960417697300583E-3,1.2266282029121989E-2,0.13238405740953765,0,0.74014316622659837,53.538755069824106,113.00232295263876,0.44127198917456018,0.88362652232746963,"Reliability Improvements Scheduled for 2026"]
["ROCKWELL","Clark - 5835 Rockwell Rd - Winchester  ",626,"Winchester - Lexington Rd - E of Substation",16.827672048801698,596,"2022-03-04",1.2541526809536104E-2,0,0,0,1.2703330751355538E-3,0,0,0.96990446682158526,0,1.6283673293743008E-2,12.966828853020132,14.667393728187918,0.13926174496644295,6.7114093959731544E-2,"Continue to Monitor"]
["ROCKWELL","Clark - 5835 Rockwell Rd - Winchester  ",628,"Winchester - Lexington RD - SE of Substation",22.3861536399803,1747,"2022-03-11",8.1924053769435665E-3,0,0,0,0.23304218546738525,0.13346342067769312,6.708790187697454E-2,0.2461593260236635,6.6576844452703954E-2,0.24547791612463607,29.220135465827134,27.555600073268465,0.36576989124212933,0.36920435031482529,"Continue to Monitor"]
["PARKER SEAL","Clark - 390 Mt Sterling Rd - Winchester ",630,"Winchester - Cherry St - SW of Substation",18.324533904409499,1417,"2024-01-01",1.5345640906179023E-2,0,0,0,0,7.0855900452313006E-2,3.9184283578902412E-2,0.70377380467066575,0.1154951177372702,5.5345252654669698E-2,32.936137374029649,67.557351206774896,0.49710656316160884,0.66478475652787572,"Continue to Monitor"]
["WINCHESTER","Clark - 2 Almond St - Winchester ",634,"Winchester - Maple St - S of Substation",1.6872153651086801,261,"2021-07-03",0,0,0,0,0,0,1,0,0,0,36.109335882758614,146.69469986590036,0.41455938697318012,0.71264367816091956,"Continue to Monitor"]
["WINCHESTER SOUTH","Clark - 105 Hood Ave - Winchester",637,"Winchester - Belmont Ave & S Burns Ave - NE of Substation",2.9621533034513501,375,"2024-01-01",0,0,0,0,0,0,0.57040487280544605,0.20637764242207093,0.14976710856323899,7.3450376209243995E-2,9.7021511077333322,7.4419555519999996,6.986666666666666E-2,0.08,"Continue to Monitor"]
["BOONE AVENUE","Clark - 660 Boone Ave. - Winchester",638,"Winchester - Boonesboro Rd & Hillcrest Dr - SW of Substation",5.2823486638852897,309,"2021-09-11",0,0,0,0,9.7643812354064954E-2,0,2.7633584840122731E-2,0.85783755620308366,0,1.6885046602728625E-2,44.366461698381876,117.70183386731391,0.25372168284789637,0.3689320388349514,"Continue to Monitor"]
["WINCHESTER WATER","Clark -  335 Waterworks Rd - Winchester ",641,"Winchester - Old Boonesboro Rd - N of Substation",23.405215554058501,1099,"2024-01-01",4.1074386973355423E-3,0,0,0,1.9381618811382753E-3,0,1.2574025427219389E-2,0.68843647314032563,0.20133314416995415,9.1610756684026989E-2,79.667306634576875,124.37776765878071,0.61728844404003647,0.96542311191992725,"Reliability Improvements Scheduled for 2026"]
["WINCHESTER WATER","Clark -  335 Waterworks Rd - Winchester ",642,"Winchester - Waterworks Rd - E of Substation",25.899899949362101,233,"2022-12-02",7.584816700263077E-3,0,0,0,0.17532201305135126,3.6728279066589225E-3,1.4537565342170898E-2,0.79684990946052148,0,2.0328675390344731E-3,44.967081519313311,143.23161657081545,0.54248927038626626,0.92274678111587949,"Continue to Monitor"]
["WINCHESTER INDUSTRIAL","Clark - 705 Tech Dr - Winchester",645,"Winchester - Tech Dr, Rolling Hills Ln, Corporate Dr - W of Subs.",3.25462377761081,20,"2021-10-23",0,0,0,0,0,0,0,0,0,0,43.800499990000006,45.659166649999996,0.5,0.85,"Continue to Monitor"]
["WINCHESTER INDUSTRIAL","Clark - 705 Tech Dr - Winchester",649,"Wnchester - Enterprise Dr - N NW of Substation",0.88380743361936198,5,"2021-10-23",0,0,0,0,0,0,0,0,0,1,20.132666559999997,20.233333200000001,0.55999999999999994,0.4,"Continue to Monitor"]
["CORPORATE DRIVE","CLARK - 4011 CORPORATE DR - WINCHESTER",651,"Nortonville - Mockingbird St, US 41, & Wells Rd - N of Substation",0.89513384504918803,2,"-",0,0,0,0,0,0,0,0,0,0,18.0833333,90.416666500000005,0.2,1,"Continue to Monitor"]
["STRINGTOWN","Muhlenberg - 5995 Paradise Rd - Greenville",652,"Greenville - Paradise Rd - S of Substation",0.96407536530918003,8,"2023-09-29",0,0,0,0,0.22674418604651161,0,0,0.77325581395348841,0,0,101.23749990000002,291.94166625000003,0.625,1.875,"Continue to Monitor"]
["STRINGTOWN","Muhlenberg - 5995 Paradise Rd - Central City",654,"Greenville - Cleaton Rd - E of Substation",2.9912466739936701,9,"2023-09-29",0,0,0,0.223267750213858,0,0.24465355004277159,0.53207869974337041,0,0,0,32.415185155555555,129.87407400000001,0.48888888888888893,1.7777777777777779,"Continue to Monitor"]
["MUHLENBERG PRISON","Muhlenberg - 1200 River Rd - Central City",656,"Centeral City - No Road - W of Substation",2.4036035621074401E-2,1,"2025-01-01",0,0,0,0,0,0,0,0,0,0,77.443333199999998,71.7,0.4,1,"Continue to Monitor"]
["MUHLENBERG PRISON","Muhlenberg - 1200 River Rd - Central City",657,"Central City - Hwy 431, S R 81, & S Carrolton St - NW of Substation",42.415986033735201,725,"2025-01-01",1.0995180835633743E-2,0,0,0,0.73838487811725073,6.4801384924905257E-3,8.7657324661956665E-2,0.13591915032985541,0,2.0563327562812896E-2,62.202588493241386,86.394505735172444,0.86317241379310394,0.93931034482758613,"Continue to Monitor"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",658,"Mt Sterling - US 460 Hwy, By-Pass, Burley Dr - SW of Substation",4.8768455632387901,349,"2023-07-14",1.9607843137254902E-2,0,0,0,0.94560762157970535,0,0,0,0,3.4784535283039771E-2,7.0158548206303735,25.866236862464181,8.7106017191977067E-2,0.32378223495702002,"Continue to Monitor"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",659,"Mt Sterling - US Hwy 460 - SE of Substation",48.6074638907332,1086,"2025-01-01",1.9711591428137553E-3,0,0,0.3441816563096447,3.0612518349347757E-2,2.3600313241603964E-2,7.3215758553848084E-2,2.8855745095178402E-2,3.2720646254350991E-2,0.46484220305321239,118.72335788213627,296.3561387265193,1.1208103130755069,3.4530386740331513,"Reliability Improvements Scheduled for 2026"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",663,"Mt Sterling - S Queen St - NW of Substation",12.0571864469698,1094,"2023-07-15",4.0323767476085355E-2,0,0,0,0.11390728476821191,3.2376747608535691E-2,0.24915378955114054,0.55143487858719653,0,1.2803532008830023E-2,7.2443967062157215,7.2272547157221201,7.9524680073126144E-2,8.9579524680073117E-2,"Continue to Monitor"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",664,"Mt Sterling - S Queen St - NW of Substation",3.2003921586451902,94,"2023-07-15",0,0,0,0,0.87803730992318552,0,0,0,0,0.12196269007681455,2.1773404212765959,8.2712765957446805,2.3404255319148935E-2,6.3829787234042548E-2,"Continue to Monitor"]
["BEECHMONT","Muhlenberg - 3660 Merle Travis Hwy - Beechmont",695,"Beechmont - US Hwy 431 - N of Substation",10.0388016952601,323,"2023-02-17",2.1984924623115578E-3,0,0,0,7.459170854271357E-3,0,1.7902010050251257E-2,4.8523869346733667E-2,0,0.92391645728643212,40.252672850154809,78.861248699690407,0.49659442724458203,0.78328173374613008,"Continue to Monitor"]
["BEECHMONT","Muhlenberg - 3660 Merle Travis Hwy - Beechmont",696,"Beechmont - US Hwy 431, Hazel Creek Rd - SE of Substation",17.4604057921741,479,"2024-01-01",1.3076126359399275E-2,0,0,0,1.2471948903849473E-2,5.6965302951838426E-3,5.5023303987571208E-2,0.5825996892801657,0,0.33113240117383047,63.879714675156585,44.73256784133612,0.97453027139874726,1.3152400835073066,"Continue to Monitor"]
["SIMMONS","Ohio - 5798 US HWY 62 W - Centertown",698,"Centertown - US HWY 62 - E of Substation",2.1102304749635201,28,"2023-09-29",0,0,0,0,0,0,0,1,0,0,33.356547607142851,9.5119047499999994,0.30714285714285711,0.7142857142857143,"Continue to Monitor"]
["BROMLEY","Owen - 7205 Hwy 127 - New Liberty",701,"Bromley - State Hwy 36, St Hwy 227, & Alexander Rd - W of Subst.",77.663246218132301,961,"2018-12-08",1.589370558802506E-2,0,0,0,0.37911953916663166,1.4817306479418072E-2,6.2481604507421268E-2,0.47466677879157382,5.7940545767985532E-3,4.7227010890131607E-2,111.86790147617069,123.55433574089493,1.0312174817898023,1.3215400624349627,"Continue to Monitor"]
["CAMPBELLSBURG","Henry - 379 Turners Station Rd. - Campbellsburg",703,"Campbellsburg - Hwy 193 & Webb Ln - W & E of Sub.",52.459652463777402,949,"2023-09-09",4.959846965405597E-3,0,0,7.2860999758896333E-4,2.0038099679146652E-2,6.2127912121685815E-2,0.16303112356960611,3.4257917341182892E-3,0.11791029353709685,0.6277783223953517,137.83969440105372,305.78001402634357,1.5618545837723925,2.8577449947312981,"Continue to Monitor"]
["CARROLLTON","Carroll - 802 Mason St - Carrollton ",704,"Carrolton - 4th St - N of Substation",6.73511042371792,517,"2024-01-01",3.1806713051456534E-2,0,0,8.4104289318755257E-3,0.5461426714580625,2.1943573667711599E-2,0.33014756479853202,0,0,6.1549048092361801E-2,8.0029271415860741,25.299613150870407,6.7311411992263051E-2,0.19729206963249515,"Continue to Monitor"]
["OWENTON","Owen - 327 Gayle Avenue - Owenton",716,"Owenton - Gratz Rd- SW of Substation",19.252396058857101,492,"2022-03-04",2.7843601895734597E-2,0,0,0,0.76562110251933158,8.1379396358194061E-3,0.18589423796457971,0,0,1.2503117984534797E-2,225.96731028821142,65.185298085365858,0.58577235772357739,0.69715447154471577,"Continue to Monitor"]
["HUNTERS BOTTOM","Trimble - 400 Hunter Heights Rd - Milton",719,"Milton - N Spillman Lan, HWY 421 N - SE of Substation",25.5576605960654,506,"2025-01-01",7.6519107955950599E-3,0,0,0,1.1637887141589445E-3,0.18070729259103011,6.3455579639516452E-2,3.7561280749479932E-2,0,0.70946014751021957,533.27306322648224,135.85546769960467,1.2956521739130431,1.3478260869565213,"Continue to Monitor"]
["LAWRENCE","Henry - 9255 HWY 55 - Campbellsburg",720,"Campbellsburg - HWY 55, HWY 316 - N & S of Substation",11.375158398186199,109,"2020-03-28",1.4470034969251175E-3,0,0,0,2.0217854415370391E-2,1.2862253306001046E-3,5.4262631134691913E-3,0,0,0.9716226536436352,61.649235453210999,193.96819568807337,0.49174311926605502,1.2477064220183482,"Continue to Monitor"]
["LAWRENCE","Henry - 9255 HWY 55 - Campbellsburg",720,"Campbellsburg - HWY 55, HWY 316 - N & S of Substation",11.375158398186199,109,"2020-03-28",1.4470034969251175E-3,0,0,0,2.0217854415370391E-2,1.2862253306001046E-3,5.4262631134691913E-3,0,0,0.9716226536436352,61.649235453210999,193.96819568807337,0.49174311926605502,1.2477064220183482,"Continue to Monitor"]
["SCHOLLS","Owen - 970 HWY 127 N - Owenton",724,"Owenton - HWY 127 N, State HWY 845 - NE of Substation",12.9072520500662,185,"2022-01-15",0,2.8063276432210207E-2,0,0,0,0.23076235588524444,0.41067119492358567,0.30655107695057648,0,2.3952095808383235E-2,37.234036027027024,60.483783767567566,0.36108108108108111,0.44324324324324327,"Continue to Monitor"]
["OWENTON","Owen - 327 Gayle Avenue - Owenton",725,"Owenton - N Main St & E Adair St - SE of Substation",7.4633096531775101,513,"2022-01-14",6.5821418937145937E-2,0,0,0,0.1025087671971945,0,0.55894254113838682,0.24143512274076073,0,3.1292149986512002E-2,3.3065951898635482,7.2225795945419105,2.8460038986354776E-2,4.2884990253411304E-2,"Continue to Monitor"]
["STANFORD NORTH","Lincoln - 300 Lee Dr - Stanford",768,"Stanford - Danville Ave, Lancaster St - SW of Substation",11.3145777471022,635,"2024-01-01",0,0,0,0,0,0,8.4006805614632064E-3,0.99159931943853685,0,0,36.032645665511808,33.485695533858269,0.42992125984251972,0.60629921259842512,"Continue to Monitor"]
["HARRODSBURG NORTH","Mercer - 1000 Warwick Rd - Harrodsburg",773,"Harrodsburg - Warwick Rd, N Greenville St - S of Substation",4.5999234898051098,197,"2021-11-13",4.2452151388689019E-2,0,0,0,2.8522089509281912E-2,0,0.17239890631745575,9.3797668729313569E-2,0,0.6628291840552597,24.744280874111677,66.017343467005091,0.45989847715736037,1.5634517766497458,"Continue to Monitor"]
["HARRODSBURG NORTH","Mercer - 1000 Warwick Rd - Harrodsburg",774,"Harrodsburg - Collin Dr - W of Substation",0.17676028661295501,5,"2021-11-13",1,0,0,0,0,0,0,0,0,0,63.113333280000006,36.813333200000002,0.48000000000000009,1.2,"Continue to Monitor"]
["MOREHEAD","Rowan - 100 E Wilkinson Blvd - Morehead ",779,"Morehead - Wilkinson Blvd - N of Substation",6.9891538733991903,501,"2022-07-08",0,0,0,0,0,0.1957344064386318,3.4366197183098593E-2,0.73408450704225348,3.5331991951710259E-2,4.8289738430583502E-4,60.858223547704597,159.42408515768463,0.92175648702594837,3.1357285429141721,"Continue to Monitor"]
["MOREHEAD","Rowan - 100 E Wilkinson Blvd - Morehead ",780,"Morehead - 2nd St - E of Substation",15.2828498495095,1359,"2024-01-01",7.8497747233848367E-3,0,0,0.55049908220638266,2.4077183207952624E-3,9.1268530406383346E-4,2.1318694042685065E-3,9.2324248481979575E-3,0,0.42696644519290694,64.337586455187648,222.99717929065488,0.83532008830022053,3.0721118469462829,"Continue to Monitor"]
["CORPORATE DRIVE","Clark - 4011 Corporate Dr - Winchester",797,"Winchester - Enterprise Dr - ESE of Substation",0.58197048550833497,2,"2021-10-23",0,0,0,0,0,0,0,0,0,0,18.0833333,90.416666500000005,0.2,1,"Continue to Monitor"]
["CORPORATE DRIVE","Clark - 4011 Corporate Dr - Winchester",798,"Winchester - Enterprise Dr - SE of Substation",1.1636421174360501,11,"2021-10-23",0,0,0,0,0.33753943217665616,0,0.38170347003154576,0,0,0.28075709779179808,39.892727218181825,119.20606045454547,0.34545454545454535,1.3636363636363633,"Continue to Monitor"]
["DETROIT HARVESTER","Bourbon - 115 W 20th St - Paris",801,"Paris - Bypass Rd, S Main, US 27/66, Bethlehem Rd - SW of Sub",36.140610978449999,1846,"2020-07-30",0.14731895052362803,0,0,0,1.1434703770861858E-2,5.4028050179476738E-3,0.20656477815194463,0.16652481219701734,0,0.46275395033860045,14.584335493824486,13.479749000541707,0.14897074756229683,0.16088840736728058,"Reliability Improvements Scheduled for 2026"]
["DETROIT HARVESTER","Bourbon - 115 W 20th St - Paris",802,"Paris - Bypass Rd, Cynthiana Rd - N of Substation",25.333617739878701,214,"2025-01-01",0.15604842272687108,0,0,0,9.7198904303260579E-3,0,6.0881859149951402E-2,0.69457453388707258,0,7.8775293805778912E-2,33.547694690654211,105.76417443457945,0.5682242990654206,1.2897196261682242,"Trees Trimmed in 2025"]
["PARIS 12KV","Bourbon - 520 Scott Ave - Paris",805,"Paris - Spears Mill Rd and WHY 460 - SE of Substation",83.190183932677101,887,"2021-07-17",1.3188083436958159E-2,0,0,1.6072064498426655E-2,0.23493937217950739,0,0.12099293015978657,0.2435504492355115,2.0024402916673963E-3,0.36925466019814235,331.81553549357386,193.00561816121757,1.8333709131905311,3.0890642615558082,"Continue to Monitor"]
["PARIS 12KV","Bourbon - 520 Scott Ave - Paris",806,"Paris - Cane Ridge Rd/KY 537, US HWY 68, & Bypass Rd - NE of Substation",115.690623595438,1058,"2021-12-11",3.2149197245469267E-2,0,0,2.916447201576247E-3,0.34264840717114375,1.1168334601353856E-2,0.27972532724683485,0.15989738787772381,0,0.17149489865589826,43.192199100189029,54.399464353497152,0.49187145557656003,0.67580340264650418,"Reliability Improvements Scheduled for 2026"]
["HANSON","Hopkins - 235 Fowler Rd - Hanson",810,"Hanson - Hanson Rd & Hwy 1069 - SW of Substation",22.081680943599999,895,"2019-08-03",7.3407991761828576E-3,0,0,0,0.11812581600191244,8.6059469299939323E-3,0.10287416560931208,0.35509828800500176,0,0.40795498427759697,85.566283043128493,205.29625696983237,1.1307262569832404,1.9787709497206709,"Continue to Monitor"]
["HANSON","Hopkins - 235 Fowler Rd - Hanson",811,"Hanson - US HWY 41 & City of Hanson - N of Substation",17.660659926569199,625,"2025-01-01",7.3302767497099922E-2,0,0,0,7.5756977927888831E-4,9.8105286416616033E-2,2.0556971614807334E-2,0.17373600271462505,0,0.6335414019775728,91.31876798367999,201.92674665759995,0.91936000000000018,1.5152000000000003,"Continue to Monitor"]
["DOZIER HEIGHTS","Hopkins - 200 Claire Ln - Madisonville",816,"Madisonville - Sandcut Ln, Mcleod Ln, Grapvine Rd - N&E of Subs.",21.518405534769801,822,"2025-01-01",2.8238687001191632E-2,0,0,0,4.0655698306680151E-2,8.2878543604738494E-2,4.9477784564853848E-2,0.74495558915714533,0,5.3793697365390587E-2,100.52799674282237,236.50419706326034,1.1598540145985405,1.860097323600973,"Trees Trimmed in 2025"]
["MORTONS GAP","Hopkins - 900 White Plains Rd - Mortons Gap",822,"Mortons Gap - Hwy 1215 & City of Mortons Gap - W of Substation",12.096127810023701,485,"2020-05-16",0,0,0,0,0,2.0538509705698184E-2,0.29411396368190357,0.57201001878522229,0,0.11333750782717596,17.584082465979378,32.54147765360824,0.22680412371134021,0.44123711340206184,"Continue to Monitor"]
["MORTONS GAP","Hopkins - 900 White Plains Rd - Mortons Gap",823,"Mortons Gap - Trabue Rd, Flat Creek Rd, & Old White Plains Rd - N/S of Substation",24.414294381216099,223,"2020-06-20",0,0,0,1.2231788984556513E-2,4.7833811671450045E-2,0,0.10520021866885336,6.4370643706437067E-2,0,0.77036353696870297,59.604872932735432,131.24760835426008,0.89058295964125556,1.2869955156950672,"Continue to Monitor"]
["EAST DIAMOND","Hopkins - 550 East Diamond Rd - Madisonville",825,"Madisonville - Randall Dr, Meadowlark Ln - W of Substation",9.6920147198434403,308,"2019-11-16",0,2.1288284576294466E-3,0,6.2834775442933657E-2,0,4.5323444581788219E-2,0.42549100398296941,6.5512978986402973E-2,0,0.39870896854827631,37.634426397402599,94.559469678571404,0.35064935064935066,0.81818181818181823,"Continue to Monitor"]
["ONTON","Webster - 6294 S R 370 - Onton",832,"Onton - KY 147, Harry Ashby Rd, Hwy 41 & Main St - SW of Substation",17.541860769289698,329,"2025-01-01",1.2383482685639663E-2,0,0,0,0.58955509524023952,3.2534786328635113E-3,1.0469671725131715E-3,2.7525104696717248E-2,0,0.36623587157202686,98.037487324620059,269.99468083282676,1.0407294832826748,2.6778115501519761,"Continue to Monitor"]
["WHITE PLAINS","Hopkins - 336 NW Railroad - White Plains",837,"White Plains - City of White Plains, HWY 813, White Plains Rd - W/SE of Substation",40.833895313962202,493,"2022-07-22",2.0216888195288048E-3,0,0,0,3.7560850173350951E-2,2.4561745746029774E-3,0.5308706562508313,0.41654770032896782,0,1.0542929852718196E-2,89.730466511561858,181.69259631845838,1.2004056795131848,1.6896551724137936,"Continue to Monitor"]
["FIES CITY","Hopkins - 2436 Central City Rd - Madisonville",841,"Madisonville - Central City Rd & Fies Ln - NW & SE of Substation",0.75788429013939396,17,"2023-09-09",0,0,0,0,0,0,1,0,0,0,43.899803905882351,48.46764705882353,0.623529411764706,1.1764705882352942,"Continue to Monitor"]
["SYLVANIA","Clark - 439 E Washington St - Winchester",847,"Winchester - E Washington, E Broadway St, Hickman St - SW of Subst.",14.3099503525294,1516,"2024-01-01",0,0,0,3.2437827497296848E-3,6.894193536462521E-3,1.9924773813154419E-2,0.89612501963828595,7.8645558974927681E-3,0,6.5947674364874725E-2,33.902594541029025,70.09917545448549,0.37757255936675471,0.61147757255936674,"Reliability Improvements Scheduled for 2026"]
["CYNTHIANA","Harrison - 208 McIlvain Blvd - Cynthiana",851,"Cynthiana - S Walnut St, Oddvill Rd - NNE of Subst.",3.2035877626737701,458,"2020-06-13",0,0,0,0.54214813411630991,0,5.2977205278777549E-2,0.23426153943297343,0,0.13916777167392813,3.1445349498010984E-2,7.741630275109169,34.576637550218337,0.10917030567685589,0.48908296943231439,"Continue to Monitor"]
["CYNTHIANA","Harrison - 208 McIlvain Blvd - Cynthiana",852,"Cynthiana - Main St, N Poplar St, W Pleasant St - NNW of Subst.",3.9247297136294201,544,"2020-06-13",0,0,0,4.3414583115388636E-3,0,0,0.27633643686578097,0.57171252223035884,0,0.14760958259232138,9.0824019588235299,34.987745091911769,9.7058823529411767E-2,0.31066176470588236,"Continue to Monitor"]
["CYNTHIANA","Harrison - 208 McIlvain Blvd - Cynthiana",853,"Cynthiana/Berry - River Rd, Poplar St, US 27, City of Berry - N of Subst.",77.154888488382895,926,"2022-10-07",1.1415525114155251E-2,8.661780020828326E-3,0,0,0.31560922855082912,7.0896419130016819E-3,0.17386645838340142,0.22921172795001202,0,0.25414563806777218,46.054132455507563,80.280453530237608,0.38164146868250515,0.73974082073434011,"Continue to Monitor"]
["KAWNEER","Harrison - RR 7 Box 729 White Oak Pike - Cynthiana",856,"Cynthiana - Western Ave, Ladish Rd, Hwy 27 - S of Substation",14.1068716365477,462,"2020-11-21",3.4439311213775727E-2,0,0,0,2.624947501049979E-2,0.28832423351532971,0.4269214615707686,0,0,0.22406551868962621,6.3806421298701306,7.3796897467532467,9.8268398268398283E-2,9.5238095238095233E-2,"Continue to Monitor"]
["ASHLAND PIPE","Fayette - 900 Forest Lake Dr - Lexington",862,"Lexington - No Road - NE of Substation",5.0065439041293699E-3,1,"-",0,0,0,0,0,0,0,0,0,0,239.97333320000001,357.05,0.6,1,"Continue to Monitor"]
["RACE STREET","Fayette - 420 Corral St - Lexington",863,"Lexington - Midland Ave & Main St. - W of Substation",1.91831363173367,99,"2024-01-01",0,0,0,0,0.47134880987364092,0,0.52865119012635908,0,0,0,43.160033668686864,171.86666666666667,0.37373737373737376,0.90909090909090917,"Continue to Monitor"]
["WEST HICKMAN","Fayette - 3172 Ashgrove Rd - Lexington",865,"Lexington - Saron Dr, Tates Creek Rd, Kenesaw Dr - NE of Subst",24.5453229688368,1296,"2024-01-01",6.3569057070502919E-4,0,0,0,5.8227874340557401E-2,5.2168084878510552E-4,0,0.82895777839964901,0,0.11165697584030347,81.841195984876549,223.34191100462965,0.75586419753086431,0.63040123456790131,"Reliability Improvements Scheduled for 2026"]
["MACKVILLE","Washington - 4685 Texas Rd - Springfield ",866,"Springfield - Texas Mackville Rd - S of Substation",9.9228610281786302,49,"2020-09-19",0,0,0,0,0,0,0,0.98499568521559999,0,1.5004314784399966E-2,182.37047617959183,117.37482991836735,1.1102040816326531,1.4285714285714286,"Tree Trim Scheduled for 2026"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",873,"Lexington - Bryant Rd & I75 - E of Substation",33.235476895115198,2076,"2022-09-03",1.5274111040153794E-3,0,0,0.18122206055658335,0.63619964316516453,0,2.2312052722017764E-2,0.14498554884752882,0,1.3753283604690206E-2,56.218482657321772,28.812572253371876,0.72263969171483622,1.1001926782273601,"Reliability Improvements Scheduled for 2026"]
["CARLISLE","Nicholas - 104 S Elm St - Carlisle",878,"Carlisle - Old Paris Rd, Concrete Rd - NW of Subst.",14.472529443134,201,"2025-01-01",0.1716779825412221,0,0,0,9.1416100872938902E-2,4.7769156159068862E-2,0.53782735208535404,0,0,0.1513094083414161,13.375638456716416,20.502902119402986,0.17910447761194032,0.21393034825870649,"Continue to Monitor"]
["CARLISLE","Nicholas - 104 S Elm St - Carlisle",879,"Carlisle - City of Carlisle, Hwy 36 - E of Substation",35.591772997776999,1091,"2019-10-21",0.37259433110669798,0,0,5.9938617078895105E-3,0.19815851236685322,1.1518324607329843E-2,0.10250947824517062,7.3659505325871094E-3,0.20140819642534755,0.10045134500812421,20.5019278852429,24.753605243813016,0.24766269477543532,0.27772685609532527,"Reliability Improvements Scheduled for 2026"]
["CYNTHIANA SOUTH","Harrison - 460 Education Dr - Cynthiana",880,"Cynthiana - New Lair Rd, Old Lair Rd, Ruddles Mill Pike, & Lake Rd - SE of Subst.",21.32057314999,227,"2020-10-03",1.1089069464387985E-2,0.30016849409440649,0,0,6.897467608462886E-3,9.2173739821877668E-2,0.58350417915155339,3.0544742237236366E-3,0,3.1125756355879449E-3,133.89543316211453,371.42224664757708,0.73303964757709261,0.92070484581497802,"Continue to Monitor"]
["CYNTHIANA SOUTH","Harrison - 460 Education Dr - Cynthiana",881,"Cynthiana - New Lair Rd, Hwy 27 - S of Substation",36.0160948050953,508,"2020-11-07",9.1662998253361928E-3,0,0,0,5.3045256386589225E-2,2.5560557220147398E-4,6.7423069822922135E-2,0.28693145510572132,0,0.58317831328722969,85.22545274448818,124.95160758661416,0.57440944881889755,0.69094488188976366,"Continue to Monitor"]
["DETROIT HARVESTER","Bourbon - 115 W 20th St - Paris",883,"Paris - Lexington Rd and Hutchison Rd - SW of Sub",55.859278796675497,749,"-",3.4573702886736356E-2,0,0,0.20518845305456987,2.5630574470125636E-2,0,4.1502829193440109E-2,5.2124292701639971E-2,0.39644672484894983,0.24453342284453822,59.284232295327094,31.708589218958604,0.63578104138851821,0.67690253671562128,"Continue to Monitor"]
["MAYSVILLE WEST","Mason - 210 Cox Alley - Maysville",901,"Maysville - Maddox Aly, 4th St, Plum St, Mulberry St- SE of Subst.",1.97050223666311,392,"2019-09-07",0,0,0,0.16751753837605057,0,8.7865527540459815E-3,0,3.2315760227825244E-2,0,0.79138014864207817,32.484132650510205,146.90943877551021,0.4816326530612246,2.181122448979592,"Continue to Monitor"]
["MAYSVILLE WEST","Mason - 210 Cox Alley - Maysville",902,"Maysville - Washington St, E 6th, Edgemont Rd - SW of Subst.",3.98561851336075,166,"2024-01-01",0,0,0,0,0,0,0.25367810967454302,0.73010983666355933,0,1.6212053661897621E-2,122.49919677951807,212.58935742771084,1.1240963855421686,2.3734939759036147,"Continue to Monitor"]
["MAYSVILLE WEST","Mason - 210 Cox Alley - Maysville",903,"Maysville - W 2nd St, W Mcdonald Pkwy - NW of Subst.",3.3095629441400698,356,"2024-01-01",0,0,0,0,0.55476946577159625,0.26631024641234874,0.17051895324998995,8.4013345660650402E-3,0,0,41.168089882584269,59.495084261235952,0.49775280898876401,0.91011235955056169,"Continue to Monitor"]
["MAYSVILLE MID","Mason - 314 Lexington St - Maysville",906,"Maysville - E Reynolds dr, Elizabeth St, Center St, Union St - E of Subst.",1.2869084759040099,75,"2025-01-01",0,0,0,0,0,0,0.98454122340425532,1.5458776595744681E-2,0,0,18.763866663999998,80.214666666666673,0.13333333333333333,0.44,"Continue to Monitor"]
["MAYSVILLE MID","Mason - 314 Lexington St - Maysville",907,"Maysville - Buckley Pl, Hwy 11, Bank St - W & S of Subst.",6.7858356306935699,226,"2025-01-01",0,0,0,0,8.9580686149936473E-2,0,0.58150833395620005,0.31452275954854625,0,1.4388220345317289E-2,31.088628312389375,118.39439527433629,0.27699115044247791,0.89823008849557529,"Trees Trimmed in 2025"]
["MAYSVILLE MID","Mason - 314 Lexington St - Maysville",908,"Maysville - Forest Ave, Wood St - E of Substation",1.3645291786823499,172,"2025-01-01",0,0,0,0,7.098765432098765E-2,0,0,0.92901234567901236,0,0,8.6740891430232558,9.4166666627906963,0.10232558139534884,0.11046511627906977,"Trees Trimmed in 2025"]
["MAYSVILLE EAST","Mason - 1107 Forest Ave - Maysville",912,"Maysville - Clark St - SE of Substation",0.59258478190138597,49,"2019-10-12",0,0,0,0,0,0,0.54591836734693877,0,0,0.45408163265306123,5.8067346897959187,8.0112244897959179,6.9387755102040816E-2,0.12244897959183673,"Continue to Monitor"]
["MAYSVILLE EAST","Mason - 1107 Forest Ave - Maysville",913,"Maysville - Bryant ln, Hwy 10, Buckner St - E of Substation",10.297973973068601,835,"2024-01-01",0,0,0,0,0.21734765959028887,2.0262482804773767E-2,0.64352901810610852,8.9898501691638474E-2,0,2.8962337807190392E-2,24.573281432814376,32.213293405988026,0.2639520958083833,0.41916167664670662,"Reliability Improvements Scheduled for 2026"]
["BEAVER DAM NORTH","Ohio - 129 Raines Ave. - Beaver Dam",919,"Beaver Dam - US Hwy 231 - NE & SE of Substation",17.243024693517501,808,"2024-02-01",5.4904034092729662E-2,0,0,0,0.16492037553269889,1.414656028709667E-2,3.4252939857092504E-2,0.71448941010605915,0,1.7286680124323113E-2,45.601328369801976,74.636262362623768,0.41039603960396054,0.51608910891089121,"Continue to Monitor"]
["KENTON","Mason - 801 Kenton Station Rd - Maysville",924,"Maysville - Old US 68, Clarks Run Rd, Slack Pike - S&W of Subst..",34.276767818022499,541,"2022-04-29",2.2898496751433042E-3,0,0,0,6.8846469353759125E-3,8.8876363215452201E-3,3.9430708142302831E-2,0.18428508880087366,0,0.75822207012475906,98.940837943807765,311.83348735489841,0.68909426987060995,1.7837338262476896,"Continue to Monitor"]
["AUGUSTA","Bracken - 318 E 4th St. - Augusta",929,"Augusta - 5th Street, Old August-Brooksville Rd - W&SW of Subst.",22.722076472491501,663,"2024-01-01",8.2730055165588401E-2,0,0,0,2.474204131004527E-2,1.3012480985283067E-2,0.38427139270201416,0.33592361123838499,0,0.15932041859868409,60.646118643740579,76.8085469939668,0.7628959276018098,0.73152337858220207,"Continue to Monitor"]
["SHARON","Bracken - 3061 Asbury Rd - Augusta",935,"Augusta - Mt Zion Rd, City of Brooksville, Hwy 10&19 - NW&SW of Subst",79.124815573231103,1222,"2025-01-01",2.9454266972996371E-2,0,0,0,0.10159824193387273,6.2045083741217991E-2,0.19434954882962074,0.10633969300436188,0,0.50621316551793027,105.21546916432078,222.76220674549913,0.88690671031096602,2.4672667757774152,"Continue to Monitor"]
["SHARON","Bracken - 3061 Asbury Rd - Augusta",936,"Augusta - Dutch Ridge Rd, KY 1235, City of Dover - N&NE of Subst",54.724814912618299,633,"2019-02-16",6.0187921405912646E-3,0,0,0,0.1441856538048657,5.0297321094720593E-3,0.13732254212551412,0.13942127926471831,0,0.56802200055483854,197.14077407772515,129.79523431595578,2.3137440758293848,3.2938388625592432,"Reliability Improvements Scheduled for 2026"]
["SHARON","Bracken - 3061 Asbury Rd - Augusta",937,"Augusta - Woodward Rd, Clarks Run Rd - S&SE of Substation",46.5868903790738,575,"2019-03-16",3.3422414667974694E-2,0,0,0,3.0716146273806706E-2,4.9727681742836843E-2,0.33824972091607186,0,0.54592199181353807,1.9620445857717939E-3,54.411617364173921,51.407623163478263,0.46504347826086967,0.49043478260869589,"Continue to Monitor"]
["SARDIS","Mason - 4000 Blue Lick Rd - Mays Lick",940,"Mays Lick/Mt Olivet - Hwy 62, Brierly Ridge Rd - W&NW of Subst.",22.4653648548131,485,"2019-11-30",0.14051498413227118,0,0,0,3.0902748864277715E-3,0.24321573634588872,7.6072575198230963E-2,0,0.16420092338153791,0.37290550605564343,114.88327146144329,221.14336767422677,2.0024742268041238,3.7731958762886593,"Continue to Monitor"]
["SARDIS","Mason - 4000 Blue Lick Rd - Mays Lick",941,"Mays Lick - Hwy 62 - NE of Substation",5.6707131253200096,46,"2019-11-30",0.18867924528301888,0,0,0,6.4203354297693915E-2,0,0.7471174004192872,0,0,0,21.148695634782605,82.934057956521727,0.46521739130434775,2.0869565217391304,"Continue to Monitor"]
["CARNTOWN","CALDWELL - 181 FREDONIA QUARRY - FREDONIA",945,"Central City - E Reservoir St, N 2nd St, Whitmer St - N of Subst.",1.1973625790322699,1,"2018-01-27",0,0,0,0,0,0,0,1,0,0,19.82,14.15,0.4,1,"Continue to Monitor"]
["CARNTOWN","Pendleton - 15125 Hwy 8 - Foster",947,"Foster - Hwy 8 - NNW of Substation",46.013034223809598,681,"2025-01-01",1.5720069404279932E-2,0,0,1.1208791208791209E-2,8.0855986119144019E-2,0,7.4783111625216891E-2,0.68618854829381137,0,0.13124349334875651,79.749255980910419,101.32342141850216,0.72187958883994141,1.0396475770925113,"Trees Trimmed in 2025"]
["FLEMINGSBURG","Fleming - 523 Fountain Ave - Flemingsburg",960,"Flemingsburg - City of Flemingsburg - S of Substation",10.634236937691901,966,"2024-01-01",8.2273747195213166E-3,0,0,0,1.7389678384442782E-2,2.4027673896783844E-2,3.4872849663425583E-2,0.90554880329094989,0,9.9336200448765892E-3,30.162184261697725,44.06452725776397,0.32380952380952382,0.57453416149068326,"Reliability Improvements Scheduled for 2026"]
["WEDONIA","Mason - 6964 KY Hwy 11 - Maysville ",965,"Maysville - Hwy 11 - N of Substation",32.827884021613997,390,"2022-03-18",7.3644456433773944E-2,0,0,0,2.4817912058268141E-2,1.8545994065281898E-2,0.77276099271648235,9.7181008902077148E-2,0,1.3049635824116536E-2,32.093546995384614,75.521111094871799,0.49692307692307702,1.4794871794871796,"Continue to Monitor"]
["WEST HIGH STREET","Fayette - 727 West High St - Lexington",1102,"Lexington - West High St - SE of Substation",2.6031666560040301,29,"2024-05-11",0,0,0,0,0,0,3.4888791975577847E-3,0,0,0.9965111208024422,75.906436779310354,158.13448275862072,0.35172413793103446,0.34482758620689657,"Continue to Monitor"]
["VINE STREET","Fayette - 112 E Vine St. - Lexington",1202,"Lexington - Water St - E of Substation, Ayers Aly - E of Subst.",1.0235732933466499,21,"2024-05-11",0,0,0,0,0,0,0,0,0,1,5.8885714095238102,10.430952380952382,0.18095238095238095,4.7619047619047616E-2,"Continue to Monitor"]
["BARLOW","Ballard - 433 Oscar Rd. - Barlow",1312,"Barlow - N 6th St - City of Barlow",6.3267671144711901,332,"2024-01-01",0.24699202379342977,0,0,0,1.6222793024199E-2,7.7463836690550222E-2,0.35433283763687984,7.1921049073948903E-2,0.2330674597809923,0,28.230140554216867,43.701004003012045,0.42590361445783131,0.42168674698795183,"Continue to Monitor"]
["BARDWELL","Carlisle - US Hwy 62 - Bardwell",1313,"Bardwell - US Hwy 62 - N of Substation",5.8453836813398601,27,"2021-11-13",0,0,0,0,0,7.7510411846367418E-3,0,0.77961591855622392,0.15386395187413235,5.876908838500694E-2,318.90296294074074,320.16111107407409,1.3111111111111111,1.6296296296296293,"Continue to Monitor"]
["FORRESTDALE","McCracken - 4250 Rice Springs Rd - Kevil",1320,"Kevil - SR 1154, SR 996, & Cairo Rd - E of Substation",41.755743671404304,943,"2025-01-01",8.2965744625418877E-3,0,0,0,8.3338573905543931E-2,4.1325655146391639E-4,2.3492736566916118E-2,0.30811869446865087,0,0.57634016404488331,70.791707307529137,173.17416046765632,0.77179215270413537,1.2778366914103911,"Trees Trimmed in 2025"]
["WICKLIFFE CITY","Ballard - Mayola Ave - Wickliffe",1324,"Wickliffe - Hwy 1290, Hwy 286, Hwy 21/Court St, & Beech Grove Rd - S of Substation",11.8196098017519,285,"2023-12-09",5.3678237308931037E-2,0,0,0,4.0906224971456809E-2,8.3499480258337165E-4,0,0.54648705758055993,0,0.35809348533646884,218.63447952210527,390.05245613333335,1.5726315789473686,2.4210526315789478,"Continue to Monitor"]
["GREENVILLE NORTH","Muhlenberg - 501 HWY 189 Bypass - Greenville",1327,"Greenville - HWY 601, S R 181, & Luzerne Depoy Rd - NW of Substation",43.6973548940746,804,"2022-01-01",9.1324200913242004E-3,0,0,0,1.4924458337164047E-2,7.6920719561153501E-3,4.1003953295945576E-2,0.88535441757837641,2.1758450553154974E-3,3.9716833685758943E-2,70.751791033084572,34.075808447761197,0.66417910447761208,0.7512437810945275,"Continue to Monitor"]
["GREENVILLE NORTH","Muhlenberg - 501 HWY 189 Bypass - Greenville",1328,"Greenville - S R 176 & Paradise Rd/St - SE of Substation",44.165345615661799,988,"2022-02-11",1.7227495945470836E-2,0,0,0,1.5458246855613396E-2,1.9926734941535389E-2,0.15814364941648804,0.45298447370510242,0,0.33625939913578989,41.54862684068825,78.284024938259108,0.5621457489878543,1.3724696356275301,"Reliability Improvements Completed in 2025"]
["CABIN","Livingston - 900 Three Rivers Rock Rd - Burna",1330,"Burna - 900 Three Rivers Rock Rd - S of Substation",1.24972977577703,2,"2022-04-23",0,0,0,0,0,0,0,0,0,1,120.6233332,224.64166650000001,0.4,0.5,"Continue to Monitor"]
["CHRISTIAN","Webster - 1678 S R 493 - Wheatcroft",1404,"Wheatcroft - City of Wheatcroft - NW of Substation",10.8606633760853,200,"2025-01-01",0,0,0,0,6.9896360568811764E-3,0,2.0125331405157869E-2,0.89696312364425168,0,7.5921908893709325E-2,14.356766661999998,41.491749989999995,0.14599999999999999,0.29000000000000004,"Trees Trimmed in 2025"]
["CLAY KU","Webster - 62 W College St - Clay",1407,"Clay – Main St, Taylor St, & Lisman St- NE & SW of Substation",10.9725951801835,439,"2025-01-01",0,0,0,0,2.0690991907738529E-2,0,0.96044321687583789,1.2469512687567637E-2,0,6.3962785288559382E-3,35.883227029157176,141.02760060364466,0.27562642369020507,1.0546697038724375,"Continue to Monitor"]
["CLAY KU","Webster - 62 W College St - Clay",1408,"Clay - S R 270, W Elm St - W & E of Substation",16.977479665353702,339,"2025-01-01",0,0,0,0,1.5834476934445266E-3,0,0.95224321756571306,4.4737675498786024E-2,0,1.4356592420563708E-3,80.930088491445417,139.71996066371679,0.46076696165191738,1.0560471976401178,"Continue to Monitor"]
["DIAMOND","Webster - 830 Bill Dorris Rd - Providence",1410,"Providence - Bill Dorris Rd, S R 109 - SW of Substation",6.6014136297338402,125,"2025-01-01",1.403428045553894E-2,0,0,0,0.96767514091798001,1.8290578626481077E-2,0,0,0,0,20.524799992000002,18.132266655999999,0.22879999999999998,0.248,"Continue to Monitor"]
["CORYDON","Henderson - 5430 Greenlick Rd - Corydon",1428,"Corydon - Hwy 266, Hwy 136 - NW of Substation",12.720992271016399,220,"2020-09-05",1.5915814702467887E-4,0,0,0,1.778826349099352E-4,1.5260457626483917E-3,1.0891410453257437E-3,0.99656717722103627,0,4.8059518905491268E-4,6.1043030190909082,10.801515131818181,5.9090909090909097E-2,8.6363636363636379E-2,"Tree Trim Scheduled for 2026"]
["CORYDON","Henderson - 5430 Greenlick Rd - Corydon",1431,"Corydon - City of Corydon - E of Substation",14.5114761402843,427,"2024-01-01",0,0,0,0,0.12042200637687583,6.3399441100072632E-4,4.8811414361512231E-3,0.79294850488114144,0,8.1114352894830793E-2,24.647736139578456,43.986065566744728,0.33021077283372369,1.2388758782201406,"Continue to Monitor"]
["MANITOU","Hopkins - 7615 Nebo Rd - Nebo",1451,"Nebo - US 41 ALT & Happy Ln - E of Substation",8.4255926781136505,135,"2025-01-01",3.5140617290718712E-2,0,0,0,2.7355956362041554E-2,2.3299161230195712E-2,0.27076366427279203,7.5105531494983821E-3,0,0.63593004769475359,16.861432075555555,50.097036992592599,0.21185185185185187,0.56296296296296311,"Continue to Monitor"]
["SENTRY","Hopkins - 1000 John Hardy Rd - Madisonville",1454,"Madisonville - Pleasant View Rd & Austin Powder Rd - SE of Substation",6.1633180421703404,72,"2025-01-01",0,0,0,0,0,0,1.3716668495555799E-2,0.98628333150444425,0,0,85.62069443055556,126.56365740277778,0.61111111111111105,0.81944444444444442,"Trees Trimmed in 2025"]
["AIRLINE ROAD","Henderson - 1830 Clay St - Henderson",1461,"Henderson - Clay St - E of Substation",11.566803648489101,832,"2025-01-01",5.5423332436515659E-3,0,0,0,8.2369254330594591E-4,0.68119994205178092,5.921066247231938E-3,0.28941410211304042,0,1.709886380098926E-2,23.731454321153848,45.355548871394241,0.28557692307692306,0.82692307692307687,"Trees Trimmed in 2025"]
["SEBREE","Webster - 199 N Railroad St - Sebree",1472,"Sebree - SR 56, College St, Jefferson St, & Old Beech Grove Rd - W/E of Substation",12.040131589838801,432,"2020-03-28",2.4258760107816711E-2,0,0,0,0.16480554485945323,0,0,0.3022718521370813,0,0.50866384289564881,6.6551466004629631,5.3221450555555556,7.5925925925925924E-2,7.8703703703703706E-2,"Continue to Monitor"]
["SEBREE","Webster - 199 N Railroad St - Sebree",1473,"Sebree - Railroad St, Dixon St, State St, & Church St - S of Substation",5.6063047278086904,328,"2020-03-28",0,0,0,0,0,0.18296622613803232,0.78120411160058745,0,0,3.5829662261380325E-2,7.6325203225609757,10.382876012195123,8.0487804878048783E-2,0.1524390243902439,"Continue to Monitor"]
["EARLINGTON","Hopkins - 310-A McEuen - Madisonville",1476,"Madisonville - Railroad St - SE of Substation",32.826769147793698,996,"2020-03-28",1.8621146789304287E-2,0,0,0,3.6777619089921346E-2,1.021600530275593E-2,0.12634362678438421,0.66088329153540748,7.6520954769405292E-2,7.0637355728821433E-2,49.594722211646584,48.459103061244967,1.0654618473895587,1.6767068273092376,"Continue to Monitor"]
["EARLINGTON","Hopkins - 310-A McEuen - Madisonville",1477,"Madisonville - Hwy 2171, Airport Rd - NW&NE of Substation",27.0708349750788,258,"2020-04-04",8.9265352663300216E-3,0,0,0,2.7040234565890212E-3,5.1637074442091549E-2,0.44297116794266167,0.49115491122332627,0,2.6062876690014659E-3,52.083307471317845,75.176679558139554,0.68992248062015504,0.69767441860465129,"Tree Trim Scheduled for 2026"]
["EARLINGTON","Hopkins - 310-A McEuen - Madisonville",1478,"Madisonville - Hwy 1337 - W of Substation",14.2370195025063,149,"2025-01-01",3.383955100693298E-3,0,0,0,0.58382304390888085,4.3974909210960714E-2,0.10009904258831298,0.26680422581710134,0,1.9148233740508419E-3,103.36590602684564,290.87393734899337,1.0429530201342281,1.8724832214765101,"Reliability Improvements Scheduled for 2026"]
["PERDUE","McLean - S R 2110 - Island",1498,"Island - Old Island-Livermore Rd & Hwy 138 - NE & NW of Substation",8.8265078209915497,25,"2020-09-26",0.60856864654333009,0,0,8.7633885102239538E-3,5.2823758519961052E-2,0.32984420642648493,0,0,0,0,67.121333287999988,164.2913332,0.4880000000000001,1.4800000000000002,"Continue to Monitor"]
["KUTTAWA","Lyon - 3487 Lake Barkley Dr - Kuttawa",1501,"Kuttawa - Hwy 295, Lake Shore Dr, & Holley St - SW & SE of Substation",11.241132490071699,440,"2024-01-01",7.5194528769322025E-3,0,0,0,1.8920757877106668E-2,5.5479953941170316E-3,4.989706549426009E-3,0.96302208730241812,0,0,165.63499998818182,215.00863634999999,1.8118181818181818,2.524999999999999,"Continue to Monitor"]
["KUTTAWA","Lyon - 3487 Lake Barkley Dr - Kuttawa",1502,"Kuttawa - Mary Blue Rd, State HWY 93, & US HWY 62 - NE of Substation",7.2414339560631902,136,"2021-02-13",0.10967489228358794,0,0,0,0,0,0.75009792401096742,7.4813944379161765E-2,0,6.5413239326282804E-2,25.119485282352944,17.98688723529412,0.37352941176470583,0.52941176470588225,"Continue to Monitor"]
["EDDYVILLE PRISON","Lyon - 328 Water St - Eddyville ",1504,"Eddyville - No Road - At Substation",5.3175491046771502E-3,1,"2024-01-01",0,0,0,0,0,1,0,0,0,0,14.2533332,71.266666000000001,0.2,1,"Continue to Monitor"]
["EDDYVILLE","Lyon - 1765 S R 3305 - Eddyville",1506,"Eddyville - City of Eddyville - NW of Substation",27.2835158403566,1039,"2021-03-06",2.941546197360151E-3,4.0854808296668762E-4,0,0,0.16727844123192959,0.22065367693274671,6.5505971087366444E-2,6.5945945945945939E-2,0.14138906348208674,0.33587680703959771,82.21482193416746,142.05067370644849,1.9795957651588068,4.0125120307988453,"Continue to Monitor"]
["FREDONIA","Caldwell - 150 Wigginton Ln - Fredonia",1507,"Fredonia - City of Fredonia & Hwy 641 - S of Substation",11.013961307678899,254,"2021-10-16",0.31774177615331423,0,0,0,0.11167638051960881,0.11977674602390595,0.14694260594685368,0.29161315815469718,0,1.2249333201620072E-2,20.50618108897638,59.672047216535439,0.45433070866141723,1.7992125984251968,"Continue to Monitor"]
["FREDONIA QUARRY","Caldwell - 181 Fredonia Quarry Rd - Fredonia",1511,"Fredonia - Fredonia Quarry Rd - E of Substation",0.78721387160234302,2,"2021-11-13",0,0,0,0,0,1,0,0,0,0,80.715000000000003,45.424999999999997,0.3,0.5,"Continue to Monitor"]
["FREDONIA QUARRY","Caldwell - 181 Fredonia Quarry Rd - Fredonia",1513,"Fredonia - Beck Rd & New Bethel Church Rd - S of Substation",12.0067230716573,73,"2021-11-13",0,0,0,0,5.7589285714285711E-2,0,6.6517857142857142E-2,0.84687500000000004,0,2.9017857142857144E-2,78.004977136986298,80.404794465753426,0.94794520547945216,1.1232876712328768,"Continue to Monitor"]
["CEDAR BLUFF","Caldwell - 10195 Hopkinsville Rd - Princeton",1514,"Princeton - Hopkinsville Rd - SSW of Substation",0.244058440720543,6,"2023-01-06",0,0,0,0,0,1,0,0,0,0,85.177222166666667,94.722222166666668,0.63333333333333341,0.83333333333333337,"Continue to Monitor"]
["CEDAR BLUFF","Caldwell - 10195 Hopkinsville Rd - Princeton",1515,"Princeton - Hopkinsville Rd, Sandlick Rd, Hwy 91 - E/NW of Subs",8.8795239116983105,83,"2023-01-06",1.66458193014529E-2,0,0,0,0.87068218993553348,5.6961416337919756E-2,2.2130279996151254E-2,0,0,3.3580294428942559E-2,111.5338152506024,123.31465861445785,0.82168674698795185,1.4216867469879517,"Continue to Monitor"]
["CLAXTON","Caldwell - 1600 Jones-Keeney Rd - Princeton",1519,"Princeton - Mt Hebron Rd, Dearing Cem. Rd - W & E of Subst.",12.2082525829708,57,"2023-12-16",0,0,0,0,5.5712555510698425E-2,0,0.28542591844973758,0.65886152603956394,0,0,34.303157866666666,32.847953210526313,0.44912280701754381,1.2280701754385965,"Continue to Monitor"]
["BARNHILL","Webster - 7390 Rabbit Ridge Rd - Providence",1520,"Providence - Hwy 109 - S of Substation",5.3146606799200704,30,"2022-12-09",0,0,0,0,0.88277133825079035,0,0.11722866174920969,0,0,0,114.39766664000001,253.0649999666667,1.42,2.9,"Continue to Monitor"]
["DAWSON SPRINGS 4KV","Hopkins - 205 Munn St - Dawson Springs",1525,"Dawson Springs - N Trim St, Sycamore St - NW of Substation",2.2853200726107099,155,"2022-10-01",0,0,0,0,0,0.23454367026496564,0.67517173699705602,0,0,9.0284592737978411E-2,5.8318064464516137,6.5711827806451613,0.30451612903225805,5.8064516129032261E-2,"Continue to Monitor"]
["DAWSON SPRINGS 12KV","Hopkins - 203 Parker St - Dawson Springs",1530,"Dawson Springs - Hospital Dr, Saddle Club Rd - NE & SE of Subst",12.4638833958672,299,"2022-09-09",4.6889594619839341E-3,0,0,0,8.5727629366710259E-2,3.8669904726321689E-3,2.0026153558752102E-2,0.55006538389688031,0,0.33562488324304129,66.559163867781493,80.551783715719068,0.68294314381270904,0.64214046822742465,"Continue to Monitor"]
["ST CHARLES KU","Hopkins - 660 St. Charles Rd - St. Charles",1553,"St. Charles - City of St. Charles & Mc Gregor Rd - SE of Substation",12.8866446505127,219,"2022-10-14",3.8789420537517477E-3,0,0,0,4.1750815597327946E-4,1.6506136398943607E-4,1.3622417275128165E-2,0.87505825695199635,0,0.1068578141991611,68.522724477625573,188.53462706392693,1.0502283105022827,2.3013698630136989,"Continue to Monitor"]
["ST CHARLES KU","Hopkins - 660 St. Charles Rd - St. Charles",1554,"St. Charles - Ilsley Rd, Union Temple Rd, & Hwy 112 - SW/NW of Substation",67.807077273403294,629,"2022-11-04",1.3188168995298276E-2,0,0,9.2000400146720465E-2,0.11670946013538298,0.26424689052652639,0.19667211310813965,0.25991196772149788,0,5.7270999366434358E-2,130.91215154181239,76.92628507790144,0.79618441971383169,0.84737678855325949,"Continue to Monitor"]
["GRAHAM","Muhlenberg - 5230 S R 175 S - Greenville",1602,"Greenville - Ford Ln, US HWY 62 McNary Rd - SW & SE of Substation",32.6613119966215,467,"2023-11-03",3.7325086499892829E-2,0,0,0,0.59554793471937295,4.562295232554579E-3,6.2616736581034324E-2,0.26148994151688659,0,3.8458005450258737E-2,62.050328320770873,66.090935023554579,0.73576017130620996,1.0214132762312638,"Continue to Monitor"]
["CALHOUN","McLean - 530 W First St - Calhoun",1606,"Calhoun - High St, W 7th St, S R 81 - N of Subst.",6.3185806540878504,328,"2024-01-01",0,0,0,0,0,0.10993762675544332,0.2096008877664256,0.66582481919412229,0,1.4636666284008724E-2,63.629857717682924,213.75813007621952,0.51158536585365844,1.1615853658536583,"Continue to Monitor"]
["CALHOUN","McLean - 530 W First St - Calhoun",1607,"Calhoun - State Hwy 81, W 2nd St, Walnut St - NE & S of Subst.",18.404217188052002,359,"2023-10-21",0,0,0,0,0,0,0.72787401574803157,0.18015748031496062,0,9.1968503937007867E-2,28.524531100835656,112.90835654038996,0.19554317548746517,0.67966573816155973,"Continue to Monitor"]
["SHAVERS CHAPEL","Muhlenberg - 7870 S R 181 N - Bremen",1609,"Bremen - S R 181, Buttermilk Rd, S R 175, & S R 81 - NW of Substation",94.816550255885303,1789,"2025-01-01",2.9095687860148998E-3,0,0,0,2.8920382241919229E-2,0.75959293783208748,1.9447572900021567E-2,0.14550492432220416,4.7042442877484077E-4,4.3154189488977819E-2,69.917115694242597,91.667868437115757,0.83801006148686363,1.1246506428172154,"Reliability Improvements Scheduled for 2026"]
["SHAVERS CHAPEL","Muhlenberg - 7870 S R 181 N - Bremen",1612,"Bremen - S R 181, HWY 70, & New Harmony Rd- S of Substation",44.378480411909003,803,"2025-01-01",4.7278601579901491E-3,0,0,2.9610815185742063E-4,1.5466715798685939E-2,0.32097794652286776,5.5681492911499854E-2,0.43719710603632922,0,0.16565277042076967,80.13085926400997,149.23972601369866,1.3494396014943961,3.5566625155666256,"Trees Trimmed in 2025"]
["GREENVILLE","Muhlenberg - 117 E Depot St - Greenville",1622,"Greenville - W Depot St, N Cherry St, & Short St - SE of Substation",4.88833795474733,416,"2021-10-30",2.7153982677438678E-3,0,0,0,0,5.9570799110917018E-3,7.2615908314717457E-3,0.98406593098969264,0,0,5.5506169841346154,7.1723157043269232,0.28653846153846152,0.22836538461538464,"Continue to Monitor"]
["CENTRAL CITY","Muhlenberg - 106 Pendleton St - Central City",1645,"Central City - Hwy 70, S Cherry Hill Rd - W of Substation",12.398351329313,418,"2024-03-01",4.3594316420137308E-3,1.8067163222249419E-3,0,0,1.7834038535510719E-3,2.0281847746267093E-3,1.4453730577799538E-3,1.4896667482603069E-2,0,0.97368022286720057,61.703963307655513,205.05219296411485,0.73157894736842088,1.9952153110047843,"Continue to Monitor"]
["CENTRAL CITY","Muhlenberg - 106 Pendleton St - Central City",1648,"Central City - E Reservoir St, N 2nd St, Whitmer St - N of Subst.",12.503070464511101,744,"2024-03-01",2.7397260273972601E-2,0,0,0,1.4749004332793558E-2,0.12919602608429254,9.4752505580112917E-2,0.21751498971508601,0,0.51639021401374241,23.099336913172046,26.938888881720434,0.30241935483870969,0.44489247311827951,"Continue to Monitor"]
["CENTRAL CITY SOUTH","Muhlenberg - 500 E Second Ave - Central City",1651,"Central City - W 2nd Ave, Center St, W Reservoir St - W of Subst.",5.5678672011841899,414,"2024-01-01",0,0,0,0,0,6.9424207621235237E-4,1.7141779659564256E-3,0.99759157995783121,0,0,101.26241545362322,281.82403380917879,1.0154589371980678,2,"Continue to Monitor"]
["DRAKESBORO","Muhlenberg - 201 S Mine St - Drakesboro",1673,"Drakesboro - Simmons St, S R 176, Merle Travis Hwy - SW of Subs",20.3104532388917,303,"2023-09-01",6.9564810043565841E-3,0,0,0,4.3964023047735043E-2,9.9545603597695227E-3,0.24352368014240877,1.7004731343982761E-2,0,0.67859652410174731,86.412739260726084,131.74889987458747,1.0066006600660067,2.1452145214521456,"Continue to Monitor"]
["DRAKESBORO","Muhlenberg - 201 S Mine St - Drakesboro",1674,"Drakesboro - Broad St, SR 2107, & Big Springs Rd - NE of Substation",13.6169549907465,382,"2024-01-01",0,0,0,0,6.0306053220091967E-3,3.8947659371309394E-3,2.929869085609468E-2,4.9526346207000527E-2,0,0.91124959167776465,74.201125647643977,102.33071552617804,0.88481675392670134,1.0837696335078533,"Continue to Monitor"]
["NELSON","Muhlenberg - 2030 S R 1379 - Central City",1690,"Central City - S R 1379, US 62, & SR 2590 - NW/S/SE of Substation",30.815860113719602,319,"2025-01-01",1.1407545962442469E-2,0,0,0,4.9346558046811546E-3,4.5900913095911992E-3,6.3498314095149031E-3,0.96231941128694842,0,1.0398464226821886E-2,198.56235107523511,306.9237721630094,1.0539184952978058,1.9780564263322875,"Trees Trimmed in 2025"]
["REED MINERALS","Muhlenberg - 4661 S R 176 Drakesboro - Drakesboro",1693,"Drakesboro - S R 176 & P&M Haul Rd - NNE of Substation",5.6338772932166297,11,"2020-03-28",0,0,0,0,0.37019230769230771,0,0,0,0,0.62980769230769229,142.74515143636364,132.43787872727273,0.63636363636363635,1.3636363636363638,"Continue to Monitor"]
["DYCUSBURG","Crittenden - 9315 S R 70 - Dycusburg",1707,"Dycusburg - City of Dycusburg, S R 70 - N & SW of Substation",6.8265419114356103,90,"2021-08-28",4.3868264257185888E-3,0,0,0,0,0,0,0.27715576507562367,0,0.7184574084986578,35.251777764444441,122.67629628888886,0.27111111111111114,0.88888888888888884,"Continue to Monitor"]
["MEXICO","Crittenden - 2747 S R 70 - Crayne",1708,"Crayne - S R 70 & Ken Spar - NE of Substation",8.9275611785417404,120,"2021-09-11",0,0,0,0,1.0929722579971457E-2,2.7637578753176233E-2,0.45608966549479618,4.3405618016638239E-2,0,0.46193741515541786,26.023277764999996,90.849027758333321,0.37333333333333335,1.35,"Continue to Monitor"]
["MEXICO","Crittenden - 2747 S R 70 - Crayne",1709,"Crayne - S R 70 & Marion Rd - W of Substation",11.265081262912201,124,"2021-09-11",0,0,0,0,8.6953781512605036E-2,9.9369747899159672E-3,3.7815126050420167E-4,0.75063025210084033,0,0.15210084033613444,139.08586020161289,196.88924730645161,0.79838709677419373,0.92741935483870963,"Continue to Monitor"]
["MARION SOUTH","Crittenden - 505 Chappell Hill Rd - Marion",1710,"Marion - Hwy 60, N Main St, Sturgis Rd, & Old Fords Ferry Rd - N & W of Substation",26.6654341420899,905,"2022-03-04",3.7571804258137815E-3,0,0,0,1.2868288125072654E-2,4.6739938630526376E-3,0,0.82724208042076919,0,0.1514584571652918,60.248394097900551,87.932983416574601,0.5569060773480663,0.60331491712707175,"Continue to Monitor"]
["MARION 4KV","Crittenden - 106 Spar Mill Rd - Marion",1713,"Marion - E Gum St, S Main St, E Depot St - NW of Substation",1.4818041678251299,61,"2022-04-08",0,0,0,0,0,0,0.48421052631578948,0,0,0.51578947368421058,0.53579234754098359,1.5571038196721312,1.3114754098360656E-2,3.2786885245901641E-2,"Continue to Monitor"]
["MARION 4KV","Crittenden - 106 Sparmill Rd - Marion",1714,"Marion - E Depot St, E Bellville St, & Old Shady Grove Rd - N of Substation",8.3850732819241607,556,"2022-04-08",0,0,0,0.30702782636922687,0.24780436782023768,0.12755405673477485,3.2154514796847666E-2,0.28165407296532075,0,3.8051613135921805E-3,45.983483210071945,34.645923258992809,0.42014388489208632,0.72841726618705027,"Continue to Monitor"]
["STURGIS","Union - 1402 N Washington St - Sturgis",1725,"Sturgis - Cs 2047, 8th St, 3rd St, & 10th St - S of Substation",4.2236811709947499,380,"2020-02-15",0,0,0,0.20064464141821112,0,0,0.79935535858178897,0,0,0,7.5299736815789471,3.2669736815789476,6.2631578947368413E-2,7.3684210526315783E-2,"Continue to Monitor"]
["STURGIS","Union - 1402 N Washington St - Sturgis",1726,"Sturgis - Midway Dr, Waller Omer Rd, & S R 109 - W of Substation",10.956918297082,351,"2020-02-15",4.7782589219053304E-3,0,0,0,3.1954606540241903E-2,1.2990891443930119E-3,3.4343736001194564E-3,0.95609974615499482,0,2.4339256383455279E-3,42.690921174358962,186.28580246438742,0.31680911680911683,1.2820512820512822,"Tree Trim Scheduled for 2026"]
["UNIONTOWN","Union - 5668 S R 130 N - Uniontown",1742,"Uniontown - City of Uniontown, S R 130, & KY 268 - NW & S of Substation",13.709203818350399,624,"2020-03-15",8.0133348517947179E-4,2.3027466895816293E-2,0,0,2.7578709790969987E-2,3.230181490645933E-4,6.3775378148650465E-4,0.17908043358974624,0,0.76855128430773689,27.769497855769238,47.563301272435908,0.43493589743589733,1.2996794871794872,"Continue to Monitor"]
["MORGANFIELD","Union - 305 Rhea St - Morganfield",1750,"Morganfield - S R 947, N Chapman St, & Hedge Rd - NW of Substation",9.3452589662543897,290,"2025-01-01",0,0,0,2.3716963816162597E-4,1.5089488572891854E-3,4.7193320753030786E-3,3.1244521896944635E-3,8.3380595398909019E-2,0,0.90702950184064257,34.400206892413799,38.768448268965514,0.53517241379310343,0.38275862068965522,"Continue to Monitor"]
["CAMP BRECKINRIDGE","Union - 1820 S Route 2091 - Morganfield",1759,"Morganfield - Marshall Rd, Headquarters Rd, & Patton Rd - NE of Substation",11.067764409023701,259,"2025-01-01",6.4895831002304916E-4,5.4907840460685808E-2,0,0,6.2247782725774088E-2,0,1.2755387472866829E-2,0.77462498414900682,0,9.4815046881643425E-2,45.097104234749033,47.352187888030898,0.39459459459459462,0.40926640926640923,"Trees Trimmed in 2025"]
["CAMP BRECKINRIDGE","Union - 1820 S Route 2091 - Morganfield",1760,"Morganfield - Routes 56, 2835, and Road A - W and E of Substation",25.4315983307505,515,"2025-01-01",1.0878268952004306E-3,0,0,0,7.1835196156430788E-4,9.4414362919650149E-2,2.8904011184662799E-2,0.8414128618472716,0,3.3462585191650636E-2,70.250440117281556,61.239643992232999,0.70019417475728152,0.84854368932038804,"Trees Trimmed in 2025"]
["MORGANFIELD INDUSTRIAL","Union - 3324 U S HWY 60 E - Morganfield",1761,"Morganfield - Hwy 60 E - W of Substation",4.1122767201924102,43,"2020-01-18",0,0,0,0,0,0.99430254109957117,0,5.6974589004288173E-3,0,0,32.952868209302324,48.336046511627906,0.39534883720930231,6.9767441860465115E-2,"Continue to Monitor"]
["MORGANFIELD INDUSTRIAL","Union - 3324 U S HWY 60 E - Morganfield",1762,"Morganfield - US HWY 60, Blessed Martin Rd, & King Mill Rd - NE of Substation",22.3805118703003,230,"2020-01-18",4.8436414803322897E-3,0,0,0,4.4747309839717857E-2,9.2624496017750996E-2,8.3370164250859136E-2,0.77279984125122891,0,1.6145471601107634E-3,60.520246363546832,99.82876810434783,0.9391304347826086,0.77391304347826073,"Tree Trim Scheduled for 2026"]
["WAVERLY","Union - 178 Blessed Martin Rd - Waverly",1764,"Waverly - E Main St, S Maple St, & E Market St - S of Substation",3.9365927340824598,165,"2024-12-06",0,0,0,0,0.60682975484277391,0,1.4226468581027876E-2,0.30421544438028247,0,7.4728332195915792E-2,84.452161608484843,75.693434333333329,0.65575757575757576,1.1696969696969697,"Continue to Monitor"]
["BORG-WARNER","Hopkins - 1000 Island Ford Rd - Madisonville",1807,"Madisonville - Whittington Dr/St Malo Dr/Pin Oak St - NW of Subst.",13.662034305601599,512,"2023-01-27",1.9807331574094682E-2,0,0,0,0.21819858201125489,5.2840746510666711E-2,0.20770673703621276,0.49435665914221222,0,7.0899437255587706E-3,21.949088530078125,48.03707680273439,0.30625000000000002,0.455078125,"Continue to Monitor"]
["RIVERVIEW","Ohio - 25 Riverview Rd - McHenry",1907,"McHenry - Watts Rd, City of McHenry, & HWY 62 - E & S of Substation",24.257020650448801,519,"2024-01-01",0,0,0,0,3.7704140547674035E-2,1.4877515671395579E-2,0.13110359617288025,0.16281755196304848,4.7137908281095348E-2,0.60635928736390632,286.18610789248561,186.87983299807323,1.2666666666666666,2.4354527938342967,"Continue to Monitor"]
["HARTFORD","Ohio - 425 Walnut St - Hartford",1911,"Hartford - US HWY 231, Old Main St, HWY 1543- E of Substation",8.8057988064327901,399,"2023-03-03",0.39607765842120823,0,0,0,0.1627081896126934,6.0609047008968166E-2,1.1826155513945007E-3,0.1914851680299596,0,0.1879373213757761,28.469665820551377,23.20956557142857,0.418546365914787,0.59899749373433586,"Continue to Monitor"]
["BEAVER DAM","Ohio - 310 Ridgecrest Dr. - Beaver Dam",1916,"Beaver Dam - Main St. - S of Substation",33.610603263755301,941,"2025-01-01",1.6890351232360601E-2,8.664669203984128E-3,0,6.5340896982922114E-2,0.6618008703027306,2.1706424129803819E-2,0.14715020606825183,6.8358401063798049E-2,0,1.0088181016148761E-2,113.17691107268861,249.08487421572789,1.7294367693942605,3.4495217853347473,"Continue to Monitor"]
["ATOKA","Boyle - 20 Parksville Cross Pike - Danville",2100,"Danville - Parksville Cross Pike & Lebanon Rd - S of Substation",15.511268409312599,285,"2020-10-10",3.3071748878923765E-2,0,0,0,0.16208893871449925,1.6816143497757848E-3,0.49766442451420029,0.29054559043348283,0,1.4947683109118086E-2,17.54250291368421,37.558187119298239,0.36350877192982467,1.1824561403508775,"Tree Trim Scheduled for 2026"]
["ATOKA","Boyle - 20 Parksville Cross Pike - Danville",2101,"Perryville - City of Perryville & Perryville Rd - W of Substation",31.172197895525201,609,"2020-10-10",2.166337006687388E-3,0,0,0,0.1390694169727795,0,4.3279645850993691E-2,0.77823302251106719,1.817839314307243E-2,1.907318451539983E-2,18.930859324794746,26.943459213464699,0.20164203612479473,0.1954022988505747,"Tree Trim Scheduled for 2026"]
["BRODHEAD","Rockcastle - 77 Cass St. - Brodhead",2103,"Brodhead - Hwy 1505, City of Brodhead, & Hwy 150 - W of Substation",22.239900173086699,790,"2020-05-30",1.5117417670199791E-2,0,0,0,0.23816804384051127,2.061466045936335E-4,4.0765491058391029E-2,0.68358214083248869,0,2.2160759993815601E-2,58.071936703037977,71.308734168354448,0.36708860759493678,0.36962025316455704,"Tree Trim Scheduled for 2026"]
["BUENA VISTA","Garrard - 164 High Bridge Rd. - Lancaster",2105,"Lancaster - Rock Quarry Rd, Lexington Rd, & US 27 - E of Substation",20.488175293835301,356,"2022-10-15",1.4229559495333541E-3,0,0,0,3.0100991240128647E-3,0,0,0.81674774081597834,0.17881920411047547,0,191.66176028988764,286.61582396067416,1.3505617977528088,2.0393258426966288,"Continue to Monitor"]
["CRAB ORCHARD","Lincoln - 635 KY HWY 39 N - Crab Orchard",2107,"Crab Orchard - City of Crab Orchard - S of Substation",10.872739215667201,503,"2025-01-01",0,0,0,0,0,0,1.0863201717296558E-2,0.98422559032069212,0,4.9112079620113186E-3,17.721597079522862,16.376176270377734,0.17932405566600398,0.29025844930417494,"Trees Trimmed in 2025"]
["RICHMOND 3","Madison - 950 Vickers Dr - Richmond",2109,"Richmond - Lancaster Rd - SW of Substation",61.4391276420521,1402,"2025-01-01",5.766399399821822E-2,0,0,0.33130773198293245,0.11827261218174145,9.3121395414263609E-3,2.9746330941998404E-2,1.5660899329488442E-2,0,0.4380362920241947,42.50014977617689,69.830777447218267,0.67931526390870134,1.5378031383737507,"Continue to Monitor"]
["DANVILLE CENTRAL","Boyle - 494 S 4TH ST - Danville",2110,"Danville - S 3rd St, MLK Blvd, & E Walnut St - N of Substation",1.5518780339287701,143,"2020-10-17",0,0,0,0.42322097378277151,0,0.45131086142322097,0,0,0,0.12546816479400749,2.3513986,3.7325174825174825,3.9160839160839164E-2,6.9930069930069935E-2,"Continue to Monitor"]
["DANVILLE EAST","Boyle - 805 East Dr - Danville",2113,"Danville - Lexington Ave, Fork Church Rd, & Lancaster Rd - NW & E of Substation",48.527627367916601,1343,"2021-04-10",5.6329226169865975E-3,0,0,0,0.10482134261175061,1.7143677529959211E-2,3.0807948585857732E-2,0.83423837312411853,0,7.3557355313273263E-3,34.509761720178702,48.819533375279221,0.5614296351451975,0.36634400595681316,"Tree Trim Scheduled for 2026"]
["DANVILLE EAST","Boyle - 805 East Dr - Danville",2114,"Danville - Hill N Dale St, Lexington St, Shakertown Rd, & 4th St - N of Substation",31.632166266391,1844,"2024-01-01",5.4421768707482989E-3,0,0,1.9441979690426896E-3,0.14076703145026126,2.9340431824903873E-3,4.2985310066055412E-3,0.83443951493640944,0,1.0174504584442473E-2,21.972579533839479,20.392977220715832,0.23958785249457693,0.26518438177874187,"Reliability Improvements Scheduled for 2026"]
["DANVILLE NORTH","Boyle - 514 N Danville Bypass - Danville",2124,"Danville - Whirlaway Dr, War Admiral Dr, & Bluegrass Pike - W of Substation",6.73380822351589,425,"2024-01-01",0.55296979378449029,0,0,0,0,0,0,0.44528753993610226,0,1.7426662794074934E-3,26.734533332235294,60.198078430588232,0.31529411764705884,0.60941176470588243,"Tree Trim Scheduled for 2026"]
["DANVILLE NORTH","Boyle - 514 N Danville Bypass - Danville",2125,"Danville - Danville Byp, Perryville Rd & Gallant Fox - SW of Substation",4.66098966916742,223,"2020-12-26",0,0,0,0,0.81825795644891119,0,0.13539921831379118,4.6342825237297602E-2,0,0,5.465754856502242,16.064050820627802,9.8654708520179379E-2,0.39461883408071752,"Continue to Monitor"]
["HARRODSBURG CITY","Mercer - 231 N Chiles St - Harrodsburg",2126,"Harrodsburg - W Broadway St, Chiles St, & Hill St - W of Substation",3.8719221168786602,487,"2021-11-06",0,0,0,0,0,0,1,0,0,0,21.550130040657084,36.98863791786448,0.38398357289527713,1.0574948665297741,"Continue to Monitor"]
["HARRODSBURG CITY","Mercer - 231 N Chiles St - Harrodsburg",2127,"Harrodsburg - Factory St, N Main St, & Greenville St - N/E/S of Substation",2.2504659440179799,315,"2021-11-06",0,0,0,0,0,7.0977788705843786E-2,0.92902221129415619,0,0,0,25.071216924444439,68.294973520634912,0.50984126984126976,1.6031746031746033,"Continue to Monitor"]
["HARRODSBURG EAST","Mercer - 709 E Office St - Harrodsburg ",2128,"Harrodsburg - E Office St & Beaumont Ave - W of Substation",4.1925541151343397,451,"2021-11-06",0,0,0,2.2798634812286691E-2,4.9829351535836175E-2,0,0.90170648464163816,0,2.5665529010238906E-2,0,10.577560972505543,16.243495924611974,0.10864745011086474,0.15077605321507762,"Continue to Monitor"]
["HARRODSBURG EAST","Mercer - 709 E Office St - Harrodsburg ",2129,"Harrodsburg - Cane Run St, N East St, & Cogar Ave - W of Substation",1.0305371546970099,427,"2021-11-06",5.0744208014920494E-3,1.1626357922272952E-3,0,4.7522738007290698E-2,9.0576594688207723E-2,0,0.75589492679027748,7.6128422811883104E-2,0,2.364026110862167E-2,41.439180323185013,175.86288055035126,0.37658079625292751,1.5292740046838411,"Continue to Monitor"]
["HARRODSBURG EAST","Mercer - 709 E Office St - Harrodsburg ",2131,"Harrodsburg - Lexington Rd, Burgin Rd, & City of Burgin - NE/SE of Substation",1.3049144165764499,862,"2021-10-23",2.9451837049820611E-2,0,0,0.13449747944956628,1.5066533448385487E-2,1.0070847904082837E-2,2.252600027249194E-2,0.37771924247241018,0.40522957445842228,5.438484944820382E-3,45.797938893967519,60.395359622969828,0.61716937354988388,0.50232018561484904,"Continue to Monitor"]
["HARRODSBURG INDUSTRIAL","Mercer - 1020 N College St - Harrodsburg",2132,"Harrodsburg - Louisville Rd, Virginia Ave, & Sleepy Hollow Rd - N of Substation",25.9656806917403,851,"2021-12-18",4.2443087677886474E-3,0,0,0,2.9823645566172632E-2,0,6.3233391588551721E-2,0.88957988152250389,0,1.3118772554983091E-2,33.111276924559341,62.136545235017628,0.51750881316098707,1.1245593419506463,"Continue to Monitor"]
["HARRODSBURG INDUSTRIAL","Mercer - 1020 N College St - Harrodsburg",2133,"Harrodsburg - N College St, Lynn Dr, & Cornishville St - S of Substation",6.4995325400047097,498,"2022-03-05",0,0,0,0,0.41762452107279696,0,6.3026819923371641E-2,0.51934865900383143,0,0,16.427195444176707,41.128614451807223,0.32369477911646588,1.1847389558232932,"Continue to Monitor"]
["HARRODSBURG INDUSTRIAL","Mercer - 1020 N College St - Harrodsburg",2134,"Harrodsburg - Tapp Rd, Moberly Rd, & Mackville Rd - SW of Substation",20.484082581681399,1005,"2022-03-05",0.35441633377718595,0,0,0,1.4203284509542832E-2,0,0.13182423435419441,0.44940079893475365,0,5.0155348424323128E-2,42.532626861492545,33.603847427860693,0.82606965174129354,1.0248756218905473,"Reliability Improvements Scheduled for 2026"]
["HARRODSBURG INDUSTRIAL","Mercer - 1020 N College St - Harrodsburg",2135,"Harrodsburg - Crosses over N College St - E of Substation",0.20272470290591399,3,"2022-03-05",0,0,0,0,0,0,0,0,0,0,10.858888866666666,30.916666666666668,0.26666666666666666,1,"Continue to Monitor"]
["KENTUCKY STATE HOSPITAL","Boyle - 4180 Shakertown Rd - Danville",2136,"Danville - Shakertown Rd, Gwinn Island Rd, & Spears Ln - S of Substation",19.175897785795801,404,"2022-04-30",7.3404667441456604E-3,0,0,0,2.0371632001496148E-2,2.4512750637865855E-3,1.2597015722892371E-2,0.95623772692662201,0,1.0018835410571874E-3,77.510165005940578,303.82116335396034,0.50891089108910892,1.4826732673267327,"Continue to Monitor"]
["KENTUCKY STATE HOSPITAL","Boyle - 4180 Shakertown Rd - Danville",2138,"Danville - Shakertown Rd, Faulkner Ln, & Curdsville Rd - N of Substation",34.174063410135197,648,"2022-06-10",2.3917122545521818E-2,5.6819683395438565E-3,0,0.72789978593514626,2.8991252411533074E-2,0,3.1819022701445598E-2,0.1658341922355242,0,1.585665583128518E-2,31.025679003395066,50.278909452160505,0.31265432098765444,0.61574074074074114,"Continue to Monitor"]
["LANCASTER 1","Garrard - 104 Hamilton Ave - Lancaster",2140,"Lancaster - Danville St, Campbell St, & Waterworks Rd - NW of Substation",16.417572593460498,850,"2023-12-30",0,0,0,4.309987567343556E-2,6.1583091587235808E-2,0,1.4484044757563199E-2,0.62420223787815998,0.25663075010360548,0,13.377023527294119,19.036647058823526,0.10823529411764705,0.10352941176470588,"Continue to Monitor"]
["LANCASTER 2","Garrard - 183 Industry Rd - Lancaster",2142,"Lancaster - Hwy 39, Stanford Rd, & Deer Run Rd - NW of Substation",5.82455271785867,348,"2023-12-16",0,0,0,0,0,0,0,1,0,0,13.005565132758624,44.607662833333336,0.1,0.13218390804597702,"Continue to Monitor"]
["MOUNT VERNON","Rockcastle - 56 Old Somerset Rd - Mt. Vernon",2145,"Mt. Vernon - W Main St & N Hwy 461 - NW of Substation",5.4166071390211004,255,"2020-08-08",2.9159177151987219E-3,0,0,0,0.15006990213700819,0,1.9972039145196726E-3,0.84501697623327343,0,0,24.795032673725487,91.395686270588229,0.47450980392156861,1.9921568627450981,"Tree Trim Scheduled for 2026"]
["MOUNT VERNON","Rockcastle - 56 Old Somerset Rd - Mt. Vernon",2146,"Mt. Vernon - Poplar St, South City of Mt Vernon, & Mchargue Branch Rd - E of Sub",18.380553026088801,708,"2024-01-01",8.689634982101747E-3,0,0,0,0.38161869402637499,0,2.7166753163798952E-2,0.53932292706295659,1.1843453497810956E-3,4.2017645414986628E-2,88.019303191807893,202.55981637288136,0.90847457627118655,2.7951977401129944,"Tree Trim Scheduled for 2026"]
["PINE HILL","Rockcastle - 501 Flat Rock Rd - Mt. Vernon",2148,"Mt. Vernon - Mullins Station Rd, Skyline Rd, & Honeycomb Rd - NE of Substation",4.7449872963717796,52,"2020-07-25",1.3187641296156745E-2,0,0,0,0,0,5.0238633509168554E-3,2.1853805576488319E-2,0.95993468977643803,0,118.3639102423077,153.11089742307695,0.53461538461538471,0.69230769230769229,"Continue to Monitor"]
["PINE HILL","Rockcastle - 501 Flat Rock Rd - Mt. Vernon",2149,"Mt. Vernon - Wilderness Rd, Limestone - W of Substation",8.4678779708875407,85,"2020-07-25",7.2049020267995418E-3,0,0,0,0.11514376136287119,0,6.6965187529459291E-2,0.81068614908086989,0,0,198.85709801411767,181.27784310588234,1.2799999999999998,1.2941176470588236,"Tree Trim Scheduled for 2026"]
["RICHMOND 3","Madison - 950 Vickers Dr - Richmond",2153,"Richmond - No Road - W of Substation",1.0046434898641999E-2,2,"2024-01-01",0,0,0,0,0,0,0,0,0,0,50.339999999999996,251.7,0.2,1,"Continue to Monitor"]
["RICHMOND 2","Madison - 200 Fairview St - Richmond",2154,"Richmond - Big Hill Ave, Boggs Ln, & Richmond East - SE of the Substation",8.3207367735846596,962,"2025-01-01",0.67660728117738189,0,0,0,0.24767621998450814,0,7.5716498838109991E-2,0,0,0,11.465384614553013,8.0757969501039497,0.16694386694386693,0.16839916839916841,"Continue to Monitor"]
["RICHMOND 2","Madison - 200 Fairview St - Richmond",2162,"Madison - Big Hill Ave, Hallie Irvine St, & Gibson Ln - NW & S of Substation",4.2500037682336602,522,"2025-01-01",0,0,0,0,0,3.185756121369885E-2,0,3.6402830879362241E-3,0,0.96450215569836495,44.279648785440614,182.39722222030653,0.32950191570881227,1.0823754789272031,"Continue to Monitor"]
["MOUNT VERNON TAP","Rockcastle - 56 Old Somerset Rd - Mt. Vernon",2166,"Mt. Vernon - Richmond St and Williams St - NE of Substation",15.4300925534135,854,"2020-10-03",0,5.1352418969209338E-3,0,0,2.5239609971101272E-2,6.1851597746314887E-4,1.142435393667228E-2,0.11644212977400778,0,0.84114014844383456,58.604223257377043,196.10882122716626,0.40187353629976574,1.1381733021077276,"Continue to Monitor"]
["BARTON","Nelson - 500 Cathedral Manor - Bardstown",2202,"Bardstown - New Haven Rd - W/N/S of Substation",1.1637684741188199,7,"2023-09-16",0,0,0,0,0.46540880503144655,0,0.53459119496855345,0,0,0,35.979999971428569,68.119047571428567,0.45714285714285713,0.71428571428571419,"Continue to Monitor"]
["CAMPBELLSVILLE 1","Taylor - 101 Old Greensburg Rd. - Campbellsville",2205,"Campbellsville - HWY 3350 Bypass - N of Substation",17.4962961906282,1252,"2023-04-28",5.1481311721321719E-2,0,0,0,1.3229717904912704E-2,2.5417725738572441E-3,6.9648735363973494E-2,3.8522438434934789E-2,0.56544022667611149,0.25913579732488856,33.675700209105436,37.896978164536733,0.46948881789137387,0.52236421725239612,"Reliability Improvements Scheduled for 2026"]
["COLUMBIA","Adair - 114 Lindsey Wilson St - Columbia",2210,"Columbia - Guthrie St, Miller Ave, & Adair Ave - S & SE of Substation",2.1682409294518998,150,"2025-01-01",0,0,0,0,0,0,0,0.95585952426442489,4.4140475735575085E-2,0,32.652488884,49.29022221333333,0.41866666666666663,0.39999999999999997,"Trees Trimmed in 2025"]
["COLUMBIA","Adair - 114 Lindsey Wilson St - Columbia",2211,"Columbia - Burkesville Rd & Greensburg St  - W of Substation",4.3851699210201902,461,"2024-01-01",3.2940264629352819E-3,0,0,0,0,0,0.63571942645186297,0.31284947129491225,4.8137075790289544E-2,0,29.806854659436009,54.971221976138828,0.36095444685466377,0.35140997830802601,"Continue to Monitor"]
["GREENSBURG","Green - 424 Old Hodgenville Rd - Greensburg",2214,"Greensburg - Buckner Hill Rd, Hawthorne Rd, HWY 1464, & HWY 88 - SW of Substation",20.519782705543399,214,"2025-01-01",8.2035055337039559E-4,0,0,0,5.4345782641284632E-2,1.757894042936562E-4,1.5186251315368632E-3,0.94155734763087151,0,1.5821046386429059E-3,167.36091899345797,168.64228970560748,1.2719626168224296,1.1028037383177569,"Trees Trimmed in 2025"]
["LEBANON CITY","Marion - 351 E Water St - Lebanon",2217,"Lebanon - Woodlawn Ave, Hood Ave, & Danville Hwy - E of Substation",3.3296437206827898,259,"2019-09-21",0.23786209710322317,0,0,0,0,0,0.70991432068543447,0,0,5.2223582211342309E-2,21.928944652509649,9.4634491621621635,0.1374517374517375,0.15057915057915058,"Continue to Monitor"]
["LEBANON SOUTH","Marion - 1157 Bradfordsville - Bradfordsville",2218,"Bradfordsville - Bradfordsville Rd, Hwy 49, & Central Ave - SE of Substation",30.202317547204501,388,"2025-01-01",2.5273950503686532E-3,0,0,0,2.4927404610255367E-2,2.0733004313898879E-3,0.12522854104178865,0.67027353225864272,8.2155276459973947E-2,9.2814550147580749E-2,164.89026630515463,177.24587627061848,2.137628865979381,2.9639175257731951,"Trees Trimmed in 2025"]
["LEBANON SOUTH","Marion - 1157 Bradfordsville - Bradfordsville",2220,"Lebanon - Metts Dr, Hill Creek Rd, & Hamilton Hts - W of Substation",5.5621216878881796,163,"2025-01-01",0.19284901479307659,0,0,0,1.0181469725100316E-3,5.0607893633586871E-2,0.37707372581900939,0.36743127507935558,1.101994370246152E-2,0,27.10820039754601,64.791615521472394,0.29693251533742326,0.6380368098159509,"Trees Trimmed in 2025"]
["RUSSELL SPRINGS","Russell - 1183 HWY 1870 - Russell Springs",2223,"Russell Springs - Gran Von Hale Ave, Lakeway Dr, & US 127 - SE of Substation",15.0431100592867,461,"2019-02-16",1.0497346418588615E-2,0,0,0,0,0,1.7226730369038677E-2,0.97052739160951107,0,1.7485316028616814E-3,30.88585682906724,78.628488785249431,0.55097613882863328,1.3210412147505421,"Tree Trim Scheduled for 2026"]
["RED HOUSE","Madison - 3858 Boonesboro Rd - Richmond",2224,"Richmond - Hwy 627, Simpson Ln, Hwy 25, & Hwy 2328 - W & NW of Substation",35.482480158970702,626,"2021-03-20",5.4141476375678694E-3,0,0,4.9613000115522353E-2,8.4184989795525439E-2,0,5.6544341330047362E-2,0.48638761600369673,0,0.31785590511764028,47.167044714376999,127.25407346485621,0.71916932907348241,2.0718849840255591,"Tree Trim Scheduled for 2026"]
["SPRINGFIELD","Washinton - 107 Commercial Ave - Springfield ",2227,"Springfield - Main St - SE of Substation",5.7595468182330398,630,"2020-06-20",4.3283998882993578E-3,0,0,0,0,1.2566322256352975E-3,0.45783300753979334,0.15275062831611283,0,0.38383133203015918,9.2799047580952383,11.197883595238094,0.12888888888888889,0.15079365079365079,"Continue to Monitor"]
["WOODLAWN","Nelson – 285 Spencer Mattingly Ln. – Bardstown ",2231,"Bardstown - Poplar Flat Rd, Ashleigh Way, Ed Piler Rd, & Old US 150 - SE of Substation",52.201315976687098,1225,"2025-01-01",8.0238802454276768E-4,0,0,0,2.2113519502077742E-2,0,1.6807820706763985E-2,0.95592938985384024,0,4.3468819127752689E-3,23.960470741061222,24.87190475673469,0.18971428571428572,0.19673469387755099,"Trees Trimmed in 2025"]
["UNION UNDERWEAR","Russell - 101 Fruit Of The Loom Dr - Jamestown",2233,"Jamestown - Fruit of the Loom Dr, N Main St, Airport Rd - N of Substation",0.87899565708580496,1,"2023-11-30",0,0,0,0,0,0,0,0,1,0,114.1466664,392.36666600000001,0.4,1,"Continue to Monitor"]
["OKONITE","Madison - 1742 Berea Rd - Richmond",2238,"Eminence - Giltner Rd, Smithfield Rd, & Hwy 22 - W of Substation",2.02684517384322,9,"2019-09-28",0,0,0,0,0,0,1,0,0,0,7.0059259111111105,35.029629555555552,2.222222222222222E-2,0.1111111111111111,"Continue to Monitor"]
["LEBANON EAST","Marion - 541 Corporate Dr. - Lebanon",2240,"Lebanon - Danville Hwy and Spalding Ave - W & E of Sub.",18.171644095264298,935,"2025-01-01",1.8340558031625862E-2,0,0,0,0,0,0.17012027596312351,0.81153916600525067,0,0,21.329500885775396,28.848484843850262,0.35272727272727283,0.31336898395721929,"Reliability Improvements Scheduled for 2026"]
["BEATTYVILLE CITY","Lee - 950 W Main St. - Beattyville",2300,"Beattyville - River Dr, Proctor Rd, Broadway, & South Fork Rd - SE of Substation",9.7054679750134092,478,"2024-01-01",0,0,0,0,0.17168553264071948,7.5748178012094894E-2,6.8847883392774076E-2,0.64365017832222049,0,4.006822763219104E-2,50.043193858577403,105.75306833263598,0.50711297071129702,1.3430962343096233,"Continue to Monitor"]
["IRVINE","Estill - 83 River Dr - Irvine",2303,"Irvine - River Dr, Broadway Ave, & KY 89 - NW of Substation",11.3004870405461,899,"2024-01-01",0.12089620484682213,0,0,2.6520347508001828E-2,0.12409693644261546,1.9204389574759945E-3,5.1211705532693188E-3,0.34814814814814815,0,0.37329675354366715,68.044304778197983,36.854134215795327,0.5521690767519466,1.2068965517241381,"Continue to Monitor"]
["IRVINE","Estill - 83 River Dr - Irvine",2304,"Irvine - City of Irvine/Ravenna & Cow Creek Rd - E of Substation",18.838657690434999,1117,"2021-01-23",4.7819682800671393E-2,0,0,0,0.10235330387421643,9.1117733703285041E-3,0,0.64744973109992121,0,0.19326550885486246,18.068069227752908,28.419337506714417,0.33625783348254262,1.1199641897940915,"Continue to Monitor"]
["IRVINE","Estill - 83 River Dr - Irvine",2305,"Irvine - Kirkland Ave - SE of Substation",3.7263937494153501,82,"2021-01-23",0,0,0,0,0.75912408759124084,0,0.24087591240875914,0,0,0,20.157520317073171,13.030284548780488,0.32439024390243909,0.95121951219512202,"Continue to Monitor"]
["OKONITE","Madison - 1742 Berea Rd - Richmond ",2306,"Richmond - Berea Rd - N of Substation",2.4093409313362102,24,"2025-01-01",0,0,0,0,0,0,0,0,1,0,25.863611099999996,47.316666666666663,0.4333333333333334,0.16666666666666666,"Continue to Monitor"]
["PAINT LICK","Garrard - 11811 HWY 52 E - Paint Lick",2310,"Paint Lick - HWY 52, White Lick Rd, & Noe Rd - S of Substation",10.9396970829347,146,"2020-04-18",0,0,0,0,8.8947024198822763E-2,0.1366906474820144,0.6638325703073904,0,0.11052975801177239,0,10.30561642328767,20.94280819178082,0.13013698630136986,0.31506849315068491,"Continue to Monitor"]
["RED HOUSE","Madison - 3858 Boonesboro Rd - Richmond",2311,"Richmond - Lost Fork Rd, Red House Rd, & Boonesboro Rd - S of Substation",9.3815420460277306,97,"2021-01-23",8.1566068515497546E-3,1.0254020041948263E-2,0,0,2.4563038918666978E-2,0,7.4900955488231183E-2,0.45984618969937074,0,0.42227918900023304,46.452783490721643,155.61958759793814,0.49896907216494835,0.97938144329896903,"Tree Trim Scheduled for 2026"]
["RED HOUSE","Madison - 3858 Boonesboro Rd - Richmond",2312,"Richmond - HWY 627, Simpson Ln, & Lexington Rd - SW of Substation",18.072589160389501,485,"2023-01-06",9.4972981824136236E-3,0.11126576060258719,0,0,1.6210905518257736E-2,7.8025216964139513E-2,6.4598002292451287E-2,0.57868020304568524,0,0.14172261339446537,10.648364255670103,23.170377993814434,0.2119587628865979,0.65360824742268031,"Continue to Monitor"]
["RICHMOND 2","Madison - 200 Fairview St - Richmond",2313,"Richmond - Four Mile Rd, Dr Robert R Martin Byp - N of Substation",29.2406211822037,3244,"2025-01-01",0.71895408968413899,0,0,0.27689431644371071,0,0,1.5780912379518804E-3,0,0,2.5735026341984512E-3,8.8655096569050578,12.696968762330457,0.13341553637484588,0.15474722564734897,"Reliability Improvements Scheduled for 2026"]
["RICHMOND EAST","Madison - 1799 Irvine Rd - Richmond",2319,"Richmond - Irvine Rd, Reba Rd, & Charlie Norris Rd - E of Substation",37.883514412422997,1566,"2023-09-09",2.3580491821686565E-3,0,0,0.64073169036301125,0.22586475170971934,5.0796977847170609E-4,2.649463423502425E-2,5.7085108999620361E-2,0,4.6957795731984449E-2,54.090744992592604,129.04357172222223,0.89054916985951527,2.7286079182630925,"Continue to Monitor"]
["RICHMOND EAST","Madison - 1799 Irvine Rd - Richmond",2320,"Richmond - DR Martin BYP, Commercial Dr, & Berea Rd - SE of Substation",25.183146008921799,1788,"2023-12-09",0.18802966101694915,0,0,0,1.0858050847457628E-2,0,0.76430084745762716,0,0,3.6811440677966101E-2,12.428637209395976,10.344202086129755,0.45682326621923941,0.87583892617449677,"Reliability Improvements Scheduled for 2026"]
["RICHMOND SOUTH","Madison - 464 Eastern Bypass - Richmond",2321,"Richmond - Lake Shore Dr, Willis Branch Rd, & Barnes Mill Rd - W of Substation",26.0485830836625,1919,"2024-02-01",0.18004138882501725,0,0,0,0.34801103702000458,0,8.3927339618303065E-2,0.10163255920901357,0,0.28638767532766152,13.661796072433557,4.4468733705054717,0.12746221990620116,0.24856696195935385,"Reliability Improvements Scheduled for 2026"]
["RICHMOND SOUTH","Madison - 464 Eastern Bypass - Richmond",2323,"Richmond - S Killarney Dr, Barnes Mill Rd, & Martin Dr - NW of Substation",5.4291056237657598,669,"2024-03-01",0,0,0,0,3.1055186216098086E-3,0.20438913298520853,3.1066688136918864E-2,3.7668790688044906E-2,0,0.72376986956821787,42.7232386612855,111.03913801046339,0.53512705530642746,0.73542600896860977,"Continue to Monitor"]
["RICHMOND","Madison - 315 Clay Dr - Richmond",2325,"Richmond - US 25, Keeneland Dr, & Jacks Creek Rd  - NW of Substation",4.2957397652682197,372,"2024-01-01",1.1571952337305225E-2,0,0,0,0,0,2.257103574702108E-2,0.83134738771769023,0,0.13450962419798351,11.074247310215053,23.460304658602148,0.1032258064516129,0.11021505376344085,"Continue to Monitor"]
["RICHMOND","Madison - 315 Clay Dr - Richmond",2327,"Richmond - Moberly Ave, 5th, 4th, 3rd, 2nd, 1st St, & Irvine St - SE of Substation",5.6174215609938098,926,"2024-01-01",3.2848907038193612E-2,0,0,0.14124429497958202,0.11740331491712706,3.0386740331491711E-2,0.51543358155176555,0,0,0.16268316118184001,11.722329010151189,17.982631381209504,0.21814254859611232,0.17602591792656588,"Reliability Improvements Scheduled for 2026"]
["RICHMOND","Madison - 315 Clay Dr - Richmond",2328,"Richmond - Georgia St, N 2nd St, & Golfview Dr - E of Substation",7.1594528046254302,734,"2024-02-03",9.5029460643601751E-2,0,0,1.9640429067835021E-3,0,3.1273606284937298E-2,1.9882157425592989E-2,0,0,0.8518507327390844,23.633106264577656,45.090281557220699,0.2277929155313351,0.5149863760217982,"Continue to Monitor"]
["RICHMOND","Madison - 315 Clay Dr - Richmond",2329,"Richmond - Sunset Ave, Barnes Mill Rd, & Kirksville Rd - SW of Substation",42.699020858014499,1516,"2024-01-01",1.2806710940230689E-2,0,0,6.4243271583362457E-3,2.6634044040545262E-3,7.0653617616218106E-2,2.8402656413841314E-2,0.42248164977280667,0,0.45656763369451242,52.030397969788922,54.099725144459107,0.52137203166226909,0.64643799472295449,"Reliability Improvements Scheduled for 2026"]
["ELIZABETHTOWN 3","Hardin - 100 Crucible Steel Rd - Elizabethtown",2332,"Elizabethtown - Leitchfield Rd, Blackbranch Rd, & Nicholas St - SW of Substation",19.510979113753798,956,"2021-01-23",0,0,0,0.70342854095942275,7.8186374704512729E-2,9.494694559479587E-2,9.9514778806675794E-2,2.3923359934592894E-2,0,0,39.654665268410035,58.850592745815895,0.36276150627615056,0.56066945606694552,"Reliability Improvements Scheduled for 2026"]
["NEW HAVEN","Nelson - 256 Lyons Station Rd - New Haven",2333,"New Haven - Center St, First St, & Depot St - SE of substation",1.4849144161874499,155,"2022-07-08",0,0,0,4.3694493783303728E-2,0,0,0.56483126110124338,0,0.15097690941385436,0.24049733570159859,13.576064513548385,13.78666666451613,0.1432258064516129,0.1806451612903226,"Continue to Monitor"]
["RINEYVILLE","Hardin - Rineyville Big Springs Rd - Radcliff",2334,"Radcliff - Rineyville Big Springs Rd & Rineyville Rd - SW of Substation",27.286096050210801,775,"2019-06-22",7.0960273498355542E-2,0,0,0,3.278085511511165E-3,7.0213778777912413E-3,9.1202181062835383E-2,0.57636965553055208,1.4248312272805954E-2,0.23692011424614853,68.699174183999986,66.621419334193547,0.8193548387096774,0.88,"Reliability Improvements Completed in 2025"]
["RINEYVILLE","Hardin - Rineyville Big Springs Rd - Radcliff",2335,"Radcliff - Big Springs Rd, Wilson Rd, & US 31 - NE of Substation",11.6937451784875,665,"2024-01-01",3.8436587739215052E-3,0,0,0,3.8193318196561792E-2,0,2.0904962698670128E-2,0.23057087252675965,0.67925721699643204,2.7229970807654883E-2,18.723403506766918,71.166215536842103,0.29684210526315791,1.1789473684210527,"Continue to Monitor"]
["BONNIEVILLE","Hart - 8074 N Dixie Hwy - Bonnieville",2401,"Bonnieville - Follows US 31  - N of Substation",12.238012706662801,160,"2023-01-20",2.5050827766482718E-3,0,0,0,8.9674702294510605E-3,0,3.9282602381643918E-2,5.1517571884984029E-2,0,0.89772727272727271,47.185270826250004,172.14812498750001,0.33000000000000007,1.1750000000000003,"Continue to Monitor"]
["LEBANON JUNCTION","Nelson - 1100 Old Nelsonville Rd. - Boston",2402,"Lebanon Junction - City of Lebanon Junction - NW of Substation",15.392673537037,721,"2021-06-12",5.235253031938536E-2,0,0,0,0.31548034795860053,0,0.45180646390246998,8.3910089529493942E-2,0,9.6450568290050165E-2,110.21787793952845,480.94405916227475,0.40665742024965318,1.3661581137309291,"Continue to Monitor"]
["LEBANON JUNCTION","Nelson - 1100 Old Nelsonville Rd. - Boston",2403,"Boston - Lebanon Junction Rd, Boston Rd, KY 52 & Nelsonville Rd - SE of Substation",31.554246409733,355,"2021-07-03",3.4164741197148332E-3,0,0,0,1.8122453278564422E-2,6.5828017720902373E-4,1.1157849003692951E-2,0.96048344096214233,0,6.1615024586764615E-3,397.60852580732393,815.39089200000001,2.2236619718309854,3.7183098591549295,"Reliability Improvements Scheduled for 2026"]
["CLARKSON","Grayson - 405 Peonia Rd - Clarkson",2405,"Leitchfield - Farmview Ln, Hwy 3155, & Grayson Springs Rd - W of Substation",7.68753589016303,151,"2021-09-11",0,0,0,0,5.8284217419777344E-2,0,0.68958742632612968,0.22576948264571053,0,2.635887360838245E-2,65.625960250331133,121.34293593377487,0.76158940397350994,1.6158940397350998,"Continue to Monitor"]
["EASTVIEW","Hardin - 12540 Sonora - Hardin Springs",2407,"Sonora - KY 84, Main St, & White Mills Rd - SE of Substation",14.855329176336999,271,"2025-01-01",1.5340706386014983E-3,0,0,0,0.37348376739207989,0.13415982875490545,8.0003567606136278E-3,0.48158223332144129,0,1.2397431323581877E-3,78.657749065682651,121.31396062361623,0.72767527675276733,1.033210332103321,"Trees Trimmed in 2025"]
["EASTVIEW","Hardin - 12540 Sonora - Hardin Springs",2408,"Sonora - W Main St, Skees St, & St. Paul Rd - SW of Substation",40.094376831556097,617,"2025-01-01",1.9854221061792864E-3,0,0,5.8882724107919933E-3,0.50407963446475201,3.1277197563098349E-4,8.5944299390774588E-3,0.30104302654482157,2.4885770234986944E-3,0.17560786553524804,44.608606148460289,155.53052403241492,0.33776337115072924,0.95786061588330629,"Trees Trimmed in 2025"]
["ELIZABETHTOWN 2","Hardin - 1011 Woodland Dr - Elizabethtown",2409,"Elizabethtown - Woodland Dr - N of Substation",1.6005065676045399E-2,1,"2021-02-13",0,0,0,0,0,0,1,0,0,0,56.386666399999989,95.48333199999999,0.6,2,"Continue to Monitor"]
["ELIZABETHTOWN 2","Hardin - 1011 Woodland Dr - Elizabethtown",2413,"Elizabethtown - Long Ave, Saint John Rd, & College Street Rd - S of Substation",11.601306691955401,891,"2021-03-24",2.7119395540448173E-2,0,0,0,3.066634645582014E-3,0,7.5760654708023123E-2,0.23243612717296927,0.64705991021780496,1.4557277715172451E-2,37.512046384511784,58.175327341189686,0.59214365881032549,0.24354657687991019,"Continue to Monitor"]
["ELIZABETHTOWN 4","Hardin - 201 Sportsman Lake Rd - Elizabethtown",2418,"Elizabethtown - Dixie Hwy, New Glendale Rd, & Nicholas St - W & SW of Substation",21.365586154515199,729,"2020-05-16",6.690708930435608E-3,0,0,0,2.0095852709499856E-2,6.678845971339091E-2,1.5848913352946758E-2,0,1.9289171490936698E-2,0.87128689380279012,46.519012342112475,54.039048919067213,0.33662551440329225,0.40192043895747614,"Continue to Monitor"]
["ELIZABETHTOWN 4","Hardin - 201 Sportsman Lake Rd - Elizabethtown",2419,"Elizabethtown - Sportsman Lake Rd & Hodenville Rd - SE of Substation",23.8632885995316,788,"2020-05-16",6.1293810176475097E-4,0,0,0,0.40235129866260311,1.7528327104633642E-2,8.2320992278682517E-3,0.38570832659385185,0,0.18556701030927836,26.856324021827408,70.893422158629434,0.41675126903553289,1.4441624365482231,"Tree Trim Scheduled for 2026"]
["ELIZABETHTOWN 4","Hardin - 201 Sportsman Lake Rd - Elizabethtown",2420,"Elizabethtown - Hawkins Dr, Springfield Rd, Bishop Ln, & S Main St - NW of Substation",18.295098489253,1366,"2020-06-27",7.3343646703987716E-3,0,0,0,0.30190537667916884,5.0082915048246538E-5,5.5146854236458138E-3,0.58530789863217991,0,9.988759167955838E-2,13.60498047452416,24.996242066617864,0.21800878477306007,0.34846266471449483,"Reliability Improvements Scheduled for 2026"]
["ELIZABETHTOWN 5","Hardin - 800 N Mulberry St - Elizabethtown",2421,"Elizabethtown - N Mulberry Ave, Quince Aly, & Wall St - SW of Substation",4.52485222222567,712,"2025-01-01",0,0,0,0,0.14565785652047633,0,0.18515829218704619,0.63941330235259952,0,2.9770548939878013E-2,17.400477523314606,22.250632021067418,0.17808988764044945,0.1601123595505618,"Trees Trimmed in 2025"]
["ELIZABETHTOWN 5","Hardin - 800 N Mulberry St - Elizabethtown",2422,"Elizabethtown - KY 61/62, Navaho Dr, & Ring Rd - NE of Substation",6.4912578029490797,435,"2024-01-01",0,0,0,0,0,0,0.20967556373676943,0.71260929590427979,0,7.771514035895076E-2,10.055486586206897,17.635632177011495,0.10160919540229885,0.16781609195402297,"Continue to Monitor"]
["ELIZABETHTOWN 5","Hardin - 800 N Mulberry St - Elizabethtown",2423,"Elizabethtown - Brooks Str, N Main St, & Guthrie St - S & E of Substation",5.5909286398287801,568,"2024-01-01",1.2482585678461966E-3,0,0,0,0,0.15151852883811648,0.35268877124547227,0.49454444134856507,0,0,64.985592712676052,157.96628520070425,0.91725352112676062,1.9577464788732393,"Continue to Monitor"]
["ELIZABETHTOWN 5","Hardin - 800 N Mulberry St - Elizabethtown",2424,"Elizabethtown - Joan Ave, McCullum Ave, & Bellwood Dr - NW of Substation",6.3764923286869202,576,"2025-01-01",4.0481054176137184E-2,0,0,0,3.5949592887763615E-2,1.4486290531403746E-2,0.50319360128894897,0.39955980090341514,0,6.3296602123313287E-3,81.800630780208323,89.32418980729166,0.7934027777777779,0.70486111111111127,"Trees Trimmed in 2025"]
["ELIZABETHTOWN WEST","Hardin - 300 College Street Rd - Elizabethtown",2426,"Elizabethtown - College Street Rd & Peters Dr - NE of Substation",6.6007253937238897,371,"2021-02-06",0.14396456256921372,0,0,0,1.9763182553880227E-2,0,4.7789419882443139E-2,0.6802112616066105,0,0.10827157338785245,29.977699906199462,31.643351296495958,0.47708894878706198,0.29380053908355797,"Tree Trim Scheduled for 2026"]
["ELIZABETHTOWN WEST","Hardin - 300 College Street Rd - Elizabethtown",2427,"Elizabethtown - Peterson Dr, Geoargetown Rd, & Leitchfield Rd - W of Substation",5.3460139975862502,265,"2021-02-06",0,0,0,0,0.35849503076194983,0,0.56956933270231902,0,0,7.1935636535731193E-2,14.800176094339625,15.948490558490565,0.19245283018867926,0.26037735849056604,"Continue to Monitor"]
["HODGENVILLE","Larue - 500 W High Ave - Hodgenville",2429,"Hodgenville - Tonieville Rd, N Lincoln Blvd, & Phillips Ln - NE of Substation",7.48620933856406,383,"2022-03-22",0,0,0,0,0.93173449971581779,9.501569179825536E-3,1.6309585588257097E-2,4.2454345516099536E-2,0,0,49.776422970757174,202.34482157702351,0.51540469973890335,2.0809399477806791,"Continue to Monitor"]
["HORSE CAVE","Hart - 501 Shewey Ave - Horse Cave",2432,"Horse Cave - Maple St, US 31 W, 3rd Street & Owen Street - SW of Substation",17.167106431323202,720,"2023-02-10",1.3819286256643887E-2,0,0,0,1.9627942293090356E-2,9.5671981776765374E-3,2.2854973424449507E-2,0.91852695520121497,4.0622627182991646E-3,1.1541381928625664E-2,13.133578698888888,14.042569440277777,0.12499999999999997,8.7499999999999994E-2,"Continue to Monitor"]
["HORSE CAVE","Hart - 501 Shewey Ave - Horse Cave",2434,"Cave City - Old Glasgow Rd, 9th St, KY 70, 3rd St, & Dixie Hwy- SW of Substation",15.605060667788701,637,"2023-06-10",0,0,0,0,2.0428633097178843E-2,0,4.7789543180721664E-2,0.54820852695462274,0.22113455727381223,0.16243873949366447,37.512124535949759,100.11860281789637,0.53877551020408165,2.0251177394034534,"Continue to Monitor"]
["HORSE CAVE","Hart - 501 Shewey Ave - Horse Cave",2435,"Horse Cave - E Main St, KY 218, & US HWY 31 E - E of Substation",18.863982514678298,410,"2023-07-14",5.9518001756268908E-3,0,0,0,0.7712622369662081,2.9173577910040004E-2,2.9628906885224574E-2,0.10010732754415064,4.9305623312843529E-2,1.4570527205906268E-2,73.169512184878059,74.989999982926832,0.49463414634146341,0.62926829268292683,"Continue to Monitor"]
["HORSE CAVE","Hart - 501 Shewey Ave - Horse Cave",2436,"Hiseville - Old Glasgow Rd & Hiseville Main St - SE of Substation",28.090428642141799,355,"2023-09-09",1.952675953425529E-4,0,0,0,6.0690428423403131E-3,6.2517125283059272E-3,1.1574329240062612E-2,0.42332439931593352,9.0752189674123573E-2,0.46183305880389147,332.72769951887324,844.92460092112674,1.5374647887323944,3.4309859154929576,"Reliability Improvements Scheduled for 2026"]
["MILLWOOD","Grayson - 6649 Beaver Dam Rd - Millwood",2440,"Caneyville - US 62, Hwy 79, & River Park Dr - W of Substation",22.2548766111125,428,"2021-10-16",0,0,0,2.1498887338286879E-3,1.4144004827820314E-2,2.1876060800362085E-2,0.10848766014156577,0.77314273501049802,8.7755692176165155E-3,7.1424081268308626E-2,269.47687693551404,166.91806850700937,1.4158878504672896,2.0700934579439245,"Continue to Monitor"]
["NEW HAVEN","Nelson - 256 Lyons Station Rd - New Haven",2445,"New Haven - KY 52, Clark Rd, & Lyons Station Rd - NW of Substation",13.7032304610875,207,"2022-06-24",1.0432865494773725E-3,0,0,7.2833211944646763E-4,3.0890139957874846E-2,1.7371705281392098E-3,0.10915139465758548,0.7094053266667979,0,0.14704434952067871,151.8455877342995,344.20032197101443,1.4840579710144932,4.5458937198067657,"Continue to Monitor"]
["NEW HAVEN","Nelson - 256 Lyons Station Rd - New Haven",2446,"New Haven - Cissal Hill Rd & US 31 - SSW of Substation",7.9724955956191801,49,"2022-07-08",0,0,0,0,6.2437018823813938E-2,0,0,0.93756298117618608,0,0,197.36721085714288,457.46156459183675,1.0163265306122451,2.3469387755102042,"Continue to Monitor"]
["RADCLIFF","Hardin - 677 N Wilson Rd - Radcliff",2447,"Radcliff - N Dixie Blvd, E Lincoln Trail, & New St - SE/E/NE of Substation",10.2794032893371,764,"2024-01-01",1.5835214446952597E-2,0,0,0,0.12680586907449209,1.3656884875846501E-3,5.1636568848758467E-2,0.14190744920993226,0,0.66244920993227996,36.200610814659683,92.591535770942414,0.43298429319371723,0.63350785340314131,"Continue to Monitor"]
["RIO","Hart - 301 Glen Lily Rd E - Munfordville",2450,"Munfordville - E US 31, Eve Rd, & Pikeview Rd - N of Substation",14.372486472137201,175,"2020-03-14",0,0,0,0,2.0755551188838669E-3,0,9.2233248182354097E-3,0.39692228335625857,0,0.59177883670662212,245.71721903657141,465.27419045714282,1.4240000000000002,2.2628571428571429,"Tree Trim Scheduled for 2026"]
["ROGERSVILLE CITY","Hardin - 180 Rogersville Rd - Radcliff",2455,"Radcliff - Rogersville Rd, Woodland Dr, Vine St, & Valley View Dr - NW & W of Substation",18.177264177999401,1160,"2024-01-01",1.8139104668200085E-2,0,0,0,1.0240081200324146E-2,1.3841708481013694E-2,9.5181186408768326E-2,0.81183134561706527,1.5969942783239335E-2,3.4796630841389245E-2,10.416077583275861,15.531853445689654,0.11724137931034484,0.12672413793103449,"Tree Trim Scheduled for 2026"]
["SONORA","Hardin - 1340 Old Sonora Rd - Sonora",2456,"Sonora - US 31 W, S Dixie Hwy, & Sonora Rd - E of Substation",12.8099288874461,201,"2022-08-12",9.2331088420595259E-4,0,0,9.3073357954956915E-2,1.2853935838945615E-3,0.22546889709609674,3.1700340357737708E-2,0.62899196176406691,0,1.8556738359041206E-2,75.945655042786072,103.19635155223881,1.0228855721393035,1.7711442786069651,"Continue to Monitor"]
["SONORA","Hardin - 1340 Old Sonora Rd - Sonora",2457,"Sonora - Sonora Hardin Springs Rd, Nolin Rd, Gilead Church Rd, & KY 222 - N of Substation",28.400200411642999,505,"2022-10-07",9.691140606107704E-4,0,0,0,0.3812206723000231,1.7942323999515443E-3,2.9770543960979445E-2,0.38427658149586413,0,0.20196885578257104,64.685564346138591,232.36491747128704,0.85742574257425763,3.160396039603961,"Continue to Monitor"]
["SONORA","Hardin - 1340 Old Sonora Rd - Sonora",2458,"Sonora - Maple St, US 31, & City of Upton - S of Substation",17.746786693904401,519,"2022-10-28",9.7502706334689614E-3,0,0,0,0.53464481690246002,6.4728060024636979E-3,9.2425995744522E-3,0.43440217999925346,0,5.4873268879017511E-3,28.523622344123318,72.920488105973021,0.45818882466281313,0.90751445086705229,"Continue to Monitor"]
["VINE GROVE","Hardin - 108 Crutcher St - Vine Grove",2459,"Vine Grove - Park St, Edgebrook Dr, Brown St, & 1st St - W of Substation",8.3135949633645794,550,"2024-01-01",0,0,0,1.5746403919933379E-2,0.66382461141784543,0,5.1830867444169508E-3,0.31491015624533275,0,3.35741672471453E-4,19.778084845454547,68.549212114545469,0.18872727272727272,0.66363636363636358,"Continue to Monitor"]
["VINE GROVE","Hardin - 108 Crutcher St - Vine Grove",2460,"Vine Grove - Main St, Highland Ave, Central Ave, & Cheryl Ave - E of Substation",8.6525927240711695,683,"2020-10-03",0,0,0,2.1834403698512645E-4,7.4584754094931288E-2,0,4.8153358575821602E-3,0.90775160554776901,5.9606614647616258E-3,6.6692989979708385E-3,23.112996580966318,70.749463146412879,0.18887262079062958,0.49487554904831621,"Tree Trim Scheduled for 2026"]
["ELIZABETHTOWN WEST","Hardin - 300 College Street Rd - Elizabethtown",2461,"Elizabethtown - Ring Rd & Ambrake Dr - W of Substation",2.15387402238296,16,"2021-02-06",0,0,0,0,0,0,1,0,0,0,9.4160416500000004,17.129166625,3.7499999999999999E-2,0.125,"Continue to Monitor"]
["ELIZABETHTOWN INDUSTRIAL","Hardin - 111 Ring Rd - Elizabethtown",2464,"Elizabethtown - N Black Branch Rd & Enterprise Dr - N of Substation",1.43113727127179,21,"2025-01-01",0,0,0,0,0,0,1.3710826210826211E-2,0,0,0.9862891737891738,66.013650780952361,267.41269838095235,0.18095238095238092,0.23809523809523808,"Continue to Monitor"]
["HORSE CAVE INDUSTRIAL","Hart - 400 Cherry St - Horse Cave",2469,"Horse Cave - Hatcher Valley Rd, N Toohey Ridge Rd, & Park Ridge Rd - W of Substation",20.311582275987099,120,"2023-02-10",1.4307984709676042E-3,0,0,0,0,0,0.27211864949708503,0.72645055203194742,0,0,295.92899997500001,780.45291664166666,0.89333333333333331,1.7583333333333333,"Continue to Monitor"]
["RADCLIFF SOUTH","Hardin - 100 Energy Dr - Radcliff",2470,"Hardin - S Wilson Rd, Miller Ave, & Shelton Rd - N of Substation",13.742441815396401,1046,"2025-01-01",0,0,0,0,1.8640538885486835E-2,0,9.1855480710349051E-4,0.83375382731169623,0,0.1466870789957134,15.230551304397704,26.422562140535373,0.13938814531548754,0.27437858508604202,"Reliability Improvements Scheduled for 2026"]
["RADCLIFF SOUTH","Hardin - 100 Energy Dr - Radcliff",2471,"Hardin - S Wilson Rd & Medical Center Dr  - SE of Substation",3.13634438297301,109,"2019-04-06",6.6367001586462193E-2,0,0,0,4.7593865679534636E-2,0,0,0.88603913273400314,0,0,8.888929658715595,33.040825678899083,8.8073394495412849E-2,0.28440366972477066,"Tree Trim Scheduled for 2026"]
["HORSE CAVE INDUSTRIAL","Hart - 400 Cherry St - Horse Cave",2473,"Horse Cave - Old Dixie Hwy - W of Substation",0.38850605237889002,4,"2023-01-28",0,0,0,0,1,0,0,0,0,0,85.687499949999989,350.17916649999995,0.5,2.25,"Continue to Monitor"]
["HORSE CAVE INDUSTRIAL","Hart - 400 Cherry St - Horse Cave",2474,"Horse Cave - Butler Rd & Top Quality Dr - S of Substation",2.56907040714733,31,"2023-01-28",0,0,0,0,0.3001389532190829,0,0.6998610467809171,0,0,0,56.527526864516133,139.27634406451611,0.39354838709677414,0.70967741935483863,"Continue to Monitor"]
["EMINENCE","Henry - 1257 Ballardsville Rd - Eminence",2501,"Eminence - City of Eminence, Hwy 22, & Castle Hwy - E of Substation",20.5348019126344,1027,"2021-11-20",1.0312134457920335E-3,0,0,6.2411500338607397E-3,1.3313427322538939E-3,2.6218986640398942E-2,0.81606692113525836,2.5934248599396663E-3,0.10191313181062611,4.4603829341870342E-2,42.951447578773127,126.425186624148,0.37429406037000967,1.0808179162609541,"Reliability Improvements Scheduled for 2026"]
["FAIRFIELD","Nelson - 5729 High Grove Rd - Coxs Creek",2503,"Bloomfield - KY 48, US 62, & Lawrenceburg Rd - E of Substation",55.752811576915697,1263,"2025-01-01",1.4924774583878425E-3,0,0,0,5.1971164945313758E-3,1.0525380245754785E-2,2.3768001586773422E-2,0.95093250034954535,0,8.0845238650072027E-3,176.68305092921611,635.4646476539981,0.57086302454473481,1.1472684085510696,"Trees Trimmed in 2025"]
["FLORIDA TILE","Anderson - 1247 Alton Rd - Lawrenceburg",2505,"Lawrenceburg - Alton Rd - N of Substation",16.1471923217753,685,"2022-04-30",6.5378386127693212E-3,0,0,3.2030501303176442E-4,0.36766365907147713,1.6531871640349132E-4,2.9780616897122678E-2,0.5718012765704632,0,2.3730985118732419E-2,76.873416050218992,149.67917273430663,0.54715328467153279,1.078832116788321,"Continue to Monitor"]
["LAGRANGE EAST","Oldham - 1810 E Highway 146 - La Grange",2509,"La Grange - Grange Dr, Hwy 53, & Hwy 22 - S of Substation",74.526279656449006,2218,"2021-07-24",1.6031390134529148E-2,0,0,6.3275088912942631E-2,0.14023117365084276,6.9545384258543376E-3,0.19431730323179217,0.49516777485696617,0,8.4022730787072827E-2,48.721414182596931,97.827832877817841,0.62813345356176797,1.5072137060414805,"Reliability Improvements Scheduled for 2026"]
["LAGRANGE EAST","Oldham - 1810 E Highway 146 - La Grange",2511,"La Grange - Waterworks Rd, Hwy 53/1st St, & Fendley Mill Rd - W of Substation",18.282176474759002,1292,"2024-01-01",8.1187147412312977E-2,0.13854725113003258,0,0,0.23288599226789072,1.6842449513531192E-2,2.1724657486246889E-3,4.4033311141478907E-3,0,0.52396136281345995,26.684896797213629,66.269195042569663,0.35402476780185754,1.2445820433436532,"Reliability Improvements Scheduled for 2026"]
["LAGRANGE PENAL","Oldham - 3011 W Highway 146 - La Grange",2512,"La Grange - W Highway 146 - W of Substation",9.3291225575972397E-3,1,"2024-01-01",0,0,0,0,0,1,0,0,0,0,154.1999998,313.98333300000002,1,2,"Continue to Monitor"]
["LAWRENCEBURG","Anderson - 108 E Broadway st - Lawrenceburg ",2516,"Lawrenceburg - Main St - N of Substation",42.2274389913498,2453,"2022-12-23",6.1360291534790889E-2,0.11255901760125088,0,0,8.8339509052818167E-3,7.6068531571827191E-2,1.0312881103739478E-2,0.65029245349295928,7.0884169682471348E-4,7.9864032093325724E-2,115.28481043163472,166.71937083326537,0.8017121891561354,1.7904606604158175,"Reliability Improvements Scheduled for 2026"]
["SHELBYVILLE SOUTH","Shelby - 614 Mack Walters Rd - Shelbyville",2524,"Shelbyville - Old Finchville Rd, KY 55, & US 60 - W of Substation",4.5849430381671201,474,"2023-02-10",0.68577144874661644,0,0,0,0,0,0.25926797693303516,5.4960574320348357E-2,0,0,15.712925453164559,17.927039375527425,0.16540084388185655,0.20886075949367089,"Continue to Monitor"]
["SHELBYVILLE SOUTH","Shelby - 614 Mack Walters Rd - Shelbyville",2526,"Shelbyville - Kentucky St, Old KY 53, Osprey Cove, & Zaring Mill Rd - S & SE of Substation",30.9084042775293,1285,"2022-09-09",2.6664285926851767E-3,0,0,0.82385501294527275,6.0887420766003036E-3,4.1662946760705887E-5,6.3321727226735708E-2,7.9260780287474325E-2,1.2165580454126119E-2,1.2600065470344909E-2,78.593836569961084,115.26202333852142,1.0334630350194551,1.3844357976653692,"Reliability Improvements Scheduled for 2026"]
["TAYLORSVILLE","Spencer - 1604 Elk Creek Rd - Taylorsville",2529,"Taylorsville - Elk Creek Rd, KY 55, & Hwy 1633 - N of Substation",51.384133448169997,1099,"2020-07-18",0.45749239954580417,1.6299769239222007E-3,0,1.8680634408996008E-3,6.4539760448335232E-2,1.5292480128933006E-2,5.4521812387824622E-2,0.3894179700377276,1.3552617120252005E-3,1.3882275374528406E-2,34.032171666424034,29.441659077343044,0.54576888080072805,1.1037306642402183,"Continue to Monitor"]
["TAYLORSVILLE","Spencer - 1604 Elk Creek Rd - Taylorsville",2530,"Taylorsville - Elk Creek Rd, City of Taylorsville, & Bloomfield Rd - SE of Substation",27.250552173813698,827,"2020-05-02",1.3306854621166866E-4,0,0,0,0.14902809337362033,0.79080467417732536,1.1504643658343614E-2,4.5710492020949615E-2,0,2.8190282235493721E-3,52.336158798307132,135.64034662515115,0.58113663845223695,1.02055622732769,"Continue to Monitor"]
["LOCKPORT","Henry - 88 Sawmill Rd - Bethlehem",2532,"Bethlehem - KY 22, Hwy 1360, Sewell Rd, & Bethlehem Rd - SW of Substation",54.113794266531698,957,"2022-05-13",0.27793141592920356,0,0,0,9.0042372881355935E-3,1.2388443077846107E-2,0.11305684715764212,9.232038398080096E-2,0.38065752962351884,0.11464114294285285,60.679414825496352,204.54792753396029,0.74357366771159839,2.4890282131661428,"Reliability Improvements Scheduled for 2026"]
["SHELBYVILLE EAST","Shelby - 183 Boone Station Rd - Shelbyville ",2533,"Shelbyville - KY 53, KY 44, & Mill St - S of Substation",55.143936584972003,1500,"2025-01-01",0.10538803000153069,0,0,0,0.10076725853359865,7.6534517067197309E-5,0.14220113271085261,0.54202701668452469,8.0361242920557168E-4,0.10873641512322058,49.846782217599994,60.600311103333325,0.39213333333333339,0.42866666666666681,"Reliability Improvements Scheduled for 2026"]
["SHELBYVILLE SOUTH","Shelby - 614 Mack Walters Rd - Shelbyville",2534,"Shelbyville - Main St/US 60, Sunset Way, Old KY 55, & Haven Hill Rd - NW of Substation",4.2454701399651604,920,"No Trimming Necessary",0,0,0,0,0,1.424634885643428E-2,0.64652796913750343,0.13664921465968585,0.20257646734637641,0,30.642891300652174,71.553007241304329,0.32478260869565218,0.78695652173913044,"Continue to Monitor"]
["SHELBYVILLE SOUTH","Shelby - 614 Mack Walters Rd - Shelbyville",2537,"Shelby - Old Finchville Rd, Hwy 55, & Gordon Ln - SW of Substation",13.6189015845609,558,"2023-01-06",1.8873804218089453E-3,0,0,0,0.82446774108198051,0,7.5642209117046985E-2,3.8112149203008053E-2,0,5.9890520176155509E-2,63.669032252329735,182.06379926881715,0.51254480286738358,1.0645161290322578,"Continue to Monitor"]
["SIMPSONVILLE","Shelby - 6801 Shelbyville Rd - Simpsonville",2540,"Simpsonville - Buck Creek Rd, Kingbrook Pky, & Rolling Ridge Way - S of Substation",5.2341851055184501,335,"2023-11-11",0,0,0,0,0.37440928396243345,0.40778847879404201,4.624035413052581E-2,0,0,0.17156188311299875,19.037293530746265,49.903283576119399,0.1546268656716418,0.35820895522388058,"Continue to Monitor"]
["WEST SHELBY","Shelby - 3900 HWY 60 - Shelbyville",2544,"Shelbyville - 3900 HWY 60 - E of Substation",31.315396972985202,992,"2023-12-16",1.329581160543241E-2,0,0,0,0.90809395009673566,7.1494103162568273E-3,1.9000128347126687E-2,3.3275180993216615E-4,5.1590791331339994E-2,5.3715649317621114E-4,45.381972444556439,212.02397513104836,0.25020161290322585,1.0685483870967745,"Continue to Monitor"]
["WEST SHELBY","Shelby - 3900 HWY 60 - Shelbyville",2545,"Shelbyville - 3900 HWY 60 - E of Substation",10.7607966027981,134,"2023-12-16",0.14516129032258066,0,0,0,0,0,0.85483870967741937,0,0,0,4.3640298462686564,3.6983830820895522,5.9701492537313418E-2,7.4626865671641784E-2,"Continue to Monitor"]
["MANNINGTON","Hopkins - 202 Russ Hill Rd - Nortonville",3418,"Nortonville - Daniel Boone Rd & Hwy 41 Alt, & Hwy 62 - S of Substation",25.262537713731501,1,"2021-09-13",0,0,0,0,0,0,0,0,0,1,456.86333333280498,953.66666666559229,2.6,5,"Continue to Monitor"]
["OAKHILL","Hopkins - 202 Russ Hill Rd - Nortonville",3418,"Nortonville - Daniel Boone Rd & Hwy 41 Alt, & Hwy 62 - S of Substation",25.262537713731501,1,"2021-09-13",0,0,0,0,0,0,0,0,0,1,456.86333333280498,953.66666666559229,2.6,5,"Continue to Monitor"]
["PRINCETON","Caldwell - 320 Marion Rd - Princeton",3423,"Princeton - Watson Rd, Mt. Hebron Rd, & Mill Dam Rd - E of Substation",19.596356182929799,1,"2021-09-20",0,0,0,0,0.98776969647718504,0,0,1.2230303522815001E-2,0,0,237.98333313023477,678.09999965168527,1.6,3,"Reliability Improvements Scheduled for 2026"]
["ALVA","Harlan - Rockhouse Branch Rd - Pathfork",4331,"Alva - Hwy 72 & Alva Rd - NW of Substation",2.9825007685112799,9,"2022-12-02",0,0,0,0,0,0,0,1,0,0,290.77370368888887,486.66666666666669,1.0444444444444445,2,"Continue to Monitor"]
["FOURMILE","Bell - Hwy 2014 - Pineville",4340,"Pineville - Hwy 2014 & 2015, US 25, & Hwy 92 - SW & N of Substation",12.5513187516505,176,"2022-12-02",0,0,0,0,6.3480132738159153E-2,9.5038681208551287E-2,1.8627315631503327E-2,0.78841148829337393,0,3.4442382128412406E-2,266.5916855840909,629.15482951704541,1.2943181818181819,2.2556818181818183,"Continue to Monitor"]
["SHAWNEE GAS","Harlan - Ball Park Rd - Harlan",4400,"Harlan - Memorial Hospital Rd & Hwy 115 - E of Substation",1.11715200145982,37,"2025-01-01",0,0,0,0,0,0,0.14866979655712051,0,0,0.85133020344287946,6.4189189135135134,5.14054054054054,8.6486486486486491E-2,0.24324324324324326,"Continue to Monitor"]
["SHAWNEE GAS","Harlan - Ball Park Rd - Harlan",4402,"Harlan - Hwy 421 & Hwy 990 - E of Substation",17.006324779951999,501,"2025-01-01",8.4342834964210272E-4,0,0,0,0.12987303790949195,0.61535686473548945,0.11741318783572305,0.10596097340090713,0,3.0552507768746375E-2,97.479288068263486,274.25302725149709,0.70419161676646747,2.3373253493013992,"Continue to Monitor"]
["HARLAN"," Harlan - Corner of River St and Rain St - Harlan ",4407,"Harlan - State HWY 38 - SW of Substation",4.3786069939258798,117,"2023-12-09",0,0,0,0,7.5464824284060008E-4,5.2695265232835008E-3,4.4888559272415002E-2,0.94908726596146087,0,0,106.54487176581196,112.92749284615384,0.9606837606837606,1.0598290598290598,"Continue to Monitor"]
["HARLAN Y","Harlan - Sunshine Pike Rd just W of US HWY 421 - Harlan",4411,"Harlan - US HWY 421 - E of Substation",4.8443240995530097,391,"2023-11-18",0,0,0,7.7721722599985374E-2,0.11735029611756964,0,0.68450683629450904,3.9189880821817652E-2,0,8.1231264166118297E-2,31.376999140153451,34.977536219948853,0.28081841432225063,0.36828644501278768,"Continue to Monitor"]
["HARLAN Y","Harlan - Sunshine Pike Rd just W of US HWY 421 - Harlan",4412,"Harlan - US HWY 421 - E of Substation",19.6323943338726,895,"2023-11-25",5.1953078167297324E-4,0,0,0,3.1087712360836212E-3,5.4834686146617052E-3,5.7177833072866821E-2,0.90300759945228415,0,3.070279684243073E-2,79.121769079106144,96.888175037988859,0.70860335195530744,0.51731843575419012,"Continue to Monitor"]
["DANIEL BRANCH","Harlan - Gilbert Rd/Bandana Branch - Smith",4421,"Rose Hill - Hwy 987 - E of Substation",20.4577709409768,234,"2021-10-16",9.8458550293412678E-3,0,0,0,0.25079552029093316,0,3.1407554343334159E-3,0.68535622778742045,0,5.0861641457971736E-2,262.6481338794872,468.94230767094018,1.9017094017094014,2.6282051282051277,"Continue to Monitor"]
["CATRONS CREEK","Harlan - Near 6872 Hwy 72 - Gulston",4427,"Gulston - Hwy 72 & Bardo Hollow Rd - SW of Substation",3.1120824411424999,92,"2020-02-15",0,0,0,0,3.8243560798046352E-3,1.1150532184490624E-2,0.3989310233608257,0.46369165553149333,0,0.12240243284338571,414.07746374999988,471.79873183695651,1.5391304347826087,2,"Tree Trim Scheduled for 2026"]
["CATRONS CREEK","Harlan - Near 6872 Hwy 72 - Gulston",4428,"Gulston - Hwy 1216, Hwy 72, & Hwy 2425 - N of Substation",9.0059185897477398,320,"2024-01-01",3.2843007640174235E-3,0,0,0,1.6616335221342388E-2,1.3137203056069694E-2,0.57036892717480547,0.38671249843439054,0,9.8807353493744528E-3,184.61045831812501,190.89130206249996,0.890625,1.0531250000000001,"Continue to Monitor"]
["LYNCH","Harlan - Hwy 160 (W Main St) - Lynch",4451,"Lynch - W Main St, Mountain St, & 1st, 2nd, & 3rd St - W of Substation",7.8877143035777602,520,"2024-02-01",0,0,0,0,0,0,3.0621224550674921E-2,0.19502722052352897,0,0.7743515549257961,385.72195512076928,588.46862179230766,1.5426923076923074,1.0211538461538461,"Reliability Improvements Scheduled for 2026"]
["EVARTS","Harlan - 1600 Block of Hwy 215 - Evarts",4476,"Evarts - Hwy 215 - E of Substation",14.727814637367601,466,"2023-04-07",4.9969404453196788E-3,0,0,0,7.7792416689422314E-2,1.9533313268501338E-4,1.4538366018413138E-2,0.90103387036656857,0,1.4430733475913231E-3,263.56363374678119,298.68022172532187,1.6201716738197423,1.8197424892703864,"Continue to Monitor"]
["VERDA","Harlan - Corner of School St - Evarts ",4479,"Evarts - Hwy 38, Nolan Ln, & Ages Creek Rd - W of Substation",13.4900476842564,498,"2021-11-13",1.8341739964150235E-3,0,0,0,4.0601942557005298E-3,8.9207553462003421E-4,7.2616615948976615E-3,0.98303389053316104,0,2.9180040852057193E-3,62.775361435341367,71.900769736947794,0.49959839357429719,0.62650602409638567,"Continue to Monitor"]
["VERDA","Harlan - Corner of School St - Evarts ",4480,"Evarts - Hwy 38, Hill St, & Hwy 1601 - NE & SE of Substation",10.293707882249,383,"2024-01-01",2.8027879058461691E-3,0,0,0,8.9428776942728869E-2,5.4141759886234923E-2,0.30817025076270554,0.15929591322105646,0.3769873750527073,9.1731362287207213E-3,343.03302000313323,521.9211488093996,2.1425587467362925,2.5326370757180157,"Continue to Monitor"]
["SOMERSET 3","Pulaski - 125 Young St. - Somerset",4500,"Somerset - Hines Addition, Jarvis Ave, & Bourne Ave - S of Substation",14.258977486253301,711,"2024-01-01",2.5219031394499877E-2,0,0,0,2.3089559503528839E-2,0,0.25550620588951084,0.59442686785105858,0,0.1017583353614018,66.220529762587915,191.50707922222222,0.5468354430379746,1.3699015471167364,"Continue to Monitor"]
["SOMERSET 3","Pulaski - 125 Young St. - Somerset",4501,"Somerset - E Mt. Vernon St & Eller St - E & SW of Substation",8.8546396942512509,765,"2020-10-10",7.02228900576008E-3,0,0,0,0,3.8026546456298521E-2,0.15621337340345604,0.28182319058352112,1.8221888304532932E-2,0.49869271224643125,100.2837690538562,228.50084966274508,1.0528104575163397,2.265359477124183,"Continue to Monitor"]
["SOMERSET 3","Pulaski - 125 Young St. - Somerset",4502,"Somerset - Pumphouse Rd, Speedway Dr, & College St - W of Substation",13.211397044242601,913,"2020-10-10",3.6976303012764864E-4,0,0,0.1781855888878171,9.9763673193787983E-2,7.250570721198675E-3,1.9541172309572041E-2,0.31104305327802967,0,0.3838461785794669,71.724990866374583,184.05023730010953,1.0105147864184008,3.3318729463307784,"Reliability Improvements Scheduled for 2026"]
["SOMERSET 2","Pulaski - 105 Tandy Ave - Somerset ",4506,"Somerset - N Main St, Robin Dr, & Elliott Dr - NW of Substation",1.71795064618749,104,"2024-02-01",0,0,0,0,0,0,1,0,0,0,36.579647428846158,119.22756408653846,0.31730769230769235,1.1730769230769231,"Continue to Monitor"]
["SOMERSET 2","Pulaski - 105 Tandy Ave - Somerset ",4507,"Somerset - N Main St, Oak St, & N Vine St - SE of Substation",1.5795831136410601,150,"2024-02-01",0,0,0,0,0,0,0,1,0,0,61.841444436000003,131.66633333333334,0.56533333333333335,0.99333333333333329,"Continue to Monitor"]
["SOMERSET 2","Pulaski - 105 Tandy Ave - Somerset ",4508,"Somerset - Clifty Rd, W Columbia St, & Ogden St - S & W of Substation",6.7213780099549902,557,"2025-01-01",0,0,0,0,7.6799883526242991E-3,0,5.7836499963601948E-2,0.93448351168377375,0,0,87.941220821543979,302.15245361400355,0.35906642728904847,1.0556552962298025,"Trees Trimmed in 2025"]
["MCKEE ROAD","Pulaski - 140 McKee Rd - Somerset",4512,"Somerset - Hwy 1247, Crab Orchard Rd, & Oak Leaf Ln - N & E of Substation",34.052068795080402,1342,"2024-01-01",4.6429851663451855E-3,0.20673232849120052,0,0,1.7786729938719423E-2,0,0.11395797415632522,0.60749705545977506,0,4.9382926787634639E-2,25.081992044560359,41.154371577496285,0.46035767511177345,0.85171385991058146,"Reliability Improvements Scheduled for 2026"]
["SOMERSET GE","Pulaski - 100 Block of W University Dr - Somerset",4516,"Somerset - W University Dr - NE of Substation",0.88657209469589304,16,"2025-01-01",0,0,0,0,0,0,0,1,0,0,21.570833325000002,107.854166625,0.125,0.625,"Trees Trimmed in 2025"]
["AISIN","Laurel - Farriston Rd/Greta Ln - Lily",4618,"Lily - Greta Ln & S Laurel Rd - S of Substation",6.1535966002317197,157,"2023-12-01",4.2846768336964412E-3,0,0,0,7.2621641249092234E-3,0,7.5599128540305011E-2,0.91023965141612195,0,2.6143790849673201E-3,57.270828012738846,60.391613579617839,0.38726114649681531,0.21019108280254775,"Continue to Monitor"]
["AISIN","Laurel - Farriston Rd/Greta Ln - Lily",4619,"Lily - Greta Ln & KY 552 - SW of Substation",2.5949899914885801,11,"2023-12-01",0,0,0,0,0,1,0,0,0,0,63.741818127272722,90.151515090909086,0.52727272727272712,1,"Continue to Monitor"]

{"sheet":"KU Section 6-7","index":2,"n_rows":31,"n_cols":1,"rows_kept":31,"cut":false,"hidden":false,"merged":[[0,0,0,8],[2,0,2,8],[4,0,4,8],[5,0,10,8],[11,0,14,8],[15,0,15,5],[26,0,27,8],[29,0,29,8],[30,0,33,8],[16,0,16,6],[17,0,17,6],[18,0,18,6],[19,0,19,6],[20,0,21,8],[23,0,24,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
[]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 6: VEGETATION MANAGEMENT PLAN REVIEW"]
["The Companies’ Vegetation Management Plan went into effect January 1, 2024.  The Distribution Vegetation Management Program encompasses right of way maintenance for Louisville Gas and Electric Company and Kentucky Utilities Company (referred to as the “Companies”).  The program is centralized and managed by a Forestry Manager and eight company Utility Arborists.  All are certified arborists by the International Society of Arboriculture."]
[]
[]
[]
[]
[]
["The Companies’ plan is to maintain a proactive trim cycle while balancing the reactive needs of worst performing circuits. The Companies’ goal is to maintain an average trim cycle of five years or less.   The effectiveness of the plan is evaluated by the cycle and system performance as measured by system SAIDI, SAIFI, and CAIDI.  "]
[]
[]
[]
["Effectiveness of the program"]
["KU/LG&E Tree Cycle – 5.0 years"]
["KU (Kentucky) Tree SAIDI – 26.86 minutes"]
["KU (Kentucky) Tree SAIFI – 0.181"]
["KU (Kentucky) Tree CAIDI – 148.8 minutes"]
["The hazard tree program, mid cycle, herbicide, and worst performing circuits were completed as planned.  "]
[]
["Adjustments made to the tree plan in 2025 included"]
["The 2025 maintenance plan was completed as planned."]
[]
["Changes to be implemented in 2026"]
["The routine trimming cycle plan is a proactive vegetation management strategy that schedules maintenance activities based on established trim intervals and clearance standards. Hazardous or danger trees are prioritized for assessment and mitigation based on their potential impact on system reliability and the level of vegetation-related risk they pose."]
[]
[]
["SECTION 7: UTILITY COMMENTS"]
["516 Circuits were above their previous 5 year average SAIDI and/or SAIFI in 2025.  Specific recommendations for each circuit are included in circuit reporting."]