{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["LGE Section 1-4","Excle LGE Section 5","LGE Section 6-7"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"LGE Section 1-4","index":0,"n_rows":45,"n_cols":8,"rows_kept":45,"cut":false,"hidden":false,"merged":[[44,3,44,5],[37,0,37,8],[38,1,38,8],[39,1,39,8],[40,1,40,8],[41,1,41,8],[43,0,43,8],[36,1,36,3],[36,6,36,8],[28,3,28,5],[29,1,29,3],[29,6,29,8],[30,1,30,3],[30,6,30,8],[31,1,31,3],[31,6,31,8],[33,0,33,8],[34,1,34,3],[34,6,34,8],[35,1,35,3],[35,6,35,8],[26,0,26,1],[26,5,26,6],[14,0,14,8],[15,0,15,3],[15,5,15,8],[16,0,16,3],[16,5,16,8],[17,0,17,3],[17,5,17,8],[18,0,18,3],[18,5,18,8],[20,0,21,8],[24,0,24,8],[25,2,25,6],[11,0,11,3],[11,5,11,8],[0,0,0,8],[1,0,1,8],[3,0,3,8],[4,0,4,3],[4,5,4,8],[5,0,5,3],[5,5,5,8],[6,0,6,3],[6,5,6,8],[7,0,7,3],[7,5,7,8],[10,0,10,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 1: CONTACT INFORMATION"]
["UTILITY NAME",null,null,null,null,"LOUISVILLE GAS AND ELECTRIC"]
["REPORT PREPARD BY",null,null,null,null,"Karmen Powell (Mgr Investment Strategy & Reliability)"]
["E-MAIL ADDRESS OF PREPARER",null,null,null,null,"Karmen.Powell@lge-ku.com"]
["PHONE NUMBER OF PREPARER",null,null,null,null,"(502) 399-4805"]
[]
[]
["SECTION 2: REPORTING YEAR"]
["CALENDAR YEAR OF REPORT",null,null,null,null,2025]
[]
[]
["SECTION 3: MAJOR EVENT DAYS (MED)"]
["TMED",null,null,null,null,3.5470000000000002]
["FIRST DATE USED TO DETERMINE TMED",null,null,null,null,"2020-01-01"]
["LAST DATE USED TO DETERMINE TMED",null,null,null,null,"2024-12-31"]
["NUMBER OF MED IN REPORTING YEAR",null,null,null,null,7]
[]
["NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years.  If five years of data are not available, then utilities should use what is available until five years are accumulated.        \n"]
[]
[]
[]
["SECTION 4: SYSTEM RELIABILITY INFORMATION AND RESULTS"]
[null,null,"System-wide Information"]
["TOTAL CUSTOMERS",null,445812,null,null,"TOTAL CIRCUITS",null,636]
[]
[null,null,null,"Excluding MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",78.369581507761893,null,null,null,"SAIDI",90.795943788952798]
["SAIFI",0.82340125119872565,null,null,null,"SAIFI",0.87109577410301586]
[]
["Including MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",416.80208720836401,null,null,null,"SAIDI",224.76890301870756]
["SAIFI",1.1707978682979479,null,null,null,"SAIFI",1.1070126099344491]
["Notes:  "]
["1)","All duration indices (SAIDI) are to be reported in units of minutes."]
["2)","Reports are due on the first business day of May of each year"]
["3)","Reports cover the calendar year ending in the December before the reports are due."]
["4)","IEEE 1366 (latest version) is used to define SAIDI, SAIFI, and TMED"]
[]
["SECTION 5: CIRCUIT REPORTING"]
[null,null,null,"BEGIN ON NEXT PAGE"]

{"sheet":"Excle LGE Section 5","index":1,"n_rows":281,"n_cols":22,"rows_kept":281,"cut":false,"hidden":false,"merged":[]}
["Substation Name","Substation Location   \n(County - Road - Town)","Circuit\nNumber","Circuit Location\n (Town - Road - General Area)","Total Circuit Length (Miles)","Average 2025 OMS Custs","Date of Last Circuit Trim (VM)","Animal","Construction","Lightning","Non-Company","Other/Unknown","Overload","Planned Work","Trees","Vehicle","Utility Equipment","2021-2025 SAIDI Average","2025 SAIDI","2021-2025 SAIFI Average","2025 SAIFI","LIST OF CORRECTION ACTION, IF ANY, TAKEN OR TO BE TAKEN"]
["ASHBY","Jefferson - 5400 Vesper Ln - Lousivlle","AB1202","Louisville - Greentree Ln & Dixie Hwy - S of Substation",19.644896430661898,1934,"2025-01-01",2.9161940873078294E-3,0,0,0,0.35430619830947668,0,9.3258189765793809E-2,0.50307142088400625,4.1820168721179558E-2,4.6278282322358456E-3,66.147768007893816,108.34242502188897,0.63040330920372278,1.5429162357807653,"Reliability Improvements Scheduled for 2026"]
["ASHBY","Jefferson - 5400 Vesper Ln - Lousivlle","AB1205","Louisville - Valley Station Rd & Dodge Ln - E of Substation",24.615976778235101,2219,"2025-01-01",9.3304105148009006E-3,0,0,0,1.2078969969692387E-2,9.6695423495469779E-3,5.5240535681382579E-3,0.89546475446916385,0,6.7932269128657685E-2,84.188796750698515,101.88084722352413,0.68571428571428561,0.60883280757097813,"Reliability Improvements Scheduled for 2026"]
["ASHBY","Jefferson - 5400 Vesper Ln - Lousivlle","AB1206","Louisville - Valley Station Rd & 3rd St - E of Substation",25.056828835881401,1417,"2025-01-01",7.0949487281013199E-3,7.2694727955156038E-3,0,0,1.3809216834155232E-3,6.544652528035655E-6,4.8095015265402025E-2,0.93033871849158845,0,5.8143783834490098E-3,95.27054339477769,102.57509996894846,0.9096683133380381,0.98094565984474247,"Reliability Improvements Scheduled for 2026"]
["ASHBY","Jefferson - 5400 Vesper Ln - Lousivlle","AB1207","Louisville - Torrington Rd & Derring Rd - S of Substation",16.082590629825201,1658,"2024-01-01",8.9785860751234972E-2,0,0,0,4.1388992450368161E-3,0,1.5981801659054898E-2,0.45201381769037186,0,0.43807962065430145,94.989632083353413,127.25643344813025,0.83124246079613973,1.1145958986730995,"Reliability Improvements Scheduled for 2026"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1289","Louisivlle - Shelbyville rd & Upton Ln - E of Substation",47.113279335352601,2970,"2023-06-16",1.2064983160638477E-3,0,0,0,0.26457153180123105,0.62611455927326221,2.5910680413435357E-2,7.7390092519710435E-2,0,4.8066376762971466E-3,82.873070704713797,250.65615038989898,1.1701683501683497,2.8569023569023564,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1290","Louisville - Shelbyville Rd & SW of Substation",24.726438252805099,1634,"2023-06-24",0.21087739320359694,1.070423643769308E-2,0,0,0.21646563428503965,0,0.29605871588516558,0.1012573542433246,0,0.16463666594518014,35.422276615911876,28.222735611995109,0.44479804161566711,0.52815177478580178,"Reliability Improvements Scheduled for 2026"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1292","Louisville - Shelbyville Rd - W of Substation",18.003084853505399,1386,"2024-01-01",2.4411467274993534E-2,3.6805343242162698E-3,0,0,0.1866489499306225,3.7181627901507489E-2,5.0222243126925518E-2,0.36570165330072196,0,0.33215352414101268,53.593621929725828,61.357659925685432,0.40432900432900426,0.46897546897546916,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1293","Louisville - New English Station Rd - NE of Substation",4.6712665233023101,158,"2025-01-01",2.8294260307194824E-3,0,0,0,0.84902991107518189,0,1.935125303152789E-2,0.12878940986257073,0,0,151.31694091265823,375.79736284810127,1.289873417721519,1.2468354430379749,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1295","Louisville - N English Station Rd & Avoca Rd - N of Substation",20.382778677574098,960,"2024-01-01",4.1559330220576392E-3,0,0,0,1.6402350668169377E-3,4.3169376911930445E-3,0.34642167122846562,0.62497987441635805,0,1.8485348575108678E-2,71.526392352291666,97.87743053749999,0.73708333333333342,0.41562499999999969,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1296","Louisville - ShelbyvilleRd  & N Beckley Station - NE of Substation",36.930373902365801,1611,"2024-01-01",1.067995728017088E-3,2.3738632318197998E-2,0,0,0.11474481374801773,1.2945402763843491E-3,0.33624065503737988,9.7608336839379917E-2,0,0.42530502605262305,70.433188491495955,88.826008682184948,0.47473618870266926,1.1365611421477353,"Reliability Improvements Scheduled for 2026"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1374","Louisville - S 7th St & Algonquin Pky - SE of Substation",3.5850668278863198,451,"2023-05-12",0.3034794491748134,0,0,0,0,0,0.6965205508251866,0,0,0,48.879519585365856,168.74360679822615,0.51086474501108647,1.2771618625277161,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1380","Louisville - S 7th St - N of Substation",2.9800301636779798,15,"2023-05-12",0,0,0,0.24443186736358491,3.6821253786996036E-2,0,0.64287378899357461,0,0,7.5873089855844456E-2,263.92066659852293,406.69888879999996,2.5333333333333337,5.7333333333333334,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1441","Louisville - Bernheim Ln & 7th St Rd - SW of Substation",4.8194322788155199,49,"2023-05-12",0,0,0,0,0,0.67544910179640716,7.6646706586826346E-2,2.6746506986027943E-2,0.16197604790419162,5.9181636726546909E-2,79.973537391836729,204.47448973469383,0.75918367346938775,1.3673469387755102,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1442","Louisville - S 4th St & S 3rd St - E of Substation",7.1139910613761899,1276,"2023-05-12",0,0,0,0,0.65931417979610751,7.0458758109360517E-2,0,0,0,0.27022706209453196,67.832954543416918,135.29711337382446,1.002664576802508,2.5909090909090908,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1444","Louisville - S 15th St - N of Substation",3.3188375427468899,33,"2023-05-12",0,0,0,0,0,0,0,0,0,1,28.136363612121215,72.682323212121219,0.38181818181818172,1.1212121212121211,"Continue to Monitor"]
["ASHBOTTOM","Fayette - 96 Burley Ave. - Lexington","AS1416","Louisville - Grade Ln - N of Substation",6.2247318610868296,55,"2021-10-30",0.51751815517900368,0,0,0,0,0,8.6635240157981915E-3,0,0,0.47381832080519809,116.62284845818181,140.19363634545454,1.0836363636363635,1.3454545454545455,"Continue to Monitor"]
["ASHBOTTOM","Jefferson - 8113 Grade Ln - Louisville","AS1417","Louisville - Grade Ln - N of Substation",1.93309479558856,25,"2021-10-30",0,0,0,0,0.20223152022315202,0,0.79776847977684806,0,0,0,75.982133288,57.336666600000001,0.68,1.08,"Continue to Monitor"]
["ASHBOTTOM","Jefferson - 8113 Grade Ln - Louisville","AS1418","Louisville - Outer Loop - S of Substation",9.4092379247749101,68,"2021-10-30",0,0,0,0,1.9299820466786355E-2,7.854578096947935E-3,0,0,0,0.97284560143626575,52.610343114705884,131.04754898529413,0.37941176470588228,0.89705882352941146,"Continue to Monitor"]
["ASHBOTTOM","Jefferson - 8113 Grade Ln - Louisville","AS1419","Louisville - Outer Loop & National Turnpike - W of Substation",1.86247679643056,4,"2021-10-30",0,0,0,0,1,0,0,0,0,0,25.983333299999998,97.333333249999995,0.4,1,"Continue to Monitor"]
["BRANDENBURG","Meade - Weldon Church Rd. - Brandenburg","BB1102","Brandenburg - E Broadway St - W of Substation",15.021427135924601,854,"2025-01-01",6.5317838669014514E-2,1.2077125385362741E-3,0,0,9.5646519793006705E-3,1.084784655149546E-3,1.0852159810561661E-2,0.90309077361536305,0,8.8820787320743645E-3,330.23283371498826,979.4354800831378,2.1295081967213108,2.3161592505854789,"Trees Trimmed in 2025"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1217","Louisville - Robarus Ln - N of Substation",2.3255647149151302,69,"2025-01-01",0,0,0,0,6.652360515021459E-2,0.9334763948497854,0,0,0,0,35.884589347826093,47.271980666666664,0.40579710144927539,1.0289855072463767,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1218","Louisivlle - Bishop Ln - N of Substation",3.02305085909836,137,"2025-01-01",1.4096916299559472E-2,0,0,0,0.30249632892804701,4.1116005873715125E-2,0.41497797356828192,0,0.21791483113069016,9.3979441997063141E-3,12.233576632116788,24.849999978102193,9.4890510948905077E-2,0.33576642335766416,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1219","Louisivlle - Pinewood Rd & Produce Rd - SE of Substation",9.1573108550216205,963,"2021-05-08",0.24945850819006363,0,0,0,9.0733721402463788E-2,6.4302152429944492E-4,5.6518207662109108E-3,6.5588195478543387E-2,1.6244754298091241E-3,0.58630025720860968,17.128816196884735,30.680668048805817,0.25856697819314645,0.34060228452751817,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1220","Louisville - Popular Level Rd. & Gilmore Ln - W of Substation",13.804345686238401,1115,"2021-05-08",1.4122522784116782E-2,3.913390659337033E-3,0,0,1.976493258805129E-3,1.756076314417512E-2,1.7847833116655998E-2,0.59471329298955322,0,0.34986570404735667,63.97321673452916,110.26733930582959,0.63605381165919272,1.3605381165919281,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1222","Louisville - Bishop Ln - E of Substation",1.2704658257499899,46,"2025-01-01",0,0,0,0,0,0,0,0,0,1,0.27536231739130435,0.32028984782608694,8.6956521739130436E-3,2.1739130434782608E-2,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1224","Louisville - Popular Level Rd & Preston Hwy - W of Substation",13.513176586092801,1224,"2025-01-01",4.2885798047038598E-2,0,0,0,2.1775740075385193E-2,3.8794718628077675E-4,3.4809442987193337E-2,0.83318491414464257,6.4736482465228035E-2,2.2196750942314897E-3,72.936985286437903,80.79748092728758,0.88986928104575147,0.96895424836601274,"Reliability Improvements Scheduled for 2026"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1179","Louisville - Breckenridge Ln - S of Substation",11.7680828035893,2397,"2025-01-01",3.5332888697085015E-2,1.2135954071691057E-2,0,0,1.5337335059568181E-2,5.9084310879202795E-2,2.5493350072580329E-2,0.63214981626060907,0,0.22046634495926348,47.416337085523573,60.974412457238202,0.3920734251147267,0.57321652065081352,"Reliability Improvements Scheduled for 2026"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1180","Louisville - Dutchmans Ln - W of Substation",8.7059721729071597,549,"2025-01-01",7.733464929937795E-3,2.3339999740269859E-2,0,0,0,0,0.72607885407062056,0.24121462800150642,0,1.6330532576652858E-3,201.51241043205829,561.04049786156645,1.2688524590163937,1.5100182149362482,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1181","Louisville - Browns Ln - SE of Substation",24.556890893348999,2127,"2024-03-01",2.061501460230201E-3,0,0,0,0.38752097842030842,1.4040675009580696E-5,8.1386359732004802E-3,4.3340260066338059E-2,0.38751271919971458,0.17141186420519869,148.66037767917257,349.92541920827466,1.1657733897508227,1.6234132581100138,"Reliability Improvements Completed in 2025"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1185","Louisville - Taylorsville Rd - S of Substation",14.8689997043196,1828,"2024-03-01",1.6306435890352675E-2,0,0,0,6.1103490539377719E-2,1.809568262858921E-2,1.4095676278112765E-2,0.87382555876254608,0,1.6573155901021475E-2,148.03677971608317,377.1696024731948,1.0903719912472645,1.7335886214442007,"Reliability Improvements Scheduled for 2026"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1186","Louisville - Richland Dr & Hunsinger Ln - S of Substation",13.131097534359499,1682,"2020-09-19",4.5513911425970636E-3,0,0,0,0.73162359335628813,5.5099536945422883E-2,6.0627168507011775E-2,1.0931254205089643E-2,0,0.13716705584359046,89.21049543638523,103.21094926040428,1.2431629013079672,1.87217598097503,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1351","Louisville - Brekenridge Ln & Shelbyville Rd - NW of Substation",8.5627536912806406,356,"2025-01-01",0,0,0,0,0.36695092370825771,0,0,0.63147778065933391,0,1.5712956324083539E-3,84.203473780337077,203.57176966011235,0.40674157303370784,0.99719101123595499,"Trees Trimmed in 2025"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1354","Louisville - Taylorsville Rd - S of Substation",9.2927465412853802,37,"2025-01-01",0,0,0,0,0,0,0.16536539662710806,0.79950031230480945,0,3.5134291068082447E-2,119.78072067027028,173.07927921621621,1.4162162162162162,1.0540540540540539,"Trees Trimmed in 2025"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1278","Louisville - Ellinsgworth Ln - NE of Substation",21.837437007962802,1964,"2021-11-13",0,1.8843836800952797E-3,0,0,3.3853646200845931E-3,1.8941726862256446E-2,4.2977815664857061E-2,0.87042211010184656,0,6.2388599070860168E-2,69.728742359877785,113.13395281364562,0.85926680244399178,2.201629327902241,"Tree Trim Scheduled for 2026"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1284","Louisville - Watterson Trail - SW of Substation",7.8622161334663501,328,"2021-10-23",2.0364100299327739E-2,0,0,0,0.52796179073228977,0.27305886778873678,5.5285669888937962E-3,9.2415394932692154E-3,8.4596888954315719E-2,7.9248245743166981E-2,60.28136178231707,37.136128039634151,0.90975609756097531,1.11890243902439,"Continue to Monitor"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1304","Louisivlle - Portland Ave & S 20th St - S of Substation",4.4217922423558003,22,"2023-03-31",0,0,0,0,0.49358296205393576,9.8023806213312862E-3,5.4105030256500165E-4,0,0,0.49607360702216796,248.26287875401286,616.96212110442457,3.1727272727272728,7.3636363636363642,"Continue to Monitor"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1341","Louisville - S 20th St & W Market St - S of Substation",6.0685675116406399,464,"2023-03-31",0,0,0,0,0,0,0,0,0,1,165.85201867453571,244.50635775431033,2.5668103448275859,3.5538793103448274,"Continue to Monitor"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1342","Louisville - Portland Ave - W of Substation",4.1221083065975597,68,"2023-03-31",0,0,0,0,0.39294780595307838,0,0,0,0,0.60705219404692168,290.24328426366873,320.23676467647061,2.7823529411764705,0.89705882352941169,"Continue to Monitor"]
["CROP","Jefferson - 116 N 26th St - Louisville","CB0002","Louisville - Duncan St - E of Substation",3.6496591694616201,622,"2023-02-24",0,0,0,0,0,7.0201197179689895E-2,5.9342680585359554E-2,0.68815243872924703,0,0.18230368350570356,37.074474808574493,48.176420144694532,0.4160771704180064,0.2347266881028939,"Continue to Monitor"]
["CENTERFIELD","Oldham - 4210 Hwy 393 - Centerfield","CF1203","Centerfield - S Camedn Ln - S of Substation",62.303477446064299,1229,"2024-01-01",0.1810081734310871,0,0,0,0.18528782404321745,1.4487669695162592E-2,0.31360718420037181,0.15045427438874662,0,0.15515487424141439,71.512432864605387,23.167331152156219,0.87046379170056942,0.90968266883645255,"Continue to Monitor"]
["CENTERFIELD","Oldham - 4210 Hwy 393 - Centerfield","CF1204","Centerfield - S Hwy 393 - N of Substation",72.699583646509694,2041,"2025-01-01",7.7526086265647344E-3,4.6937622486272708E-2,0,0,2.6799555076890483E-2,9.293949398824131E-3,2.0874309221561114E-2,0.74678754921520518,0,0.14155440597468175,114.12444552572269,268.86932875012252,1.3365017148456637,1.0489955903968642,"Trees Trimmed in 2025"]
["CLARKS LANE","Jefferson - 934 Clarks Ln - Louisville","CK0003","Louisville - Eastern PKY - W of Substation",0.26422801893724102,222,"2023-05-12",0,0,0,0,0,0,0.10415166786657068,0,0,0.89584833213342929,50.015795789189184,37.53971471171171,0.49459459459459465,0.9144144144144144,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1231","Louisville - Payne St, Grindstead Dr, & Lexington Rd - SE of Substation",5.2559332493623696,673,"2022-05-13",0,0,0,0,0.6562238987236616,5.8692599766132565E-5,0,0.33817773022172259,0,5.5396784548495887E-3,96.29617136790489,280.82233778306085,0.85973254086181261,1.0312035661218424,"Tree Trim Scheduled for 2026"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1232","Louisville - Frankfort Ave, Story Ave, & E Main St - W of Substation",13.521942243142799,1932,"2022-08-12",2.3725396933251793E-3,1.2949876559987316E-2,0,0,0.10374623451337456,0.37355326040180292,5.9466376752508439E-2,1.1607891100994315E-3,0.18826866888632193,0.25848225408258024,50.249199443271223,73.491330221532081,0.98281573498964792,1.915631469979296,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1404","Louisville - None - In Sub",2.7096151802130399,2,"2022-05-13",0,0,0,0,0,0,0,0.1038961038961039,0,0.89610389610389607,75.6566665,76.999999500000001,0.8,1,"Continue to Monitor"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1192","Louisville - Winchester Acres Rd & La Grange Rd - S of Substation",28.890624726215702,1115,"2024-01-01",2.2637173612137663E-2,0,0,0,9.6434762743069086E-2,2.6877024175883245E-4,0.17308131643664415,0.51820246462311692,0.16376842755970059,2.5607084783572764E-2,100.98849027713004,131.22813153273543,0.8356950672645741,1.0690582959641255,"Reliability Improvements Scheduled for 2026"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1193","Louisville - Westport Rd, Rollington Rd, Collins Ln - NE of Substation",6.74603034910277,322,"2023-12-16",3.023598820058997E-2,0,0,0,0.96976401179941008,0,0,0,0,0,1.9557867478260871,4.2105072453416152,8.6956521739130418E-3,6.2111801242236021E-3,"Continue to Monitor"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1194","Louisville - Collins Ln & La Grange Rd - S of Substation",1.3291679823879701,34,"2023-12-16",0,0,0,0,0,0,1,0,0,0,83.058627441176469,345.09411764705885,0.4,0.70588235294117652,"Continue to Monitor"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1196","Louisville - Westport Rd & Accomack Dr - NW of Substation",10.546106318341099,982,"2025-01-01",9.9916197421232922E-2,0,0,0,0,1.2658600055868385E-2,1.9289295323228015E-2,0.63495890733199056,0,0.23317699986768015,66.64301425262083,69.260522739307532,0.9741344195519348,0.57026476578411411,"Trees Trimmed in 2025"]
["CANE RUN GENERATING","Jefferson - 5252 Cane Run Rd. - Louisville","CR1421","Louisville - Elmwood St, Lees Ln, & Campground Rd - NE of Substation",2.2040804409999599,3,"2025-01-01",0,0,0,0,0.10079726651480637,0,0,0,0,0.89920273348519364,307.32222200000001,585.18333300000006,0.66666666666666663,0.66666666666666663,"Continue to Monitor"]
["CONESTOGA","Bullitt - 1365 N Buckman St. - Shepherdsville","CS1260","Shepherdsville - Buckman St & N Preston Hwy - N of Substation",8.6213477625005197,249,"2025-01-01",9.7664920536269205E-3,0,0,0.69368729468170109,0,0,0.15533161679836632,4.7278700168693955E-2,6.0152712421202167E-2,3.3783183876409481E-2,65.10278446104418,72.835073618473913,0.85702811244979915,0.87550200803212863,"Continue to Monitor"]
["CARTER","Jefferson - Opposite 2215 Carter St - Louisville","CT0003","Louisville - Portland Ave & N 20th St - SE of Substation",0.51210101605382796,48,"2023-04-07",0,0,0,0,1,0,0,0,0,0,9.4870833250000004,14.352430541666665,0.10416666666666667,0.14583333333333334,"Continue to Monitor"]
["CRESTWOOD","Oldham - Floydsburg Rd. - Crestwood","CW1223","Crestwood - Floydsburg Rd - NW of Substation",0.343982261592362,46,"2023-04-04",1.4933363387901158E-3,0,0,0,0,0,0.33152066721140572,0.66698599644980427,0,0,188.97057969999997,771.53840576086952,0.79565217391304355,2.9347826086956523,"Continue to Monitor"]
["CRESTWOOD","Oldham - Floydsburg Rd. - Crestwood","CW1226","Crestwood - Floydsburg Rd, Hawley Gibson Rd, & Ash Ave - S of Substation",27.6054533330277,664,"2023-03-10",5.0832229998108566E-3,1.3594666162284851E-3,0,0,2.9683658029128049E-2,6.4781539625496497E-3,9.7042273501040291E-2,0.83821165121997354,0,2.2141573671269149E-2,63.124116453614455,127.39558231174699,0.38192771084337351,0.30572289156626514,"Continue to Monitor"]
["CRESTWOOD","Oldham - Floydsburg Rd. - Crestwood","CW1227","Crestwood - HWY 22, Carriage Hill Dr, & Mary Clayton Ln - NE of Substation",16.497736144512999,990,"2022-12-17",0.29551582233574569,0,0,0,0.65343408542642267,2.0930892578402156E-3,4.6686533276571587E-2,0,0,2.270469703419895E-3,36.872781139393943,28.472070704040402,0.255959595959596,0.30909090909090919,"Continue to Monitor"]
["CRESTWOOD","Oldham - Floydsburg Rd. - Crestwood","CW1228","Crestwood - HWY 329, I 71, Covered Bridge Rd, & Halls Hill Rd - N of Substation",78.900872880980103,1517,"2023-12-16",2.4395904205038801E-3,0,0,0,0.26107579711211359,6.7869858322625931E-2,0.11662204461450509,0.37375827111717391,1.1306454443054526E-2,0.16692798397002304,125.42216435003294,220.58910128675012,0.9676994067237974,1.0837178642056693,"Continue to Monitor"]
["CLAY LGE","Jefferson - 908 Clay St. - Louisville","CY1483","Louisville - Breckinridge St, Vine St, Highland Ave, & Barrett Ave - E of Substation",1.9982558601428,25,"2022-06-17",0,0,0,0,0,0,1,0,0,0,51.617333327999994,215.82,0.36000000000000004,0.60000000000000009,"Continue to Monitor"]
["CLAY LGE","Jefferson - 908 Clay St. - Louisville","CY1486","Louisville - Caldwell St, Logan St, Jackson St, Goss Ave, & Ash St - S of Substation",4.3679151459403203,266,"2022-06-17",0,0,0,0,0,0,0.34022556390977443,0,0,0.65977443609022557,23.54210526060217,15.632456136777943,0.86842105263157898,2.011278195488722,"Continue to Monitor"]
["CLAY LGE","Jefferson - 908 Clay St. - Louisville","CY1487","Louisville - Clay St, Shelby St, & Bergman St - S of Substation",1.7444991269793799,15,"2022-06-17",0,0,0,0,0,1,0,0,0,0,57.247333306402403,30.616666666492964,0.78666666666666674,1.1333333333333333,"Continue to Monitor"]
["DAHLIA","Jefferson - 2135 Dahlia Ave. - Louisville","DA1237","Louisville - Bardstown Rd, Landor Ave, & Wood Creek Rd - NE of Substation",7.6207413766641103,952,"2024-03-01",1.9232426779444804E-2,0,0,0,0.22189405214073515,2.3174298536450821E-2,4.606703480454407E-2,0.24676347045607344,0,0.44286871728275173,67.890413160714289,87.242279404411747,0.53466386554621848,0.91701680672268893,"Reliability Improvements Scheduled for 2026"]
["DAHLIA","Jefferson - 2135 Dahlia Ave. - Louisville","DA1238","Louisville - Bardstown Rd, Gold Smith Ln, & Peabody Ln - SE of Substation",10.0085177494158,1784,"2022-02-11",9.5130544265771333E-2,0.10408751546209577,0,0,0.1651186163633151,4.9119764976144197E-2,4.2023767450079519E-3,0.55661888142781413,0,2.5722300759851564E-2,67.548394989013445,79.270945437219723,0.57107623318385647,0.46804932735426008,"Continue to Monitor"]
["DAHLIA","Jefferson - 2135 Dahlia Ave. - Louisville","DA1240","Louisville - Eleanor Ave, Lakeside Dr, Dundee Rd, & Newburg Rd - W of Substation",11.696775221100101,1272,"2024-03-01",1.216028543362652E-2,0,0,0,0.10169702033488771,0,9.6424176047512061E-3,0.75612248354353206,0,0.12037779308320255,80.967769909591198,109.65714098034591,0.46525157232704401,0.43867924528301894,"Reliability Improvements Scheduled for 2026"]
["DAHLIA","Jefferson - 2135 Dahlia Ave. - Louisville","DA1242","Louisville - Bardstown Rd, Doup Ave, Taylorsville Rd, & Millvale Rd - N of Substation",11.1188904809826,1287,"2024-03-01",2.1718960266307812E-2,0,0,0,5.2330193356470003E-2,2.8560804589560167E-2,1.3949288193214816E-2,0.73974785749698979,9.4482612083008708E-3,0.13424463488915644,114.57868686247085,157.09642579020979,0.97544677544677527,0.69930069930069905,"Reliability Improvements Scheduled for 2026"]
["DEL PARK","Jefferson - 3135 Del Park Terrance - Louisville","DE1408","Louisville - Magazine St, S 28th St, W KY St, & Grand Ave - E & S of Substation",2.64764772696115,79,"2023-03-24",0,0,0,0,0,0,0,0,0,1,58.758649784810132,291.7339662278481,0.20506329113924049,1,"Continue to Monitor"]
["DUMESNIL","Jefferson - 1309 Dumesnil St - Louisville","DU0001","Louisville - Dumesnil St, W Magnolia Ave, & S 13th St - S & E of Substation",1.9829143492690899,46,"2022-11-18",0,0,0,0,0.85090331546555498,0,0,0,9.529481834425254E-3,0.13956720270001985,60.291811582608695,69.220289847826081,0.41304347826086951,0.39130434782608692,"Continue to Monitor"]
["DUMESNIL","Jefferson - 1309 Dumesnil St - Louisville","DU0003","Louisville - S 15th St, Wilson Ave, & W Kentucky St -  W & N of Substation",2.70758719590214,388,"2022-11-18",0,0,0,0,0,1.351460929264535E-4,2.1772035570451657E-2,0.97434927156255913,3.7435467740627617E-3,0,23.360541230927833,31.728865974226807,0.2020618556701031,0.17268041237113399,"Tree Trim Scheduled for 2026"]
["DIXIE","Jefferson - 1706 Bernheim Ln. - Louisville","DX1220","Louisville - Bernheim Ln, 7th Street Rd, & Taylor Blvd - SE of Substation",20.689345246664299,3145,"2023-08-19",2.3820973612260579E-3,6.1430524714668408E-4,0,0,5.7031144396656776E-3,1.1013274520829345E-2,3.4493302439683765E-2,0.92560147895558553,1.9051502648421925E-2,1.1409243874409376E-3,80.344586108616852,107.72577635135134,0.93945945945945974,1.5608903020667724,"Reliability Improvements Scheduled for 2026"]
["DIXIE","Jefferson - 1706 Bernheim Ln. - Louisville","DX1221","Louisville - Dixie Hwy, Ralph Ave, & Fitzgerald Rd - SW of Substation",14.2739336449406,1560,"2023-06-16",1.9657465063878436E-2,3.973671650405692E-2,0,0,0.39896551341391673,7.9473433008113836E-3,0.21335730855893353,5.3389275526400493E-2,2.992463343434007E-2,0.23702174419766242,28.994273500000002,41.495106831410254,0.38115384615384607,0.66410256410256374,"Reliability Improvements Scheduled for 2026"]
["EIGHTH STREET","Jefferson - 841 S 8th St - Louisville","EI0001","Louisville - S 8th St, York St, S 6th St, & S 5th St - NE of Substation",1.1477304722297399,128,"2025-01-01",0,0,0,0,0,6.360548201944477E-2,0.93639451798055529,0,0,0,13.8304427078125,66.697265625,8.59375E-2,0.3984375,"Continue to Monitor"]
["EIGHTH STREET","Jefferson - 841 S 8th St - Louisville","EI0002","Louisville - W Breckenridge St, S 6th St, & S 4th St - E of Substation",1.9673744658771199,167,"2025-01-01",0,0,0,0,1,0,0,0,0,0,45.755429135589807,102.2013972048951,0.34491017964071863,1.0119760479041917,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1167","Louisville - Shepherdsville Rd, Bashford Ave, & Buechel Bank Rd - NE & SE of Substation",9.5543738152868301,806,"2020-04-25",0,0,0,0,8.862902019785469E-3,1.8115531547535427E-3,7.273402910267507E-4,0.98117072330706456,3.2175177983114828E-4,7.1057294475385989E-3,382.39698923995036,705.47450371588093,1.120843672456576,1.186104218362283,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1168","Louisville - Ethel Ave, Bardstown Rd, Buechel Bank Rd, & Bradford Dr - E of Substation",13.071363458254099,1682,"2024-02-01",1.205050150406206E-3,0,0,0,9.5731395993369009E-2,1.1574654593015853E-4,2.9746862304050742E-3,0.85255433335776876,4.1153041369101591E-2,6.2657463530192484E-3,102.75083035659927,311.26834125505354,0.616884661117717,1.5362663495838287,"Reliability Improvements Scheduled for 2026"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1172","Louisville - Hikes Ln - NE of Substation",13.592291069864499,2031,"2020-07-11",4.4625437915626509E-2,0,0,0,0.21453670100065031,3.5169607082170803E-2,1.546602613858063E-2,0.6660827791646563,6.0416622962512325E-3,1.8077786402064235E-2,55.355637611422956,61.270909234859673,0.36267848350566212,0.24766125061546038,"Reliability Improvements Scheduled for 2026"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1173","Louisville - Shepherdsville Rd, Rural Way, & Rangeland Rd - S of Substation",13.229501594624899,1765,"2020-07-11",1.0867774355854656E-3,0,0,1.1672559978708034E-2,4.7526710011026196E-4,0,0.16572246936111429,0.12157332420820502,0.5295299291535176,0.16993967276275934,137.155671383796,178.816591117847,1.2747875354107649,0.74504249291784674,"Reliability Improvements Scheduled for 2026"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1421","Louisville - Ethel Ave, Bardstown Rd, Buechel Bank Rd, & Progress Blvd - E of Substation",3.4659582573715499,9,"2020-05-02",0,0,0,0,0,0,0,1,0,0,681.86481473333333,1416.1925924444445,1.4222222222222221,2,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1423","Louisville - Jennings Ln, Bishop Ln, & Robards Ln - W of Substation",5.1849348628033596,58,"2020-05-02",1.6862019329631914E-2,0,0,0,6.5803002261978199E-3,0,0,0,0,0.97655768044417024,163.40218389310343,83.831896534482766,0.70344827586206882,0.87931034482758619,"Continue to Monitor"]
["EASTWOOD WEST","Jefferson - 100 Flat Road Rd. - Louisville","EW1240","Louisville - Shelbyville Rd & Beckley Creek PKWY - W of Substation",14.920710038554001,370,"2025-01-01",2.640671273445212E-3,0,0,0,0.19945705824284304,4.3682132280355376E-3,0.22840572556762093,0.10404738400789733,0,0.46108094768015795,100.88398196918919,98.109909881081066,0.92702702702702722,2.4729729729729737,"Continue to Monitor"]
["EASTWOOD WEST","Jefferson - 100 Flat Road Rd. - Louisville","EW1241","Louisville - Gilliland Rd, Shelbyville Rd, & Long Run Rd - E & SW of Substation",84.331609820856301,2267,"2025-01-01",3.4915319724386634E-2,0,0,5.718333440659411E-4,9.9377938051387726E-2,0.10328546590250499,0.43349861549359264,0.18943911391589927,1.4671904179277481E-2,0.12423980938888531,73.180832222055557,167.35593293206873,0.51662990736656422,1.3149536832818718,"Reliability Improvements Scheduled for 2026"]
["EASTWOOD WEST","Jefferson - 16000 Shelbyville Rd - Middletown","EW1242","Simpsonville - Liberty Ave, Johnson Rd, & Aiken Rd- N & NW of Substation",35.904120803081703,1210,"2024-01-20",7.5773901394915397E-2,0,0,0,0.56419814205422414,0,3.0300824135822243E-2,0.30321937156003381,0,2.6507760855004513E-2,35.276140490578513,37.436129470247934,0.42181818181818176,0.3487603305785123,"Continue to Monitor"]
["EASTWOOD WEST","Jefferson - 16000 Shelbyville Rd - Middletown","EW1243","Simpsonville - Eastwood Fisherville Rd & Shakes Creek Rd - SSE of Substation",23.131383517657099,620,"2024-01-20",0,0,0,0,1.924188620034685E-2,3.179453299198943E-3,0.7210752332975473,0.19939714262119085,0,5.7106284581716078E-2,25.85657526516129,39.059247306451617,0.2129032258064516,0.1290322580645161,"Continue to Monitor"]
["FARNSLEY","Jefferson - 2428 Farnsley Rd. - Louisvlle","FA1149","Louisville - Farnsley Rd & Burrell Dr - E of Substation",7.6666039809522202,1023,"2021-10-16",0,0,0,0,0.29667240279201068,0,2.4221272646416211E-2,0.34757439238964405,7.3512635588468461E-2,0.25801929658346062,65.54799282971652,196.32041381329427,1.0087976539589443,2.9882697947214076,"Tree Trim Scheduled for 2026"]
["FARNSLEY","Jefferson - 2428 Farnsley Rd. - Louisvlle","FA1216","Louisville - Crums Ln, Hillview Ave, & Garrs Ln - SE of Substation",10.4202590489302,1337,"2024-01-01",1.2578126217677956E-2,0,0,0,6.4705319151304903E-3,6.7065526938654635E-3,0.10029547129564274,0.47456876109130663,0,0.39938055678637668,124.445681868362,168.97726252206434,1.4683620044876591,1.6125654450261779,"Reliability Improvements Scheduled for 2026"]
["FALLS CITY","Jefferson - 1048 S 43rd St - Louisville","FC0001","Louisville - Greenwood Ave & Cecil Ave - E of Substation",2.3864795303466901,491,"2023-02-10",0,0,0,0,0.91811208286509993,0,2.0129965310011239E-2,4.1237113402061855E-2,0,2.0520838422826988E-2,33.175207057433809,41.682824167006117,0.30509164969450103,0.73930753564154794,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1210","Louisville - N Hurstbourne PKY, Whipps Mill Rd, & La Grange Rd - SW of Substation",17.330218080511099,1586,"2024-01-01",2.0134582747257827E-2,0,0,0,0.37074971439137294,0.24206404236913182,1.6245022485488439E-3,0.2202983537056481,0,0.14512880453804042,54.918669606305158,91.925746106557384,0.94312736443883993,2.4974779319041622,"Reliability Improvements Scheduled for 2026"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1213","Louisville - Westport Rd, Blossom Ln, Goose Creek Rd & Brownsboro Rd - W of Substation",30.907428594956698,2396,"2024-01-01",7.2517013342855768E-3,0,0,0,5.5225551259777093E-3,2.9597379498836019E-3,1.1279966488349896E-2,0.9355450106784049,0,3.7441028423098315E-2,97.211035054590994,136.53096827629383,1.0779632721202002,0.44574290484140228,"Reliability Improvements Scheduled for 2026"]
["FLOYD","Jefferson - 1806 S Floyd St. - Louisville","FL1495","Louisville - Floyd St, Burnett Ave, & Shelby St - E of Substation",4.1603958000305399,20,"2025-01-01",0,0,0,0,6.1140043453102315E-4,3.5046346336510431E-3,0,0,1.6606072516458681E-2,0.97927789241535923,65.87483329328083,163.20666663333333,0.80999999999999994,2.5,"Continue to Monitor"]
["FLOYD","Jefferson - 1806 S Floyd St. - Louisville","FL1496","Louisville - Floyd St, Warnock St, & Crittenden Dr - SE of Substation",3.82117009621521,143,"2025-01-01",0,0,0,9.3480240127366825E-4,0,2.1471242654254566E-3,0,0.24504481695887356,0,0.75187325637442726,208.33624708220378,482.83228437172124,1.6377622377622376,4.2027972027972025,"Continue to Monitor"]
["FLOYD","Jefferson - 1806 S Floyd St. - Louisville","FL1497","Louisville - S Floyd St & Crittenden Dr - S of Substation",3.73721991063602,428,"2025-01-01",0,0,0,0,0,1,0,0,0,0,42.955210278971961,73.973247661214941,0.54859813084112152,0.85747663551401876,"Continue to Monitor"]
["FLOYD","Jefferson - 1806 S Floyd St. - Louisville","FL1499","Louisville - S Floyd St, W Cardinal Blvd, & S Brook St - N & S of Substation",2.1568208994812599,8,"2025-01-01",0,0,0,0,0.21058965102286403,0,0,0,0,0.78941034897713602,68.394999949999999,311.58958312499999,0.4,1.875,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1256","Louisville - Bardstown Rd, Lands Ln, & HWY 44 -  S of Substation",39.344455323495701,2073,"2023-06-16",2.0238127415736413E-3,2.2670757088412573E-3,0,0,7.7915101224423605E-2,4.0513420007027595E-2,3.046192934562262E-2,0.35447806578911806,1.1331999891883125E-2,0.48100859529151013,37.40740954857695,84.891743041485782,0.41630487216594314,0.55571635311143297,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1259","Louisville - Fairmount Rd & Cedar Creek Rd - W of Substation",26.9556100368332,1018,"2024-01-01",3.3529384522762006E-3,0,0,0,0.5253647015236419,2.5471217524197657E-3,1.3421016070022693E-2,0.4312138192932895,4.5199833279303478E-3,1.9580419580419582E-2,103.22151931375245,75.893582184675822,1.2899803536345775,1.3654223968565817,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1260","Louisville - Thixton Ln & Independence School Rd - SW of Substation",47.394836483881001,1884,"2021-07-24",2.4614804599525759E-2,1.9445794846864366E-2,0,0,2.2372585397795484E-2,1.1601334748775543E-2,0.2793514099854818,0.45381127657674641,0.15095294316073538,3.784985068407528E-2,29.258895962420375,98.635881099256892,0.24108280254777087,0.90552016985138084,"Reliability Improvements Scheduled for 2026"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1261","Louisville - Fairmount Rd, Back Run Rd, & Dawson Hill Rd - E of Substation",34.650721169379104,870,"2021-11-20",1.1550948621655554E-4,2.5302077933150261E-4,0,0,1.2939812682116519E-3,4.1544911875887811E-2,3.4611592477032174E-3,0.25806881890175232,0,0.695262598440897,240.24849041241379,650.10001914712632,1.2643678160919536,1.4356321839080457,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1262","Louisville - Bardstown Rd & Stone Breaker Rd - NNW of Substation",35.894809629749098,2364,"2021-08-28",0,0,0,0,9.1022889842632335E-2,1.3170074896911554E-2,0.12334848102331061,0.30298535723302195,0,0.46947319700412354,31.438464464805417,38.952531017766503,0.37453468697123515,0.39128595600676819,"Reliability Improvements Scheduled for 2026"]
["FORTY FOURTH STREET","Jefferson - 128 N 44th St - Louisville","FO0002","Louisville - N 44th St, W Market St, & Fontaine Landing Ct - SW of Substation",2.5737583685971899,359,"2023-03-17",3.3020961775585694E-2,0,0,0,0.65886559802712696,0,1.998766954377312E-2,0.24435265104808879,0,4.3773119605425403E-2,137.21447538941504,192.79712162674093,0.51866295264623952,0.66852367688022274,"Continue to Monitor"]
["FORTY FOURTH STREET","Jefferson - 128 N 44th St - Louisville","FO0003","Louisville - Duncan St & N Longworth Ave - W of Substation",1.48871050385967,250,"2023-03-17",2.8770386659336632E-2,0,0,0,0.43033412742043858,0,0.13986113656262089,0.31745159122839167,0,8.3582758129212231E-2,84.121093328000001,140.90586665200004,0.3952,0.65600000000000014,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1134","Louisville - Preston Hwy, Loretta St, & Ulrich Ave - NW of Substation",15.5462235483102,1841,"2021-01-23",2.2082656585787949E-2,9.457916350457115E-3,0,0,3.3999914889391671E-2,4.9470541090692449E-4,0,0.51689977516614305,0.32874681721787608,8.8318214379437279E-2,57.345908017816406,65.114946585008155,0.52797392721347092,0.63443780554046714,"Reliability Improvements Scheduled for 2026"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1137","Louisville - Fern Valley Rd, Industrial Blvd, & Orange Dr - W of Substation",6.4267050627012301,434,"2021-06-12",0,0,0,0,0.17717989823656513,5.7154805882762951E-3,3.3665574684603052E-2,0,0.70934690179131521,7.4092144699240262E-2,35.176528413364053,33.057757288018429,0.42534562211981564,1.161290322580645,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1138","Louisville - Fern Valley Rd & Shepherdsville Rd - E of Substation",11.101219723713299,1565,"2021-05-01",0,8.563429571303588E-2,0,0,0.1152755905511811,8.7489063867016617E-5,0.12817147856517935,0,0,0.67083114610673666,14.534306707220447,36.518551647923324,0.16421725239616614,0.5335463258785943,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1139","Louisville - Industrial Blvd, Grade Ln, & Knopp Ave - W of Substation",8.49660719530136,222,"2021-06-12",0,0,0,8.658515181653309E-3,0.6133212426139355,0,0.18092201485988418,0,9.2055227286023514E-2,0.10504300005850348,80.800450431531516,86.990090067567564,0.80180180180180172,1.3468468468468466,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1140","Louisville - Preston Hwy, Minor Ln, & Rossmoor Dr - SE of Substation",11.6422792774698,1342,"2021-05-01",0,0,0,0,0,2.4643120434287246E-2,3.9608605321359161E-3,0,0.61191609141478454,0.35947992761879233,154.48245404709388,111.18469945156481,1.2257824143070044,2.0163934426229506,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1143","Louisville - Preston Hwy, Clay Ave, Minor Ln, Foreman Ln, & Bonaventure Blvd - S of Substation",18.719811593795399,1508,"2021-06-12",7.890994647982005E-3,0,0,0,0.7295808878661737,1.1164257827649508E-2,2.8931923365307546E-2,7.0367401815032191E-2,0,0.15206453447785506,55.838649421220154,119.74332448607426,0.60145888594164476,2.0232095490716184,"Reliability Improvements Scheduled for 2026"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1145","Louisville - Preston Hwy, Lipps Ln, & Lone Oak Ave - S of Substation",7.6343839156818696,1222,"2021-06-12",3.6995691524204039E-2,0,0,0,3.9380575878071054E-2,0,4.5345093227297465E-3,0.42027935898736979,0,0.49880986428762536,54.444596286906702,147.1065739181669,0.98690671031096566,2.3281505728314245,"Tree Trim Scheduled for 2026"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1472","Louisville - Grade Ln & Lotus Ave - W of Substation",7.2077643418758299,3,"2021-02-27",0,0,0,0,0.43163841807909603,9.0395480225988704E-3,0.55932203389830504,0,0,0,73.29222213333334,295.0111106666667,0.73333333333333328,1.6666666666666665,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1475","Louisville - Old/Fern Valley Rd, & Industrial Blvd - W of Substation",2.4227984084827598,11,"2021-02-27",0,0,0,0,0,0,0,0,1,0,97.719696945454558,164.86666663636365,0.83636363636363631,1,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1476","Louisville - Forest Dr, E Indian Trail, Poplar Level Rd, & Taylor Ave - NNW of Substation",11.9159735711947,103,"2021-02-27",0,0,0,0,0,2.0228353489270282E-2,1.4459169140898448E-2,0,0,0.96531247736983128,142.4505501514563,402.19320386407765,0.73980582524271832,0.69902912621359214,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1477","Louisville - Preston Hwy & Outer Loop - SW of Substation",6.2746704301651901,29,"2021-02-27",0,0,0,0,0.94937339198273718,0,0,0,0,5.062660801726284E-2,234.76597698620691,166.34252872413791,1.0137931034482759,1.5517241379310345,"Continue to Monitor"]
["GAULBERT","Jefferson - 2950 Wilson Ave - Louisville","GA0003","Louisville - Southern Ave & S 32nd St - NW of Substation",4.8580781455455897,536,"2023-01-20",0,0,0,0,8.084456326040701E-2,3.491734409951443E-4,3.6215832833215125E-2,1.4730754541982651E-3,0.83369523705603144,4.7422117955153033E-2,58.31320273208955,158.60740049253735,0.36007462686567171,0.49813432835820898,"Continue to Monitor"]
["GRAND","Jefferson - 1038 S 34th St - Louisville","GD0001","Louisville - Greenwood Ave, S 28th St, Virginia Ave, & S 26th St - E of Substation",4.1441434284026899,768,"2023-01-13",0,0,0,3.1279841796184762E-3,0,0,4.5446000917341516E-2,2.2843307542502238E-2,0,0.92858270736053772,66.861935759635429,173.16597221614586,0.54010416666666661,1.548177083333333,"Continue to Monitor"]
["GRAND","Jefferson - 1038 S 34th St - Louisville","GD0003","Louisville - Louisville Coleman Jr Dr - N of Substation",1.1103448183829101,157,"2023-01-13",0,0,0,0,0,1.7481425984891053E-4,0.16210276581132546,0,0.12708996691015795,0.71063245301866762,105.91641188407645,510.09639065605097,0.45095541401273892,2.0127388535031847,"Continue to Monitor"]
["GOSS","Jefferson - 1260 Goss Ave - Louisville","GO0002","Louisville - Reasor Ave, E Burnett Ave, & Texas Avenue - SW of Substation",2.0369273439172599,704,"2022-07-15",0,0,0,0,6.0469661523882848E-2,0,0.91904557434333267,4.8861381740649714E-4,0,1.9996150315378009E-2,67.60374525738635,191.86254732244316,0.61392045454545463,1.4133522727272736,"Continue to Monitor"]
["GOSS","Jefferson - 1260 Goss Ave - Louisville","GO0003","Louisville - Ash St & Hickory St - NW of Substation",1.5131025999829599,412,"2022-07-15",0,0,0,0,4.1373435069264393E-2,4.8892510556337509E-3,0.43803244684791465,0,0,0.51570486702718721,37.91601941262136,65.530097077669907,0.2645631067961165,0.33009708737864074,"Continue to Monitor"]
["GRADY","Jefferson - 1838 S 39th St. - Louisville","GR1124","Louisville - I 264 East & Stratton Ave - N of Substation",2.0574977758947299,255,"2025-01-01",9.448187665820465E-3,0,0,0,0,0,0,0.99055181233417955,0,0,43.21390849254901,134.88209149803919,0.47686274509803911,1.0862745098039213,"Trees Trimmed in 2025"]
["GRADY","Jefferson - 1838 S 39th St. - Louisville","GR1462","Louisville - Bells Ln, Wilson Ave, & Millers Ln - E of Substation",5.8075165522455103,21,"2025-01-01",0,0,0,0,0.94317408193504471,0,5.682591806495535E-2,0,0,0,102.31936506628865,154.8833333314432,1.1333333333333333,3,"Continue to Monitor"]
["GRADY","Jefferson - 1838 S 39th St. - Louisville","GR1463","Louisville - Stratton Ave, Louis Coleman Jr Dr, & Grand Ave - NE of Substation",5.0807785971601103,89,"2025-01-01",0,0,0,0,0,0,1,0,0,0,69.673520589208891,139.48202247191008,1.2764044943820225,0.97752808988764039,"Reliability Improvements Scheduled for 2026"]
["GRADY","Jefferson - 1838 S 39th St. - Louisville","GR1464","Louisville - Algonquin Pky, Virgina Ave, & S 43rd St - NW of Substation",3.38249842257349,8,"2025-01-01",0,0,0,0,0,0.90324042601404941,9.67595739859506E-2,0,0,0,111.95958323316127,266.27083312499997,1.2,2.5,"Continue to Monitor"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1142","Louisville - Hurstbourne Pky, Taylorsville Rd, & Stony Brook Dr - W of Substation",20.045783948503299,2032,"2023-09-09",1.5493118394038477E-3,0,0,1.9073327757078043E-3,1.7425797784705851E-5,2.3762451524598889E-5,2.477790028641675E-2,0.95407510202012524,2.0277291967657719E-3,1.5621435632271309E-2,95.923146321850396,221.80520832972442,0.81476377952755941,1.1151574803149613,"Reliability Improvements Scheduled for 2026"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1143","Louisville - Hurstbourne Pky & Stone Creek Pky - N of Subsation",4.69574491348249,404,"2023-11-18",0.14575596495060561,0,0,0,0.11553678487341926,0,0.59274496953809563,0,0,0.14596228063787955,92.655396034653464,203.95445544059407,1.0207920792079208,2.7970297029702968,"Continue to Monitor"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1145","Louisville - Gateway Dr, Taylorsville Rd, & Greene Way - SW of Substation",17.5780063008662,1902,"2024-01-01",2.3998001541264167E-2,1.1924765569949591E-2,0,0,5.9336313739168138E-2,4.1241778156940283E-4,2.0109491029324082E-2,0.49219116389011308,0,0.39202784644861155,72.43141604994743,106.7645373254469,0.68948475289169298,0.68243953732912721,"Reliability Improvements Scheduled for 2026"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1146","Louisville - Plantside Dr, Carton Dr, & Bunsen Way - SW of Substation",3.8046033273843598,166,"2023-11-18",3.5091083413231063E-2,0,0,0,0,0,0,0,0.96490891658676892,0,28.055722883132535,62.828514048192773,0.64216867469879535,1.0120481927710843,"Continue to Monitor"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1148","Louisville - Old Hickory Rd, Taylorsville Rd, College Dr, & Rown Tree Rd - S of Substation",19.897232041762699,2290,"2024-01-20",2.4234113080498394E-2,9.5526899844291158E-4,0,1.037315991309175E-2,0.23683771996395453,0.12041908712371689,3.0785135589820229E-2,0.38386847856429435,0.15431309259846965,3.8213944167711268E-2,102.77064337109171,188.53982532183409,0.97240174672489077,1.0716157205240171,"Reliability Improvements Scheduled for 2026"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1150","Louisville - Bunsen Way & Production Dr - E of Substation",2.7849769709082302,327,"2023-11-18",0.60651547288845375,0,0,0,0,0,0,1.5228150323598194E-2,0,0.37825637678794799,120.58028541957188,56.230784911314984,0.25198776758409785,0.35474006116207951,"Continue to Monitor"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1290","Louisville - Frankfort Ave, Fenley Ave, & Breckenridge Ln - E of Substation",14.445646899238399,1678,"2022-10-15",0,0,0,1.8733793666054831E-2,0.22739853742388486,4.2580776738630075E-2,6.393671881828511E-2,0.22722372752964484,8.0703901174139798E-3,0.41205605570608628,42.461545487723484,39.19950337306318,0.41156138259833142,0.4201430274135875,"Reliability Improvements Scheduled for 2026"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1291","Louisville - Frankfort Ave, Birchwood Ave, & Brownsboro Rd - W of Substation",7.5659558126167497,1549,"2024-01-01",0.11427328952454581,0,0,0,3.1662433044342589E-2,1.6096968358274892E-2,1.1120161245789387E-2,0.69370892926169314,0,0.13313821856535424,49.311624700968366,92.706563371207238,0.53376371852808258,0.460942543576501,"Reliability Improvements Scheduled for 2026"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1292","Louisville - Grinstead Dr, Lexington Rd, & Alta Vista Rd - S of Substation",14.5592972218356,856,"2024-01-01",4.317187152288406E-3,1.1883391439804169E-2,0,0,0.16891921964245976,5.19249313849121E-5,0.12366293301683851,3.2074771901194274E-2,0,0.65909057191602993,153.34836447570086,157.49003114369151,1.1471962616822429,1.6787383177570092,"Continue to Monitor"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1293","Louisville - Lexington Rd, Cannons Ln, & Old Cannons Ln - SE of Substation",19.715445089530899,2324,"2024-01-01",2.146189221247213E-2,0,0,0,2.9270316711742252E-3,1.6762405307443561E-3,2.1663341747108673E-2,0.82776666130470145,2.1131154170531539E-2,0.10337367836326763,76.44561244440618,92.182343653184148,0.35344234079173836,0.54733218588640264,"Continue to Monitor"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1294","Louisville - Hillcrest Ave, Zorn Ave, & River Rd - N of Substation",20.689708182363798,1136,"2024-01-01",2.1256183480737521E-2,0,0,0,0.1198470993853995,1.9112576825063709E-4,8.6868535451956226E-3,0.73859616249437854,2.6686403837505621E-2,8.473617148853245E-2,173.04833038626757,132.59300174647885,1.1797535211267607,1.5220070422535206,"Continue to Monitor"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1431","Louisville - Hillcrest Ave &  Zorn Ave - N of Substation",2.2731171427008801,6,"2023-05-19",0,0,0,0,0,0,0,1,0,0,28.092222199999998,140.46111099999999,6.6666666666666666E-2,0.33333333333333331,"Continue to Monitor"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1434","Louisville - Stilz Ave, Lexington Rd, & Alta Vista Rd - S & E of Substation",3.2478849249125901,1,"2025-01-01",0,0,0,0,0,0,3.7336652146857496E-2,0.10392034847542003,0.85874299937772247,0,222.60999996190475,563.1833332380952,2,4,"Continue to Monitor"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1103","Louisville - Bardstown Rd, Alta Ave, & Speed Ave - E of Substation",9.1839120623892398,1883,"2024-01-01",4.4208632766719061E-2,0,0,0,8.4280466495259033E-3,0.10317770368284136,0.13092393559191659,0.14229861874521135,0,0.57096306256378571,77.2208019079129,173.5199061710037,1.1978757302177376,3.3043016463090811,"Reliability Improvements Completed in 2025"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1105","Louisville - Stevens Ave, Baxter Ave, Barret Ave & Winter Ave - W of Substation",14.3676542165712,2704,"2024-01-01",3.2291860481758722E-2,9.7410868911820686E-3,0,0,3.2595285462794658E-2,9.8183743863516004E-4,3.8552147590490776E-2,0.80525268717170706,0,8.0585094963431567E-2,63.647506159763317,73.97861809430475,0.95532544378698248,1.2644230769230775,"Reliability Improvements Completed in 2025"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1472","Louisville - Bardstown Rd, Grinstead Dr, Baxter Ave,  & Payne St - NW of Substation",5.7664592625321696,350,"2025-01-01",1.0227867370724514E-3,0,0,0,0,0,0,0,0,0.99897721326292754,91.609190475047626,120.11833333142857,0.95542857142857152,0.81428571428571428,"Continue to Monitor"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1473","Louisville - Eastern Pky, Poplar Level Rd, & Nightingale Rd - SW of Substation",5.6491888500031102,33,"2025-01-01",0,0,0,0,2.9277594974573735E-2,0.51772360155548913,0,0.1907717618905175,0,0.26222704157941967,118.38545452076394,374.23333327048636,1.4424242424242424,4.666666666666667,"Continue to Monitor"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1474","Louisville - Eastern Pky & Castlewood Ave - W of Substation",2.3350377651474798,2,"2025-01-01",0,0,0,0,0.18982824001784518,0,0,0.77381217934418911,0,3.6359580637965648E-2,459.99999979999996,2241.9333324999998,1,4,"Trees Trimmed in 2025"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1475","Louisville - Cherokee Pky, Bardstown Rd, & Richmond Dr - N & SE of Substation",4.6473210050334997,21,"2025-01-01",0,0,0,0,4.9358341559723592E-3,1.7769002961500493E-2,6.959526159921027E-2,0,0,0.9076999012833169,77.199523771428574,96.477777714285708,0.79047619047619033,1.1428571428571428,"Continue to Monitor"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1233","Louisville - US 42, Hunting Creek Dr, & Westover Dr - NE of Substation",29.568547245208801,1231,"2024-01-01",8.87164331921627E-3,0,0,1.9273281519058036E-2,7.062409829199051E-3,0.19641527435193373,4.9477591101596316E-2,0.58702354912272536,4.0431423651510218E-3,0.12783310839112022,75.514278359545102,94.450880034930989,0.53208773354995931,0.95125913891145386,"Continue to Monitor"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1234","Louisville - HWY 42, Wolf Pen Branch Rd, & Barbour Ln - SE of Substation",54.646393845724099,2334,"2024-01-01",0,1.5444354699713757E-3,0,0,6.5562468528325354E-3,0,1.0506892507967191E-2,0.92907425118536269,0,5.2318173983866227E-2,85.68335760899744,125.03518994173095,0.93633247643530415,1.7909168808911744,"Reliability Improvements Scheduled for 2026"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1243","Louisville - US 42, Covered Bridge Rd, Rose Island Rd, & River Bluff Rd - NNE of Substation",53.113016807390899,1527,"2022-11-18",6.4875623270619076E-3,0,0,0,4.1089050548200751E-2,1.5097192074841018E-2,6.2417215098579046E-2,0.68722043842190306,0,0.18768854152941422,186.72378082436146,167.55695261886044,1.3222003929273078,1.6633922724295995,"Reliability Improvements Scheduled for 2026"]
["HARMONY LANDING","Oldham - 11943 W Hwy 42 - Goshen","HL1155","Goshen - Goshen Ln - NW of Substation",15.2771701675179,390,"2021-12-24",9.7505307855626326E-3,0,0,0,7.6698513800424629E-3,0,7.4501061571125266E-2,0.80420382165605087,0,0.10387473460721869,167.10519656923077,417.65824785384615,0.48666666666666653,0.80256410256410238,"Tree Trim Scheduled for 2026"]
["HARMONY LANDING","Oldham - 11943 W Hwy 42 - Goshen","HL1156","Goshen - US 42, Harmony Landing Rd, & Hwy 1793 - W & SW of Substation",48.809822461160699,1295,"2022-01-07",6.3632454073885196E-3,9.9787257524956326E-3,0,0,0.1671760053889686,9.3854063990196343E-2,4.0185112593669484E-2,0.58470309294829104,5.0464494080126654E-2,4.7275259838863749E-2,86.185601021158305,239.80100385019304,1.0500386100386101,2.605405405405405,"Tree Trim Scheduled for 2026"]
["HARMONY LANDING","Oldham - 11943 W Hwy 42 - Goshen","HL1157","Goshen - Meadowridge Trl, Hwy 1793, & Rose Island Rd - W of Substation",33.573483950566597,1349,"2024-01-01",2.1322143891277619E-2,0,0,0,2.8826636401335752E-2,2.445780678205324E-2,5.4092003695862525E-3,0.90013168329077287,3.6995001855206584E-3,1.6153029079453769E-2,289.12783542179392,410.07286877909559,3.1648628613787997,3.8636026686434382,"Reliability Improvements Completed in 2025"]
["HARMONY LANDING","Oldham - 11943 W Hwy 42 - Goshen","HL1158","Goshen - US 42 & Buckeye Ln - NE of Substation",32.2780471383712,546,"2021-11-21",5.1030999169665095E-3,0,0,0,6.5596457237752565E-2,5.0166066980348737E-3,9.2028784943260448E-3,0.88499861610849717,0,3.0082341544422918E-2,168.51971916117219,113.63150182234432,1.4326007326007326,2.0073260073260073,"Tree Trim Scheduled for 2026"]
["HANCOCK","Jefferson - 630 E Caldwell St - Louisville","HN1201","Louisville - Shelby St, Logan St, & Barrett Ave - E & S of Substation",6.5954717276877197,922,"2022-06-10",8.5849373834537435E-3,0,0,0,0,6.9290889267045047E-3,0.93238024394468955,2.2855803621467947E-2,0,2.9249926123684239E-2,93.496713661605213,212.87865147722343,0.63058568329718001,0.47830802603036876,"Continue to Monitor"]
["INTERNATIONAL","Jefferson - 5599 Cane Run Rd. - Louisville","IN1292","Louisville - Logistics Dr, International Dr, & Riberport Dr - SE of Substation",2.9112674215968699,46,"2021-10-02",1.239561586638831E-3,0,0,0,0.66200743736951984,0.32027987995824636,7.5515396659707728E-3,0,0,8.9215814196242169E-3,29.377101439130435,23.599637673913044,0.18695652173913041,0.2608695652173913,"Continue to Monitor"]
["INTERNATIONAL","Jefferson - 5599 Cane Run Rd. - Louisville","IN1293","Louisville - Cane Run Rd, Port Rd, & Intermodal Rd - S of Substation",3.2364428759286099,258,"2021-10-02",5.6436415375649925E-2,0,0,0,2.8532289924393214E-3,0.86185679363661816,0,0,0,7.8853561995292545E-2,39.462984490444192,69.407364333333334,0.92170542635658914,2.2403100775193803,"Continue to Monitor"]
["INTERNATIONAL","Jefferson - 5599 Cane Run Rd. - Louisville","IN1296","Louisville - Greenwood Rd - S of Substation",10.8805351356256,646,"2021-10-02",5.7404496685573708E-4,0,0,0,0.30514590309574247,2.9112280461969522E-2,0.12171120071072235,0.41074284152258594,0.1133192100047837,1.9394519237340258E-2,37.15146026501548,39.709107320433432,0.31795665634674919,0.20123839009287925,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1120","Louisville - Taylorsville Rd & Tucker Station Rd - E of Substation",13.751462424394701,783,"2020-04-04",4.6767907539309234E-2,0,0,0,1.0885633651390942E-2,6.7195269453030509E-4,8.076871388254267E-2,0.30143797876629486,0,0.559467813465932,6.4155214955300126,9.5029799885057464,6.5134099616858246E-2,4.3422733077905486E-2,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1121","Louisville - Taylorsville Rd, Neal Dr, & Watterson Trl - W of Substation",14.303068440783701,1559,"2022-12-23",1.6241955635180688E-2,0,0,0,0.20527568892765374,2.3573230239739751E-4,5.1766813606468495E-2,1.6619127319016522E-2,0,0.70986068220928311,23.109499677870428,26.757750694034637,0.17921744708146245,0.25914047466324569,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1123","Louisville - Taylorsville Rd, I 265 S, & Eastwood Fisherville Rd - E of Substation",68.548250448028099,1437,"2020-08-01",1.7970848671773952E-3,0,0,1.6447368421052631E-2,3.5562381852551984E-2,4.4454531887374388E-2,0.22579842801711272,0.65217391304347827,9.9492587802208735E-4,2.2771366033230524E-2,65.995745758246343,111.58525862769659,0.63716075156576202,0.7981906750173976,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1124","Louisville - Ramblin Creek Rd, Rehl Rd, & Pope Lick Rd - NE of Substation",17.774844404731301,512,"2023-04-28",9.0743390235776024E-3,0,0,0,0.12811869157046821,0,8.031671991062854E-2,0.76573310075848144,2.1362914763929991E-3,1.4620857260451169E-2,27.515266918359373,35.306380199218744,0.40156249999999999,1.142578125,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1127","Louisville - Taylorsville Rd, Old Routt Rd, & Taylorsville Lake Rd - SE of Substation",45.120731852872296,395,"2020-06-27",2.9771336925101077E-3,0,0,0,0.12493397485762579,1.2484754194397226E-4,0,0.39011015394662285,0,0.48185388996129724,131.16276791645569,230.20654007594936,0.83594936708860779,1.3949367088607596,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1155","Louisville - Southside Dr, 3rd St, & W Southland Blvd - N of Substation",5.2020702564387902,1264,"2021-07-17",4.3150628286769245E-3,0,0,0,1.5127043817103605E-2,6.2028420064312438E-2,4.1350658448425998E-3,0.84531691631113204,0,6.9077491133932356E-2,47.17508174810127,82.517550101265826,0.36202531645569619,0.55854430379746844,"Tree Trim Scheduled for 2026"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1156","Louisville - Strawberry Ln, Southside Dr, & National TPke - S of Substation",12.778881749108701,1271,"2025-01-01",6.8904843886839658E-3,0,0,0,0.30149958804718408,5.7493850631694229E-3,5.2067644048827875E-4,0.63244831637976262,1.4882169525067279E-3,5.1403332728204902E-2,104.70426435121951,107.51765014004719,1.1276160503540518,1.003147128245476,"Reliability Improvements Scheduled for 2026"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1159","Louisville - Kenwood Dr, Homestead Dr, & Southside Dr - SW of Substation",12.562944454967599,1452,"2024-01-01",1.5898128098650983E-3,0,0,0,3.3726743180709583E-2,1.7395029770277211E-3,3.7177359620303149E-2,0.79987715082832866,3.4978462681983243E-2,9.0910967901782602E-2,126.01172864283747,192.72318639807156,1.0473829201101927,1.1556473829201099,"Reliability Improvements Scheduled for 2026"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1161","Louisville - Southside Dr, 3rd St, & W Kenwood Way - N of Substation",5.8066355653573396,740,"2021-07-17",0.10350091293648003,0,0,1.8145321342300147E-5,6.2050194495163136E-2,3.4169908252718963E-2,1.3915193304376424E-2,0.78470122594327318,0,1.6444197466459508E-3,103.47926576108107,240.75788287162163,0.82243243243243247,1.541891891891892,"Tree Trim Scheduled for 2026"]
["LOGAN","Jefferson - Rear of 1130 Logan St, St Catherine St - Louisville","LG0001","Louisville - Shelby St, E Oak St, & Bergman St - N & S of Substation",2.4136083823348602,517,"2022-07-22",1.1677340485704382E-3,0,0,5.5668071596693854E-2,0,6.6049957122265406E-3,0.18296932873538052,0,4.7439195723174049E-4,0.75311547794989686,86.806382974468079,106.00996130754355,0.34468085106382979,0.61895551257253389,"Continue to Monitor"]
["LOGAN","Jefferson - Rear of 1130 Logan St, St Catherine St - Louisville","LG0002","Louisville - E Oak St, Reutlinger Ave, & Ellison Ave - SE of Substation",1.7196357154688899,364,"2022-07-22",0,0,0,0,0.93500738552437224,0,0,0,6.4992614475627764E-2,0,9.9923717928571438,16.73791208791209,0.14505494505494504,0.24725274725274723,"Continue to Monitor"]
["LOGAN","Jefferson - Rear of 1130 Logan St, St Catherine St - Louisville","LG0003","Louisville - Logan St, E Kentucky St, & Swan St - NE of Substation",1.33967364464185,293,"2022-07-22",0,0,0,1.6597574677463096E-2,0,2.2471039479291774E-4,4.5329510673743755E-3,0.88159311921273875,0,9.7051644647630858E-2,35.49938566211604,52.151763365187705,0.29692832764505123,0.27986348122866889,"Tree Trim Scheduled for 2026"]
["LOGAN","Jefferson - Rear of 1130 Logan St, St Catherine St - Louisville","LG0004","Louisville - Logan St, Goss Ave, & Charles St - SE of Substation",3.0073269353945999,740,"2022-07-22",0,0,0,0,5.8720333323365528E-2,0.69183204914791885,0.11441045423282796,9.8109772102774703E-2,0,3.6927391193112911E-2,46.931756753243242,135.94788287837838,0.31486486486486492,0.69459459459459472,"Continue to Monitor"]
["LYNN","Jefferson - Rear of 2071 S Preston St & Lynn St - Louisville","LN0001","Louisville - Shelby St - NE & SE of Substation",3.4602852512667801,589,"2022-07-15",0,0,0,0,0,4.2149108670319591E-4,2.0991909024041522E-2,0,0,0.97858659988925534,24.129026596112453,84.962620255604719,0.27232597623089971,1.1052631578947363,"Continue to Monitor"]
["LYNN","Jefferson - Rear of 2071 S Preston St & Lynn St - Louisville","LN0002","Louisville - Preston St & Miller Ave - S of Substation",2.55541672413346,484,"2022-07-15",0,0.17258287150538743,0,0.12898906034322916,0,0,0,0,0,0.69842806815138347,28.420454544628097,100.28712121074379,0.36446280991735536,1.3471074380165291,"Continue to Monitor"]
["LYNN","Jefferson - Rear of 2071 S Preston St & Lynn St - Louisville","LN0003","Louisville - Barbee Ave, Crittenden Dr, Warnock St, & Floyd St - W of Substation",3.3767206119054798,451,"2022-07-15",0,0,0,0,3.685799025308021E-2,8.2966408403778566E-4,1.5221396187464886E-3,0.10181350196636921,0,0.85897670407776627,56.826895784035472,121.53847005986694,0.75033259423503329,2.0598669623059873,"Continue to Monitor"]
["LYNN","Jefferson - Rear of 2071 S Preston St & Lynn St - Louisville","LN0004","Louisville - Preston St & Gernert Ct - NW of Substation",2.2208911321974498,499,"2022-07-15",0,0,0,1.4736167681112992E-2,3.2813143563223651E-2,3.4094549448537826E-3,6.72738089789941E-3,0,0,0.94231385291291014,74.599632595190371,47.75788243086172,0.49739478957915828,1.1462925851703407,"Continue to Monitor"]
["LOCUST","Jefferson - 2929 Preston Hwy - Louisville","LO1193","Louisville - Preston Hwy, Belmar Dr, & Phillips Ln - SE of Substation",12.667097700539401,1314,"2025-01-01",1.1286828818167362E-2,0,0,0,1.4646810884360834E-2,1.5639947554042534E-5,3.3834419875245353E-3,0.96610302033453854,0,4.564258027854747E-3,101.51520293257229,146.3167554452055,1.0243531202435314,1.6088280060882802,"Reliability Improvements Scheduled for 2026"]
["LOCUST","Jefferson - 2929 Preston Hwy - Louisville","LO1194","Louisville - Preston Hwy, Clarks Ln, Pindell Ave, E Burnett Ave, Hickory St - NE of Substation",9.9047092446996299,1069,"2019-12-06",0.33937278820593941,0,0,0,0.66021950781976224,4.0770397429834148E-4,0,0,0,0,13.433146240224511,33.276317430308708,0.13152478952291857,0.25257249766136575,"Continue to Monitor"]
["LYNDON SOUTH","Jefferson - 918 Ormsby Ln. - Bellemeade","LS1244","Lyndon - New La Grange Rd, La Grange Rd, Whipps Mill Rd - N & NE of Substation",16.770210966301502,1910,"2021-07-24",3.2658713752222679E-2,1.8897415470872366E-2,0,0,0.12738108443332963,6.6285491477339571E-3,2.61511726011005E-2,0.59883832323252695,0.18204308556946028,7.4016557927536379E-3,112.68159685434554,122.73550610418847,0.85602094240837678,1.1366492146596858,"Reliability Improvements Scheduled for 2026"]
["LYNDON SOUTH","Jefferson - 918 Ormsby Ln. - Louisville","LS1245","Louisville - Ormsby Ln, Westport Rd, & Colonel Dr - N of Substation",21.006213562700601,1931,"2020-12-26",4.3182731250746495E-2,0,0,0,0.39207031716559715,8.3053736820960511E-2,6.3411403194458017E-3,9.3564394062781622E-2,0,0.3817876803804684,23.382894869083373,26.541325733298809,0.37027446918694973,0.20455722423614711,"Reliability Improvements Scheduled for 2026"]
["LYNDON SOUTH","Jefferson - 918 Ormsby Ln. - Louisville","LS1248","Louisville - Whipps Mill Rd, Ormsby Station Rd, & Shelbyville Rd - NE of Substation",14.6001410626785,540,"2021-05-22",6.3331568731251106E-2,0,0,0,0.61859890594670897,0,0,0.10825833774483853,0,0.20981118757720135,99.896216044814821,104.94382715555557,1.0218518518518518,0.89074074074074061,"Reliability Improvements Scheduled for 2026"]
["LYNDON","Jefferson - 8407 LaGrange Rd. - Louisville","LY1111","Louisville - Ormsby Ln, Herr Ln, & Graymoor Rd - NW of Substation",25.6934178639669,2277,"2024-01-01",4.0235059788132417E-2,7.6179562213081767E-2,0,0,0.46328469792156945,2.032387227917954E-2,4.1841460835874242E-2,0.34284213613822556,0,1.5293210823937082E-2,74.042655535177886,81.650812466403181,0.8692138779095302,0.83091787439613485,"Reliability Improvements Completed in 2025"]
["MILL CREEK SWITCHING","Jefferson - 14660 Dixie Hwy - Louisville","MC1261","Louisville - Dixie Hwy, Pendleton Rd, & Blevins Gap Rd - NE of Substation",69.654744563039998,3069,"2024-01-13",8.558330223205084E-3,0,0,1.7557834459478278E-3,6.602681580427916E-2,2.2638020064504986E-3,2.1215345279939395E-2,0.79840130124052344,1.0304086987037728E-2,9.1474535012616903E-2,60.381068745715211,77.862381876507015,0.68686868686868707,0.6337569240795049,"Reliability Improvements Scheduled for 2026"]
["MADISON","Jefferson - 635 E Madison - Louisville","MD1451","Louisville - Madison St, Wenzel St, Baxter Ave, & Lexington Rd - E of Substation",2.16725851822273,25,"2022-06-03",0,0,0,0,0,0,0,0,0,1,39.546799984000003,5.9466666400000001,0.53600000000000003,0.8,"Continue to Monitor"]
["MADISON","Jefferson - 635 E Madison - Louisville","MD1452","Louisville - Clay St, E Main St, & River Rd - N of Substation",8.9091946353203699,538,"2022-06-03",0,0,0,0,2.7155863254077098E-2,0,0,0,0,0.97284413674592285,182.37345105018591,224.98658611895911,1.8401486988847584,2.949814126394052,"Continue to Monitor"]
["MADISON","Jefferson - 520 S Clay St - Louisville","MD1454","Louisville - E Madison St, S Hancock St, E Muhammed Ali Blvd, S Floyd St - W of Substation",0.58280826146725295,1,"-",0,0,0,0,1,0,0,0,0,0,19.61,98.05,0.2,1,"Continue to Monitor"]
["MADISON","Jefferson - 520 S Clay St - Louisville","MD1455","Louisville - E Madison St - W of Substation",9.4327068649966303E-2,2,"-",0,0,0,0,0,0,0,0,0,1,53.901666599999999,269.50833299999999,0.1,0.5,"Continue to Monitor"]
["MADISON","Jefferson - 635 E Madison - Louisville","MD1457","Louisville - Clay St, E Main St, Story Ave, & Buchanan St - NE of Substation",3.0564542943612798,123,"-",0,0,0,0,0,0,0,0,0,1,22.388482382113821,81.553387528455289,0.24065040650406505,0.37398373983739835,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG0411","Louisville - W Broadway, 15th St, Garland Ave, & 16th St  - SW of Substation",4.3490514880459497,389,"2023-03-17",0,0,0,0,5.1517261697511849E-2,2.6903607681388435E-2,0.11263625893885422,2.3930685379114552E-2,0,0.78501218630313097,172.43164523907458,191.96251069922877,0.6766066838046273,0.89974293059125965,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG1314","Louisville - Magazine St, W Chestnut St - W and E of Substation",1.88812905754566,6,"2023-03-17",0,0,0,0,0,0,0,0,0,1,81.133888833333344,208.50833333333333,0.56666666666666665,1.1666666666666665,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG1326","Louisville - W Broadway, Dixie Hwy, & Dr W J Hodge St - SW of Substation",2.1915619509503501,117,"2023-03-17",0,0,0,0,0,0,0,0,0,1,35.265868940170947,91.266666666666666,0.42051282051282046,0.99145299145299148,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1291","Louisville - Saint Anthonys Church Rd - NW of Substation",8.1804924812870095,149,"2024-01-01",4.2672854558326121E-3,0,0,0,4.7343270667820339E-3,0,0,0.23414025013765438,0.68905352788484231,6.7804609454888698E-2,299.22080535838933,1045.5214764966445,0.8093959731543624,2.3020134228187921,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1292","Louisville - Outer Loop & National Tpike - NE of Substation",17.190980301665899,1395,"2021-10-30",0,0.17030700409927627,0,0,0.65388911691509977,9.0921843583255827E-5,4.6481844206719899E-2,3.7251978199539675E-3,5.2085227538407983E-2,7.342068757695884E-2,79.413930701075273,104.67175626738354,0.81491039426523293,1.1304659498207885,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1293","Louisville - Manslick Rd and Brown Austin Rd - SE of Substation",20.162740095034099,1650,"2022-05-06",2.8389435369852302E-3,0,0,0,2.1459404987516171E-2,0.61894233372439311,4.267815780765875E-3,8.9868543753572182E-3,0.16090229522004632,0.18260235237493608,102.73361211684849,161.0275252466667,0.87757575757575768,1.6169696969696967,"Reliability Improvements Scheduled for 2026"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1295","Louisville - Outer Loop, New Cut Rd, & Scottsdale Blvd - NE of Substation",19.571853394427599,1804,"2022-03-25",2.545242183860898E-2,0,0,0,8.3177485626090647E-2,1.6317081140457601E-2,8.7918963827109856E-2,3.0159138469239486E-2,0.63258410561955547,0.12439080347893797,44.746154838345454,70.192747594720643,0.76840354767184027,1.5992239467849223,"Reliability Improvements Scheduled for 2026"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1296","Louisville - 3rd St Rd, Christland Rd, & Manslick Rd - N of Substation",17.929346622522701,1746,"2024-01-01",1.6892418065715537E-2,0,0,4.4993708297383692E-4,5.0898514465971656E-2,7.5253213218261514E-3,1.0833100536216228E-2,0.87579264328147521,8.6501640292607433E-3,2.8957901216560653E-2,103.13965062542954,167.01361206185558,0.58006872852233671,0.58419243986254277,"Reliability Improvements Completed in 2025"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1297","Louisville - Outer Loop & National Tpke - NE of Substation",8.2711033421004601,622,"2022-03-25",2.1566405106368176E-3,0,0,1.0067221093335575E-2,0.87880491969122942,0,1.902133740698763E-2,5.6397308837298286E-2,0,3.3552572460512319E-2,59.496152192926047,75.571704172025719,0.60836012861736344,0.81993569131832811,"Continue to Monitor"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1281","Louisville - Mud Ln, Brookley Dr, & Elda Dr - W of Substation",4.3365307721095796,378,"2023-10-07",0.18217671596511187,0,0,0,0.69169510807736068,0,6.0599165718619646E-2,6.552901023890785E-2,0,0,20.237081127513221,34.877821865079362,7.0370370370370375E-2,0.20105820105820105,"Continue to Monitor"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1282","Louisville - Mud Ln, Blue Lick Rd, Vanguard Dr & Caven Ave - NW of Substation",30.445812783454599,2654,"2019-10-05",1.0951836563320761E-2,0,0,9.5724459596063325E-3,0.16952356829751936,6.1610498428932292E-4,3.004995014113368E-2,0.68112345602949997,2.8865659449110871E-3,9.5276072079719415E-2,77.3737314682743,101.66458175810095,0.86028636021100124,0.58779201205727161,"Reliability Improvements Scheduled for 2026"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1284","Louisville - Christman Dr, Mount Washington Rd, & Cedar Creek Rd- E of Substation",58.8821787392964,3219,"2019-08-24",2.7853581372975274E-2,0,0,0,0.21830972886467287,2.705802906541105E-3,9.1877040915440189E-2,0.20279645886717051,0.44582381291569922,1.0633574157500856E-2,40.877974522460391,48.939168474370916,0.6840012426219324,0.69835352593973332,"Continue to Monitor"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1285","Louisville - Preston Hwy, Lees Ln, Rogers Ave, & Zoneton Rd - S of Substation",29.7556874337766,1898,"2023-11-04",0.13349172188958258,1.9142997166052292E-2,0,0,0.10683343632140803,5.3546696213590166E-3,3.1373718863863968E-2,0.55841554622744027,0,0.14538790991029382,48.358440460906209,79.185335436775532,0.51359325605900952,0.93677555321390948,"Continue to Monitor"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1287","Louisville - Preston Hwy, Interchange Dr, & Commerce Crossings Dr - NW of Substation",14.9948055816807,701,"2023-11-24",0,0,0,0,0.66561514195583593,0,0.19242902208201892,0,0,0.14195583596214512,0.46506894835948642,0.45175938944365196,5.9914407988587732E-3,7.1326676176890159E-3,"Continue to Monitor"]
["MULDRAUGH","Meade - 100 Carpenter Test Rd. - Muldraugh","MU1101","Muldraugh - Carpenter Test Rd, Main St, & Dixie Hwy - E & SE of Substation",10.371130317918199,561,"2024-01-01",6.187190293150558E-3,0,0,0,1.1170286666975409E-2,2.4971055434631594E-2,0.1717871532441069,0.77528828787106929,0,1.0596026490066225E-2,73.026755787073313,101.38850266085676,0.74652406417112294,1.2834224598930482,"Continue to Monitor"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1266","Louisville - Six Mile Ln, Stony Brook Dr, & Hampton Ridge Ct - E of Substation",31.161890838494202,2682,"2021-06-26",0.15549637520343246,0,0,0,0.12860412695926129,4.1034611802999053E-3,9.9662323873179998E-2,0.19501231473503738,2.0700068753644378E-2,0.39642132929514462,48.001792190976872,68.928877697986579,0.62826249067859796,0.86353467561521235,"Reliability Improvements Scheduled for 2026"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1268","Louisville - Breckenridge Ln, Manner Dale Dr, & Klondike Ln - NW of Substation",14.768371794775801,1947,"2021-07-24",1.7012718773779759E-2,0,0,0,3.4170380838496939E-2,7.6099757219987685E-2,0.36249411167880563,0.39983965648440045,0,0.11038337500452948,56.387704155213157,69.602354044170525,0.50570107858243463,1.2121212121212124,"Reliability Improvements Scheduled for 2026"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1269","Louisville - Wisteria Landing Cir, Beargrass Ave, Bardstown Rd & Fegenbush Ln - SW of Substation",22.913297991447699,2815,"2024-01-01",3.588273256456108E-3,0,0,0,0.21851406601290901,1.4112110034294435E-3,2.1598100615875852E-2,0.52550540249180067,5.3557557053179654E-2,0.17582538956634927,90.887179393534637,225.59158081314391,1.106216696269982,2.3889875666074598,"Reliability Improvements Scheduled for 2026"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1272","Louisville - Six Mile Ln, Raintree Dr, & Stony Brook dr - NE of Substation",19.8756714655322,1393,"2021-07-24",3.3306823820496612E-3,0,0,0,1.5287152402509567E-2,0,2.4035291638627759E-2,1.2418687167356593E-2,0,0.94492818640945642,30.456188080976307,105.61227565900931,0.26590093323761665,0.91529073941134242,"Reliability Improvements Scheduled for 2026"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1273","Louisville - Valosta Ave, Nachand Ln, & Pear View Ln - S of Substation",1.7153604441776,113,"2021-08-17",0,0,0,0,0,0,1,0,0,0,5.7497935097345136,28.748967548672567,2.3008849557522124E-2,0.11504424778761062,"Continue to Monitor"]
["OLD HENRY","Jefferson - 13601 Terra View Trail - Louisville","OH1171","Louisville - Nelson Miller Pky & Eastpoint Pky - WNW of Substation",8.0197787965510408,206,"0/00/00",0,0,0,0,0,0,0,0,0,1,31.610097087378641,158.05048543689321,0.19805825242718447,0.99029126213592233,"Continue to Monitor"]
["OLD HENRY","Jefferson - 13601 Terra View Trail - Louisville","OH1172","Louisville - Eastpoint Pky & Nelson Miller Pky - NW of Substation",8.3652698143164592,103,"0/00/00",0,0,0,0,0.55341880341880345,0,3.6160420775805391E-3,0,0,0.44296515450361607,36.485954687378637,59.062783165048543,0.4932038834951456,1.0194174757281553,"Continue to Monitor"]
["OLD HENRY","Jefferson - 13601 Terra View Trail - Louisville","OH1173","Louisville - Old Henry Rd and Factory Ln - NW of Substation",41.240764921390401,2975,"2020-11-21",1.0496645059648656E-2,7.9199369821670914E-3,0,9.1171809010411234E-2,0.33845036871126633,0,0.30440270672981107,0.22903755445253257,0,1.852097905416307E-2,40.078294676571431,70.834621846722698,0.21942857142857145,0.41310924369747903,"Continue to Monitor"]
["OLD HENRY","Jefferson - 13601 Terra View Trail - Louisville","OH1174","Louisville - Bush Farm Dr and Aiken Rd - SE of Substation",20.546399319540701,888,"2025-01-01",4.459097910980191E-4,0,0,7.3507553441612842E-3,0,6.3575926276247868E-3,0,0.94421398265005541,0,4.1631759587060509E-2,6.1384947432432426,9.2982732713963951,0.10653153153153154,0.13400900900900903,"Trees Trimmed in 2025"]
["OKOLONA","Jefferson - 811 N 27th St. - Louisville","OK1271","Louisville - Outer Loop, Robbs Ln, & Monaco Dr - E of Substation",11.097044963816799,956,"2023-11-04",0,0,0,0,0.11017690743105814,2.3650726077290572E-5,4.779811740220425E-2,0.50941298897876164,0.32917474733140972,3.4135881304889395E-3,74.62961993786611,166.41846233577408,0.49476987447698734,0.74476987447698728,"Continue to Monitor"]
["OKOLONA","Jefferson - 811 N 27th St. - Louisville","OK1272","Louisville - Outer Loop, Shepherdsville Rd, & Applegate Ln - E of Substation",18.541064279075002,1690,"2023-11-04",1.8297905473798958E-2,3.1632017441407772E-3,0,0,1.6181966830179865E-2,3.48438838277661E-4,0.12164603285836642,9.0921124347893789E-2,0.74427509148952742,5.1662384178151523E-3,91.689808674319494,285.48045364260344,0.76201183431952657,1.0627218934911244,"Reliability Improvements Scheduled for 2026"]
["OKOLONA","Jefferson - 811 N 27th St. - Louisville","OK1273","Louisville - Preston Hwy, St. Rita Dr, & High School Dr - S of Substation",9.4714798548675105,796,"2023-11-11",3.8895367327467401E-2,0,0,0,0.1576062758401357,0.11867910526873741,0.17443019187957171,0.45835895261316656,2.4583907558570973E-2,2.744619951235026E-2,46.448320764070345,102.65536012060301,0.5879396984924623,1.1331658291457287,"Continue to Monitor"]
["OKOLONA","Jefferson - 811 N 27th St. - Louisville","OK1274","Louisville - Preston Hwy, Miles Ln, & Cooper Ave - S of Substation",13.5319712965672,1546,"2023-11-11",1.3673109616524733E-2,0,0,6.8709093550375544E-5,0.4557690118061854,0,4.9755199315264807E-2,0.44867430711786949,1.9218915024519331E-3,3.0137771548153294E-2,44.562059072703754,59.720148763260028,0.64501940491591214,0.66494178525226388,"Continue to Monitor"]
["OKOLONA","Jefferson - 811 N 27th St. - Louisville","OK1275","Louisville - Blue Lick Rd & Freedom Way - S of Substation",10.906484038709801,1280,"2023-11-11",5.6874618224311474E-2,0,0,0,5.8627466602926726E-2,0,6.7112846253950545E-2,0.81366690569144562,3.7181632273656814E-3,0,25.723458331250004,38.250091144531247,0.36687500000000001,0.25234374999999998,"Continue to Monitor"]
["ORMSBY","Jefferson - Rear of 436 E Ormsby Jackson St - Louisville","OR0001","Louisville - Jackson St, Oak St, & Preston St - N of Substation",2.4576837641146798,590,"2025-01-01",0,0,0,0,0.20890180225703217,6.6784571332322726E-2,0.5445932289034866,1.8906855314131717E-2,2.5644264780192015E-2,0.13516927741283477,34.717858753898305,40.251045191525421,0.30305084745762711,0.56271186440677978,"Continue to Monitor"]
["ORMSBY","Jefferson - Rear of 436 E Ormsby Jackson St - Louisville","OR0002","Louisville - E Ormsby Ave - E of Substation",0.388605961654992,138,"2025-01-01",0,0,0,0,0,0,1,0,0,0,8.7714492753623183,25.501811594202898,0.10724637681159419,0.25362318840579712,"Continue to Monitor"]
["OXMOOR","Jefferson - 8004 Shelbyville Rd - Louisville","OX1273","Louisville - Shelbyville Rd, Lyndon Rd, & Hurstbourne Club Ln - E of Substation",25.419882159616101,1981,"2024-01-01",0.25862459561588719,0,0,7.8158273902839068E-2,9.034643371725281E-3,0,0,0.31612189972180188,0,0.33806058738774658,38.174522964563359,55.705249870772342,0.35557799091367998,0.54921756688541146,"Reliability Improvements Scheduled for 2026"]
["OXMOOR","Jefferson - 8004 Shelbyville Rd - Louisville","OX1277","Louisville - Oxmoor Woods Pky, Linn Station Rd, & Hogarth Dr - SE of Substation",14.666720377010799,555,"2023-12-09",0.54431040304509315,0,0,0,0,8.0793197654787124E-2,8.042483961076834E-3,0.36685391533904288,0,0,120.21696095531532,58.697027021621622,1.2897297297297297,1.3747747747747749,"Continue to Monitor"]
["OXMOOR","Jefferson - 8004 Shelbyville Rd - Louisville","OX1278","Louisville - Christian Way & Oxmoor Ln - W of Substation",1.07278741392303,6,"0/00/00",0,0,0,0,0,0,0,0,0,1,121.6155555,81.369444333333334,0.5,0.83333333333333326,"Continue to Monitor"]
["OXMOOR","Jefferson - 8004 Shelbyville Rd - Louisville","OX1279","Louisville - Shelbyville Rd, New La Grange Rd, & Wood Rd - N of Substation",13.3173917237895,1499,"2024-01-01",4.0337989620181258E-2,7.3071858297399884E-3,0,0,1.2910222314028248E-3,2.3690257946241836E-3,0.2547638720338764,0.21509721397402465,0.41636112473856801,6.2472565777582693E-2,56.548530128218815,101.73783633288861,0.62108072048032026,0.45630420280186806,"Reliability Improvements Scheduled for 2026"]
["PIRTLE","Jefferson - Rear 1506 W Main St - Louisville","PI0001","Louisville - W Market St, S 12th St, & W Main St - E of Substation",2.81182078566941,142,"2023-03-24",0,0,0,0,0.18169141478857315,1.0213311223336097E-2,0.57115399110575116,0,0.1467174191603226,9.0223863722017031E-2,35.200211260563385,153.3811032746479,0.24507042253521125,0.95774647887323949,"Continue to Monitor"]
["PIRTLE","Jefferson - Rear 1506 W Main St - Louisville","PI0003","Louisville - Main St, 15th St, Rowan St, & Portland Ave - NW of Substation",5.1759293099379802,565,"2023-03-24",0,0,0,0,0,5.1576671077687763E-2,0.46057515411677369,0.2855759610108769,0,0.20227221379466159,71.045734506548655,53.402418872566372,0.41876106194690266,0.57699115044247784,"Continue to Monitor"]
["PIRTLE","Jefferson - Rear 1506 W Main St - Louisville","PI0004","Louisville - Market St & 10th St - SE of Substation",2.2316071071155799,323,"-",0,0,0,0,0,5.208333333333333E-3,0.3030753968253968,0,0,0.69171626984126988,6.4389989671826626,12.481630544891642,7.3065015479876164E-2,0.11764705882352941,"Continue to Monitor"]
["PLEASURE RIDGE","Jefferson - 4400 Atlas Power Rd. - Louisville","PL1273","Louisville - Atlas Power Rd, Greenwood Rd & St. Pauls Church Rd - N of Substation",9.7962741105826296,1087,"2023-03-03",0.60106382978723405,0,0,0,1.0096532702915681E-3,9.8502758077226153E-4,0.32525610717100079,0,0,7.1685382190701336E-2,13.752431767801289,37.356884385464582,0.16669733210671572,0.41674333026678934,"Continue to Monitor"]
["PLEASURE RIDGE","Jefferson - 4400 Atlas Power Rd. - Louisville","PL1274","Louisville - Dixie Hwy, Lower Hunters Trace, & Flintlock Dr - N of Substation",7.53184681013557,1377,"2023-03-03",8.1998388396454479E-3,0,0,0,1.8275584206285254E-2,0,3.1845286059629333E-3,0.50646253021756649,3.5100725221595484E-2,0.42877679290894438,60.008758167029761,57.575296536673918,0.60871459694989105,0.97966594045025412,"Reliability Improvements Scheduled for 2026"]
["PLEASURE RIDGE","Jefferson - 4400 Atlas Power Rd. - Louisville","PL1276","Louisville - Dixie Hwy, Cofer Ave, and Fury Way - W of Substation",17.605650567279099,1896,"2023-09-09",5.1192416057280919E-3,0,0,0,1.4954366305717656E-2,1.0384976601192817E-2,8.779770266256752E-2,0.70649347000698359,0,0.17525024281781038,44.807410335654012,99.552601964662458,0.44356540084388191,1.1334388185654005,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1385","Louisville - By Schenk Ln - SE of substation",0.29655285564387301,1,"2021-11-13",0,0,0,0,0,0,1,0,0,0,46.32,13.6,0.4,1,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1387","New Albany - No Road - SE of Substation",0.30052225713897701,1,"2021-11-13",0,0,0,0,0,0,1,0,0,0,315.23666659999998,1467.55,0.4,1,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1391","New Albany - No Road - S of Substation",0.60683225056293399,1,"2021-11-13",0,0,0,0,0,0,1,0,0,0,554.81999999999994,2774.1,0.2,1,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1392","New - Albany - No Road - SE of Substation",0.15780309726826,3,"2021-11-13",0,0,0,0,1,0,0,0,0,0,37.777777733333338,38.699999999999996,0.26666666666666666,0.33333333333333331,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1393","Shepherdsville - Grade Lane - NE of Substation",0.61138118565406696,1,"2021-11-13",0,0,0,0,0,0,1,0,0,0,640.83000000000004,3204.15,0.2,1,"Continue to Monitor"]
["PLAINVIEW","Jefferson - 9900 Shelbyville Rd - Louisville","PV1250","Louisville - Shelbyville Rd, Dorsey Ln, & Ward Ave - NE of Substation",33.620596434114297,2865,"2024-02-01",7.2070413083849622E-2,0,0,0,7.2694642550601596E-2,2.2981007818474071E-2,6.5025983551553548E-2,1.5836701571497681E-2,0.64243511914979945,0.108956132274224,66.301834784083781,111.83134380000001,0.57263525305410123,0.57486910994764384,"Reliability Improvements Scheduled for 2026"]
["PLAINVIEW","Jefferson - 9900 Shelbyville Rd - Louisville","PV1251","Louisville - Dorsey Way & Cambridge Station Rd - N & S of Substation",20.5220793244665,1425,"2024-01-01",1.2919147400706203E-2,0,0,0,0.18429598700997449,1.965256836516405E-4,3.3570452846722852E-2,8.0598082424804762E-2,0,0.6884198046341401,124.48771929235083,208.41505262456135,0.79129824561403517,1.52140350877193,"Reliability Improvements Scheduled for 2026"]
["PLAINVIEW","Jefferson - 9900 Shelbyville Rd - Louisville","PV1253","Louisville - Shelbyville Rd, Hurstbourne Pky, & Whittington Pky - NW of Substation",5.3648703312702404,396,"2025-01-01",0,0,0,0,0.25501958431843041,0,2.8264935248244468E-2,0.28406083489184514,0.43265464554147992,0,38.20046295959596,71.564225585858594,0.54141414141414146,1.2196969696969697,"Trees Trimmed in 2025"]
["PLAINVIEW","Jefferson - 9900 Shelbyville Rd - Louisville","PV1254","Louisville - Hurstbourne Pky & Whittington Pky - W of Substation",6.6738825167180504,935,"2025-01-01",0,0,0,0,1.4404644539379998E-2,1.0406397195749809E-3,5.9480775550443642E-2,0,0,0.92507394019060141,11.332021388235294,19.527254898395721,0.10652406417112301,0.10053475935828877,"Continue to Monitor"]
["PLAINVIEW","Jefferson - 9900 Shelbyville Rd - Louisville","PV1256","Louisville - Hurstbourne Pky, Timberwood Cir, & Vieux Carre Dr - S of Substation",11.006183647026401,1095,"2023-11-04",6.7174745232393501E-2,0,0,0,2.9986540579279485E-2,0,9.0020800922931707E-4,0,0,0.90193850617909765,140.35939116803652,104.49009132054795,1.2131506849315066,1.5771689497716892,"Reliability Improvements Scheduled for 2026"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1282","Louisville - Berry Blvd, Powell Ave, Wheeler Ave & Southgate Ave - E of Substation",10.3142812643905,2108,"2022-01-01",1.0551941280215443E-2,0,0,0,0.74672504384128036,1.7569883251212623E-3,3.4432299218615736E-2,0.19078757460526161,4.5050982695416978E-4,1.5295642902551388E-2,53.168851987381402,69.574486079696385,0.68225806451612925,0.45588235294117657,"Reliability Improvements Scheduled for 2026"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1283","Louisville - Elderwood Way & Crums Ln - S of Substation",0.83799342983829495,9,"2021-12-25",1.0947484310258897E-3,0,0,0,0.99890525156897414,0,0,0,0,0,62.546666666666667,98.144444444444446,0.2,0.33333333333333331,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1458","Louisville - 7th Street Rd, Arcade Ave, Taylor Blvd, & Berry Blvd - NE of Substation",5.2027839591014997,15,"2021-08-07",0,0,0,0,8.027522935779817E-2,0,0,0,0,0.91972477064220182,37.993777733333332,87.219999866666669,0.34666666666666668,1.0666666666666667,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1459","Louisville - Manslick Rd, Bluegrass Ave, & Taylor Blvd - SE of Substation",4.4508535112220002,16,"2021-08-07",0,0,0,0,0,0,0,0.41242553191489362,0.58757446808510638,0,81.09020831250001,215.76562493750001,0.47499999999999998,0.9375,"Tree Trim Scheduled for 2026"]
["SKYLIGHT","Oldham - 8617 W Hwy 42 - Skylight","SK1127","Skylight - Hwy 42, Axton Ln, Shiloh Ln, & Hwy 1694 - W of Substation",27.672490954292702,271,"2022-05-20",2.1676300578034682E-2,7.9028179190751453E-3,0,0,9.1040462427745661E-2,0.26341221098265893,0.20447976878612717,7.2344653179190754E-2,0,0.33914378612716761,163.40849936014763,182.85910204428046,1.5682656826568264,2.6568265682656826,"Continue to Monitor"]
["SKYLIGHT","Oldham - 8617 W Hwy 42 - Skylight","SK1128","Skylight - Hwy 42, Hwy 393, & Hwy 524 - NE of Substation",160.29728430968899,1542,"2022-03-11",1.3711622276784461E-2,0,0,7.3003859221104975E-4,4.3632285176784774E-2,5.2787405898337449E-2,6.571439267964721E-2,0.66265977393762221,3.5222802162661335E-3,0.15724220122234667,249.75920231738004,394.23064199870299,1.6870298313878074,2.1634241245136185,"Tree Trim Scheduled for 2026"]
["SOLITE","Bullit - 1797 CORAL RIDGE RD - Shepherdsville","SL0001","Shepherdsville - Grade Lane - NE of Substation",1.12671417615949E-2,1,"-",0,0,0,0,0,0,0,0,0,1,41.493333200000002,207.466666,0.2,1,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1231","Louisville - Crittenden Dr, Phillips Ln, & Park Blvd - N & SE of Substation",6.8687179260743996,138,"2021-10-23",0.11406360424028268,0,0,0,6.219081272084806E-2,0,9.4558303886925793E-2,0,1.215547703180212E-2,0.71703180212014139,39.24557968985507,46.970289833333339,0.38405797101449279,0.26811594202898553,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1232","Louisville - Tug Rd, Crittenden Dr, Woodlawn Ave, & 1st St - S of Substation",11.5756937311915,1485,"2022-01-14",0.11401343360698088,0,0,0,7.5741049046060827E-2,0,1.2266299251774882E-2,0.49111123868572631,1.8322904108540483E-2,0.28854507530091661,59.70974185925926,111.77681256498317,0.51272727272727292,0.41885521885521881,"Reliability Improvements Scheduled for 2026"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1233","Louisville - Whitney Ave, 5th St, Bluegrass Ave & Taylor Ave - SW of Substation of Substation",14.5577406564584,2767,"2022-01-14",1.2241078520624856E-2,2.205207626826641E-4,0,0,0.28968013608452331,8.8683440268977301E-2,4.2995745545154167E-2,0.50677484757590374,3.8813830423885878E-2,2.0590400818248093E-2,66.256491984170566,90.273497163353809,0.90242139501264929,1.5334297072641851,"Reliability Improvements Scheduled for 2026"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1234","Louisville - Whitney Ave, Taylor Blvd, & Ashland Ave - W of Substation",13.6670935414597,2326,"2022-02-04",9.7883416310734963E-3,0,0,0,6.4305286443622003E-3,2.7078966680569562E-2,1.3536843550200888E-2,9.5787422984124293E-2,1.4941211874831713E-3,0.84588377532218639,44.778796212209798,74.064925475924341,0.67764402407566615,1.1423043852106618,"Reliability Improvements Scheduled for 2026"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1235","Louisville - Fairmont Ave, 3rd St, 5th St, & 4th St - NW of Substation",12.528773052218,2273,"2022-01-01",2.1056605433300589E-2,0,0,1.4297966544004457E-2,2.2280784060754445E-2,1.3158087642393232E-3,9.6211643624741605E-2,0.74755164274509234,8.8159187204034664E-2,9.1263616238326326E-3,48.438029032908041,66.567011287725464,0.52916849978002634,0.33743950725912891,"Reliability Improvements Scheduled for 2026"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1360","Louisville - Allmond Ave, Strawbery Ln, & Crittenden Dr - S of Substation",7.8696865519052599,107,"2021-08-21",0,2.3539070517519425E-2,0,0,0,0,0,0.80803401260812191,0,0.1684269168743586,292.32423674392527,427.77710278504674,1.8299065420560747,2.8598130841121496,"Tree Trim Scheduled for 2026"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1361","Louisville - Whitney Ave, 5th, 4th St, & Central Ave - NW of Substation",8.5995210781082498,59,"2021-08-21",0,0,0,0,0,0,0,0,0,1,46.713559322033902,233.56779661016949,0.15254237288135591,0.76271186440677963,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1364","Louisville - Park Blvd, Farmington Ave, & Floyd St - N of Substation",2.3079255184885699,52,"2021-08-21",0,0,0,0,4.6575342465753428E-2,0,4.5890410958904108E-2,0,0,0.90753424657534243,7.5130769115384624,28.056089730769234,8.076923076923076E-2,0.28846153846153844,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1384","Louisville - Crittenden Dr - S of Substation",2.3795019655335401,1,"-",0,0,0,0,0,0,1,0,0,0,211.11666640000004,356.95,0.8,1,"Continue to Monitor"]
["SHAWNEE","Jefferson - Rear of 3908 W Broadway - Louisville","SN0001","Louisville - 39th St, River Park Dr, & Louis Coleman Jr Dr - NE of Substation",3.9000347713487198,693,"2023-03-03",0,0,0,0,3.6712792996328723E-4,2.8974865857102513E-2,0.1275910759672409,2.8212369387178762E-2,0.8148545608585146,0,30.475257331601739,51.0949975930736,0.21702741702741704,0.27994227994227994,"Continue to Monitor"]
["SHAWNEE","Jefferson - Rear of 3908 W Broadway - Louisville","SN0002","Louisville - Broadway, 37th St, & Lindell Ave - E of Substation",2.43875442436982,541,"2023-03-03",0,0,0,0,0,0,0,5.0075954861111112E-2,0.78304036458333337,0.16688368055555555,28.301663583733824,34.071719035120147,0.20443622920517562,0.21256931608133087,"Continue to Monitor"]
["SHAWNEE","Jefferson - Rear of 3908 W Broadway - Louisville","SN0003","Louisville - 40th St & Garland Ave - S of Substation",1.5587244458724001,276,"2023-03-03",3.3172102751813842E-2,0,0,0,0,0.18301849794104189,7.9220864108765277E-2,0,0,0.70458853519837894,38.043695648550724,110.86231882971016,0.54420289855072468,1.8550724637681162,"Continue to Monitor"]
["SOUTHERN","Jefferson - 1475 S 3rd Street - Louisville","SO0409","Louisville - 3rd St - S of Substation",1.9709796082868101,177,"2025-01-01",0,0,0,0,0.29625895462987528,0,0.3673653488989122,0.33637569647121252,0,0,36.029227870056495,106.46949152542373,0.24293785310734464,0.76836158192090398,"Trees Trimmed in 2025"]
["SOUTHERN","Jefferson - 1475 S 3rd Street - Louisville","SO0422","Louisville - 2nd St & 3rd St - N of Substation",1.47864329597912,791,"2025-01-01",0,0,0,0,0,6.2676588801782797E-5,6.2338334195550958E-3,0.96259401488320262,0,3.1109475108440449E-2,47.390303411378,47.533375472819216,0.25587863463969657,0.20606826801517064,"Trees Trimmed in 2025"]
["SOUTHERN","Jefferson - 1475 S 3rd Street - Louisville","SO0453","Louisville - 3rd St, Oak St, & Brook St - N of Substation",2.3166543231214001,630,"2025-01-01",0,0,0,1.9609524626247035E-3,9.9202469771031643E-2,3.4302375439499183E-5,2.7573392790784097E-2,8.6464854357830939E-2,0.76769287939856501,1.7071148843724095E-2,70.913698410793657,275.26169311746031,0.60507936507936499,1.5349206349206344,"Continue to Monitor"]
["SOUTH PARK","Jefferson - 1412 Fairdale Rd. - Louisville","SP1114","Louisville - Farmers Ln, South Park Rd, & Minor Ln - NE & S of Substation",9.2393977377210099,535,"2025-01-01",0,0,0,0,0.10494698399816516,0,0,0.57487517863128734,0.32017783737054745,0,146.13697818504673,204.92464174018693,1.5727102803738318,0.9214953271028038,"Trees Trimmed in 2025"]
["SHEPHERDSVILLE","Bullitt - 1706 4th St. - Shepardsville","SV1121","Shepherdsville - Hwy 44, Blue Lick Rd, & Buckman St - E of Substation",9.3642015679636401,1020,"2025-01-01",1.7874655367022554E-2,6.1784134855577967E-2,0,0,6.9675998741742684E-2,5.837943859519272E-2,0.14211831319504839,6.5965990044964196E-3,0,0.64357086024091925,50.640163395490198,78.896094762745108,0.46843137254901956,0.56862745098039202,"Continue to Monitor"]
["SHEPHERDSVILLE","Bullitt - 1706 4th St. - Shepardsville","SV1122","Shepherdsville - HWY 44, Preston Hwy, & Old Preston Hwy - SE of Substation",18.865343611956899,939,"2025-01-01",0,0,0,0,3.8297243730996022E-2,0,1.9690273657257517E-2,0.24994768136102324,0.17939138035035024,0.51267342090037304,59.570319482854096,138.20001774227899,0.84813631522896726,1.8913738019169331,"Reliability Improvements Scheduled for 2026"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1184","Louisville - Romania Dr, Meyers Ln, & Blanton Ln - SW of Substation",16.138409659833901,1450,"2022-09-02",3.3113862881304738E-2,1.2781636967683479E-2,0,0,0,6.8076109936575049E-2,0.25884627000906069,4.3612201751736634E-2,0.48479613409845967,9.8773784355179708E-2,37.251993097379319,56.548965511034496,0.5346206896551724,0.42758620689655175,"Continue to Monitor"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1186","Louisville - Gagel Ave, Hazelwood Ave, Bluegrass Ave, & Lonsdale Ave - E of Substation",13.970530757494799,2082,"2022-05-13",1.6587705932768308E-2,0,0,0,4.5567088848681075E-2,1.6012363901850617E-2,3.2429451163381265E-2,0.64556153382217563,2.1247976383201601E-2,0.22259387994794147,65.471276012488005,109.75889368683958,0.98780019212295866,1.5302593659942361,"Reliability Improvements Scheduled for 2026"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1188","Louisville - Rockford Ln, Imperial Ter, & Dover Rd - W of Substation",14.082350498413399,1903,"2022-07-08",6.908734658613162E-3,0,0,0,9.0270224402736951E-3,9.874028989531986E-5,1.4368254996798654E-2,0.93105150694653371,0,3.8545740667885492E-2,48.866349619653185,59.271352246452977,0.86925906463478708,1.2664214398318443,"Reliability Improvements Scheduled for 2026"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1191","Louisville - Gagel Ave, Manslick Rd, & Parkwood Rd - SE of Substation",17.456337697687299,1362,"2022-07-08",3.0103970477896702E-2,0,0,0,8.0094783101352082E-2,7.7786454744514372E-3,2.2176030134595067E-2,0.77917374860275301,0,8.067282220895157E-2,76.773551144199701,74.183932938325981,0.66226138032305426,0.77386196769456694,"Reliability Improvements Completed in 2025"]
["SMYRNA","Jefferson - 7000 Manslick Rd. - Louisville","SY1250","Louisville - Vaughn Mill Rd, Outer Loop & Fegenbush Ln - N of Substation",28.297125171484701,2243,"2022-10-07",1.6040256460786155E-2,0,0,2.725927012250173E-2,0.5523210251098758,6.8835614868859446E-3,6.9092258972232021E-2,3.6466377330992984E-2,0.1426574580318147,0.14927979248491069,93.518770986000874,314.675479261703,0.96353098528756154,3.6790013374944275,"Reliability Improvements Scheduled for 2026"]
["SMYRNA","Jefferson - 7000 Manslick Rd. - Louisville","SY1251","Louisville - Smyrna Pky, Michael Ray Dr, & Lantana Dr - NW & SW of Substation",21.8038741262435,1560,"2022-11-18",2.5547379023111053E-2,0,0,0,0.28434672933661204,1.7693975881749799E-4,9.3505857159708553E-3,1.9667534730098815E-2,0.40158066184543634,0.25933016958995347,46.909822645897449,81.428151706410276,0.46397435897435901,1.0698717948717948,"Continue to Monitor"]
["SMYRNA","Jefferson - 7000 Manslick Rd. - Louisville","SY1252","Louisville - Cooper Chapel Rd, McNeely Lake Dr, & Beulah Church Rd - SW & SE of Substation",38.754077920042697,2462,"2022-10-29",1.0750768509788388E-2,4.982063455755594E-3,0,0,7.2401711642853556E-2,2.4798736910228013E-2,0.14292887309406782,0.66427140808846086,0,7.9866438298845696E-2,36.036617921256678,45.466084477120091,1.007717303005687,1.3050365556458174,"Continue to Monitor"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1138","Louisville - Brownsboro Rd, Chenoweth Ln, Canoe Ln, & Wampum Rd - W of Substation",11.8468089805086,574,"2024-01-01",5.51305959299508E-3,0,0,0,0.21217137783843093,1.5418732771688771E-2,6.3446709029088943E-2,0.6338661590413015,0,6.9583961726494864E-2,209.6753716463414,349.26451797735177,1.5526132404181185,2.9198606271776999,"Continue to Monitor"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1173","Louisville - Hubbards Ln, Rudy Ln, Massie Ave, & Westport Rd - S of Substation",25.930707436242798,2041,"2024-01-01",4.4476436332535523E-3,0,0,0,1.8857426881992472E-2,4.0412769987529135E-4,9.1717956927375686E-3,0.91825425789392379,0,4.8864748198217359E-2,70.556371054875058,87.481030534541915,0.67819696227339543,0.70357667809897129,"Continue to Monitor"]
["TERRY","Jefferson - 8408 Terry Ln. - Louisville","TE1244","Louisville - Terry Rd, Johnsontown Rd, & Dixie Hwy - S of Substation",11.4583023732838,1897,"2025-01-01",2.473298143073789E-3,0,0,0,0.28677566534974386,0.32391418957179396,3.0493162632370266E-3,0.38378753067215132,0,0,34.490228429625731,65.199674924090672,0.38608328940432263,0.820242488139167,"Reliability Improvements Scheduled for 2026"]
["TIP TOP","Meade - US 60 - Tip Top","TT3316","Tip Top - Chaffee Ave, Bullion Blvd, & Black Horse Regiment Ave - SE of Substation",4.4394277881102902,2,"2020-02-15",0,0,0,0,0.28162650602409639,0,0,0,0,0.71837349397590367,97.186666500000015,331.75833250000005,0.5,1.5,"Continue to Monitor"]
["VERMONT","Jefferson - Rear 529 Southwestern Pkwy - Louisville","VE0001","Louisville - Southwestern Pky - N of Substation",2.1237478391733702,264,"2023-02-03",0,0,0,0,0,0,0.94363636363636361,5.6363636363636366E-2,0,0,29.791717165151518,39.5840277689394,0.22121212121212119,0.30681818181818182,"Continue to Monitor"]
["VERMONT","Jefferson - Rear 529 Southwestern Pkwy - Louisville","VE0002","Louisville - River Park Dr, 44th, 43rd, & 42nd St - SE of Substation",1.2005798226870801,316,"2023-02-03",0,0,0,0,0.9709781159306613,8.4973984887703606E-5,2.07859439956075E-3,0,0,2.6858315684890319E-2,26.847183542405059,24.222784806962025,0.15632911392405063,0.17721518987341772,"Continue to Monitor"]
["WESTERN","Jefferson - 2807 W Broadway - Louisville","WE0001","Louisville - 28th St, Chestnut St, 26th St, & Muhammad Ali Blvd - NE of Substation",5.0574433624807504,899,"2022-11-04",0,0,0,0,6.4683713808874416E-2,5.0498958758978547E-3,1.3161975748684294E-2,0.82467150445789006,2.0406354770262352E-3,9.0392274631627148E-2,64.452795693659624,101.12469409788658,0.52814238042269179,0.43159065628476073,"Continue to Monitor"]
["WESTERN","Jefferson - 2807 W Broadway - Louisville","WE0004","Louisville - Broadway, 24th, 234d, 22nd, & Dr W J Hodge St - E of Substation",3.5593676645441499,432,"2022-11-04",0,0,0,0,0.2888921180416803,1.5136653709691091E-3,1.1273779682977925E-2,1.3078068805173102E-3,0.678558021821,1.8454608202855379E-2,87.014220673611106,135.93730709027778,0.31712962962962965,0.83333333333333337,"Continue to Monitor"]
["WHAS","Jefferson - 1310 Flat Road Rd. - Louisville","WH1116","Louisville - Flat Rock Rd, Long Run Rd, & Aiken Rd - NW & SE of Substation",34.571932764305203,1197,"2024-01-01",8.2463401074803887E-3,0,0,3.3942800667119646E-2,0.64506763851998272,1.8191364506763851E-2,7.2085984310334181E-2,3.2985360429921548E-2,0,0.18948051145839767,21.673071564912277,26.920857694235586,0.2252297410192147,0.20885547201336674,"Reliability Improvements Scheduled for 2026"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1178","Louisville - Chamberlain Rd, Sweet Water Dr, & Shenandoa Dr - E of Substation",11.7747356299417,713,"2024-01-01",2.1817338990053711E-2,0,0,0,0,1.2092751403263028E-4,0,0.91871655598440027,0,5.934517751151331E-2,33.290467504347831,29.43202430575035,0.61626928471248243,0.6241234221598877,"Continue to Monitor"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1179","Louisville - Chamberlain Ln - NW of Substation",27.644671742901501,1312,"2025-01-01",0,0,0,0,0,1.6141111856578925E-2,0.10432822081103431,9.0020439687319598E-2,0,0.78951022764506718,57.935820626371957,95.478988817073201,0.72942073170731703,0.89176829268292668,"Reliability Improvements Scheduled for 2026"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1182","Louisville - Brownsboro Rd, Park Plaza Ave, & Ten Broeck Way - W of Substation",18.554926380335399,1024,"2024-01-01",0,0,0,0.17399249469734052,0.36996247348670253,0,2.9858051884483604E-3,0.2704193179964105,0,0.18263990863109805,42.375514318945314,43.855485022460947,0.6,0.4951171875,"Reliability Improvements Scheduled for 2026"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1183","Louisville - Ballardsville Rd, Haunz Ln, & Hitt Ln - NE of Substation",32.417909411735899,1679,"2025-01-01",3.2796895444937767E-2,0,0,0,3.9656888511133232E-3,1.4314951295614928E-4,1.0389523245020522E-2,0.84081103145934222,0,0.11189371148663006,105.85973793305538,243.62359538773077,0.97200714711137581,2.405598570577725,"Reliability Improvements Scheduled for 2026"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1184","Louisville - Brownsboro Rd & Worthington Ln - N of Substation",46.000161530899703,3019,"2025-01-01",4.1463818820031036E-3,0,0,0,1.2747400978768625E-5,0,8.5248823472832386E-2,0.68901556457659507,1.5285292628178014E-3,0.22004795340477287,55.975627689566068,160.3198520440543,0.45445511758860546,1.7727724412056971,"Trees Trimmed in 2025"]
["WEST POINT","Hardin - Crop St and I-C Railroad - West Point","WP1104","West Point - Main St, Dixie Hwy, 16th St, & Private Rd - W, SW & NE of Substation",24.222466308334901,700,"2019-02-09",5.5825828122334446E-3,0,0,0,2.5086747269425381E-2,7.2944180054472832E-4,7.8036826726478655E-3,0.9443178752738558,1.4983810257733301E-3,1.4981289145519437E-2,120.86189046542856,99.855976181428588,1.4579999999999997,1.5599999999999996,"Reliability Improvements Scheduled for 2026"]
["WATERSIDE WEST","Jefferson - 150 North 3rd Street - Louisville","WS1304","Louisville - N 3rd St - E of substation",2.1727316733592801E-2,1,"-",0,0,0,0,0,0,1,0,0,0,14.673333199999998,73.366665999999995,0.2,1,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1152","Louisville - Bardstown Rd, Seatonville Rd, & Fern Creek Rd - SE of Substation",32.511389558746799,2628,"2025-01-01",3.1681146687491862E-2,3.2702069504099963E-3,0,0,0.10590752310295458,1.321912013536379E-3,6.0803885201093325E-2,2.696700507614213E-3,4.9459846414161134E-3,0.78937264089548353,86.712663618721493,110.26353373477929,1.1896499238964993,1.3896499238964992,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1153","Louisville - Bardstown Rd, Watterson Trl, & Woodhaven Rd - W of Substation",19.471922888273401,1099,"2021-09-18",6.6419438755742518E-4,0,0,0,0.28182353917932923,0,1.1724333282324941E-2,0.40927723278385353,0,0.29651070036693483,82.716417949226553,253.01521078980886,0.77561419472247506,2.747042766151047,"Reliability Improvements Completed in 2025"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1154","Louisville - Walt Lee Rd, Fairground Rd, Billtown Rd, & Easum Rd - E of Substation",44.467293551253597,2910,"2025-01-01",1.0209048626068157E-2,0,0,0,0.14813783762224078,9.5969289827255271E-3,3.4513128826765257E-4,0.62331850245580445,0,0.2083925510248934,83.229286364398632,213.73921534432992,1.1206872852233676,3.3185567010309276,"Trees Trimmed in 2025"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1155","Louisville - Hurstbourne Pky, Watterson Trl, & Glaser Ln - S of Substation",20.872914291303399,2123,"2025-01-01",2.2112471628822194E-3,0,0,0,2.0748706858762674E-2,0.41744352552675412,0.13762334765286341,0.22194784573872214,6.0492708729068647E-3,0.19397605618710853,46.733187310409804,50.379855545925579,0.59114460668864832,1.405558172397551,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1209","Louisville - Laverne Dr, Watterson Trl, & Dell Rd - NE of Substation",25.640776243455701,1644,"2024-01-01",0,0,0,0,3.4375354441313244E-3,0.23665773838086845,3.351742469848859E-3,0.72241755876818747,0,3.4135424936963976E-2,34.534531626277371,23.714101780413632,0.55608272506082712,1.1222627737226272,"Reliability Improvements Scheduled for 2026"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1210","Louisville - Bardstown Rd, Hudson Ln, Fairground Rd & Janet Lee Dr - SE of Substation",22.315567690383801,1971,"2024-01-01",2.2500291866993558E-3,0,0,3.6040267031765744E-2,1.5758164315810702E-2,0,6.2711603570329332E-3,0.77421700045637387,0,0.16546337865231742,118.80384575900557,236.7476407864028,0.96915271435819383,2.1263318112633178,"Reliability Improvements Scheduled for 2026"]

{"sheet":"LGE Section 6-7","index":2,"n_rows":31,"n_cols":1,"rows_kept":31,"cut":false,"hidden":false,"merged":[[0,0,0,8],[2,0,2,8],[4,0,4,8],[5,0,10,8],[11,0,14,8],[15,0,15,3],[26,0,27,8],[29,0,29,8],[30,0,33,8],[16,0,16,3],[17,0,17,3],[18,0,18,3],[19,0,19,3],[20,0,21,8],[23,0,24,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
[]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 6: VEGETATION MANAGEMENT PLAN REVIEW"]
["The Companies’ Vegetation Management Plan went into effect January 1, 2024.  The Distribution Vegetation Management Program encompasses right of way maintenance for Louisville Gas and Electric Company and Kentucky Utilities Company (referred to as the “Companies”).  The program is centralized and managed by a Forestry Manager and eight company Utility Arborists.  All are certified arborists by the International Society of Arboriculture."]
[]
[]
[]
[]
[]
["The Companies’ plan is to maintain a proactive trim cycle while balancing the reactive needs of worst performing circuits. The Companies’ goal is to maintain an average trim cycle of five years or less.   The effectiveness of the plan is evaluated by the cycle and system performance as measured by system SAIDI, SAIFI, and CAIDI.  "]
[]
[]
[]
["Effectiveness of the program"]
["KU/LG&E Tree Cycle – 5.0 years"]
["LGE Tree SAIDI – 27.51 minutes"]
["LGE Tree SAIFI – 0.183"]
["LGE Tree CAIDI – 150.3 minutes"]
["The hazard tree program, mid cycle, herbicide, and worst performing circuits were completed as planned.  "]
[]
["Adjustments made to the tree plan in 2025 included"]
["The 2025 maintenance plan was completed as planned."]
[]
["Changes to be implemented in 2026"]
["The routine trimming cycle plan is a proactive vegetation management strategy that schedules maintenance activities based on established trim intervals and clearance standards. Hazardous or danger trees are prioritized for assessment and mitigation based on their potential impact on system reliability and the level of vegetation-related risk they pose."]
[]
[]
["SECTION 7: UTILITY COMMENTS"]
["280 Circuits were above their previous 5 year average SAIDI and/or SAIFI in 2025.  Specific recommendations for each circuit are included in circuit reporting. "]