{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["KU Section 1-4","Excel KU Section 5","KU Section 6-7"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"KU Section 1-4","index":0,"n_rows":46,"n_cols":8,"rows_kept":46,"cut":false,"hidden":false,"merged":[[36,1,36,3],[36,6,36,8],[37,0,37,8],[41,1,41,8],[38,1,38,8],[39,1,39,8],[40,1,40,8],[44,0,44,8],[45,2,45,6],[20,0,21,8],[24,0,24,8],[25,2,25,6],[26,0,26,1],[26,5,26,6],[28,3,28,5],[29,1,29,3],[29,6,29,8],[30,1,30,3],[30,6,30,8],[31,1,31,3],[31,6,31,8],[34,1,34,3],[34,6,34,8],[35,1,35,3],[35,6,35,8],[33,3,33,5],[18,0,18,3],[18,5,18,8],[17,0,17,3],[17,5,17,8],[6,0,6,3],[6,5,6,8],[7,0,7,3],[7,5,7,8],[10,0,10,8],[11,0,11,3],[11,5,11,8],[14,0,14,8],[15,0,15,3],[15,5,15,8],[16,0,16,3],[16,5,16,8],[5,0,5,3],[5,5,5,8],[0,0,0,8],[1,0,1,8],[3,0,3,8],[4,0,4,3],[4,5,4,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 1: CONTACT INFORMATION"]
["UTILITY NAME",null,null,null,null,"KENTUCKY UTILITIES COMPANY"]
["REPORT PREPARD BY",null,null,null,null,"Tiffany Koller (Dir. Substations & Asset Mgmt)"]
["E-MAIL ADDRESS OF PREPARER",null,null,null,null,"Tiffany.Koller@lge-ku.com"]
["PHONE NUMBER OF PREPARER",null,null,null,null,"(502) 364-8633"]
[]
[]
["SECTION 2: REPORTING YEAR"]
["CALENDAR YEAR OF REPORT",null,null,null,null,2021]
[]
[]
["SECTION 3: MAJOR EVENT DAYS (MED)"]
["TMED",null,null,null,null,3.5950000000000002]
["FIRST DATE USED TO DETERMINE TMED",null,null,null,null,"2016-01-01"]
["LAST DATE USED TO DETERMINE TMED",null,null,null,null,"2020-12-31"]
["NUMBER OF MED IN REPORTING YEAR",null,null,null,null,6]
[]
["NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years.  If five years of data are not available, then utilities should use what is available until five years are accumulated.        \n"]
[]
[]
[]
["SECTION 4: SYSTEM RELIABILTIY INFORMATION AND RESULTS"]
[null,null,"System-wide Information"]
["TOTAL CUSTOMERS",null,551019,null,null,"TOTAL CIRCUITS",null,1112]
[]
[null,null,null,"Excluding MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",80.760000000000005,null,null,null,"SAIDI",72.260000000000005]
["SAIFI",0.74,null,null,null,"SAIFI",0.63800000000000001]
[]
[null,null,null,"Including MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",152.80000000000001,null,null,null,"SAIDI",213.29]
["SAIFI",0.85599999999999998,null,null,null,"SAIFI",0.78400000000000003]
["Notes:  "]
["1)","All duration indices (SAIDI) are to be reported in units of minutes."]
["2)","Reports are due on the first business day of May of each year"]
["3)","Reports cover the calendar year ending in the December before the reports are due."]
["4)","IEEE 1366 (latest version) is used to define SAIDI, SAIFI, and TMED"]
[]
[]
["SECTION 5: CIRCUIT REPORTING"]
[null,null,"BEGIN ON NEXT PAGE"]

{"sheet":"Excel KU Section 5","index":1,"n_rows":416,"n_cols":22,"rows_kept":416,"cut":false,"hidden":false,"merged":[]}
["Substation Name","Substation Location   \n(County - Road - Town)","Circuit\nNumber","Circuit Location\n (Town - Road - General Area)","Total Circuit Length (Miles)","Average 2021 OMS Custs","Date of Last Circuit Trim (VM)","Animal","Construction","Lightning","Non-Company","Other/Unknown","Overload","Planned Work","Trees","Vehicle","Utility Equipment","2017-2021 SAIDI Average","2021 SAIDI","2017-2021 SAIFI Average","2021 SAIFI","LIST OF CORRECTION ACTION, IF ANY, TAKEN OR TO BE TAKEN"]
["BUCHANAN","Fayette - 108 Buchanan St. - Lexington",10,"Lexington - Manchester St. - S of Station",3.533666666666667,331,"2017-09-30",0,0,0,0,0,0,0.80224291579052764,0.1977570842094723,0,0,15.726289374883129,24.086113973416182,0.10277696149492876,0.16237020152682802,"Continue to Monitor"]
["LEXINGTON WATER COMPANY 4KV","Fayette - 2300 Richmond Rd. - Lexington",11,"Lexington - Richmond Rd and Holiday Rd - NW of Station",3.3882585227272735,152,"2017-12-02",0,0,0,0,0,0,3.7729658792650916E-2,7.0931758530183728E-2,0.89133858267716537,0,40.141409743036739,99.630951152390779,0.25473586819097649,0.37925696594427244,"Continue to Monitor"]
["G E LAMP WORKS","Fayette - 1809 Edision Dr - Lexington",12,"Lexington - Edision Dr - S of Station",0.65832181186868688,18,"2020-05-09",0,0,0,0,0,0,1,0,0,0,11.51431371764706,24.889215647058823,0.10588235294117647,5.8823529411764705E-2,"Continue to Monitor"]
["RACE STREET 4KV","Fayette - 420 Corral St - Lexington",14,"Lexington - Race St. and E Third St. and Chestnut Street - N of Station",5.7633707386363628,928,"2018-12-08",0,0,0,0,8.3927480138521082E-2,0,0.6676852040469885,2.1796699938887758E-2,4.8346574319277517E-2,0.17824404155632512,14.057694920209752,14.510612374961182,0.10283664513731901,0.15053532957121116,"Continue to Monitor"]
["RACE STREET 4KV","Fayette - 420 Corral St - Lexington",15,"Lexington - Coral St & Forrest Ave. - SE of Substation",3.0562045454545457,519,"2018-12-08",0,0,0,0,1.6127725099278709E-2,0,0.84771861577113217,0.1361536591295891,0,0,7.9109198590538883,23.730833328846153,6.287795731145937E-2,0.11153846153846153,"Continue to Monitor"]
["SCOTT STREET","Fayette - 301 Scott St. - Lexington",17,"Lexingotn - Broadway Rd. - SE of Substation",4.8451066919191916,987,"2019-07-20",0,0,0,0,2.6861611696701801E-2,0,0.57412444746684799,0,0,0.3990139408364502,4.2547046686868955,11.904441387758506,2.2667158663340629E-2,7.5911983609987521E-2,"Continue to Monitor"]
["SCOTT STREET","Fayette - 301 Scott St. - Lexington",18,"Lexington - Limestone St. - SE of Substation",3.2531822916666671,883,"2019-07-20",0,0,0,0.12949715601772691,0.2912028474718219,0,0.48452385106605717,0,0,9.4776145444394042E-2,18.65306336880986,32.415882286588058,0.19990452648702675,0.23972888531579439,"Continue to Monitor"]
["KUNKEL","Fayette - 2000 Versailles Rd. - Lexington",19,"Lexington - Versailles Rd. - NE of Substation",2.1492410037878789,175,"2020-03-28",0,0,0,0,0.80376670716889431,0,0.19623329283110572,0,0,0,16.59677516870126,28.349408317733992,0.16666982531173513,0.26407224958949094,"Continue to Monitor"]
["HIGBY MILL 12KV","Fayette - 308 Waveland Museum Ln. - Lexington",23,"Lexington - Nicholasville Rd - S of Substation",56.73810479797978,1726,"2019-01-27",1.7966832908453952E-3,0,0.3847817215299898,0,2.5566962227251286E-2,0,2.8566734329370739E-3,0.35370281056386177,0,0.23129514895511472,88.303416192140006,87.493481957020691,1.1156240181182719,1.1323971172878677,"Continue to Monitor"]
["KUNKEL","Fayette - 2000 Versailles Rd. - Lexington",26,"Lexington - Duntreath Dr. & Pine Mt. Rd. - SE of Substation",4.6641103219696962,570,"2020-03-28",0,0,0,0,4.6250044075645562E-3,0,8.4119838741904776E-2,0.91125515685053071,0,0,113.54819139525003,297.13557899204744,0.53297881062292551,1.1807490367173377,"Continue to Monitor"]
["MOUNT TABOR","Fayette - 248 Old Mt. Tabor Rd - Lexington",27,"Lexington - Tates Creek Rd. & Raintree Rd. - NW of Substation",3.0942503156565651,189,"2019-03-23",0,0,0.3175123998473865,0,0,0,0,0.65463563525371993,0,2.7851964898893553E-2,23.043349406497661,94.148684205263166,0.23034444750620003,0.97894736842105257,"Continue to Monitor"]
["RACE STREET 4KV","Fayette - 420 Corral St - Lexington",30,"Lexington - Midland Ave. & Winchester Rd. - E of Substation",5.1810288825757578,911,"2018-12-08",0,0,0,0,8.0825815826118547E-3,0,0.22940001210873645,0.5596355270327541,0,0.20288187927589757,34.603864267780793,36.633778059719042,0.51525910254151097,0.19705771882063278,"Continue to Monitor"]
["G E LAMP WORKS","Fayette - 1809 Edision Dr - Lexington",32,"Lexington - Edision Dr. - Rosemont Garden",2.1384057765151514,284,"2020-05-09",0,0,0,0,0.32199618563254928,0,0.24793388429752067,0,0,0.43006993006993005,9.0069883235603001,11.041958852545093,0.10681685231321199,9.1289844329132688E-2,"Continue to Monitor"]
["LANSDOWNE SWITCHING","Fayette - 3200 Montavesta Rd. - Lexington",33,"Lexington - Pepperhill Dr & Claiborne Way - S of Substation",17.638677714646455,2508,"2021-12-04",9.1052018107397464E-3,0,4.0579003008863954E-2,0,5.9407443549917324E-2,0,4.5279336423517932E-2,0.7592610663847551,2.1216556883792793E-2,6.515139193841317E-2,59.224569378830516,40.827912949586612,0.39898660110028084,0.93719348631832733,"Trees Trimmed in 2021"]
["HUGHES LANE","Fayette - 251 Hughes Ln. - Lexington",37,"Lexington - Mir Station Rd. & US 27 - SW of Substation",138.71284816919191,1110,"2020-01-25",3.8111318820478802E-3,3.5608755954893564E-3,7.2113007296629075E-2,0,0.23262980160405233,2.5930169450642224E-4,3.0543327504070433E-2,0.4675209551950793,4.7817041548573844E-2,0.14174455767955135,266.98647491744629,275.91368157138356,1.6761090522888675,1.0302774291981083,"Continue to Monitor"]
["LEXINGTON WATER COMPANY 12KV","Fayette - 2300 Richmond Rd. - Lexington",39,"Lexington - St. Phillip Dr. & Richmond Rd.  - E of Substation",13.866044665404029,2047,"2020-01-04",0,0,4.5360591216694508E-2,0,0.10171683136544252,0,3.5110569980462665E-3,0.84209209917792183,0,7.3194212418948379E-3,53.876186376151907,71.866480811284362,0.47373804225947991,0.33464202336407128,"Continue to Monitor"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",40,"Lexington - Reynolds Rd. - W of Substation",12.698947127525251,1095,"2021-12-25",3.2760052767870231E-2,0,0,0,2.6782951417729354E-2,0,2.4673865246494356E-2,0.78174622563150431,0,0.13403690493640169,28.925295474463212,98.292293185978082,0.21516376723852865,0.74830373124609384,"Trees Trimmed in 2021"]
["VILEY ROAD","Fayette - 308 Alexandria Rd. - Lexington ",41,"Lexington - Leestown Rd. & Adams Ln. - NE of Substation",63.096738478535315,1120,"2021-12-27",5.5696478408533666E-3,2.151276478529613E-2,1.5952197892009372E-3,0,0.13278464230147535,0,4.4738801678159109E-3,0.30632760426441297,0,0.52773624085094528,153.69473807902148,224.32231839148443,0.98168876012635964,0.66716588702070445,"Trees Trimmed in 2021"]
["LIBERTY ROAD","Fayette - 2125 Liberty Rd. - Lexington",42,"Lexington - Codell Dr. & Plumbo Dr. - S of Substation",12.410075126262626,1786,"2019-08-10",0.78731351187240084,6.5875408632290952E-3,0,0,8.5934576469840637E-2,0,3.343900699705573E-2,2.0461622102505808E-2,0,6.6263741694967904E-2,117.39028760850672,79.283691969141131,0.8512537049982235,1.305769889817801,"Continue to Monitor"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",44,"Lexington - Nicholasville Rd . - E of Substation",14.481703125000001,1646,"2017-10-14",1.7127823975274119E-2,0,4.4190153800868347E-2,0,0.14752741187725366,0,3.9701228935168149E-2,0.7445237569602865,0,6.929624451149214E-3,89.347296623603597,76.689024175708568,0.83435268033611787,1.3014374358779479,"Tree Trim Scheduled for 2022"]
["HALEY","Fayette - 5481 Winchester Rd - Lexington",46,"Lexington - Winchester & Haley Rd - W of Substation",45.990377683080794,395,"2021-08-17",2.6153992803183757E-3,0,1.5251531110740415E-3,0,4.2060863141338799E-2,0,2.2990491623573146E-2,0.91470462073731618,1.2808903081285895E-3,1.482258179825084E-2,190.23006151790074,324.62772138940556,1.2891577260124643,1.950190968083352,"Trees Trimmed in 2021"]
["ASHLAND AVENUE","Fayette - 448 S Ashland Ave. - Lexington",49,"Lexington - Euclid Ave. - NW of Substation",1.9299296085858584,1054,"2020-09-18",0,0,0,0,0.10463625967965985,0,0.8072510149732538,8.8112725347086321E-2,0,0,43.812682890144877,110.83071366121797,0.38345265372411386,1.0345057171804892,"Continue to Monitor"]
["ASHLAND AVENUE","Fayette - 448 S Ashland Ave. - Lexington",50,"Lexington - Fountaine Rd & Ridge Way Rd. - SE of Substation",4.7397703598484853,987,"2019-11-23",1.9695415930444021E-2,0,0,0,0.40857405815759285,0,1.9334835903810899E-2,0.54876775695246249,0,3.6279330556897868E-3,123.28664432435846,484.12659116184858,0.47244601416468646,1.2511793172124033,"Continue to Monitor"]
["AMERICAN AVENUE","Fayette - 96 Burley Ave. - Lexington",52,"Lexington - Waller Ave. & St. Joseph Dr. - SE of Substation",0.45888068181818181,88,"2019-07-20",0.24875621890547264,0,0,0,0.75124378109452739,0,0,0,0,0,1.9942134808733403,4.5628787840909091,5.2221654749744627E-2,0.14772727272727271,"Continue to Monitor"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",53,"Lexington - New Circle Rd. - West of Substation",4.0408319128787902,126,"2020-05-09",0.26008614109693601,0,5.4519681605059425E-4,0,0,0,0,0,0,0.73936866208701346,58.153257203144904,288.8462546216723,0.27758360688784867,1.3543932008498936,"Continue to Monitor"]
["WEST HIGH STREET","Fayette - 727 West High St - Lexington",54,"Lexington - West High St & Broadway - S of Substation",3.2423969381313125,748,"2019-05-11",0,0,0,0,0,0,9.4904807166105009E-3,0,0.99050951928338948,0,40.942073753998123,47.451746645161286,0.53357975259917723,1.0026881720430108,"Continue to Monitor"]
["HAEFLING"," Fayette - 1555 Baunmann Dr - Lexington  ",55,"Lexington - Fairman Rd & Leestown Rd - S of Substation",17.079333964646462,1338,"2021-12-20",7.8583206699214328E-2,0,2.7005399463286884E-2,0,0.11423744705616089,0,0.28228361731708107,0.47621972905687221,1.7863493808399885E-3,1.9884251026544668E-2,49.23810323298077,92.501835640233395,0.45449511422144628,0.91139425827321041,"Trees Trimmed in 2021"]
["PROCTOR & GAMBLE","Fayette - 120 Zesta Pl - Lexington",68,"Lexington - Delware Rd - SE of Substation",3.3295806502525256,378,"2019-10-19",0,0,0,0,3.1545741324921134E-2,0,0.14061346399087188,0.38271024901000067,4.2553191489361701E-2,0.40257735418484464,37.553467947053115,39.335979596067268,0.26315777764732329,0.25611151155519996,"Continue to Monitor"]
["WILSON DOWNING","Fayette - 680 Wilson Downing Rd - Lexington",72,"Lexington - Tates Creek Rd & Trent Blvd - NE of Substation",8.3162200126262622,1372,"2019-02-16",4.882425905887942E-3,0,0,0,1.6837771502467604E-2,0,6.5855568164823672E-2,0.49049466452015866,0,0.42192956990666208,39.395159324255928,79.68667249176977,0.50971574751336168,0.4574770326055087,"Continue to Monitor"]
["WILSON DOWNING","Fayette - 680 Wilson Downing Rd - Lexington",73,"Lexington - Wilson Downing Rd - W of Substation",17.741611584595955,3086,"2018-07-28",0.18007900652180661,0,2.0226024269455689E-2,0,1.8168839863268175E-2,0,8.7018013664315386E-2,0.62960483438335446,8.6321940492394174E-3,5.6271087248560191E-2,33.08059654810053,64.981454841375538,0.30597028718742225,0.68209376834837687,"Continue to Monitor"]
["LOUDON AVENUE","Fayette - 811 E Loudon Ave - Lexington  ",75,"Lexington - Floyd Dr - NE of Substation",11.197719065656564,1276,"2018-06-16",2.5646432301755038E-3,7.1398098339111541E-3,0,0,0.36199228155173174,0,3.5228292477209981E-2,0.58721993654592086,0,5.8550363610507684E-3,69.138548550419827,66.82629837192323,0.33248182846900132,0.37128730567486601,"Continue to Monitor"]
["TRAFTON AVENUE 4KV","Fayette - 141 Trafton St - Lexington ",78,"Lexington - Versailles Rd - W of Substation",5.226217171717173,500,"2020-01-22",0,0,0,0,3.3425005288766657E-2,0,0.41421620478104504,0.47556589803257882,0,7.6792891897609475E-2,8.7515849976218316,9.4404899500958095,8.1289354656378918E-2,8.392015968063872E-2,"Continue to Monitor"]
["TRAFTON AVENUE 12KV","Fayette - 141 Trafton St - Lexington ",79,"Lexington - Red Mile Rd - S of Substation",7.1995451388888885,1247,"2020-01-25",7.2323121697950576E-2,0,0,0,0.15053796152637075,0,0.57160820581464922,8.4775840913469819E-3,0,0.19705312686968249,43.815811350244715,78.783935940085243,0.47093539740821394,0.48783673415058387,"Continue to Monitor"]
["BELT LINE","Fayette - 1090 W. New Circle Rd - Lexington",86,"Lexington - New Circule Rd & New Town Rd. - E of Substation",2.6870773358585858,149,"2021-09-11",0,0,0,0,0.20600231326474705,0,5.9170877214342242E-2,0,0,0.73482680952091073,56.853840414468763,109.56173601342282,0.78264246469138921,1.6004474272930649,"Continue to Monitor"]
["AMERICAN AVENUE","Fayette - 96 Burley Ave. - Lexington",90,"Lexington - Stanley Ave. & Waller Ave. - W of Substation",1.1548865214646464,220,"2019-07-20",0,0,0,0,0,0,0,1,0,0,19.726024934507866,26.303834151501441,0.12219219428230195,6.7893870835047304E-2,"Continue to Monitor"]
["LIBERTY ROAD","Fayette - 2125 Liberty Rd. - Lexington",91,"Lexington - Liberty Rd. & Winchester Rd. - W of Substation",12.555583964646466,1715,"2017-09-30",9.5477521328661986E-3,0,2.2970471206677782E-2,0,1.6403234289891506E-2,1.3556441092479176E-2,0.34037305471607848,0.52793155809924541,0,6.9217488462761392E-2,87.985634972164263,174.08207767920518,0.46563772649696833,1.0934790776593775,"Tree Trim Scheduled for 2022"]
["G E LAMP WORKS","Fayette - 1809 Edision Dr - Lexington",94,"Lexington - Edision Dr. & Bob O Link Dr. - N of Substation",1.6018432765151518,150,"2020-05-09",4.0170636331318878E-2,0,0.9598293636686811,0,0,0,0,0,0,0,40.805771003205301,37.506444440000003,0.2407858719646799,0.34,"Continue to Monitor"]
["LIBERTY ROAD","Fayette - 2125 Liberty Rd. - Lexington ",95,"Lexington - Liberty Rd. - SE  of Substation",18.457621527777775,1684,"2017-09-23",1.9430140748369379E-2,0,0,0,0.18582217645039478,0,2.6433230346721594E-2,0.13827669069687606,0,0.63003776175763815,17.183703204221477,17.29275320297214,0.506962547390718,1.1145904676764467,"Continue to Monitor"]
["STONEWALL","Fayette - 3060 Arrowhead Dr - Lexington",96,"Lexington - New Circle Rd & Southview Dr - NE of Substation",13.025803188131315,1296,"2017-02-16",1.6577153311666846E-2,0,0,0,3.0274169424070747E-2,0,4.9233981691491485E-2,0.71745854075230497,0,0.18645615482046599,159.63951894440271,182.93867829694733,1.1446920040795701,1.1237082091454851,"Tree Trim Scheduled for 2022"]
["STONEWALL","Fayette - 3060 Arrowhead Dr - Lexington",97,"Lexington - W New Circle Rd & Harrodsburg Rd - NW of Substation",22.823009154040413,2132,"2017-09-30",8.5770224584808374E-2,0,0,0,0.282797008571331,0,1.7028832910268524E-2,0.41479322944531083,0,0.1996107044882813,24.389419130049699,28.553757487652444,0.39637588238072913,0.21395148894656107,"Tree Trim Scheduled for 2022"]
["STONEWALL","Fayette - 3060 Arrowhead Dr - Lexington",98,"Lexington - Chelsea Dr & Clays Mill Dr - S of Substation",5.7360303030303026,476,"2021-12-11",1.6666477489850662E-2,0,0,0.11853440937106276,1.0268517572634438E-2,0,0,0.63229323919894964,0,0.22223735636750244,85.229308797655364,203.88331321207917,0.74015401328513375,1.5703451191797475,"Trees Trimmed in 2021"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",101,"Lexington - Shilito Park Rd. & Tiverton Way - SE of Substation",18.068352114898978,1955,"2020-10-24",5.601617936297233E-3,0,0.19805124854920875,0,1.2231820803825224E-3,0,2.0564748726431159E-2,0.77181399292500363,0,2.7452097826766836E-3,14.077350150520541,35.050522075680036,0.22613065681671846,0.7126030281709701,"Continue to Monitor"]
["REYNOLDS","Fayette - 200 W. Reynold Rd. - Lexington",102,"Lexington - Mall Rd - S of Substation",5.3596238952020201,610,"2020-10-24",0,0,0,0,9.4818652849740934E-2,0,0.89170984455958546,0,0,1.3471502590673576E-2,2.3579504790082999,6.2953762639669062,2.1278051855680068E-2,5.2149417956247085E-2,"Continue to Monitor"]
["IBM","Fayette - 740 W New Circle Rd - Lexington ",103,"Lexington - Newtown Rd - S of Substation",10.400622159090902,1158,"2018-03-24",4.4345094248429195E-2,0,5.0507491541807635E-2,0,0.33743354277428705,0,0.10302078298695022,0.428153697438376,0,3.653939101014983E-2,67.712582341957727,25.668349066026408,1.033503890144841,1.1753482144333536,"Continue to Monitor"]
["LANSDOWNE SWITCHING","Fayette - 3200 Montavesta Rd. - Lexington",106,"Lexington - Nicholasville Rd - W of Substation",19.892742582070706,2099,"2021-09-11",3.3854264654851643E-3,5.6127632354601208E-3,6.9955725018500167E-3,9.8040445341929109E-4,7.6054509651444266E-2,1.0911964278995097E-3,2.4421268714436822E-2,0.87115206930142519,0,1.0306789248579563E-2,113.3568679584738,46.118559038775409,1.090963332501929,1.2162930558188443,"Reliability Improvements Scheduled for 2022"]
["STONEWALL","Fayette - 3060 Arrowhead Dr - Lexington",108,"Lexington - Tomahawk Tr & Harrodsburg Rd - W of Substation",4.5711046401515167,363,"2021-10-09",0.50141235410115648,0,0,0,0.16580504183765923,0,0,1.2151574908063742E-2,0,0.32063102915312053,45.078752189072283,50.546059890342434,0.47551859182127698,0.75462515768757987,"Continue to Monitor"]
["LEXINGTON WATER COMPANY 12KV","Fayette - 2300 Richmond Rd - Lexington ",109,"Lexington - Lakeshore Dr. - SE of Substation",14.638197127525249,1002,"2019-03-16",9.6866338593811861E-3,3.447593189660049E-2,7.8454663725323837E-2,0,1.9344985576107247E-2,0,2.5185248034391088E-2,0.45357486283160808,0,0.37927767407658802,64.993265348277376,70.42957857151869,0.56434151687263667,0.51013972626102322,"Continue to Monitor"]
["IBM","Fayette - 740 W New Circle Rd - Lexington ",110,"Lexington - Russell Cave Rd - NE of Substation",22.646350536616147,2003,"2017-12-23",0.36028970600839977,0,6.3941030256278392E-3,0,0.11942230221993658,0,1.6396674380731981E-2,4.5187280363418188E-2,1.094540155995543E-2,0.44136453244193025,32.455024386843853,53.264579195678479,0.64522240699416522,0.33130541800303093,"Continue to Monitor"]
["VILEY ROAD","Fayette - 308 Alexandria Rd. - Lexington ",115,"Lexington - Alexandria Rd & Leestown Rd - NE of Substation",2.0726403093434356,22,"2021-12-11",1,0,0,0,0,0,0,0,0,0,6.9515941971014481,2.0920289565217391,3.4420289855072464E-2,4.3478260869565216E-2,"Continue to Monitor"]
["VILEY ROAD","Fayette - 308 Alexandria Rd. - Lexington ",116,"Lexington - Alexandria Rd. & Old Frankfort Rd. - SW of Substation",24.730887784090882,305,"2021-12-11",2.2086107863569359E-2,0,0,0,6.4860468662634063E-2,0,0,0,0,0.91305342347379659,15.568106308157937,35.560731607886019,0.14381993069263793,0.31489227335331554,"Continue to Monitor"]
["LANSDOWNE SWITCHING"," Fayette - 3200 Montavesta Rd - Lexington",118,"Lexington - New Circle Rd. & Chinoe Rd. - SW of Substation",13.836818181818181,1095,"2020-06-27",1.0907322495484229E-2,0,0,0,2.1131489972673799E-2,0,2.2347274327265989E-2,0.1319878653142513,0,0.81362604789032467,55.1180531474104,74.549332117942328,0.58527544965676681,0.14322584163309826,"Continue to Monitor"]
["LOUDON AVENUE","Fayette - 811 E Loudon Ave - Lexington  ",127,"Lexington - Floyd Dr - N of Substation",10.274690025252525,1304,"2019-01-26",6.0417406231952402E-2,1.2981026507785966E-3,0,0,5.2257903855629791E-2,0,2.6974043245362594E-2,0.28191610548011253,1.9868918124162195E-3,0.57514954672374785,101.42707961963004,119.01873834120649,0.65354985003034516,0.27358501354889025,"Continue to Monitor"]
["LAKESHORE","Fayette - 3710 Richmond Rd - Lexington ",132,"Lexington - Richmond Rd - SE of Substation",60.412756944444453,1115,"2019-01-19",0,6.6399165023773632E-2,2.6997564652673084E-3,3.8487765278905253E-2,5.3772468978313809E-2,0,1.8244230546213616E-2,9.062739185898179E-2,1.8462252116432797E-3,0.7279229966369013,172.92179539430279,186.77035563335812,1.0371473577786072,0.55587588428619372,"Continue to Monitor"]
["LAKESHORE","Fayette - 3710 Richmond Rd - Lexington ",134,"Lexington - Richmond Rd & Yorkshire Blvd - N of Substation",7.4367593118686885,1056,"2018-03-03",2.7979147285461026E-2,0,0,0,0.12190412666093275,0,0,0.85011672605360622,0,0,17.961891735820711,53.9545858340393,0.28940913625284242,0.61941698416990487,"Continue to Monitor"]
["RACE STREET 12KV","Fayette - 420 Corral St - Lexington ",138,"Lexington - Midland Ave & Main St. - W of Substation",2.7734670138888884,51,"Underground Circuit",0,0,0,0,1,0,0,0,0,0,11.2733332,37.966665999999996,0.29199999999999998,1,"Continue to Monitor"]
["IBM","Fayette - 740 W New Circle Rd - Lexington ",140,"Lexington - Newtown Rd - N of Substation",26.09673974116161,969,"2017-12-30",1.2794024157660521E-2,1.5694532739987286E-3,0.27137635092180545,0,3.0594405594405595E-3,0,0.11389462809917354,0.37647012078830261,0,0.22083598219961856,63.301318828024613,51.121633631201099,1.0323199765081088,1.2739916030153213,"Tree Trim Scheduled for 2022"]
["ASHLAND PIPE","Fayette - 448 S Ashland Ave. - Lexington",143,"Lexington - Forest Lake Dr - N of Substation",4.960641887626263,473,"2019-08-17",1.2493802677243432E-2,0,0,0,0,0,0,0,0,0.98750619732275657,19.386317694982644,62.204016911205073,0.13273719570960901,0.42494714587737847,"Continue to Monitor"]
["CLAYS MILL","Fayette - 4454 Clays Mill Rd - Lexington ",145,"Lexington - Glenview Dr - NW of Substation",31.381706597222223,1922,"2018-02-03",2.0118196342428146E-2,0,0.139400331942484,0,3.9709007429927562E-3,0,0.1264638818657029,0.51291318308024003,0,0.19713350602615209,17.761113642556914,32.824476172539001,0.19350748340599955,0.26744797742929421,"Continue to Monitor"]
["CLAYS MILL","Fayette - 4454 Clays Mill Rd - Lexington ",147,"Lexington - clays Mill Rd - N of Substation",15.103109374999995,1498,"2017-05-27",3.9127979943070617E-4,0,0,0,3.2143452682204741E-4,0,0.95816176750227455,3.3019078364201773E-2,0,8.1064398072709289E-3,31.490976034708229,41.718112462902795,0.52558688862958447,0.90312552487280562,"Continue to Monitor"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",149,"Lexington - Man O War Blvd & Liberty Rd - NW of Substation",20.557007575757581,1282,"2016-08-13",0.84761927328302156,8.2208821543236929E-2,0,0,6.9153032331441711E-2,0,1.0188728422998092E-3,0,0,0,20.737774429259765,66.013239043206767,0.29654717657350438,0.44123253985724842,"Continue to Monitor"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",151,"Lexington - I75 - N of Substation",6.5324449179292916,321,"2016-10-22",6.3452281497394278E-2,0,0,0,0,0,0,0,0,0.93654771850260576,37.664759914102206,78.778397186207414,0.27142340588760727,0.59538633573376554,"Continue to Monitor"]
["LAKESHORE","Fayette - 3710 Richmond Rd - Lexington ",152,"Lexington - Richmond Rd - NW of Substation",1.6104138257575755,8,"2018-09-01",0,0,0,0,0,0,0,0,0,1,39.213333325000001,87.8125,0.2,0.5,"Continue to Monitor"]
["LAWRENCEBURG 12KV","Anderson - 108 E Broadway st - Lawrenceburg ",160,"Lawrenceburg - US HWY 127 - S of Substation",25.806673453282826,812,"2022-03-14",0.19839733032050316,0,2.0401252335815634E-2,1.7064152964754196E-2,6.5849220984321175E-3,0,0,0.70668004790153716,0,5.0872294378957801E-2,126.17713456959891,393.60117356518941,1.1304445333443081,2.1970892659220596,"Trees Trimmed in 2022"]
["DANVILLE 1 12KV","Boyle - 494 S 4TH ST - Danville",161,"Danville - 2nd St - S & E of Substation",3.3216515151515158,153,"2020-10-17",0,0,0,0,5.4031296049400039E-3,0,0.11514981404813697,0,0,0.879447056346923,20.091913616787675,92.544108403881594,0.25054236529212054,1.1298734156419168,"Continue to Monitor"]
["DANVILLE 1 12KV","Boyle - 494 S 4TH ST - Danville",162,"Danville - 4th St - S of Substation",13.32955018939394,1279,"2020-10-17",7.489168702274048E-3,0,0,0,0.7157265543524669,0,3.829274950480497E-2,0.23731565796196624,0,1.1758694784878879E-3,37.292306175531813,85.609872476887091,0.43080935780446411,1.1016003799871155,"Continue to Monitor"]
["DANVILLE 1 12KV","Boyle - 494 S 4TH ST - Danville",163,"Danville - Russel St - W of Substation",2.4707687815656563,108,"2020-10-17",0,0,0,0,0.80867932401418741,0,0.19132067598581265,0,0,0,41.850720972188398,89.544984128697607,0.44103721007734509,1.1585355397410613,"Continue to Monitor"]
["DANVILLE 1 12KV","Boyle - 494 S 4TH ST - Danville",164,"Danville - 4th St - N of Substation",1.755855271464646,223,"2020-10-17",0,0,0,0,0,0,0.68621973929236502,0,0,0.31378026070763498,7.8442393003653219,19.222560653747593,0.10881137784164689,9.3990230621396526E-2,"Continue to Monitor"]
["DANVILLE WEST","Boyle - 1353 Lebanon Rd - Danville ",167,"Danville - Lebanaon Rd - SW of Substation",6.5482481060606039,23,"2021-07-31",0,0,0,0,0,0,0.16642754662840745,0.83357245337159258,0,0,20.578405794202897,30.339130434782607,0.22391304347826085,0.34782608695652173,"Trees Trimmed in 2021"]
["DANVILLE WEST","Boyle - 1353 Lebanon Rd - Danville ",168,"Danville - S Danville Bypass - S of Substation",2.2004291351010106,19,"2021-07-31",1.6871165644171779E-2,0,0,0,5.2147239263803678E-2,0,0.93098159509202449,0,0,0,28.709481471111111,97.77333329999999,0.11333333333333333,0.4,"Continue to Monitor"]
["DANVILLE WEST","Boyle - 1353 Lebanon Rd - Danville ",169,"Danville - Danville Bypass - N of Substation",1.2551620896464646,6,"2021-07-31",1,0,0,0,0,0,0,0,0,0,2.0249999999999999,10.125,3.3333333333333333E-2,0.16666666666666666,"Continue to Monitor"]
["EASTLAND","Fayette - 1159 Industry Rd - Lexington",182,"Lexington - Eastland Pky - E of Substation",17.666857954545456,2369,"2019-06-22",1.0802526061071068E-2,0,1.1601142039292644E-2,0,1.5496469859163241E-2,0,1.0011287597659853E-2,0.12179723638295203,0.79312341844526257,3.716791961459863E-2,117.85575590643563,228.16961758654071,0.97890006541363284,1.9609641910247757,"Reliability Improvements Completed in 2021"]
["ASHLAND AVENUE","Fayette - 448 S Ashland Ave. - Lexington",187,"Lexington - High St. - NW of Substation",3.8065508207070713,1004,"2019-12-21",0,0,0,0,8.4019769357495888E-2,0,0.61603514552443717,0,0,0.299945085118067,15.081013735042868,9.0723724674874173,0.12914111541921489,0.13157641404541009,"Continue to Monitor"]
["LAKESHORE","Fayette - 3710 Richmond Rd - Lexington ",195,"Lexington - Hays Blvd & Chilesburg Rd - E of Substation",12.904033617424238,958,"2019-01-19",6.8947853703513987E-2,2.4587644708533963E-2,0,0,0,0,0.89294129699825842,0,0,1.352320458969368E-2,2.5145290832367517,9.9043620691768925,6.5513035013725129E-2,0.30153574673990008,"Continue to Monitor"]
["STONEWALL","Fayette - 3060 Arrowhead Dr - Lexington",198,"Lexington - Clays Mill Rd and Pasadena Dr - E of Substation",9.5257957702020164,904,"2017-02-25",0.15701173272017108,0,0,0,4.4290737779508746E-2,0,1.2095973875692336E-2,0.4259805041362239,0,0.36062105148840395,68.338581742032432,126.7941029701328,0.40021150915160314,0.70426350091794043,"Tree Trim Scheduled for 2022"]
["STONEWALL","Fayette - 3060 Arrowhead Dr - Lexington",199,"Lexington - Harrodsburg Rd and Man O War Blvd - W of Substation",16.338630208333335,1140,"2021-10-09",1.4511249763660427E-2,1.9852524106636414E-3,1.8930799773114012E-2,0,0.11756948383437323,0,6.045566269616184E-3,0,0,0.84095764794857253,98.260248725314256,185.69407565368903,0.69941372224423959,1.2673887603015426,"Continue to Monitor"]
["LONDON","Laurel - Near corner of Foster Heights & Substation Rd - London",201,"London - Waterworks Rd & Daniel Boone PKWY - W & SW of Substation",25.055413983585851,586,"2019-11-09",8.216082982438122E-5,0,0,0,0.34577972094661014,0,5.449023606566997E-3,0.63556977068325538,0,1.311932393374316E-2,86.069081968427142,147.99885690530292,0.89119600692313428,1.5837908456781593,"Continue to Monitor"]
["FARISTON","Laurel - 57 Rocky Branch Rd - North Corbin ",216,"North Corbin - S Laurel Rd - S of Substation",3.2127228535353538,92,"2019-03-26",0,0,0,0,0.24377693176588713,0,0,0.2237794419110572,0,0.53244362632305564,57.460843287898264,63.397132602150535,0.34415008856473156,0.15053763440860213,"Continue to Monitor"]
["FARISTON","Laurel - 57 Rocky Branch Rd - North Corbin ",217,"North Corbin - S Laurel Rd - N of Substation",29.245262626262623,863,"2019-03-26",8.5639139545823882E-3,0,4.051019971774366E-2,0,1.9244750459735706E-3,0,2.5338921438652013E-3,0.67789633494419022,0.22540948552367104,4.3161698669973915E-2,88.595496910246197,108.27386801850973,0.93169895647731438,0.49743164178764104,"Continue to Monitor"]
["LEBANON WEST","Marion - 2255 Saint Mary's Rd - St Mary ",219,"St Mary - Sait Mary's Rd - W of Substation",40.987928661616159,817,"2020-05-16",3.7115780799340747E-2,0,4.2538112896580139E-2,1.2855377008652658E-3,4.944375772558714E-3,0,1.8903996703749485E-2,0.52875154511742894,0,0.36646065100947672,27.312396438148141,36.027765173743241,0.24905677988108091,0.30232820148410899,"Continue to Monitor"]
["EAST BERNSTADT","Laurel - 440 State HWY 490 - East Bernstadt ",221,"East Bernstadt - US HWY 25 - N & S of Substation",28.644057922979801,783,"2019-05-11",2.1171010958115273E-3,0,0,1.6259336415832529E-3,4.5729383669528986E-2,0,1.3075216367731991E-2,0.9139948850837526,4.6689136166296876E-3,1.8788566524962032E-2,57.383984292362641,80.828953272163332,0.48640231451110399,0.34706705071818345,"Continue to Monitor"]
["EAST BERNSTADT","Laurel - 440 State HWY 490 - East Bernstadt ",222,"East Bernstadt - KY HWY 490 - N of Substation",11.202138573232324,331,"2019-05-04",1.7875209797738757E-3,0,0,0.19633233731641775,0.20947917066105828,0,4.3213172200804086E-3,0.58596471563372932,0,2.1149381889403775E-3,128.57266618925297,322.55953899037382,0.9622726172032543,1.2713575527592926,"Continue to Monitor"]
["WILLIAMSBURG SOUTH"," Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg ",225,"Williamsburg - I75 - NW of Substation",15.481185606060599,622,"2018-11-03",1.2421161024584888E-2,0,1.415883640108122E-3,0,9.3371090230402881E-2,0,4.4021109537907069E-3,0.85787102587205555,0,3.0518728279057793E-2,115.77751635569709,122.83292650068829,0.67993050769826235,0.32766222304627862,"Continue to Monitor"]
["WILLIAMSBURG SOUTH"," Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg ",226,"Williamsburg - Highway 25 - N of Substation ",29.893543244949495,1226,"2019-01-22",1.6420547993141337E-2,0,0.35441088987647407,0,0.56931273401686666,0,1.9876124155789623E-2,1.4110998355320712E-2,0,2.5868705602407529E-2,107.0248535784942,94.746083262822737,0.89692733724637308,1.4396687411443845,"Continue to Monitor"]
["WILLIAMSBURG SOUTH"," Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg ",227,"Williamsburg - Savoy Clear Creek Rd - N of Substation",10.566237058080809,138,"2018-12-31",0,0,0.39356725146198829,0,0.12003559623696924,0,1.1390795830155098E-2,0.37869310958555807,0,9.6313246885329259E-2,159.22533146657469,226.63179025436483,1.0509373003517426,2.0434643664776448,"Continue to Monitor"]
["WILLIAMSBURG SOUTH"," Whitley - Corner of Savoy Clear Creek Rd and Railroad Tracks East of I75 - Williamsburg ",230,"Williamsburg - Highway 92 - N of Substation",23.848915404040405,659,"2018-12-29",0.13168048698653118,0,0.3134136988927767,0,0.23534486890667689,0,1.6596366773714233E-2,0.24272635766668263,0,6.0238220773618366E-2,187.43696545458516,125.23496551034644,0.54791160549461515,1.3146270164413409,"Continue to Monitor"]
["CAMPBELLSVILLE 1","Taylor - 101 Old Greensburg Rd. - Campbellsville",233,"Campbellsville - Central Ave - E of Substation",9.2368901515151514,885,"2019-08-10",0,0,1.9155085475341286E-2,0,0.83470667814536958,0,5.4605829541261836E-2,1.8909113270200468E-2,0,7.2623293567826833E-2,53.189475013091077,35.61401676279187,0.70425788445669235,1.0011342858723316,"Continue to Monitor"]
["WILLIAMSBURG","Whitley -  Corner of 2nd and 3rd St - Williamsburg ",236,"Williamsburg - 2nd St - N of Substation",2.1965175189393933,212,"2018-07-14",0,0,0.99665616483367803,0,0,0,3.3438351663219747E-3,0,0,0,50.219518743607772,219.87083299056602,0.75538482815094921,2.3867924528301887,"Continue to Monitor"]
["CORBIN EAST","Knox - Corner of State HWY 1232 and E Barbourville Rd - Corbin ",277,"Corbin - State HWY 1232 & Hancock - NW of Substation",14.588193181818182,738,"2017-04-07",5.8357869496993954E-3,0,0.25142368518485869,0,2.6499056753468857E-2,0,5.0335866288192671E-3,0.51370792856009451,0.18546695110985736,1.2033004813201926E-2,71.975453670021125,100.05181155575784,0.68333278592268676,1.112442457233527,"Tree Trim Scheduled for 2022"]
["CORBIN EAST","Knox - Corner of State HWY 1232 and E Barbourville Rd - Corbin ",278,"Corbin - Commonwealth Ave - N of Substation",17.67452225378787,755,"2017-02-03",3.5144973013681437E-3,0,7.4511907071214212E-3,5.4771386514828214E-4,5.7601241484761E-2,0,5.4200851238632086E-3,0.7651391535538643,0.13991236578157629,2.0413752182297431E-2,85.498017536275185,56.664437507669504,1.0542924664224247,1.3559095638245318,"Tree Trim Scheduled for 2022"]
["HOPEWELL","Laurel - Corner of American Greeting Rd and Hopewell Church Rd - North Corbin",286,"North Corbin - Robinson Creek Rd & US HWY 25 - NW of Substation",73.511800662878755,2026,"2022-01-08",6.6617360682322451E-3,0,2.4033274754205144E-3,6.8313667483155677E-3,8.1829840072194821E-4,1.0351542621404678E-2,2.6850501089028967E-2,0.92961005299262445,5.3196181274129967E-4,1.5941212791510322E-2,68.874985395952621,93.240945453538416,0.86576801860950281,0.53702595358285321,"Trees Trimmed in 2022"]
["HOPEWELL","Laurel - Corner of American Greeting Rd and Hopewell Church Rd - North Corbin",287,"North Corbin - National Cash Regist Rd - W of Substation",15.638772727272732,290,"2021-10-02",3.0511417312782453E-3,0,0,0,5.6341864047592706E-3,0,3.4596627999012742E-3,0.98566346374801062,0,2.1915453160506228E-3,23.222143089812583,78.258348344418323,0.18951949749144115,0.54121415195801659,"Trees Trimmed in 2021"]
["CORBIN US STEEL","Whitley  - S Woodbine Ave off HWY 830 - Corbin",288,"Corbin - 0.15 miles E of Substation",20.136767834595954,397,"2015-09-25",8.3745143158927161E-3,0.55656569466973482,0,1.1807310724659549E-2,0.15572069863065374,0,6.0847259421328605E-2,0.12822060432306009,0,7.8463917914670486E-2,40.384826857759187,62.861981789288301,0.34182581197680884,0.47736985990912123,"Continue to Monitor"]
["CORBIN US STEEL","Whitley  - S Woodbine Ave off HWY 830 - Corbin",289,"Corbin - S Main St - S of Substation",0.79373200757575757,5,"2021-12-04",0,0,0,0,1,0,0,0,0,0,7.9306666400000001,31.653333199999999,0.27999999999999997,0.4,"Continue to Monitor"]
["HUME ROAD","Fayette - 2319 Hume Rd. - Lexington",295,"Lexington - Winchester Rd - E of Substation",11.112757417929291,83,"2021-04-24",0,0,0,0,7.8967110198602287E-3,0,1.1292296758400128E-2,0.50305997552019577,0.44355825798554904,3.4192758715994788E-2,140.35164908076786,301.50753964285718,0.47457384684898613,1.1547619047619047,"Trees Trimmed in 2021"]
["PINEVILLE","Bell - Corner of E Park Ave and Maple St - Pineville  ",300,"Pineville - Park Ave - W of Substation",9.1086867108585867,321,"2019-06-27",0.13297655222459068,0,4.163454124903624E-2,0,0.13247766338609462,0,1.587373577032972E-3,0.67694680030840404,0,1.4377069254841489E-2,60.2108440741805,68.492680234689743,1.0770413989636904,0.6647800932644492,"Continue to Monitor"]
["CROCKETT","Bell - On HWY 66 across the street from Chaz Coal Co - Pineville ",304,"Pineville - State HWY 66 - NW of Substation",17.271629892676764,102,"2019-04-06",0,0,6.0626501960453641E-3,0,0,0,0,0.91513554534339558,0,7.8801804460559052E-2,1019.7333818539379,2179.6416677356747,3.4091643435821792,4.8734018656006084,"Continue to Monitor"]
["MELDRUM","Bell - HWY 25/Wilderness Rd S of HWY 2486 Middlesborough",308,"Middlesborough - US HWY 25E - N of Substation",50.737099116161602,831,"2022-03-07",6.9072176746299934E-4,0,4.3699391347422423E-3,1.8473741946347676E-4,0.19221683268511752,0,1.7958765954037984E-3,0.76028194526867854,0,4.0459947129131459E-2,782.84936114179709,1268.5572370103405,3.9638543570823712,4.902452547582719,"Reliability Improvements Scheduled for 2022"]
["GREASY CREEK 12KV"," Bell - US HWY 25 at HWY 3085 - Pineville US HWY 25 AT HWY 3085 PINEVILLE ",309,"Pineville - State HWY 92 - S of Substation",21.147786931818185,328,"2020-11-21",3.8598049202355353E-4,0,1.4162291737405573E-3,8.4161159914910167E-5,2.3562222667212265E-2,0,1.2754768890552765E-2,0.53905222925499963,2.5344117570238293E-2,0.39740029079131806,325.41417013700675,534.97582648777961,1.8959445303627298,1.9288281947255632,"Reliability Improvements Completed in 2021"]
["GREASY CREEK 12KV"," Bell - US HWY 25 at HWY 3085 - Pineville US HWY 25 AT HWY 3085 PINEVILLE ",310,"Pineville - Mocking Bird - E of Substation",7.508377525252528,162,"2020-08-29",0,0,0,0,0.47619776519210166,0,0.11120465329863768,0.41259758150926068,0,0,134.59540996553969,78.214850485347014,1.6830083741653172,1.7368018855059126,"Continue to Monitor"]
["CALLOWAY","Bell - Hwy 119 - Calloway",311,"Calloway - US HWY 119 - S of Substation",66.983049400252511,914,"2019-09-28",8.3600909882168804E-3,0,0,0,0.15372181303530549,0,0.10061365847236342,0.7326843230618072,0,4.6201144423070831E-3,552.5098784175608,448.23590323816217,3.8097972212146742,3.9988965226904756,"Continue to Monitor"]
["CALLOWAY","Bell - Hwy 119 - Calloway",312,"Calloway - US HWY 119 - NW of Substation",22.852553030303039,334,"2019-06-27",6.6472704436969514E-4,0,2.231345053462092E-3,0,6.9732873257596764E-2,0,4.9376860150114742E-2,0.48406158245120601,0.18214523116801559,0.21178738087523508,458.21668612023097,818.82676150985992,2.0142149409821619,3.5477543310106592,"Continue to Monitor"]
["STINKING CREEK","Knox -  Croner of New US HWY 25 E and HWY 930 - Barbourville ",313,"Barbourville - US HWY 25E - S of Substation",36.568407986111104,836,"2020-08-15",4.4941352194350481E-3,0,0,3.2491323639239116E-2,4.4572332293634408E-2,0,1.8692615208891622E-2,0.8181654439221544,0,8.1584149716645432E-2,160.51044197300672,264.4669808280218,1.6997500274446444,1.8386051779591424,"Continue to Monitor"]
["STINKING CREEK","Knox -  Croner of New US HWY 25 E and HWY 930 - Barbourville ",314,"Barbourville - US HWY 25E & Stinking Creek Rd - NW of Substation",27.187780460858583,393,"2020-08-22",1.8147989497055447E-3,0,0,0,0.11393340505331585,0,6.5725151151498106E-4,0.82681586166981125,2.632275954077412E-3,5.4146406861574986E-2,300.65536584657696,777.23958437101146,2.1408979210494143,4.2197544457153047,"Continue to Monitor"]
["MILL CREEK - KU"," Bell - 5539 HWY 221 Kettle Island - Pineville ",315,"Pineville - Martha Lock Branch Rd - SW of Substation",14.244624999999997,344,"2017-04-07",1.8190592864832757E-3,0,0,9.8006459516649953E-4,2.1910383487396518E-2,0,3.9395626832980653E-2,0.47473735011322715,0,0.46115751568474589,189.53550585251696,366.21019355849324,1.2574427173030318,1.5832829640416297,"Tree Trim Scheduled for 2022"]
["STRAIGHT CREEK","Bell - 3582 HWY 66 Arjay - Pineville",317,"Pineville - State HWY 66 - NE of Substation",8.1139572285353534,221,"2018-01-16",3.9216658403569658E-2,0,0,0,7.615270203272187E-2,0,2.4293505205751115E-3,0.85870104115022317,0,2.3500247892910262E-2,46.863816528787183,91.19848610711594,0.4579968769850053,0.51560499150893102,"Continue to Monitor"]
["PUCKETT CREEK"," Harlan - 5627 E HWY 72 Pathfork - Alva",321,"Alva - E Highway 72 - SE of Substation",3.403393939393939,63,"2018-01-02",0,0,0,0,6.298579469311176E-2,0,0,0.85339051192709725,0,8.3623693379790948E-2,212.72716980277909,117.08237565120967,1.0331954888902832,1.034274193548387,"Continue to Monitor"]
["BRUSH CREEK","Knox - HWY 225 Kay Jay Road - Barbourville",323,"Trosper - State HWY 225 - N of Substation",3.0173617424242423,30,"2020-05-09",0,0,0,0,0,0,0,1,0,0,215.82923808934524,118.63333333333334,0.82964285714285713,1,"Continue to Monitor"]
["BRUSH CREEK","Knox - HWY 225 Kay Jay Road - Barbourville",324,"Trosper - State HWY 225 - N of Substation",1.054303188131313,36,"2020-05-02",0,0,0,0,0,0,0,1,0,0,219.50029910608501,118.58333332432431,0.70642484589853005,1,"Continue to Monitor"]
["WACO","Madison - 3761 New Irvine Rd - Madison East ",330,"Madison East - College Hill Rd - N of Substation",7.4918102904040413,177,"2018-11-10",0,0,0,0.72199815256856992,1.1029714379784346E-2,0,6.4660100053959627E-3,0,0.26050612304624982,0,119.45897033835558,573.93940859760221,0.44294479272293386,2.0477316221997075,"Continue to Monitor"]
["DARK HOLLOW","Estill - 37 Dark Hollow Rd - Red Lick",336,"Red Lick - Wisemantown Rd - S of Substation",11.981747948232323,537,"2018-10-27",1.7338492432776608E-3,0,3.7076945682519472E-2,0,2.4489396091492382E-3,0,4.9958368026644458E-4,0.95663417740118528,0,1.6065043836019004E-3,96.325475220616141,190.81692680086542,0.51606478625165553,0.5663923033307795,"Continue to Monitor"]
["RICHMOND INDUSTRIAL","Madison - 110 Mikron Way - Richmond",343,"Richmond - Pavilion Way - NW of Substation",8.8069559659090917,479,"2019-09-07",0,0,0,0,1,0,0,0,0,0,13.941359033338093,69.221487603305775,0.16688597194885915,0.8223140495867769,"Continue to Monitor"]
["RICHMOND INDUSTRIAL","Madison - 110 Mikron Way - Richmond",344,"Richmond - 1.51 miles S of Substation",5.0354987373737377,5,"2019-09-07",0,0,0,0,0,0,0,0,0,1,19.489999919999999,8.9633331999999992,0.16,0.2,"Continue to Monitor"]
["MIDDLESBORO 2 4KV","Bell - Intersection of Cumberland Ace and S 38th St - Middlesborough",350,"Middlesborough - Dorchester Ave - E of Substation",5.5971726641414143,447,"2019-03-02",0,0,0,0,0.77842777527778739,0,0.16706474205868441,2.5153749408656119E-3,0,5.1992107722662606E-2,74.489918572594817,194.19790010382076,0.63865499524694358,1.7315393695173318,"Continue to Monitor"]
["MIDDLESBORO 2 4KV","Bell - Intersection of Cumberland Ace and S 38th St - Middlesborough",351,"Middlesborough - Dorchester Ave - E of Substation",7.8351987058080805,658,"2019-03-02",9.4169669177857837E-3,0,0.10319767441860465,3.0502784146740911E-3,0.21953815918768424,0,0.36621765476580415,9.601211922698985E-3,0,0.28897805437274809,31.683987982134351,74.113077738015079,0.68953150160757803,1.0026287670670861,"Continue to Monitor"]
["MIDDLESBORO 2 12KV","Bell - Intersection of Cumberland Ace and S 38th St - Middlesborough",360,"Middlesborough - State HWY 74 - E of Substation",30.457989425505037,397,"2021-12-14",9.5258034125405636E-3,0,0,0,0.29903844715945627,0,4.0226705148719177E-2,0.63350331234765445,0,1.7705731931629557E-2,251.88232572879116,148.84095831839159,1.0914897579916472,1.1025784148230531,"Trees Trimmed in 2021"]
["MIDDLESBORO 1 12KV","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",365,"Middlesborough - N 12th St - NE of Substation",15.774714962121211,478,"2021-12-31",6.6533836191560525E-3,0,0,0,0.30203515263644776,0,9.7488080836831987E-3,0.53828364050380706,0,0.143279015156906,33.958782304967002,56.121256366082321,0.3191430640059113,0.34143478297467428,"Trees Trimmed in 2021"]
["MIDDLESBORO 1 12KV","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",366,"Middlesborough - Asbury Rd & N 12th St - E of Substation",10.838175820707072,444,"2021-12-18",1.004079071226859E-2,0,0.35520661382518653,0,0.19284866509324566,7.2850302178687877E-3,2.1132044583293541E-2,0.12312246763345658,0,0.29036438793468028,132.99340568299567,164.4646379746188,1.1453830412229435,1.9833691338016932,"Continue to Monitor"]
["MIDDLESBORO 1 12KV","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",367,"Middlesborough - N 19th St - N & S of Substation",10.671621212121213,530,"2021-12-31",2.5848142164781908E-3,0,0,0,8.8637587506731286E-2,0,2.994076467420571E-2,0.78714054927302102,0,9.169628432956381E-2,89.800976024945541,262.42338581581015,0.78758956553185244,1.816257189601554,"Trees Trimmed in 2021"]
["MIDDLESBORO 1 4KV","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",370,"Middlesborough - N 19th St - SW of Substation",4.7707050189393945,658,"2021-12-18",0.52981815294211065,0,2.5569760978321289E-2,0,0.342253632970698,0,4.5660287461288016E-2,0,0,5.669816564758199E-2,37.199627009650158,37.126642071566742,0.45763028277363721,0.56477425989521057,"Continue to Monitor"]
["MIDDLESBORO 1 4KV","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",371,"Middlesborough - N 19th St - S of Substation",1.3552116477272727,1296,"2021-12-18",3.0843166086862964E-4,0,8.6791234802567868E-4,0,3.7729082236488184E-3,0,8.4424201126134212E-3,0.77372592619158631,0,0.21288240146325718,46.375804196737718,193.59179721818512,0.4507451550119761,1.8638668284118185,"Trees Trimmed in 2021"]
["MIDDLESBORO 1 4KV","Bell - Corner of N 19th and Ironwood Rd - Middlesborough",372,"Middlesborough - Lynnwood Dr - E of Substation",8.6821852904040391,492,"2018-02-23",1.3917248790972595E-2,0,0,0,0.62106394411606658,0,6.6684578183772159E-2,0.13734551316496507,0,0.16098871574422355,27.254985279909967,36.294738276471492,0.22104895176083059,0.37210098210766562,"Continue to Monitor"]
["MELDRUM","Bell - HWY 25/Wilderness Rd S of HWY 2486 Middlesborough",390,"Middlesborough - S of Substation on US HWY 25E and E of Substation Colmar Rd",13.764785037878788,320,"2016-06-24",1.7551228586001021E-3,0,0.63239176742371961,1.5826107827547928E-3,0.21564009480663646,0,1.7348714410008702E-2,0.13128168971828028,0,0,175.52177012642332,386.04886540739966,1.5693524694632701,3.2531986189982307,"Continue to Monitor"]
["DELAPLAIN","Scott Ky -  413 Triport Cir - Sadieville ",401,"Sadieville - I75 - N of Substation",10.558016887626259,104,"2019-09-28",1.0059289854106989E-3,0,0.82471520884684568,0,6.7950169875424684E-4,0,0.17359936046898941,0,0,0,158.86148538128737,474.47021968710129,0.74163952759315221,1.7144706426259824,"Continue to Monitor"]
["DELAPLAIN","Scott Ky -  413 Triport Cir - Sadieville ",403,"Sadieville - 0.41 Miles N of Substation",0.12189741161616162,1,"2019-09-28",0,0,0,0,1,0,0,0,0,0,198.28000000000003,751.85,0.6,1,"Continue to Monitor"]
["FORKS OF ELKHORN","Franklin - 3286 Georgetown Rd - Frankfort ",407,"Frankfort - Old Grand Dad Rd - N of Substation",3.7035984848484853E-2,3,"2017-12-23",0,0,0,0,0,0,0,0.41323345817727841,0,0.58676654182272159,85.143333333333331,267,0.73333333333333328,2,"Tree Trim Scheduled for 2022"]
["HOOVER 1","Scott Ky - 3 Quality Dr - Georgetown",411,"Georgetown - Pocaontas Trl - E of Substation",20.099980271464652,1640,"2019-01-12",0.3888373797322881,1.3324524342240409E-3,0,0,8.2501013219038518E-3,0,3.1568018920824566E-2,0,0,0.57001204759075941,56.828479071413632,109.85251784412362,1.0701800910870982,1.2701383863563604,"Continue to Monitor"]
["DAYHOIT","Harlan - Dayhoit Dr (Keith Tremont Rd) - Harlan",415,"Harlan - S US HWY 119 - S of Substation",14.402193970959605,392,"2019-11-09",0.12911267784552846,0,0,0,0.24903137703252035,0,0.43308561991869921,0.18684895833333334,0,1.9213668699186992E-3,216.38135946904481,160.47658851297632,1.8860545691575392,2.244155230013666,"Continue to Monitor"]
["GEORGETOWN 4KV","Scott Ky - 207 W Clinton St - Georgetown ",421,"Georgetown - Water St - N of Substation",2.7900680239898992,317,"2018-10-20",0,0.19533221194280909,0,0,0,0,2.0605550883095038E-2,6.0765349032800675E-2,0,0.72329688814129522,14.26925607724235,14.988837574987102,0.12248597286849025,8.5234712908217936E-2,"Continue to Monitor"]
["KENTENIA"," Harlan - Near HWY 219 on Meadow Creek Ln (Wilson Ln) - Wallins Creek ",423,"Wallins Creek - E on Wilson Ln & S on HWY 219",9.2241262626262639,211,"2019-10-19",0,0,0,0.12654810370687808,7.1471085398661996E-2,0,3.6597385901007071E-2,0.76194557531604878,0,3.4378496774039951E-3,523.64427998187523,995.84873047341091,2.1868490532622946,2.8520330603850228,"Continue to Monitor"]
["GEORGETOWN 12KV","Scott Ky - 207 W Clinton St - Georgetown ",427,"Georgetown - S Broadway St - S of Substation",7.8243136047979807,752,"2019-04-13",1.9753618503753189E-2,0,0,0,4.9096720899328379E-2,0,1.2821894192436159E-2,0.86617821355457392,0,5.2149552849908416E-2,20.472674032928772,36.999146003145064,0.26117197432940981,0.57802530963865817,"Continue to Monitor"]
["NEWTOWN","Scott Ky - 5849 Paris Pike - Georgetown ",430,"Georgetown - US 460 Pike - E of Substation",68.632303977272713,805,"2021-01-16",1.1895072935578789E-2,6.1040505853627994E-4,4.6484692919301317E-3,0,0.69806861578914414,7.9571777374319169E-2,2.4275339635635135E-2,4.8018531271520691E-2,6.3231703499655673E-3,0.12658861829337006,34.227818508126873,50.731470262335343,0.25769837072231816,0.41011619052944331,"Continue to Monitor"]
["TURTLE CREEK","Harlan - HWY 990 - Cawood",432,"Cawood - HWY 990 - SW of Substation",3.4946287878787881,88,"2019-07-06",0,0,0,0,0.23257806789827859,0,7.1325957103611668E-3,0.75567709252211612,0,4.6122438692441465E-3,283.3650016575977,445.91930963968343,1.7194828070406942,2.1238508682328905,"Continue to Monitor"]
["ROGERS GAP","Scott Ky - 192 Harbor Village Dr - Stamping Ground ",450,"Stamping Ground - Cincinnati Rd - S of Substation",12.107714962121209,542,"2019-11-02",6.0809953027802462E-2,0,7.1093055731877618E-3,0,0.37653929160848038,1.0875544835174136E-2,6.4660826879945829E-2,0.12957555753036265,0,0.35042952054504678,32.535874658878349,37.912174891868091,0.26904452658414568,0.28548191924376959,"Continue to Monitor"]
["ADAMS 12KV","Scott - 900 W Main St - Georgetown",452,"Georgetown - Paynes Depot Rd - SW of Substation",43.535734848484864,1577,"2019-01-26",0.20234278668310726,2.3510069872585287E-2,6.1405672009864368E-2,0,0.10168516235100698,0,0.10756267981915331,0.25861076859843812,0,0.24488286066584464,14.024795671254395,11.253830612096056,0.10064387349176269,0.12046958303506028,"Continue to Monitor"]
["ADAMS 12KV","Scott - 900 W Main St - Georgetown",453,"Georgetown Rd - Frankfort Rd - E of Substation",43.196430397727269,1581,"2019-04-20",7.3130167633719137E-3,7.5772202406961427E-3,0.71795262628418133,0,8.3332486527316271E-2,0,7.4857651908531405E-4,3.6819125621979018E-3,0,0.17939416110315112,65.758274989465264,144.36862689621159,0.8972702886169277,0.33537674468460921,"Continue to Monitor"]
["CLOVERLICK","Harlan - HWY 179 1/4 miles W from intersection of HWY 2006 and HWY 179 - Cumberland ",458,"Cumberland - State Hwy 2006 - S of Substation",8.7927594696969678,146,"2021-07-10",0,0,0.11673735010236912,0,0.2797784439894706,0,2.0199619771863117E-2,0.58328458613629719,0,0,210.91212021444252,373.45811204400553,1.2629307273506032,2.2596128418046226,"Trees Trimmed in 2021"]
["CLOVERLICK","Harlan - HWY 179 1/4 miles W from intersection of HWY 2006 and HWY 179 - Cumberland ",459,"Cumberland - State Hwy 2006 - N of Substation",7.2033112373737378,449,"2021-07-17",0,0,0,0,0.31001197246333434,0,0.68998802753666566,0,0,0,20.777211053302306,33.355213322287455,0.17680616278243683,0.29888272085279483,"Continue to Monitor"]
["PEPPER PIKE","Scott Ky - 4341 Frankfort Rd - Georgetown ",461,"Georgetown - E on US HWY 460 & S on Fishers Mill Rd ",50.540037089646447,537,"2017-09-02",4.4114663343091505E-2,2.666589374221037E-3,0.21952986869945798,0,6.8693661053302801E-3,0,2.8694820439987244E-2,0.22909480884612041,0,0.46902988319179156,61.824108852382736,63.980735981590392,0.63085551137981022,0.34952964792490543,"Continue to Monitor"]
["OXFORD","Scott Ky - 1827 Oxford Dr - Georgetown ",472,"Georgetown - Oxford Rd - S of Substation",17.508642518939393,1108,"2019-08-31",1.146366335268062E-3,0,0,1.4787447401682695E-3,9.0036109409022159E-3,0,0,0.81120680493909791,3.0965457517743808E-2,0.14619901552681977,30.880941856590731,75.359194013943863,0.23068920423538769,0.35828514586500837,"Continue to Monitor"]
["SHADRACK","Franklin - 74 Bethel Ln - Frankfort ",475,"Frankfort  - US HWY 127 - N of Substation",47.458059974747457,579,"2018-03-09",2.3657326328079393E-2,0,4.1301809690601288E-3,0,1.0624635143023935E-2,0,8.2457676590776408E-3,0.69826328079392885,0,0.25507880910683012,83.678816289340361,118.06081547538778,0.54827747115014547,0.4346181961290887,"Continue to Monitor"]
["SHADRACK","Franklin - 74 Bethel Ln - Frankfort ",476,"Frankfort - S on US HWY 127 & N on Peaks Mill Rd",55.748420296717157,687,"2018-09-29",7.9144039211939948E-3,0,2.522762178408448E-2,0,3.7609952895701827E-2,0,4.8206582844041411E-3,0.89580470455096595,0,2.8622658563649591E-2,108.50101790763335,158.68447785134489,0.66112001625149674,1.0972864474562929,"Continue to Monitor"]
["STAMPING GROUND","Scott Ky - 3540 Main St - Stamping Ground ",481,"Stamping Ground - SE on Main St & N on Locust Fork Rd ",101.09057717803029,1285,"2017-12-16",1.4782487395627828E-2,1.4387915745003089E-3,8.8121001972858246E-3,6.3809011378808712E-3,3.1159203682668737E-2,0,6.7077180606205534E-3,0.76534943504513664,0.12295490325023416,4.2414459656045116E-2,117.64144078352373,193.47165228805218,0.72765585177427217,1.1572858451417636,"Tree Trim Scheduled for 2022"]
["ROBBINS","Harlan - E of 15537 HwY 38 - Upper Clover ",488,"Upper Clover - Highway 38 - SW of Substation",2.2680178345959603,33,"2017-07-28",0,0,0,0,0.98545169798878995,0,1.4548302011210023E-2,0,0,0,234.07953285632442,500.40606060606058,2.1959353762954334,4.6363636363636367,"Continue to Monitor"]
["HOLMES MILL"," Harlan - 1/4 mile E of 25511 HWY 38 - Upper Clover ",491,"Upper Clover - Highway 38 - W of Substation",8.9249376578282824,194,"2017-11-09",0,0,0,0,3.5947944815815674E-2,0,0.93077087185322149,3.3281183330962881E-2,0,0,143.63459698625888,144.55930489837101,1.2170177327189822,1.2229648351844016,"Continue to Monitor"]
["ALEXANDER","Woodford - 2915 Troy Pike - Versailles",500,"Woodford South - Troy Pike - S of Substation",93.26271780303037,948,"2022-03-26",4.607779385955712E-3,7.0899670673127344E-3,6.4292156986134705E-2,0,3.0093903607213028E-2,0,1.1453023724120572E-2,0.30788916157992996,0.42820883938497684,0.14636516826435647,104.00909078614204,142.36602588962393,0.64520461675177443,1.0796789965179916,"Trees Trimmed in 2022"]
["ALEXANDER","Woodford - 2915 Troy Pike - Versailles",501,"Woodford South - Troy Pike - N of Substation",50.898925662878838,1899,"2020-03-21",1.2546675583793123E-2,0,2.5427743409686229E-3,0,9.3845789444351554E-2,0,2.8883129911386057E-2,0.29269074290809788,1.6301621802374184E-3,0.56786072563116541,48.612883537901816,75.894907358221346,0.4275215709488574,1.0175411991221279,"Continue to Monitor"]
["MIDWAY 12KV","Woodford - 860 Weisenburger Rd - Midway ",504,"Midway - Weisenberger Mill Rd - E of Substation",63.547364898989898,552,"2017-03-17",3.0811643765486455E-2,0,4.0264779964368355E-3,0,1.7833739479450373E-2,0,2.4471156799705119E-3,0.89636618679990998,0,4.8514836278745928E-2,221.33276253167747,184.02145782221157,1.2090166894154373,1.6091348027026569,"Tree Trim Scheduled for 2022"]
["VERSAILLES","Woodford - 150 Tanner Alley - Versailles ",505,"Versailles - Main St - N of Substation",5.2541392045454556,546,"2020-06-10",0,0,0,0,0.38981654399648463,0,0.54026145226848288,6.6818631220476765E-2,0,3.1033725145556408E-3,42.273573136955733,66.7270204681233,0.36912890320453506,0.74571737889557488,"Continue to Monitor"]
["VERSAILLES","Woodford - 150 Tanner Alley - Versailles ",506,"Versailles - Main St - S of Substation",4.9365093118686865,504,"2020-06-10",0,0,0,0,0.34495714248267784,0,0.15548410208914015,0.31523211211980884,0,0.18432664330837317,94.392326680521052,149.29444601940122,0.81549746938043666,1.2999921420713492,"Continue to Monitor"]
["VERSAILLES BYPASS","Woodford - 350 Markham Dr - Versailles ",507,"Versailles - Big Sink Rd & Lexington Rd - E of Substation",24.699176609848458,1146,"2020-06-22",7.4867825936926168E-3,0,4.594050010475334E-2,0,0.12764502175172227,0,1.6030341495877648E-2,0.48184378196517264,0,0.32105357208878155,108.45130598567773,244.68129838996933,0.81615174945701807,2.3064080834140492,"Continue to Monitor"]
["VERSAILLES BYPASS","Woodford - 350 Markham Dr - Versailles ",511,"Versailles - 0.28 miles E of Substation",0.28275647095959594,4,"2020-06-20",1,0,0,0,0,0,0,0,0,0,30.659166649999996,66.470833249999998,0.15,0.25,"Continue to Monitor"]
["VERSAILLES WEST","Woodford - 115 Rutter Rd - Versailles",514,"Versailles - Rutter Rd - E of Substation",null,1,"No Trimming Necessary",0,0,0,0,0,0,0,0,0,1,72.12,360.6,0.2,1,"Continue to Monitor"]
["MIDWAY 12KV","Woodford - 860 Weisenburger Rd - Midway ",516,"Midway - State HWY 341 - N of Substation",25.285256786616159,813,"2017-02-04",9.8508226253258661E-3,0,3.7607284166299303E-3,0,0.23271888146902436,0,0,0.73512172024752231,0,1.8547847241497543E-2,107.04679195320853,192.24684677232827,0.66254491872990973,0.75891532754748581,"Tree Trim Scheduled for 2022"]
["SOMERSET 1","Pulaski - 144 Railroad Dr - Somerset ",523,"Somerset - S Main St - N of Substation",1.8272479482323227,75,"2020-08-15",0,0,0,0,0.73357664233576647,0,0,0,0,0.26642335766423358,3.3297067043363362,3.5240890816816819,3.6924924924924926E-2,2.4624624624624628E-2,"Continue to Monitor"]
["DENHAM STREET","Pulaski - 114 Adams St - Somerset ",531,"Somerset - Monticello St - S of Substation",5.1907758838383833,199,"2021-01-23",0,0,0.47141581062974541,0,0,0,0,0,0.47610540419830283,5.2478785171951765E-2,7.9888350922959663,22.385249999999999,0.12531881124868599,0.26500000000000001,"Continue to Monitor"]
["WAITSBORO"," Pulaski - 676 Old Monticello Rd at W Summitt Dr just W of HWY 27 - Somerset ",534,"Somerset - Old Monticello Rd - N of Substation",11.43694523358586,478,"2021-01-09",0.20249679897567222,0,0.34436619718309858,0,0.32215108834827144,0,3.8220230473751601E-2,4.7311139564660688E-2,0,4.5454545454545456E-2,40.304257583162119,32.644279722469186,0.3290457201782771,0.54114525019221438,"Continue to Monitor"]
["BURNSIDE","Pulaski - S Hwy 27 - Burnside",544,"Burnside - City of Burnside - NW of Substation",13.667715593434346,482,"2021-03-27",1.1201314287543071E-3,0,7.812116621683611E-2,0,2.9016737963921098E-3,0,7.1475053072893886E-3,0.86325862234502182,1.0241201634325094E-3,4.6426780742273757E-2,42.715004922263425,37.610092742735858,0.41536245771316993,0.50869381474083497,"Trees Trimmed in 2021"]
["WAYNESBURG","Lincoln - On Old Somerset Rd (HWY 1247) just S of Clear Fork Rd - Waynesburg ",546,"Waynesburg - KY HWY 1247 - S of Substation",10.01077619949495,263,"2017-12-02",0,0,0.6531255796698201,0,0,0,4.0808755332962347E-3,0.29688369504730105,0,4.5909849749582635E-2,15.982931213537512,28.721971369685445,0.14043740626969098,0.20843415139993088,"Tree Trim Scheduled for 2022"]
["SHELBY CITY","Boyle - 401 Grubbs Ln - Junction City ",553,"Junction City - Hustonville Rd & Hwy 127 - SE & NE of Substation",20.173618371212122,891,"2017-09-30",1.5981068580297186E-3,0,0.55518078583831465,0,0.23270894478848134,0,3.5949721099620455E-2,0.16739401017256481,0,7.1684312429890745E-3,29.527285729260477,43.272374919991996,0.26352244276544157,0.38644206976868534,"Continue to Monitor"]
["WINCHESTER WATER","Clark -  335 Waterworks Rd - Winchester ",555,"Winchester - Boonesboro Rd - SW of Substation",19.596184343434341,263,"2018-09-01",4.398156231448825E-2,0,5.1157593323322972E-3,0,0,0,4.6094213779376333E-3,0.90253867374375807,0,4.3754583231483742E-2,52.849214166319072,125.3877411665694,0.62365201038674256,1.3983956687805954,"Continue to Monitor"]
["EDDYVILLE","Lyon - 1765 S R 3305 - Eddyville",560,"Eddyville - US HWY 62 & Riley Rd - NE of Substation",48.26839441287877,503,"2021-05-08",2.8280883326313257E-2,0,0.46777784463565797,0,0.18256212768517963,0,3.2613273963535715E-2,4.9100427221854502E-2,0,0.23966544316745894,44.798009561318068,32.27448001615037,0.7077218272733512,1.3893833404435294,"Continue to Monitor"]
["WHITLEY CITY"," McCreary - Corner of US HWY 27 & Hicks Rd - Stearns-Whitley City ",576,"Stearns-Whitley City - US HWY 27 - N of Substation",39.350536931818176,747,"2021-09-11",3.7409843313897257E-3,0,8.825683256418051E-4,0,6.9494915301074975E-2,0,0.11243851383093376,0.81046197529499553,0,2.9810429159642968E-3,320.64970069312977,528.05149178737918,2.2299141536200322,3.3469108048135929,"Reliability Improvements Scheduled for 2022"]
["REVELO"," McCreary - N of 4850 S HWY 1651 - Stearns-Whitley City ",577,"Stearns-Whitley City - N & S on State HWY 1651",17.201307607323237,539,"2021-10-16",9.9431953338344585E-3,0,2.5833277829053159E-3,0,2.1266068489110062E-3,0,0.18914431430012274,0.58359896095987507,6.0420373559663925E-4,0.21199939103875468,132.81336819094676,241.1078647082079,0.88960018040611488,1.2853057420987357,"Trees Trimmed in 2021"]
["SHUN PIKE","Jessamine - 1201 Short Shun Rd Nicholasville ",580,"Nicholasville - N & S on Nicholasville Bypass ",32.603178503787888,1357,"2020-11-07",0.43214680151207235,1.5054876972024267E-3,0,0,0.56046942483186724,0,1.9155310660229683E-4,3.8280691147552759E-3,0,1.8586637375004116E-3,77.352966643386495,245.90153197257408,0.68920429251081505,2.3919877394666287,"Continue to Monitor"]
["WILMORE 12KV","Jessamine - 210 W Linden St - Wilmore ",585,"Wilmore - College St - E & S of Substation",21.887912878787887,853,"2021-01-16",9.4269126860953029E-3,0,1.347933551761798E-2,0,8.3836293613841456E-2,0,7.6938552624015638E-2,0.73271253664424907,0,8.3606368914180607E-2,20.303114596527582,39.810445708464158,0.15095904631204832,0.22339175888795437,"Trees Trimmed in 2021"]
["WILMORE 4KV","Jessamine - 210 W Linden St - Wilmore ",588,"Wilmore - Main St - SE of Substation",1.1594425505050507,48,"2021-01-16",0,0,0,0,0,0,0,1,0,0,0.6714583291666667,0.93715277083333337,8.3333333333333332E-3,2.0833333333333332E-2,"Trees Trimmed in 2021"]
["INNOVATION DRIVE","Fayette - 2350 Innovation Dr - Lexington ",591,"Lexington - Jaggie Fox Way - S of Substation",6.4283170770202034,99,"2019-11-09",4.925271739130435E-3,0,0,5.6640625E-2,0,0,6.122622282608696E-2,0,0,0.87720788043478259,27.191230538606828,114.0119458321789,0.10822069174675955,0.34198065171625391,"Continue to Monitor"]
["INNOVATION DRIVE","Fayette - 2350 Innovation Dr - Lexington ",596,"Lexington - Spurr Rd and Kearney Rd - NW of Substation",25.673243529040406,753,"2019-11-09",3.093732490194509E-2,2.5214119907148004E-3,2.1812214840310575E-2,0,0.9364844312815177,0,0,8.2446169855118871E-3,0,0,30.400061396473159,34.056540572661135,0.34048344208499415,0.22053075867556568,"Continue to Monitor"]
["MOUNT STERLING 12KV","Montgomery 346 Calk Ave - Mount Sterling ",601,"Mount Sterling - 686 Bypass - N of Substation",18.139400726010102,1360,"2019-01-12",7.1708664934893029E-2,1.3732854613742781E-2,0,0,4.8412448915435398E-2,0,1.4179586028888632E-2,0.81902414004202584,0,3.294230546501431E-2,14.849298115797177,42.951136974280679,0.17724362692888013,0.46345661833553758,"Continue to Monitor"]
["MOUNT STERLING 12KV","Montgomery 346 Calk Ave - Mount Sterling ",602,"Mount Sterling - Richmond Ave - N of Substation",4.0150910669191919,373,"2019-01-12",0,0.19431988041853512,0,0,0.17688091679123069,0,0.57100149476831097,5.7797708021923272E-2,0,0,5.9373044301643976,5.0735930911888492,6.339053261521721E-2,9.9332641471359812E-2,"Continue to Monitor"]
["CAMARGO","Montgomery - 555 S Queen St - Mt Sterling",604,"Mount Sterling - US 460 HWY - S of Substation",23.579874526515155,628,"2018-09-01",4.3282154084468543E-3,9.2259328443209255E-4,8.1324889516606672E-3,0,3.7256822634288582E-2,0,3.8726137865050799E-4,5.7531094810697521E-2,0.22897398514738712,0.66246753838443662,53.919316455609092,131.70243376412506,0.87897202425083731,1.8853809465503537,"Continue to Monitor"]
["A O SMITH","Montgomery - 1871 Owingsville Rd - Mt. Sterling",607,"Mount Sterling - Maysville Rd - W of Substation",36.048284564393938,1059,"2018-09-08",2.5160612648704108E-3,2.2717834721645456E-3,9.4388939101546276E-2,0,3.4198890978821114E-3,0,3.3124068690915311E-2,0.85682878569509247,0,7.4504726775288859E-3,35.207785741638574,33.017968878279781,0.45884606027849301,0.61475742229556463,"Continue to Monitor"]
["A O SMITH","Montgomery - 1871 Owingsville Rd - Mt. Sterling",608,"Mount Sterling - 6 miles W of Substation",6.3244422348484859,212,"2018-09-15",0,0,0.52643335815338799,0,0.47356664184661207,0,0,0,0,0,9.9262878096623979,25.219092328638499,0.13222259306232337,0.28638497652582162,"Continue to Monitor"]
["SALT LICK","Bath - 11457 US HWY 60 E - Salt Lick ",612,"Salt Lick - US HWY 60 - SW of Substation",30.122655460858589,711,"2018-02-19",3.6072826271907436E-3,2.1342278616398066E-3,0.10300201755025645,0.58519652884124551,1.022873672184545E-2,0,9.4703322880964544E-3,0.27330756702885339,0,1.3053307080872165E-2,134.32931791102283,234.05291789690028,0.76456339312196187,1.4848765265006267,"Continue to Monitor"]
["SALT LICK","Bath - 11457 US HWY 60 E - Salt Lick ",613,"Salt Lick - US HWY 60 - NE of Substation",9.9835613952020203,237,"2017-10-28",0,6.0623318620875704E-3,0,0,8.3179089825923403E-4,0,1.4537606690296523E-3,0.32115371645672064,0,0.67049840011390294,48.609691897378625,150.18622853761823,0.47770852918644452,1.4657163386669738,"Tree Trim Scheduled for 2022"]
["FARMERS"," Rowan - 6901 US 60 W - Morehead ",614,"Morehead - US HWY 60 - SW of Substation",5.164547032828283,138,"2017-09-01",0,1.3947847180109158E-2,0.54780675156660608,0,0,0,0,0.32282191227006268,0,0.11542348898322216,11.487554999012499,35.847592912325041,0.12449415461071642,0.23892647227822311,"Tree Trim Scheduled for 2022"]
["FARMERS"," Rowan - 6901 US 60 W - Morehead ",615,"Morehead - US HWY 60 - NE of Substation",22.384594696969693,623,"2017-08-17",2.8186236087160997E-2,0,0.53704342373412761,0,2.7621884307885248E-2,0,0,0.39915347233108633,0,7.9949835397397709E-3,38.750145774179828,51.18973925306998,0.38758377334942795,0.57289029752192189,"Tree Trim Scheduled for 2022"]
["MOREHEAD WEST","Rowan - 133 Gregory Ct - Morehead ",616,"Morehead - US HWY 60 - SW of Substation",7.8828093434343423,371,"2017-05-27",3.7599639043465181E-3,0.15791848398255376,0,0,1.2225254066132394E-2,0,0,0.58638248501385815,0,0.23971381303310918,34.458931593137592,51.747311819892474,0.27113562922302592,0.45161290322580644,"Tree Trim Scheduled for 2022"]
["MOREHEAD WEST","Rowan - 133 Gregory Ct - Morehead ",617,"Morehead - Clearfield Rd - S of Substation",27.446819760101008,1434,"2017-05-27",3.6163072590804674E-2,1.6377129185589819E-2,5.7484041032807194E-3,0,1.9553043054805687E-2,0,4.2557245847492618E-3,0.48468680196059749,2.5830766136289052E-3,0.43063274790654343,35.163805049986408,63.21579046592425,0.24869068654169085,0.46287055958035644,"Tree Trim Scheduled for 2022"]
["MOREHEAD 4KV","Rowan - 100 E Wilkinson Blvd - Morehead ",619,"Morehead - Wilkinson Blvd - N of Substation",2.3070907512626264,200,"2016-11-18",0,0,0,0,0,0,1,0,0,0,1.0946459806997486,1.1267326732673266,1.6204835976691458E-2,9.9009900990099011E-3,"Continue to Monitor"]
["RODBURN 12KV"," Rowan - 1974 US HWY 60 E - Morehead ",623,"Morehead - Rodburn Hollow Rd - NW of Substation",4.4209438131313128,306,"2017-01-27",0,0,0,0,0.33625834872815125,0,0,0.65752451328691208,0,6.2171379849367625E-3,32.646785605461297,31.502668843137254,0.27458402449644553,0.40196078431372551,"Continue to Monitor"]
["ROCKWELL","Clark - 5835 Rockwell Rd - Winchester  ",624,"Boonesborough - Boonesboro Rd - NW of Sub",0.54134659090909099,8,"2018-09-01",0,0,0,0,0,0,0,0,0,1,3.6245833000000003,18.122916500000002,0.05,0.25,"Continue to Monitor"]
["ROCKWELL","Clark - 5835 Rockwell Rd - Winchester  ",627,"Winchester - N & S on Van Meter Rd",25.749697601010105,1032,"2017-12-16",7.1586108157092193E-4,0,6.1208191436977331E-2,0,3.1199956965576596E-3,0,9.4634352228479685E-3,0.92421803556133031,0,1.274481000715861E-3,74.388663928471843,111.22287620874697,0.64765295494704089,0.9521447186121641,"Tree Trim Scheduled for 2022"]
["PARKER SEAL","Clark - 390 Mt Sterling Rd - Winchester ",630,"Winchester - Cherry St - SW of Substation",18.304098327020206,1407,"2021-06-19",3.2813098809319291E-2,0,0.16909384044085582,0,5.7485694651848132E-4,0,0.13797227471554491,0.65135917326320514,0,8.1867558245563021E-3,28.73509608787392,41.792451429946084,0.29620053924554285,0.31150709986949948,"Trees Trimmed in 2021"]
["BOONE AVENUE","Clark - 660 Boone Ave. - Winchester",638,"Winchester - Boonesboro Rd & Hillcrest Dr - SW of Substation",5.2823495896464632,307,"2021-09-11",0,0,0,0,0,0,0.22514986755890143,0.77485013244109857,0,0,26.610438278159272,92.155556602142042,0.23688476382413953,0.75772429714430278,"Trees Trimmed in 2021"]
["BOONE AVENUE","Clark - 660 Boone Ave. - Winchester",639,"Winchester - By-Pass, Colby Rd, McClure Rd - NW of Substation",42.693905934343448,1473,"2021-10-30",2.6832788368687959E-3,0,4.9622853743498648E-3,2.0527816238340515E-4,0.19654755645673133,0,2.0513153512455987E-2,0.68683978458360995,0,8.8248663073600603E-2,63.34226348212551,101.25089957422914,0.78536691327570696,1.4764577268731061,"Trees Trimmed in 2021"]
["WINCHESTER WATER","Clark -  335 Waterworks Rd - Winchester ",641,"Winchester - Old Boonesboro Rd - N of Substation",23.408439393939396,1095,"2018-08-25",2.7739916199707206E-2,0,1.6444545408652634E-2,0,6.3910343783128876E-2,0,6.2345398556211823E-3,0.30872330758746025,0,0.57694734716542984,27.22309464421344,64.257403671404461,0.39104700662833802,1.0163150716559577,"Continue to Monitor"]
["WINCHESTER WATER","Clark -  335 Waterworks Rd - Winchester ",642,"Winchester - Waterworks Rd - E of Substation",24.99956328914141,224,"2018-08-04",1.9868617257082982E-2,0,1.2916616289848063E-2,0,1.5757868859065813E-2,0,0,0.93036916132672387,0,2.108773626727925E-2,34.211879412933428,36.303296033624171,0.35781979177591788,0.3467153325466652,"Continue to Monitor"]
["BOONESBORO","Clark - 170 Settlers Ln. - Winchester",643,"Boonesboro - Ford Rd and HWY 418 - N and S of Substation",8.7437803030303041,111,"2018-09-01",0,0,3.3096498223736677E-2,0,0.11766838251286885,0,0,0.84608134561009207,0,3.1537736533023999E-3,77.198988634375766,215.03521830516684,0.79960453529827369,2.4327057127114333,"Continue to Monitor"]
["WINCHESTER INDUSTRIAL","Clark - 705 Tech Dr - Winchester",644,"Winchester - Rolling Hills Ln - E of Substation",0.90999163510101022,13,"2021-10-23",0,0,0,0,0,0,0.47334754797441364,0,0,0.5266524520255863,19.096556360049018,68.423958270833339,0.27279411764705885,1.1875,"Continue to Monitor"]
["WINCHESTER INDUSTRIAL","Clark - 705 Tech Dr - Winchester",645,"Winchester - Tech Dr, Rolling Hills Ln, Corporate Dr - W of Subs.",3.1546377840909088,15,"2021-10-23",0,0,0,0,1.7624250969333802E-2,0,0,0,0.98237574903066616,0,55.893111106666666,188.96666666666667,0.48011904761904756,1.0625,"Continue to Monitor"]
["EWINGTON","Montgomery - 4006 Old Owingsville Rd - Mt Sterling",646,"Mt. Sterling - Old Owingsville Rd, Arlington Ave - S of Substation",9.5357676767676764,605,"2018-09-01",2.7146024284806667E-3,0,0,0,2.6857236792415109E-2,8.9746266866300281E-4,8.2637651668969567E-4,2.0543897920285766E-2,0.86291924168847378,8.5241181984991934E-2,89.555948440799753,356.12280755645367,0.68790541378707903,2.0693568864392287,"Continue to Monitor"]
["CORPORATE DRIVE","Clark - 4011 Corporate Dr - Winchester",648,"Winchester - Corporate Dr - W NW of Substation",4.6643041351010099,38,"2021-10-23",1,0,0,0,0,0,0,0,0,0,0.55859648947368412,2.7929824473684208,5.263157894736842E-3,2.6315789473684209E-2,"Continue to Monitor"]
["WINCHESTER INDUSTRIAL","Clark - 705 Tech Dr - Winchester",649,"Wnchester - Enterprise Dr - N NW of Substation",0.88380697601010105,5,"2021-10-23",0,0,6.1538461538461542E-2,0,0,0,0,0,0,0.93846153846153846,50.213999960000002,38.869999799999995,0.48,1.4,"Continue to Monitor"]
["STRINGTOWN","Muhlenberg - 5995 Paradise Rd - Greenville",654,"Greenville - Cleaton Rd - E of Substation",2.5118773674242423,8,"2018-12-30",0,0,0,0,0,1,0,0,0,0,33.833617709126983,7.2604166250000004,0.490079365079365,0.625,"Continue to Monitor"]
["BEECHMONT","Muhlenberg - 3660 Merle Travis Hwy - Beechmont",696,"Beechmont - US Hwy 431, Hazel Creek Rd - SE of Substation",16.891855429292931,412,"2018-09-08",9.538037232820042E-3,0,0,3.1027350034474833E-3,0.88822492913506468,0,2.1527618172067723E-2,7.5423274343062896E-2,0,2.1834061135371178E-3,69.235439778138854,68.971497261892864,0.58178577963204892,0.98834125406608331,"Continue to Monitor"]
["SIMMONS","Ohio - 5798 US HWY 62 W - Centertown",699,"Centertown - Midway Rd & US HWY 62 - W of Substation",3.8205137310606063,14,"2018-03-31",0,0,0,0,1,0,0,0,0,0,163.97555554666667,184.3,0.45333333333333331,1,"Continue to Monitor"]
["CAMPBELLSBURG","Henry - 379 Turners Station Rd. - Campbellsburg",703,"Campbellsburg - Hwy 193 & Webb Ln - W & E of Sub.",51.189243686868672,939,"2018-08-04",1.2256875977819128E-2,0,0.79728941594689917,0,0.14792494052082464,0,2.2143842401014618E-2,1.3284453948769219E-2,1.2960442876848021E-4,6.9708667759046852E-3,80.161987055889597,114.23969219515581,1.1054683616892753,3.0966649183058239,"Continue to Monitor"]
["CARROLLTON 4KV","Carroll - 802 Mason St - Carrollton ",705,"Carrollton - 9th St - N of Substation",5.2956546717171715,499,"2020-03-19",0,0,0,0,0.22234365513054039,0.63570127504553731,2.3679417122040074E-2,0.11827565270188221,0,0,11.378694405712132,16.477343285238476,0.13401723715385533,0.21212024048096192,"Continue to Monitor"]
["SCHOLLS","Owen - 970 HWY 127 N - Owenton",724,"Owenton - HWY 127 N, State HWY 845 - NE of Substation",12.72245138888889,182,"2022-01-15",0,0,2.8463594904859255E-2,0,4.639094197200818E-3,0,1.9578550086491585E-2,0.92663940871206163,0,2.0679352099386695E-2,30.046751386939953,68.962072388398482,0.28705138829366217,1.0438959947156667,"Trees Trimmed in 2022"]
["WARSAW","Gallatin - RR 1 Box 51 - Warsaw",727,"Warsaw - City of Warsaw - N of Substation",7.964724116161614,500,"2021-10-16",0,0,1.1070791561596655E-2,0,0.11027738483301557,0,1.5622116981364167E-2,6.273448551571437E-3,2.300264468909527E-2,0.83375361338335696,14.323163519167679,32.577657033349418,9.7989455162333608E-2,0.19230099977353052,"Continue to Monitor"]
["SPARTA","Owen - RR 1 Box 136C - Sparta",730,"Sparta - State HWY 467 - NE & SE of Substation",28.226528251262629,383,"2018-12-31",1.181183946950335E-2,0,0.22691165296677487,0,0.21855356772812046,0,4.9872211093458588E-2,0.47268080403398494,0,2.0169924708157767E-2,111.55151214488311,37.741669725745211,0.46856826451427558,0.48498980851250101,"Continue to Monitor"]
["STANFORD NORTH","Lincoln - 300 Lee Dr - Stanford",768,"Stanford - Danville Ave, Lancaster St - SW of Substation",11.394408775252522,614,"2018-06-16",7.7488309953239812E-3,0,0.25220440881763528,0,0.12227788911155645,0,3.7174348697394791E-2,0.58059452237808951,0,0,25.38462528835128,27.898962462426844,0.37614717162097006,0.42298667937819445,"Continue to Monitor"]
["BOONE AVENUE","Clark - 660 Boone Ave. - Winchester",769,"Winchester - Boone Ave, Harkins Ave, Skylark Dr- NW of Subst.",16.752965277777776,1443,"2021-08-14",2.2630933071125237E-2,1.7507422992501517E-2,8.6714488674855504E-4,0,8.4198220030272646E-4,0,1.6179607384667793E-2,0.94059476848392887,0,1.3781409807253821E-3,27.376934493949392,53.727737810510931,0.3803420594581382,1.0389789922559249,"Trees Trimmed in 2021"]
["MOREHEAD 12KV","Rowan - 100 E Wilkinson Blvd - Morehead ",779,"Morehead - Wilkinson Blvd - N of Substation",6.979371843434345,466,"2017-01-27",1.4616248295773519E-2,0,6.5562595236185739E-3,0,0.70009623867190629,0,0,0.25609511588740075,0,2.2636137621300827E-2,96.087216684598459,107.02292538018372,1.0173200347517761,1.285302253487915,"Continue to Monitor"]
["PARIS 12KV","Bourbon - 520 Scott Ave - Paris",795,"Paris - Clintonville Rd - SW of Substation",16.893132102272723,1038,"2021-08-28",0.18827333619295872,0,2.0853268221862935E-2,0,2.969610980961494E-3,0,1.0888573596858811E-2,0.68304352129870982,0,9.3971689708648165E-2,10.688390553694964,24.45996663729947,0.13951842326868596,0.30029152085987526,"Trees Trimmed in 2021"]
["CORPORATE DRIVE","Clark - 4011 Corporate Dr - Winchester",798,"Winchester - Enterprise Dr - SE of Substation",1.1506920770202018,9,"2017-09-02",0,0,0,0,0,0,1,0,0,0,18.546333320000002,79.398333300000004,0.08,0.2,"Continue to Monitor"]
["CORPORATE DRIVE","Clark - 4011 Corporate Dr - Winchester",799,"Winchester - Corporate Dr & Fortune Dr - NW of Substation",0,38,"2021-10-23",1,0,0,0,0,0,0,0,0,0,3.0154694079658606,2.5346491052631581,3.741109530583215E-2,5.2631578947368418E-2,"Continue to Monitor"]
["DETROIT HARVESTER 12KV","Bourbon - 115 W 20th St - Paris",802,"Paris - Bypass Rd, Cynthiana Rd - N of Substation",25.065481060606061,210,"2020-01-18",0,0,3.7301700728883808E-2,0,4.2303844504787767E-2,0,0.11433471487780478,4.1160497356009719E-2,0,0.76489924253251396,34.371959499680706,33.157952811307077,0.4962410781759633,1.108607697571796,"Continue to Monitor"]
["PARIS 12KV","Bourbon - 520 Scott Ave - Paris",806,"Paris - Cane Ridge Rd/KY 537, US HWY 68, & Bypass Rd - NE of Substation",114.03384990530301,1036,"2022-01-08",8.4307351822394353E-3,0,4.7264679438412061E-2,5.3945639394148968E-4,2.5375198838093919E-2,0,0,0.80558821495262456,0,0.11280171519468843,35.258176751683337,33.255887311039871,0.48352301806559594,0.49993698693412902,"Trees Trimmed in 2022"]
["MILLERSBURG","Bourbon - Vimont Ln. – Millersburg",808,"Millersburg - Old US Hwy 68/Vimont St/HWY 68/HWY 1879 - NE/NW/SW of Subst.",34.960075757575765,625,"2022-01-22",2.3149784406587968E-2,4.1351523291157134E-3,0,0,9.1892273980349187E-4,0,7.0686364600268614E-2,0.47610800876510923,0,0.42500176715911503,39.014546603159701,45.132285552022473,0.52263490045276995,1.1165858093432761,"Trees Trimmed in 2022"]
["HANSON","Hopkins - 235 Fowler Rd - Hanson",809,"Hanson - Hanson Rd, N Main, Hwy 1069, & University Circle Dr - SW of Substation",1.366163667929293,42,"2019-06-22",0,0,1,0,0,0,0,0,0,0,7.1863602741971206,14.87698411904762,0.10830564784053157,0.23809523809523808,"Continue to Monitor"]
["HANSON","Hopkins - 235 Fowler Rd - Hanson",810,"Hanson - Hanson Rd & Hwy 1069 - SW of Substation",21.789092487373736,887,"2019-08-03",4.2750171917581438E-2,0,0,0,1.0315054886279704E-3,2.410666530830553E-2,0.12979140666785524,0.69436874411023108,0,0.10795150650739882,54.571936759254982,88.631706508724704,0.67389950899899875,0.87509662437427937,"Continue to Monitor"]
["CROSSROADS","Hopkins - 1340 Amanda Ln - Nortonville",813,"Nortonville - No Road - N of Substation",0.40892424242424241,5,"2017-12-30",0,0,0,0,0.99852791303363153,0,1.4720869663684747E-3,0,0,0,12.897333320000001,22.4866666,0.27999999999999997,0.4,"Continue to Monitor"]
["DOZIER HEIGHTS","Hopkins - 200 Claire Ln - Madisonville",815,"Madisonville - Country Club Ln, US 41A - NW of Substation",13.598418402777776,652,"2019-07-27",0.14217557251908397,0,0.49952290076335876,0,4.1984732824427483E-3,8.2156488549618323E-2,0.24379770992366412,0,0,2.8148854961832059E-2,22.990004655246572,16.073975696960172,0.34494897550308123,0.43405867658650538,"Continue to Monitor"]
["NORTONVILLE","Hopkins - 55 Holly Ln - Nortonville ",818,"Nortonville - Mockingbird St, US 41, & Wells Rd - N of Substation",17.785937973484852,369,"2017-04-15",7.7675380277198908E-5,0,9.1472980721175022E-4,0,0.99802387700307948,0,3.0712436543813514E-4,6.5921868787885906E-4,0,1.7374756114636597E-5,14.731963727925864,25.243873859459455,0.18968818479891275,0.32702702702702707,"Continue to Monitor"]
["MORTONS GAP","Hopkins - 900 White Plains Rd - Mortons Gap",822,"Mortons Gap - Hwy 1215 & City of Mortons Gap - W of Substation",12.208742266414143,483,"2020-05-30",6.4638359523013483E-3,0,7.0990750027861357E-2,0,0,0,0.41591440989635575,0.24986069319068316,0,0.2567703109327984,38.459341328942315,18.568984671668851,0.27419259330354351,0.29434649420591308,"Continue to Monitor"]
["MORTONS GAP","Hopkins - 900 White Plains Rd - Mortons Gap",823,"Mortons Gap - Trabue Rd, Flat Creek Rd, & Old White Plains Rd - N/S of Substation",24.112192866161614,214,"2020-06-20",0,0,4.6325765859936879E-4,0,0,3.7871138908123359E-4,1.0970053152353077E-4,0.99784791313953836,0,1.2004172812574896E-3,58.797539387919095,16.887683554545713,0.85586525452671736,1.195828402843182,"Continue to Monitor"]
["SYLVANIA 12KV","Clark - 439 E Washington St - Winchester",847,"Winchester - E Washington, E Broadway St, Hickman St - SW of Subst.",14.187394412878785,1496,"2018-02-26",5.3880397043781425E-3,0,2.3929235157679397E-2,0,0.17156728566694998,0,0.34100240588938668,4.1361128318902797E-2,9.5515249304885252E-3,0.40720038033221445,20.933987225414228,43.445632090250946,0.2857000551278851,0.60804776016623541,"Continue to Monitor"]
["SYLVANIA 12KV","Clark - 439 E Washington St - Winchester",849,"Winchester - Ecton Rd, Iron Works Rd - NE of Subst.",46.246723800505059,1215,"2018-02-26",6.8215047354746186E-3,9.0006611970460323E-3,0.23756996116631435,0,0.14951434611337203,0,4.8570044980024402E-2,0.23495311088553841,0,0.31357037092223017,54.163922757268857,145.48153374126215,0.60702318525244137,1.0256675477372235,"Continue to Monitor"]
["ASHLAND PIPE","Fayette - 900 Forest Lake Dr - Lexington",862,"Lexington - No Road - NE of Substation",5.0064709595959598E-3,1,"No Trimming Necessary",0,0,0,0,1,0,0,0,0,0,69.156666600000008,345.78333300000003,0.2,1,"Continue to Monitor"]
["MACKVILLE","Washington - 4685 Texas Rd - Springfield ",866,"Springfield - Texas Mackville Rd - S of Substation",9.6499678030303038,45,"2020-09-19",0,0,0,0,0.27170042501052954,0,5.743385534326301E-4,0.72772523643603781,0,0,158.59499988848299,157.90128737372802,0.49386006223194012,1.064754856614246,"Continue to Monitor"]
["SHANNON RUN","Woodford - 2770 Shannon Run Rd - Versailles",867,"Versailles - Shannon Run, Hwy 169 - SW of Substation",41.282813920454558,379,"2021-09-25",1.3726761781236489E-2,0,7.2957198443579768E-4,0,7.2578901859057507E-2,0,1.6415369649805448E-2,0.62767509727626458,0.26887429744920016,0,78.548065987981914,104.21052399647751,0.52679286522616919,0.53310213601913281,"Trees Trimmed in 2021"]
["SHANNON RUN","Woodford - 2770 Shannon Run Rd - Versailles",868,"Versailles - Shannon Run, Lexington Rd, Pisgah Rd - N of Subst",66.243165246212143,1117,"2021-08-07",2.7967546736380428E-2,2.0865346451228086E-3,3.625825134649114E-2,0,9.8785552576903551E-2,0,2.6386569901127969E-3,0.80898784222161624,5.1220988631601354E-4,2.2763405597057123E-2,163.07828782948795,223.6111083206996,1.0101495722809268,0.90049329205220574,"Trees Trimmed in 2021"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",873,"Lexington - Bryant Rd & I75 - E of Substation",31.843970170454547,1920,"2016-11-12",5.1459747201714034E-2,0,0.30436847365718167,0,0.45394355386458896,0,3.5285737162673325E-3,0.11172160160801356,0,7.4978049952234491E-2,81.665438785538953,93.62240352388504,0.40067126756999966,0.70465985338074844,"Continue to Monitor"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",874,"Lexington - Todds Rd - S of Substation",29.857853219696974,2411,"2016-10-29",1.3683999732995128E-3,0,0,0,0.14147443905136983,0,0,4.5819943356823403E-3,0,0.85257516663964827,23.698745794117404,86.938690609199355,0.14938367686727541,0.47688221065405317,"Continue to Monitor"]
["CARLISLE 4KV","Nicholas - 104 S Elm St - Carlisle",876,"Carlisle - Main St, Eastern Ave - ENE of Substation",7.2792799873737382,397,"2019-06-15",0,0,4.8710601719197708E-2,0,0,0,0.11155024207094161,0,0,0.83973915620986073,14.682125080645175,25.208574494645102,0.17576528284094711,0.31270442436235957,"Continue to Monitor"]
["CYNTHIANA SOUTH","Harrison - 460 Education Dr - Cynthiana",880,"Cynthiana - New Lair Rd, Old Lair Rd, Ruddles Mill Pike, & Lake Rd - SE of Subst.",20.999082228535343,219,"2020-10-03",2.5561921551344204E-2,0,0.43190832966064346,0,4.6275892463640368E-2,0,0.42133098281181136,7.4922873512560606E-2,0,0,23.732135672210163,10.317821004732254,0.2916456311546245,0.52287256122872561,"Continue to Monitor"]
["MAYSVILLE WEST","Mason - 210 Cox Alley - Maysville",900,"Maysville - Maddox Aly, 4th St, Hwy 62 - SE of Substation",1.5798910984848482,169,"2019-09-07",0,0,0,1,0,0,0,0,0,0,2.2296351076923075,0.43668639053254438,4.275147928994083E-2,5.3254437869822487E-2,"Continue to Monitor"]
["MAYSVILLE WEST","Mason - 210 Cox Alley - Maysville",901,"Maysville - Maddox Aly, 4th St, Plum St, Mulberry St- SE of Subst.",1.9750557133838385,389,"2019-09-07",0,0,0,0,0,0,0.67822838847385269,0,0.11739594450373532,0.20437566702241194,4.4644137107053838,4.8120812725921933,5.4018692104936261E-2,0.12071742746500636,"Continue to Monitor"]
["MAYSVILLE WEST","Mason - 210 Cox Alley - Maysville",903,"Maysville - W 2nd St, W Mcdonald Pkwy - NW of Subst.",3.3352058080808082,351,"2019-09-07",0,0,0,0,0.22535276859311693,0,5.5511572672658688E-2,0.71676058305779344,0,2.3750756764308665E-3,32.40688350393652,49.303995807325627,0.32880925007203843,0.58688631125428881,"Continue to Monitor"]
["BRYANT ROAD","Fayette - 3097 Helmsdale Pl. - Lexington",904,"Lexington - Bryant Rd - NE of Substation",16.097127209595961,1074,"2017-02-11",0,0,0,0,0.99505261833885372,0,0,0,0,4.9473816611462834E-3,55.11629330680082,44.112899033436477,0.50674484501557315,0.63940693512768865,"Continue to Monitor"]
["MAYSVILLE MID","Mason - 314 Lexington St - Maysville",907,"Maysville - Buckley Pl, Hwy 11, Bank St - W & S of Subst.",6.7527804608585864,222,"2019-10-12",0,0,0,0,0.3991031390134529,0,0.60089686098654704,0,0,0,3.2238385361913231,2.0121395155978501,4.4529983740961107E-2,4.4954944033620235E-2,"Continue to Monitor"]
["KENTON","Mason - 801 Kenton Station Rd - Maysville",920,"Maysville - Lexington Rd, Duke of York St, Hwy 2515 - S of Subst.",55.272782039141404,1295,"2021-06-25",2.329752863676415E-2,6.8182771787018005E-4,2.8636764150547561E-3,0.49115721898208364,4.1853732220031052E-3,0,1.9049217471573027E-2,1.6951286031972476E-2,0,0.44181387152267865,33.741366511552002,73.512093206668538,0.64560917481241176,1.4203691031711103,"Continue to Monitor"]
["KENTON","Mason - 801 Kenton Station Rd - Maysville",921,"Maysville - W Maple Leaf Rd, Jersey Ridge Rd - E&NE of Subst.",20.49351893939394,889,"2021-09-10",2.5628436763550668E-2,0,0.27395915161036921,0,0.19069128043990574,0,0.10722702278083268,4.2124901806755696E-2,0,0.36036920659858601,57.359530042347203,34.364442863615928,0.55110283630936441,0.56129602384591915,"Continue to Monitor"]
["KENTON","Mason - 801 Kenton Station Rd - Maysville",922,"Maysville - Parker Rd, Hwy 10, Martha Comer Dr - W of Subst.",4.2843109217171715,116,"2021-01-23",0,0,0,0,0,0,0.75806451612903225,0.22204301075268817,0,1.9892473118279571E-2,7.3830608541171072,12.510534729760121,0.12183331482837993,9.5127436281859074E-2,"Continue to Monitor"]
["AUGUSTA","Bracken - 318 E 4th St. - Augusta",929,"Augusta - 5th Street, Old August-Brooksville Rd - W&SW of Subst.",21.571377683080804,654,"2018-05-08",2.8569005004665367E-2,0,0.17551955212486217,0,0,0,9.7650352023072359E-2,0.63493086775807961,0,6.3330223089320556E-2,93.731477399988336,82.057298695936282,1.1453796459534313,1.4863588761745488,"Continue to Monitor"]
["AUGUSTA","Bracken - 318 E 4th St. - Augusta",931,"Augusta - Hamilton Ave, E 2nd St - N of Substation",2.9339791666666666,281,"2018-02-10",0,0,0,0,0,0,0.69842861919090604,3.2430625208960215E-2,0,0.26914075560013373,12.803810989728131,31.894581242973238,0.17235294601726384,0.26660175837437816,"Continue to Monitor"]
["SHARON","Bracken - 3061 Asbury Rd - Augusta",936,"Augusta - Dutch Ridge Rd, KY 1235, City of Dover - N&NE of Subst",52.845730271464667,625,"2019-02-16",4.045419935776476E-3,0,0,0,2.3438275896315421E-3,0,1.5890356539874863E-3,0.26445525871486741,0,0.72756645810573706,84.150720206873515,241.17012914235573,0.54650581589376812,1.0524970380562759,"Continue to Monitor"]
["SHARON","Bracken - 3061 Asbury Rd - Augusta",937,"Augusta - Woodward Rd, Clarks Run Rd - S&SE of Substation",45.851822285353535,558,"2019-03-16",7.3600128232528322E-3,0,0.28416862577473817,0,1.2622889506304765E-2,0,9.3369309681555889E-3,0.56941921350715963,2.5512930113272066E-3,0.11454103440906177,96.568816817929019,133.91659161324986,0.94980884340980842,0.69811914723743995,"Continue to Monitor"]
["PARKERS MILL","Fayette - 2085 Parkers Mill Rd - Lexington",939,"Lexington - Parkers Mill Rd - SW out of Substation",61.928318023989895,1361,"2018-07-14",7.8283295489585958E-2,0,0,0.30839570543548339,0.44679729767611359,0,1.0007568749474392E-2,0.10000840972163821,1.2053934348106412E-3,5.5302329492893786E-2,41.538199899749607,130.45211666928969,0.46454187651076417,1.7404671285417537,"Continue to Monitor"]
["CARNTOWN","Pendleton - 15125 Hwy 8 - Foster",947,"Foster - Hwy 8 - NNW of Substation",48.326644728535349,655,"2017-12-02",2.901367077166422E-2,0,9.1515083041464242E-3,0,1.1072195232177156E-2,0,0.11490227092983844,0.75756411704892102,0,7.8296237713252739E-2,54.910372269195953,65.553025218410696,0.34019973123322589,0.47383436545200464,"Tree Trim Scheduled for 2022"]
["CARNTOWN","Pendleton - 15125 Hwy 8 - Foster",948,"Foster - Hwy 8 - S&SE of Substation",23.401561079545456,231,"2018-02-06",2.7535044602221008E-3,0,1.9046968869470236E-2,0,2.0912980156562899E-2,0,2.5031858729291825E-2,5.1087748042963774E-2,0.48300109229929,0.39816584744219918,117.29969247258217,189.41837677692567,1.1102446090835487,2.3793290043290054,"Continue to Monitor"]
["BUTLER","Pendleton - 11095 Hwy 27 N - Burnside Butler",950,"Butler - City of Butler, Flour Creek Rd, Hwy 10 - ESE of Substation",58.528782196969715,935,"2017-06-17",2.9490119541351549E-2,2.3225176872407903E-2,0.63033910709929253,0,3.0495242742132225E-3,0,1.7614052207855575E-2,2.3932666504025372E-2,4.610880702610393E-3,0.26773847279824348,172.06397520275792,101.32675026932132,1.6506245069690473,1.9193430097321409,"Continue to Monitor"]
["WEDONIA","Mason - 6964 KY Hwy 11 - Maysville ",966,"Flemingsburg - Hwy 170, City of Ewing - SW of Substation",27.381595486111106,523,"2017-12-17",0.40393738742167085,0,3.2853844787781921E-3,0,2.8566354618565593E-2,0,2.4101276099145041E-3,0.55709465459065888,0,4.7060912804120052E-3,231.84268508682922,66.644960730293135,0.92323157400997646,1.0726468109388643,"Tree Trim Scheduled for 2022"]
["EWINGTON","Montgomery - 4006 Old Owingsville Rd - Mt Sterling",968,"Mt Sterling - Owinsville Rd - W of Substation",1.5398382260101009,15,"2018-09-01",0,0,0,0,1,0,0,0,0,0,8.6840170851282057,15.727777733333333,0.14358974358974358,0.33333333333333331,"Continue to Monitor"]
["EWINGTON","Montgomery - 4006 Old Owingsville Rd - Mt Sterling",969,"Mt Sterling - Woodland Ln, Clarence Dr - N of Substation",5.0842539457070703,175,"2018-09-01",0,0,0,0,0.15141343470700044,0,0,0,0,0.84858656529299958,55.132426601119604,140.36361903999997,0.54115962973817977,1.3942857142857144,"Continue to Monitor"]
["EWINGTON","Montgomery - 4006 Old Owingsville Rd - Mt Sterling",970,"Mt Sterling - Woodland Ln, Clarence Dr - N of Substation",2.9149294507575751,5,"2018-09-01",0,0,0,0,0,0,1,0,0,0,1.28466664,6.4233332000000001,0.04,0.2,"Continue to Monitor"]
["BARLOW","Ballard - 433 Oscar Rd. - Barlow",1310,"Barlow - US Hwy 60 - S of Substation",14.174366635101014,209,"2017-07-29",1.0248447204968944E-3,0,0.10944099378881987,0,0.19167701863354036,0,0,0.69785714285714284,0,0,233.44247827838271,153.69574009668861,0.75368709873842954,1.319845067213488,"Tree Trim Scheduled for 2022"]
["BARLOW","Ballard - 433 Oscar Rd. - Barlow",1311,"Barlow - US Hwy 60 - E of Substation",25.037292929292935,680,"2017-09-08",3.2709056381376465E-2,0,3.9290157815467224E-3,3.4378888088533823E-3,0.13817038831772641,1.6698317071573571E-3,4.7803025342151792E-2,2.7928753847161286E-2,0,0.74435203981402653,36.917425741149103,44.90563671530446,0.56993449212164071,0.47346911214831727,"Continue to Monitor"]
["BARDWELL","Carlisle - US Hwy 62 - Bardwell",1313,"Bardwell - US Hwy 62 - N of Substation",5.958039299242424,27,"2021-11-13",0,0,0,0.26284279644650443,0,0,0,0.1093086133642333,0.62784859018926231,0,110.10464264904212,191.7592592222222,0.88067432950191571,1.5555555555555554,"Continue to Monitor"]
["CLINTON 12KV","Hickman - 318 Moss Drive - Clinton",1316,"Clinton - City of Clinton, Hwy 58, ",27.047328282828289,658,"2021-12-04",3.1883516688727899E-3,0,0.14586228298062823,0,3.4135410201626853E-3,0,5.8384458639307076E-3,0.82474501425283819,0,1.6952364213567384E-2,156.18092967964122,548.67647220421725,0.83035039693065149,2.0898306380932645,"Trees Trimmed in 2021"]
["CLINTON 12KV","Hickman - 318 Moss Drive - Clinton",1318,"Clinton - S Washington St, Mayfield Rd - E&SE of Substation",6.8028197601010101,281,"2021-07-24",4.1719281980786751E-3,0,0.90805773565000558,0,1.4497850098304055E-2,0,9.6385927334921122E-3,2.8771918607439139E-3,8.951263566758844E-3,5.1805437892616803E-2,58.833161784663389,221.85082615175034,0.35012672464231198,1.1241387143181643,"Continue to Monitor"]
["FORESTDALE","McCracken - 4250 Rice Springs Rd - Kevil",1322,"Kevil - Clarkline Rd, Kevil Rd, Woodville Rd, & Hwy 473 - NW of Substation",26.316268781565658,610,"2019-12-20",4.0976705023856301E-2,0,8.7473103190195533E-3,0,0.1140424735709608,0,5.5664702030124427E-2,2.03480213303396E-2,3.9620170268500329E-2,0.72060061745719894,77.467710408406276,34.117414866296343,0.72045544822081542,1.229492363016047,"Continue to Monitor"]
["CRUTCHFIELD","Fulton - 200 Crutchfield St - Fulton",1323,"Fulton - Depot St, Hwy 924 - SW of Substation",1.2033470643939395,41,"2021-07-24",0,0,0,7.1602549130826462E-2,0,0,0,0.92839745086917347,0,0,311.03909405551684,731.0166666341463,1.4281765389082461,2.024390243902439,"Trees Trimmed in 2021"]
["GREENVILLE NORTH","Muhlenberg - 501 HWY 189 Bypass - Greenville",1327,"Greenville - HWY 601, S R 181, & Luzerne Depoy Rd - NW of Substation",41.294748263888891,798,"2021-12-11",4.3543108091312094E-2,0,0.44394498073497118,1.698636947425115E-3,0.18492356133736587,0,6.73240253552637E-3,0.25705348634875919,3.8240046401789782E-2,2.3863777602850397E-2,56.081891148096055,49.790946943713863,0.78610996692194313,0.9880765712812758,"Trees Trimmed in 2021"]
["CLAY - KU","Webster - 62 W College St - Clay",1408,"Clay - S R 270, W Elm St - W & E of Substation",17.026679766414141,337,"2019-09-07",0,0,0,0,0.38915447390023661,0,0,0,0,0.61084552609976339,19.620207380699018,61.198335419334271,0.19936184271982071,0.73295057904514616,"Continue to Monitor"]
["SPENCER CHEMICAL 12KV","Henderson - 1413 Hwy 136 W - Henderson",1437,"Henderson - Hwy 136 & Hwy 60 - S of Substation",4.2816321022727264,84,"2020-03-28",0,0,0,0,0,0,1,0,0,0,1.9775861091424525,2.8411764705882354,2.1233167965981573E-2,2.3529411764705882E-2,"Continue to Monitor"]
["TUNNEL HILL","Henderson - 12990 HWY 416 W - Corydon",1443,"Corydon - US HWY 41 A & S R 416 - N & E of Substation",23.329203914141424,376,"2020-10-17",4.0691631759629615E-2,0,1.5747535510692576E-3,0,0.75723599256716334,0,0,9.5146609555604555E-2,0,0.10535101256653334,49.616846180397019,84.435700430692719,0.64367867903101017,1.2551075863621717,"Continue to Monitor"]
["SENTRY","Hopkins - 1000 John Hardy Rd - Madisonville",1455,"Madisonville - Manitou-Richland Rd - W of Substation",0.95925915404040418,4,"2019-01-26",1,0,0,0,0,0,0,0,0,0,12.856666649999999,64.283333249999998,0.2,1,"Continue to Monitor"]
["AIRLINE RD 12KV","Henderson - 1830 Clay St - Henderson",1461,"Henderson - Clay St - E of Substation",11.666478061868689,822,"2020-09-19",0.15777029024058639,0,0,0,5.4560501270910916E-2,0,0,0.75279304841283912,0,3.4876160075663534E-2,14.986433282791278,20.576557595498041,0.17720562609870799,0.18249656966905825,"Continue to Monitor"]
["ZION","Henderson - 7485 HWY 351 - Henderson",1468,"Henderson - HWY 351/Zion Rd, Adams Ln, & Spring Garden Rd - W of Substation",12.716799558080808,720,"2020-08-29",2.7158294056788138E-3,0.11591849637889412,0,0,4.7203701574893668E-2,0,0.61906540981722036,0.13800436831819748,0,7.7092194505115536E-2,92.310539688836315,96.516366149791978,0.45377545234157413,0.78363384188626894,"Continue to Monitor"]
["SEBREE","Webster - 199 N Railroad St - Sebree",1473,"Sebree - Railroad St, Dixon St, State St, & Church St - S of Substation",5.5813008207070718,321,"2020-03-28",0,0,0,0,0.12716763005780346,0,0.11730703842230533,0,0,0.75552533151989121,7.405220337558001,9.1737399984326622,5.0698725035651551E-2,9.6613777089783276E-2,"Continue to Monitor"]
["CROFTON","Christian - 13770 Madisonville Rd - Crofton",1491,"Crofton - Madisonville Rd, W Princeton St, W Mill St - S of Subst",6.4376041666666666,265,"2018-06-30",0,0,0,3.8081876033471964E-5,0.96818893955337304,0,1.0221977251089842E-3,0,0,3.0750780845484459E-2,42.021174259942939,179.21228068796995,0.29063251419367275,1.1090225563909768,"Continue to Monitor"]
["CROFTON","Christian - 13770 Madisonville Rd - Crofton",1492,"Crofton - City of Crofton, Madisonville Rd - N&S of Substation",25.660055082070706,465,"2018-09-01",7.2656539789652948E-5,0,0.78201253516512792,6.13119221733738E-4,1.9626188476162921E-2,0,5.4390430751306866E-3,7.4678176142396607E-2,0,0.11755828137965846,96.136040577118351,314.03721203350131,0.97553645416243895,2.1358710350732797,"Continue to Monitor"]
["KUTTAWA","Lyon - 3487 Lake Barkley Dr - Kuttawa",1501,"Kuttawa - Hwy 295, Lake Shore Dr, & Holley St - SW & SE of Substation",11.144713226010097,416,"2021-02-13",5.2872924338219968E-2,0,4.5925102480372404E-2,0,4.4257625234488986E-2,0,1.9731814076287085E-2,0,0,0.83721253387063155,58.292886467905511,34.526673595941283,0.88635768724770903,1.4869747866728509,"Continue to Monitor"]
["EDDYVILLE PRISON","Lyon - 328 Water St - Eddyville ",1503,"Eddyville - HWY 93, HWY 1055, Perry Springs Rd, E of Substation",59.970526830808069,923,"2021-08-14",2.759998184211721E-3,0,8.0106526245706418E-3,0,5.9427724060707857E-2,0,2.343274774161333E-2,0.79339053066412457,0,0.11297834672477189,38.410078955918969,54.01912797603125,0.44983133012786602,0.5603119605707374,"Trees Trimmed in 2021"]
["EDDYVILLE","Lyon - 1765 S R 3305 - Eddyville",1506,"Eddyville - City of Eddyville - NW of Substation",27.385274305555551,1023,"2021-03-06",1.8403658803997119E-2,1.5083168875105723E-2,0.33906587726717413,0,0.35294301913980514,0,4.6204930614290639E-3,0.14693167935344423,5.1216990884315385E-3,0.11783040441061304,48.840950992670926,60.119926478210623,1.1958278720719051,3.0359769502816443,"Continue to Monitor"]
["FREDONIA","Caldwell - 150 Wigginton Ln - Fredonia",1508,"Fredonia - Hwy 651, Loyd Rd, & Crayne Cemetery Rd - NW of Substation",15.960535037878786,220,"2021-10-23",2.0689655172413793E-2,0,0,0.81697612732095493,0,0,3.1072375899962108E-2,0.12701780977643046,0,4.2440318302387264E-3,32.108849872334886,59.005189489756077,0.4349990524630008,0.71014339093130241,"Continue to Monitor"]
["FREDONIA","Caldwell - 150 Wigginton Ln - Fredonia",1509,"Fredonia - Hwy 91, Princeton Fredonia Rd, & Marion Rd - SE of Substation",34.855648674242424,193,"2021-11-06",1.268938590162543E-2,0,2.5463650638713237E-3,0.86733438017230402,0,0,0,0.11492594321605908,0,2.503925646140135E-3,140.85485772224177,120.45903086224054,1.0711823126087299,1.1034939509860722,"Continue to Monitor"]
["FREDONIA QUARRY 12KV","Caldwell - 181 Fredonia Quarry Rd - Fredonia",1513,"Fredonia - Beck Rd & New Bethel Church Rd - S of Substation",12.316762941919192,71,"2021-11-13",1.2328632014991616E-2,0,3.3533879080777196E-3,0,2.1106618009665647E-2,0,8.9752441069138964E-3,0.55340763388894365,0,0.40082848407140742,96.056947328038518,142.79272297183098,0.78077682643337565,1.464788732394366,"Trees Trimmed in 2021"]
["SUNSET 2 2.4KV","Hopkins - 1515 Olney Rd - Dawson Springs",1523,"Dawson Springs - Hwy 1220, Purdy Ln, & Walnut Grove Rd - S of Substation",2.3105984848484842,27,"2017-09-02",0,0,0,0,0.98686499513222781,0,7.1819589191949825E-4,1.2416808975852659E-2,0,0,19.333897704761903,30.512345666666665,0.27380952380952384,0.33333333333333331,"Continue to Monitor"]
["DAWSON SPRINGS","Hopkins - 205 Munn St - Dawson Springs",1525,"Dawson Springs - N Trim St, Sycamore St - NW of Substation",2.1743028724747466,154,"2017-02-11",0,0,0,0,0.13920186319323027,0,2.5228905495164094E-4,0.86054584775181808,0,0,5.1924743108174969,6.4977251463373227,0.12870947664583984,0.31300398947457769,"Tree Trim Scheduled for 2022"]
["SIXTH VEIN","Hopkins - 2395 Sixth Vein Rd - Dawson Springs",1541,"Dawson Springs - Charleston Rd, Hwy 70, Campbell Rd, & High Glory Rd - N of Substation",40.216908933080809,456,"2017-05-13",3.938360690402559E-3,0,7.4670261411994817E-3,0,0,0,7.4405941902571833E-3,0.7964871937197685,0,0.18466682525837233,27.270081528091545,36.296486425521046,0.33770597462813778,0.42455602369954443,"Tree Trim Scheduled for 2022"]
["SIXTH VEIN","Hopkins - 2395 Sixth Vein Rd - Dawson Springs",1544,"Dawson Springs - Fergusontown Rd, Hwy 109, Niles Rd & Fox Rd - W & S of Substation",26.644622316919193,350,"2017-08-05",3.3143416297091272E-4,0,0,0,0.98823803285932987,0,2.4857562222818452E-4,2.7224949101182115E-3,8.3805495494073644E-3,7.8912895945455405E-5,17.057208611970204,17.771362260843741,0.4195213074126925,0.19781504289192431,"Continue to Monitor"]
["ST CHARLES","Hopkins - 660 St. Charles Rd - St. Charles",1554,"St. Charles - Ilsley Rd, Union Temple Rd, & Hwy 112 - SW/NW of Substation",68.576161773989867,625,"2017-08-19",1.0869630036826632E-4,0,2.6171141647272104E-3,0,0.23120895765940272,0,1.4312131320310377E-4,0.12950933785249721,0,0.63641277270980146,49.137260428300557,58.985355527781252,0.60514329090941255,0.6569827289588499,"Continue to Monitor"]
["SHAVERS CHAPEL","Muhlenberg - 7870 S R 181 N - Bremen",1609,"Bremen - S R 181, Buttermilk Rd, S R 175, & S R 81 - NW of Substation",95.272070075757568,1784,"2019-08-03",5.175445226353935E-4,0,0.11070514021117395,0,2.12887521323071E-2,2.3647682197367815E-3,0.68875156427043027,0.10921988210398889,1.0824254345362193E-4,6.7044105996274E-2,79.812954455977746,75.594771233165645,0.8592747642970584,1.1445935673511167,"Continue to Monitor"]
["GREENVILLE 12KV","Muhlenberg - 200 N Boggess Ave - Greenville",1615,"Greenville - Hwy 181, 62, 171, SR 189, & Bards Hill Rd - W&S of Substation",97.176148200757581,1838,"2021-10-23",2.7557352388115831E-2,0,2.4388867995487024E-2,5.9232794283565246E-4,0.33590635577284694,0,0.13027453930048891,0.10557540428732606,0.36520308386611511,1.0502068446784505E-2,55.859524562867797,57.865928219642122,0.72927341146068148,0.880822725354376,"Continue to Monitor"]
["GREENVILLE","Muhlenberg - 117 E Depot St - Greenville",1621,"Greenville - College St & E Depot St - NE & S of Substation",4.861442077020202,403,"2021-10-23",0,0,0,0,5.5468341182626901E-3,0,2.9042386185243328E-3,0.94005756148613295,0,5.1491365777080064E-2,44.405389829543502,94.61035478217822,0.35283023148002235,0.60148514851485158,"Trees Trimmed in 2021"]
["POWDERLY","Muhlenberg - Opportunity Way - Greenville",1625,"Greenville - Opportunity Way & N Main St - E of Substation",1.1132544191919187,27,"2021-05-22",0,0,0,0,0,0,0,0,0,1,1.3671428571428572,6.8357142857142863,2.1428571428571429E-2,0.10714285714285714,"Continue to Monitor"]
["ISLAND","McLean - 499 E Main St - Island",1638,"Island - City of Island, Hwy 85, 1412, & Old Island Rd - W & E of Substation",38.404035353535349,615,"2020-11-14",4.401211033864095E-3,0,6.0813336323540405E-2,0,0.82668012259848989,0,1.392315167825372E-3,6.9167227330492631E-2,0,3.7545787545787544E-2,154.84643139178701,101.91824176314819,0.78940220178574516,1.3446442025887919,"Continue to Monitor"]
["CENTRAL CITY","Muhlenberg - 106 Pendleton St - Central City",1648,"Central City - E Reservoir St, N 2nd St, Whitmer St - N of Subst.",12.613588857323229,742,"2020-12-05",9.4048397645519949E-2,0,0,0,0,1.9032047089601045E-2,3.1850882930019621E-2,3.832570307390451E-2,0.81674296926095491,0,14.522154065772336,20.578817052948821,0.1740709881372858,0.18035900207870037,"Continue to Monitor"]
["CENTRAL CITY SOUTH","Muhlenberg - 500 E Second Ave - Central City",1650,"Central City - Everly Borthers Blvd, S R 604, US 431 - E of Subst.",18.57719491792929,781,"2020-12-12",4.4504685265427226E-3,0,0,2.1932165040876007E-3,0.64207880637793768,0,4.3597515421887343E-3,0.129191658306474,0,0.21772609874276933,94.861769005806053,123.18180433574886,0.84040297152756549,2.3521603284812489,"Continue to Monitor"]
["CENTRAL CITY SOUTH","Muhlenberg - 500 E Second Ave - Central City",1651,"Central City - W 2nd Ave, Center St, W Reservoir St - W of Subst.",5.5291054292929296,413,"2020-12-05",2.0721672079539342E-3,0,0.16312339357229672,0,0.69218354619538147,0,5.9375560381756962E-3,7.7307776604435231E-3,0.10765307139014525,2.129948793560342E-2,31.305156895886331,31.74444716575702,0.37702593741616919,0.45486083074889044,"Continue to Monitor"]
["BEECH CREEK 1","Muhlenberg - 169 Beech Creek Browder Rd - Beech Creek",1668,"Beech Creek - Arnold Hill Rd, State Route 1163 - SW of Subst.",21.387310763888888,282,"2018-09-08",2.081853693181818E-2,0,0,6.787109375E-2,2.840909090909091E-3,0,0,0,0,0.90846946022727271,119.28481355056465,79.604130840024553,1.0324222017012294,1.1096032879733353,"Continue to Monitor"]
["BEECH CREEK 1","Muhlenberg - 169 Beech Creek Browder Rd - Beech Creek",1671,"Beech Creek - Beech Creek Browder Rd - NE of Substation",5.0600866477272728,109,"2018-07-21",4.3958752721745204E-3,0.39587527217452034,0,0,5.8748613450556675E-3,0,7.1484326855922103E-3,0.57516125056489054,0,1.1544307957766731E-2,59.585115926001414,16.902664505436629,0.51964561284933397,1.0646449201495074,"Continue to Monitor"]
["CENTERTOWN SOUTH","Ohio - 7526 S R 69 S - Centertown",1683,"Centertown - City of Centertown - N & E of Substation",11.39517692550505,300,"2020-12-19",0,0,0,0,1.1157180550320391E-2,0,0.14271506857258837,0.84550146423497352,0,6.2628664211777669E-4,44.66892347689766,164.54617939867109,0.35854710292137515,1.0299003322259137,"Continue to Monitor"]
["SALEM","Livingston - 266 W Main St - Salem",1704,"Salem - Hayden Ave, Hwy 723, & Jayna Ln - NE/SE of Substation",13.24423974116162,302,"2022-03-08",2.7346350122032393E-2,0,0,0,2.0301752828932772E-2,0,3.4945640115376084E-2,0,0,0.91740625693365874,37.036639966361136,59.519351684673005,0.37206459243654666,1.0695806458382304,"Continue to Monitor"]
["MEXICO","Crittenden - 2747 S R 70 - Crayne",1708,"Crayne - S R 70 & Ken Spar - NE of Substation",8.972474431818183,117,"2021-09-11",0,0,0,0,8.9343379978471471E-2,0,0.31754574811625402,0.59311087190527445,0,0,2.9629080914153754,7.8653954745762702,4.2136117397837056E-2,0.11864406779661017,"Trees Trimmed in 2021"]
["MARION SOUTH","Crittenden - 505 Chappell Hill Rd - Marion",1710,"Marion - Hwy 60, N Main St, Sturgis Rd, & Old Fords Ferry Rd - N & W of Substation",26.692475063131312,900,"2016-10-01",7.5834958368155509E-3,0,2.8889507949773525E-3,0,0.64394713220045197,1.1246272737590408E-3,5.7882192713653389E-3,2.6516441225327846E-3,0.26185243652046514,7.41634939796329E-2,93.078265821993327,107.81180896959495,1.1271208248445612,1.4328830752476767,"Continue to Monitor"]
["MARION","Crittenden - 106 Sparmill Rd - Marion",1715,"Marion - Gum St, Mill Rd, Sturgis Rd/Main St - N of Substation",9.4770326704545464,373,"2016-10-08",0,0,0.1544580709313888,0,0,0,0,0.84554192906861125,0,0,6.4777541375387155,20.517605002680963,8.2940749666324073E-2,0.2359249329758713,"Tree Trim Scheduled for 2022"]
["STURGIS 4KV","Union - 1402 N Washington St - Sturgis",1725,"Sturgis - Cs 2047, 8th St, 3rd St, & 10th St - S of Substation",4.2237103851010112,378,"2020-02-15",0,0,0,0,0,0,0,0.8280683583635422,0,0.1719316416364578,3.3896823544781425,10.213175274406334,4.1591325598404096E-2,8.4607223129650563E-2,"Continue to Monitor"]
["STURGIS 12KV","Union - 1402 N Washington St - Sturgis",1728,"Sturgis - Hwy 60, King St, Hwy 270, & Hwy 143 - S & N of Substation",46.141666351010088,984,"2019-12-06",4.6847190439867785E-2,0,6.5556403085007209E-2,0,1.9916942113738451E-3,0,9.1745063140944147E-2,8.7443851173828288E-2,0.6848461734045258,2.1569624544452919E-2,33.192183314611249,48.010281736557367,0.30765464736626891,0.54290785967930077,"Continue to Monitor"]
["SUNOCO","Union - 2823 S R 130 S - Morganfield",1732,"Morganfield - S R 130 - NE of Substation",4.0988674242424246,31,"2020-02-29",0.11270801815431165,0,0,0,0,0,6.8078668683812403E-3,0.88048411497730716,0,0,66.079025964354827,42.820734745161282,0.66190860215053759,1.0655913978494624,"Continue to Monitor"]
["MORGANFIELD","Union - 305 Rhea St - Morganfield",1750,"Morganfield - S R 947, N Chapman St, & Hedge Rd - NW of Substation",9.2026898674242439,285,"2019-11-23",0,0,0,0,0,0,0,0.80678851174934718,0,0.19321148825065274,4.8512384020150794,8.6104521471455371,4.4408716438122893E-2,4.5357081942447794E-2,"Continue to Monitor"]
["CAMP BRECKINRIDGE","Union - 1820 S Route 2091 - Morganfield",1759,"Morganfield - Marshall Rd, Headquarters Rd, & Patton Rd - NE of Substation",19.562213068181812,256,"2020-01-11",0.97912589693411611,0,0,0,2.0874103065883887E-2,0,0,0,0,0,37.854506598146415,47.724384674367705,0.77243825364796526,0.87553197957198448,"Continue to Monitor"]
["CAMP BRECKINRIDGE","Union - 1820 S Route 2091 - Morganfield",1760,"Morganfield - Routes 56, 2835, and Road A - W and E of Substation",24.573024305555546,511,"2019-12-21",2.325722859807778E-2,0,4.9677602498073726E-3,0,2.8954945456020113E-2,0,4.0553144896386716E-3,0,8.3620584776349399E-2,0.8551441664301066,25.492405367598277,96.204686000834684,0.32639927474470415,1.1979434664196527,"Continue to Monitor"]
["MORGANFIELD INDUSTRIAL","Union - 3324 U S HWY 60 E - Morganfield",1761,"Morganfield - Hwy 60 E - W of Substation",3.9909398674242413,39,"2020-01-18",0,0,0,0,0,0,0,0,1,0,29.6459829025641,85.516666666666666,0.45628205128205135,1,"Continue to Monitor"]
["ECHOLS","Ohio - 5590 S R 1245 - Rockport",1903,"Rockport - Hwy 1245, Hwy 62, & City of Rockport - NW & SE of Substation",14.140542771464645,323,"2020-12-05",6.9597895527996993E-3,0,4.0240511086057876E-2,9.1694851559564073E-4,4.1187523487410749E-3,0,0,2.6110484780157834E-2,0,0.92165351371664783,151.3918275002984,150.54364511728397,0.68053732420395896,1.0772273821809428,"Continue to Monitor"]
["RIVERVIEW","Ohio - 25 Riverview Rd - McHenry",1907,"McHenry - Watts Rd, City of McHenry, & HWY 62 - E & S of Substation",24.332970486111108,512,"2018-03-31",1.0070606768122874E-3,0,0,3.156206925651917E-3,0.27952966328166756,0,8.1014937129033162E-4,0.12879124588596022,0,0.58670567385861772,93.127004680057993,316.30896034486346,0.76148439187003358,2.1326373956128974,"Continue to Monitor"]
["BEAVER DAM","Ohio - 310 Ridgecrest Dr. - Beaver Dam",1916,"Beaver Dam - Main St. - S of Substation",33.330997948232323,923,"2019-05-25",0.10282714054927303,0,0,0,2.1970920840064618E-3,0,0,5.8255250403877218E-2,1.0452342487883683E-2,0.82626817447495959,41.926457143978027,67.096439823563159,0.5925892123284251,1.1502943127466134,"Continue to Monitor"]
["ATOKA","Boyle - 20 Parksville Cross Pike - Danville",2100,"Danville - Parksville Cross Pike & Lebanon Rd - S of Substation",15.08259138257576,278,"2020-10-10",2.3355068168346177E-2,0,3.0823947836395968E-3,0,0.46413752222880855,0,1.7308832246591584E-2,0.46105512744516897,0,3.106105512744517E-2,20.216629470911744,16.201376529589229,0.18883026398682484,0.21866377865449577,"Continue to Monitor"]
["ATOKA","Boyle - 20 Parksville Cross Pike - Danville",2102,"Danville – Parksville Cross Pike & Lebanon Rd - S of Substation",12.70139962121212,209,"2020-10-10",1.7122114923635367E-2,0,6.2324498322032735E-3,0,4.0887610437641261E-2,0,1.0615711252653927E-2,1.5615368810355456E-2,1.9930141771111569E-2,0.88959660297239918,48.559347394369283,68.746579889111402,0.40113938992191711,1.0620191149999081,"Continue to Monitor"]
["BUENA VISTA","Garrard - 164 High Bridge Rd. - Lancaster",2106,"Lancaster - Kennedy Bridge Rd, Ashley Camp Rd, & Chminey Rock Rd - W of Substation",30.354517361111117,1172,"2017-06-03",5.068479701536498E-3,0,6.6066139773861537E-3,6.2993962004810763E-2,1.3098686040613289E-2,3.7185214275195131E-3,1.0824210888027097E-2,0.34439480961497548,5.4816487490386666E-4,0.55274655147022733,69.012666088158582,204.19826740005647,0.61994567953933744,1.6987291752679341,"Tree Trim Scheduled for 2022"]
["DANVILLE INDUSTRIAL","Boyle - 1866 S Danville Bypass - Danville",2119,"Danville - Crosses S Danville Bypass and Stops - W of Substation",0.18483980429292929,1,"2021-08-07",0,0,0,0,0,0,1,0,0,0,898.64999979999993,358.249999,0.8,2,"Continue to Monitor"]
["DANVILLE INDUSTRIAL","Boyle - 1866 S Danville Bypass - Danville",2122,"Danville - Crosses S Danville Bypass - NW of Substation",0.6197280618686869,3,"2021-08-07",0.14545454545454545,0,0,0,0,0,0,0.8545454545454545,0,0,11.734444399999999,55.011111,0.33333333333333331,1.3333333333333333,"Trees Trimmed in 2021"]
["DANVILLE NORTH","Boyle - 514 N Danville Bypass - Danville",2123,"Danville - Harrodsburg Rd, Maple Ave, Lexington Ave, & Springhill Rd - N & E of Substation",22.781509469696964,1214,"2020-12-26",9.2592002548988375E-2,0,2.1634538792416759E-2,0,2.0742392862832564E-2,0,0.15086824916361319,0.65977377728214104,0,5.4389039350007967E-2,21.738107411784636,17.843618590949525,0.24193852644176378,0.3853653473582998,"Continue to Monitor"]
["DANVILLE NORTH","Boyle - 514 N Danville Bypass - Danville",2124,"Danville - Whirlaway Dr, War Admiral Dr, & Bluegrass Pike - W of Substation",6.7379625946969703,421,"2021-03-27",0,0,0,0,0.57534246575342463,0,5.1181695017311457E-2,0.15444829143459279,0,0.2190275477946711,30.359063979682908,15.779320468372527,0.21332343538323517,0.22089698416093481,"Continue to Monitor"]
["HARRODSBURG 1","Mercer - 231 N Chiles St - Harrodsburg",2126,"Harrodsburg - W Broadway St, Chiles St, & Hill St - W of Substation",3.9314960542929303,484,"2021-11-06",0,0,0,7.4087459342247919E-2,0.19371160101192628,0,7.9869895193350193E-2,0,0.65233104445247558,0,10.841865580088534,11.432152817532405,0.14736294346822026,0.19418947405332998,"Continue to Monitor"]
["HARRODSBURG 1","Mercer - 231 N Chiles St - Harrodsburg",2127,"Harrodsburg - Factory St, N Main St, & Greenville St - N/E/S of Substation",2.248011521464647,310,"2021-11-06",0,0,0,0,0,0,0.1202000357206644,0.8797999642793356,0,0,8.7729055710360804,36.121075267741929,0.16063593035970908,0.72580645161290325,"Trees Trimmed in 2021"]
["HARRODSBURG 2 12KV","Mercer - 709 E Office St - Harrodsburg ",2130,"Harrodsburg - Beaumont Ave, S College St, & Perryville St - SW of Substation",20.308938289141423,1101,"2021-09-11",4.4143217061140487E-2,0,8.3425002661367584E-2,0,0.44895496966040949,0,0.15109470920123486,0.26925943011248715,0,3.1226713033604202E-3,20.756978350389762,19.860294826328044,0.21761916792644706,0.3097027989873416,"Trees Trimmed in 2021"]
["HARRODSBURG 2 12KV","Mercer - 709 E Office St - Harrodsburg ",2131,"Harrodsburg - Lexington Rd, Burgin Rd, & City of Burgin - NE/SE of Substation",42.674016256313138,824,"2021-10-23",1.2719388808589718E-2,0,1.6167664670658683E-2,0,1.0943629981416477E-3,0,2.8659921536237868E-2,0.89787321907908324,0,4.3485442907288868E-2,40.006735252957725,57.950377997122871,0.72040734909405668,1.0716235948342741,"Trees Trimmed in 2021"]
["HARRODSBURG 3","Mercer - 1020 N College St - Harrodsburg",2132,"Harrodsburg - Louisville Rd, Virginia Ave, & Sleepy Hollow Rd - N of Substation",24.636888257575762,721,"2022-01-15",4.6644051369033199E-2,0,0,0,1.4150714804943058E-2,0,7.734431790646959E-2,0.85788708504967293,0,3.9738308698812697E-3,44.115366171629532,55.805294394017579,0.51627627264095144,0.6604164561249074,"Trees Trimmed in 2022"]
["HARRODSBURG 3","Mercer - 1020 N College St - Harrodsburg",2133,"Harrodsburg - N College St, Lynn Dr, & Cornishville St - S of Substation",6.3659578598484838,493,"2016-11-26",7.0435172723194259E-2,0,6.9986541049798109E-2,0,0.62079407806191123,0,1.727231942575146E-2,0.14535666218034993,0,7.6155226558995065E-2,12.650696624490772,16.814623707890767,0.13611369568587586,0.17033696834376436,"Continue to Monitor"]
["HARRODSBURG 3","Mercer - 1020 N College St - Harrodsburg",2134,"Harrodsburg - Tapp Rd, Moberly Rd, & Mackville Rd - SW of Substation",20.033958806818184,962,"2022-04-01",2.0516749670114503E-2,0,0.37934703954369386,0,4.9532484853644351E-2,0,1.3592701372039898E-2,2.8661019594489138E-3,2.0644447282169156E-2,0.51350047531888932,36.826438842899734,72.96230793752774,0.80051538272483991,1.934323447682923,"Continue to Monitor"]
["LANCASTER 1","Garrard - 104 Hamilton Ave - Lancaster",2141,"Lancaster - Richmond St, Cowden Ct, & Hamilton Ave - N/E/SE of Substation",4.9807678345959605,364,"2018-02-03",0,0,0,0,3.9599380926120295E-2,0,7.4431181399320437E-2,0.88596943767455938,0,0,15.248990359008321,19.046750330468161,0.3099693392448819,0.2278112298660244,"Continue to Monitor"]
["LANCASTER 2","Garrard - 183 Industry Rd - Lancaster",2143,"Lancaster - Crab Orchard St & Richmond St - NE of Substation",3.7186786616161629,110,"2018-02-24",0,0,0,0,0.11420184512161029,0,3.8020687727145654E-2,0.84777746715124402,0,0,20.289302748657214,65.029999981818179,0.18023352793994996,0.77272727272727271,"Continue to Monitor"]
["PINE HILL","Rockcastle - 501 Flat Rock Rd - Mt. Vernon",2149,"Mt. Vernon - Wilderness Rd, Limestone - W of Substation",8.1941392045454542,78,"2020-07-25",0,0,0,0,0.14221478902201629,0,0,0.85778521097798366,0,0,357.26056578199501,464.73695417483793,2.1338920418883367,2.9020006364943076,"Continue to Monitor"]
["SALVISA","Mercer - 4455 Louisville Rd - Salvisa",2150,"Salvisa - Main St, Louisville Rd, & Talmage Rd - NW & SW of Substation",38.894541824494944,689,"2022-01-15",3.423464665664839E-3,0,0.95299702437228184,0,2.6223341261705963E-2,0,3.632455241185076E-3,1.5226456216474429E-3,4.7669755082949353E-3,7.4340933292198676E-3,63.852501282454412,145.21383560306984,0.67236993434182935,1.1144774071458818,"Continue to Monitor"]
["SHAKERTOWN","Mercer - 3499 Lexington Rd - Harrodsburg",2151,"Harrodsburg - Shakertown Rd, HWY 342, & Handy Pike - S of the Substation",31.363482796717172,319,"2017-02-28",1.4104810272559934E-2,0,7.2298241334190858E-3,0,0.47790024616885851,0,0,0.47171275864363177,0,2.9052360781530683E-2,69.740717257476561,77.333037395129409,0.68149251003045008,1.1128661593595552,"Tree Trim Scheduled for 2022"]
["SHAKERTOWN","Mercer - 3499 Lexington Rd - Harrodsburg",2152,"Harrodsburg - Lexington Rd & Sexton Rd - SW of the Substation",12.969067077020203,70,"2017-02-28",0,0,0.73551684967815223,0,0,0,0,4.7141234380916316E-2,0,0.21734191594093147,41.397445737388772,73.932136131388333,0.20748267382070198,0.56519114688128769,"Continue to Monitor"]
["WEST CLIFF","Mercer - 815 Dix Dam Rd - Burgin",2160,"Burgin - Dix Dam Rd - NW of Substation",1.823347222222222,20,"2022-02-15",0,0,0,0,0,0,0,0,0,1,1.3088333266666665,6.2108333,1.9523809523809523E-2,0.05,"Continue to Monitor"]
["RICHMOND NORTH","Madison - 2236 Lexington Rd - Richmond",2170,"Richmond - Lexington Rd - N of Substation",36.127470643939397,816,"2018-09-17",9.3596179747765393E-2,0,0.12139096363413739,1.1313823925554059E-2,0.21288110689359618,0,0.10645279784498592,0.45436512795396106,0,0,25.588538834433383,24.266129328911848,0.20704547552765687,0.25885905715896579,"Continue to Monitor"]
["RICHMOND NORTH","Madison - 2236 Lexington Rd - Richmond",2171,"Richmond - Jacks Creek Rd, N Keeneland Dr, and Foxhaven Dr - SE of Substation",20.211800820707069,2075,"2019-06-22",1.2983011787613455E-2,0,0,0,0.1630979302355674,0,0.22817319719759194,0.28160873503441392,0,0.31413712574481328,31.093914888912572,55.309533788571208,0.35906769835549879,0.732932341863201,"Continue to Monitor"]
["CAMPBELLSVILLE 1","Taylor - 101 Old Greensburg Rd. - Campbellsville",2204,"Campbellsville - New Columbia Rd - S of Substation",15.175561237373733,200,"2019-08-10",0,0,0,0,1.214619603224263E-3,0,2.7126504472008539E-2,0.85185321506128309,1.1226029666163642E-2,0.10857963119732048,39.780673707521622,135.80601768820216,0.5466080725254916,2.1835651027414293,"Continue to Monitor"]
["CAMPBELLSVILLE 1","Taylor - 101 Old Greensburg Rd. - Campbellsville",2205,"Campbellsville - HWY 3350 Bypass - N of Substation",17.285738952020203,1239,"2019-12-31",0.10650377654990623,1.9009479393724337E-2,0,0,2.8640948953211336E-2,0,7.8420438992244129E-2,0.14396512394180563,0,0.62346023216910829,28.602921258000464,15.528609806792218,0.40605754537471961,0.43706633466464706,"Continue to Monitor"]
["LEBANON EAST","Marion - 541 Corporate Dr. - Lebanon",2207,"Lebanon - Corporate Dr - SE of Substation",0.13525410353535353,1,"2019-10-05",0,0,0,0,0,0,1,0,0,0,84.976666600000001,424.88333299999999,0.2,1,"Continue to Monitor"]
["COLUMBIA SOUTH","Adair - 1139 Gaston Ave - Columbia",2209,"Columbia - KY 55, Tutt St, Bomar Hts, Hwy 61/80, & Greensburg St - NW & S of Substation",16.146260101010103,881,"2019-03-23",0.17317991776372621,0,0,0,9.2014788708061235E-2,0,0.12936664247952731,0,0.57302788431636775,3.2410766732317471E-2,22.814247945297033,32.767730073059816,0.26470626268966291,0.40990602321891523,"Continue to Monitor"]
["COLUMBIA","Adair - 114 Lindsey Wilson St - Columbia",2211,"Columbia - Burkesville Rd & Greensburg St  - W of Substation",4.385169191919192,457,"2019-03-23",7.6467910787437416E-3,0,0,0,0,0,0.36003641329085112,0,0.61511151570323164,1.7205279927173418E-2,28.930512199394151,24.031093866028687,0.34807431526302912,0.35441411139671103,"Continue to Monitor"]
["GREENSBURG","Green - 424 Old Hodgenville Rd - Greensburg",2212,"Greensburg - City of Greensburg - SE of Substation",8.68726546717172,673,"2019-11-09",2.327784706898206E-2,0,0,0,0.88609325530077709,0,3.614602321788353E-2,0,3.6445840928715341E-2,1.8037033483641947E-2,35.884385278118415,123.72177784493719,0.37862932549608719,1.1573175066651276,"Continue to Monitor"]
["GREENSBURG","Green - 424 Old Hodgenville Rd - Greensburg",2213,"Greensburg - US 68, Cemetery Rd, Valley Dr, & E Columbia Ave - SE of Substation",11.072835542929296,492,"2019-11-09",2.641590184982643E-2,0,8.0484093394835698E-2,0,0,0,1.9259118360359505E-2,0.86630367587617108,0,7.5372105188073616E-3,41.254680019005676,85.06993289489067,0.71413159270258475,2.1318228251661635,"Continue to Monitor"]
["GREENSBURG","Green - 424 Old Hodgenville Rd - Greensburg",2214,"Greensburg - Buckner Hill Rd, Hawthorne Rd, HWY 1464, & HWY 88 - SW of Substation",19.850776672979801,211,"2019-12-31",1.2628804656185369E-3,0,2.3793400076870985E-3,0,2.7636949320057834E-3,0,5.8934421728865059E-3,0.98446107948825889,0,3.2395629335432033E-3,120.22816108939662,256.54318081480858,0.47552097568111512,1.056717238661034,"Continue to Monitor"]
["LEBANON SOUTH","Marion - 1157 Bradfordsville - Bradfordsville",2218,"Bradfordsville - Bradfordsville Rd, Hwy 49, & Central Ave - SE of Substation",29.963905934343426,386,"2020-04-11",2.9230077394617878E-3,0,0.23853873281105772,0,0,0,1.2780762585500934E-3,0.72949752668575885,0,2.7762656505171474E-2,185.78476570007231,214.95926542503656,1.6929192331494509,3.349563752443617,"Continue to Monitor"]
["SPRINGFIELD","Washinton - 107 Commercial Ave - Springfield ",2226,"Springfield - State HWY 55 & Bloomfield Rd - S & N of Substation",37.772156249999988,383,"2020-06-27",1.6648781235627779E-2,0,2.1462517246665647E-3,0,0,0,1.9316265521999081E-3,0.71234094741683274,8.6187337114824472E-2,0.18074505595584853,37.515777822875734,50.78378310853045,0.24446318450167021,0.4785818395187616,"Continue to Monitor"]
["SPRINGFIELD","Washinton - 107 Commercial Ave - Springfield ",2227,"Springfield - Main St - SE of Substation",5.6266483585858582,617,"2020-06-20",0.11955770559778853,0,0,0.2994701681640175,0,0,0.18290716424786915,0.21055056438608616,0,0.18751439760423866,5.5883077334013347,7.0046373763046015,9.6034019262891707E-2,6.7793195410203469E-2,"Continue to Monitor"]
["UNION UNDERWEAR","Russell - 101 Fruit Of The Loom Dr - Jamestown",2230,"Jamestown - Geneva Dr, Shawnee Ave, & Comanche Way - N of Substation",5.7467315340909098,183,"2018-12-29",3.6085084831602937E-3,0,3.8617371486452268E-3,0,0,0,0,0.98183084325145609,0,1.0698911116738414E-2,74.576161909149931,86.319125672131136,0.65365268695756651,0.80327868852459028,"Continue to Monitor"]
["WOODLAWN","Nelson – 285 Spencer Mattingly Ln. – Bardstown ",2232,"Bardstown - My Old KY Home St Park &  Gilkey Run Rd - SW of Substation",6.5951068497474754,132,"2018-10-13",0,0,1.2778700189753321E-2,0,0.98656902277039848,0,0,0,0,6.5227703984819738E-4,139.1542996134595,253.5868382903281,1.1324357910737985,2.0452267031214402,"Continue to Monitor"]
["RICHMOND 1","Madison - 315 Clay Dr - Richmond",2237,"Richmond - Westover Ave, Tates Creek Rd, S Keeneland Dr - NW of Substation",7.068460385101007,529,"2019-08-31",3.1244218791753171E-2,0,0,8.4811609693929993E-2,4.0699706057678475E-2,0,1.3299348393594935E-2,0.77204053526280092,8.7771588316306604E-3,4.9127422968611896E-2,20.262735156069038,15.968786836794235,0.17074758459027833,0.19058030459749617,"Continue to Monitor"]
["BEATTYVILLE 4KV","Lee - 950 W Main St. - Beattyville",2301,"Beattyville - W Main St, Lee Ave, & Grand Ave - E of Substation",8.1621693497474723,228,"2020-11-21",0,0,0,0,0.22537131376910383,0,5.668364784386884E-3,0.76896032144650939,0,0,34.463899212343179,58.377336953015693,0.24263313733146613,0.41959915649984869,"Continue to Monitor"]
["IRVINE","Estill - 83 River Dr - Irvine",2303,"Irvine - River Dr, Broadway Ave, & KY 89 - NW of Substation",11.451395991161613,896,"2020-12-12",2.7899852294899614E-3,0,0,0,5.6816316854793117E-2,0,3.5239519320191836E-3,3.405423147759806E-3,0,0.93346432283593794,168.49187957509918,244.24026570563427,1.0227538630175499,1.1393335924657819,"Continue to Monitor"]
["OKONITE","Madison - 1742 Berea Rd - Richmond",2307,"Richmond - 0.00 miles",1.2705176767676767E-3,1,"2019-09-28",0,0,0,0,1,0,0,0,0,0,1860.5666666000002,9302.8333330000005,0.2,1,"Continue to Monitor"]
["PAINT LICK","Garrard - 11811 HWY 52 E - Paint Lick",2309,"Paint Lick - HWY 52, Kirksville Rd, & Curtis Pike - N of Substation",18.009104008838385,313,"2020-04-18",1.9413853212613757E-3,0,0.13228821118541104,1.3817066700869251E-3,2.8508631294198582E-2,0,5.2120074390620717E-3,0.71598640447276518,9.7302465501058144E-2,1.737918811615664E-2,179.62009760411814,269.73439750840078,1.2125483721057693,2.8621181122452977,"Continue to Monitor"]
["RICHMOND EAST","Madison - 1799 Irvine Rd - Richmond",2318,"Richmond - E Irvine St, Bluegrass Dr, &E Main St - W of Substation",5.8404607007575757,746,"2019-01-19",0,0,0,0,0.33424657534246577,0,0,0.31819274212929582,0,0.34756068252823841,38.551334185833767,115.33013851340485,0.36149847015173747,1.0120643431635388,"Continue to Monitor"]
["RICHMOND EAST","Madison - 1799 Irvine Rd - Richmond",2319,"Richmond - Irvine Rd, Reba Rd, & Charlie Norris Rd - E of Substation",35.975049400252523,1371,"2018-12-29",6.804643863586507E-3,0,2.0713454042287508E-3,1.2444946929683941E-3,0.29729501695887683,0,1.614468199996625E-2,0.63711378478257197,0,3.9326032297801253E-2,30.990761380355025,36.210889754178403,0.41337572377410658,0.36348734187294324,"Continue to Monitor"]
["RICHMOND EAST","Madison - 1799 Irvine Rd - Richmond",2320,"Richmond - DR Martin BYP, Commercial Dr, & Berea Rd - SE of Substation",20.836019886363637,1467,"2019-01-19",0.36474294277762487,0,0,0,4.0064837752699027E-2,0,0.10248646664831636,0.15346973728476618,0,0.33923601553659355,13.638038184302365,18.078818639959604,0.20166373454850789,0.45567999603569648,"Continue to Monitor"]
["RICHMOND SOUTH","Madison - 464 Eastern Bypass - Richmond",2321,"Richmond - Lake Shore Dr, Willis Branch Rd, & Barnes Mill Rd - W of Substation",25.840041982323235,1748,"2019-12-13",1.8724276200738372E-3,0.21713094628252461,0,0,3.8155128861881967E-3,0,5.6208157425235376E-2,0.70850188125982583,1.247107452615216E-2,0,4.4690748218061609,11.299437983754043,2.9565548436974436E-2,3.20315027257028E-2,"Continue to Monitor"]
["RICHMOND SOUTH","Madison - 464 Eastern Bypass - Richmond",2323,"Richmond - S Killarney Dr, Barnes Mill Rd, & Martin Dr - NW of Substation",5.3206096906565667,658,"2019-12-28",4.8238791864380079E-3,0,0,0.49317765657918056,0.19663706708145465,0,3.0045876075528166E-2,0.16940676130658214,0,0.10590875977081651,19.142643894374665,53.518053007820171,0.3696525426316552,1.297572540138646,"Continue to Monitor"]
["RICHMOND SOUTH","Madison - 464 Eastern Bypass - Richmond",2324,"Richmond - Eastern Ave, Barnes Mill Rd, & Brookview Dr - N of Substation",5.8918587436868677,692,"2019-12-07",0,0,0,0,0.12633785722167054,0,0.44698223546287097,0.10945603001213726,0,0.31722387730332119,7.3252421711983207,11.430436032388291,8.9131384725498253E-2,0.10828141030453167,"Continue to Monitor"]
["ELIZABETHTOWN 3","Hardin - 100 Crucible Steel Rd - Elizabethtown",2332,"Elizabethtown - Leitchfield Rd, Blackbranch Rd, & Nicholas St - SW of Substation",18.619973011363637,895,"2021-01-23",1.2315270935960592E-2,0.11241379310344828,9.29064039408867E-2,0,0,0,0.6370443349753695,0,0,0.14532019704433496,10.862896974822249,11.390179620240323,0.12597675109910414,0.11437658921945645,"Continue to Monitor"]
["BONNIEVILLE","Hart - 8074 N Dixie Hwy - Bonnieville",2401,"Bonnieville - Follows US 31  - N of Substation",11.935304608585859,158,"2018-08-25",0,0,2.6692891261590336E-2,0,0.64582747962910925,0,1.4048890137679123E-3,0.27802753582466982,0,4.8047204270862599E-2,12.145572721863887,44.86976554203487,0.10112161803836432,0.24576068784332458,"Continue to Monitor"]
["BOSTON","Nelson - 1100 Old Nelsonville Rd. - Boston",2403,"Boston - Lebanon Junction Rd, Boston Rd, KY 52 & Nelsonville Rd - SE of Substation",30.083245580808068,351,"2021-07-03",6.7592293617479288E-2,0,3.3096545043590571E-3,7.3727262942632652E-3,0.36010655473038422,0,2.0718975352491658E-3,4.3805833602410936E-2,0,0.51574103971585405,77.902229730355344,105.6443339809213,0.71171041232101451,1.0487073878539883,"Continue to Monitor"]
["CLARKSON","Grayson - 405 Peonia Rd - Clarkson",2405,"Leitchfield - Farmview Ln, Hwy 3155, & Grayson Springs Rd - W of Substation",7.4340029987373724,140,"2021-09-11",0,0,0,0,0.15772251308900523,3.5994764397905762E-2,0,0.75719895287958117,0,4.9083769633507857E-2,5.1236824531580822,10.914841545786228,5.7460895730829666E-2,7.8622816032887982E-2,"Trees Trimmed in 2021"]
["EASTVIEW","Hardin - 12540 Sonora - Hardin Springs",2407,"Sonora - KY 84, Main St, & White Mills Rd - SE of Substation",14.775257575757577,268,"2019-09-21",0.11238532110091744,4.2660550458715599E-2,5.321100917431193E-2,0,0,0,0.23211009174311928,0.55963302752293576,0,0,26.171217711815405,8.1038372178188975,0.17806006052411369,0.24545025800366199,"Continue to Monitor"]
["ELIZABETHTOWN 2","Hardin - 1011 Woodland Dr - Elizabethtown",2410,"Elizabethtown - Dixie Hwy, Grays Rd, & Diecks Dr - E & NW of Substation",15.664230429292925,1387,"2021-02-13",1.0618316596128321E-2,2.9300543437429565E-3,0,0,6.636447872580201E-3,0,5.0837695023916253E-2,0.92897748616363218,0,0,23.634926628269753,23.674685367630126,0.43798094119246933,0.10279167384180186,"Trees Trimmed in 2021"]
["ELIZABETHTOWN 2","Hardin - 1011 Woodland Dr - Elizabethtown",2413,"Elizabethtown - Long Ave, Saint John Rd, & College Street Rd - S of Substation",11.684357796717171,886,"2021-03-27",0.11565315987348571,0,0,0,0.58960434445306442,0,0.13448111237094945,0.13821089693859281,1.2323208211493705E-2,9.7272781524139172E-3,24.879264786288481,37.77549428861979,0.44459086628683231,1.2257854727684168,"Continue to Monitor"]
["ELIZABETHTOWN 2","Hardin - 1011 Woodland Dr - Elizabethtown",2414,"Elizabethtown - Woodland Dr, Ring Rd, & N Dixie HWY - N of Substation",17.549882417929304,1325,"2021-03-20",0.38229303069983994,0,4.9105194238323879E-3,9.9301615015277168E-3,0.37603666521169793,0,0.1313473010330278,3.8447548377709882E-2,0,5.7034773752364328E-2,18.841961876070382,20.776318466668453,0.27220461854380412,0.35896130203207371,"Continue to Monitor"]
["ELIZABETHTOWN 2","Hardin - 1011 Woodland Dr - Elizabethtown",2415,"Elizabethtown - Woodland Dr, Saint John Rd, & Westport Rd - S of Substation",8.6918481691919176,549,"2021-04-03",2.3165615992125799E-2,0,0,0,0,0,1.4061071922382882E-3,0.55168615687469247,0,0.42374211994094352,35.638326616164093,69.563303025454545,0.73098773666045103,1.0363636363636364,"Trees Trimmed in 2021"]
["ELIZABETHTOWN 4","Hardin - 201 Sportsman Lake Rd - Elizabethtown",2417,"Elizabethtown - Hodgenville Rd - NE of Substation",0.36991351010101015,6,"2020-05-16",0,0,0,0,0,0,0,0,1,0,9.7244444333333337,48.622222166666667,0.13333333333333333,0.66666666666666663,"Continue to Monitor"]
["ELIZABETHTOWN 5","Hardin - 800 N Mulberry St - Elizabethtown",2421,"Elizabethtown - N Mulberry Ave, Quince Aly, & Wall St - SW of Substation",4.5105378787878783,699,"2020-10-17",0,3.5186418109187746E-2,0,0,0.17643142476697737,0,0.72170439414114518,4.6271637816245006E-2,0,2.0406125166444741E-2,36.864738560345252,42.953295880511803,0.64591266006660053,0.44758860149277263,"Continue to Monitor"]
["ELIZABETHTOWN 5","Hardin - 800 N Mulberry St - Elizabethtown",2423,"Elizabethtown - Brooks Str, N Main St, & Guthrie St - S & E of Substation",5.589771938131312,565,"2020-11-14",5.579680260061619E-3,0.38247495208752819,0,0,2.7364692753693506E-2,1.3512530021105747E-2,0.56386307949831393,0,7.2050653792969602E-3,0,54.307333750811232,72.706608865101586,0.86666853553373124,1.578791864795932,"Continue to Monitor"]
["ELIZABETHTOWN 5","Hardin - 800 N Mulberry St - Elizabethtown",2424,"Elizabethtown - Joan Ave, McCullum Ave, & Bellwood Dr - NW of Substation",6.3867851957070698,574,"2020-10-24",3.0481270687971805E-3,0.63608220417688666,0,4.1316409877836781E-2,0,0,0.30128830995642131,1.8264948920058102E-2,0,0,36.468614201658596,73.045101235833002,0.47829628176367728,1.2679903417554714,"Continue to Monitor"]
["HODGENVILLE 4KV","Larue - 500 W High Ave - Hodgenville",2429,"Hodgenville - Tonieville Rd, N Lincoln Blvd, & Phillips Ln - NE of Substation",7.5174285037878796,374,"2017-06-17",0,0,0,0,0.1948173005219985,0,0.60085756897837439,0,0,0.20432513049962714,7.779935974579165,14.318354654908919,8.841437757036652E-2,0.15756172671359553,"Continue to Monitor"]
["HORSE CAVE","Hart - 501 Shewey Ave - Horse Cave",2433,"Horse Cave - W Main St, KY 335, New St, US 31 - N & NW of Substation",22.708441603535352,885,"2018-11-10",0,1.3784753433740149E-3,3.4540503851082731E-3,0,5.7340381203466635E-3,0,1.9550239660779756E-3,0.91020779336497359,1.2479657005983002E-2,6.4790961814136447E-2,32.617376981474521,38.927960722506668,0.28174629487063374,0.27123441550549487,"Continue to Monitor"]
["MILLWOOD","Grayson - 6649 Beaver Dam Rd - Millwood",2440,"Caneyville - US 62, Hwy 79, & River Park Dr - W of Substation",22.049434343434339,425,"2021-10-16",5.4166568110320034E-3,0,2.1761241336897131E-3,0,4.8016652080327363E-2,0,0,2.8076732029235756E-2,0,0.91631383494571517,48.83194317260849,99.162507427905609,0.45717771445823718,0.95057176949972122,"Continue to Monitor"]
["MILLWOOD","Grayson - 6649 Beaver Dam Rd - Millwood",2441,"Millwood - US HWY 62, School House Rd, & Rock Quarry Rd - NE of Substation",11.659314236111108,171,"2021-10-02",0,0,0,0,0.40033500837520936,0,0,0,0,0.59966499162479059,2.7907761595065415,3.4831169689655175,3.9659893683577266E-2,2.9006085192697768E-2,"Continue to Monitor"]
["MUNFORDVILLE","Hart - 75 Gorin Mill Rd - Munfordville",2442,"Munfordville - Mill St, KY 88, US 31 W, & HWY 571 - SE of Substation",25.115490845959599,503,"2019-01-12",4.2205501998589232E-2,4.0559604984716667E-3,0.21490712438278861,0.11591817540559606,3.9383964260521986E-2,0,3.0213966611803433E-2,0.54602633435222203,0,7.2889724900070535E-3,39.691711068040632,33.76778717429945,0.29472951179261186,0.32561772223800056,"Continue to Monitor"]
["MUNFORDVILLE","Hart - 75 Gorin Mill Rd - Munfordville",2443,"Munfordville - City of Munfordville & US 31 - E & N of Substation",16.109964488636358,978,"2019-02-23",1.3275438658931559E-2,0,2.4023917144179092E-3,0,0,0,1.9005587785172796E-2,0.96138377762750471,0,3.9328042139730223E-3,43.823671665472588,57.180895224071293,0.31724988870709336,0.61165076803878227,"Continue to Monitor"]
["NEW HAVEN","Nelson - 256 Lyons Station Rd - New Haven",2446,"New Haven - Cissal Hill Rd & US 31 - SSW of Substation",8.0994725378787873,48,"2018-01-13",0,0,0,0,0.28735325506937032,0,0.201974386339381,0.51067235859124871,0,0,88.583273873737042,76.469047591836741,0.51082830490686837,0.5714285714285714,"Continue to Monitor"]
["RIO","Hart - 301 Glen Lily Rd E - Munfordville",2451,"Munfordville - E US 31, S Jackson HWY & J McGuire Rd - S of Substation",16.712055239898991,256,"2020-03-14",9.9091659785301399E-3,0,1.6011126081098701E-2,0,0.93581641966187146,0,3.8263288278499716E-2,0,0,0,76.415640763476461,117.82103183698072,0.53232041142258768,0.80823107939750383,"Continue to Monitor"]
["SONORA","Hardin - 1340 Old Sonora Rd - Sonora",2456,"Sonora - US 31 W, S Dixie Hwy, & Sonora Rd - E of Substation",12.708478377525251,197,"2018-02-24",0,0,4.1264300950164826E-2,0,1.9119643203412837E-2,0,0.91301144076013185,2.3346907116540624E-2,0,3.2577079697498545E-3,52.323538608716873,130.39723471741931,0.50810683039594995,1.1567740989210007,"Continue to Monitor"]
["ELIZABETHTOWN INDUSTRIAL","Hardin - 111 Ring Rd - Elizabethtown",2464,"Elizabethtown - N Black Branch Rd & Enterprise Dr - N of Substation",1.3861895517676766,18,"2020-11-14",0,0,0,0,7.5927523727351162E-2,0,0.58843830888697157,0,0,0.33563416738567731,18.415740733333333,64.414814777777778,0.22222222222222218,0.61111111111111105,"Continue to Monitor"]
["LEITCHFIELD EAST","Grayson - 705 Wallace Ave - Leitchfield",2465,"Leitchfield - Mill St, Lee Ave, & Grayson Springs Rd - N of Substation",6.3481682449494974,382,"2021-08-28",1.6357688113413305E-2,0,0,0,0.95045957314223395,0,2.7574388534039571E-2,0,0,5.608350210313133E-3,16.2366996729932,33.580395238296788,0.17956608653362277,0.44985855131254576,"Continue to Monitor"]
["LEITCHFIELD EAST","Grayson - 705 Wallace Ave - Leitchfield",2466,"Leitchfield - Wallace Ave, Bobby Bland Way, Clinton St, & White Oak St - S & W of Substation",4.4263478535353533,230,"2021-08-28",0,0.1102803738317757,0.50560747663551397,0,0,0,9.3224299065420568E-2,0.17079439252336448,0,0.12009345794392523,5.391749029015477,18.577804436156597,6.4250669887050679E-2,0.25627705627705627,"Continue to Monitor"]
["HODGENVILLE 12KV","Larue - 500 W High Ave - Hodgenville",2467,"Hodgenville - Hwy 61, Glendale Rd, & Railroad Dr - NW of Substation",7.5497242739899013,42,"2017-06-24",2.6906707108262807E-3,0,0.87642483244459668,0,0,0,0,0,0,0.12088449684457707,104.38976894023094,475.3927301474759,0.42532570891125793,1.5592739648326717,"Continue to Monitor"]
["LA GRANGE E 12KV","Oldham - 1810 E Highway 146 - La Grange",2472,"La Grange - Jericho Rd, Adams St, 1st St, Hwy 53, & Zale Smith Ln - S of Substation",29.880997790404038,940,"2021-01-16",1.3352866303225342E-2,2.6897860179158962E-3,5.285909844136507E-2,0,5.0649631355219868E-2,0,0,0.10264415571939768,0,0.77780446216287613,30.370844898259556,43.734318379885416,0.3049330769334172,0.48852059263821196,"Continue to Monitor"]
["BLACK BRANCH ROAD","Hardin - 1220 N Black Branch Rd - Elizabethtown",2479,"Elizabethtown - N BlackBranch Rd - E of Substation",4.9898085542929298,27,"2019-05-18",0,0,0.91624713958810067,0,0,0,8.3752860411899319E-2,0,0,0,27.954346525670495,78.28641974074074,0.32837803320561937,0.53703703703703698,"Continue to Monitor"]
["EMINENCE","Henry - 1257 Ballardsville Rd - Eminence",2500,"Eminence - Jim Doyle Rd, Mulberry Pike, & Hill Spring Rd - SE of Substation",39.290397569444437,582,"2021-12-18",9.9281308756084281E-3,0.41736807886274579,4.4597515331494142E-2,0,0.21024793969319441,0,2.117415523027992E-2,7.3573599957827404E-2,6.3786044386652373E-3,0.21673197561018467,62.555632249024725,55.671849117780013,0.74617678115741859,0.81305130555112126,"Continue to Monitor"]
["EMINENCE","Henry - 1257 Ballardsville Rd - Eminence",2501,"Eminence - City of Eminence, Hwy 22, & Castle Hwy - E of Substation",20.337045928030303,1010,"2021-12-04",0,0,0,0,2.3559833357276252E-2,0,0.22403390317483121,0.74867116793564148,0,3.7350955322511133E-3,11.921887288684982,13.78156624679499,0.14478133448335867,9.4013899065560555E-2,"Trees Trimmed in 2021"]
["EMINENCE","Henry - 1257 Ballardsville Rd - Eminence",2502,"New Castle - Jackson Rd, Eminence Rd, & City of New Castle - N of Substation",27.766556344696966,924,"2022-04-12",4.9871942810503507E-2,0,5.6570318876474068E-3,0,5.7949396301820943E-2,0,8.1281134783709991E-2,6.3634572626720329E-2,0.21688103346373588,0.52472488812586193,29.949110795587796,22.616130460243181,0.27740819570644998,0.33885860071892548,"Continue to Monitor"]
["FINCHVILLE 1","Shelby - 198 Parent Ln - Finchville",2504,"Simpsonville - Hwy 55, Buck Creek Rd, & Finchville Rd - NE & SW of Substation",44.95546275252525,544,"2017-03-18",1.9323431523520937E-2,1.162386369281208E-2,3.3530376036957927E-3,0.33130495256072723,2.280065570513139E-2,0,4.7762157865977845E-2,0.32934280462967563,0,0.23448909641845908,107.05598123749704,73.293589585833885,0.69761373599982301,0.83546465825300675,"Tree Trim Scheduled for 2022"]
["FLORIDA TILE","Anderson - 1247 Alton Rd - Lawrenceburg",2505,"Lawrenceburg - Alton Rd - N of Substation",15.928308238636365,643,"2016-05-21",1.2873968006113057E-2,0,4.8173557700294028E-3,0,0.35213209521752853,0,2.35552085582817E-2,0.44193425139952491,7.1546038970747017E-2,9.3141082077775383E-2,74.974245890134725,93.46861489181984,0.55675482724810477,0.40211398827307576,"Tree Trim Scheduled for 2022"]
["LA GRANGE E 12KV","Oldham - 1810 E Highway 146 - La Grange",2510,"La Grange - Jefferson St, Jericho Rd, & Walnut Aly - SW of Substation",7.834918876262627,722,"2020-12-19",1.3611803823773898E-2,0,4.8836242726517038E-3,0,0.65949709060681627,0,0.12822111388196175,0.16282211138819619,1.672901080631754E-2,1.4235245220282626E-2,12.262122386188054,13.323016365670098,0.12420253381293711,0.16334690316952602,"Reliability Improvements Scheduled for 2022"]
["LAWRENCEBURG 12KV","Anderson - 108 E Broadway st - Lawrenceburg ",2515,"Lawrenceburg - Fox Creek Rd - SW of Substation",36.150484690656562,1906,"2016-12-03",4.7196083956756252E-3,0,1.2097939534936819E-2,0,1.0255760115313461E-2,0,2.2531548674453971E-4,0.93336429668822296,0,3.9337079779106707E-2,225.95676164864275,822.91487300996152,1.0126782624916346,2.6060845449537839,"Tree Trim Scheduled for 2022"]
["LAWRENCEBURG 12KV","Anderson - 108 E Broadway st - Lawrenceburg ",2516,"Lawrenceburg - Main St - N of Substation",39.094246843434348,2391,"2016-08-13",5.8825884389997344E-3,0,4.7566144715178631E-3,0,7.1232866429461486E-2,0,6.2454022729661156E-3,0.73800587508194582,0,0.17387665330510893,91.420426981823255,294.72444740020478,0.56940183272379519,1.1175538488767425,"Tree Trim Scheduled for 2022"]
["LAWRENCEBURG 12KV","Anderson - 108 E Broadway st - Lawrenceburg ",2517,"Lawrenceburg - Industry Rd & Tyron Rd - NE of Substation",10.63655429292929,176,"2016-10-31",6.7115028475152119E-2,0,3.6203127393235587E-4,0,1.1536265786652185E-2,0,0,0.90828076917721434,3.3905621231741789E-3,9.315343163874848E-3,150.10958309726126,592.12374090704247,0.74196729849160747,2.2049420796425467,"Tree Trim Scheduled for 2022"]
["LAWRENCEBURG 12KV","Anderson - 108 E Broadway st - Lawrenceburg ",2518,"Lawrenceburg - Waterfill Rd - N of Substation",12.621589172979798,995,"2016-07-02",0.315688622754491,0,0,5.5337600660747472E-4,8.0173446211026234E-2,0,1.4714020235391286E-2,0.52992360107371472,0,5.8946933718769357E-2,105.17644874503029,239.6518079831051,0.76408979629706997,1.5993272689413904,"Tree Trim Scheduled for 2022"]
["SHELBYVILLE SOUTH","Shelby - 614 Mack Walters Rd - Shelbyville",2524,"Shelbyville - Old Finchville Rd, KY 55, & US 60 - W of Substation",11.858295296717172,460,"2018-05-25",1.1324273914201972E-2,0,0.47148947508659739,0,0,0,0.15161204369837464,0,0,0.36557420730082602,26.209164412504396,12.903470312096522,0.15443323687171592,0.15668690946662389,"Continue to Monitor"]
["SHELBYVILLE SOUTH","Shelby - 614 Mack Walters Rd - Shelbyville",2525,"Shelbyville - Medical Ave, Shelby House Apt, & Village Ln - N of Substation",3.4478361742424242,466,"2017-08-05",0.3529797429543855,0,1.3257228805306748E-2,0,0,0,7.8907025849185769E-2,1.2148442396135639E-3,0,0.55364115815150838,29.186400065766556,97.21642157910965,0.34895762845564693,1.1759334993704682,"Continue to Monitor"]
["SHELBYVILLE SOUTH","Shelby - 614 Mack Walters Rd - Shelbyville",2526,"Shelbyville - Kentucky St, Old KY 53, Osprey Cove, & Zaring Mill Rd - S & SE of Substation",28.537785353535348,1266,"2017-05-06",6.363272624887005E-2,0,2.2722445330290502E-4,0,6.4956555672460892E-2,0,1.1366162327173576E-2,0.85282276986608574,0,6.9945614321068154E-3,67.942287615696387,157.13777774901797,0.87076697322244867,2.3292509940684454,"Tree Trim Scheduled for 2022"]
["SIMPSONVILLE","Shelby - 6801 Shelbyville Rd - Simpsonville",2527,"Simpsonville - Main St, 3rd St, & Grand Central Dr - NW of Substation",6.716301609848486,313,"2019-04-13",2.3759608665269043E-2,0,0,0,0,0,0.84466407107916541,0.13157632025556554,0,0,15.775970360869419,31.938736310616392,0.15430882370858184,0.23905699924706458,"Continue to Monitor"]
["EMINENCE","Henry - 1257 Ballardsville Rd - Eminence",2535,"Eminence - Giltner Rd, Smithfield Rd, & Hwy 22 - W of Substation",14.008183396464647,238,"2021-12-18",0,0,0.1493617666818369,1.2136185336887502E-3,2.3838935483171879E-3,0,0,5.0300153869492666E-2,0.48967340658388053,0.30706716078278395,108.4325019051001,193.36618729916319,0.83807825319102702,1.7107872437677998,"Continue to Monitor"]
["MID VALLEY SIMPSONVILLE","Shelby - 2860 Veechdale Rd - Simpsonville",2536,"Simpsonville - Veechdale Rd - S of Substation",5.3342803030303025E-3,1,"No Trimming Necessary",0,0,0,0,1,0,0,0,0,0,1629.4583324999999,1254.149999,1.5,2,"Continue to Monitor"]
["MID VALLEY CLARKSON","Grayson - 1960 Peonia Rd - Clarkson",2538,"Clarkson - No Road - W of Substation",5.920612373737374E-3,1,"No Trimming Necessary",0,0,0,0,1,0,0,0,0,0,206.39666660000003,422.85,0.6,1,"Continue to Monitor"]
["Frankfort to Adams","Scott - 900 W Main St - Georgetown",3401,"Georgetown - Frankfort Rd - W of Substation",7.875107796717173,1366,"2019-04-20",0,0,0.27488146358919308,0,0,0,0,0,0,0.72511853641080692,65.854769099315988,196.39238653001465,0.79408585402323928,3.018301610541728,"Continue to Monitor"]
["Reed Minerals Tap (Bevier)","Muhlenberg - 2665 S Route 2107 - Bevier",3405,"Drakesboro - HWY 246, 7th Ave, and HWY 431 - N and S of Substation",9.1595003156565689,1788,"2021-09-23",0,0,0,0,1,0,0,0,0,0,17.053412745403374,15.928970917225952,0.54491641825439463,0.93008948545861303,"Continue to Monitor"]
["Earlington - Oak Hill (Sec 3A)","Hopkins - 202 Russ Hill Rd - Nortonville",3409,"Madisonville/Nortonville - Wells Rd - SSE of Substation",7.3807749368686872,80,"2021-09-25",0,0,0,0,1,0,0,0,0,0,18.030434782608694,38.5,0.39130434782608697,1,"Continue to Monitor"]
["FRANKFORT","Franklin - 801 E Main St - Frankfort ",3411,"Frankfort - Georgetown Rd - E of Substation",14.053075599747475,3271,"2017-12-30",0,0,0,0,0.16267054815336138,0,0,0,0,0.83732945184663865,74.884488646917887,38.226230510547232,0.98675650063447973,1.957199633139713,"Continue to Monitor"]
["Princeton - Hardesty Tap","Caldwell - 320 Marion Rd - Princeton",3423,"Princeton - Watson Rd, Mt. Hebron Rd, & Mill Dam Rd - E of Substation",19.63781976010101,838,"2021-09-20",0,0,0,0,6.0746433647418011E-2,0,0,0,0,0.93925356635258195,31.606510683567233,56.71217183770883,0.95397018932343136,1.7804295942720763,"Continue to Monitor"]
["West Cliff - High Bridge","Garrard - 815 Dix Dam Rd - Burgin",3427,"Burgin - Dix Dr, High Bridge Rd, & Blake Ln - N of Substation",3.5606991792929303,139,"2021-07-10",0,0,0,0,1,0,0,0,0,0,117.50171330518238,287.93525179856113,0.60300511844710569,0.99280575539568339,"Continue to Monitor"]
["GARDNER","Clay - HWY 66/Redbird Rd - Ashers Fork",4336,"Ashers Fork - State Hwy 66 - N of Substation",4.4040351957070696,28,"2017-12-29",0,0,0,0,1.3755731554814505E-2,0,0,0.98624426844518553,0,0,156.08975722313366,171.07857142857142,1.2195698924731182,2,"Continue to Monitor"]
["FOURMILE","Bell - Hwy 2014 - Pineville",4340,"Pineville - Hwy 2014 & 2015, US 25, & Hwy 92 - SW & N of Substation",14.80718970959596,174,"2016-10-03",0,0,7.212278003076493E-2,0,7.5164312683540764E-3,0,2.5765627185009091E-2,0.70227940148231016,0,0.19231576003356174,202.71420280883714,164.35796221592776,1.2886193553601057,1.3330377668308706,"Continue to Monitor"]
["SHAWNEE GAS 4KV","Harlan - Ball Park Rd - Harlan",4400,"Harlan - Memorial Hospital Rd & Hwy 115 - E of Substation",0.83558917297979796,15,"2020-03-14",0,0,0,0,0.47120418848167539,0.16230366492146597,0.36649214659685864,0,0,0,3.4166666541666673,12.228124958333334,5.0833333333333328E-2,0.19166666666666665,"Continue to Monitor"]
["SHAWNEE GAS 12KV","Harlan - Ball Park Rd - Harlan",4401,"Harlan - Morris Ln & Tway Hollow Rd - N of Substation",3.1087460542929297,113,"2020-03-14",4.0439052570768342E-3,0,0,0,0.1228576930483343,0,1.797291225367482E-3,0.87130111046922143,0,0,41.660776237481748,138.7932878806391,0.25838024315141012,0.68515037593984951,"Continue to Monitor"]
["HARLAN WYE 12KV","Harlan - Sunshine Pike Rd just W of US HWY 421 - Harlan",4412,"Harlan - US HWY 421 - E of Substation",19.708430871212119,889,"2018-09-14",3.5984084840277831E-3,0,1.1769001955160636E-2,0,2.7965643947750807E-2,0,1.6987835401340464E-2,0.67049076814229314,0.26918834206942721,0,51.927966464856198,147.94748784138878,0.61905130821865284,1.6874403304780048,"Continue to Monitor"]
["DANIEL BRANCH","Harlan - Gilbert Rd/Bandana Branch - Smith",4421,"Rose Hill - Hwy 987 - E of Substation",20.646925189393937,231,"2021-11-02",5.1760575993122469E-3,0,0,0,0.3916072643908729,0,9.6177956084106467E-3,0.59359888240140413,0,0,85.00168566798142,237.84166591518158,0.62855177131826712,1.7063444218616635,"Trees Trimmed in 2021"]
["CATRONS CREEK","Harlan - Near 6872 Hwy 72 - Gulston",4428,"Gulston - Hwy 1216, Hwy 72, & Hwy 2425 - N of Substation",8.8168410669191886,317,"2020-03-21",5.3892106176583424E-4,0,0,0,9.2392992199345991E-2,0,2.576773415663421E-2,0.88029558450099565,0,1.004768081258335E-3,152.87514246135916,345.0511591465978,0.87048875803973735,1.3304612379452556,"Continue to Monitor"]
["LYNCH 7.2KV","Harlan - Hwy 160 (W Main St) - Lynch",4450,"Lynch - Church St, E Main St, Gap Branch Rd, & Hwy 160 - E of Substation",0,368,"2021-06-12",0,0,0,0,0.17457516798652278,0,1.1869133234211182E-3,6.129194877128946E-3,0,0.8181087238129271,214.86057238548378,849.80977849714418,0.95748520757809907,2.9100217128654786,"Continue to Monitor"]
["LYNCH 7.2KV","Harlan - Hwy 160 (W Main St) - Lynch",4451,"Lynch - W Main St, Mountain St, & 1st, 2nd, & 3rd St - W of Substation",7.9213592171717195,243,"2021-05-01",0,0.45854709348861944,0,0,5.104995406954569E-2,0,5.4149588237506112E-3,0.48100735424467234,3.9806393734119075E-3,0,211.82729858644103,840.46507097245285,1.4622460573551985,5.9114529883993105,"Trees Trimmed in 2021"]
["EVARTS","Harlan - 1600 Block of Hwy 215 - Evarts",4475,"Evarts - Hwy 215 & City of Evarts - W of Substation",11.014289614898992,603,"2017-05-31",0,0,0,0,0.59992025079749212,0,6.7704322956770424E-2,0.27366351336486633,0,5.8711912880871193E-2,84.377185981115787,121.42601584382655,0.91795822084136314,0.85670214219839425,"Tree Trim Scheduled for 2022"]
["EVARTS","Harlan - 1600 Block of Hwy 215 - Evarts",4476,"Evarts - Hwy 215 - E of Substation",14.76352462121212,461,"2017-05-31",3.412732544427951E-3,0,0,0,0.46801603706837952,0,0.19616275682199688,0.33240847356519571,0,0,183.75885667396179,156.62267004638207,1.3384153863312733,1.5953914548280677,"Tree Trim Scheduled for 2022"]
["VERDA","Harlan - Corner of School St - Evarts ",4480,"Evarts - Hwy 38, Hill St, & Hwy 1601 - NE & SE of Substation",9.9302118055555582,380,"2021-11-23",2.4513915181374218E-2,0,0,0,9.3953234255261031E-2,0,3.8215827889790423E-2,0.84331702267357445,0,0,440.8804313329004,507.87311023334479,2.1967231380816679,2.6778036132780816,"Trees Trimmed in 2021"]
["SOMERSET 3","Pulaski - 125 Young St. - Somerset",4501,"Somerset - E Mt. Vernon St & Eller St - E & SW of Substation",8.6521704545454519,733,"2020-10-10",2.7771040504487025E-2,0,0,1.1318619128466328E-3,1.6075134071738488E-2,0,0.10689357803109925,0.21113267038564154,0.62164820653785002,1.534750855633708E-2,34.037223421091277,97.268219178904005,0.49223327347068924,0.62322991742823919,"Continue to Monitor"]
["SOMERSET 3","Pulaski - 125 Young St. - Somerset",4502,"Somerset - Pumphouse Rd, Speedway Dr, & College St - W of Substation",13.092038667929295,909,"2020-10-10",1.3122116854479783E-3,6.7179827112728449E-2,2.3998593092625913E-2,0,6.6598125025364927E-2,0,0.11271492539332531,0.15246005871132695,0.47272087769375415,0.10301538128542634,51.660162499639242,77.164895261502181,0.60811455364717726,0.60825312690725242,"Continue to Monitor"]
["SOMERSET 2","Pulaski - 105 Tandy Ave - Somerset ",4507,"Somerset - N Main St, Oak St, & N Vine St - SE of Substation",1.5795836489898993,149,"2020-07-25",0,0,0,0,0,0.75776193088315957,0.24223806911684037,0,0,0,14.057530211188109,61.185123013422817,0.17004064912307679,0.77181208053691241,"Continue to Monitor"]
["AISIN","Laurel - Farriston Rd/Greta Ln - Lily",4618,"Lily - Greta Ln & S Laurel Rd - S of Substation",6.1214419191919189,154,"2019-03-26",2.430763100219167E-2,0,0,0.21896792189679218,0,0,7.3321378760709308E-2,0.31858936043036462,4.8216776250249054E-2,0.31659693165969316,23.222058847685542,32.339460905094377,0.32081166145682272,0.27072497395078038,"Continue to Monitor"]

{"sheet":"KU Section 6-7","index":2,"n_rows":29,"n_cols":1,"rows_kept":29,"cut":false,"hidden":false,"merged":[[28,0,31,8],[27,0,27,8],[20,0,21,8],[15,0,15,5],[16,0,16,6],[17,0,17,6],[18,0,18,6],[19,0,19,6],[0,0,0,8],[2,0,2,8],[4,0,4,8],[5,0,10,8],[11,0,14,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
[]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 6: VEGETATION MANAGEMENT PLAN REVIEW"]
["The Companies’ Vegetation Management Plan was submitted December 19, 2007.  The Distribution Vegetation Management Program encompasses right of way maintenance for Louisville Gas and Electric Company and Kentucky Utilities Company (referred to as the “Companies”).  The program is centralized and managed by a Forestry Manager and eight company Utility Arborists.  All are certified arborists by the International Society of Arboriculture."]
[]
[]
[]
[]
[]
["The Companies’ plan is to maintain a proactive trim cycle while balancing the reactive needs of worst performing circuits. The Companies’ goal is to maintain an average trim cycle of five years or less.   The effectiveness of the plan is evaluated by the cycle and system performance as measured by system SAIDI, SAIFI, and CAIDI.  "]
[]
[]
[]
["Effectiveness of the program"]
["KU/LG&E Tree Cycle – 4.94 years"]
["KU (Kentucky) Tree SAIDI – 24.98 minutes"]
["KU (Kentucky) Tree SAIFI – 0.146"]
["KU (Kentucky) Tree CAIDI – 170.6 minutes"]
["The hazard tree program, mid cycle, herbicide, and worst performing circuits were completed as planned. "]
[]
["Adjustments made to the tree plan in 2021 included"]
["No changes made to plan."]
["Changes to be implemented in 2022"]
["No changes made to plan. Continue targeted hazard tree and mid-cycle trim work."]
[]
["SECTION 7: UTILITY COMMENTS"]
["SAIDI and SAIFI improved in 2021 compared to the previous 5 year average including and excluding major events.  415 Circuits were above their previous 5 year average SAIDI and/or SAIFI in 2021.  "]