{"text_format":"1","workbook":"xlsx","n_sheets":3,"sheets":["LGE Section 1-4","Excel LGE Section 5","LGE Section 6-7"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"LGE Section 1-4","index":0,"n_rows":45,"n_cols":8,"rows_kept":45,"cut":false,"hidden":false,"merged":[[43,0,43,8],[44,3,44,5],[35,6,35,8],[36,6,36,8],[35,1,35,3],[36,1,36,3],[41,1,41,8],[38,1,38,8],[39,1,39,8],[40,1,40,8],[37,0,37,8],[24,0,24,8],[6,0,6,3],[7,0,7,3],[16,0,16,3],[16,5,16,8],[17,0,17,3],[18,0,18,3],[17,5,17,8],[18,5,18,8],[6,5,6,8],[7,5,7,8],[15,0,15,3],[15,5,15,8],[14,0,14,8],[11,5,11,8],[0,0,0,8],[10,0,10,8],[11,0,11,3],[28,3,28,5],[29,6,29,8],[29,1,29,3],[1,0,1,8],[20,0,21,8],[25,2,25,6],[26,0,26,1],[26,5,26,6],[3,0,3,8],[4,0,4,3],[5,0,5,3],[4,5,4,8],[5,5,5,8],[34,6,34,8],[30,1,30,3],[31,1,31,3],[30,6,30,8],[31,6,31,8],[34,1,34,3],[33,0,33,8]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 1: CONTACT INFORMATION"]
["UTILITY NAME",null,null,null,null,"LOUISVILLE GAS AND ELECTRIC"]
["REPORT PREPARD BY",null,null,null,null,"Tiffany Koller (Dir. Substations & Asset Mgmt)"]
["E-MAIL ADDRESS OF PREPARER",null,null,null,null,"Tiffany.Koller@lge-ku.com"]
["PHONE NUMBER OF PREPARER",null,null,null,null,"(502) 364-8633"]
[]
[]
["SECTION 2: REPORTING YEAR"]
["CALENDAR YEAR OF REPORT",null,null,null,null,2021]
[]
[]
["SECTION 3: MAJOR EVENT DAYS (MED)"]
["TMED",null,null,null,null,3.2909999999999999]
["FIRST DATE USED TO DETERMINE TMED",null,null,null,null,"2016-01-01"]
["LAST DATE USED TO DETERMINE TMED",null,null,null,null,"2020-12-31"]
["NUMBER OF MED IN REPORTING YEAR",null,null,null,null,3]
[]
["NOTE: Per IEEE 1366 TMED should be calculated using the daily SAIDI values for the five prior years.  If five years of data are not available, then utilities should use what is available until five years are accumulated.        \n"]
[]
[]
[]
["SECTION 4: SYSTEM RELIABILTIY INFORMATION AND RESULTS"]
[null,null,"System-wide Information"]
["TOTAL CUSTOMERS",null,439603,null,null,"TOTAL CIRCUITS",null,625]
[]
[null,null,null,"Excluding MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",77.22,null,null,null,"SAIDI",74.38]
["SAIFI",0.88800000000000001,null,null,null,"SAIFI",0.82799999999999996]
[]
["Including MED"]
[null,"5 YEAR AVERAGE",null,null,null,null,"REPORTING YEAR"]
["SAIDI",185.31,null,null,null,"SAIDI",97.81]
["SAIFI",1.1120000000000001,null,null,null,"SAIFI",0.89100000000000001]
["Notes:  "]
["1)","All duration indices (SAIDI) are to be reported in units of minutes."]
["2)","Reports are due on the first business day of May of each year"]
["3)","Reports cover the calendar year ending in the December before the reports are due."]
["4)","IEEE 1366 (latest version) is used to define SAIDI, SAIFI, and TMED"]
[]
["SECTION 5: CIRCUIT REPORTING"]
[null,null,null,"BEGIN ON NEXT PAGE"]

{"sheet":"Excel LGE Section 5","index":1,"n_rows":246,"n_cols":22,"rows_kept":246,"cut":false,"hidden":false,"merged":[]}
["Substation Name","Substation Location   \n(County - Road - Town)","Circuit\nNumber","Circuit Location\n (Town - Road - General Area)","Total Circuit Length (Miles)","Average 2021 OMS Custs","Date of Last Circuit Trim (VM)","Animal","Construction","Lightning","Non-Company","Other/Unknown","Overload","Planned Work","Trees","Vehicle","Utility Equipment","2017-2021 SAIDI Average","2021 SAIDI","2017-2021 SAIFI Average","2021 SAIFI","LIST OF CORRECTION ACTION, IF ANY, TAKEN OR TO BE TAKEN"]
["ASHBY","Jefferson - 5400 Vesper Ln - Lousivlle","AB1202","Louisville - Greentree Ln & Dixie Hwy - S of Substation",19.396872474747472,1889,"2020-10-24",9.4608971297060231E-3,9.0538017282556782E-3,6.7849233575057533E-3,0,2.7736766685483522E-3,0,2.3828650831560208E-3,0.9306038038994312,0,3.8940032133397022E-2,60.276123908268609,97.049981245107759,0.55865718528920871,0.31344587471047003,"Continue to Monitor"]
["ASHBY","Jefferson - 5400 Vesper Ln - Lousivlle","AB1206","Louisville - Valley Station Rd & 3rd St - E of Substation",24.769650568181817,1414,"2021-01-30",6.6918989325052622E-3,1.1411150647953261E-2,0.29725622705263854,3.1194253839111272E-3,4.5587971571227667E-2,0,1.3081765755221852E-2,0.60641912618335236,0,1.6432434473189931E-2,79.606194373034981,102.87439837571776,0.93342571937632712,1.5873441835152811,"Trees Trimmed in 2021"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1289","Louisivlle - Shelbyville rd & Upton Ln - E of Substation",41.17130129419192,2579,"2020-02-29",0,0,0,0,7.2262682069311898E-2,0,0.35033693286455719,3.4069981583793735E-2,0.19306671689268373,0.35026368658965346,39.736188217980065,67.662501952799332,0.39344888841619674,0.42895179687494595,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1290","Louisville - Shelbyville Rd & SW of Substation",26.145522569444438,1627,"2019-10-05",1.3750476093365284E-2,0,0,0,6.48431665981892E-2,0,8.9970399738486043E-4,0.90029630251647208,0,2.0210350794588581E-2,34.964138441961204,38.137662740086022,0.42992292187446202,0.60210807106001119,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1291","Louisville - Shelbyville Rd & Bellewood Rd -  SW of Substation",22.154822443181818,1443,"2020-03-07",7.4407429301500738E-2,0,0,0,9.3876928357582795E-2,0,2.6760232133890148E-3,0.395136121228301,0.31721363055624419,0.11668986734298227,65.965876103857468,104.01739159161144,0.32175268893678877,0.49622563213160087,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1293","Louisville - New English Station Rd - NE of Substation",4.4160108901515152,146,"2020-11-21",3.6222005842259006E-3,0,0,0,0.66687439143135341,0,2.2706913339824733E-2,0,0,0.30679649464459591,92.611440259879231,175.86347029452054,1.7418172537813192,2.9589041095890414,"Continue to Monitor"]
["AIKEN","Jefferson - 12909 Shelbyville Rd. - Louisville","AK1295","Louisville - N English Station Rd & Avoca Rd - N of Substation",19.760963857323233,804,"2020-03-28",6.9245508527631802E-3,0,0,0,0.11752765077498056,0,0,0.59979890345468689,0.14010358369220846,0.13564531122536094,30.938542908095123,25.023321028594459,0.61062334346747915,0.97451581255374164,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1373","Louisville - S 12 St - N of Substation",3.050491003787879,30,"2019-02-09",0,0,0,0,0.25175943698016634,0,0,0,0,0.74824056301983366,81.654382827409989,403.46777769139777,0.65159887798036453,3.1311827956989244,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1377","Louisville - W Hill St & S 10th St - N of Substation",1.177578282828283,5,"2019-02-09",0,0,0,0,0.20380348652931854,0,0,0,0,0.79619651347068143,187.74999987999999,630.98333300000002,0.84000000000000008,2.4,"Continue to Monitor"]
["ALGONQUIN","Jefferson - 1800 S 11th St - Louisville","AL1442","Louisville - S 4th St & S 3rd St - E of Substation",7.1018039772727271,1271,"2019-02-09",1.5475648611743287E-3,0,0,0,0.88317402518585952,0,0,0,0,0.11527840995296616,44.262744256532997,51.851806979471306,0.74079592888575641,0.4091149196641084,"Continue to Monitor"]
["BRANDENBURG","Meade - Weldon Church Rd. - Brandenburg","BB1102","Brandenburg - E Broadway St - W of Substation",14.785147727272729,851,"2020-11-17",1.5027871649154071E-2,2.7491334253333189E-3,0.58744526181964385,0,0.10184833041758576,0,0.23365460887328993,0,5.92747938149931E-2,0,58.504010346047394,99.819914122060865,0.63322740727151405,1.5967208539134057,"Continue to Monitor"]
["BRANDENBURG","Meade - Weldon Church Rd. - Brandenburg","BB1103","Brandenburg - State Hwy 1638 - E of Substation",47.009499368686861,581,"2020-12-19",3.4718964759841257E-2,0,1.769081283924144E-2,0,0.34265153714996238,3.6111297251818596E-4,2.7604666919818031E-2,0.21284817619334809,4.7354195983828097E-3,0.3593893095668878,392.29016145481881,438.19588416191817,2.8084604181539889,8.7102469045801474,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1217","Louisville - Robarus Ln - N of Substation",2.3255653409090908,67,"2021-05-08",1.7692591227423518E-2,0,0,0,5.5289347585698485E-2,0,0.79874677478805745,2.838186509399189E-2,0,9.9889421304828599E-2,21.966089682817486,39.893811944842739,0.22795067950715545,0.26494474847339683,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1220","Louisville - Popular Level Rd. & Gilmore Ln - W of Substation",13.60679198232323,1111,"2021-05-08",7.06960475690801E-2,0,0,0,0.44724728926197971,0,5.8342077649527813E-2,0.16997551591465548,6.7338230150402245E-2,0.18640083945435468,49.216586144848904,60.804192655895122,0.69259803652162433,0.34875057190629649,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1223","Louisville - Bishop Ln & Gilmore Ln - SW of Substation",8.8423407512626255,70,"2021-05-08",0,0,0,0,0.66467065868263475,0,0,0,0,0.33532934131736525,22.921193450835677,9.298809500195695,0.35799706843729023,1.0714285714285712,"Continue to Monitor"]
["BISHOP","Jefferson - 3920 Bishop Ln - Louisville","BI1224","Louisville - Popular Level Rd & Preston Hwy - W of Substation",14.131932449494947,1211,"2021-05-08",0.2897460506861041,1.6763508080205443E-2,0,0,0.25992192161033434,0,5.9382376592046898E-2,8.1521880106871406E-2,2.0920339290809577E-2,0.2717439236336282,67.196612276421192,96.077904032204188,0.8049700295404133,1.6326591601060128,"Continue to Monitor"]
["BROOK","Jefferson - 913 S 1st Street - Louisivlle","BK0002","Louisville - S Brook St & S Floyd St - E of Substation",2.0560481376262629,187,"2020-02-08",0,0,2.1036024191427818E-2,0,9.371548777281094E-2,0,0.20336576387062846,0,0,0.68188272416513274,36.871764515485232,82.680251141408405,0.29071270967003782,0.54452774519794123,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1177","Louisville - Breckenridge Ln - NW of Substation",15.459689078282828,2009,"2020-09-19",3.1989721176523558E-2,0,1.7316077285116137E-5,0,0.13673986749737663,0,2.5208745311672075E-2,9.3705952228405984E-2,0.22200076883383146,0.49033762887490517,167.55188107969906,281.56212859805566,2.0892199542582377,3.3005747766889804,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1180","Louisville - Dutchmans Ln - W of Substation",8.6018907828282831,547,"2020-07-18",5.1632752528329474E-3,0,0,0,0,0,2.03941757036676E-2,0.1605641525526989,2.5953454368222249E-2,0.78792494212257824,106.51988350949554,120.03864659356387,1.0616136526528563,1.4587733676625976,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1181","Louisville - Browns Ln - SE of Substation",24.141351010101008,2079,"2020-08-01",2.7352937516333361E-3,0,0,0,3.8983535970730614E-2,0,8.365170426969647E-3,4.9588710379929561E-2,1.0030240053760095E-3,0.89932426546536082,136.11656109152659,184.40210374067811,1.579820911386415,1.2741209668880633,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1182","Louisville - I - 264 East - E of Substation",6.0484648042929283,226,"2020-08-01",0,0.41501022096758494,0,0,0,0,0,0,0,0.58498977903241511,83.552256635398223,227.2720501415929,0.82654867256637166,1.6150442477876106,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1184","Louisville - I - 264 East - E of Substation",1.2630699179292928,9,"2020-07-18",1,0,0,0,0,0,0,0,0,0,153.72444444444446,24.288888888888888,0.28888888888888886,0.44444444444444442,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1186","Louisville - Richland Dr & Hunsinger Ln - S of Substation",13.145377840909092,1679,"2020-09-19",3.7390690266550473E-2,6.119842533882261E-2,0.17981638969859062,7.2121885987318571E-4,0.2327884124169847,0,5.9523094028908853E-2,0.30711903116266487,0,0.12144273822760465,89.723387696916092,72.776904789994774,0.81457995370117575,1.0767095383579166,"Continue to Monitor"]
["BRECKENRIDGE","Jefferson - 3920 Dutchmans Ln. - Louisville","BR1351","Louisville - Brekenridge Ln & Shelbyville Rd - NW of Substation",8.5476955492424214,354,"2019-03-16",0,0,0,0,0,0,0,0,0.26045528844237131,0.73954471155762869,158.80694514016079,211.9656337971831,1.2044826065699701,1.0084507042253521,"Continue to Monitor"]
["BLUEGRASS PARKWAY","Jefferson - 11240 Bluegrass Parkway - Louisville","BY1284","Louisville - Watterson Trail - SW of Substation",7.766522095959596,326,"2021-10-23",6.6760986824652927E-3,0,8.3340702095676018E-3,0,0.17956936952869396,0,0.11634538862852595,0,0,0.68907507295074721,61.686902140803696,138.6705107001153,0.54894201387849528,1.1746309276922204,"Continue to Monitor"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1340","Louisville - S 22nd St - S of Substation",3.9485785984848492,89,"2019-02-23",0,0,0,0.3276487663280116,0.67235123367198835,0,0,0,0,0,39.596355969458628,123.87003743820225,0.60451991828396334,2.01123595505618,"Continue to Monitor"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1341","Louisville - S 20th St & W Market St - S of Substation",5.6951377840909103,1069,"2019-02-23",0,0,0,0.54400341833386745,0.3273207282271971,0,0,0,0,0.12867585343893542,162.85704708850426,406.43953009694019,2.1091071974239579,2.6186046575852844,"Continue to Monitor"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1342","Louisville - Portland Ave - W of Substation",4.1355064709595961,1168,"2019-02-23",0,0,5.9355663169222493E-2,0,3.9278988431530805E-2,0,0,0,0,0.90136534839924676,235.93728386810707,266.57002450263388,2.7232266091437909,3.2052238805970155,"Continue to Monitor"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1343","Louisville - S 20th St & W Chestnut St - S of Substation",2.7314938446969688,13,"2019-02-23",0,0,0,0,0,0,0,0,0,1,18.372649572649571,29.307692307692307,0.38632478632478628,0.15384615384615385,"Continue to Monitor"]
["CANAL","Jefferson - 2005 Northwestern Parkway - Louisville","CA1346","Louisivlle - Northwestern PKY & W Market St - W fo Substation",5.0731950757575781,2200,"2019-02-23",5.7248695066509513E-4,0,0,0,0.25103365699425645,0,8.7556827748779258E-4,0,0,0.74751828777759066,112.54089910907355,213.61309171007369,1.486481963246669,1.875982800982801,"Continue to Monitor"]
["CROP","Jefferson - 116 N 26th St - Louisville","CB0001","Louisville - N 26th St - N of Substation",3.3848117108585858,678,"2019-01-26",0,0,0,0,3.701072609431596E-3,0,1.4956309217892611E-2,0.97830224256935128,0,3.0403756033245337E-3,95.449201936815754,355.61290087844446,0.43490846327905652,1.1485850428314897,"Continue to Monitor"]
["CROP","Jefferson - 116 N 26th St - Louisville","CB0003","Louisville - N 26th St - S of Substation",2.4657897727272724,402,"2019-01-26",0,0,0.20036367469562008,0,0.11308174774679808,0,2.1609655826701102E-2,2.4982870394771518E-2,0,0.63996205133610917,39.471183591471572,95.507890964566911,0.30244106391972403,0.43923007488747717,"Continue to Monitor"]
["CENTERFIELD","Oldham - 4210 Hwy 393 - Centerfield","CF1204","Centerfield - S Hwy 393 - N of Substation",71.760336489899004,1809,"2021-04-24",1.7709627736843026E-2,2.1899119659765124E-3,0,2.2074137599103908E-3,0.49884488160036405,1.3601081610865113E-2,2.2977667710940373E-2,0.36582030908168084,1.3520135813920927E-3,7.5297092952027578E-2,128.98007550581264,118.12916667033953,1.8187672628980422,2.5368511255657715,"Trees Trimmed in 2021"]
["CENTERFIELD","Oldham - 4210 Hwy 393 - Centerfield","CF1205","Centerfield - Elder Park Rd - NE of Substation",27.317852114898983,790,"2018-03-17",4.5200963611005451E-2,0,3.0509065550906557E-3,0,4.0176873335869149E-3,0,9.8896918980600993E-3,0.70967256244452903,5.1984277925700519E-2,0.1761839102320274,123.92684386378798,132.75242833643202,1.4498709177849247,0.4350413672806413,"Reliability Improvements Completed in 2021"]
["CLARKS LANE","Jefferson - 934 Clarks Ln - Louisville","CK0001","Louisville - Clarks Ln - E of Substation",0.85711947601010097,148,"2019-09-28",0,0,0,0.10848400556328233,0.1070931849791377,0,0,0.78442280945757992,0,0,11.737164365438142,19.413790885951389,7.8062099246663005E-2,0.13490839833121712,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1226","Louisville - Lexington Rd, E Jefferson St, & E Muhammad Ali Blvd - W of Substation",11.883699179292929,2510,"2018-07-28",8.0449555671719807E-3,1.2279142707788814E-2,5.3403031887088344E-2,0,0.14703606900156821,0,0.13786199686356509,7.3366440146366965E-2,3.7271301620491375E-3,0.56428123366440142,74.062490314500039,58.140377760449063,1.1817219209259415,1.777836988203455,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1227","Louisville - Frankfort Ave, Clifton Ave, & Ewing Ave - E of Substation",3.1388360164141411,650,"2018-09-15",0.31539647364871376,0,0,0,0,0.36366701994411793,0.2500240870989498,0,0,7.0912419308218524E-2,25.711325172721708,31.156272990703059,0.39609255181313835,0.31503722084367247,"Continue to Monitor"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1230","Louisville - Mellwood Ave, Shiloh Ave, & River Rd - N of Substation",15.419173926767678,2101,"2018-11-03",1.0472938010969678E-2,0,0,0,9.6051950739935832E-2,0,0.27431956949187625,0.28899927558729172,8.1449860291834833E-2,0.2487064058780917,59.533466509522455,77.765672433454739,0.70181021240104946,1.2071681267449914,"Tree Trim Scheduled for 2022"]
["CLIFTON","Jefferson - 2009 New Main Street - Louisville","CL1407","Louisville - Payne St, Spring St, & Story Ave - W of Substation",1.4995041035353536,5,"2018-07-28",0,0,0,0,0,0,0,0,0,1,65.816666640000008,122.4,0.88000000000000012,1,"Continue to Monitor"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1192","Louisville - Winchester Acres Rd & La Grange Rd - S of Substation",28.888926609848482,950,"2019-11-09",5.6923332184656223E-3,0,2.1824865030439945E-3,0,0.16659646973235823,0,7.2621919311814786E-3,0.12881775599545633,0.48449924059680155,0.20494952202269276,112.21306610231807,82.039165466414858,0.9450865687026464,1.3276067522737851,"Continue to Monitor"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1194","Louisville - Collins Ln & La Grange Rd - S of Substation",1.3291680871212121,34,"2019-11-09",0,0,0,0.17614601018675721,0.1931239388794567,0,0,6.7062818336162983E-2,0.56366723259762308,0,12.930196070588234,64.650980352941176,0.24705882352941178,1.2352941176470589,"Continue to Monitor"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1195","Louisville - Collins Ln, Westport Rd, & Northumberland Dr - N of Substation",16.576873106060606,1116,"2020-04-25",3.8733600295062967E-2,0,0.24656857579429897,0,0.25102745139364563,0,1.9304230992149219E-2,6.5598819748142684E-3,0.30749776068286,0.13030849886716897,48.241963076289089,135.65210200788661,0.57405491208901738,1.8001625604469855,"Continue to Monitor"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1196","Louisville - Westport Rd & Accomack Dr - NW of Substation",10.558273042929292,976,"2020-04-25",5.4031112779745682E-3,0,0,0,7.2147042980036227E-2,0,7.9855046440639229E-3,0.88410244690749418,3.5585445879107426E-4,3.0006039731640032E-2,18.564976688149237,33.97783402868852,0.30194456630029487,1.1188524590163935,"Continue to Monitor"]
["COLLINS","Jefferson - 3401 Coillins Ln. - Louisville","CO1197","Louisville - La Grange Rd, Reamers Rd, & Chamberlain Ln - E of Substation",32.433263257575746,1838,"2019-12-21",4.9204727488301105E-2,0,0,0,5.6949332122450524E-3,0,4.0791614636545959E-2,0.1347422459353439,0.48191243803685624,0.28765404069070771,50.654975102656003,79.195958279893631,0.67623788246242611,2.0992403109302225,"Continue to Monitor"]
["CANE RUN","Jefferson - 5252 Cane Run Rd. - Louisville","CR1421","Louisville - Elmwood St, Lees Ln, & Campground Rd - NE of Substation",2.3017138573232323,3,"2021-06-12",0,0,0,0,0.70692943420216148,0,0.29307056579783852,0,0,0,140.75333319999999,524.33333299999993,0.46666666666666662,1.3333333333333333,"Continue to Monitor"]
["CONESTOGA","Bullitt - 1365 N Buckman St. - Shepherdsville","CS1260","Shepherdsville - Buckman St & N Preston Hwy - N of Substation",8.4638005050505054,245,"2021-05-15",8.4253681392235606E-3,0,0,0,6.9109772423025431E-3,0,1.0960508701472558E-3,2.501673360107095E-3,3.8345046854082999E-2,0.94272088353413652,195.88964370103255,489.57074558340736,1.3818190491187676,1.2693452983179196,"Continue to Monitor"]
["CONESTOGA","Bullitt - 1365 N Buckman St. - Shepherdsville","CS1261","Shepherdsville - I 65 S, HWY 44, & Joe B Hall Ave - S of Substation",7.0768158143939397,203,"2021-05-15",3.1777812002669541E-2,0,0,0,0.39781302941629448,0,0,0,0.56219518455772888,8.213974023307152E-3,20.042579410564144,71.912114609178502,0.12749511485088449,0.35699706266012265,"Continue to Monitor"]
["CARTER","Jefferson - Opposite 2215 Carter St - Louisville","CT0001","Louisville - N 22nd St & Griffiths Ave - S of Substation",2.3977337436868686,371,"2019-02-23",0,0,0,0,7.0704384536116743E-2,0,0,0,0.74846258684306755,0.18083302862081574,29.56687486279991,80.757453752265178,0.18600356548964331,0.42924512103758566,"Continue to Monitor"]
["CARTER","Jefferson - Opposite 2215 Carter St - Louisville","CT0002","Louisville - Portland Ave, 24th St, & Northwestern Pky - W of Substation",1.85525946969697,263,"2019-02-23",0,0,0,0,0.133301404853129,0,0.11613984674329503,0,0,0.75055874840357595,38.075738887885187,47.489423702197833,0.33387270917391049,0.62183143219264891,"Continue to Monitor"]
["CARTER","Jefferson - Opposite 2215 Carter St - Louisville","CT0004","Louisville - Portland Ave, Bank St, & N 28th St - W of Substation",3.1127814078282827,416,"2019-02-23",0,0,0,0,0.59092980164636555,0,0.13055496491601107,0,6.6431760882111723E-2,0.21208347255551169,62.526024039636454,79.190189393376656,0.61026930207729535,0.49494487175818203,"Continue to Monitor"]
["CRESTWOOD","Oldham - Floydsburg Rd. - Crestwood","CW1222","Crestwood - W HWY 22, Clore Ln, & Lake Ave - W of Substation",53.165539457070714,1904,"2018-02-03",1.1592399909522732E-3,6.094649274925231E-4,0,0,0.8674005378370907,0,1.115572143054613E-2,9.4413657040890692E-2,0,2.5261378773027723E-2,54.089479245011887,165.03822565845724,0.47967618601569006,1.427107889446398,"Continue to Monitor"]
["CLAY","Jefferson - 908 Clay St. - Louisville","CY1481","Louisville - S Preston St, S Floyd St, E KY St, & 3rd St - W of Substation",5.2587512626262622,786,"2018-07-06",1.9966226283897884E-2,0,0,0,0,0.63340617860335746,0.34369722856859042,2.4833614780967518E-3,0,4.4700506605741534E-4,48.703553127435256,68.752567110764986,0.55661401572247848,0.84364916496188092,"Continue to Monitor"]
["CLAY","Jefferson - 908 Clay St. - Louisville","CY1482","Louisville - Clay St, E Broadway, Logan St, Chestnut St, & Preston St - N of Substation",3.8352526830808089,35,"2018-07-06",0,0,0,0,0,0,0.43541788427819988,0,0,0.56458211572180017,23.562661292508796,95.070370333333329,6.5426512485336014E-2,0.22222222222222221,"Continue to Monitor"]
["CLAY","Jefferson - 908 Clay St. - Louisville","CY1483","Louisville - Breckinridge St, Vine St, Highland Ave, & Barrett Ave - E of Substation",2.0878682133838389,19,"2018-07-06",0,0,0,0,0,0,0,0,0,1,17.779628183205126,47.90027774166667,0.45858974358974358,1.575,"Continue to Monitor"]
["CLAY","Jefferson - 908 Clay St. - Louisville","CY1486","Louisville - Caldwell St, Logan St, Jackson St, Goss Ave, & Ash St - S of Substation",4.2251035353535373,258,"2018-07-06",0,0.88137235898429933,0,0,0,0,0.11862764101570071,0,0,0,28.147125400047752,10.660852046511629,0.61015872464273635,1.1744186046511629,"Continue to Monitor"]
["DAHLIA","Jefferson - 2135 Dahlia Ave. - Louisville","DA1243","Louisville - Bon Air Ave, Gardiner Ln, & Goldsmith Ln - E of Substation",13.850754419191919,1641,"2019-02-23",0.13826023216639297,0,0,0,0.22047349539402739,0,2.3628956660863683E-2,0.55517652116914884,0,6.2460794609567175E-2,116.55214291938719,147.79786507739277,1.1866434604007543,2.2867613760847365,"Reliability Improvements Completed in 2021"]
["DEL PARK","Jefferson - 3135 Del Park Terrance - Louisville","DE1406","Louisville - River Park Dr, S 41st St, & W Broadway - W of Substation",2.3356862373737375,2140,"2020-03-21",0,0,0,0,1,0,0,0,0,0,124.89246466094524,268.10124610591902,1.2003457758124152,1.9962616822429906,"Continue to Monitor"]
["DEL PARK","Jefferson - 3135 Del Park Terrance - Louisville","DE1410","Louisville - River Park Dr, Cecil Ave, Greenwood Ave, & Virginia Ave - SW of Substation",5.5404562815656559,1623,"2020-03-21",0,0,0,0,0,0,0,0.18392560731136995,0,0.81607439268863002,296.172830384836,679.14640293748607,2.4097511116238164,5.8042637091805283,"Continue to Monitor"]
["DUMESNIL","Jefferson - 1309 Dumesnil St - Louisville","DU0001","Louisville - Dumesnil St, W Magnolia Ave, & S 13th St - S & E of Substation",1.9774371843434344,44,"2019-02-09",0,0,0,0.41864350150350821,0.53859004343468098,0,0,4.2766455061810892E-2,0,0,73.46558838237236,201.97636362878788,0.79324944348845561,1.4969696969696971,"Continue to Monitor"]
["DUMESNIL","Jefferson - 1309 Dumesnil St - Louisville","DU0002","Louisville - S 13th St, W Hill St, & S 15th St - S of Substation",3.8243333333333336,133,"2019-02-09",0,0,0,0.42608915906788247,0,0,0,0,0.57391084093211753,0,85.703573158279298,294.93095358585481,0.82495259738367044,3.1573923614558135,"Continue to Monitor"]
["DIXIE","Jefferson - 1706 Bernheim Ln. - Louisville","DX1222","Louisville - Millers Ln, Cane Run Rd, Bells Ln, & Algonquin PKY - W of Substation",26.789462752525253,2427,"2019-03-01",1.3945716812011304E-2,0,4.6474886873905585E-3,0,7.1137242323896042E-3,0,2.4651519617191701E-3,0.96029642504204304,0,1.1531493264446331E-2,177.28147977292383,379.94810512340632,1.4845254104699588,0.95930847808561459,"Reliability Improvements Completed in 2021"]
["EIGHTH","Jefferson - 841 S 8th St - Louisville","EI0002","Louisville - W Breckenridge St, S 6th St, & S 4th St - E of Substation",2.0000078914141413,165,"2019-12-21",0,0,0.44223213691150032,0,0.38130119198241991,0,8.330558700139841E-2,0,0,9.3161084104681366E-2,32.242086061599807,90.451920251857743,0.18755645353067624,0.45151864944809178,"Continue to Monitor"]
["EIGHTH","Jefferson - 841 S 8th St - Louisville","EI0003","Louisville - S 9th St, W Kentucky St, & S 8th St - SW of Substation",0.58854087752525264,34,"2019-12-21",0,0,0,0,0,0,0,0,4.6007485963817839E-2,0.95399251403618213,48.560409328273202,188.34,0.21508728744022859,0.85210084033613442,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1173","Louisville - Shepherdsville Rd, Rural Way, & Rangeland Rd - S of Substation",13.250161142676768,1751,"2020-07-11",1.7456561642129657E-2,0,0,1.4673474581318664E-2,0,0,5.5748374276478579E-2,0.88923421789297563,1.9546584220870985E-3,2.0932713185010315E-2,75.95437508976309,104.96234188073436,0.76334837949629541,1.1782616876676388,"Continue to Monitor"]
["ETHEL","Jefferson - 3532 Ethel Ave. - Louisville","ET1423","Louisville - Jennings Ln, Bishop Ln, & Robards Ln - W of Substation",5.1798604797979797,51,"2020-06-13",0,0,0,0,0,0,0,0,0,1,41.279106311001939,96.712083319999991,0.55540483467629898,1.04,"Continue to Monitor"]
["EASTWOOD","Jefferson - 100 Flat Road Rd. - Louisville","EW1240","Louisville - Shelbyville Rd & Beckley Creek PKWY - W of Substation",14.574446969696968,366,"2020-02-29",0.45781512605042018,0,0,0,0.35215686274509805,0,0.16448179271708682,0,0,2.5546218487394957E-2,19.098350290801601,24.385519117486336,0.19543853019878193,0.20491803278688525,"Continue to Monitor"]
["FARNSLEY","Jefferson - 2428 Farnsley Rd. - Louisvlle","FA1123","Louisville - Kramers Ln, Campground Rd, & Lees Ln - SW of Substation",17.191440025252525,920,"2021-10-30",3.8359134607719655E-3,6.4505843151634965E-3,2.2001498652806785E-4,0,3.7944613618608804E-4,0,1.2885225515361191E-2,0.97622881558598917,0,0,142.1662285666778,337.62338751628494,1.1850252604787042,0.81054591726422787,"Trees Trimmed in 2021"]
["FARNSLEY","Jefferson - 2428 Farnsley Rd. - Louisvlle","FA1148","Louisville - Cane Run Rd & Lees Ln - SW of Substation",18.123017992424238,2579,"2021-10-16",7.261120928164097E-3,1.1558759981581547E-2,0,2.8930352272593107E-2,1.0913327010189183E-2,0,6.5283183716198401E-2,0.83713049946279516,2.5262403922973086E-2,1.3660352705505464E-2,66.894145927665676,98.479063358775917,0.53893676321028461,0.35391204421806399,"Trees Trimmed in 2021"]
["FARNSLEY","Jefferson - 2428 Farnsley Rd. - Louisvlle","FA1149","Louisville - Farnsley Rd & Burrell Dr - E of Substation",7.666603693181818,1021,"2021-10-16",5.1336622925929942E-2,0,2.21369699598742E-2,0,0,0,0.11669016375664244,0.17081932545277087,0,0.63901691790478254,50.451316331439926,72.275347019669098,0.76463352113031857,1.3093030887639832,"Continue to Monitor"]
["FARNSLEY","Jefferson - 2428 Farnsley Rd. - Louisvlle","FA1214","Louisville - Farnsley Rd, Cane Run Rd, Ralph Ave, & Campground Rd - N & E of Substation",12.962463857323231,982,"2021-10-16",0,2.1824484984114934E-2,2.237896377405239E-2,0,9.9491478010669973E-2,0,3.8378923811617081E-2,0.67431114752132992,2.2708653865366555E-2,0.12090634803284912,71.394274329326294,203.58015403702834,0.68489936808419238,2.2440005114436898,"Trees Trimmed in 2021"]
["FALLS CITY","Jefferson - 1048 S 43rd St - Louisville","FC0002","Louisville - S 43rd St, Virginia Ave, Southwestern PKY - S of Substation",2.0460422979797976,326,"2019-01-05",0,0,0,0,0,0,0.45402154848408921,0,0,0.54597845151591085,29.737251706357988,49.101727333564931,0.3959021692117885,0.25547084287370586,"Continue to Monitor"]
["FALLS CITY","Jefferson - 1048 S 43rd St - Louisville","FC0003","Louisville - S 43rd St, Fordson Way, & Cecil Ave - S of Substation",1.9055230429292931,283,"2019-01-05",0,0,0,0,0,0,0,2.8823802882380289E-2,0,0.97117619711761971,6.297328869941774,7.5744131408450706,0.27112966796428412,0.10563380281690141,"Continue to Monitor"]
["FALLS CITY","Jefferson - 1048 S 43rd St - Louisville","FC0004","Louisville - Greenwood Ave, S 45th St, & Garland Ave - NW of Substation",3.6206530934343433,411,"2019-01-05",0,0,0,0,6.4716266297783612E-2,0,1.8581796033818869E-2,0.91670193766839758,0,0,89.450629554461287,192.8077310079054,0.61761925363484182,0.86802906038020133,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1213","Louisville - Westport Rd, Blossom Ln, Goose Creek Rd & Brownsboro Rd - W of Substation",28.306087436868687,1991,"2019-07-20",2.9409793833622467E-3,3.3370809104378708E-2,0,7.09557810720056E-3,4.7018442546664783E-2,0,5.7553849704785227E-3,0.20708962169325959,0.10443082742035158,0.59229835677430398,66.435802544540692,57.476119025349703,0.56909884966632729,0.65292385731381219,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1214","Louisville - Freys Hill Rd, Evergreen Rd, & Park Rd - SE of Substation",26.29178724747474,723,"2019-05-04",3.4912595579376982E-3,0,0,0,0.76668387710110719,0,5.6056843606323604E-3,0.20314049451314961,4.7451626386054635E-3,1.6333521828567683E-2,89.209411665272924,141.37299103191867,0.83570747563244152,0.20343671844956021,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1215","Louisville - Springhurst Blvd, Fischer Pard Dr, & I 265 S - NE of Substation",4.253040404040406,80,"Underground Circuit",0,0,0,0,0,0,0,0,0,1,27.403688572303441,28.8604166625,0.24182432432432432,8.7499999999999994E-2,"Continue to Monitor"]
["FREYS HILL","Jefferson - 3300 Freys Hill Rd. - Louisville","FH1217","Louisville - Westport Rd & Chamberlain Ln - NE of Substation",8.0850640782828282,550,"2019-08-10",0,0,0,0,0.91469048512910356,0,8.5309514870896427E-2,0,0,0,86.670419444459199,349.31923460904,0.30173433016498696,2.7269511634749204E-2,"Continue to Monitor"]
["FLOYD","Jefferson - 1806 S Floyd St. - Louisville","FL1495","Louisville - Floyd St, Burnett Ave, & Shelby St - E of Substation",3.9173339646464642,1847,"2019-12-07",0,0,0,0,0,0,0,0,0,1,41.193048362682013,93.747698971304814,0.64688901463186932,0.99133730373578777,"Continue to Monitor"]
["FLOYD","Jefferson - 1806 S Floyd St. - Louisville","FL1496","Louisville - Floyd St, Warnock St, & Crittenden Dr - SE of Substation",3.7602640467171713,1121,"2019-12-07",0,0,0,0,0,0,0,0.20612491960806567,0,0.79387508039193433,83.248042452201233,112.216666,0.93318043282787966,1,"Continue to Monitor"]
["FLOYD","Jefferson - 1806 S Floyd St. - Louisville","FL1497","Louisville - S Floyd St & Crittenden Dr - S of Substation",3.7321545138888901,427,"2019-12-07",0,0,0,0,0,0,0,0,9.4398268597610112E-4,0.99905601731402394,98.196422336427844,202.95778816121492,1.3985290767607852,2.004672897196262,"Continue to Monitor"]
["FLOYD","Jefferson - 1806 S Floyd St. - Louisville","FL1498","Louisville - S Floyd St & Byrne Ave - S of Substation",2.6085287247474751,134,"2019-12-07",0,0,0,0,0,0,0,0,0,1,36.353927733314755,139.03333332846714,0.62180539639842025,1,"Continue to Monitor"]
["FLOYD","Jefferson - 1806 S Floyd St. - Louisville","FL1499","Louisville - S Floyd St, W Cardinal Blvd, & S Brook St - N & S of Substation",2.1568208648989895,8,"2019-12-07",0,0,0,0,0,0,0.18764478764478765,0,0,0.81235521235521235,76.003095196428575,161.885416625,0.94214285714285706,1.125,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1256","Louisville - Bardstown Rd, Lands Ln, & HWY 44 -  S of Substation",37.810889046717172,1929,"2018-08-25",0.10123950203883232,0,0,0,0.4776808619805028,0,0.14525667683832463,4.0965677405417081E-2,0.19464772757959548,4.0209554157327645E-2,25.472006235226555,19.263401167211143,0.6029814571504365,1.1287672317320225,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1257","Louisville - Brentlinger Ln, Seatonville Rd, Brush Run Rd, & Routt Rd - E of Substation",94.921948863636374,2048,"2019-01-05",4.069047015314544E-3,0,5.0414559581278079E-2,0,7.5814407440543116E-2,0,3.5451661826549994E-3,0.71034652683752997,1.091777223862174E-2,0.14489252070405756,82.298372619506637,108.17347447494647,0.66783182297503463,1.1864038161696118,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1259","Louisville - Fairmount Rd & Cedar Creek Rd - W of Substation",25.956955018939396,942,"2021-08-28",2.4210138613149834E-3,0,0,0,5.8158232794631545E-2,0,8.7767367068821468E-3,4.3254848765238016E-3,0,0.92631853176064749,71.900089692509113,234.36964858981725,0.87036512338097993,3.1953162429794495,"Continue to Monitor"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1261","Louisville - Fairmount Rd, Back Run Rd, & Dawson Hill Rd - E of Substation",34.251876420454543,826,"2021-11-20",0.26744144561979344,0,0,0,7.9220107386860264E-2,0,1.2067643018962165E-2,0.57545621577266803,0,6.5814588201716054E-2,32.010387417851568,76.227971023725388,0.39376763196413489,1.6375139030207455,"Trees Trimmed in 2021"]
["FAIRMOUNT","Jefferson - 10713 Fairmount Rd. - Louisville","FM1262","Louisville - Bardstown Rd & Stone Breaker Rd - NNW of Substation",32.769694128787876,2088,"2021-08-28",0,0,0,0,9.5966800674361294E-3,0,2.019841784463753E-2,1.4500389054597329E-2,0,0.95570451303332904,41.85736205720319,57.919681377074085,0.62731309166985882,0.61086240106830247,"Continue to Monitor"]
["FORTY FOURTH","Jefferson - 128 N 44th St - Louisville","FO0001","Louisville - N 44th St & Bank St - N of Substation",1.3422484217171717,213,"2020-04-18",0,0,0,0,0,0,0.15959481784192681,0.79293104947395876,0,4.7474132684114427E-2,38.262755019728857,107.49293725808434,0.43536758824943317,0.25235838708262032,"Continue to Monitor"]
["FORTY FOURTH","Jefferson - 128 N 44th St - Louisville","FO0002","Louisville - N 44th St, W Market St, & Fontaine Landing Ct - SW of Substation",2.5847132260101007,357,"2020-04-18",0,0.10250038825904643,0,0,0,0,0.26261841900916294,0.35913961795309829,0.27574157477869232,0,34.123409022604243,36.062321556194988,0.60562951029761758,0.33617445471691915,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1135","Louisville - Forest Dr, E Indian Trl, & Poplar Level Rd - N of Substation",16.954053819444443,2112,"2021-01-23",5.2937607442613006E-2,0,0,0.10666810689563243,0.14938315299828092,0,1.5903804962354867E-3,5.4236111749510471E-2,0.32743911968302708,0.30774552073470063,82.489393217866365,197.42936387993251,1.0494575453866626,2.6283742495282949,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1137","Louisville - Fern Valley Rd, Industrial Blvd, & Orange Dr - W of Substation",6.3324251893939394,427,"2021-07-28",0,0,0,0,0,0,2.0520958739192297E-2,0,0,0.97947904126080776,48.667075444501926,85.788387592123968,0.4211438842834106,0.50923653779318134,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1140","Louisville - Preston Hwy, Minor Ln, & Rossmoor Dr - SE of Substation",11.0735680239899,1078,"2021-05-01",0,0,0,0.27524312692259945,3.1230601575324515E-3,0,2.4333383912929526E-3,1.7463755121184114E-3,0.67661981156801343,4.08342874484433E-2,96.654587022032885,336.34367700746276,0.75142180337066899,2.9068243537443883,"Continue to Monitor"]
["FERN VALLEY","Jefferson - 1256 Old Fern Valley Rd. - Louisville","FV1143","Louisville - Preston Hwy, Clay Ave, Minor Ln, Foreman Ln, & Bonaventure Blvd - S of Substation",18.408026357323234,1504,"2021-07-28",1.8378424584348421E-3,0,0,0,2.9102410176906908E-2,0,1.3583715083907415E-2,0.26069775845388105,0,0.69477827382686985,124.98085970790699,126.6887335606915,1.682979651150746,0.65082147058406181,"Trees Trimmed in 2021"]
["GAULBERT","Jefferson - 2950 Wilson Ave - Louisville","GA0001","Louisville - Catalpa St, Woodland Ave, & Hemlock St - NE of Substation",2.8838701073232325,461,"2019-01-09",0,8.326853291861068E-2,0,0,3.9679453948505271E-2,7.2274062554000346E-2,5.1062726801451526E-2,0.17381631242439952,0.38355365474339037,0.1963452566096423,68.359518796823522,100.7063224827891,0.48088281840102776,0.73875216364564333,"Continue to Monitor"]
["GRAND","Jefferson - 1038 S 34th St - Louisville","GD0001","Louisville - Greenwood Ave, S 28th St, Virginia Ave, & S 26th St - E of Substation",4.144142676767677,739,"2019-01-09",0,0,0,0.26025473874235283,0.56076908749659726,0,2.1920712924624268E-2,1.4069372609137928E-2,8.1522128458243193E-2,6.1463959769044514E-2,45.254299978455471,94.385303981794479,0.33989629433803153,0.60907364796275065,"Continue to Monitor"]
["GRAND","Jefferson - 1038 S 34th St - Louisville","GD0002","Louisville - Louis Coleman Jr Dr, Virginia Ave, & Kirby Ave - S of Substation",4.0526425189393942,583,"2019-01-09",0,4.2884094427244585E-2,0,0,1.7390673374613003E-2,0,0.15910410216718265,0.72750580495356043,2.1042956656346749E-2,3.2072368421052634E-2,33.033913897635031,65.875008648321611,0.40593410269239427,1.2231675988048667,"Continue to Monitor"]
["GILLIGAN","Jefferson - 35th Street & Gilligan Ave - Louisville","GI0001","Louisville - Bank ST, 33rd St, Portland Ave, & Rudd Ave - N & E of Substation",4.1134176136363632,672,"2020-04-04",0,5.5589272677696562E-3,0,0.5064077191686237,0.14187578612203253,2.5771609010387807E-3,0.18880122437132227,8.4052387612036136E-2,1.023827743620867E-2,6.0488517120968241E-2,66.634361790733138,169.40840484893891,0.64266263334981166,1.4642632754913532,"Continue to Monitor"]
["GILLIGAN","Jefferson - 35th Street & Gilligan Ave - Louisville","GI0002","Louisville - S 32nd St - S of Substation",2.3506070075757575,169,"2020-04-04",0,0,0,0,0.1600168173218415,0,0.25453016607105317,0.55551818372924111,0,2.9934832877864199E-2,103.00430163047947,140.85895945775698,1.2945946283154217,0.65937207927142083,"Continue to Monitor"]
["GRADE LANE","Jefferson - 6909 Grade Lane - Louisville","GL1330","Shepherdsville - Grade Lane - NE of Substation",0.55349763257575746,2,"2021-06-12",0,0,0,0,1,0,0,0,0,0,298.79999980000002,105.3499995,0.9,2,"Continue to Monitor"]
["GRADE LANE","Jefferson - 6909 Grade Lane - Louisville","GL1333","Shepherdsville - Grade Lane - NE of Substation",2.7536751893939369,1,"2021-06-12",0,0,0,0,1,0,0,0,0,0,456.21666599999998,621.69999899999993,1.5,2,"Continue to Monitor"]
["GRADE LANE","Jefferson - 6909 Grade Lane - Louisville","GL1334","Shepherdsville - Grade Lane - NE of Substation",2.7478778409090907,1,"2021-06-12",0,0,0,0,1,0,0,0,0,0,456.08333249999998,622.04999899999996,1.5,2,"Continue to Monitor"]
["GRADE LANE","Jefferson - 6909 Grade Lane - Louisville","GL1335","Louisville - Grade Ln & Midfield Access Rd - N of Substation",2.7715047348484858,1,"Underground Circuit",0,0,0,0,1,0,0,0,0,0,419.32999980000005,622.13333299999999,0.8,2,"Continue to Monitor"]
["GRADE LANE","Jefferson - 6909 Grade Lane - Louisville","GL1336","Shepherdsville - Grade Lane - NE of Substation",2.7736250000000053,1,"Underground Circuit",0,0,0,0,1,0,0,0,0,0,453.8749995,619.34999900000003,1.5,2,"Continue to Monitor"]
["GOSS","Jefferson - 1260 Goss Ave - Louisville","GO0001","Louisville - Goss Ave - E of Substation",0.37058428030303026,41,"2018-07-21",0,0,0,0,0,0,0,0,0,1,40.889529616724737,70.246428571428567,0.35017421602787457,0.21428571428571427,"Continue to Monitor"]
["GOSS","Jefferson - 1260 Goss Ave - Louisville","GO0002","Louisville - Reasor Ave, E Burnett Ave, & Texas Avenue - SW of Substation",3.3622312184343435,702,"2018-07-21",4.6837726188398206E-3,0.12105079420492232,0,0,0.30587071623901785,0,0.21684994472566474,0,0.22010822133007504,0.13143655088148018,26.178754365402085,46.317560496657897,0.19370481639249476,0.31303516449736135,"Continue to Monitor"]
["GOSS","Jefferson - 1260 Goss Ave - Louisville","GO0003","Louisville - Ash St & Hickory St - NW of Substation",1.6303434343434342,410,"2018-07-21",0,0,0,0,0.25830023049384532,0,0.69609141287823062,4.5608356627924083E-2,0,0,16.202934995841137,49.5448609799152,0.13944399731814389,0.47182458129591576,"Continue to Monitor"]
["GRADY","Jefferson - 1838 S 39th St. - Louisville","GR1124","Louisville - I 264 East & Stratton Ave - N of Substation",2.0574976325757577,253,"2019-01-26",0.64079995209867668,0.26483444105143406,0,0,9.4365606849889233E-2,0,0,0,0,0,35.692051776736456,65.771713705767013,0.48219587670118302,1.1891008683203137,"Continue to Monitor"]
["GRADY","Jefferson - 1838 S 39th St. - Louisville","GR1463","Louisville - Stratton Ave, Louis Coleman Jr Dr, & Grand Ave - NE of Substation",5.0899303977272741,1794,"2019-01-26",0,0,0,0,1.3729814327381375E-2,0,0,0,0.98627018567261859,0,43.809045951303929,52.404177280100335,0.6999975186457752,1.9781016085363912,"Continue to Monitor"]
["GRADY","Jefferson - 1838 S 39th St. - Louisville","GR1464","Louisville - Algonquin Pky, Virgina Ave, & S 43rd St - NW of Substation",3.3997394255050497,783,"2019-03-16",0,0,0,0,0.99382961783439494,0,2.0302547770700637E-3,0,0,4.1401273885350318E-3,102.77510277862106,199.56915692145591,1.6312039999473344,3.2397828863346101,"Continue to Monitor"]
["HALE","Jefferson - Rear 185 Hale Ave - Louisville","HA0002","Louisville - Dixie Hwy, Hale Ave, Dumesnil St, & St Louis Ave - S of Substation",2.7721014835858586,595,"2019-02-09",0,0,0,0,1.1225298680708906E-2,0,1.9124058660325009E-2,9.0595096540399751E-4,0.69785119755393243,0.27089349413962971,51.396716460881727,118.24148526680105,0.63547461654847481,2.136127810088237,"Continue to Monitor"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1142","Louisville - Hurstbourne Pky, Taylorsville Rd, & Stony Brook Dr - W of Substation",19.954759469696967,2028,"2019-12-14",8.0513057523620757E-2,0,8.3857841899380122E-4,0,0.16640540501908241,0,1.9296832937073267E-3,0.22684975628814696,0,0.52346351945644876,30.404752501512387,80.692744252322171,0.3776011883054996,1.3399894093528038,"Continue to Monitor"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1148","Louisville - Old Hickory Rd, Taylorsville Rd, College Dr, & Rown Tree Rd - S of Substation",19.86028330176768,2278,"2020-07-18",1.4493773306128192E-2,0,0.11870118905227608,0,6.2773517202561038E-2,0,9.27038626609442E-2,0.64697577335303369,3.7484462581204997E-2,2.6867421843851873E-2,45.953103437752489,64.432040091842651,0.36335024674559452,0.64723227762996138,"Continue to Monitor"]
["HURSTBOURNE","Jefferson - 1830 Plantside Drive - Louisville","HB1149","Louisville - Plantside Dr, Production Dr, & Research Dr - E of Substation",2.382044349747475,32,"2019-11-26",0,0,0,0,0.69680589680589677,0,0,0,0.30319410319410317,0,26.995891165591399,61.667676757575755,0.25645161290322582,0.45454545454545459,"Continue to Monitor"]
["HILLCREST","Jefferson - 3015 Frankfort Ave. - Louisville","HC1434","Louisville - Stilz Ave, Lexington Rd, & Alta Vista Rd - S & E of Substation",3.2478847853535346,1,"2021-04-10",0,0,0,0,1,0,0,0,0,0,93.581391057657669,19.216666,0.85069069069069081,1,"Continue to Monitor"]
["HERMAN","Jefferson - Rear 3619 Jefferson St - Louisville","HE0001","Louisville - W Market St, 37th, 36th, 35th & 34th St - NE of Substation",3.5891029040404043,678,"2020-03-28",0,0,0,7.5425494235976498E-2,4.1054623976966758E-3,0,7.919581684610609E-2,0,0.75522227765569716,8.6050948864523552E-2,88.541522490077824,386.05943928612157,0.43420902356136154,1.6239916816876334,"Continue to Monitor"]
["HERMAN","Jefferson - Rear 3619 Jefferson St - Louisville","HE0002","Louisville - Amy Ave, W Market St, 39th, 40th, 41st, & 42nd St - NW of Substation",2.9138617424242423,592,"2020-03-28",0,0,1.8456469020159575E-2,0,9.2504489161221046E-2,0,7.7065476961809737E-2,0.8119735648568096,0,0,36.88298903293056,91.076160038220749,0.39296036010322849,1.2443151126751464,"Continue to Monitor"]
["HERMAN","Jefferson - Rear 3619 Jefferson St - Louisville","HE0003","Louisville - 38th St, Amy Ave, & W Muhammad Ali Blvd - N & SW of Substation",3.0745688131313136,664,"2020-03-28",0,0,0,0,2.8411584028082491E-2,0,0.18352347520842474,4.2014041246160594E-2,0,0.74605089951733217,14.33690920280605,13.14761100543301,0.10885862349030076,0.14903070930337892,"Continue to Monitor"]
["HERMAN","Jefferson - Rear 3619 Jefferson St - Louisville","HE0004","Louisville - W Market St, S 43rd St, & Herman St - W of Substation",1.8840921717171719,295,"2020-03-28",0,0,0,0,0,0.19415384615384615,0,0.80584615384615388,0,0,59.45113760368762,10.939562289562289,0.55771014146955111,1.0437710437710437,"Continue to Monitor"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1101","Louisville - Bardstown Rd, Longest Ave, & Grinstead Dr - NW of Substation",7.6957817234848482,1887,"2021-04-24",1.0077975247235851E-2,0,0,0,3.9665474068853443E-2,0,4.8773808935954358E-2,0.3983965021121102,0.47814942337820915,2.4936816257637041E-2,104.77220980127956,118.17474068241071,0.81658770405635051,0.65763762197343967,"Reliability Improvements Scheduled for 2022"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1103","Louisville - Bardstown Rd, Alta Ave, & Speed Ave - E of Substation",9.1507593118686881,1860,"2021-04-24",8.393204046087889E-2,0,0,0,6.7825562700964629E-3,0,4.8294312700964633E-2,0.74860580787781339,1.323854501607717E-2,9.9146737674169344E-2,84.671126355806962,127.09316892693084,0.74321047103449844,1.4496917383906733,"Trees Trimmed in 2021"]
["HIGHLAND","Jefferson - 1917 Stevens Ave. - Louisville","HI1472","Louisville - Bardstown Rd, Grinstead Dr, Baxter Ave,  & Payne St - NW of Substation",5.9123432765151511,350,"2017-04-01",0,0,0,0,0.34012706974933615,0,0,0,0.25085848545093076,0.40901444479973309,107.75156386462454,205.36371361714285,1.2372981401235525,2.5742857142857143,"Continue to Monitor"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1238","Louisville - Timber Bridge Dr & Fox Harbor Rd - E of Substation",10.443365688131314,429,"2018-08-25",0,0,0,0,1.331891469174044E-2,0,5.4558673484973452E-3,0,0,0.98122521795976225,169.06207531702736,381.53216782517484,0.72696244853510139,0.66899766899766899,"Continue to Monitor"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1241","Louisville - River Rd, Avish Ln, & Rockledge Dr - SW of Substation",19.790134311868684,540,"2018-06-09",1.8454414923811537E-2,0,0.13236423538839975,0,0.1768529545985775,0,1.8409892813018264E-2,0.19009828255957614,3.5506383357634987E-3,0.46026958138085328,131.63740303174967,123.01137228341672,1.1234418159681052,1.2718902527903904,"Continue to Monitor"]
["HARRODS CREEK","Jefferson - 6611 Del Haven Rd. - Louisville","HK1242","Louisville - River Rd, Shirley Ave, & Duroc Ave - N of Substation",10.871148674242423,582,"2018-06-09",5.8399929744445418E-2,0,0,0,0,0,0,0.17116009484499869,0,0.77043997541055587,18.546890323975745,19.549855780056941,0.36361053671129612,1.1991653551661332,"Continue to Monitor"]
["HARMONY LANDING","Oldham - 11943 W Hwy 42 - Goshen","HL1155","Goshen - Goshen Ln - NW of Substation",15.08917960858586,383,"2021-12-18",2.123383704626889E-2,0,0,0,9.5918367346938774E-2,6.7611777535441656E-3,1.7307991899049698E-2,0.38563639196136468,0,0.47314223399283378,41.049187182084445,95.281441025816122,0.36877004281588516,0.39068651574803148,"Trees Trimmed in 2021"]
["HARMONY LANDING","Oldham - 11943 W Hwy 42 - Goshen","HL1156","Goshen - US 42, Harmony Landing Rd, & Hwy 1793 - W & SW of Substation",46.324351483585843,1250,"2021-12-25",8.3473273821799299E-3,1.2137996052205167E-2,0,0,0.34878079918294397,0,2.1909279281933439E-2,0.60564279331035364,0,3.1818047903838789E-3,96.867382451137686,76.299026613943823,0.91604942783148446,1.4880100275949717,"Trees Trimmed in 2021"]
["HANCOCK","Jefferson - 630 E Caldwell St - Louisville","HN1204","Louisville - S Preston St, E Broadway, S Shelby St, & E Madison St - N of Substation",8.6276272095959623,1223,"2018-07-06",0,1.2005586758194407E-2,0,0,3.771061781224927E-2,0,0.35974166196150686,0,0.44125484136182186,0.14928729210622765,40.885318123388927,82.452639277552436,0.64130810258044413,0.42325492481229432,"Continue to Monitor"]
["INTERNATIONAL","Jefferson - 5599 Cane Run Rd. - Louisville","IN1290","Louisville - Cane Run Rd, Greenbelt Hwy, & Rockaway Dr - ENE of Substation",13.824608112373735,1146,"2021-11-27",1.4301328446592967E-3,0,0.32814207798846107,0,6.7863338027939254E-3,0,7.3953637594549181E-4,0.34712532422688541,0,0.3157765947612548,69.324681118732514,103.43184083346905,0.8419543789114462,1.2689219491810497,"Trees Trimmed in 2021"]
["INTERNATIONAL","Jefferson - 5599 Cane Run Rd. - Louisville","IN1291","Louisville - Lower Hunters Trace, Terry Rd, & Mt Everest Dr - ESE of Substation",33.637075599747476,3004,"2021-11-27",3.1902195536586252E-3,0,0,4.2073281006980864E-2,0.37762505877672081,0,2.629580062936304E-3,0.4936484971244619,7.0604405541288386E-3,7.3772922921112594E-2,52.24075954266128,84.850845444471645,1.0089599734583288,1.2642151671464374,"Trees Trimmed in 2021"]
["INTERNATIONAL","Jefferson - 5599 Cane Run Rd. - Louisville","IN1292","Louisville - Logistics Dr, International Dr, & Riberport Dr - SE of Substation",4.7324649621212123,44,"2021-10-02",0,0,0,0,1.8551919608348365E-2,0,0.98144808039165166,0,0,0,61.76192114493999,86.23259257777778,0.36607626790553616,0.22222222222222224,"Continue to Monitor"]
["INTERNATIONAL","Jefferson - 5599 Cane Run Rd. - Louisville","IN1293","Louisville - Cane Run Rd, Port Rd, & Intermodal Rd - S of Substation",4.8657095959595971,254,"2021-10-02",0.78473075182623309,0,0,0,3.5425690089857131E-2,0,1.5127028250048483E-2,0.12205055271833991,0,4.2665977115521364E-2,16.669647834256484,53.742556868576017,0.33765593120179377,1.2450230072422896,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1124","Louisville - Ramblin Creek Rd, Rehl Rd, & Pope Lick Rd - NE of Substation",14.845526041666666,461,"2019-04-06",1.3930931906023819E-3,2.2205695970504134E-3,1.785882624042903E-3,0,0,0,0,0.94900021996208273,0,4.5600234626221578E-2,124.42509488676524,413.36587925581489,0.5578627916610952,1.3335886731719584,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1125","Louisville - Blankenbaker Pky & Chenoweth Run Rd - NW & SW of Substation",13.120112847222222,422,"2019-04-06",4.2057402671213412E-2,1.6339869281045753E-2,0,0,5.0866723500994603E-2,0,8.1841432225063945E-2,0.57502131287297531,0,0.23387325944870702,17.936438973509528,14.11526933436237,0.12728233587170723,0.12908729213967549,"Continue to Monitor"]
["JEFFERSONTOWN","Jefferson - 11412 Taylorsville Rd. - Louisville","JT1127","Louisville - Taylorsville Rd, Old Routt Rd, & Taylorsville Lake Rd - SE of Substation",43.600912247474739,380,"2020-06-27",1.6066767563773551E-3,0,0,0,0.15049022833453973,0,1.0254216841043189E-3,0.82659406461801666,0,2.0283608606961899E-2,81.789835061729349,117.84090478659385,0.6787275804759858,1.4376387772707093,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1156","Louisville - Strawberry Ln, Southside Dr, & National TPke - S of Substation",12.544377051767675,1266,"2020-12-19",0.122718010404848,0,0,4.7432749847266546E-4,0.38240662388865065,0,3.5517643085633188E-3,0.31298784583217915,0,0.17786142806728619,61.631383983002266,131.68489792999188,0.59867453755510358,1.3981723542488385,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1157","Louisville - S 3rd St - NW of Substation",2.0325751262626262,303,"2020-12-19",0,0,0,0,2.1514755051606337E-3,0,8.0593109463584819E-2,1.9537723506323594E-2,0.89745602558511417,2.6166593981683385E-4,45.073246513438633,113.17866043747929,0.44384874541583086,1.0561056824574058,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1158","Louisville - Inverness Ave, New Cut Rd, & Palatka Rd - W & SW of Substation",19.558025726010101,2409,"2021-07-28",3.4001836498409696E-2,4.4315505103602465E-3,0,0,4.1148210744846495E-2,0,5.2459976311832107E-2,0.34719135514951494,0.29880361444179765,0.22196345634323889,27.50491329140393,31.211136494365174,0.21758984975109025,0.22407385944364483,"Trees Trimmed in 2021"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1159","Louisville - Kenwood Dr, Homestead Dr, & Southside Dr - SW of Substation",12.439545928030304,1433,"2021-07-17",7.2365575897361978E-2,3.8866280036814853E-2,0,0,0.26331488894556504,0,0.14861223539326465,0.17489271576052604,0.1204910125192668,0.18145729144720063,60.550806180597121,62.944059117050912,0.94570036481972974,1.3397378232809463,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1160","Louisville - Steedly Dr, Enterprise Dr, & National TPke - SE of Substation",6.9730696022727265,126,"2021-07-28",0,0,0,0,0,0,6.6164646821194648E-2,0,0,0.93383535317880539,59.161056723850209,201.53523933189598,0.8314127559991269,2.0555555555555554,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1161","Louisville - Southside Dr, 3rd St, & W Kenwood Way - N of Substation",5.8075053661616156,738,"2021-07-17",2.8289621938324464E-2,0,0,0,0.43595832827748793,0,4.7253375860215989E-2,3.6506093015999587E-2,0.41016484945136855,4.1827731456603512E-2,52.273967339207353,78.190338082937288,0.49359823847320755,0.73457386976477557,"Continue to Monitor"]
["KENWOOD","Jefferson - 115 Steedly Dr. - Louisville","KE1162","Louisville - Strawberry Ln & Eiler Ave - E of Substation",2.7674136679292918,79,"2020-12-19",0,0,0,0,0,0,0.28329369797859694,0,0,0.71670630202140306,16.885715042989908,40.708269879302293,0.13815541333662587,0.25269740807715491,"Continue to Monitor"]
["LOGAN","Jefferson - Rear of 1130 Logan St, St Catherine St - Louisville","LG0003","Louisville - Logan St, E Kentucky St, & Swan St - NE of Substation",1.3845972222222225,287,"2018-07-21",0,0,0,0,0.21108505122824342,0,0,0,0,0.78891494877175661,26.818130850225806,28.2186278044909,0.1977116095163175,0.23326800232288039,"Continue to Monitor"]
["LYNN","Jefferson - Rear of 2071 S Preston St & Lynn St - Louisville","LN0002","Louisville - Preston St & Miller Ave - S of Substation",2.5554169823232327,482,"2018-07-21",0,0,0,0,0.43549129400935799,0.12146199278975224,0,0,0,0.44304671320088979,33.012527168077938,39.95318462444267,0.31975911578438226,0.41421612845029765,"Continue to Monitor"]
["LYNN","Jefferson - Rear of 2071 S Preston St & Lynn St - Louisville","LN0004","Louisville - Preston St & Gernert Ct - NW of Substation",2.220891414141414,497,"2018-07-21",0,0.45342576886201047,0,0,4.8897411313518699E-2,0,3.1123239176930453E-2,0,0.10989010989010989,0.35666347075743049,22.589346932703982,27.171676685370738,0.21366558838129684,0.29659318637274545,"Continue to Monitor"]
["LOCUST","Jefferson - 2929 Preston Hwy - Louisville","LO1193","Louisville - Preston Hwy, Belmar Dr, & Phillips Ln - SE of Substation",12.469428345959592,1291,"2020-02-08",2.6824434078953251E-2,8.5093065883790592E-2,0,0,1.1638823897590272E-2,1.1325872166669151E-3,0.67214580570168247,0.12342220168993935,7.2902850841244052E-2,6.8402306901330793E-3,90.676595955610281,92.197787357542552,1.5500326866070238,1.0410832593123482,"Continue to Monitor"]
["LYNDON SOUTH","Jefferson - 918 Ormsby Ln. - Bellemeade","LS1244","Lyndon - New La Grange Rd, La Grange Rd, Whipps Mill Rd - N & NE of Substation",16.894655776515151,1906,"2021-07-24",1.8906498769720653E-2,0,0.21432792975346165,0,0.3189800742992232,0,2.9345780865537706E-2,0.32103657065663144,0,9.7403145655425294E-2,77.839642366628397,86.964844342348101,0.52617208320459741,0.61146733385753382,"Trees Trimmed in 2021"]
["LYNDON  ","Jefferson - 8407 LaGrange Rd. - Louisville","LY1112","Louisville - New La Grange Rd & Willow Springs Dr - E & SW of Substation",1.8895530303030303,176,"2021-01-23",0,0,0,0,0,0,0,0,1,0,27.787720753103759,65.285310728813556,0.13886935431647854,9.03954802259887E-2,"Continue to Monitor"]
["MILL CREEK - LGE","Jefferson - 14660 Dixie Hwy - Louisville","MC1262","Louisville - Watson Ln, Galston Blvd, & Dixie Hwy - NE & S of Substation",19.733466224747474,1302,"2019-10-12",3.5250632911392403E-2,0,0,0,4.091139240506329E-3,1.0126582278481013E-4,7.1291139240506332E-3,0.89662784810126583,1.0187341772151899E-2,4.6612658227848103E-2,67.150569763032479,55.035629295066968,1.1772994487075918,1.5047871958440713,"Continue to Monitor"]
["MADISON","Jefferson - 635 E Madison - Louisville","MD1451","Louisville - Madison St, Wenzel St, Baxter Ave, & Lexington Rd - E of Substation",2.1698080808080804,17,"2018-07-28",0,0,0,0,1,0,0,0,0,0,46.87025641025641,104,0.44205128205128197,1,"Continue to Monitor"]
["MADISON","Jefferson - 635 E Madison - Louisville","MD1452","Louisville - Clay St, E Main St, & River Rd - N of Substation",8.8266739267676755,457,"2018-07-28",2.886029754035787E-3,0,0,0,0.88338577839015398,0,0.11222000856499152,0,0,1.5081832908187015E-3,121.47129890724469,117.99691970001565,1.3054815189332931,2.0273594458900739,"Continue to Monitor"]
["MADISON","Jefferson - 635 E Madison - Louisville","MD1457","Louisville - Clay St, E Main St, Story Ave, & Buchanan St - NE of Substation",2.5533855744949494,98,"2018-07-28",0,0,0,0,0,0,1.5637860082304528E-2,0,0,0.9843621399176955,8.2715900316771798,36.441333329999999,0.21218346732632448,1.01,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG0417","Louisville - 15th St, Cedar St, Chestnut St, 18th & 19th St - NW of Substation",5.0767290088383845,748,"2020-02-01",1.0670081092616304E-4,1.9788896549459929E-2,3.296234282149775E-2,0,0.37501231163202992,2.6708033750287272E-2,1.8984536590170391E-2,0,1.3944975212580847E-2,0.51249220263304773,114.29995900341478,162.88577045203931,0.83492906683048851,1.7260290359298156,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG1328","Louisville - 15th St, 13th St, 12th St, 11th St & W Kentucky St - S of Substation",5.5631661931818179,53,"2020-02-01",0,0,0,0,0.37166638064183971,0,8.0487386305131293E-3,0,0,0.6202848807276472,153.25786126812773,217.44798470588233,3.2918400913529808,8.1492374727668846,"Continue to Monitor"]
["MAGAZINE","Jefferson - 646 S 13th St. - Louisville","MG1329","Louisville - W Broadway, 9th St, 8th St, 7th St, & 5th St - SE of Substation",4.5025369318181809,136,"2020-02-01",0,0,0.47369199755876534,0,0,0,0,3.5323925949214919E-3,0,0.52277560984631322,126.89665752698457,117.75563515827338,1.557442978544064,2.0071942446043165,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1290","Louisville - 3rd Street Rd, Chistland Rd - N of Substation",12.055337121212121,482,"2018-01-06",0,0,0,0,2.836181003495987E-3,0,0,0,0.89917770446600032,9.7986114530503723E-2,102.53999018007346,421.26211122575882,0.42632340078883735,1.1852701390857623,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1291","Louisville - Saint Anthonys Church Rd - NW of Substation",8.1807397411616165,144,"2018-01-06",4.4363044363044363E-2,0,0,0,0,0,0,0.86487586487586487,9.0761090761090762E-2,0,84.846729922588025,86.306807251603942,0.59151544227139718,0.37025249789334302,"Tree Trim Scheduled for 2022"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1292","Louisville - Outer Loop & National Tpike - NE of Substation",17.177491003787878,1338,"2021-10-30",1.1364726191617914E-3,0,0.70662462836865825,0,0.11437853649180013,0,4.7472906876378628E-3,0,4.5434928550877529E-3,0.16856957897765418,42.907877768548666,55.284320718632252,0.36120539348666669,0.35624811054802813,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1293","Louisville - Manslick Rd and Brown Austin Rd - SE of Substation",18.64360085227273,1299,"2019-01-26",3.9379146845673792E-2,9.9498358121462693E-3,0.13355501719692686,0,5.446471647118023E-2,0,4.9334170267732545E-3,0.55933328837404739,1.3036463710074856E-2,0.18534811456317732,38.192995612959926,47.173606410536415,0.28309667801605459,0.48402209832091997,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1294","Louisville - Greyling Dr and Blevins Gap Rd - SW of Substation",21.363781881313134,421,"2019-05-04",1.3148307429341544E-4,0,1.8078922715344622E-4,0,8.1434589909769733E-2,0,2.3760087217105947E-2,0.86696652112220807,2.7340261760887073E-2,1.8626768858233853E-4,503.55407587057243,791.55651999294025,4.1926093867113652,5.9078475660845537,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1295","Louisville - Outer Loop, New Cut Rd, & Scottsdale Blvd - NE of Substation",19.067373737373735,1779,"2017-10-07",3.8025718977093531E-2,0,0,3.7911918193493849E-2,7.6571670107785594E-2,0,0.1363983677716181,1.7541577929150884E-2,9.9624457414121056E-2,0.59392628960673699,37.87619401818263,27.940119856341362,0.56225462600928655,1.1011258120931462,"Continue to Monitor"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1296","Louisville - 3rd St Rd, Christland Rd, & Manslick Rd - N of Substation",17.258235321969696,1740,"2018-01-06",6.3276730926437571E-3,0,7.9527933856931465E-2,0,0.24166744275085628,0,8.2373575885512057E-2,0.53196949471745358,0,5.8133879696602823E-2,46.057035926421761,51.068711970906584,0.3757167409096801,0.55529607275897208,"Tree Trim Scheduled for 2022"]
["MANSLICK","Jefferson - 8703 Manslick Rd. - Louisville","MK1299","Louisville - Arnold Town Rd, Timber Hills Rd, & St Andrews Church Rd - NW of Substation",17.312778093434346,788,"2017-12-30",1.5391755423831371E-3,0,0,0,6.5080101750077834E-2,0,9.2996751282156728E-3,0.92129055756927758,9.1645566645713519E-4,1.8740343435886288E-3,68.945395304449249,85.533466538216814,0.28406445630111776,0.38151165628050687,"Tree Trim Scheduled for 2022"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1284","Louisville - Christman Dr, Mount Washington Rd, & Cedar Creek Rd- E of Substation",52.353489109848489,2695,"2019-08-24",9.0208630596583239E-2,0,0,8.3606494157572025E-3,0.52465388916740585,0,1.4214646562030003E-2,5.2369750491689487E-2,5.3372411399483241E-3,0.30485519262658595,31.325069744566473,45.508615322121614,0.48929084319984978,1.2660896452420485,"Continue to Monitor"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1285","Louisville - Preston Hwy, Lees Ln, Rogers Ave, & Zoneton Rd - S of Substation",28.215085858585859,1713,"2019-06-15",2.4325747515911902E-2,0,0,0,0.48163835340445993,0,1.583176885388525E-2,2.5069829204633913E-3,0,0.47569714730527957,72.30040048619523,50.624897841988059,0.45071276433283025,0.89299841413386827,"Continue to Monitor"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1286","Louisville - Overdale Dr, Blossom Rd, Summers Dr, & Summit Dr - SW of Substation",27.145553030303027,2560,"2019-06-15",6.5057299652973938E-2,4.3781777096279558E-3,0.15922847227826648,0,0.16606306997013962,0,8.5162618029214751E-2,0.16622952142684208,0,0.3538808409329352,31.696444067827485,64.792813701665139,0.57854409879465973,1.0380788510156711,"Continue to Monitor"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1288","Louisville - Preston Hwy, Hebron Ln, & Bells Mill Rd - S of Substation",37.902866319444456,1610,"2019-08-03",0.16758464120027639,0,9.4758661533905829E-4,1.7175007403020433E-3,0.34969894383575167,0,0,0.39828249925969794,0,8.1768828348632902E-2,57.251873203278663,26.931694655355784,0.76584363092389052,1.2447723335609655,"Continue to Monitor"]
["MUD LANE","Jefferson - 4900 Mud Ln. - Louisville","ML1290","Louisville - Southpoint Dr - NW of Substation",0.74792645202020192,2,"2019-07-13",0,0,0,0,1,0,0,0,0,0,2763.5966665999999,13627.3666665,0.4,1,"Continue to Monitor"]
["MULDRAUGH","Meade - 100 Carpenter Test Rd. - Muldraugh","MU1101","Muldraugh - Carpenter Test Rd, Main St, & Dixie Hwy - E & SE of Substation",10.27820817550505,558,"2021-11-27",4.366004746103983E-3,0,6.2665009297021873E-4,0,3.0890767697728649E-2,0,1.0889329484400521E-2,0.95175821579363695,0,1.469032185159693E-3,79.158325145918951,172.69313466643365,1.3790743629794107,2.0269171122822591,"Trees Trimmed in 2021"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1266","Louisville - Six Mile Ln, Stony Brook Dr, & Hampton Ridge Ct - E of Substation",31.272414614898992,2678,"2021-07-26",1.5481498802602826E-3,2.2456236544400456E-2,0.13849490803828446,0,7.8213822075649697E-2,0,0.12360202872140559,0.17794854014304259,1.0393568727372418E-2,0.4473427458695845,29.686728427625518,43.180815395884217,0.48087181314330757,1.1246988988136892,"Reliability Improvements Scheduled for 2022"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1267","Louisville - Breckenridge Ln & Bardstown Rd - S of Substation",12.844995265151516,1418,"2021-09-11",1.328274396721809E-2,0,0,0,6.2947336469874021E-2,0,6.2006374260130517E-2,7.2727272727272727E-3,0.71490666261951741,0.13958415541053271,56.316938574964084,116.08322761804089,0.52590768808766541,1.4453840732910503,"Continue to Monitor"]
["NACHAND","Jefferson - 7201 Verona Way - Louisville","NA1269","Louisville - Wisteria Landing Cir, Beargrass Ave, Bardstown Rd & Fegenbush Ln - SW of Substation",22.935481218434344,2622,"2021-10-23",0.57714912215277669,1.5356732648160025E-2,0,0,0.27704768865884039,0,2.3933829561896807E-2,0.10526708333954862,0,1.2455436387774281E-3,55.834395498889322,51.135976394028134,1.0248262985500243,1.5145036681712065,"Continue to Monitor"]
["OLD HENRY","Jefferson - 13601 Terra View Trail - Louisville","OH1174","Louisville - Bush Farm Dr and Aiken Rd - SE of Substation",19.648862058080809,876,"2020-11-21",0.68625696101829758,0,0,0,6.3345266507557674E-2,0,7.5676213206046145E-2,0,0,0.17472155926809865,15.653912356773963,10.935311214950218,0.128556687822728,0.15868382255195954,"Continue to Monitor"]
["OKOLONA","Jefferson - 811 N 27th St. - Louisville","OK1271","Louisville - Outer Loop, Robbs Ln, & Monaco Dr - E of Substation",10.946594065656566,952,"2019-05-04",2.0480893087161871E-2,0,0,0,0.18329755259768141,0,2.8166595105195362E-2,0.71118505796479181,0,5.68699012451696E-2,13.5091699888922,14.249813588217927,0.11518455491568425,0.15325665868679145,"Continue to Monitor"]
["OKOLONA","Jefferson - 811 N 27th St. - Louisville","OK1274","Louisville - Preston Hwy, Miles Ln, & Cooper Ave - S of Substation",12.809936237373739,1342,"2019-05-04",9.0676744881590041E-2,0,0,0,1.9086978982571577E-2,3.825552625139346E-2,3.7222327958889585E-2,0.26409092144974033,0.40430680551401615,0.14636069496179885,40.958029234982739,25.553756812261067,0.55869828151412426,1.4788504282846531,"Continue to Monitor"]
["ORMSBY","Jefferson - Rear of 436 E Ormsby Jackson St - Louisville","OR0001","Louisville - Jackson St, Oak St, & Preston St - N of Substation",2.4601988636363634,586,"2020-02-29",0,0,0,0,1.3067215609057549E-2,0,0.46907723977445626,3.0520003580059071E-2,0,0.48733554103642712,42.015133800421481,38.114400142162268,0.35058739915082776,0.40056572549062369,"Continue to Monitor"]
["OXMOOR","Jefferson - 8004 Shelbyville Rd - Louisville","OX1274","Louisville - Shelbyville Rd, Oxmoore Ln, Bramton Rd, & Sherburn Ln - W of Substation",20.569037563131317,2630,"2019-03-16",5.2327864724806611E-3,0,0,0,0.25036091721551168,0,3.8899691698014577E-2,0.14186817592781381,0,0.56363842868617919,137.73622456712323,250.20896749777322,1.5269221925311016,2.2828252656536798,"Continue to Monitor"]
["OXMOOR","Jefferson - 8004 Shelbyville Rd - Louisville","OX1275","Louisville - Christian Way & Oxmoor Ln - W of Substation",0.83349463383838363,89,"Underground Circuit",0,0,0,0,1,0,0,0,0,0,224.78978481290324,613.06666666666672,0.60430107526881716,1,"Continue to Monitor"]
["OXMOOR","Jefferson - 8004 Shelbyville Rd - Louisville","OX1278","Louisville - Christian Way & Oxmoor Ln - W of Substation",0.83201672979797991,5,"Underground Circuit",0,0,0,0,1,0,0,0,0,0,301.95999992333338,614.08333319999997,0.8,1,"Continue to Monitor"]
["PIRTLE","Jefferson - Rear 1506 W Main St - Louisville","PI0002","Louisville - W Market St, 22nd St, 19th St, & Cedar St - W of Substation",4.7018773674242436,544,"2019-01-12",0,8.4117163791224456E-2,0,0,5.6955552202270172E-2,0,0.15589423737907215,0,0.18778398135573329,0.5152490652717,95.229781695764302,109.49545750862758,0.82677415789842712,0.55038011543771825,"Continue to Monitor"]
["PIRTLE","Jefferson - Rear 1506 W Main St - Louisville","PI0003","Louisville - Main St, 15th St, Rowan St, & Portland Ave - NW of Substation",5.194769412878788,562,"2019-01-12",0,0,0,4.8491157427532086E-2,5.405065318355487E-2,0,0,2.1826168523645016E-2,0.66296414925987779,0.21266787160539019,135.64620971303739,153.133172173237,0.80094818026534187,0.47753266368999059,"Continue to Monitor"]
["PLEASURE RIDGE","Jefferson - 4400 Atlas Power Rd. - Louisville","PL1272","Louisville - Dixie Hwy, Greenwood Rd, Sky Blue Ave, & Galaxie Dr - NW of Substation",14.83243023989899,1436,"2018-10-06",3.1880031345729143E-2,0,0,0,3.7965139749709102E-2,0,3.826791099712664E-2,2.5587138752344992E-3,0.83875353233121985,5.057467170098074E-2,94.774011337483643,117.36443080371532,1.0401540977112371,1.1991338570544161,"Continue to Monitor"]
["PLEASURE RIDGE","Jefferson - 4400 Atlas Power Rd. - Louisville","PL1274","Louisville - Dixie Hwy, Lower Hunters Trace, & Flintlock Dr - N of Substation",11.511386521464644,1247,"2018-10-06",4.4500129612027994E-3,2.8004838849045192E-2,0,0,0,2.8419597338633026E-2,3.922924047351594E-2,1.3989458221722977E-2,0.88590685215588005,0,81.729929545023083,93.875996075692925,0.88497903939103861,0.44926757446799415,"Continue to Monitor"]
["PLEASURE RIDGE","Jefferson - 4400 Atlas Power Rd. - Louisville","PL1276","Louisville - Dixie Hwy, Cofer Ave, and Fury Way - W of Substation",2.3541671401515152,255,"2018-10-06",0.86141066744389394,0,0,0,0,0,0,0,0,0.13858933255610609,13.625087099158563,26.905751627450982,0.23334105295661572,0.46274509803921571,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1380","New Albany - Bells Ln & Algonquin Pky - NE of Substation",2.2529682765151517,1,"2021-12-04",0.20704845814977973,0,0,0,0.61674008810572689,0,0,0,0,0.1762114537444934,79.403333000000003,228.01666500000002,1.6,4,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1386","New Albany - Campground Rd - SE of Substation",2.2107664141414145,1,"2021-12-04",0,0,0,0,0,0,0,1,0,0,15.076666599999999,75.383332999999993,0.2,1,"Trees Trimmed in 2021"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1387","New Albany - No Road - SE of Substation",0.30052225378787878,1,"2021-12-04",0,0,0,0,1,0,0,0,0,0,72.8633332,108.63333299999999,0.4,1,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1389","New Albany - Campground Rd & Senn Rd - S of Substation",4.7042247474747461,7,"2021-12-04",0,0,0,0,0.72486772486772488,0,0,0,0,0.27513227513227512,94.123174523809524,27.097618857142855,0.57619047619047625,1.2857142857142856,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1390","New Albany - Algonquin Pky & Gibson Ln - NE of Substation",2.8557168560606057,14,"2021-12-04",0,0,0.45600814663951122,0,0.54399185336048883,0,0,0,0,0,166.63534185970695,350.71666664285715,1.4628205128205127,2,"Continue to Monitor"]
["PADDYS RUN","Floyd - 4222 Hwy 111 - New Albany","PR1392","New - Albany - No Road - SE of Substation",0.16448137626262624,1,"2021-12-04",0,0,0,0,1,0,0,0,0,0,42.230000000000004,211.15,0.2,1,"Continue to Monitor"]
["PLAINVIEW","Jefferson - 9900 Shelbyville Rd - Louisville","PV1250","Louisville - Shelbyville Rd, Dorsey Ln, & Ward Ave - NE of Substation",33.613041035353532,2842,"2020-02-08",0.18275720666304626,0,0,0,7.214236368942728E-2,3.4689512241075486E-3,4.688440892987103E-2,0.64604136881342655,0,4.8705700680121318E-2,55.88345490929332,95.342026902341743,0.46519183309179796,1.1800574081903636,"Continue to Monitor"]
["SEVENTH","Louisville - 1231 S 7th St - Louisville","SE0002","Louisville - Ormsby Ave, 6th St, & 4th St - SE of Substation",1.883493213383838,432,"2019-12-21",0.10329346447787792,0,0,0,6.7617121902738275E-2,0,0.2808869392371226,0.53634463141300248,0,1.1857842969258714E-2,30.254739930758433,68.662457747043661,0.19085440566587791,0.3305078717105443,"Continue to Monitor"]
["SEVENTH","Louisville - 1231 S 7th St - Louisville","SE0004","Louisville - Oak St, Garvin Pl, & 4th St - NE of Substation",1.9400176767676764,552,"2019-12-21",0.17624211037384691,0,0,0,0.42380104655553757,0,0,0.15218212224200248,0,0.24777472082861304,17.545282100485764,33.519529837251355,0.12258765518927381,0.25497287522603979,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1281","Louisville - 7th Street Rd, Arcade Ave, Taylor Blvd, & Clara Ave - NE of Substation",12.666589646464651,1638,"2021-12-25",4.3120629665912236E-2,9.1342093706718919E-2,0.2626085194068169,4.3593554707293182E-2,5.3035165354862685E-3,0,0.24565077863730028,0,0.23033138533256764,7.8049522007904604E-2,25.528648600660794,36.42412180950511,0.23030861602676539,0.24768928655686917,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1283","Louisville - Elderwood Way & Crums Ln - S of Substation",0.83799384469696969,9,"2021-12-25",0,0,0,0,0,0,0,0,0,1,62.865925911111106,214.58888888888887,0.35555555555555557,0.66666666666666663,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1284","Louisville - Manslick Rd - S of Substation",9.0731996527777774,1319,"2022-01-01",0.12094170403587444,1.4278026905829596E-2,0,0,0.68290582959641255,0,2.134529147982063E-2,1.8645739910313902E-2,0,0.14188340807174887,80.771575311991214,84.474555569597015,0.96749601525930762,0.45608013939893866,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1285","Louisville - Nobel Pl, Dixie Hwy, & Appleton Ln - NW & SW of Substation",8.2407035984848473,1117,"2021-12-25",2.8551894876019117E-3,1.7107042499555759E-3,0,3.0548720435386281E-2,0.17418462956325842,0,1.7703379544434638E-2,4.2147174777954807E-2,0.60625491300406287,0.12459528893734546,107.27651842184619,297.08980533541336,1.2673390743800987,3.6215755342877265,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1456","Louisville - Dixie Hwy, Ralph Ave, & Fitzgerald Rd - N of Substation of Substation",3.457009627525252,22,"2021-08-07",0,0,2.6322786492954001E-2,0,0,0,0.25285828237170965,5.5836213772932727E-2,0.66498271736240366,0,180.9389196071146,167.35974962648223,0.74980237154150198,1.6126482213438735,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1457","Louisville - Crums Ln & San Jose Ave - SW of Substation",2.4110280934343438,48,"2021-08-07",0,0,0,0,0,0,0,0,0,1,19.053333333333335,95.26666666666668,0.4,2,"Continue to Monitor"]
["SHIVELY","Jefferson - 3624 Elderwood Way - Louisville","SH1458","Louisville - 7th Street Rd, Arcade Ave, Taylor Blvd, & Berry Blvd - NE of Substation",5.2571199494949497,9,"2021-08-07",0,0,0,0,1,0,0,0,0,0,38.852857,68.983333285714281,0.42857142857142855,1,"Continue to Monitor"]
["SKYLIGHT","Oldham - 8617 W Hwy 42 - Skylight","SK1127","Skylight - Hwy 42, Axton Ln, Shiloh Ln, & Hwy 1694 - W of Substation",27.149012626262632,267,"2018-04-21",0,0,0,0,8.8706985025904808E-2,0,8.6184511518059177E-3,0.65897147379224219,0,0.24370309003004711,128.47777149232124,244.36586308777743,0.9056596995493077,2.6463189669629386,"Tree Trim Scheduled for 2022"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1232","Louisville - Tug Rd, Crittenden Dr, Woodlawn Ave, & 1st St - S of Substation",11.504466224747478,1481,"2022-02-19",6.0013540961408263E-2,1.5274204468517264E-2,0,0,9.489505754908599E-2,0,6.7433987813134734E-3,0.39691266079891674,0.22323628977657414,0.20292484766418414,27.655087149807468,24.917675041744026,0.27742643657032429,0.2827873870837323,"Trees Trimmed in 2022"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1233","Louisville - Whitney Ave, 5th St, Bluegrass Ave & Taylor Ave - SW of Substation of Substation",14.43096038510101,2758,"2017-09-16",0.26450372876143613,0,2.1757515184131623E-3,9.9892365649265777E-2,4.2492504036288153E-2,0,4.7505189513338972E-2,0.10411316983162913,5.0226800953332817E-2,0.38909048973629584,41.653118951516397,46.646446079356053,0.46162426274554258,0.77988729760044939,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1360","Louisville - Allmond Ave, Strawbery Ln, & Crittenden Dr - S of Substation",7.8374910037878802,103,"2021-08-21",0,0,0,0,0.93776398147676965,0,6.2236018523230373E-2,0,0,0,64.841959991428979,190.79223299029124,0.52197458966490307,1.1359223300970873,"Continue to Monitor"]
["SEMINOLE","Jefferson - 4161 Park Blvd. - Louisville","SM1362","Louisville - Crittenden Dr, Phillips Ln, & Air Freight Dr - E of Substation",2.8248257575757574,17,"2021-08-21",0,0,0,0,0,0,0.419175911251981,0,0,0.58082408874801905,36.191895420915031,74.237254882352943,0.8,2,"Continue to Monitor"]
["SHAWNEE","Jefferson - Rear of 3908 W Broadway - Louisville","SN0002","Louisville - Broadway, 37th St, & Lindell Ave - E of Substation",2.453613952020202,539,"2020-03-28",0,0,0,0,0.3737373737373737,0,8.0703946683328129E-2,0,0,0.54555867957929816,30.793676641753741,35.618684862045626,0.80376098328916556,0.28376966948395521,"Continue to Monitor"]
["SHAWNEE","Jefferson - Rear of 3908 W Broadway - Louisville","SN0003","Louisville - 40th St & Garland Ave - S of Substation",1.5587244318181817,273,"2020-03-28",4.0684931506849313E-2,0,0,0,0,0,0.13607305936073058,0,0.17132420091324202,0.65191780821917811,15.086998819370621,45.197179862864189,0.17766215612588671,0.42030019377050792,"Continue to Monitor"]
["SHAWNEE","Jefferson - Rear of 3908 W Broadway - Louisville","SN0004","Louisville - Broadway, 40th, 41st, 42nd, 43rd, & 44th St - W of Substation",2.7270167297979797,632,"2020-03-28",0,5.0438355734696759E-2,0,0,0.41621053622120102,0,0.26241746522168724,0.27093364282241494,0,0,77.197617815963056,98.905402188923986,0.60224947892662894,0.51385681395141236,"Continue to Monitor"]
["SOUTHERN","Jefferson - 1475 S 3rd Street - Louisville","SO0409","Louisville - 3rd St - S of Substation",1.9709801136363632,176,"2020-02-01",0,0,0,0,0,0,1,0,0,0,26.336721932727492,35.079166664772728,0.45033093806234092,0.13068181818181818,"Continue to Monitor"]
["SOUTHERN","Jefferson - 1475 S 3rd Street - Louisville","SO0421","Louisville - Burnett Ave, Brook St, & Lee St - E of Substation",2.9005266729797983,511,"2020-02-01",0,0,0.3319041020680279,0,7.5740542236398339E-2,0,1.35951266699783E-3,0.39091218071060679,0,0.20008366231796909,66.951528274050219,91.111487381115452,0.63745331589427834,0.54188325587084152,"Continue to Monitor"]
["SOUTHERN","Jefferson - 1475 S 3rd Street - Louisville","SO0453","Louisville - 3rd St, Oak St, & Brook St - N of Substation",2.3091439393939392,628,"2020-02-01",0,0,0,0,0.14210951793388077,0,0,0.53890992639237545,0,0.31898055567374378,31.499021127007911,37.445376065367967,0.23524592200492536,0.4209538999012683,"Continue to Monitor"]
["SOUTH PARK","Jefferson - 1412 Fairdale Rd. - Louisville","SP1114","Louisville - Farmers Ln, South Park Rd, & Minor Ln - NE & S of Substation",9.4537122790404027,533,"2019-10-12",3.863620958449129E-3,0,0,0,2.972954653290856E-2,0,3.714498746017759E-3,0.83908357622178542,0,0.12360875754083915,242.02487083616506,37.270475049869646,1.5512383697379166,1.8127973241703028,"Continue to Monitor"]
["South Park","Jefferson - 1412 Fairdale Rd. - Louisville","SP3302","Louisville - Blue Lick Rd, Raymond Rd, & Hwy 44 - S of Substation",9.3672847222222213,1,"2019-10-12",0,0,0,0,0,0,0,0.67915106117353308,0,0.32084893882646692,231.6,801,1.8,5,"Continue to Monitor"]
["SHEPHERDSVILLE","Bullitt - 1706 4th St. - Shepardsville","SV1121","Shepherdsville - Hwy 44, Blue Lick Rd, & Buckman St - E of Substation",9.3692660984848484,981,"2021-05-15",3.9373485635167882E-3,0,0,0.27738836967808933,7.716049382716049E-3,0,8.5814007153571029E-3,0,0.70161243798315454,7.6439367716626288E-4,47.991596228412568,72.14610005661909,0.26168874668990005,0.3464450842279384,"Continue to Monitor"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1184","Louisville - Romania Dr, Meyers Ln, & Blanton Ln - SW of Substation",16.123326231060606,1441,"2018-02-10",0.21165400517322147,1.8024807022546285E-2,0,0,0.13482962993136316,0,0.17654127375302958,0.29599380842787021,0.16112344446933746,1.8330312226318255E-3,75.070376100244729,33.985587792638263,1.0895785365283379,1.36071997338358,"Tree Trim Scheduled for 2022"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1186","Louisville - Gagel Ave, Hazelwood Ave, Bluegrass Ave, & Lonsdale Ave - E of Substation",13.966192077020203,2078,"2017-12-16",1.004760478732742E-2,0,0,0,6.2313048806093958E-2,0,0.12524912483606812,0.21989074649676266,0.575291635257145,7.2078398166028146E-3,130.50542014488329,116.38662805548236,1.1316347920024732,1.8245392721579878,"Continue to Monitor"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1188","Louisville - Rockford Ln, Imperial Ter, & Dover Rd - W of Substation",14.106964804292927,1900,"2018-02-10",0.10837933540535943,0,0,0,0.11668290269208764,0,4.2863107111379133E-2,3.6848046264941009E-2,0.69425244700097422,9.7416152525861674E-4,71.53332357849564,34.021649627551902,0.69956627746008793,0.88272489910891294,"Continue to Monitor"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1191","Louisville - Gagel Ave, Manslick Rd, & Parkwood Rd - SE of Substation",17.469236426767676,1357,"2018-02-03",1.9487879822465005E-2,1.1198361215431888E-3,0.12539433253670196,0,0.13390235575281667,0,0.10974393991123249,9.3192215773301473E-2,0,0.51715944008193926,57.511459490390997,49.460705821567529,0.34581869959542277,0.38398749935928589,"Continue to Monitor"]
["STEWART","Jefferson - 4701 Stewart Ln. - Louisville","SW1451","Louisville - Gagel Ave, Hazelwood Ave, Manslick Rd, & Brick Kiln Ln - E & SW of Substation",10.198822443181822,39,"2017-12-02",0,0,0,0,0.30387029288702927,0,0,0.68628476495200585,0,9.8449421609648046E-3,378.35602475424093,803.10530480426814,1.9437479016490566,2.8786585365853661,"Continue to Monitor"]
["SMYRNA","Jefferson - 7000 Manslick Rd. - Louisville","SY1250","Louisville - Vaughn Mill Rd, Outer Loop & Fegenbush Ln - N of Substation",28.290476483585856,2222,"2018-07-06",3.0904217982260226E-2,0,0,0,0.18838619105353838,0,7.1463212302980028E-2,0.3806138727585987,0,0.32863250590262266,52.121912588049007,53.28538283001614,0.50886786118356153,0.29961800366238933,"Tree Trim Scheduled for 2022"]
["SMYRNA","Jefferson - 7000 Manslick Rd. - Louisville","SY1251","Louisville - Smyrna Pky, Michael Ray Dr, & Lantana Dr - NW & SW of Substation",21.87204387626263,1518,"2018-04-14",5.6485245209312147E-2,0,0,0,2.0693659927149871E-3,0,1.0241250065987435E-3,0.85721374650266591,0,8.3207517288708233E-2,77.139006370863768,56.414114711185299,0.34117097491607307,0.36551891914855555,"Tree Trim Scheduled for 2022"]
["SMYRNA","Jefferson - 7000 Manslick Rd. - Louisville","SY1253","Louisville - Manslick Rd, Cinderella Ln, & Shepherdsville Rd - W of Substation",19.618877998737375,1558,"2018-04-14",4.1530229214918933E-3,0,2.306712957525475E-3,9.6167849777080393E-3,3.8100696711876989E-3,0,0,0.16612091685967573,0.79296429058006079,2.1028202032350358E-2,50.459913489427116,134.00209876142949,0.44239676050764576,1.5752096612286077,"Continue to Monitor"]
["SMYRNA","Jefferson - 7000 Manslick Rd. - Louisville","SY1254","Louisville - Vaughn Mill Rd, Outer Loop & Smyrna Rd - NW of Substation",17.049061553030302,1209,"2018-04-14",0.17694296079439217,9.7101481663575212E-2,0,0,0.29849300884230601,0,1.0630135353580501E-2,0.30447478788149673,0,0.1123576254646494,56.366653057944177,59.71240242094381,0.69068390647815558,0.7389120234151404,"Tree Trim Scheduled for 2022"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1106","Louisville - Blankenbaker Ln, Riviera Dr, & Woodside Rd - NW of Substation",40.869617266414153,1214,"2020-04-18",1.911873239959264E-2,0,0,0,0.30924766118159291,0,1.4509126442563403E-2,0.54060617555259616,1.0884937143611079E-3,0.11542981070929384,161.21231631678253,148.52131881282597,1.6380967316078228,2.3830971427474816,"Continue to Monitor"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1133","Louisville - US 42 & Lime Kiln Ln - N of Substation",32.295696811868687,1165,"2020-04-10",5.7316532049549772E-3,0,2.6990148095509762E-3,0,8.4523535475863998E-2,0,2.3757335548593946E-2,0.82813380974781392,7.6733424746195853E-4,5.4387316965760213E-2,169.91730896473734,231.46624527254261,0.94499263838937142,1.3264070849919076,"Reliability Improvements Scheduled for 2022"]
["TAYLOR","Jefferson - 4488 Brownsboro Rd. - Louisville","TA1134","Louisville - Brownsboro Rd, Winding Bluff Trce, I264, & Blankenbaker Ln - NE of Substation",19.709960542929295,1128,"2018-12-22",6.2882549542870106E-2,0,0,0,0.31465598899800962,0,2.611101625740541E-2,0.32963871652801136,0,0.26671172867370352,175.03229728490635,268.05862023903109,1.110083997435231,2.5758493481198843,"Tree Trim Scheduled for 2022"]
["TERRY","Jefferson - 8408 Terry Ln. - Louisville","TE1245","Louisville - Pages Ln, Poinsettia Dr, Greenwood Rd, & Feyhurst Dr - NE of Substation",23.72572190656566,2358,"2020-09-12",2.1602144133412746E-2,4.8123883263847525E-3,7.7605717689100658E-3,0,1.6527695056581301E-2,0,6.1762954139368675E-3,0.3275759380583681,0,0.61554496724240615,37.991798316330538,71.114198271215699,0.62056408625741333,1.4510340885496653,"Continue to Monitor"]
["TERRY","Jefferson - 8408 Terry Ln. - Louisville","TE1246","Louisville - Trade Port Dr - SW of Substation",2.5947842487373736,26,"2020-09-19",0,0,0,0,0,0,0,0,0,1,22.257699230006931,77.383333307692311,0.46121506121506117,2,"Continue to Monitor"]
["TERRY","Jefferson - 8408 Terry Ln. - Louisville","TE1247","Louisville - Cane Run Rd - W of Substation",11.330659722222222,366,"2020-09-19",0,0,0,0,0,0,9.3336987636275046E-3,0,0.99066630123637245,0,96.704005577826308,358.88419854098368,0.77966620914210039,0.79508196721311475,"Continue to Monitor"]
["Tip Top","Meade - US 60 - Tip Top","TT3314","Tip Top - Chaffee Ave, Gold Vault Rd, & 5th Ave - SE of Substation",6.4141922348484872,1,"2020-02-15",0,0,0,0,0.95115970164503938,0,0,4.8840298354960662E-2,0,0,5372.6599998000002,18618.233333,0.6,1,"Continue to Monitor"]
["WESTERN","Jefferson - 2807 W Broadway - Louisville","WE0001","Louisville - 28th St, Chestnut St, 26th St, & Muhammad Ali Blvd - NE of Substation",5.09581865530303,894,"2019-02-23",0,0.13254430406357082,0,6.3066282663078893E-4,0.6672202484811538,0,5.526708570707814E-2,0.10494229435136329,0,3.9395404570203282E-2,28.380922010304005,53.223559406172264,0.23916049669167369,0.45091407323135885,"Continue to Monitor"]
["WESTERN","Jefferson - 2807 W Broadway - Louisville","WE0002","Louisville - Broadway, Louis Coleman Jr Dr, & 35th St - W of Substation",2.6855716540404035,376,"2019-02-23",0,0,0,0,4.5125654770397247E-2,0,1.5965867014518748E-3,0.45894733981479596,0.21371841645775161,0.28061200225560334,156.5932348618538,318.27657339811782,0.76644158004132135,0.74853970314351836,"Continue to Monitor"]
["WESTERN","Jefferson - 2807 W Broadway - Louisville","WE0004","Louisville - Broadway, 24th, 234d, 22nd, & Dr W J Hodge St - E of Substation",3.3981748737373736,429,"2019-02-23",0,0,0,0,9.9441595136387381E-2,0,1.0686021131004191E-2,0,0.69031964326365547,0.19955274046895297,65.918199187543351,140.30961227716082,0.5505540182495301,0.32144277804040089,"Continue to Monitor"]
["WESTERN","Jefferson - 2807 W Broadway - Louisville","WE0006","Louisville - 28th St, Chestnut St, 30th St, & 31st St  - NW of Substation",1.8693380681818184,193,"2019-02-23",0,0,0,0,1.431818664627281E-2,0,0.92195101225755738,6.3730801096169784E-2,0,0,150.92326548793454,242.42860427718739,0.4408813777398799,0.59127676447264066,"Continue to Monitor"]
["WHAS","Jefferson - 1310 Flat Road Rd. - Louisville","WH1115","Louisville - Flat Rock Rd, Polo Fields Ln, & Glen Lakes Dr - SW of Substation",26.758372790404035,984,"2020-10-31",9.8340212404014943E-2,0,0,0,9.4266989271360707E-2,0.38158848924763977,6.7977417671417628E-3,0.16457583582403135,0.19799524225850396,5.6435489227307539E-2,66.443753315947816,139.312439102675,0.74942161864485457,1.8619553204114312,"Continue to Monitor"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1179","Louisville - Chamberlain Ln - NW of Substation",26.002727746212123,1152,"2021-10-23",6.2737852297170592E-4,0,0,0,5.6829463350063426E-2,0,2.930064530362363E-3,0,2.5398488776129283E-2,0.91421460482047323,63.874230079697519,127.16734311530776,0.4023336271532858,0.78387066056005794,"Continue to Monitor"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1180","Louisville - Brownsboro Rd, Norton Health Care Blvd, & Summit Plaza Dr - W of Substation",8.1927754103535388,172,"2021-10-23",0,0,0,0,0,0,4.3868739205526773E-2,0,0,0.95613126079447319,4.0257308681555743,16.742137720123672,1.7601485050651906E-2,4.0563247748353272E-2,"Continue to Monitor"]
["WORTHINGTON","Jefferson - 10300 Ballardsville Rd. - Louisville","WO1181","Louisville - Chamberlain Ln - S of Substation",7.9919520202020209,752,"2021-09-11",0.11522597241318136,4.2533374728345237E-2,0,0,0.47407637379695744,0,0.27750920299818155,0,0,9.0655076063334367E-2,14.318508517206658,30.22827575287539,0.30631967913722458,0.34290423338257692,"Continue to Monitor"]
["WATERSIDE","Jefferson - 221 North Third St. - Louisville","WS1305","Louisville - Main St, 1st St, Floyd St, & Bingham Way - E of Substation",3.5355026830808076,48,"2019-01-12",0,0,0,0,0,0,0,0,0,1,24.782857138775512,92.985714265306129,0.1034013605442177,0.32653061224489799,"Continue to Monitor"]
["WATERSIDE","Jefferson - 221 North Third St. - Louisville","WS1306","Louisville - Main St, 2nd St, & 3rd St - W of Substation",2.4271947601010093,38,"2019-01-12",0,0,0,0,9.5783490285908199E-2,0,3.2069228811402395E-2,0,0,0.87214728090268945,124.23210524736842,620.36052623684213,0.44300751879699246,2.1578947368421053,"Continue to Monitor"]
["WATERSIDE","Jefferson - 221 North Third St. - Louisville","WS1322","Louisville - Main St, 13th St, Market St, 10th St, & Portland Ave - W of Substation",5.5894270833333337,70,"2019-01-12",0,0,0,0,0.25790139064475348,0,3.9190897597977246E-2,0,0.11567635903919089,0.58723135271807836,84.332972908838798,167.77070701515152,1.2323041006242468,1.5909090909090908,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1151","Louisville - Hurstbourne Pky, Watterson Trl, Ferndale Rd, & Johnson School Rd - S of Substation",11.189420928030309,2655,"2021-12-04",7.7402136684431534E-3,0,0,0,4.9796082364105272E-2,1.3170939654426164E-2,5.6234555096960921E-3,5.720800252181682E-2,0,0.86646130628151252,80.486044787565248,217.71559407123226,0.63744681065837761,1.5018700768792075,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1152","Louisville - Bardstown Rd, Seatonville Rd, & Fern Creek Rd - SE of Substation",12.360112215909094,2372,"2021-11-13",0.18544552711904203,0,0,0,3.6320145574078422E-2,0,5.1449870861704626E-2,0.38107536980511852,2.1483916412303357E-2,0.32422517022775299,28.638593013914623,28.558099423960783,0.22420968375956002,0.24715426734076459,"Trees Trimmed in 2021"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1155","Louisville - Hurstbourne Pky, Watterson Trl, & Glaser Ln - S of Substation",7.7998678977272711,1792,"2021-12-04",9.08369720149374E-2,0,0,0,0.40189103949125105,0,2.6630634581771982E-2,2.691441949860365E-2,0.14117009680935458,0.31255683760408132,65.109003316025408,54.387014856429339,0.55757141126489673,1.0411208199063093,"Continue to Monitor"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1209","Louisville - Laverne Dr, Watterson Trl, & Dell Rd - NE of Substation",9.789725852272726,1522,"2021-12-18",1.7317997647366358E-3,0,0,0,0.14488302182721213,0,0.109544503986407,0.25099660175140504,0,0.49284407267023916,29.308324315199627,34.412441127052041,0.23146330485766028,0.26409261869459194,"Trees Trimmed in 2021"]
["WATTERSON","Jefferson - 5239 Bardstown Rd. - Louisville","WT1210","Louisville - Bardstown Rd, Hudson Ln, Fairground Rd & Janet Lee Dr - SE of Substation",12.48955855429293,1962,"2022-01-08",2.8552514733188018E-2,0,0,9.2516347783967061E-4,2.625333010414144E-3,8.6219423589246793E-4,2.7125211915718091E-3,0.80385242593041095,0.11483167837248728,4.563816904819569E-2,52.42358756423922,63.985615949784233,0.85134810609225675,0.64104261878449842,"Trees Trimmed in 2022"]

{"sheet":"LGE Section 6-7","index":2,"n_rows":29,"n_cols":1,"rows_kept":29,"cut":false,"hidden":false,"merged":[[15,0,15,3],[0,0,0,8],[2,0,2,8],[4,0,4,8],[5,0,10,8],[11,0,14,8],[28,0,31,8],[20,0,21,8],[27,0,27,8],[16,0,16,3],[17,0,17,3],[18,0,18,3],[19,0,19,3]]}
["KENTUCKY PUBLIC SERVICE COMMISSION"]
[]
["ELECTRIC DISTRIBUTION UTILITY ANNUAL RELIABILITY REPORT"]
[]
["SECTION 6: VEGETATION MANAGEMENT PLAN REVIEW"]
["The Companies’ Vegetation Management Plan was submitted December 19, 2007.  The Distribution Vegetation Management Program encompasses right of way maintenance for Louisville Gas and Electric Company and Kentucky Utilities Company (referred to as the “Companies”).  The program is centralized and managed by a Forestry Manager and eight company Utility Arborists.  All are certified arborists by the International Society of Arboriculture."]
[]
[]
[]
[]
[]
["The Companies’ plan is to maintain a proactive trim cycle while balancing the reactive needs of worst performing circuits. The Companies’ goal is to maintain an average trim cycle of five years or less.   The effectiveness of the plan is evaluated by the cycle and system performance as measured by system SAIDI, SAIFI, and CAIDI.  "]
[]
[]
[]
["Effectiveness of the program"]
["KU/LG&E Tree Cycle – 4.94 years"]
["LGE Tree SAIDI – 19.38 minutes"]
["LGE Tree SAIFI – 0.111"]
["LGE Tree CAIDI – 175.2 minutes"]
["The hazard tree program, mid cycle, herbicide, and worst performing circuits were completed as planned.  "]
[]
["Adjustments made to the tree plan in 2021 included"]
["No changes made to plan."]
["Changes to be implemented in 2022"]
["No changes made to plan. Continue targeted hazard tree and mid-cycle trim work."]
[]
["SECTION 7: UTILITY COMMENTS"]
["SAIDI and SAIFI improved in 2021 compared to the previous 5 year average including and excluding major events.  245 Circuits were above their previous 5 year average SAIDI and/or SAIFI in 2021.  "]