## Notes (hidden)
Assumptions
1 | Estimate the probable retirement costs for the tasks the company is legally obligated to perform. A list of potential items is below. Legal and Environment will also be reviewing. Please include everything you believe is potentially a legal obligation.
2 | All estimates should be provided in today's dollars.
3 | The coal pile will be burned down before retirement (there should be no transfer of usable coal)
4 | Make your best possible estimate, bids are not needed. Estimates may be based on burdened internal labor estimates.
5 | Estimate costs at retirement, assuming no future use for the plant.
6 | Use the FASB 143 Questionnaire distributed in the plant managers' meeting to assist in your determination of applicable assets and costs.
7 | Disposal of interim assets should be included. (Assets that are expected to be replaced during the remaining life of the plant which will have related retirement obligations such as batteries, mercury switches, hazardous waste or fuel storage tanks, etc...)
8 | Any qualifying retirement costs that are not probable, but are possible, should be disclosed with a note, but no dollar estimate.
9 | All plant assets should be assessed, including service buildings, screenwells, ash handling systems, yard facilities, boilers, service water equipment, station piping systems, precipitators, stacks, coal handling systems, fuel oil systems, reactant supply systems, SDRS systems, station water treatment facilities, misc. plant equipment, waste disposal systerms, gypsum plants, sludge processing plants, transformers, SCRs, CTs, ice plants, locks, dams, and all other plant assets.
Potential Retirement Obligations
1 | Holding pond remediation (drain and cap fly ash ponds, waste water ponds, etc…)
2 | Storage pile remediation (remove coal and limestone inventories, establish topsoil and sow grass)
3 | Drain boiler water.
4 | Drain all storage tanks.
5 | Remove and dispose of underground storage tanks.
6 | Empty and remediate all above ground hazardous material storage.
7 | Remove and remediate all mercury switches.
8 | Drain generation transformers and wrap in nitrogen blanket.
9 | Ground water monitoring (This may be necessary for 20 years. Legal is reviewing this issue.)
10 | Discretionary costs (Tearing down cooling towers for safety considerations)
11 | Disposal of batteries.
12 | Disposal of ammonia and SCR catalyst.

## Summary (hidden)
Asset Retirement Obligation Summary
Location | Description | Cost ($000s) | Comment
CR | Ash Pond Closure | 700 | 70 acres @ $10k per acre - based on Pineville - not unit specific - estimate of $10k/acre confirmed by Environmental
CR | Landfill Closure | 1000 | 110 acres - based on 65 acre closure bond estimate
CR | Coal Pile | 100 | 100k for closure - based on Pineville - $10k/acre
CR | Mecury Removal | 5 | Based on Pineville estimate - allocate evenly across 3 units
CR | Nuclear Source Removal | 50 | 50 cesium sources - allocate evenly across 3 units - current telephone estimate from nuclear disposal company (Ghent called)
CR | Station Oil Reservoirs | 500 | 420,000 gallons - allocate evenly across 3 units ($1.20 per gallon - per oil recycling price estimate)
CR | Sewage Treatment Plant | 50 | Based on Pineville estimate
OF | Total Cost | 8000 | Developed from work done in conjunction with rehabilitation analyses - This assumes we would walk away from our FERC license and close the facility.
Lou CTs
Lou CTs
Lou CTs
Lou CTs
Lou CTs
MC | Refrigerant Removal | 50 | Not unit specific, estimate of labor hours (internal and contracted labor, $36/hour at 1,400 hours)
MC | River cell, work barge, and bridge removal | 800 | Not unit specific, estimate of labor hours (contracted labor @ $35/hour at 17,000 hours; equipment fees for contractor work $100k; hauling $100k)
MC | Ash Pond & Landfill | 5000 | Status of landfill unknown - need to hire consultant - not unit specific - Range of $4M - $6M was provided. An average was used.
MC | Storage Pile Remediation (Coal Pile) | 2000 | Assumes maximum fuel utilization (zero tons of usable coal) - not unit specific
MC | Drain Boiler Water | 120 | Allocate evenly across units ($30k per unit; labor of 400 hours @ $75/hour)
MC | Drain all oil storage tanks | 200 | 16 tanks - Allocate evenly across units ($12,500 per each of 16 tanks) (industrial cleaning equipment $7,500; industrial disposal fees $1,250k, and labor $3,750 - 107 hours @$35/hour)
MC | Empty & Remediate above ground haz mat storage | 30 | Asbestos, mercury, used oil, chemicals - Allocate evenly across units. This is a building which contains waste material that has already been removed for disposal. This is not associated with an asset. Only the material must go, not the building. The cost is for disposal of the material. (Equipment $15k; disposal fees $9k; labor $3k - 85 hours @ $35/hour)
MC | Mercury Switch Removal | 60 | All encapsulated - Allocate evenly across units (labor and materials to encapsulate the mercury switches - internal labor of 400 hours @ $75/hour and $30k disposal fees)
MC | Drain transformers & wrap in nitrogen blanket | 280 | Including OCB (oil current breaker) - 28 transformers - Allocate evenly across units - $10k per transformer; equipment $6k; disposal fees $1k; labor $3k - 85 hours @ $35/hour)
MC2 | Demo Unit 2 Cooling Tower | 150 | (Equipment $90k; disposal $15k; labor $45k - 1,285 hours @ $35/hour)
MC3 | Asbestos Fill in Unit 3 Cooling towers | 425 | (Disposal fees $128k; Equipment $170k; labor $128k - 3,600 hours @ $35/hour)
MC4 | Asbestos Fill in Unit 4 Cooling towers | 425 | (Disposal fees $128k; Equipment $170k; labor $128k - 3,600 hours @ $35/hour)
MC | Lab Chemical disposal | 10 | Not unit specific ($1k internal labor - 13 hours @ $75/hour, $9 disposal fees)
MC | Fill Underground Tunnel under 31W | 25 | Not unit specific (equipment $15k; external contract labor 285 hours @ $35/hour)
MC | Chemical Tank clean up | 150 | Not unit specific (Equipment $60k; Disposal fees $45k; internal labor 600 hours @ $75/hour)
MC | Radiation Sources | 50 | Allocate evenly across units (disposal fees $15k ; internal labor 1,000 hours @ $35/hour)
TC1 | Ash Pond Closure | 1000 | $10k/acre at 100 acres - Pineville estimate
TC1 | Coal storage area | 225 | $5k/acre at 45 acres | Tom working on details
TC1 | Mercury Removal - Level Instrumentation | 2 | 1 barrel - Located throughout the plant. Small 4" cube box. Used wherever level indication is needed. These are potentially used wherever there is water in the system that needs to be measured. - Tie to boiler asset on TC1.
TC1 | Nuclear Source Removal - Coal Flow indicators | 40 | Cesium source removal - $1,600 flat fee per 25 sources - 25 boxes attached to outside of ductwork and above coal feeders. Tie to conveyors on TC1.
TC1 | Sewage Treatment Plant | 10
TC1 | Hazardous Material Disposal |  | $2k?? Per drum at x drums
GH | Ash Pond ATB I & II | 1950 | Closure at $10k per acre - 195 acres - $1M for ATB 1 and $1.5M for ATB II - used Pineville estimate
GH | Gypsum Stack | 400 | Closure at $10k per acre - 40 acres - based on Pineville estimate.
GH | Radiation Sources - Cesium | 140 | Cesium Sources - 154 - Cesium sources - 154. Unit 1 - 15%; Unit 2 - 24%; Unit 3 - 16%; Unit 4 - 19%; Scrubber - 9%; Coal Yard - 17% - based on phone conversations with vendors and physical counts (approx. $900 per source for disposal fee)
GH | Radiation Sources - Radium | 300 | Radium Sources - 42 - Redium Sources - 42; Unit 1 - 6; Unit 2 - 12; Unit 3 - 12; Unit 4 - 12 - based on conversations with vendors and physical counts (approx. $7,150 per source for disposal fee)
GH | Demolition of Cooling Towers | 500 | $125K per unit - crane rental ($50k) and associated external labor and tipping fee to remove items on top of tower. Remainder of the tower would be brought down not to be a fire hazard (controlled burn or landfilled)
GH | Removal of 10,000 Gallon underground tank | 30 | Common to the plant in the Coal Yard flat removal fee for outside contractor.
GH | Remediation of underground fuel oil piping | 75 | Common to the plant or divide equally among the 4 units no strong basis for the number
GH | Remove railroad crossing from highway 42 | 50 | Common to the plant - flat contractor fee for removal
GH | Mercury Removal | 50 | 12.5 per unit - flat disposal fee.
GH | Remove pipe bridge over highway 42 | 50 | Unit 1 specific today - will ultimately serve unit 2 if it is a limestone FGD - contracted bid
GH | Fill underground tunnel for piping under highway 42 | 25 | Common to the entire plant - contracted bid flat fee
GH | Chemical Tank clean up | 150 | Common to the plant - divide equally among the units - 50% labor and 50% disposal costs. Internal labor 75% ($75/hour at 750 hours), external labor 25% ($30/hour at 625 hours)
GH | Sewage Plant | 50 | Pineville Estimate
GH | Coal Yard covering | 500 | Assuming that we would be required to close in similar to the ash pond - Not unit specific - based on Pineville estimate $10k for 50 acres.
BR ST | Ash Pond | 5850 | Closure at $50,000 per acre - 117 acres - Not unit specific - Steam units only 1,2,3 - historical problems with leakage estimate use of wells and monitoring equipment included in estimate.
BR3 | Radiation Sources - BR3 | 135 | Radiation Sources at $7,500 per source (18) - Sources located with the following 10 assets with UOP 5676: 3-1 Feeder Upper; 3-1 Feeder Lower; 3-2 Feeder Upper; 3-2 Feeder Lower; 3-3 Feeder Upper; 3-3 Feeder Lower; 3-4 Feeder Upper; 3-4 Feeder Lower; 3-5 Feeder Upper; 3-5 Feeder Lower. Also, the following assets with UOP 5025: Hoppers A26 & A22; Hoppers A25 & A21; Hoppers A24 & A20; Hoppers A23 & A19; Hoppers B26 & B22; Hoppers B25 & B21; Hoppers B24 & B20; Hoppers B23 & B19 (Estimate from GHENT)
BR1 | Demolition Service Water Pump structures - BR1 | 50 | Flat fee for contractor removal.
BR2 | Demolition Service Water Pump structures - BR2 | 50 | Flat fee for contractor removal.
BR3 | Demolition Service Water Pump structures - BR3 | 100 | Flat fee for contractor removal.
BR ST | GSU, transformer oil, lubricating oils, ehc fluid | 45 | 9 oil-field transformers at $5,000 each - Not unit specific - include BR 1, 2,3 Transformers only. This oil has no PCBs (non-hazardous). Should be able to sell for reuse. Tie to BR3
BR CT | GSU, transformer oil, lubricating oils, ehc fluid | 35 | 7 Units at $5,000 each - Not unit specific - include BR 5, 6, 7, 8, 9, 10,11 Transformers only. This oil has no PCBs (non-hazardous). Should be able to sell for reuse. Tie to BR 7.
BR ST | Removal of Fuel Oil Tanks - BR Steam units 1, 2, 3 | 495 | 3 tanks at $165,000 each - Tanks are not unit specific - for BR 1, 2, 3 - flat fee paid to contractor for removal. ESTIMATE
BR CT | Removal of Fuel Oil Tanks - BR CTs | 1000 | 2 tanks at $500,000 each - Tanks are not unit specific - include BR 5, 6, 7, 8, 9, 10, 11 - flat fee paid to contractor for removal. ESTIMATE
BR ST | Remediation of underground fuel oil piping - Steam | 75 | Estimate - Not unit specific - include BR 1, 2,3 - flat fee to contractor for removal. (assume no leaks)
BR CT | Remediation of underground fuel oil piping - CTs | 100 | Not unit specific - include BR 5, 6, 7, 8, 9, 10,11 - flat fee to contractor for removal. (assume no leaks)
BR | Remove railroad crossing from highway 395 | 10 | Not unit specific - flat fee to contractor for removal.
BR ST | Mercury Removal | 15 | Includes BR 1,2,3 - Tie to BR3 - UOP 5373 - Instrument or measuring device (instrumentation) - contractor fee for removal of devices and disposal
BR CT | Mercury Removal | 35 | Not unit specific - includes BR 5, 6,7 ,8,9,10,11Not unit specific - Tie to BR7 - UOP 5373 - Instrument or measuring device (instrumentation) - contractor fee for removal of devices and disposal
BR | Lab Chemical disposal | 10 | BR1 - Lab Equipment UOP 5389 - contractor to pick up non-saleable chemicals.
BR | Sewage Plant | 50 | Pineville Estimate - Not unit specific
BR ST | Coal Yard covering | 500 | Assuming that we would be required to close similar to the ash pond (10 acres) - Not unit specific - Steam units 1, 2,3 - $200k may be better estimate
BR ST | Coal pile retention pond closing | 100 | Estimate - Not unit specific - Steam units 1, 2,3 - flat fee to contractor for disposal of funky mud to ash pond.
BR CT | Gas pipeline remediation | 250 | For CT units only BR 5,6,7,8,9,10,11 - this is on an easement - 13 miles of pipe. CHECK with LEGAL - could be $1.5M to $2M to remove. It was $1M per mile to build.
Dix Dam
Lock 7
TY | Ash Pond | 500 | Closure at $50,000 per acre - 10 acres - Not unit specific - Pineville estimate
TY | Radiation Sources | 0 | none
TY | Demolition Service Water Pump structures | 200 | 2 structures which have asbestos and lead paint issues - Not unit specific - flat fee for contractor removal
TY | GSU, transformer oil, lubricating oils, ehc fluid | 40 | 8 oil-field transformers at $5,000 - Not unit specific - Tie to transformer on TY3. This oil has no PCBs (non-hazardous). Should be able to sell for reuse.
TY | Removal of Fuel Oil Tanks | 100 | one underground and one above ground - Not unit specific - flat fee for contractor removal
TY | Remediation of underground fuel oil piping | 75 | could be less if no problems are found - Not unit specific - flat fee for contractor removal
TY | Mercury Removal | 100 | Not unit specific - allocable among units. UOP 5373 - Instrument or measuring device (instrumentation). Tie to TY3 - flat fee for contractor removal
TY | Sewage Plant | 50 | Pineville Estimate - Not unit specific
TY | Coal Yard covering | 100 | Assuming that we would be required to close similar to the ash pond - Not unit specific - 2 acres at $50k per acre Pineville estimate
TY | Coal pile retention pond closing | 10 | Estimate 2 ponds - Not unit specific - flat fee to contractor for disposal of funky mud to ash pond
GR | Holding Pond Remediation | 275 | Based on Pineville cost of $10K/acre
GR | Coal Storage Pile Remediation | 150 | Removal of remaining coal at $12/ton and $10K/acre to fill coal pile area. Based on Pineville estimate.
GR | Oil Storage Tanks | 70 | Based on $1.20/gallon (41,700 gallons) plus removal of underground line ($20k)
GR | Underground Storage Tanks | 65 | Not unit specific
GR 1/2 | Mercury Switches - Units 1/2 | 24 | Based on approx. 100 mercury sources (total) and some pre-existing on-site mercury storage from years past.
GR3 | Mercury Switches - Unit 3 | 15 | Based on approx. 100 mercury sources (total) and some pre-existing on-site mercury storage from years past.
GR4 | Mercury Switches - Unit 4 | 15 | Based on approx. 100 mercury sources (total) and some pre-existing on-site mercury storage from years past.
GR 1/2 | Generator Transformers - Units 1/2 | 300 | Includes units in switchyard not covered in item below. | Transformers - do not include Transmission transformers - perpetual assets.
GR3 | Generator Transformers - Unit 3 | 175 | Includes units in switchyard not covered in item below.
GR4 | Generator Transformers - Unit 4 | 225 | Includes units in switchyard not covered in item below.
GR | Sewage Treatment Plant | 60
GR | Switchyard transformers, OCB's, etc. | 650 | This includes all transformers, OCB's, capacitors, and oil containing switches for 161KV, 138KV, 69KV, 33KV yards AND some stored spare units (both transformers and OCB's).
GR | Acid Tank Disposal | 50
GR | Caustic Tank Disposal | 50
GR | Lime Storage Silo | 100
GR | Nuclear Source | 15
| Total | 37181
Assume Not Included in ARO
GH | Asbestos removal | 4000 | Unit 1 only
GH | Demolition of Barge Mooring Cells | 500 | River Hazard eleminating need for lighting
GH | Demolition of work barges | 150 | Potential of sinking - river hazard
GH | Demolition of Coal Barge Unloader | 150 | Removing Risk of falling due to cable failure
GH | Demolition of Chimneys | 1600 | Chimneys must keep aviation lights or remove
GH | Lab Chemical disposal | 10 | Common to the plant
GH | Demolition of Cooling Towers | 500 | $125K per unit - crane rental ($50k) and associated external labor and tipping fee to remove items on top of tower. Remainder of the tower would be brought down not to be a fire hazard (controlled burn or landfilled)
GH | GSU, transformer oil, lubricating oils, ehc fluid | 600 | Ghent has the ability to burn the oil. (disposal cost of $1/gal at 600,000 gallons). If environmental rules stay the same they could burn all oil in the final boiler and the remaining oil could be recycled at no cost - marketable at TC)
GH | Refrigeration gases | 50 | Estimate - need to validate
MC | Chimney Lights upkeep | 200
MC | Ground water monitoring | 20 | Check quarterly - not unit specific
MC | Demo Coal Barge Unloading Facilities | 150 | Not unit specific
MC3 | Asbestos Fill in Unit 3 Cooling towers | 425 | (Disposal fees $128k; Equipment $170k; labor $128k - 3,600 hours @ $35/hour)
MC4 | Asbestos Fill in Unit 4 Cooling towers | 425 | (Disposal fees $128k; Equipment $170k; labor $128k - 3,600 hours @ $35/hour)
MC2 | Demo Unit 2 Cooling Tower | 150 | (Equipment $90k; disposal $15k; labor $45k - 1,285 hours @ $35/hour)
TC | Chimney Removal | 0 | Maintain lighting
TC | Coal Barge Unloader | 0 | Maintain lighting, swing bucket to shore
TC | Barge Mooring Cells | 0 | Maintain lighting
TC | Station Oil Reservoirs | 0 | Items are marketable, third parties are expected to remove them at no cost.
TC | Refrigerant Removal | 0 | Items are marketable, third parties are expected to remove them at no cost.
TC | Limestone Barge Unloader | 0 | Maintain lighting
TC | Work barges | 0 | Items are marketable, third parties are expected to remove them at no cost.
TC | GSU, transformer oil, lubricating oils, ehc fluid | 0 | Items are marketable, third parties are expected to remove them at no cost.
TC CTs | Transformers | 0 | Items are marketable, third parties are expected to remove them at no cost.
TC CTs | GSU, transformer oil, lubricating oils, ehc fluid | 0 | Items are marketable, third parties are expected to remove them at no cost.
BR | Asbestos removal | 4500 | All Units Estimate $1,500,000 per unit
BR | Demolition of Chimneys | 750 | Chimneys must keep aviation lights or remove 3 at $250k - $250k per units 1, 2, 3
BR1 | Demolition of Cooling Towers - Unit 1 | 250 | Estimate - need to validate 1 tower at $250k
BR2 | Demolition of Cooling Towers - Unit 2 | 250 | Estimate - need to validate 1 tower at $250k
BR3 | Demolition of Cooling Towers - Unit 3 | 500 | Estimate - need to validate 2 towers at $250k each
BR ST | Chemical Tank clean up (acid and caustic for demineralizers) | 250 | Steam units only - not unit specific - the chemicals are saleable or they can be diluted and put on the ash pond. No clean up of the tanks are necessary.
TY | Chemical Tank clean up | 20 | 2 tanks $10,000 each - Not unit specific - the chemicals are saleable or they can be diluted and put on the ash pond. No clean up of the tanks are necessary.
BR ST | Refrigeration gases | 15 | Estimate - need to validate - Not unit specific - includes BR 1,2,3 - Tie to BR3 - 5008 UOP Air Conditioner, central install - saleable
BR CT | Refrigeration gases | 35 | Estimate - need to validate - Not unit specific - includes BR 5,6,7,8,9,10,11- Tie to BR7 - 5008 UOP Air Conditioner, central install - saleable
GR | Ground Water Monitoring | 52 | $1k per year for 30 years with inflation
TY | Demolition of Cooling Towers | 0 | none
TY | Asbestos and lead paint removal | 4500 | All Units Estimate $1,500,000 per unit
TY | Warehouses | 100 | 2 at $50,000 each, remove material and tear down
TY | Refrigeration gases | 5 | 8 separate units - Not unit specific - Tie to TY3 - 5008 UOP Air Conditioner, central install - saleable
TY | Lab Chemical disposal | 1 | very small amounts - Not unit specific - Lab Equipment UOP 5389. Tie to TY1/2
TY | Demolition of Chimneys | 150 | Chimneys steel 3 at $50,000
CR | Cane Run 6 Chimney Removal | 500 | Tallest stack to avoid FAA lighting - based on 1986 CR4 removal project
CR | River cell, work barge, and bridge removal | 500 | Coast Guard issues no facts for estimate.
CR | Asbestos removal | 20000 | Based on PR estimates
CR | Refrigerant Removal | 50 | Items are marketable, third parties are expected to remove them at no cost.
GR 1/2 | Generator Transformers - Units 1/2 | 300 | Includes units in switchyard not covered in item below. |  | Transformers - do not include Transmission transformers - perpetual assets?? SOURCE of estimate?
GR3 | Generator Transformers - Unit 3 | 175 | Includes units in switchyard not covered in item below. |  | Source of estimate?
GR4 | Generator Transformers - Unit 4 | 225 | Includes units in switchyard not covered in item below. |  | Source of estimate?
PI | Ash Pond | 50 | 11 acres, unlined, approaching closure as a beneficial reuse application - to be used as a laydown area for Transmission; FMSM estimate to close the pond with a geotechnical membrane is $750k to $1M (average $75k/acre). It is expected that other locations will not be able to qualify for beneficial reuse and the $75k/acre estimate for capping and closure will be used for the other locations. One other option would be excavation, transportation, and disposal of ash for approx. $10M for the 11 acres. This estimate is not being used for other locations, it is assumed this will not be necessary.
PI | Coal Inventory - check acres | 6.5 | Required only to haul in clean fill, grade the land, and seed. Based on actual contractor costs (time and material rate of $60/hour for 108 hours) for .5 acres. Estimate for other locations is $15k/acre.
PI | Cooling Tower | 25 | Not legal requirement
PI | Mercury Removal | 3 | 2 drums were disposed of at Pineville for $1,500/drum
PI | Removal of PCBs related to bushings | 2 | Based on actual cost of disposal. PCBs are not at other locations.
PI | Bearing/Seal Oil Removal | 25 | 1,500 gallons of oil sold. Cost is related to employee labor to wipe down tanks and dispose of rags.
PI | Fuel Oil Tank | 10 | One 15,000 gallon tank, cleaning and closure, based on actual contractor costs.
PI | Sewage Treatment Plant | 1 | Costs to pump out tank, fill with dirt, remove above-ground equipment, and bury the tank totaling $1k. The tank was used for approximately 50 people. An estimate of $5k - $10k was used for other locations based on employee base.
PI | Switchyard Relay | 500 | Put in automatic relaying. All other locations should have automatic relaying.
PI | TVA Relocation | 25 | N/A at other plants.
| Total | 42705.5
Note on D160: E008422: Original estimate was $75k, but Mike Toll estimates closer to $500k.
Note on F122: E008422: These items are saleable. There should be no cost to remove.
Note on F123: E008422: These items are saleable. There should be no cost to remove.
Note on F125: E008422: These items are saleable. There should be no cost to remove.
Note on F126: E008422: These items are saleable. There should be no cost to remove.
Note on F127: E008422: These items are saleable. There should be no cost to remove.
Note on F128: E008422: These items are saleable. There should be no cost to remove.
Note on F148: E008422: These items are saleable. There should be no cost to remove.
Note on D159: Shannon Charnas: Total cost of $50k included cost to install a new septic tank for use by the Transmission group.

## Draft (hidden)
Asset Retirement Obligation Summary - DRAFT
Location | Description | Cost ($000s) | Comment
CR | Ash Pond Closure | 700 | 70 acres @ $10k per acre - based on Pineville - not unit specific - estimate of $10k/acre confirmed by Environmental
CR | Landfill Closure | 1000 | 110 acres - based on 65 acre closure bond estimate
CR | Coal Pile | 100 | 100k for closure - based on Pineville - $10k/acre
CR | Mecury Removal | 5 | Based on Pineville estimate - allocate evenly across 3 units
CR | Nuclear Source Removal | 50 | 50 cesium sources - allocate evenly across 3 units - current telephone estimate from nuclear disposal company (Ghent called)
CR | Station Oil Reservoirs | 500 | 420,000 gallons - allocate evenly across 3 units ($1.20 per gallon - per oil recycling price estimate)
CR | Sewage Treatment Plant | 50 | Based on Pineville estimate
OF | Total Cost | 8000 | Developed from work done in conjunction with rehabilitation analyses - This assumes we would walk away from our FERC license and close the facility.
MC | Refrigerant Removal | 50 | Not unit specific, estimate of labor hours (internal and contracted labor, $36/hour at 1,400 hours)
MC | River cell, work barge, and bridge removal | 800 | Not unit specific, estimate of labor hours (contracted labor @ $35/hour at 17,000 hours; equipment fees for contractor work $100k; hauling $100k)
MC | Ash Pond & Landfill | 5000 | Status of landfill unknown - need to hire consultant - not unit specific - Range of $4M - $6M was provided. An average was used.
MC | Storage Pile Remediation (Coal Pile) | 2000 | Assumes maximum fuel utilization (zero tons of usable coal) - not unit specific
MC | Drain Boiler Water | 120 | Allocate evenly across units ($30k per unit; labor of 400 hours @ $75/hour)
MC | Drain all oil storage tanks | 200 | 16 tanks - Allocate evenly across units ($12,500 per each of 16 tanks) (industrial cleaning equipment $7,500; industrial disposal fees $1,250k, and labor $3,750 - 107 hours @$35/hour)
MC | Empty & Remediate above ground haz mat storage | 30 | Asbestos, mercury, used oil, chemicals - Allocate evenly across units. This is a building which contains waste material that has already been removed for disposal. This is not associated with an asset. Only the material must go, not the building. The cost is for disposal of the material. (Equipment $15k; disposal fees $9k; labor $3k - 85 hours @ $35/hour)
MC | Mercury Switch Removal | 60 | All encapsulated - Allocate evenly across units (labor and materials to encapsulate the mercury switches - internal labor of 400 hours @ $75/hour and $30k disposal fees)
MC | Drain transformers & wrap in nitrogen blanket | 280 | Including OCB (oil current breaker) - 28 transformers - Allocate evenly across units - $10k per transformer; equipment $6k; disposal fees $1k; labor $3k - 85 hours @ $35/hour)
MC2 | Demo Unit 2 Cooling Tower | 150 | (Equipment $90k; disposal $15k; labor $45k - 1,285 hours @ $35/hour)
MC3 | Asbestos Fill in Unit 3 Cooling towers | 425 | (Disposal fees $128k; Equipment $170k; labor $128k - 3,600 hours @ $35/hour)
MC4 | Asbestos Fill in Unit 4 Cooling towers | 425 | (Disposal fees $128k; Equipment $170k; labor $128k - 3,600 hours @ $35/hour)
MC | Lab Chemical disposal | 10 | Not unit specific ($1k internal labor - 13 hours @ $75/hour, $9 disposal fees)
MC | Fill Underground Tunnel under 31W | 25 | Not unit specific (equipment $15k; external contract labor 285 hours @ $35/hour)
MC | Chemical Tank clean up | 150 | Not unit specific (Equipment $60k; Disposal fees $45k; internal labor 600 hours @ $75/hour)
MC | Radiation Sources | 50 | Allocate evenly across units (disposal fees $15k ; internal labor 1,000 hours @ $35/hour)
TC1 | Ash Pond Closure | 1000 | $10k/acre at 100 acres - Pineville estimate
TC1 | Coal storage area | 225 | $5k/acre at 45 acres | Tom working on details
TC1 | Mercury Removal - Level Instrumentation | 2 | 1 barrel - Located throughout the plant. Small 4" cube box. Used wherever level indication is needed. These are potentially used wherever there is water in the system that needs to be measured. - Tie to boiler asset on TC1.
TC1 | Nuclear Source Removal - Coal Flow indicators | 40 | Cesium source removal - $1,600 flat fee per 25 sources - 25 boxes attached to outside of ductwork and above coal feeders. Tie to conveyors on TC1.
TC1 | Sewage Treatment Plant | 10
TC1 | Hazardous Material Disposal |  | $2k?? Per drum at x drums
GH | Ash Pond ATB I & II | 1950 | Closure at $10k per acre - 195 acres - $1M for ATB 1 and $1.5M for ATB II - used Pineville estimate
GH | Gypsum Stack | 400 | Closure at $10k per acre - 40 acres - based on Pineville estimate.
GH | Radiation Sources - Cesium | 140 | Cesium Sources - 154 - Cesium sources - 154. Unit 1 - 15%; Unit 2 - 24%; Unit 3 - 16%; Unit 4 - 19%; Scrubber - 9%; Coal Yard - 17% - based on phone conversations with vendors and physical counts (approx. $900 per source for disposal fee)
GH | Radiation Sources - Radium | 300 | Radium Sources - 42 - Redium Sources - 42; Unit 1 - 6; Unit 2 - 12; Unit 3 - 12; Unit 4 - 12 - based on conversations with vendors and physical counts (approx. $7,150 per source for disposal fee)
GH | Demolition of Cooling Towers | 500 | $125K per unit - crane rental ($50k) and associated external labor and tipping fee to remove items on top of tower. Remainder of the tower would be brought down not to be a fire hazard (controlled burn or landfilled)
GH | Removal of 10,000 Gallon underground tank | 30 | Common to the plant in the Coal Yard flat removal fee for outside contractor.
GH | Remediation of underground fuel oil piping | 75 | Common to the plant or divide equally among the 4 units no strong basis for the number
GH | Remove railroad crossing from highway 42 | 50 | Common to the plant - flat contractor fee for removal
GH | Mercury Removal | 50 | 12.5 per unit - flat disposal fee.
GH | Remove pipe bridge over highway 42 | 50 | Unit 1 specific today - will ultimately serve unit 2 if it is a limestone FGD - contracted bid
GH | Fill underground tunnel for piping under highway 42 | 25 | Common to the entire plant - contracted bid flat fee
GH | Chemical Tank clean up | 150 | Common to the plant - divide equally among the units - 50% labor and 50% disposal costs. Internal labor 75% ($75/hour at 750 hours), external labor 25% ($30/hour at 625 hours)
GH | Sewage Plant | 50 | Pineville Estimate
GH | Coal Yard covering | 500 | Assuming that we would be required to close in similar to the ash pond - Not unit specific - based on Pineville estimate $10k for 50 acres.
BR ST | Ash Pond | 5850 | Closure at $50,000 per acre - 117 acres - Not unit specific - Steam units only 1,2,3 - historical problems with leakage estimate use of wells and monitoring equipment included in estimate.
BR3 | Radiation Sources - BR3 | 135 | Radiation Sources at $7,500 per source (18) - Sources located with the following 10 assets with UOP 5676: 3-1 Feeder Upper; 3-1 Feeder Lower; 3-2 Feeder Upper; 3-2 Feeder Lower; 3-3 Feeder Upper; 3-3 Feeder Lower; 3-4 Feeder Upper; 3-4 Feeder Lower; 3-5 Feeder Upper; 3-5 Feeder Lower. Also, the following assets with UOP 5025: Hoppers A26 & A22; Hoppers A25 & A21; Hoppers A24 & A20; Hoppers A23 & A19; Hoppers B26 & B22; Hoppers B25 & B21; Hoppers B24 & B20; Hoppers B23 & B19
BR1 | Demolition Service Water Pump structures - BR1 | 50 | Estimate - need to validate
BR2 | Demolition Service Water Pump structures - BR2 | 50 | Estimate - need to validate
BR3 | Demolition Service Water Pump structures - BR3 | 100 | Estimate - need to validate
BR ST | GSU, transformer oil, lubricating oils, ehc fluid | 450 | 3 Units at $150,000 each - Not unit specific - include BR 1, 2,3 Transformers only. Tie to BR3
BR CT | GSU, transformer oil, lubricating oils, ehc fluid | 1050 | 7 Units at $150,000 each - Not unit specific - include BR 5, 6, 7, 8, 9, 10,11 Transformers only. Tie to BR 7.
BR1 | Demolition of Cooling Towers - Unit 1 | 250 | Estimate - need to validate 1 tower at $250k
BR2 | Demolition of Cooling Towers - Unit 2 | 250 | Estimate - need to validate 1 tower at $250k
BR3 | Demolition of Cooling Towers - Unit 3 | 500 | Estimate - need to validate 2 towers at $250k each
BR ST | Removal of Fuel Oil Tanks - BR Steam units 1, 2, 3 | 600 | Estimate - need to validate 3 tanks at $200,000 each - Tanks are not unit specific - for BR 1, 2, 3
BR CT | Removal of Fuel Oil Tanks - BR CTs | 400 | Estimate - need to validate 2 tanks at $200,000 each - Tanks are not unit specific - include BR 5, 6, 7, 8, 9, 10, 11
BR ST | Remediation of underground fuel oil piping - Steam | 40 | Estimate - need to validate - Not unit specific - include BR 1, 2,3
BR CT | Remediation of underground fuel oil piping - CTs | 35 | Estimate - need to validate - Not unit specific - include BR 5, 6, 7, 8, 9, 10,11
BR | Remove railroad crossing from highway 395 | 10 | Estimate - need to validate - not unit specific
BR ST | Mercury Removal | 15 | Estimate - need to validate - Not unit specific - includes BR 1,2,3 - Tie to BR3 - UOP 5373 - Instrument or measuring device (instrumentation)
BR CT | Mercury Removal | 35 | Estimate - need to validate - Not unit specific - includes BR 5, 6,7 ,8,9,10,11Not unit specific - Tie to BR7 - UOP 5373 - Instrument or measuring device (instrumentation)
BR | Lab Chemical disposal | 10 | Estimate - need to validate - BR1 - Lab Equipment UOP 5389
BR ST | Chemical Tank clean up | 250 | Estimate - need to validate - Steam units only - not unit specific
BR | Sewage Plant | 50 | Pineville Estimate - Not unit specific
BR ST | Refrigeration gases | 15 | Estimate - need to validate - Not unit specific - includes BR 1,2,3 - Tie to BR3 - 5008 UOP Air Conditioner, central install
BR CT | Refrigeration gases | 35 | Estimate - need to validate - Not unit specific - includes BR 5,6,7,8,9,10,11- Tie to BR7 - 5008 UOP Air Conditioner, central install
BR ST | Coal Yard covering | 500 | Assuming that we would be required to close similar to the ash pond - Not unit specific - Steam units 1, 2,3
BR ST | Coal pile retention pond closing | 100 | Estimate - Not unit specific - Steam units 1, 2,3
BR CT | Gas pipeline remediation | 250 | Estimate - For CT units only BR 5,6,7,8,9,10,11
Dix Dam
Lock 7
TY | Ash Pond | 500 | Closure at $50,000 per acre - need to validate acreage - Not unit specific
TY | Radiation Sources | 0 | none
TY | Demolition Service Water Pump structures | 200 | 2 structures which have asbestos and lead paint issues - Not unit specific
TY | GSU, transformer oil, lubricating oils, ehc fluid | 1200 | 8 Units at $150,000 - Not unit specific - Tie to transformer on TY3
TY | Demolition of Cooling Towers | 0 | none
TY | Removal of Fuel Oil Tanks | 100 | one underground and one above ground - Not unit specific
TY | Remediation of underground fuel oil piping | 75 | could be less if no problems are found - Not unit specific
TY | Mercury Removal | 100 | Estimate - need to validate - Not unit specific - allocable among units. UOP 5373 - Instrument or measuring device (instrumentation). Tie to TY3
TY | Lab Chemical disposal | 1 | very small amounts - Not unit specific - Lab Equipment UOP 5389. Tie to TY1/2
TY | Chemical Tank clean up | 20 | 2 tanks $10,000 each - Not unit specific
TY | Sewage Plant | 50 | Pineville Estimate - Not unit specific
TY | Refrigeration gases | 5 | 8 separate units - Not unit specific - Tie to TY3 - 5008 UOP Air Conditioner, central install
TY | Coal Yard covering | 500 | Assuming that we would be required to close similar to the ash pond - Not unit specific
TY | Coal pile retention pond closing | 100 | Estimate 2 ponds - Not unit specific
TY | Gas pipeline remediation | 0 | none
GR | Holding Pond Remediation | 275 | Based on Pineville cost of $10K/acre
GR | Coal Storage Pile Remediation | 150 | Removal of remaining coal at $12/ton and $10K/acre to fill coal pile area. Based on Pineville estimate.
GR | Oil Storage Tanks | 70 | Based on $1.20/gallon (41,700 gallons) plus removal of underground line ($20k)
GR | Underground Storage Tanks | 65 | Not unit specific
GR 1/2 | Mercury Switches - Units 1/2 | 24 | Based on approx. 100 mercury sources (total) and some pre-existing on-site mercury storage from years past.
GR3 | Mercury Switches - Unit 3 | 15 | Based on approx. 100 mercury sources (total) and some pre-existing on-site mercury storage from years past.
GR4 | Mercury Switches - Unit 4 | 15 | Based on approx. 100 mercury sources (total) and some pre-existing on-site mercury storage from years past.
GR 1/2 | Generator Transformers - Units 1/2 | 300 | Includes units in switchyard not covered in item below. | Transformers - do not include Transmission transformers - perpetual assets.
GR3 | Generator Transformers - Unit 3 | 175 | Includes units in switchyard not covered in item below.
GR4 | Generator Transformers - Unit 4 | 225 | Includes units in switchyard not covered in item below.
GR | Sewage Treatment Plant | 60
GR | Switchyard transformers, OCB's, etc. | 650 | This includes all transformers, OCB's, capacitors, and oil containing switches for 161KV, 138KV, 69KV, 33KV yards AND some stored spare units (both transformers and OCB's).
GR | Acid Tank Disposal | 50
GR | Caustic Tank Disposal | 50
GR | Lime Storage Silo | 100
GR | Nuclear Source | 15
| Total | 40982
Assume Not Included in ARO
GH | Asbestos removal | 4000 | Unit 1 only
GH | Demolition of Barge Mooring Cells | 500 | River Hazard eleminating need for lighting
GH | Demolition of work barges | 150 | Potential of sinking - river hazard
GH | Demolition of Coal Barge Unloader | 150 | Removing Risk of falling due to cable failure
GH | Demolition of Chimneys | 1600 | Chimneys must keep aviation lights or remove
GH | Lab Chemical disposal | 10 | Common to the plant
GH | GSU, transformer oil, lubricating oils, ehc fluid | 600 | Ghent has the ability to burn the oil. (disposal cost of $1/gal at 600,000 gallons). If environmental rules stay the same they could burn all oil in the final boiler and the remaining oil could be recycled at no cost - marketable at TC)
GH | Refrigeration gases | 50 | Estimate - need to validate
MC | Chimney Lights upkeep | 200
MC | Ground water monitoring | 20 | Check quarterly - not unit specific
MC | Demo Coal Barge Unloading Facilities | 150 | Not unit specific
TC | Chimney Removal | 0 | Maintain lighting
TC | Coal Barge Unloader | 0 | Maintain lighting, swing bucket to shore
TC | Barge Mooring Cells | 0 | Maintain lighting
TC | Station Oil Reservoirs | 0 | Items are marketable, third parties are expected to remove them at no cost.
TC | Refrigerant Removal | 0 | Items are marketable, third parties are expected to remove them at no cost.
TC | Limestone Barge Unloader | 0 | Maintain lighting
TC | Work barges | 0 | Items are marketable, third parties are expected to remove them at no cost.
TC | GSU, transformer oil, lubricating oils, ehc fluid | 0 | Items are marketable, third parties are expected to remove them at no cost.
TC CTs | Transformers | 0 | Items are marketable, third parties are expected to remove them at no cost.
TC CTs | GSU, transformer oil, lubricating oils, ehc fluid | 0 | Items are marketable, third parties are expected to remove them at no cost.
BR | Asbestos removal | 4500 | All Units Estimate $1,500,000 per unit
BR | Demolition of Chimneys | 750 | Chimneys must keep aviation lights or remove 3 at $250k - $250k per units 1, 2, 3
GR | Ground Water Monitoring | 52 | $1k per year for 30 years with inflation
TY | Asbestos and lead paint removal | 4500 | All Units Estimate $1,500,000 per unit
TY | Warehouses | 100 | 2 at $50,000 each, remove material and tear down
TY | Demolition of Chimneys | 150 | Chimneys steel 3 at $50,000
CR | Cane Run 6 Chimney Removal | 500 | Tallest stack to avoid FAA lighting - based on 1986 CR4 removal project
CR | River cell, work barge, and bridge removal | 500 | Coast Guard issues no facts for estimate.
CR | Asbestos removal | 20000 | Based on PR estimates
CR | Refrigerant Removal | 50 | Items are marketable, third parties are expected to remove them at no cost.
PI | Ash Pond | 50 | 5 acres, unlined
PI | Coal Inventory | 75 | 8,900 tons - check acreage with Lois
PI | Cooling Tower | 25
PI | Mercury Removal | 25 | 20 lbs.
PI | Bearing/Seal Oil Removal | 25 | 1,500 gallons
PI | Fuel Oil Tank | 50 | One 15,000 gallon tank
PI | Sewage Treatment Plant | 50
PI | Switchyard Relay | 500
PI | TVA Relocation | 25
| Total | 39357
Note on F123: E008422: These items are saleable. There should be no cost to remove.
Note on F124: E008422: These items are saleable. There should be no cost to remove.
Note on F126: E008422: These items are saleable. There should be no cost to remove.
Note on F127: E008422: These items are saleable. There should be no cost to remove.
Note on F128: E008422: These items are saleable. There should be no cost to remove.
Note on F129: E008422: These items are saleable. There should be no cost to remove.
Note on F139: E008422: These items are saleable. There should be no cost to remove.
Note on D141: E008422: This was bid at $7/ton by a former employee. The other bids came in @ $11-$12/ton, which would be a better estimate for other locations.
Note on D147: E008422: Original estimate was $75k, but Mike Toll estimates closer to $500k.

## Questions (hidden)
Asset Retirement Obligation
1. | Reverify all estimates. They don't need to be exact, but they need to be reasonable and supportable.
2. | What is the source of the estimate?
- Is the estimate based on historical knowledge of plant operations? If so, detail.
- Is the estimate based on telephone conversation with vendor? If so, detail vendor name and date.
- Is the estimate based on current arrangement with vendor? If so, what is the arrangement?
- Is the estimate attributed from another plant? If so, why is it applicable to this location as well?
- Is the estimate based on Pineville's cost? If so, note it is based on Pineville.
- Is there an assumed number of labor hours and rate used to calculate? If so, detail calculation.
- Is any documentation available?
- Is the number based on a calculation? If so, detail calculation.
3. | Add information for Trimble County CTs, Louisville CTs, and Dix Dam (SC).
4. | Are any items marketable and therefore may have no cost associated with disposal?
- Transformer oil?
- Lab chemicals?
- Transformers?
- Refrigerant?
5. | Does anything on the list appear to not be a legal obligation upon retirement of the unit?
6. | Does it appear that an legal obligations upon retirement are missing?

## MC
Asset Retirement Obligation
Probability Weighted Settlement Estimates
Probability of Occurrence |  |  | 5% | 85% | 10%
Location | Description | Legal Requirement |  | Cost ($000s) |  | Weighted Cost | Comment | Support
MC | Ash Pond | Resource Conservation and Recovery Act | 4033.8 | 4482 | 4930.2 | 4504.41 | 54 acres @ $83k per acre - not unit specific. Acreage verified by Paul Puckett-Environmental Dept. | Based on Pineville $83k/acre estimate from FMSM engineering study
MC | Landfill | Resource Conservation and Recovery Act | 7320.6 | 8134 | 8947.4 | 8174.67 | 98 acres @ $83k per acre - not unit specific. Acreage verified by Paul Puckett-Environmental Dept. | Based on Pineville $83k/acre estimate from FMSM engineering study
MC | Storage Pile Remediation (Coal Pile) | Clean Water Act | 270 | 300 | 330 | 301.5 | Assumes maximum fuel utilization (zero tons of usable coal) - not unit specific 20 acres Acreage verified by Delbert Billiter-Fuels Dept. | Based on Pineville $15k/acre from PMR Construction invoice
MC | Drain all oil storage tanks | Clean Water Act | 15.3 | 17 | 18.7 | 17.085 | 16 tanks - Allocate evenly across units | Supported by engineering estimate based on hourly rates provided by American Enviro Services Inc.
MC | Empty & Remediate above ground haz mat storage | Clean Water Act | 27 | 30 | 33 | 30.15 | Asbestos, mercury, used oil, chemicals - allocate evenly across units. This is a building which contains waste material that has already been removed for disposal. This is not associated with an asset. The cost is for disposal of the material, not the building | Supported by engineering estimate based on hourly rates provided by American Enviro Services Inc.
MC | Mercury Switch Removal | Resource Conservation and Recovery Act | 0 | 0 | 0 | 0 | Due to immaterial costs of $ 268 no ARO is being established | Supported by ENSCO quote provided by Mike Winkler
MC | Drain transformers | Clean Water Act Toxic Substances Control Act | 13.5 | 15 | 16.5 | 15.075 | Including OCB (oil current breaker) - 28 transformers - Allocate evenly across units | Supported by engineering estimate based on hourly rates provided by American Enviro Services Inc.
MC | Lab Chemical disposal | Resource Conservation and Recovery Act | 2.7 | 3 | 3.3 | 3.015 | Not unit specific | 40 man hours at internal burdened labor rate of $75 per hour . Supported by Shannon Charnas email.
MC | Chemical Tank clean up | Clean Water Act | 5.4 | 6 | 6.6 | 6.03 | Not unit specific | 80 man hours at internal burdened labor rate of $75 per hour . Supported by Shannon Charnas email.
MC | Radiation Sources | The Cabinet for Human Resources - KRS 211.844, regulation 902 KAR Chapter 100 | 21.6 | 24 | 26.4 | 24.12 | Allocate evenly across units | 40 sources at $870. Supported by OHMART email
Total |  |  |  | 13011 |  | 13076.055
Note on L7: Revised acreage verified by Paul Puckett Price from FSMF estimate

## CR
Asset Retirement Obligation
Probability Weighted Settlement Estimates
Probability of Occurrence |  |  | 5% | 85% | 10%
Location | Description | Legal Requirement |  | Cost ($000s) |  | Weighted Cost | Comment | Support
CR | Ash Pond Closure | Resource Conservation and Recovery Act | 3212.1 | 3569 | 3925.9 | 3586.845 | 43 acres @ $83k per acre - not unit specific. Acreage verified by Paul Puckett-Environmental Dept. | Based on Pineville $83k/acre estimate from FMSM engineering study
CR | Landfill Closure | Resource Conservation and Recovery Act | 1078.2 | 1198 | 1317.8 | 1203.99 | 110 acres Acreage verified by Paul Puckett-Environmental Dept. | Based on Permit Consultant detailed estimate. See attached.
CR | Coal Pile | Clean Water Act | 229.5 | 255 | 280.5 | 256.275 | $15k/acre at 17 acres Acreage verified by Delbert Billiter-Fuels Dept. | Based on Pineville $15k/acre from PMR Construction invoice
CR | Mercury Removal | Resource Conservation and Recovery Act | 4.5 | 5 | 5.5 | 5.025 | Allocate evenly across 3 units | Based on Pineville estimate increased due to size of plant. Estimate provided from Mike Winkler based on ENSCO price per lb.
CR | Nuclear Source Removal | The Cabinet for Human Resources - KRS 211.844, regulation 902 KAR Chapter 100 | 39.6 | 44 | 48.4 | 44.22 | 50 cesium sources - allocate evenly across 3 units - $870/source | Current telephone estimate from nuclear disposal company (Ohmart called by Ghent 12/02) Supported by email from OHMART
CR | Station Oil Reservoirs (including transformers) | Clean Water Act Toxic Substances Control Act | 10.8 | 12 | 13.2 | 12.06 | 420,000 gallons on site - Cost of $0.60 per gallon for 20,000 gallons of contaminated oils at the time of closure. Allocate evenly across 3 units (there will likely be some contaminated oils on site that will require a charge). Most oil will be recycled at no cost. | American Enviro Services invoice for similar work. AES will reclaim some oils at $0.60 per gallon if contaminated, including up to 50 ppm pf PCB (based on work performed in Dec. 2002 & confirming telephone interview). For uncontaminated oil there is no charge. We have estimated a portion of the oils will be contaminated, some with non-PCB oil at < 50 ppm.
CR | Sewage Treatment Plant | Clean Water Act | 4.5 | 5 | 5.5 | 5.025 | Estimated cost to pump out tank, fill tank with soil, and grade land. | Based on PMR Invoice for Pineville. Pineville estimate of $1k for 50 people, assumed $3k for 150 people and additional fee for equipment use.
Total |  |  |  | 5088 |  | 5113.44
Note on L7: Revised acreage verified by Paul Puckett Price from FSMF estimate

## TC
Asset Retirement Obligation
Probability Weighted Settlement Estimates
Probability of Occurrence |  |  | 5% | 85% | 10%
Location | Description | Legal Requirement |  | Cost ($000s) |  | Weighted Cost | Comment | Support
TC1 | Ash Pond Closure | Resource Conservation and Recovery Act | 6443.1 | 7159 | 7874.9 | 7194.795 | $83k/acre at 115 acres * 75% Acreage verified by Paul Puckett-Environmental Dept | FSMS estimate of $83k/acre per study during Pineville retirement
TC1 | Coal storage area | Clean Water Act | 223.2 | 248 | 272.8 | 249.24 | $15k/acre at 22 acres * 75% Acreage verified by Delbert Billiter-Fuels Dept. | Pineville estimate of $15k/acre
TC1 | Mercury Removal - Level Instrumentation | Resource Conservation and Recovery Act | 0 | 0 | 0 | 0 | Since the $ 80 estimate is immaterial no aro will be established | Per Mike Winkler in Environmental $4.50/lb. Supported by ENSCO quote.
TC1 | Nuclear Source Removal - Coal Flow indicators | The Cabinet for Human Resources - KRS 211.844, regulation 902 KAR Chapter 100 | 15.1875 | 16.875 | 18.5625 | 16.9594 | Cesium source removal - 25 boxes attached to outside of ductwork and above coal feeders. Tie to conveyors on TC1. | Used estimate of $900 * 75% per source based on Ghent's estimate from call to Ohmart 12/02. Supported by OHMART email
TC1 | Sewage Treatment Plant |  | 3.375 | 3.75 | 4.125 | 3.7688 | Estimated cost to pump out tank, fill tank with soil, and grade land. | Supported by PMR invoice
TC1 | Hazardous Material Disposal | Clean Water Act Toxic Substances Control Act | 2.025 | 2.25 | 2.475 | 2.2612 | $480 per drum for 6 drums | Supported by faxed estimate provided by ENSCO Inc.
TC CTs | Transformer Oil | Clean Water Act Toxic Substances Control Act | 0 | 0 | 0 | 0 | Marketable - no PCBs
Total |  |  |  | 7429.875 |  | 7467.0244

## GH
Asset Retirement Obligation
Probability Weighted Settlement Estimates
Probability of Occurrence |  |  | 5% | 85% | 10%
Location | Description | Legal Requirement |  | Cost ($000s) |  | Weighted Cost | Comment | Support
GH | Ash Pond ATB I & II | Resource Conservation and Recovery Act | 20617.2 | 22908 | 25198.8 | 23022.54 | $83k/acre at 276 acres Acreage verified by Paul Puckett-Environmental Dept | FSMS estimate of $83k/acre per study during Pineville retirement
GH | Gypsum Stack | Clean Water Act | 747 | 830 | 913 | 834.15 | Assume closure similar to ash pond - $83k/acre at 10 acres Acreage verified by Paul Puckett-Environmental Dept | FSMS estimate of $83k/acre per study during Pineville retirement
GH | Radiation Sources - Cesium | The Cabinet for Human Resources - KRS 211.844, regulation 902 KAR Chapter 100 | 120.6 | 134 | 147.4 | 134.67 | Cesium Sources - 154 - Cesium sources - 154. Unit 1 - 15%; Unit 2 - 24%; Unit 3 - 16%; Unit 4 - 19%; Scrubber - 9%; Coal Yard - 17%. | Cost based on phone conversations with vendors (Ohmart 12/02) and physical counts. Supported by email from OHMART.
GH | Radiation Sources - Radium | The Cabinet for Human Resources - KRS 211.844, regulation 902 KAR Chapter 100 | 44.1 | 49 | 53.9 | 49.245 | Radium Sources - 42; Unit 1 - 6; Unit 2 - 12; Unit 3 - 12; Unit 4 - 12 | Cost based on phone conversations with vendors (Ohmart 12/02) and physical counts. Supported by email from OHMART.
GH | Removal of 10,000 Gallon underground tank | Comprehensive Emergency Response and Liability Act | 11.7 | 13 | 14.3 | 13.065 | Common to the plant in the Coal Yard. | Supported by email from Evergreen USA
GH | Remediation of underground fuel oil piping | Comprehensive Emergency Response and Liability Act | 3.6 | 4 | 4.4 | 4.02 | Common to the plant or divide equally among the 4 units | Supported by email from Evergreen USA
GH | Station Oil Reservoirs (including transformers) | Clean Water Act Toxic Substances Control Act | 10.8 | 12 | 13.2 | 12.06 | 226,000 gallons on site - Cost of $0.60 per gallon for approx. 20,000 gallons of contaminated oils at the time of closure. Allocate evenly across all units (there will likely be some contaminated oils on site that will require a charge). Most oil will be recycled at no cost. | American Enviro Services will reclaim some oils at $0.60 per gallon if contaminated, including up to 50 ppm pf PCB (based on work performed in 12/02 & confirming phone interview). There is no charge for uncontaminated oil. It is estimated a portion of the oils will be contaminated, some with non-PCB oil at <50 ppm. Supported by Enviro-Services invoice.
GH | Mercury Removal | Resource Conservation and Recovery Act | 0 | 0 | 0 | 0 | Since the $ 214 estimate is immaterial no aro will be established | Supported by ENSCO quote provided by Mike Winkler
GH | Chemical Tank clean up | Clean Water Act | 11.7 | 13 | 14.3 | 13.065 | Anticipate needing to work with 1 40,000 gallon acid tank and 2 10,000 gallon caustic tanks. | Supported by email from Evergreen USA
GH | Sewage Plant | Clean Water Act | 9 | 10 | 11 | 10.05 | Estimated cost to pump out tank, fill tank with soil, and grade land. | Based on Pineville estimate of $1k for 50 people, assumed $4k for 200 people and additional fee for equipment use. Supported by PMR invoice
GH | Coal Yard covering | Clean Water Act | 607.5 | 675 | 742.5 | 678.375 | Not unit specific | Based on Pineville estimate - $15k/acre for 45 acres Acreage verified by Delbert Billiter-Fuels Dept.
Total |  |  |  | 24648 |  | 24771.24

## BR
Asset Retirement Obligation
Probability Weighted Settlement Estimates
Probability of Occurrence |  |  | 5% | 85% | 10%
Location | Description | Legal Requirement |  | Cost ($000s) |  | Weighted Cost | Comment | Support
BR ST | Ash Pond | Resource Conservation and Recovery Act | 8590.5 | 9545 | 9628 | 9505.575 | Not unit specific - Steam units only 1,2,3 | $83k/acre for 116 acres Acreage verified by Paul Puckett-Environmental Dept
BR3 | Radiation Sources - BR3 | The Cabinet for Human Resources - KRS 211.844, regulation 902 KAR Chapter 100 | 14.4 | 16 | 17.6 | 16.08 | Sources located with the following 10 assets w/UOP 5676: 3-1,3-2,3-3,3-4,&3-5 Feeders Upper & Lower. Also, the assets with UOP 5025: Hoppers A26,A22,A25,A21,A24,A20,A23,A19,B26,B22,B25,B21,B24,B20,B23,B19 | Radiation Sources at $870 per 18 sources. Cost based on conversations with vendors (Secoal, contract supplier of radition sources, 12/02) and physical counts. Supported by OHMART email
BR ST | GSU, transformer oil, lubricating oils, ehc fluid | Clean Water Act Toxic Substances Control Act | 0 | 0 | 0 | 0 | Not unit specific - include BR 1, 2,3. Transformers only. This oil has no PCBs (non-hazardous). Should be able to sell for reuse. Tie to BR3 | Supported by internal email from Shannon Charnas. American Enviro Services will take oil at no cost
BR CT | GSU, transformer oil, lubricating oils, ehc fluid | Clean Water Act Toxic Substances Control Act | 0 | 0 | 0 | 0 | Not unit specific - include BR 5, 6, 7, 8, 9, 10,11. Transformers only. This oil has no PCBs (non-hazardous). Should be able to sell for reuse. Tie to BR 7. | Supported by internal email from Shannon Charnas. American Enviro Services will take oil at no cost
BR ST | Removal of Fuel Oil Tanks - BR Steam units 1, 2, 3 | Clean Water Act, Comprehensive Emergency Response and Liability Act | 126 | 140 | 154 | 140.7 | Tanks are not unit specific - for BR 1, 2, 3 - flat fee paid to contractor for removal. ESTIMATE | Supported by email from Somerset Environmental
BR CT | Removal of Fuel Oil Tanks - BR CTs | Clean Water Act | 252 | 280 | 308 | 281.4 | Tanks are not unit specific - include BR 5, 6, 7, 8, 9, 10, 11 - flat fee paid to contractor for removal. ESTIMATE | Supported by email from Somerset Environmental
BR ST | Remediation of underground fuel oil piping - Steam | Clean Water Act, Comprehensive Emergency Response and Liability Act | 15.3 | 17 | 18.7 | 17.085 | Estimate - Not unit specific - include BR 1, 2,3. | Supported by engineering estimate provided by Barry Currens
BR CT | Remediation of underground fuel oil piping - CTs | Clean Water Act | 28.8 | 32 | 35.2 | 32.16 | Not unit specific - include BR 5, 6, 7, 8, 9, 10,11. | Supported by engineering estimate provided by Barry Currens
BR ST/CT | Mercury Removal | Resource Conservation and Recovery Act | 0 | 0 | 0 | 0 | Due to immaterial costs of $305 no ARO is being establised | Per Mike Winkler in Environmental $4.50/lb. Supported by ENSCO quote. 15 bs per Shannon Charnas email
BR | Lab Chemical disposal | Resource Conservation and Recovery Act | 16.2 | 18 | 19.8 | 18.09 | BR1 - Lab Equipment UOP 5389. | Supported by estimate from GE Betz Inc.
BR | Sewage Plant | Clean Water Act | 9 | 10 | 11 | 10.05 | Estimated cost to pump out tank, fill tank with soil, and grade land. | Based on Pineville estimate of $1k for 50 people, assumed $4k for 200 people and additional fee for equipment use. Supported by BMR invoice
BR ST | Coal Yard covering | Clean Water Act | 54 | 60 | 66 | 60.3 | Not unit specific - Steam units 1, 2,3. | Based on Pineville estimate - $15k/acre for 4 acres Acreage verified by Delbert Billiter-Fuels Dept.
BR ST | Coal pile retention pond closing | Clean Water Act | 165.6 | 184 | 202.4 | 184.92 | Estimate - Not unit specific - Steam units 1, 2,3. | Supported by engineering estimate provided by Barry Currens
Total |  |  |  | 10302 |  | 10266.36
Note on L7: E008422: Estimate from Ghent

## TY
Asset Retirement Obligation
Probability Weighted Settlement Estimates
Probability of Occurrence |  |  | 5% | 85% |  | 10%
Location | Description | Legal Requirement |  | Cost ($000s) |  |  | Weighted Cost | Comment | Support
TY | Ash Pond | Resource Conservation and Recovery Act | 672.3 | 747 |  | 821.7 | 750.735 | Not unit specific. | $83k/acre at 9 acres based on Pineville estimate Acreage verified by Paul Puckett-Environmental Dept
TY | Demolition Service Water Pump structures | Corps of Engineers | 162 | 180 | 180 | 198 | 180.9 | 2 structures which have asbestos and lead paint issues - Not unit specific. | Flat fee for contractor removal. Supported by estimate from Evans Construction Co
TY | GSU, transformer oil, lubricating oils, ehc fluid | Clean Water Act Toxic Substances Control Act | 0 | 0 |  | 0 | 0 | Not unit specific - Tie to transformer on TY3. This oil has no PCBs (non-hazardous). Should be able to sell for reuse. | 8 oil-field transformers at $5,000. Based upon estimate from Somerset Environmental (contractor) received on 12/23/02.
TY | Removal of Fuel Oil Tanks | Clean Water Act, Comprehensive Emergency Response and Liability Act | 90 | 100 |  | 110 | 100.5 | One underground and one above ground - Not unit specific. | Flat fee for contractor removal. Based upon estimate from Somerset Environmental (contractor) received on 12/23/02.
TY | Remediation of underground fuel oil piping | Clean Water Act, Comprehensive Emergency Response and Liability Act | 12.6 | 14 |  | 15.4 | 14.07 | Not unit specific. | Engineering estimate provided by Barry Currens
TY | Mercury Removal | Resource Conservation and Recovery Act | 2.25 | 2.5 |  | 2.75 | 2.5125 | Not unit specific - allocable among units. UOP 5373 - Instrument or measuring device (instrumentation). Tie to TY3 | Supported by ENSCO quote provided by Mike Winkler
TY | Sewage Plant | Clean Water Act | 4.5 | 5 |  | 5.5 | 5.025 | Estimated cost to pump out tank, fill tank with soil, and grade land. | Based on Pineville estimate of $1k for 50 people and additional fee for equipment use. Supported by PMR invoice
TY | Coal Yard covering | Clean Water Act | 27 | 30 |  | 33 | 30.15 | Assuming that we would be required to close similar to the ash pond - Not unit specific | 2 acres at $15k per acre Pineville estimate Acreage verified by Delbert Billiter-Fuels Dept.
Total |  |  |  | 1078.5 |  |  | 1083.8925

## GR
Asset Retirement Obligation
Probability Weighted Settlement Estimates
Probability of Occurrence |  |  | 5% | 85% | 10%
Location | Description | Legal Requirement |  | Cost ($000s) |  | Weighted Cost | Comment | Support
GR | Ash Pond Remediation | Clean Water Act | 8739.9 | 9711 | 10682.1 | 9759.555 | $83k/acre at 117 acres Acreage verified by Paul Puckett-Environmental Dept | FSMS estimate of $83k/acre per study during Pineville retirement
GR | Coal Storage Pile Remediation | Clean Water Act | 81 | 90 | 99 | 90.45 | Coal pile is 6 acres. Common to the plant divide evenly among the units. Acreage verified by Delbert Billiter-Fuels Dept. | Based on Pineville estimate - $15k/acre
GR | Oil Storage Tanks | Clean Water Act | 9 | 10 | 11 | 10.05 | Based on $0.22 gallon (41,700 gallons) plus removal of underground line $1K/100 feet. | Based on Ghent estimate. Supported by email from Evergreen USA
GR | Underground Storage Tanks | Comprehensive Emergency Response and Liability Act | 11.7 | 13 | 14.3 | 13.065 | Based on Ghent estimate. | Supported by email from Evergreen USA
GR 1/2 | Mercury Switches - All Units | Resource Conservation and Recovery Act | 1.8 | 2 | 2.2 | 2.01 | Based on approx. 100 mercury sources (total) and some pre-existing on-site mercury storage from years past. | Supported by ENSCO quote provided by Mike Winkler
GR | Sewage Treatment Plant | Clean Water Act | 4.5 | 5 | 5.5 | 5.025 | Common - divide evenly among the units. Estimated cost to pump out tank, fill tank with soil, and grade land. | Based on Pineville estimate of $1k for 50 people, assumed $1k for 50 people and additional fee for equipment use. Supported by PMR invoice
GR | Switchyard transformers, OCB's, etc. | Clean Water Act Toxic Substances Control Act | 22.5 | 25 | 27.5 | 25.125 | 41,700 gallons at $0.60 per gallon. Allocate evenly across all units | Supported by invoice from American Enviro Services
GR | Acid Tank Disposal | Clean Water Act Toxic Substances Control Act | 2.7 | 3 | 3.3 | 3.015 | Common to the plant divide evenly among the units | $75/hr company employee to neutralize chemicals and dispose of in ash pond. ($3,000) Tank removal for scrap $0. Supported by Shannon Charnas email
GR | Caustic Tank Disposal | Clean Water Act Toxic Substances Control Act | 2.7 | 3 | 3.3 | 3.015 | Common to the plant divide evenly among the units | $75/hr company employee to neutralize chemicals and dispose of in ash pond. ($3,000) Tank removal for scrap $0. Supported by Shannon Charnas email
GR | Lime Storage Silo | Clean Water Act | 5.4 | 6 | 6.6 | 6.03 |  | 80 manhours at $75 per hour internal burdened labor rate. Supported by Shannon Charnas email
GR | Nuclear Source | The Cabinet for Human Resources - KRS 211.844, regulation 902 KAR Chapter 100 | 0.9 | 1 | 1.1 | 1.005 | Plant has one nuclear source at the scrubber. | $1k/nuclear source based on Ghent's 12/02 phone estimate from nuclear disposal co. Supported by email from OHMART
Total |  |  |  | 9869 |  | 9918.345