## FEB-14 Impact By Unit
Dated: 03/03/14 15:00 hours | [16 empty] | EAF | EUOR | EFOR
Denominator
Unit | Event | Event | Cause | Event | Event | Evt. | Equiv. | MWH | EAF | EUOR | EFOR |  |  |  | Event | Event
Name | Type | No | Code | Start | End | Hrs | Dur Hrs | Lost | Lost | Impact | Impact | GAC | GMC | NMC | Cause | Description | 8163240 | 7889119.6965 | 7609319.473
BR1 | PD | 1 | 260 | 2014-01-03 | 2014-01-03 02:00 | 2 | 0.59649 | 63.8246 | 0.0007819% |  |  | 80 | 114 | 107 | Primary Air Fan | 1-3 mil primary air fan housing leak repair
BR1 | PD | 2 | 310 | 2014-02-19 22:00 | 2014-02-20 02:51 | 4.85 | 1.2338 | 132.0136 | 0.001617% |  |  | 85 | 114 | 107 | Pulverizer Mills | 1-1 & 1-4 mill inspection
BR1 | PD | 3 | 310 | 2014-02-20 22:00 | 2014-02-21 03:39 | 5.65 | 1.4373 | 153.789 | 0.001884% |  |  | 85 | 114 | 107 | Pulverizer Mills | 1-3 mill inspection
BR1 | PD | 4 | 1400 | 2014-02-26 23:00 | 2014-02-27 | 1 | 0.5614 | 60.0702 | 0.0007359% |  |  | 50 | 114 | 107 | Forced Draft Fans | Repair leaking cooler hose 1-1 FD Fan
BR1 | PD | 5 | 310 | 2014-02-27 | 2014-02-27 02:28 | 2.4667 | 0.84386 | 90.293 | 0.001106% |  |  | 75 | 114 | 107 | Pulverizer Mills | 1-2 mill inspection
[9 empty] | 0% | 0% | 0%
BR1 | [5 empty] | 15.9667 | 4.6728 | 499.9904 | 0.006125% | 0% | 0%
BR2 | PD | 1 | 310 | 2014-01-02 22:00 | 2014-01-03 02:00 | 4 | 1.2222 | 205.3333 | 0.002515% |  |  | 125 | 180 | 168 | Pulverizer Mills | Inspect 2-3 mill gearbox
BR2 | D1 | 2 | 310 | 2014-01-11 18:55 | 2014-01-11 21:25 | 2.5 | 0.625 | 105 | 0.001286% | 0.001331% | 0.00138% | 135 | 180 | 168 | Pulverizer Mills | Repair 2-2 mill broken spring bolt
BR2 | PD | 3 | 344 | 2014-01-13 09:44 | 2014-01-13 12:15 | 2.5167 | 0.9088 | 152.6778 | 0.00187% |  |  | 115 | 180 | 168 | Pulverizer Inspection | Inspect 2-3 mill concerning thrust bearing issue
BR2 | D1 | 4 | 310 | 2014-02-11 20:04 | 2014-02-12 02:17 | 6.2167 | 1.7269 | 290.1111 | 0.003554% | 0.003677% | 0.003813% | 130 | 180 | 168 | Pulverizer Mills | 2-4 mill west door broken spring bolt
BR2 | D1 | 5 | 310 | 2014-02-14 18:23 | 2014-02-14 19:11 | 0.8 | 0.2 | 33.6 | 0.0004116% | 0.0004259% | 0.0004416% | 135 | 180 | 168 | Pulverizer Mills | 2-4 hot air damper not making limit
BR2 | D1 | 6 | 310 | 2014-02-16 06:34 | 2014-02-16 17:57 | 11.3833 | 3.4782 | 584.3444 | 0.007158% | 0.007407% | 0.007679% | 125 | 180 | 168 | Pulverizer Mills | 2-2 mill shaft broken
BR2 | D1 | 7 | 310 | 2014-02-16 17:57 | 2014-02-19 12:47 | 66.83 | 18.5639 | 3118.7333 | 0.0382% | 0.03953% | 0.04099% | 130 | 180 | 168 | Pulverizer Mills | Broken coal mill shaft 2-2 mill 6543464
BR2 | D1 | 8 | 310 | 2014-02-19 12:47 | 2014-02-20 22:00 | 33.22 | 8.305 | 1395.24 | 0.01709% | 0.01769% | 0.01834% | 135 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
BR2 | PD | 9 | 3410 | 2014-02-20 22:00 | 2014-02-21 09:00 | 11 | 4.2778 | 718.6667 | 0.008804% |  |  | 110 | 180 | 168 | Feedwater Pump | Repair 2-2 BFP drain valve 6532228
BR2 | D1 | 10 | 310 | 2014-02-21 09:00 | 2014-02-21 22:13 | 13.22 | 3.6722 | 616.9333 | 0.007557% | 0.00782% | 0.008108% | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
BR2 | MO | 11 | 3110 | 2014-02-21 22:13 | 2014-02-23 02:07 | 27.9 | 27.9 | 4687.2 | 0.05742% | 0.05941% |  | 0 | 180 | 168 | Condenser Tube Leaks | Repair condenser tube leak and other misc. issues 6522386
BR2 | D1 | 12 | 310 | 2014-02-23 08:51 | 2014-02-24 08:24 | 23.55 | 6.5417 | 1099 | 0.01346% | 0.01393% | 0.01444% | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
BR2 | D1 | 13 | 3410 | 2014-02-24 08:24 | 2014-02-26 20:00 | 59.6 | 24.8333 | 4172 | 0.05111% | 0.05288% | 0.05483% | 105 | 180 | 168 | Feedwater Pump OB Bearing | 2-2 BFP OB bearing hot 6546733
BR2 | MO | 15 | 8560 | 2014-02-28 12:26 | 2014-03-02 18:19 | 53.88 | 53.88 | 9051.84 | 0.1109% | 0.1147% |  | 0 | 180 | 168 | Electrostatic Precipitator Problems | Precipitator fields out of service and tube leak repair
BR2 | [5 empty] | 316.6167 | 156.135 | 26230.68 | 0.3213% | 0.3188% | 0.15%
BR3 | PD | 1 | 310 | 2014-01-08 22:33 | 2014-01-09 01:15 | 2.7 | 0.63217 | 261.7168 | 0.003206% |  |  | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
BR3 | PD | 2 | 310 | 2014-01-09 21:20 | 2014-01-10 00:33 | 3.2167 | 0.75314 | 311.7985 | 0.00382% | 0.003952% | 0.004098% | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
BR3 | MO | 4 | 740 | 2014-01-11 10:37 | 2014-01-12 04:08 | 17.5167 | 17.5167 | 7251.9 | 0.08884% | 0.09192% |  | 0 | 457 | 414 | 3-1 Boiler Recirculation Pump Replacement | Replace 3-1 BCWP
BR3 | PD | 5 | 310 | 2014-01-13 22:00 | 2014-01-14 00:29 | 2.4833 | 0.58144 | 240.7149 | 0.002949% |  |  | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
BR3 | PD | 6 | 310 | 2014-01-14 21:35 | 2014-01-15 00:37 | 3.0333 | 0.71021 | 294.0276 | 0.003602% |  |  | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
BR3 | PD | 7 | 310 | 2014-01-15 21:57 | 2014-01-16 00:40 | 2.7167 | 0.63607 | 263.3324 | 0.003226% |  |  | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
BR3 | U1 | 8 | 339 | 2014-01-30 03:57 | 2014-02-01 16:05 | 60.1333 | 60.1333 | 24895.2 | 0.305% | 0.3156% | 0.3272% | 0 | 457 | 414 | Pulverizer System Puff | 3-5 Mill puff causing D corner burner damage and associated boiler tube leak.
BR3 | PD | 9 | 3412 | 2014-02-04 22:00 | 2014-02-05 01:52 | 3.8667 | 1.2438 | 514.9182 | 0.006308% |  |  | 310 | 457 | 414 | Feedwater Pump Drive - Steam Turbine | Collecting 3-2 BFP vibration data
BR3 | D1 | 10 | 3414 | 2014-02-21 22:08 | 2014-02-22 23:58 | 25.8333 | 8.5923 | 3557.1991 | 0.04358% | 0.04509% | 0.04675% | 305 | 457 | 414 | Feedwater Pump Local Controls | 3-2 BFPT LP governor valve indication 6545010
BR3 | NC | 11 | 1710 | 2014-02-24 22:00 | 2014-02-25 02:05 | 4.0833 | [5 empty] | 0 | 457 | 414 | Combustion/Steam Condition Controls | Combustion tuning 6544234
BR3 | D1 | 12 | 3414 | 2014-02-25 05:51 | 2014-02-25 07:39 | 1.8 | 0.61838 | 256.0096 | 0.003136% | 0.003245% | 0.003364% | 300 | 457 | 414 | Feedwater Pump Local Controls | 3-2 BFP LP gov. servo problems 6546920
BR3 | [5 empty] | 127.3833 | 91.4174 | 37846.8171 | 0.4636% | 0.4598% | 0.3814%
CR4 | D1 | 1 | 8280 | 2014-01-07 21:20 | 2014-01-07 23:43 | 2.3833 | 0.7377 | 114.3433 | 0.001401% | 0.001449% | 0.001503% | 116 | 168 | 155 | Wet Scrubber - Reagent Feed Piping | Reactive feed line from supply pump frozen.
CR4 | NC | 2 | 1150 | 2014-01-08 21:00 | 2014-01-09 06:07 | 9.1167 | [5 empty] | 0 | 168 | 155 | Second Superheater Slagging or Fouling | Boiler deslag. Full load available if needed.
CR4 | D1 | 3 | 250 | 2014-01-09 19:11 | 2014-01-10 02:13 | 7.0333 | 1.8002 | 279.0308 | 0.003418% | 0.003537% | 0.003667% | 125 | 168 | 155 | Pulverizer Feeders | 4A feeder belt broke. Repaired same.
CR4 | D4 | 4 | 255 | 2014-01-19 21:00 | 2014-01-20 06:24 | 9.4 | 2.406 | 372.9226 | 0.004568% | 0.004727% |  | 125 | 168 | 155 | Pulverizer Feeder Coal Scales | 4C2 Feeder Belt Repair
CR4 | D4 | 5 | 344 | 2014-01-20 09:52 | 2014-01-20 16:35 | 6.7167 | 1.5192 | 235.4831 | 0.002885% | 0.002985% |  | 130 | 168 | 155 | Pulverizer Inspection | 4C mill making noise - made roller adjustment after removing debris buildup on journal
CR4 | NC | 6 | 1150 | 2014-01-24 21:30 | 2014-01-25 06:09 | 8.65 | [5 empty] | 0 | 168 | 155 | Second Superheater Slagging or Fouling | Boiler deslag. Full load available if needed.
CR4 | NC | 7 | 1150 | 2014-01-30 21:45 | 2014-01-31 04:30 | 6.75 | [5 empty] | 0 | 168 | 155 | Second Superheater Slagging or Fouling | Boiler deslag. Full load availabe if needed.
CR4 | D1 | 8 | 8560 | 2014-02-09 | 2014-02-09 11:42 | 11.7 | 6.1286 | 949.9286 | 0.01164% | 0.01204% | 0.01248% | 80 | 168 | 155 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
CR4 | MO | 9 | 8100 | 2014-02-16 11:30 | 2014-02-18 04:28 | 40.9667 | 40.9667 | 6349.8333 | 0.07779% | 0.08049% |  | 0 | 168 | 155 | Wet Scrubber/absorber Tower Or Module | Flue gas desulfurization module cleaning.
CR4 | D1 | 10 | 4261 | 2014-02-18 11:05 | 2014-02-18 22:14 | 11.15 | 0.8628 | 133.7336 | 0.001638% | 0.001695% | 0.001757% | 155 | 168 | 155 | Turbine Control Valves | Governor valve sticking at 155 MW. Lubrication issues.
CR4 | MO | 11 | 4261 | 2014-02-18 22:14 | 2014-02-20 00:32 | 26.3 | 26.3 | 4076.5 | 0.04994% | 0.05167% |  | 0 | 168 | 155 | Turbine Control Valves | Governor valve sticking at 155 MW. Lubrication issues. CSS cleaned hardened grea
CR4 | NC | 12 | 9999 | 2014-02-24 09:40 | 2014-02-24 14:12 | 4.5333 | [5 empty] | 0 | 168 | 155 | Total Unit Performance Testing | Full Load winter capability test.
CR4 | D4 | 13 | 310 | 2014-02-28 22:00 | 2014-03-01 06:51 | 8.85 | 2.0018 | 310.2768 | 0.003801% | 0.003933% |  | 130 | 168 | 155 | Pulverizer Mills | 4A Mill inspection
CR4 | [5 empty] | 153.55 | 82.7229 | 12822.0521 | 0.1571% | 0.1625% | 0.01941%
D4
CR5 | D4 | 1 | 250 | 2014-01-09 19:40 | 2014-01-10 04:37 | 8.95 | 3.2635 | 548.274 | 0.006716% | 0.00695% |  | 115 | 181 | 168 | Pulverizer Feeders | 5C1 coal feeder repair - changing out a roller bearing.
CR5 | U1 | 2 | 1470 | 2014-01-11 19:43 | 2014-01-11 22:26 | 2.7167 | 2.7167 | 456.4 | 0.005591% | 0.005785% | 0.005998% | 0 | 181 | 168 | Induced Draft Fan Motors and Drives | 5A induced draft fan tripped due to bad thyrister card causing unit to trip.
CR5 | D4 | 3 | 3416 | 2014-01-24 23:00 | 2014-01-25 07:25 | 8.4167 | 5.1616 | 867.1492 | 0.01062% | 0.01099% |  | 70 | 181 | 168 | Other Feedwater Pump Problems | 51 boiler feed pump maintenance.
CR5 | D4 | 4 | 344 | 2014-02-02 23:00 | 2014-02-03 04:50 | 5.8333 | 1.8048 | 303.2044 | 0.003714% | 0.003843% | 0.003985% | 125 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
CR5 | D4 | 5 | 344 | 2014-02-03 23:00 | 2014-02-04 04:55 | 5.9167 | 1.6671 | 280.0773 | 0.003431% | 0.00355% |  | 130 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
CR5 | D4 | 6 | 344 | 2014-02-04 23:00 | 2014-02-05 05:00 | 6 | 1.8564 | 311.8674 | 0.00382% | 0.003953% |  | 125 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
CR5 | U2 | 7 | 1060 | 2014-02-07 10:51 | 2014-02-09 | 37.15 | 37.15 | 6241.2 | 0.07645% | 0.07911% | 0.08202% | 0 | 181 | 168 | First Reheater Leaks | Reheat boiler tube leak - cracked. Total of 6 leaks - 1 dutchman & 4 padwelds.
CR5 | SF | 8 | 8560 | 2014-02-09 | 2014-02-10 00:12 | 24.2 | 24.2 | 4065.6 | 0.0498% | 0.05153% | 0.05343% | 0 | 181 | 168 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
CR5 | NC | 9 | 9999 | 2014-02-13 10:00 | 2014-02-13 14:00 | 4 | [5 empty] | 0 | 181 | 168 | Total Unit Performance Testing | Full load winter capability test.
CR5 | U1 | 10 | 1475 | 2014-02-21 04:01 | 2014-02-21 14:53 | 10.8667 | 10.8667 | 1825.6 | 0.02236% | 0.02314% | 0.02399% | 0 | 181 | 168 | Induced Draft Fan Controls | 5A ID Fan trip - Replaced I/O PCB and batteries in Sigma controller and reset faul
CR5 | [5 empty] | 114.05 | 88.6867 | 14899.3724 | 0.1825% | 0.1889% | 0.1694%
D4
CR6 | U2 | 1 | 1070 | 2014-01-03 11:03 | 2014-01-04 17:05 | 30.0333 | 30.0333 | 7208 | 0.0883% | 0.09137% | 0.09473% | 0 | 261 | 240 | Reheater Tube Leaks | Boiler Tube Leak - A tube leak was discovered in the RH Pendants.
CR6 | D1 | 2 | 310 | 2014-01-05 02:54 | 2014-01-05 19:35 | 16.6833 | 3.26 | 782.3908 | 0.009584% | 0.009917% | 0.01028% | 210 | 261 | 240 | Pulverizer Mills | 6C coal mill roller maintenance.
CR6 | MO | 3 | 1070 | 2014-01-09 20:23 | 2014-01-17 04:37 | 176.2333 | 176.2333 | 42296 | 0.5181% | 0.5361% |  | 0 | 261 | 240 | Reheater Tube Leaks | Boiler Leak Repair - A tube within the RH Pendants was discovered to be cracked,
CR6 | U1 | 4 | 1700 | 2014-01-17 06:00 | 2014-01-17 06:42 | 0.7 | 0.7 | 168 | 0.002058% | 0.00213% | 0.002208% | 0 | 261 | 240 | Feedwater Controls | Low drum level - high boiler pressure
CR6 | D4 | 5 | 344 | 2014-01-20 07:54 | 2014-01-20 11:54 | 4 | 0.62835 | 150.8046 | 0.001847% | 0.001912% |  | 220 | 261 | 240 | Pulverizer Inspection | 6A coal mill making noise. Removed a piece of metal from journal shield area of mill
CR6 | D1 | 6 | 344 | 2014-01-20 13:08 | 2014-01-20 18:00 | 4.8667 | 0.7645 | 183.4789 | 0.002248% | 0.002326% | 0.002411% | 220 | 261 | 240 | Pulverizer Inspection | 6D coal mill making noise. Removed metal from journal shield area of mill.
CR6 | D1 | 7 | 250 | 2014-02-07 01:12 | 2014-02-07 02:10 | 0.96667 | 0.22593 | 54.2222 | 0.0006642% | 0.0006873% | 0.0007126% | 200 | 261 | 240 | Pulverizer Feeders | D1 feeder plugged due to torn belt.
CR6 | D1 | 8 | 250 | 2014-02-08 00:05 | 2014-02-08 01:13 | 1.1333 | 0.22146 | 53.1494 | 0.0006511% | 0.0006737% | 0.0006985% | 210 | 261 | 240 | Pulverizer Feeders | D2 feeder plugged due to wet coal.
CR6 | D1 | 9 | 8560 | 2014-02-09 | 2014-02-09 06:50 | 6.8333 | 2.5134 | 603.2184 | 0.007389% | 0.007646% | 0.007927% | 165 | 261 | 240 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
CR6 | D1 | 10 | 340 | 2014-02-09 06:50 | 2014-02-09 07:15 | 0.41667 | 0.15326 | 36.7816 | 0.0004506% | 0.0004662% | 0.0004834% | 165 | 261 | 240 | Other Pulverizer Problems | Support fuel unavailable due to loss of communication between precipitator & DCS.
CR6 | D1 | 11 | 4240 | 2014-02-11 08:00 | 2014-02-11 14:00 | 6 | 0.94253 | 226.2069 | 0.002771% | 0.002867% | 0.002973% | 220 | 261 | 240 | Lp Turbine Bearings | #4 Turbine bearing temperature running high.
CR6 | D1 | 12 | 250 | 2014-02-16 04:54 | 2014-02-16 12:17 | 7.3833 | 1.4427 | 346.2529 | 0.004242% | 0.004389% | 0.00455% | 210 | 261 | 240 | Pulverizer Feeders | 6B feeder belt torn. Repaired & put back in service.
CR6 | NC | 13 | 4240 | 2014-02-17 12:00 | 2014-02-17 15:01 | 3.0167 | [5 empty] | 0 | 261 | 240 | Lp Turbine Bearings | Turbine cool down in prep for removing #3 & #4 turbine bearing during maintenance
CR6 | MO | 14 | 4240 | 2014-02-17 15:01 | 2014-02-23 22:51 | 151.8333 | 151.8333 | 36440 | 0.4464% | 0.4619% |  | 0 | 261 | 240 | Lp Turbine Bearings | The #3 and #4 turbine bearings were removed. The #3 was found OK and was polished
CR6 | D1 | 15 | 9600 | 2014-02-28 08:13 | 2014-02-28 08:35 | 0.36667 | 0.029502 | 7.0805 | 8.674e-05% | 8.975e-05% | 9.305e-05% | 240 | 261 | 240 | So2 Stack Emissions - Fossil Steam Units | Dropped load to keep SO2 in compliance.
CR6 | D1 | 16 | 9600 | 2014-02-28 08:35 | 2014-02-28 09:53 | 1.3 | 0.20421 | 49.0115 | 0.0006004% | 0.0006213% | 0.0006441% | 220 | 261 | 240 | So2 Stack Emissions - Fossil Steam Units | Dropped load an additional 20 MW to remain in SO2 compliance . Unit now at 220 MW
CR6 | [5 empty] | 411.7667 | 369.1858 | 88604.5977 | 1.085% | 1.123% | 0.1277%
D4
GH1 | D1 | 1 | 9270 | 2014-01-08 07:48 | 2014-01-08 09:10 | 1.3667 | 0.15068 | 72.4756 | 0.0008878% | 0.0009187% | 0.0009525% | 460 | 517 | 481 | Wet Coal | Feeder plugged due to wet coal and this tripped the mill.
GH1 | PD | 2 | 344 | 2014-01-14 23:37 | 2014-01-15 02:30 | 2.8833 | 0.31789 | 152.9059 | 0.001873% |  |  | 460 | 517 | 481 | Pulverizer Inspection | 1-6 Mill off to inspect and clean air flow transmitters.
GH1 | PD | 3 | 340 | 2014-01-16 21:57 | 2014-01-17 00:49 | 2.8667 | 0.31605 | 152.0221 | 0.001862% |  |  | 460 | 517 | 481 | Other Pulverizer Problems | 1-1 Mill journal replacement.
GH1 | D1 | 4 | 344 | 2014-01-27 06:00 | 2014-01-27 11:33 | 5.55 | 0.6119 | 294.3218 | 0.003605% | 0.003731% | 0.003868% | 460 | 517 | 481 | Pulverizer Inspection | 1-6 Mill off to inspect grinding section.
GH1 | D1 | 5 | 250 | 2014-01-28 21:25 | 2014-01-29 04:05 | 6.6667 | 0.73501 | 353.5397 | 0.004331% | 0.004481% | 0.004646% | 460 | 517 | 481 | Pulverizer Feeders | 1-4 Feeder belt was torn when cleanout conveyor failed.
GH1 | MO | 6 | 1060 | 2014-02-01 15:04 | 2014-02-03 01:27 | 34.3833 | 34.3833 | 16538.3833 | 0.2026% | 0.2096% |  | 0 | 517 | 481 | First Reheater Leaks | Unit 1 had been running with a tube leak, located around IK #6, for s
GH1 | D1 | 7 | 250 | 2014-02-07 12:35 | 2014-02-07 13:45 | 1.1667 | 0.12863 | 61.8694 | 0.0007579% | 0.0007842% | 0.0008131% | 460 | 517 | 481 | Pulverizer Feeders | Metal hung in 1-4 mill feeder.
GH1 | D1 | 8 | 250 | 2014-02-09 16:20 | 2014-02-09 19:43 | 3.3833 | 2.9449 | 1416.4845 | 0.01735% | 0.01795% | 0.01862% | 67 | 517 | 481 | Pulverizer Feeders | 1-4 Feeder belt bound up.
GH1 | PD | 9 | 250 | 2014-02-10 09:00 | 2014-02-10 15:33 | 6.55 | 0.84884 | 408.2918 | 0.005002% |  |  | 450 | 517 | 481 | Pulverizer Feeders | 1-4 Mill off to replace feeder discharge pipe pluggage detector.
GH1 | D1 | 10 | 9650 | 2014-02-13 07:23 | 2014-02-13 09:08 | 1.75 | 0.091393 | 43.9599 | 0.0005385% | 0.0005572% | 0.0005777% | 490 | 517 | 481 | Other Stack Or Exhaust Emissions -fossil Stm Unit | U1 H2SO4 was high. Dropped load to keep it in compliance.
GH1 | D1 | 11 | 344 | 2014-02-21 08:30 | 2014-02-21 12:30 | 4 | 0.51838 | 249.3385 | 0.003054% | 0.003161% | 0.003277% | 450 | 517 | 481 | Pulverizer Inspection | 1-6 Mill off to inspect grinding section.
GH1 | MO | 12 | 1060 | 2014-02-22 14:49 | 2014-02-23 11:03 | 20.2333 | 20.2333 | 9732.2333 | 0.1192% | 0.1234% |  | 0 | 517 | 481 | First Reheater Leaks | A leak was detected in Reheater pendant section of the boiler. Dispa
GH1 | PD | 13 | 344 | 2014-02-24 13:42 | 2014-02-24 16:59 | 3.2833 | 0.36199 | 174.1183 | 0.002133% |  |  | 460 | 517 | 481 | Pulverizer Inspection | 1-1 Mill off to inspect grinding section.
GH1 | D1 | 14 | 320 | 2014-02-25 11:17 | 2014-02-25 12:57 | 1.6667 | 0.18375 | 88.3849 | 0.001083% | 0.00112% | 0.001162% | 460 | 517 | 481 | Foreign Object in Mill | 1-3 Mill had a noise in the pyrite section. Removed the mill to
GH1 | [5 empty] | 95.75 | 61.826 | 29738.3289 | 0.3643% | 0.3657% | 0.03391%
PD
GH2 | D1 | 1 | 9650 | 2014-01-06 11:20 | 2014-01-06 12:00 | 0.66667 | 0.21218 | 101.2102 | 0.00124% | 0.001283% | 0.00133% | 347 | 509 | 477 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Lost SO3 mitigation system. Air pressure / injection causing H2S
GH2 | PD | 2 | 344 | 2014-01-14 23:43 | 2014-01-15 04:11 | 4.4667 | 0.51775 | 246.9654 | 0.003025% |  |  | 450 | 509 | 477 | Pulverizer Inspection | 2-6 Mill off to inspect and repair spring can shaft.
GH2 | D1 | 3 | 9650 | 2014-01-15 19:30 | 2014-01-15 21:03 | 1.55 | 0.27102 | 129.2773 | 0.001584% | 0.001639% | 0.001699% | 420 | 509 | 477 | Other Stack Or Exhaust Emissions -fossil Stm Unit | H2SO4 in high alarm. Dropped load to investigate. Blower for ou
GH2 | PD | 4 | 344 | 2014-01-17 23:30 | 2014-01-18 11:44 | 12.2333 | 1.1777 | 561.7479 | 0.006881% |  |  | 460 | 509 | 477 | Pulverizer Inspection | 2-6 Mill off for gear box inspection.
GH2 | D1 | 5 | 280 | 2014-01-18 13:37 | 2014-01-18 14:14 | 0.61667 | 0.059365 | 28.317 | 0.0003469% | 0.0003589% | 0.0003721% | 460 | 509 | 477 | Pulverizer Fires | 2-6 Mill off due to fire in the pyrite line.
GH2 | D1 | 6 | 312 | 2014-02-01 14:40 | 2014-02-01 18:00 | 3.3333 | 0.18991 | 90.5894 | 0.00111% | 0.001148% | 0.001191% | 480 | 509 | 477 | Pulverizer Mill Classifiers | 2-1 Mill not grinding, took off for inspection.
GH2 | PD | 7 | 344 | 2014-02-06 23:00 | 2014-02-07 01:24 | 2.4 | 0.23104 | 110.2067 | 0.00135% |  |  | 460 | 509 | 477 | Pulverizer Inspection | 2-2 Mill was removed from service to inspect due to high differen
GH2 | PD | 8 | 340 | 2014-02-13 23:00 | 2014-02-14 02:11 | 3.1833 | 0.30645 | 146.1769 | 0.001791% |  |  | 460 | 509 | 477 | Other Pulverizer Problems | 2-5 Mill off to replace pyrite scraper.
GH2 | PD | 9 | 340 | 2014-02-14 02:11 | 2014-02-14 03:39 | 1.4667 | 0.14119 | 67.3485 | 0.000825% |  |  | 460 | 509 | 477 | Other Pulverizer Problems | 2-6 Mill off to inspect grinding section and classifiers.
GH2 | D1 | 10 | 250 | 2014-02-15 03:20 | 2014-02-15 10:00 | 6.6667 | 0.64178 | 306.1297 | 0.00375% | 0.00388% | 0.004023% | 460 | 509 | 477 | Pulverizer Feeders | 2-1 Feeder control issue.
GH2 | D1 | 11 | 340 | 2014-02-17 06:24 | 2014-02-17 14:00 | 7.6 | 0.80629 | 384.5988 | 0.004711% | 0.004875% | 0.005054% | 455 | 509 | 477 | Other Pulverizer Problems | Removed 2-4 Mill from service for journal issue.
GH2 | D1 | 12 | 250 | 2014-02-19 05:20 | 2014-02-19 11:30 | 6.1667 | 0.7148 | 340.9597 | 0.004177% | 0.004322% | 0.004481% | 450 | 509 | 477 | Pulverizer Feeders | 2-6 Feeder off to replace the belt.
GH2 | D1 | 13 | 344 | 2014-02-24 23:55 | 2014-02-25 06:30 | 6.5833 | 0.63376 | 302.303 | 0.003703% | 0.003832% | 0.003973% | 460 | 509 | 477 | Pulverizer Inspection | 2-6 Mill off to inspect the grinding section.
GH2 | D1 | 14 | 280 | 2014-02-27 07:34 | 2014-02-27 12:11 | 4.6167 | 0.44443 | 211.9948 | 0.002597% | 0.002687% | 0.002786% | 460 | 509 | 477 | Pulverizer Fires | Load was reduced due to a fire in 2-1 Mill.
GH2 | [5 empty] | 61.55 | 6.3476 | 3027.8254 | 0.03709% | 0.02403% | 0.02491%
PD
GH3 | U1 | 1 | 1455 | 2014-01-07 21:20 | 2014-01-08 06:15 | 8.9167 | 8.9167 | 4297.8333 | 0.05265% | 0.05448% | 0.05648% | 0 | 527 | 482 | 3-2 Induced Draft Fan OB Bearing | 3-2 ID fan tripped on high vibration on OB fan bearing. This caused
GH3 | D1 | 2 | 1455 | 2014-01-08 06:15 | 2014-01-10 11:31 | 53.2667 | 33.0516 | 15930.8774 | 0.1952% | 0.2019% | 0.2094% | 200 | 527 | 482 | 3-2 Induced Draft Fan Out Of Service | Unit running with 3-2 ID fan out of service.
GH3 | MO | 3 | 1455 | 2014-01-10 11:31 | 2014-01-13 03:25 | 63.9 | 63.9 | 30799.8 | 0.3773% | 0.3904% |  | 0 | 527 | 482 | 3-2 Induced Draft Fan Trip | Unit derated to minimum load due to 3-2 ID Fan tripping on
GH3 | SF | 4 | 4609 | 2014-01-13 03:25 | 2014-01-13 06:19 | 2.9 | 2.9 | 1397.8 | 0.01712% | 0.01772% | 0.01837% | 0 | 527 | 482 | Other Exciter Problems | During the previous event, the unit had been rolled up to synchronise spe
GH3 | D1 | 5 | 1455 | 2014-01-21 23:18 | 2014-01-22 01:31 | 2.2167 | 0.029443 | 14.1917 | 0.0001738% | 0.0001799% | 0.0001865% | 520 | 527 | 482 | Induced Draft Fans | Load was reduced when 3-1 ID Fan blade position feedback failed,
GH3 | D1 | 6 | 9290 | 2014-01-24 23:19 | 2014-01-25 03:33 | 4.2333 | 0.37755 | 181.9771 | 0.002229% | 0.002307% | 0.002392% | 480 | 527 | 482 | Other Fuel Quality Problems | Load Reduction #3Derate was reported as a coal quality issue. Actually, we were b
GH3 | U1 | 7 | 1040 | 2014-01-25 03:33 | 2014-01-26 19:21 | 39.8 | 39.8 | 19183.6 | 0.235% | 0.2432% | 0.2521% | 0 | 527 | 482 | Superheater Tube Leaks | Unit was taken off line after developing a boiler tube leak in the Prim
GH3 | D1 | 8 | 1455 | 2014-01-26 19:21 | 2014-01-26 20:47 | 1.4333 | 0.88937 | 428.6782 | 0.005251% | 0.005434% | 0.005634% | 200 | 527 | 482 | Induced Draft Fans | Load Reduction #4Unit 3 was derated during startup when 3-2 ID Fan OB bearing fail
GH3 | MO | 9 | 1455 | 2014-01-26 20:47 | 2014-01-27 22:30 | 25.7167 | 25.7167 | 12395.4333 | 0.1518% | 0.1571% |  | 0 | 527 | 482 | 3-2 Induced Draft Fan OB Bearing | Unit was taken off line to replace 3-2 ID Fan OB bearing.
GH3 | D1 | 10 | 1455 | 2014-01-28 11:27 | 2014-01-30 14:13 | 50.7667 | 2.6009 | 1253.6573 | 0.01536% | 0.01589% | 0.01648% | 500 | 527 | 482 | Induced Draft Fans | 3-2 ID Fan IB bearing running 9+ mils vibration. OB fan bearing
GH3 | MO | 11 | 1455 | 2014-01-30 14:13 | 2014-02-01 09:26 | 43.2167 | 43.2167 | 20830.4333 | 0.2552% | 0.264% |  | 0 | 527 | 482 | Induced Draft Fans OB Bearing | Unit 3 has been running with 3-2 ID Fan OB Fan bearing having periodi
GH3 | D1 | 12 | 9650 | 2014-02-02 20:10 | 2014-02-02 20:45 | 0.58333 | 0.14058 | 67.7574 | 0.00083% | 0.0008589% | 0.0008905% | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | 3-2B SO3 injection blower pressure sensing line came off causing
GH3 | D1 | 13 | 9650 | 2014-02-05 14:10 | 2014-02-05 15:00 | 0.83333 | 0.27989 | 134.9051 | 0.001653% | 0.00171% | 0.001773% | 350 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | D1 | 14 | 9650 | 2014-02-05 15:00 | 2014-02-05 19:50 | 4.8333 | 2.9257 | 1410.1777 | 0.01727% | 0.01787% | 0.01853% | 208 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | D1 | 15 | 9650 | 2014-02-15 04:41 | 2014-02-15 07:07 | 2.4333 | 0.5864 | 282.6453 | 0.003462% | 0.003583% | 0.003714% | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | D1 | 16 | 9650 | 2014-02-15 11:22 | 2014-02-15 14:52 | 3.5 | 2.0721 | 998.7552 | 0.01223% | 0.01266% | 0.01313% | 215 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | PD | 17 | 9510 | 2014-02-15 22:00 | 2014-02-16 13:04 | 15.0667 | 9.3488 | 4506.1055 | 0.0552% |  |  | 200 | 527 | 482 | Plant Modific. Strictly For Compliance W/ Reg. Req | KBR electrical tie-in for Bag House and ID fan.
GH3 | D1 | 18 | 1455 | 2014-02-17 10:50 | 2014-02-17 12:00 | 1.1667 | 0.12619 | 60.8216 | 0.0007451% | 0.000771% | 0.0007993% | 470 | 527 | 482 | Induced Draft Fans | ID Fans out the top. Reduced load to swap mills.
GH3 | D1 | 19 | 9650 | 2014-02-17 13:35 | 2014-02-18 10:26 | 20.85 | 1.3847 | 667.4374 | 0.008176% | 0.00846% | 0.008771% | 492 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | H2SO4 out of limit for probe pluggage.
GH3 | D1 | 20 | 1400 | 2014-02-18 10:26 | 2014-02-25 04:00 | 161.5667 | 7.0513 | 3398.725 | 0.04163% | 0.04308% | 0.04467% | 504 | 527 | 482 | Forced Draft Fans | FD fans were topping out.
GH3 | D1 | 21 | 9650 | 2014-02-20 12:30 | 2014-02-20 13:05 | 0.58333 | 0.15164 | 73.0927 | 0.0008954% | 0.0009265% | 0.0009606% | 390 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | D1 | 22 | 250 | 2014-02-20 13:50 | 2014-02-20 16:25 | 2.5833 | 0.62255 | 300.0686 | 0.003676% | 0.003804% | 0.003943% | 400 | 527 | 482 | Pulverizer Feeders | 3-3 Feeder controls.
GH3 | [5 empty] | 510.3667 | 246.0887 | 118614.7733 | 1.453% | 1.446% | 0.6582%
PD
GH4 | MO | 3 | 1000 | 2014-01-01 | 2014-01-01 00:53 | 0.88333 | 0.88333 | 433.7167 | 0.005313% | 0.005498% |  | 0 | 534 | 491 | Furnace Wall Leaks | Unit 4 developed a tube leak on 8 2/3 floor on the south side of the
GH4 | D1 | 2 | 250 | 2014-01-07 03:55 | 2014-01-07 04:36 | 0.68333 | 0.17147 | 84.1933 | 0.001031% | 0.001067% | 0.001106% | 400 | 534 | 491 | Pulverizer Feeders | 4-4 Feeder tripped.
GH4 | D1 | 5 | 9650 | 2014-02-03 00:50 | 2014-02-03 01:48 | 0.96667 | 0.24257 | 119.1027 | 0.001459% | 0.00151% | 0.001565% | 400 | 534 | 491 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH4 | PD | 6 | 3416 | 2014-02-08 23:00 | 2014-02-09 00:20 | 1.3333 | 0.58427 | 286.8764 | 0.003514% |  |  | 300 | 534 | 491 | Other Feedwater Pump Problems | Planned derate to inspect 4-2 BFP leak. Derate was planned with
GH4 | U1 | 7 | 250 | 2014-02-09 03:51 | 2014-02-09 05:38 | 1.7833 | 1.7833 | 875.6167 | 0.01073% | 0.0111% | 0.01151% | 0 | 534 | 491 | Pulverizer Feeders | 4-6 Mill Feeder coal inlet plugged causing controls to see this feeder as
GH4 | PD | 8 | 250 | 2014-02-25 03:58 | 2014-02-25 05:33 | 1.5833 | 0.041511 | 20.3817 | 0.0002497% |  |  | 520 | 534 | 491 | Pulverizer Feeders | Boiler exit gas was high due to both top mills being in service w
GH4 | [5 empty] | 7.2333 | 3.7065 | 1819.8875 | 0.02229% | 0.01917% | 0.01418%
PD
GR3 | D1 | 1 | 250 | 2014-01-07 13:15 | 2014-01-07 14:15 | 1 | 0.26667 | 18.9333 | 0.0002319% | 0.00024% | 0.0002488% | 55 | 75 | 71 | Pulverizer Feeders | 4-4 Feeder plugged with coal and ice.
GR3 | U3 | 2 | 1050 | 2014-01-12 21:48 | 2014-01-14 18:35 | 44.7833 | 44.7833 | 3179.6167 | 0.03895% | 0.0403% | 0.04179% | 0 | 75 | 71 | Second Superheater Leaks | GR3 taken out of service due to Sec SH tube leak. Dispatch was notified at 2200
GR3 | D1 | 3 | 340 | 2014-01-23 18:56 | 2014-01-23 19:09 | 0.21667 | 0.043333 | 3.0767 | 3.769e-05% | 3.9e-05% | 4.043e-05% | 60 | 75 | 71 | Other Pulverizer Problems | 4-4 Pulverizer Pyrite Trap plugged. Pulv O/S to clear trap.
GR3 | D1 | 4 | 9630 | 2014-02-11 08:17 | 2014-02-11 09:18 | 1.0167 | 0.094889 | 6.7371 | 8.253e-05% | 8.54e-05% | 8.854e-05% | 68 | 75 | 71 | Opacity - Fossil Steam Units | Load reduced on GR3 due to high opacity.
GR3 | D1 | 5 | 9630 | 2014-02-11 09:18 | 2014-02-11 09:40 | 0.36667 | 0.024444 | 1.7356 | 2.126e-05% | 2.2e-05% | 2.281e-05% | 70 | 75 | 71 | Opacity - Fossil Steam Units | GR3 derate reduction from event #4. Derate due to igh opacity.
GR3 | D1 | 6 | 9630 | 2014-02-11 09:40 | 2014-02-11 13:13 | 3.55 | 0.80467 | 57.1313 | 0.0006999% | 0.0007242% | 0.0007508% | 58 | 75 | 71 | Opacity - Fossil Steam Units | Continuation of previous event. GR3 derate increased to blow soot and clean boile
GR3 | D1 | 7 | 9630 | 2014-02-11 13:13 | 2014-02-11 17:20 | 4.1167 | 0.38422 | 27.2798 | 0.0003342% | 0.0003458% | 0.0003585% | 68 | 75 | 71 | Opacity - Fossil Steam Units | Continuation of previous event. GR3/B4 soot blowing completed, raised load as muc
GR3 | D1 | 8 | 9630 | 2014-02-12 07:40 | 2014-02-12 08:20 | 0.66667 | 0.08 | 5.68 | 6.958e-05% | 7.2e-05% | 7.465e-05% | 66 | 75 | 71 | Opacity - Fossil Steam Units | GR3 load reduced due to high opacity.
GR3 | D1 | 9 | 9630 | 2014-02-12 08:20 | 2014-02-12 09:30 | 1.1667 | 0.093333 | 6.6267 | 8.118e-05% | 8.4e-05% | 8.709e-05% | 69 | 75 | 71 | Opacity - Fossil Steam Units | GR3 derate decreased from Event #8 due to high opacity.
GR3 | D1 | 10 | 9630 | 2014-02-12 09:30 | 2014-02-12 11:00 | 1.5 | 0.08 | 5.68 | 6.958e-05% | 7.2e-05% | 7.465e-05% | 71 | 75 | 71 | Opacity - Fossil Steam Units | GR3 Derate reduction from Event #9 due to high opacity.
GR3 | PD | 11 | 346 | 2014-02-19 22:00 | 2014-02-19 23:20 | 1.3333 | 0.26667 | 18.9333 | 0.0002319% |  |  | 60 | 75 | 71 | Pulverizer Pyrite Removal System | 4-4 Pulv Pyrite Trap running heavy. Maint found Pyrite Swing Gaate stuck in the op
GR3 | U1 | 13 | 580 | 2014-02-22 23:25 | 2014-02-23 01:09 | 1.7333 | 1.7333 | 123.0667 | 0.001508% | 0.00156% | 0.001617% | 0 | 75 | 71 | Desuperheater/Attemperator Piping | While GR3 was off line on Reserve, Ops discovered a leak in B4 Attemperator supply
GR3 | [5 empty] | 61.45 | 48.6549 | 3454.4971 | 0.04232% | 0.04355% | 0.04515%
GR4 | D1 | 1 | 9630 | 2014-01-02 12:20 | 2014-01-02 15:10 | 2.8333 | 0.24286 | 23.8 | 0.0002916% | 0.0003017% | 0.0003128% | 96 | 105 | 98 | Opacity - Fossil Steam Units | Load reduced on GR4 to blow soot and to stay within 3 hr Particulate limit
GR4 | D1 | 2 | 9630 | 2014-01-04 05:51 | 2014-01-04 06:41 | 0.83333 | 0.039683 | 3.8889 | 4.764e-05% | 4.929e-05% | 5.111e-05% | 100 | 105 | 98 | Opacity - Fossil Steam Units | Load reduced on GR4 due to Opacity issues.
GR4 | D1 | 3 | 9630 | 2014-01-04 07:34 | 2014-01-04 16:06 | 8.5333 | 0.40635 | 39.8222 | 0.0004878% | 0.0005048% | 0.0005233% | 100 | 105 | 98 | Opacity - Fossil Steam Units | Load reduced on GR4 due to Opacity issues.
GR4 | D1 | 4 | 9630 | 2014-01-04 16:06 | 2014-01-04 17:34 | 1.4667 | 0.027937 | 2.7378 | 3.354e-05% | 3.47e-05% | 3.598e-05% | 103 | 105 | 98 | Opacity - Fossil Steam Units | GR4 Derate reduced from 5MW to 2MW due to Opacity issues.
GR4 | D1 | 5 | 9630 | 2014-01-08 05:00 | 2014-01-08 08:04 | 3.0667 | 0.29206 | 28.6222 | 0.0003506% | 0.0003628% | 0.0003761% | 95 | 105 | 98 | Opacity - Fossil Steam Units | GR4 load reduction to avoid opacity exceedances. B5 has a tube leak and we have a
GR4 | D1 | 6 | 310 | 2014-01-08 09:10 | 2014-01-08 13:30 | 4.3333 | 1.3619 | 133.4667 | 0.001635% | 0.001692% | 0.001754% | 72 | 105 | 98 | Pulverizer Mills | A Sluice Water line on the Conveyor Floor had frozen and burst. When it thawed it
GR4 | D1 | 7 | 9630 | 2014-01-08 13:30 | 2014-01-08 17:55 | 4.4167 | 0.12619 | 12.3667 | 0.0001515% | 0.0001568% | 0.0001625% | 102 | 105 | 98 | Opacity - Fossil Steam Units | GR4 load reduction to avoid opacity exceedances. B5 has a tube leak and we have a
GR4 | MO | 8 | 1050 | 2014-01-09 10:36 | 2014-01-10 16:22 | 29.7667 | 29.7667 | 2917.1333 | 0.03573% | 0.03698% | 0.03834% | 0 | 105 | 98 | Second Superheater Leaks | GR4 taken O/S in an orderly manner for repair of a tube leak in the DR Sec SH Sect
GR4 | PD | 9 | 345 | 2014-01-10 19:25 | 2014-01-11 03:57 | 8.5333 | 0.8127 | 79.6444 | 0.0009756% |  |  | 95 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
GR4 | PD | 10 | 345 | 2014-01-11 03:57 | 2014-01-11 05:23 | 1.4333 | 0.16381 | 16.0533 | 0.0001967% |  |  | 93 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
GR4 | PD | 11 | 345 | 2014-01-11 05:23 | 2014-01-11 06:15 | 0.86667 | 0.16508 | 16.1778 | 0.0001982% |  |  | 85 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
GR4 | PD | 12 | 345 | 2014-01-11 06:15 | 2014-01-11 22:02 | 15.7833 | 2.5554 | 250.4289 | 0.003068% |  |  | 88 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
GR4 | PD | 13 | 345 | 2014-01-11 22:02 | 2014-01-14 13:24 | 63.3667 | 12.0698 | 1182.8444 | 0.01449% |  |  | 85 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
GR4 | D1 | 14 | 8551 | 2014-01-11 22:02 | 2014-01-11 23:49 | 1.7833 | 0.50952 | 49.9333 | 0.0006117% | 0.0006329% | 0.0006562% | 75 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing loss of two half cabinets.
GR4 | D1 | 15 | 8551 | 2014-01-12 00:59 | 2014-01-12 12:30 | 11.5167 | 2.7421 | 268.7222 | 0.003292% | 0.003406% | 0.003531% | 80 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets.
GR4 | D1 | 16 | 8551 | 2014-01-12 12:30 | 2014-01-12 14:38 | 2.1333 | 0.60952 | 59.7333 | 0.0007317% | 0.0007572% | 0.000785% | 75 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets. Derate increased
GR4 | D1 | 17 | 8551 | 2014-01-13 12:40 | 2014-01-15 08:51 | 44.1833 | 10.5198 | 1030.9444 | 0.01263% | 0.01307% | 0.01355% | 80 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets.
GR4 | D1 | 18 | 8551 | 2014-01-16 02:31 | 2014-01-16 06:41 | 4.1667 | 0.19841 | 19.4444 | 0.0002382% | 0.0002465% | 0.0002555% | 100 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets.
GR4 | D1 | 19 | 8551 | 2014-01-16 10:36 | 2014-01-16 14:30 | 3.9 | 0.37143 | 36.4 | 0.0004459% | 0.0004614% | 0.0004784% | 95 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets.
GR4 | D1 | 20 | 8551 | 2014-01-17 20:13 | 2014-01-18 00:33 | 4.3333 | 0.4127 | 40.4444 | 0.0004954% | 0.0005127% | 0.0005315% | 95 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded
GR4 | D1 | 21 | 8551 | 2014-01-18 17:09 | 2014-01-18 22:26 | 5.2833 | 0.25159 | 24.6556 | 0.000302% | 0.0003125% | 0.000324% | 100 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result ot two half cabinets grounded
GR4 | D1 | 22 | 8551 | 2014-01-20 09:20 | 2014-01-20 18:30 | 9.1667 | 0.43651 | 42.7778 | 0.000524% | 0.0005422% | 0.0005622% | 100 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded o
GR4 | D1 | 23 | 8551 | 2014-01-20 18:30 | 2014-01-24 12:00 | 89.5 | 2.5571 | 250.6 | 0.00307% | 0.003177% | 0.003293% | 102 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded o
GR4 | D1 | 24 | 8551 | 2014-01-24 12:00 | 2014-02-05 11:55 | 287.9167 | 5.4841 | 537.4444 | 0.006584% | 0.006812% | 0.007063% | 103 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded o
GR4 | D1 | 25 | 263 | 2014-02-01 21:38 | 2014-02-01 22:48 | 1.1667 | 0.27778 | 27.2222 | 0.0003335% | 0.0003451% | 0.0003577% | 80 | 105 | 98 | Primary Air Fan Drives | 5-2 PA Fan Control Jack Minimum Stop failed to disengage. I&E found and repaired
GR4 | D1 | 26 | 338 | 2014-02-04 22:14 | 2014-02-05 11:55 | 13.6833 | 3.2579 | 319.2778 | 0.003911% | 0.004047% | 0.004196% | 80 | 105 | 98 | Pulverizer Control Systems (Temp and Pressure) | 5-3 PA Fan control jack would not react to input from PA Controller.
GR4 | U1 | 27 | 1050 | 2014-02-07 04:42 | 2014-02-08 17:57 | 37.25 | 37.25 | 3650.5 | 0.04472% | 0.04627% | 0.04797% | 0 | 105 | 98 | Second Superheater Leaks | Ops discovered leak in B5 Sec SH Section at 0344, unit was removed from service in
GR4 | D1 | 28 | 9630 | 2014-02-13 14:41 | 2014-02-13 16:28 | 1.7833 | 0.16984 | 16.6444 | 0.0002039% | 0.000211% | 0.0002187% | 95 | 105 | 98 | Opacity - Fossil Steam Units | GR4 derated due to opacity, blowing soot to clean up the boiler.
GR4 | [5 empty] | 663 | 113.0789 | 11081.7311 | 0.1358% | 0.1209% | 0.1253%
D4
MC1 | D1 | 1 | 8280 | 2014-01-07 07:15 | 2014-01-07 08:58 | 1.7167 | 0.36414 | 110.3348 | 0.001352% | 0.001399% | 0.00145% | 260 | 330 | 303 | Wet Scrubber - Reagent Feed Piping | FGD Reactant Feed Line - Leak
MC1 | D1 | 2 | 250 | 2014-01-07 16:50 | 2014-01-07 18:06 | 1.2667 | 0.26869 | 81.4121 | 0.0009973% | 0.001032% | 0.00107% | 260 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen/Wet Coal
MC1 | D1 | 3 | 250 | 2014-01-08 05:45 | 2014-01-08 06:43 | 0.96667 | 0.26364 | 79.8818 | 0.0009786% | 0.001013% | 0.00105% | 240 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen/Wet Coal
MC1 | D4 | 4 | 310 | 2014-01-09 21:26 | 2014-01-10 01:17 | 3.85 | 0.99167 | 300.475 | 0.003681% | 0.003809% |  | 245 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Roller Adjustment
MC1 | D4 | 5 | 310 | 2014-01-13 22:00 | 2014-01-14 07:17 | 9.2833 | 2.5318 | 767.1409 | 0.009398% | 0.009724% |  | 240 | 330 | 303 | Pulverizer Mills | 1D Coal Mill & Feeder - Inspection
MC1 | D4 | 6 | 310 | 2014-01-14 22:34 | 2014-01-15 04:42 | 6.1333 | 1.6727 | 506.8364 | 0.006209% | 0.006424% |  | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Inspection
MC1 | D4 | 7 | 250 | 2014-01-15 23:00 | 2014-01-16 06:17 | 7.2833 | 1.9864 | 601.8682 | 0.007373% | 0.007629% |  | 240 | 330 | 303 | Pulverizer Feeders | 1B Coal Feeder - Calibration & Mill Inspection
MC1 | D4 | 8 | 250 | 2014-01-16 23:00 | 2014-01-17 04:14 | 5.2333 | 1.4273 | 432.4636 | 0.005298% | 0.005482% |  | 240 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Calibration & Mill Inspection
MC1 | D1 | 9 | 4261 | 2014-01-17 21:42 | 2014-01-18 08:33 | 10.85 | 0.98636 | 298.8682 | 0.003661% | 0.003788% | 0.003928% | 300 | 330 | 303 | Turbine Control Valves | Turbine #2 Control Valve - Would Not Open during Valve Test
MC1 | U1 | 10 | 800 | 2014-01-18 08:33 | 2014-01-18 11:21 | 2.8 | 2.8 | 848.4 | 0.01039% | 0.01075% | 0.01115% | 0 | 330 | 303 | Boiler Drums And Drum Internals | High Drum Level Trip due to Turbine #2 Control Valve Issue, Replaced Fast Acting S
MC1 | NC | 11 | 1850 | 2014-01-18 11:21 | 2014-01-18 15:45 | 4.4 | [5 empty] | 0 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Very Hot Start Up
MC1 | D1 | 12 | 1850 | 2014-01-18 15:45 | 2014-01-18 16:36 | 0.85 | 0.11591 | 35.1205 | 0.0004302% | 0.0004452% | 0.0004615% | 285 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | D1 | 13 | 1850 | 2014-01-18 16:36 | 2014-01-18 18:40 | 2.0667 | 0.18788 | 56.9273 | 0.0006974% | 0.0007216% | 0.0007481% | 300 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | D4 | 14 | 250 | 2014-01-20 22:08 | 2014-01-21 04:20 | 6.2 | 1.6909 | 512.3455 | 0.006276% | 0.006494% |  | 240 | 330 | 303 | Pulverizer Feeders | 1A Coal Feeder - Calibration & Mill Inspection
MC1 | D1 | 15 | 250 | 2014-01-24 02:53 | 2014-01-24 03:08 | 0.25 | 0.079545 | 24.1023 | 0.0002953% | 0.0003055% | 0.0003167% | 225 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen Coal
MC1 | D1 | 16 | 250 | 2014-01-24 03:08 | 2014-01-24 03:45 | 0.61667 | 0.14949 | 45.297 | 0.0005549% | 0.0005742% | 0.0005953% | 250 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen Coal
MC1 | D1 | 17 | 250 | 2014-01-24 07:43 | 2014-01-24 09:04 | 1.35 | 0.36818 | 111.5591 | 0.001367% | 0.001414% | 0.001466% | 240 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen Coal
MC1 | D1 | 18 | 4261 | 2014-02-01 21:20 | 2014-02-02 08:50 | 11.5 | 7.3182 | 2217.4091 | 0.02716% | 0.02811% | 0.02914% | 120 | 330 | 303 | Turbine Control Valves | Turbine #2 Control Valve - Stuck Closed
MC1 | NC | 19 | 1160 | 2014-02-04 23:00 | 2014-02-05 04:15 | 5.25 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater. Full load available if needed.
MC1 | D1 | 20 | 250 | 2014-02-05 07:28 | 2014-02-05 09:30 | 2.0333 | 0.40051 | 121.353 | 0.001487% | 0.001538% | 0.001595% | 265 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Wet Coal
MC1 | D4 | 21 | 250 | 2014-02-06 | 2014-02-06 03:12 | 3.2 | 0.87273 | 264.4364 | 0.003239% | 0.003352% |  | 240 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Repair Discharge Flapper
MC1 | D1 | 22 | 1160 | 2014-02-08 07:15 | 2014-02-08 08:27 | 1.2 | 0.10909 | 33.0545 | 0.0004049% | 0.000419% | 0.0004344% | 300 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC1 | D1 | 23 | 1160 | 2014-02-08 08:27 | 2014-02-08 15:05 | 6.6333 | 1.6081 | 487.2485 | 0.005969% | 0.006176% | 0.006403% | 250 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC1 | NC | 24 | 1160 | 2014-02-08 22:00 | 2014-02-09 04:00 | 6 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC1 | D1 | 25 | 1488 | 2014-02-10 23:05 | 2014-02-11 06:25 | 7.3333 | 0.15556 | 47.1333 | 0.0005774% | 0.0005974% | 0.0006194% | 323 | 330 | 303 | Air Heater (Regenerative) | Air Heater - High Differential
MC1 | D1 | 26 | 1488 | 2014-02-11 06:25 | 2014-02-11 10:00 | 3.5833 | 0.10859 | 32.9015 | 0.000403% | 0.000417% | 0.0004324% | 320 | 330 | 303 | Air Heater (Regenerative) | Air Heater - High Differential
MC1 | D1 | 27 | 1488 | 2014-02-11 10:00 | 2014-02-12 10:30 | 24.5 | 0.44545 | 134.9727 | 0.001653% | 0.001711% | 0.001774% | 324 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | NC | 28 | 8460 | 2014-02-11 12:45 | 2014-02-11 16:00 | 3.25 | [5 empty] | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
MC1 | NC | 29 | 8460 | 2014-02-12 07:00 | 2014-02-12 22:45 | 15.75 | [5 empty] | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
MC1 | D1 | 30 | 1488 | 2014-02-12 10:30 | 2014-02-12 22:45 | 12.25 | 0.37121 | 112.4773 | 0.001378% | 0.001426% | 0.001478% | 320 | 330 | 303 | Air Heater (Regenerative) | 1A Air heater - High Differential
MC1 | D1 | 31 | 1488 | 2014-02-12 22:45 | 2014-02-13 07:26 | 8.6833 | 0.52626 | 159.4576 | 0.001953% | 0.002021% | 0.002096% | 310 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | D1 | 32 | 1488 | 2014-02-13 07:26 | 2014-02-13 22:00 | 14.5667 | 0.26485 | 80.2491 | 0.0009831% | 0.001017% | 0.001055% | 324 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | NC | 33 | 8460 | 2014-02-13 13:40 | 2014-02-13 22:00 | 8.3333 | [5 empty] | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
MC1 | D4 | 34 | 310 | 2014-02-13 22:00 | 2014-02-14 03:00 | 5 | 1.3636 | 413.1818 | 0.005061% | 0.005237% |  | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Inspection
MC1 | D1 | 35 | 250 | 2014-02-14 03:00 | 2014-02-14 05:05 | 2.0833 | 0.56818 | 172.1591 | 0.002109% | 0.002182% | 0.002262% | 240 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor Gearbox
MC1 | D1 | 36 | 250 | 2014-02-14 05:05 | 2014-02-14 06:50 | 1.75 | 0.42424 | 128.5455 | 0.001575% | 0.001629% | 0.001689% | 250 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor Gearbox
MC1 | D1 | 37 | 250 | 2014-02-14 06:50 | 2014-02-14 12:00 | 5.1667 | 0.78283 | 237.197 | 0.002906% | 0.003007% | 0.003117% | 280 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor GearboxGas Guns in Service
MC1 | D1 | 38 | 1488 | 2014-02-15 06:54 | 2014-02-16 06:20 | 23.4333 | 0.35505 | 107.5803 | 0.001318% | 0.001364% | 0.001414% | 325 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | D1 | 39 | 1488 | 2014-02-16 06:20 | 2014-02-17 09:00 | 26.6667 | 0.80808 | 244.8485 | 0.002999% | 0.003104% | 0.003218% | 320 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | D1 | 40 | 1488 | 2014-02-17 09:00 | 2014-02-18 22:26 | 37.4333 | 2.2687 | 687.4121 | 0.008421% | 0.008713% | 0.009034% | 310 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | MO | 41 | 1488 | 2014-02-18 22:26 | 2014-02-21 22:16 | 71.8333 | 71.8333 | 21765.5 | 0.2666% | 0.2759% |  | 0 | 330 | 303 | Air Heater Dirty | Air Heater Wash
MC1 | SF | 42 | 4261 | 2014-02-21 22:16 | 2014-02-22 17:58 | 19.7 | 19.7 | 5969.1 | 0.07312% | 0.07566% | 0.07844% | 0 | 330 | 303 | Turbine Control Valves | Turbine #2 & #3 Control Valves - Cleaned Servovalves
MC1 | NC | 43 | 1850 | 2014-02-22 17:58 | 2014-02-23 03:16 | 9.3 | 9.3 | 2817.9 |  |  |  | 0 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Warm Start Up
MC1 | D1 | 44 | 1850 | 2014-02-23 03:16 | 2014-02-23 04:11 | 0.91667 | 0.15278 | 46.2917 | 0.0005671% | 0.0005868% | 0.0006084% | 275 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | D1 | 45 | 1850 | 2014-02-23 04:11 | 2014-02-23 04:39 | 0.46667 | 0.063636 | 19.2818 | 0.0002362% | 0.0002444% | 0.0002534% | 285 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | D1 | 46 | 1850 | 2014-02-23 04:39 | 2014-02-23 05:36 | 0.95 | 0.10076 | 30.5295 | 0.000374% | 0.000387% | 0.0004012% | 295 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | NC | 47 | 4490 | 2014-02-27 07:00 | 2014-02-27 13:18 | 6.3 | [5 empty] | 0 | 330 | 303 | Turbine Performance Testing | Capability Test - Full Load
MC1 | D4 | 48 | 310 | 2014-02-27 22:00 | 2014-02-28 02:02 | 4.0333 | 1.1 | 333.3 | 0.004083% | 0.004225% |  | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Inspection & Adjust Rollers
MC1 | [5 empty] | 414.2167 | 136.8863 | 41476.5529 | 0.4736% | 0.49% | 0.1677%
D4
MC2 | D1 | 1 | 250 | 2014-01-01 | 2014-01-01 10:30 | 10.5 | 2.5455 | 761.0909 | 0.009323% | 0.009647% | 0.01% | 250 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Replace Belt
MC2 | D1 | 2 | 1850 | 2014-01-01 10:30 | 2014-01-01 15:30 | 5 | 0.30303 | 90.6061 | 0.00111% | 0.001148% | 0.001191% | 310 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 3 | 250 | 2014-01-02 04:15 | 2014-01-02 05:24 | 1.15 | 0.27879 | 83.3576 | 0.001021% | 0.001057% | 0.001095% | 250 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Belt Slipping
MC2 | MO | 4 | 1000 | 2014-01-02 10:39 | 2014-01-04 11:51 | 49.2 | 49.2 | 14710.8 | 0.1802% | 0.1865% |  | 0 | 330 | 299 | Furnace Wall Tube Leaks | Boiler Tube Leak - Waterwall
MC2 | NC | 5 | 1850 | 2014-01-04 11:51 | 2014-01-04 21:11 | 9.3333 | [5 empty] | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Warm Start Up
MC2 | D1 | 6 | 1850 | 2014-01-04 21:11 | 2014-01-05 05:35 | 8.4 | 3.1818 | 951.3636 | 0.01165% | 0.01206% | 0.0125% | 205 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 7 | 1850 | 2014-01-05 05:35 | 2014-01-06 01:00 | 19.4167 | 4.1187 | 1231.4874 | 0.01509% | 0.01561% | 0.01618% | 260 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 8 | 1850 | 2014-01-06 01:00 | 2014-01-06 09:28 | 8.4667 | 1.2828 | 383.5657 | 0.004699% | 0.004862% | 0.005041% | 280 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 9 | 1850 | 2014-01-06 09:28 | 2014-01-06 19:00 | 9.5333 | 0.28889 | 86.3778 | 0.001058% | 0.001095% | 0.001135% | 320 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 10 | 1850 | 2014-01-06 19:00 | 2014-01-06 22:36 | 3.6 | 0.32727 | 97.8545 | 0.001199% | 0.00124% | 0.001286% | 300 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 11 | 250 | 2014-01-07 05:45 | 2014-01-07 07:15 | 1.5 | 0.40909 | 122.3182 | 0.001498% | 0.00155% | 0.001607% | 240 | 330 | 299 | Pulverizer Feeders | 2A Coal Feeder - Plugged, Frozen/Wet Coal
MC2 | D1 | 12 | 1850 | 2014-01-07 12:15 | 2014-01-08 09:50 | 21.5833 | 3.2702 | 977.7904 | 0.01198% | 0.01239% | 0.01285% | 280 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 13 | 1850 | 2014-01-08 09:50 | 2014-01-08 12:15 | 2.4167 | 0.25631 | 76.6376 | 0.0009388% | 0.0009714% | 0.001007% | 295 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 14 | 1850 | 2014-01-08 12:15 | 2014-01-09 09:35 | 21.3333 | 0.9697 | 289.9394 | 0.003552% | 0.003675% | 0.00381% | 315 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D4 | 15 | 250 | 2014-01-09 21:02 | 2014-01-10 04:09 | 7.1167 | 2.2644 | 677.0538 | 0.008294% | 0.008582% |  | 225 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Calibration
MC2 | D4 | 16 | 250 | 2014-01-13 00:35 | 2014-01-13 05:00 | 4.4167 | 1.1376 | 340.1503 | 0.004167% | 0.004312% |  | 245 | 330 | 299 | Pulverizer Feeders | 2D Coal Feeder - Calibration
MC2 | NC | 17 | 1160 | 2014-01-16 23:00 | 2014-01-17 04:00 | 5 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 18 | 1160 | 2014-01-17 22:15 | 2014-01-18 05:00 | 6.75 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 19 | 1160 | 2014-01-18 21:05 | 2014-01-19 05:00 | 7.9167 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | D4 | 20 | 310 | 2014-01-19 23:30 | 2014-01-20 04:26 | 4.9333 | 1.2707 | 379.9414 | 0.004654% | 0.004816% |  | 245 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Inspection
MC2 | D1 | 21 | 250 | 2014-01-23 22:08 | 2014-01-23 23:28 | 1.3333 | 0.36364 | 108.7273 | 0.001332% | 0.001378% | 0.001429% | 240 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Plugged, Frozen Coal
MC2 | D1 | 22 | 250 | 2014-01-24 05:33 | 2014-01-24 07:30 | 1.95 | 0.53182 | 159.0136 | 0.001948% | 0.002016% | 0.00209% | 240 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Plugged, Frozen Coal
MC2 | NC | 23 | 1160 | 2014-01-24 23:00 | 2014-01-25 06:50 | 7.8333 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | U1 | 24 | 4267 | 2014-01-25 22:11 | 2014-01-26 12:32 | 14.35 | 14.35 | 4290.65 | 0.05256% | 0.05439% | 0.05639% | 0 | 330 | 299 | Turbine Control Valve Testing Trip | Turbine Control Valve Test - Trip
MC2 | D1 | 27 | 1850 | 2014-01-26 06:15 | 2014-01-27 08:08 | 25.8833 | 13.3338 | 3986.8177 | 0.04884% | 0.05054% | 0.05239% | 160 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 25 | 310 | 2014-01-26 12:32 | 2014-01-26 18:32 | 6 | 1.6364 | 489.2727 | 0.005994% | 0.006202% | 0.00643% | 240 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Explosion, Ductwork Repair
MC2 | D1 | 26 | 1850 | 2014-01-26 18:32 | 2014-01-27 06:15 | 11.7167 | 5.8583 | 1751.6417 | 0.02146% | 0.0222% | 0.02302% | 165 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 28 | 1850 | 2014-01-27 08:08 | 2014-01-27 09:55 | 1.7833 | 0.75657 | 226.2131 | 0.002771% | 0.002867% | 0.002973% | 190 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 29 | 310 | 2014-01-27 09:55 | 2014-01-27 13:56 | 4.0167 | 1.0346 | 309.3442 | 0.003789% | 0.003921% | 0.004065% | 245 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Ductwork Repair
MC2 | D1 | 30 | 310 | 2014-01-27 13:56 | 2014-01-27 15:52 | 1.9333 | 0.35152 | 105.103 | 0.001288% | 0.001332% | 0.001381% | 270 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Ductwork Repair
MC2 | D1 | 31 | 310 | 2014-01-27 15:52 | 2014-01-27 16:39 | 0.78333 | 0.21364 | 63.8773 | 0.0007825% | 0.0008097% | 0.0008395% | 240 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Ductwork Repair
MC2 | D1 | 32 | 310 | 2014-01-27 16:39 | 2014-01-27 20:39 | 4 | 0.72727 | 217.4545 | 0.002664% | 0.002756% | 0.002858% | 270 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Ductwork Repair
MC2 | NC | 33 | 1160 | 2014-01-29 21:00 | 2014-01-30 01:55 | 4.9167 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater. Full load available if needed.
MC2 | NC | 34 | 1160 | 2014-01-30 22:15 | 2014-01-31 04:00 | 5.75 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | U1 | 35 | 3149 | 2014-02-01 23:37 | 2014-02-02 06:35 | 6.9667 | 6.9667 | 2083.0333 | 0.02552% | 0.0264% | 0.02737% | 0 | 330 | 299 | Condenser Loss of Vacuum | Condenser Vacuum Trip
MC2 | NC | 36 | 1850 | 2014-02-02 06:35 | 2014-02-02 14:15 | 7.6667 | [5 empty] | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Hot Start Up
MC2 | D1 | 37 | 1850 | 2014-02-02 14:15 | 2014-02-02 22:00 | 7.75 | 1.6439 | 491.5379 | 0.006021% | 0.006231% | 0.00646% | 260 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D4 | 38 | 310 | 2014-02-02 22:00 | 2014-02-03 06:25 | 8.4167 | 2.2955 | 686.3409 | 0.008408% | 0.0087% |  | 240 | 330 | 299 | Pulverizer Mills | 2A Coal Mill - Inspection
MC2 | D1 | 39 | 1700 | 2014-02-03 08:15 | 2014-02-03 10:23 | 2.1333 | 0.32323 | 96.6465 | 0.001184% | 0.001225% | 0.00127% | 280 | 330 | 299 | Feedwater Controls | Feedwater Flow Issue
MC2 | D1 | 40 | 1850 | 2014-02-03 10:23 | 2014-02-03 21:05 | 10.7 | 0.32424 | 96.9485 | 0.001188% | 0.001229% | 0.001274% | 320 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D4 | 41 | 310 | 2014-02-03 23:00 | 2014-02-04 04:15 | 5.25 | 1.4318 | 428.1136 | 0.005244% | 0.005427% |  | 240 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Adjust Rollers & Inspection
MC2 | D4 | 42 | 310 | 2014-02-04 23:00 | 2014-02-05 04:45 | 5.75 | 1.5682 | 468.8864 | 0.005744% | 0.005943% |  | 240 | 330 | 299 | Pulverizer Mills | 2B Coal Mill - Inspection
MC2 | D1 | 43 | 250 | 2014-02-05 03:53 | 2014-02-05 04:29 | 0.6 | 0.25455 | 76.1091 | 0.0009323% | 0.0009647% | 0.001% | 190 | 330 | 299 | Pulverizer Feeders | 2A Coal Feeder - Wet Coal
MC2 | D1 | 44 | 250 | 2014-02-05 05:48 | 2014-02-05 07:56 | 2.1333 | 0.51717 | 154.6343 | 0.001894% | 0.00196% | 0.002032% | 250 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Wet Coal
MC2 | D1 | 45 | 1850 | 2014-02-05 07:56 | 2014-02-05 09:43 | 1.7833 | 0.1351 | 40.3952 | 0.0004948% | 0.000512% | 0.0005309% | 305 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 46 | 1850 | 2014-02-05 09:43 | 2014-02-05 13:25 | 3.7 | 0.17939 | 53.6388 | 0.0006571% | 0.0006799% | 0.0007049% | 314 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | NC | 47 | 1160 | 2014-02-07 23:00 | 2014-02-08 05:30 | 6.5 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | D1 | 48 | 1160 | 2014-02-08 05:30 | 2014-02-08 07:35 | 2.0833 | 1.1995 | 358.649 | 0.004393% | 0.004546% | 0.004713% | 140 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | D1 | 49 | 1160 | 2014-02-08 07:35 | 2014-02-08 09:28 | 1.8833 | 0.51364 | 153.5773 | 0.001881% | 0.001947% | 0.002018% | 240 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC2 | NC | 50 | 1160 | 2014-02-08 22:00 | 2014-02-09 04:00 | 6 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 51 | 1160 | 2014-02-09 21:12 | 2014-02-10 03:17 | 6.0833 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 52 | 8460 | 2014-02-11 08:00 | 2014-02-11 12:20 | 4.3333 | [5 empty] | 0 | 330 | 299 | Wet Scrubber Testing | Particulate Matter Testing - Full Load
MC2 | NC | 53 | 1160 | 2014-02-11 12:21 | 2014-02-11 16:30 | 4.15 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 54 | 1160 | 2014-02-12 22:00 | 2014-02-13 04:50 | 6.8333 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 55 | 8460 | 2014-02-13 08:00 | 2014-02-13 13:11 | 5.1833 | [5 empty] | 0 | 330 | 299 | Wet Scrubber Testing | Particulate Matter Testing - Full Load
MC2 | D1 | 56 | 1160 | 2014-02-14 11:25 | 2014-02-15 00:32 | 13.1167 | 2.1861 | 653.6472 | 0.008007% | 0.008285% | 0.00859% | 275 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC2 | MO | 57 | 1050 | 2014-02-15 00:32 | 2014-02-17 22:00 | 69.4667 | 69.4667 | 20770.5333 | 0.2544% | 0.2633% |  | 0 | 330 | 299 | Second Superheater Leaks | Boiler Tube Leak - Second Superheater
MC2 | SF | 58 | 380 | 2014-02-17 22:00 | 2014-02-18 13:40 | 15.6667 | 15.6667 | 4684.3333 | 0.05738% | 0.05938% | 0.06156% | 0 | 330 | 299 | Light-off (Igniter) Systems | Gas Igniter Issues
MC2 | NC | 59 | 1850 | 2014-02-18 13:40 | 2014-02-18 22:15 | 8.5833 | [5 empty] | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Warm Start Up
MC2 | D1 | 60 | 1850 | 2014-02-18 22:15 | 2014-02-19 02:00 | 3.75 | 1.0227 | 305.7955 | 0.003746% | 0.003876% | 0.004019% | 240 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 61 | 1850 | 2014-02-19 02:00 | 2014-02-19 04:15 | 2.25 | 0.40909 | 122.3182 | 0.001498% | 0.00155% | 0.001607% | 270 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 62 | 1850 | 2014-02-19 04:15 | 2014-02-19 07:00 | 2.75 | 0.375 | 112.125 | 0.001374% | 0.001421% | 0.001474% | 285 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 63 | 1850 | 2014-02-19 07:00 | 2014-02-19 08:50 | 1.8333 | 0.13333 | 39.8667 | 0.0004884% | 0.0005053% | 0.0005239% | 306 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 64 | 1850 | 2014-02-19 08:50 | 2014-02-19 21:41 | 12.85 | 0.38939 | 116.4288 | 0.001426% | 0.001476% | 0.00153% | 320 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 65 | 1850 | 2014-02-20 02:40 | 2014-02-20 08:09 | 5.4833 | 0.14955 | 44.7141 | 0.0005477% | 0.0005668% | 0.0005876% | 321 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 66 | 250 | 2014-02-24 00:16 | 2014-02-24 03:46 | 3.5 | 0.15909 | 47.5682 | 0.0005827% | 0.000603% | 0.0006251% | 315 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Plugged, Foreign Material
MC2 | MO | 67 | 1000 | 2014-02-24 09:31 | 2014-02-25 19:47 | 34.2667 | 34.2667 | 10245.7333 | 0.1255% | 0.1299% |  | 0 | 330 | 299 | Furnace Wall Leaks | Boiler Tube Leak - Waterwall
MC2 | NC | 68 | 1850 | 2014-02-25 19:47 | 2014-02-26 05:39 | 9.8667 | [5 empty] | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Hot Start Up
MC2 | D1 | 69 | 1850 | 2014-02-26 05:39 | 2014-02-26 11:21 | 5.7 | 0.15545 | 46.4809 | 0.0005694% | 0.0005892% | 0.0006108% | 321 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 70 | 1850 | 2014-02-26 11:21 | 2014-02-26 15:29 | 4.1333 | 0.46343 | 138.5669 | 0.001697% | 0.001756% | 0.001821% | 293 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 71 | 1850 | 2014-02-26 15:29 | 2014-02-26 16:46 | 1.2833 | 0.035 | 10.465 | 0.0001282% | 0.0001327% | 0.0001375% | 321 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | [5 empty] | 600.2167 | 252.4934 | 75495.5369 | 0.9248% | 0.957% | 0.352%
D4
MC3 | D4 | 1 | 310 | 2014-01-01 23:20 | 2014-01-02 01:35 | 2.25 | 0.54787 | 215.8617 | 0.002644% | 0.002736% |  | 320 | 423 | 394 | Pulverizer Mills | 3A Coal Mill - Inspection
MC3 | D1 | 2 | 360 | 2014-01-05 23:16 | 2014-01-06 02:00 | 2.7333 | 0.60095 | 236.7726 | 0.0029% | 0.003001% | 0.003112% | 330 | 423 | 394 | Burners | 3A Mill - Burners High Temperature
MC3 | NC | 6 | 1990 | 2014-01-14 08:00 | 2014-01-14 16:40 | 8.6667 | [5 empty] | 0 | 423 | 394 | Boiler Performance Testing | Full Load Winter Capability Test
MC3 | NC | 3 | 8460 | 2014-01-15 | 2014-01-15 03:06 | 3.1 | [5 empty] | 0 | 423 | 394 | Wet Scrubber Testing | Mid Flow RATA Test
MC3 | D4 | 4 | 360 | 2014-01-15 03:06 | 2014-01-15 08:13 | 5.1167 | 1.3669 | 538.5443 | 0.006597% | 0.006826% |  | 310 | 423 | 394 | Burners | 3C Mill - Coal Burner Logic Change
MC3 | D4 | 5 | 360 | 2014-01-15 08:13 | 2014-01-15 09:42 | 1.4833 | 0.17884 | 70.4636 | 0.0008632% | 0.0008932% |  | 372 | 423 | 394 | Burners | 3C Mill - Coal Burner Logic Testing
MC3 | NC | 7 | 8460 | 2014-01-15 09:42 | 2014-01-15 12:09 | 2.45 | [5 empty] | 0 | 423 | 394 | Wet Scrubber Testing | Full Load RATA Test
MC3 | D1 | 8 | 360 | 2014-01-15 12:09 | 2014-01-15 13:13 | 1.0667 | 0.17147 | 67.5606 | 0.0008276% | 0.0008564% | 0.0008879% | 355 | 423 | 394 | Burners | 3D Mill - 3D7 Coal Burner High Temperature
MC3 | NC | 9 | 8460 | 2014-01-15 13:14 | 2014-01-15 16:42 | 3.4667 | [5 empty] | 0 | 423 | 394 | Wet Scrubber Testing | Full Load RATA Test
MC3 | D4 | 10 | 310 | 2014-01-17 04:00 | 2014-01-17 05:15 | 1.25 | 0.27482 | 108.2801 | 0.001326% | 0.001373% |  | 330 | 423 | 394 | Pulverizer Mills | 3B Mill - Coal Burner Logic Change
MC3 | D1 | 11 | 360 | 2014-01-20 08:37 | 2014-01-20 09:20 | 0.71667 | 0.14909 | 58.7429 | 0.0007196% | 0.0007446% | 0.000772% | 335 | 423 | 394 | Burners | 3C Mill - 3C3 Coal Burner High Temperature
MC3 | D4 | 12 | 360 | 2014-01-20 21:00 | 2014-01-21 00:55 | 3.9167 | 0.90741 | 357.5185 | 0.00438% | 0.004532% |  | 325 | 423 | 394 | Burners | 3A & 3D Mills - Coal Burner Logic Change Over
MC3 | D1 | 13 | 300 | 2014-01-23 17:19 | 2014-01-23 23:03 | 5.7333 | 1.1928 | 469.9436 | 0.005757% | 0.005957% | 0.006176% | 335 | 423 | 394 | Pulverizer Motors and Drives | 3C Coal Mill Motor - Failed to Start, Breaker Issue
MC3 | D1 | 14 | 360 | 2014-01-23 22:08 | 2014-01-23 23:03 | 0.91667 | 0.42908 | 169.0567 | 0.002071% | 0.002143% | 0.002222% | 225 | 423 | 394 | Burners | 3D Mill - 3D7 Coal Burner High Temperature
MC3 | D1 | 15 | 300 | 2014-01-23 23:03 | 2014-01-23 23:23 | 0.33333 | 0.073286 | 28.8747 | 0.0003537% | 0.000366% | 0.0003795% | 330 | 423 | 394 | Pulverizer Motors and Drives | 3C Coal Mill Motor - Failed to Start, Breaker Issue
MC3 | D1 | 16 | 360 | 2014-01-24 23:56 | 2014-01-25 01:35 | 1.65 | 0.24574 | 96.8234 | 0.001186% | 0.001227% | 0.001272% | 360 | 423 | 394 | Burners | 3D Mill - 3D10 Coal Burner High Temperature
MC3 | D1 | 17 | 360 | 2014-01-28 09:43 | 2014-01-28 10:42 | 0.98333 | 0.14645 | 57.7028 | 0.0007069% | 0.0007314% | 0.0007583% | 360 | 423 | 394 | Burners | 3C Mill - 3C2 Coal Burner High Temperature
MC3 | D1 | 18 | 360 | 2014-01-28 16:30 | 2014-01-28 17:05 | 0.58333 | 0.086879 | 34.2305 | 0.0004193% | 0.0004339% | 0.0004498% | 360 | 423 | 394 | Burners | 3B Mill - 3B6 Coal Burner High Temperature
MC3 | D1 | 19 | 360 | 2014-01-31 08:09 | 2014-01-31 09:12 | 1.05 | 0.20603 | 81.1752 | 0.0009944% | 0.001029% | 0.001067% | 340 | 423 | 394 | Burners | 3C Mill - 3C2 Coal Burner High Temperature
MC3 | D1 | 20 | 250 | 2014-02-07 18:02 | 2014-02-08 05:30 | 11.4667 | 2.6566 | 1046.6925 | 0.01282% | 0.01327% | 0.01376% | 325 | 423 | 394 | Pulverizer Feeders | 3C Coal Feeder - Replace Speed Sensor
MC3 | D1 | 21 | 360 | 2014-02-09 09:05 | 2014-02-09 10:25 | 1.3333 | 0.29314 | 115.4988 | 0.001415% | 0.001464% | 0.001518% | 330 | 423 | 394 | Burners | 3C Mill - 3C3 Coal Burner High Temperature
MC3 | D1 | 22 | 360 | 2014-02-09 10:50 | 2014-02-09 16:36 | 5.7667 | 1.2678 | 499.5324 | 0.006119% | 0.006332% | 0.006565% | 330 | 423 | 394 | Burners | 3C Mill - 3C10 Coal Burner High Temperature
MC3 | D1 | 23 | 310 | 2014-02-09 21:52 | 2014-02-10 07:58 | 10.1 | 2.4593 | 968.9792 | 0.01187% | 0.01228% | 0.01273% | 320 | 423 | 394 | Pulverizer Mills | 3C Primary Air Fan Housing InspectionRepair Suction Box & Hot Air Damper Linkage
MC3 | D4 | 24 | 250 | 2014-02-10 11:00 | 2014-02-10 16:05 | 5.0833 | 1.1176 | 440.3392 | 0.005394% | 0.005582% |  | 330 | 423 | 394 | Pulverizer Feeders | 3C Coal Feeder - Calibration
MC3 | D1 | 25 | 360 | 2014-02-10 19:42 | 2014-02-10 19:57 | 0.25 | 0.060875 | 23.9846 | 0.0002938% | 0.000304% | 0.0003152% | 320 | 423 | 394 | Burners | 3D Mill - 3D4 Coal Burner High Temperature
MC3 | D1 | 26 | 360 | 2014-02-15 11:11 | 2014-02-15 12:43 | 1.5333 | 0.22837 | 89.9773 | 0.001102% | 0.001141% | 0.001182% | 360 | 423 | 394 | Burners | 3C Mill - 3C1 & 3C3 Coal Burners High Temperature
MC3 | D1 | 27 | 360 | 2014-02-15 13:28 | 2014-02-15 14:20 | 0.86667 | 0.12908 | 50.8567 | 0.000623% | 0.0006446% | 0.0006683% | 360 | 423 | 394 | Burners | 3A Mill - 3A4 Coal Burner High Temperature
MC3 | D4 | 28 | 8160 | 2014-02-17 20:00 | 2014-02-18 00:46 | 4.7667 | 1.048 | 412.9083 | 0.005058% | 0.005234% |  | 330 | 423 | 394 | Wet Scrubber Mist Eliminators/demisters & Washdown | FGD Demister Wash Line - Relocation
MC3 | D1 | 29 | 360 | 2014-02-21 14:09 | 2014-02-21 15:29 | 1.3333 | 0.29314 | 115.4988 | 0.001415% | 0.001464% | 0.001518% | 330 | 423 | 394 | Burners | 3D Mill - 3D1 Coal Burner High Temperature
MC3 | D1 | 30 | 360 | 2014-02-21 18:21 | 2014-02-21 19:10 | 0.81667 | 0.16024 | 63.1362 | 0.0007734% | 0.0008003% | 0.0008297% | 340 | 423 | 394 | Burners | 3A Mill - 3A4 Coal Burner High Temperature
MC3 | D1 | 31 | 360 | 2014-02-22 09:20 | 2014-02-22 11:18 | 1.9667 | 0.43239 | 170.3608 | 0.002087% | 0.002159% | 0.002239% | 330 | 423 | 394 | Burners | 3C Mill - 3C3 Coal Burner High Temperature
MC3 | D1 | 32 | 360 | 2014-02-22 14:45 | 2014-02-22 16:15 | 1.5 | 0.71986 | 283.6241 | 0.003474% | 0.003595% | 0.003727% | 220 | 423 | 394 | Burners | 3D Mill - 3D1 Coal Burner High Temperature3B Mill - 3B7 Coal Burner Fire
MC3 | D1 | 33 | 360 | 2014-02-22 16:15 | 2014-02-22 17:00 | 0.75 | 0.16489 | 64.9681 | 0.0007959% | 0.0008235% | 0.0008538% | 330 | 423 | 394 | Burners | 3D Mill - 3D1 Coal Burner High Temperature
MC3 | D1 | 34 | 360 | 2014-02-22 19:25 | 2014-02-22 20:28 | 1.05 | 0.23085 | 90.9553 | 0.001114% | 0.001153% | 0.001195% | 330 | 423 | 394 | Burners | 3D Mill - 3D2 Coal Burner High Temperature
MC3 | D4 | 35 | 310 | 2014-02-24 23:00 | 2014-02-25 06:39 | 7.65 | 1.8628 | 733.9298 | 0.008991% | 0.009303% |  | 320 | 423 | 394 | Pulverizer Mills | 3C Coal Mill Pyrite Hopper - Replace Top Gate
MC3 | D4 | 36 | 876 | 2014-02-25 20:00 | 2014-02-26 04:28 | 8.4667 | 4.1633 | 1640.3316 | 0.02009% | 0.02079% |  | 215 | 423 | 394 | Soot Blower Controls | Sootblower Regulator - Rebuilt
MC3 | [5 empty] | 112.1667 | 23.8658 | 9403.1251 | 0.1152% | 0.1192% | 0.0642%
D4
MC4 | D1 | 1 | 360 | 2014-01-01 | 2014-01-01 03:30 | 3.5 | 0.7 | 340.2 | 0.004167% | 0.004312% | 0.004471% | 420 | 525 | 486 | Burners | 4C Mill - 4C7 & 4C9 Burners High Temperature
MC4 | D1 | 2 | 4261 | 2014-01-02 11:34 | 2014-01-02 12:11 | 0.61667 | 0.029365 | 14.2714 | 0.0001748% | 0.0001809% | 0.0001876% | 500 | 525 | 486 | Turbine Control Valves | Turbine Control Valves - EHC Issue
MC4 | D1 | 3 | 380 | 2014-01-06 05:40 | 2014-01-06 05:48 | 0.13333 | 0.068571 | 33.3257 | 0.0004082% | 0.0004224% | 0.000438% | 255 | 525 | 486 | Light-off (Igniter) Systems (Including Fuel Supply) | 4C Mill - Gas Igniter Issue
MC4 | D1 | 4 | 380 | 2014-01-06 06:40 | 2014-01-06 08:55 | 2.25 | 0.79286 | 385.3286 | 0.00472% | 0.004884% | 0.005064% | 340 | 525 | 486 | Light-off (Igniter) Systems (Including Fuel Supply) | 4B & 4C Mills - Gas Igniter Issues
MC4 | D1 | 5 | 380 | 2014-01-06 08:55 | 2014-01-06 12:30 | 3.5833 | 0.71667 | 348.3 | 0.004267% | 0.004415% | 0.004577% | 420 | 525 | 486 | Light-off (Igniter) Systems (Including Fuel Supply) | 4C Mill - Gas Vent Valve Stuck Open
MC4 | D4 | 6 | 360 | 2014-01-08 21:00 | 2014-01-08 21:55 | 0.91667 | 0.20079 | 97.5857 | 0.001195% | 0.001237% |  | 410 | 525 | 486 | Burners | 4B Mill - Coal Burners Inspection
MC4 | D1 | 7 | 250 | 2014-01-08 21:55 | 2014-01-09 05:00 | 7.0833 | 1.5516 | 754.0714 | 0.009237% | 0.009558% | 0.00991% | 410 | 525 | 486 | Pulverizer Feeders | 4A Coal Feeder - VFD Beck Drive Bad Card
MC4 | D1 | 8 | 310 | 2014-01-09 07:00 | 2014-01-09 08:38 | 1.6333 | 0.15556 | 75.6 | 0.0009261% | 0.0009583% | 0.0009935% | 475 | 525 | 486 | Pulverizer Mills | 4A Coal Mill - Breaker Issue
MC4 | D1 | 9 | 360 | 2014-01-12 02:48 | 2014-01-12 09:33 | 6.75 | 1.2214 | 593.6143 | 0.007272% | 0.007524% | 0.007801% | 430 | 525 | 486 | Burners | 4B Mill - Fire, 4B1 Burner Blanked Off
MC4 | NC | 10 | 1160 | 2014-01-18 21:00 | 2014-01-19 07:41 | 10.6833 | [5 empty] | 0 | 525 | 486 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC4 | NC | 11 | 8825 | 2014-01-22 10:35 | 2014-01-22 20:00 | 9.4167 | [5 empty] | 0 | 525 | 486 | Other Scr Problems | SCR Flow Test @ Full Load
MC4 | NC | 12 | 8825 | 2014-01-23 08:47 | 2014-01-23 15:10 | 6.3833 | [5 empty] | 0 | 525 | 486 | Other Scr Problems | SCR Flow Test @ Full Load
MC4 | NC | 13 | 8825 | 2014-01-24 12:20 | 2014-01-24 18:02 | 5.7 | [5 empty] | 0 | 525 | 486 | Other Scr Problems | SCR Flow Test - Full Load
MC4 | NC | 14 | 1160 | 2014-01-26 11:35 | 2014-01-27 05:50 | 18.25 | [5 empty] | 0 | 525 | 486 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC4 | D1 | 15 | 310 | 2014-01-30 02:30 | 2014-01-30 06:55 | 4.4167 | 0.88333 | 429.3 | 0.005259% | 0.005442% | 0.005642% | 420 | 525 | 486 | Pulverizer Mills | 4E Coal Mill - Primary Air Fan Flow Issues
MC4 | D4 | 16 | 310 | 2014-02-02 23:00 | 2014-02-03 03:55 | 4.9167 | 0.98333 | 477.9 | 0.005854% | 0.006058% |  | 420 | 525 | 486 | Pulverizer Mills | 4C Coal Mill - Inspection
MC4 | D1 | 17 | 360 | 2014-02-03 03:55 | 2014-02-03 06:08 | 2.2167 | 0.82333 | 400.14 | 0.004902% | 0.005072% | 0.005259% | 330 | 525 | 486 | Burners | 4B Mill - 4B3 Coal Burner High Temperature4C Coal Mill - Inspection
MC4 | D1 | 18 | 1710 | 2014-02-04 14:30 | 2014-02-19 06:00 | 351.5 | 4.6867 | 2277.72 | 0.0279% | 0.02887% | 0.02993% | 518 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issues
MC4 | D1 | 19 | 310 | 2014-02-07 06:50 | 2014-02-07 07:05 | 0.25 | 0.030952 | 15.0429 | 0.0001843% | 0.0001907% | 0.0001977% | 460 | 525 | 486 | Pulverizer Mills | 4B Coal Mill - Swing Valve & Ignitor Gas Valve Issues
MC4 | D1 | 20 | 250 | 2014-02-11 09:10 | 2014-02-11 09:20 | 0.16667 | 0.030159 | 14.6571 | 0.0001796% | 0.0001858% | 0.0001926% | 430 | 525 | 486 | Pulverizer Feeders | 4C Coal Feeder - Microprocessor Issue
MC4 | NC | 21 | 1160 | 2014-02-12 23:59 | 2014-02-13 04:20 | 4.35 | [5 empty] | 0 | 525 | 486 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC4 | D4 | 22 | 8160 | 2014-02-17 20:00 | 2014-02-18 00:24 | 4.4 | 1.6343 | 794.2629 | 0.00973% | 0.01007% |  | 330 | 525 | 486 | Wet Scrubber Mist Eliminators/demisters & Washdown | FGD Demister Wash Line - Relocation
MC4 | NC | 23 | 4490 | 2014-02-19 06:00 | 2014-02-19 12:30 | 6.5 | [5 empty] | 0 | 525 | 486 | Turbine Performance Testing | Full Load Capability Test
MC4 | D1 | 24 | 1710 | 2014-02-19 17:42 | 2014-02-21 10:13 | 40.5167 | 0.54022 | 262.548 | 0.003216% | 0.003328% | 0.00345% | 518 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
MC4 | NC | 25 | 1160 | 2014-02-20 23:00 | 2014-02-21 04:00 | 5 | [5 empty] | 0 | 525 | 486 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC4 | D1 | 26 | 1710 | 2014-02-21 10:13 | 2014-03-01 | 181.7833 | 1.0388 | 504.8383 | 0.006184% | 0.006399% | 0.006634% | 522 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
MC4 | D1 | 27 | 4460 | 2014-02-23 04:00 | 2014-02-23 04:33 | 0.55 | 0.31952 | 155.2886 | 0.001902% | 0.001968% | 0.002041% | 220 | 525 | 486 | Turbine Overspeed Trip Test | Turbine Overspeed Test - Linkage Stuck
MC4 | D1 | 28 | 1520 | 2014-02-25 08:16 | 2014-02-25 09:00 | 0.73333 | 0.069841 | 33.9429 | 0.0004158% | 0.0004302% | 0.0004461% | 475 | 525 | 486 | Flue Gas Dampers (Except Recirculation) | 4A Economizer Outlet Damper - Failed to Open Completely
MC4 | [5 empty] | 684.2 | 16.4772 | 8007.9377 | 0.0981% | 0.1015% | 0.08724%
D4
TC1 | NC | 1 | 1489 | 2014-01-02 09:00 | 2014-01-02 15:00 | 6 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Holding the unit above 525 MW's for Air Heater Slip Testing to be conducted.
TC1 | NC | 2 | 1489 | 2014-01-03 05:00 | 2014-01-03 09:40 | 4.6667 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Holding load above 525 MW's for ammonia slip testing for the air heaters.
TC1 | D1 | 3 | 280 | 2014-01-03 09:40 | 2014-01-03 11:31 | 1.85 | 0.13988 | 53.5733 | 0.0006563% | 0.0006791% | 0.000704% | 379 | 410 | 383 | Pulverizer Fires | Derate due to fires in the B and D coal mills.
TC1 | D1 | 4 | 280 | 2014-01-04 02:47 | 2014-01-04 03:56 | 1.15 | 0.098171 | 37.5994 | 0.0004606% | 0.0004766% | 0.0004941% | 375 | 410 | 383 | Pulverizer Fires | Derate due to fire in the D coal mill.
TC1 | D1 | 5 | 280 | 2014-01-04 05:09 | 2014-01-04 08:18 | 3.15 | 0.33037 | 126.5301 | 0.00155% | 0.001604% | 0.001663% | 367 | 410 | 383 | Pulverizer Fires | Derate due to fires in the D coal mill and the E coal mill was unavailable for a m
TC1 | D1 | 6 | 280 | 2014-01-07 17:25 | 2014-01-07 21:08 | 3.7167 | 0.38073 | 145.8202 | 0.001786% | 0.001848% | 0.001916% | 368 | 410 | 383 | Pulverizer Fires | Derate required due to A & B coal mill fires.
TC1 | D1 | 7 | 590 | 2014-01-08 12:00 | 2014-01-08 17:26 | 5.4333 | 0.46382 | 177.6435 | 0.002176% | 0.002252% | 0.002335% | 375 | 410 | 383 | Desuperheater/Attemperator Valves | The SH Spray control valve was leaking and required a unit derate to accomplish th
TC1 | NC | 8 | 1489 | 2014-01-09 07:00 | 2014-01-09 13:00 | 6 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | A 525 MW minimum limit was set on the unit to accomplish air heater slip testing.
TC1 | NC | 9 | 1489 | 2014-01-10 06:30 | 2014-01-10 15:00 | 8.5 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | A 525 MW minimum limit was set on the unit to accomplish air heater slip testing.
TC1 | D1 | 10 | 8000 | 2014-01-11 05:23 | 2014-01-11 19:09 | 13.7667 | 2.4176 | 925.9259 | 0.01134% | 0.01174% | 0.01217% | 338 | 410 | 383 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup
TC1 | D1 | 11 | 8000 | 2014-01-11 19:09 | 2014-01-11 21:03 | 1.9 | 0.94537 | 362.0751 | 0.004435% | 0.00459% | 0.004758% | 206 | 410 | 383 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup
TC1 | U1 | 12 | 9900 | 2014-01-11 21:03 | 2014-01-12 07:57 | 10.9 | 10.9 | 4174.7 | 0.05114% | 0.05292% | 0.05486% | 0 | 410 | 383 | Operator Error | During load drop, operator error in valve closing caused the TDBFP main extraction
TC1 | D1 | 13 | 280 | 2014-01-13 06:39 | 2014-01-13 10:33 | 3.9 | 0.33293 | 127.511 | 0.001562% | 0.001616% | 0.001676% | 375 | 410 | 383 | Pulverizer Fires | Unit derate due to two coal mill issues: 1E mill had a fire that needed to be put out
TC1 | D1 | 14 | 280 | 2014-01-14 08:36 | 2014-01-14 10:39 | 2.05 | 0.175 | 67.025 | 0.0008211% | 0.0008496% | 0.0008808% | 375 | 410 | 383 | Pulverizer Fires | Derate due to fire in the 1B Coal Mill.
TC1 | U1 | 15 | 3344 | 2014-01-14 10:39 | 2014-01-16 22:16 | 59.6167 | 59.6167 | 22833.1833 | 0.2797% | 0.2894% | 0.3001% | 0 | 410 | 383 | Deaerator Heater Head Leak | Leak in the deaerator heater head was discovered. Unit was taken offline to repair
TC1 | D1 | 16 | 280 | 2014-01-17 15:20 | 2014-01-17 16:00 | 0.66667 | 0.043902 | 16.8146 | 0.000206% | 0.0002131% | 0.000221% | 383 | 410 | 383 | Pulverizer Fires | Fires in the 1A and 1B coal mills required unit derate.
TC1 | D1 | 17 | 280 | 2014-01-17 16:00 | 2014-01-17 16:45 | 0.75 | 0.22866 | 87.5762 | 0.001073% | 0.00111% | 0.001151% | 285 | 410 | 383 | Pulverizer Fires | Additional fire in the 1C mill following 1A and 1B mill fires
TC1 | D1 | 18 | 280 | 2014-01-17 16:45 | 2014-01-17 19:40 | 2.9167 | 1.5793 | 604.8598 | 0.00741% | 0.007667% | 0.007949% | 188 | 410 | 383 | Pulverizer Fires | Additional fire in the 1D mill after fires in the 1A, 1B, and 1C mills
TC1 | D1 | 19 | 280 | 2014-01-17 19:40 | 2014-01-17 20:08 | 0.46667 | 0.056911 | 21.7967 | 0.000267% | 0.0002763% | 0.0002864% | 360 | 410 | 383 | Pulverizer Fires | Some of the mills were returned to service. However, unit derate was still necessary
TC1 | NC | 20 | 4267 | 2014-01-19 01:00 | 2014-01-19 01:30 | 0.5 | [5 empty] | 0 | 410 | 383 | Turbine Control Valve Testing | Weekly valve check on the unit, Unit available to return to full load if required
TC1 | NC | 21 | 1489 | 2014-01-21 18:00 | 2014-01-21 23:59 | 5.9833 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running and good for full load but with a 525 MW limit set for ammonia slip
TC1 | NC | 22 | 1489 | 2014-01-29 06:00 | 2014-01-29 08:00 | 2 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running and good for full load but with a 525 MW limit set for ammonia sl
TC1 | NC | 23 | 9999 | 2014-01-29 08:00 | 2014-01-29 10:00 | 2 | [5 empty] | 0 | 410 | 383 | Total Unit Performance Testing | Unit was running and requested full load production to allow for the full-load tes
TC1 | NC | 24 | 1489 | 2014-01-29 10:00 | 2014-01-29 14:37 | 4.6167 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running and good for full load but with a 525 MW limit set for ammonia sl
TC1 | NC | 25 | 1489 | 2014-01-31 13:00 | 2014-01-31 20:00 | 7 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running & good for full load with a 525 MW limit set for ammonia slip mit
TC1 | NC | 147 | 1489 | 2014-01-31 13:00 | 2014-01-31 20:00 | 7 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running and good for full load with a 525 MW limit set for ammonia slip m
TC1 | NC | 26 | 9999 | 2014-02-05 10:45 | 2014-02-05 16:26 | 5.6833 | [5 empty] | 0 | 410 | 383 | Total Unit Performance Testing | Unit running and good for full load, this non-curtailing event was for the complet
TC1 | D1 | 27 | 310 | 2014-02-10 07:22 | 2014-02-10 07:45 | 0.38333 | 0.032724 | 12.5331 | 0.0001535% | 0.0001589% | 0.0001647% | 375 | 410 | 383 | Pulverizer Mills | Derate on TC1 to 500 MW's due to D coal mill fire. Additional issue with the E co
TC1 | D1 | 28 | 310 | 2014-02-10 10:00 | 2014-02-10 13:58 | 3.9667 | 0.33862 | 129.6907 | 0.001589% | 0.001644% | 0.001704% | 375 | 410 | 383 | Pulverizer Mills | Derate required due to fire on the 1D coal mill.
TC1 | D1 | 29 | 310 | 2014-02-11 22:17 | 2014-02-11 23:30 | 1.2167 | 0.10386 | 39.7791 | 0.0004873% | 0.0005042% | 0.0005228% | 375 | 410 | 383 | Pulverizer Mills | Derate required due to high temperature on the 1B coal mill.
TC1 | NC | 30 | 9999 | 2014-02-19 08:00 | 2014-02-19 14:00 | 6 | [5 empty] | 0 | 410 | 383 | Total Unit Performance Testing | Test run at full load to maintain high temperatures for unit testing.
TC1 | [5 empty] | 183.75 | 78.1844 | 29944.637 | 0.3668% | 0.3796% | 0.3935%
D4
TC2 | D1 | 1 | 3439 | 2014-01-01 | 2014-01-04 02:00 | 74 | 5.2422 | 2988.0395 | 0.0366% | 0.03788% | 0.03927% | 564 | 607 | 570 | High Pressure Heater Head Leaks | 7A FWH is out of service due to a heater head leak and unit derate required until
TC2 | NC | 2 | 1190 | 2014-01-04 12:00 | 2014-01-04 17:00 | 5 | [5 empty] | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate due to boiler OEM recommended deslag, unit available to retu
TC2 | NC | 3 | 1190 | 2014-01-11 | 2014-01-11 05:23 | 5.3833 | [5 empty] | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate at 561MW for boiler OEM recommended weekly deslag.
TC2 | D1 | 4 | 8000 | 2014-01-11 05:23 | 2014-01-11 19:09 | 13.7667 | 3.3793 | 1926.1993 | 0.0236% | 0.02442% | 0.02531% | 458 | 607 | 570 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup
TC2 | D1 | 5 | 8000 | 2014-01-11 19:09 | 2014-01-12 02:45 | 7.6 | 3.0926 | 1762.7743 | 0.02159% | 0.02234% | 0.02317% | 360 | 607 | 570 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup
TC2 | D1 | 6 | 8650 | 2014-01-17 19:30 | 2014-01-17 22:15 | 2.75 | 0.54366 | 309.8847 | 0.003796% | 0.003928% | 0.004072% | 487 | 607 | 570 | Baghouse Systems - General | The bags in the baghouse are deteriorating ... holes in the bags
TC2 | D1 | 7 | 8650 | 2014-01-18 04:15 | 2014-01-18 05:45 | 1.5 | 0.29654 | 169.028 | 0.002071% | 0.002143% | 0.002221% | 487 | 607 | 570 | Baghouse Systems - General | The bags in the baghouse are deteriorating ... holes in the bags
TC2 | D1 | 8 | 9620 | 2014-01-18 11:25 | 2014-01-18 14:00 | 2.5833 | 0.31919 | 181.9399 | 0.002229% | 0.002306% | 0.002391% | 532 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | High particulate matter readings required derate to avoid an exceedance.
TC2 | D1 | 9 | 9620 | 2014-01-18 17:55 | 2014-01-18 18:10 | 0.25 | 0.049423 | 28.1713 | 0.0003451% | 0.0003571% | 0.0003702% | 487 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | The bags in the baghouse are deteriorating … holes in the bags
TC2 | D1 | 10 | 9620 | 2014-01-18 18:10 | 2014-01-18 19:15 | 1.0833 | 0.10708 | 61.0379 | 0.0007477% | 0.0007737% | 0.0008021% | 547 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | The bags in the baghouse are deteriorating … holes in the bags
TC2 | NC | 11 | 1190 | 2014-01-19 | 2014-01-19 06:15 | 6.25 | [5 empty] | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate to conduct boiler OEM recommended deslag.
TC2 | D1 | 12 | 9620 | 2014-01-19 10:29 | 2014-01-19 13:00 | 2.5167 | 0.31096 | 177.2446 | 0.002171% | 0.002247% | 0.002329% | 532 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | High particulate readings required unit derate to avoid an exceedance
TC2 | D1 | 13 | 9620 | 2014-01-19 17:50 | 2014-01-19 20:15 | 2.4167 | 0.2986 | 170.2018 | 0.002085% | 0.002157% | 0.002237% | 532 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | High particulate readings required unit derate to avoid an exceedance
TC2 | D1 | 14 | 9610 | 2014-01-20 01:45 | 2014-01-20 16:30 | 14.75 | 1.8286 | 1042.2807 | 0.01277% | 0.01321% | 0.0137% | 531.75 | 607 | 570 | Nox Stack Emissions - Fossil Steam Units | High NOx readings required unit derate to avoid exceedance. Mill configuration ma
TC2 | NC | 15 | 1190 | 2014-01-26 12:00 | 2014-01-26 18:00 | 6 | [5 empty] | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate at 561 MW to conduct boiler OEM recommended deslag. Unit av
TC2 | NC | 16 | 1190 | 2014-02-01 00:01 | 2014-02-01 06:15 | 6.2333 | 6.2333 | 3553 |  |  |  | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate at 550 MW to conduct boiler OEM recommended deslag. Unit av
TC2 | D1 | 17 | 310 | 2014-02-02 16:30 | 2014-02-02 19:00 | 2.5 | 0.40259 | 229.479 | 0.002811% | 0.002909% | 0.003016% | 509.25 | 607 | 570 | Pulverizer Mills | The 2D mill was performing poorly and was taken off-line to investigate. Some mil
TC2 | D1 | 18 | 1455 | 2014-02-04 15:45 | 2014-02-04 16:15 | 0.5 | 0.015651 | 8.9209 | 0.0001093% | 0.0001131% | 0.0001172% | 588 | 607 | 570 | Induced Draft Fans | Derate required on the unit due to ID fan stall alarms. Required derate to avoid
TC2 | PO | 20 | 360 | 2014-02-08 03:21 | 2014-03-01 | 500.65 | 500.65 | 285370.5 | 3.496% |  |  | 0 | 607 | 570 | Burners | TC2 began the planned outage for the replacement of all 30 burners. This effort i
TC2 | [5 empty] | 655.7333 | 522.7697 | 297978.702 | 3.607% | 0.1148% | 0.119%
D4
[9 empty] | 9.856% | 6.435% | 2.933%
BR5 | U1 | 2 | 5054 | 2014-01-06 08:23 | 2014-01-06 11:47 | 3.4 | 3.4 | 442 |  |  |  | 0 | 131 | 130 | Water Injection System | Instrument measuring DP across water injection control started to freeze. Operato
BR5 | MO | 10 | 5048 | 2014-02-18 08:00 | 2014-02-18 12:46 | 4.7667 | 4.7667 | 533.8667 |  |  |  | 0 | 113 | 112 | Gas Fuel System with controls and instruments | Inspect orifice, calibrate transmitter for fuel gas system flow meter.
BR5 | MO | 12 | 5272 | 2014-02-27 06:55 | 2014-02-27 14:53 | 7.9667 | 7.9667 | 892.2667 |  |  |  | 0 | 113 | 112 | Gas Turbine - Boroscope Inspection | Eddy Current Inspection of R3 blade
BR5 | [5 empty] | 0 | 0 | 0
BR6 | SF | 2 | 4810 | 2014-01-02 16:13 | 2014-01-02 17:03 | 0.83333 | 0.83333 | 142.5 |  |  |  | 0 | 172 | 171 | Generator Output Breaker | Generator circuit breaker loss of 120VAC control power prevented the unit from sta
BR6 | U1 | 7 | 5109 | 2014-01-23 13:31 | 2014-01-23 14:49 | 1.3 | 1.3 | 222.3 |  |  |  | 0 | 172 | 171 | Other Gas Turbine Exhaust Problems | Loss TC on TAT2 readings. TC reading was coming in and out of service
BR6 | MO | 10 | 5048 | 2014-02-04 06:30 | 2014-02-04 08:00 | 1.5 | 1.5 | 256.5 |  |  |  | 0 | 172 | 171 | Gas Fuel System with controls and instruments | Change cable for fuel gas flow meter RTD.
BR6 | [5 empty] | 3.6333 | 3.6333 | 621.3
BR7 | U1 | 4 | 4700 | 2014-01-04 06:11 | 2014-01-04 11:16 | 5.0833 | 5.0833 | 869.25 |  |  |  | 0 | 172 | 171 | Generator Voltage Control | AVR Fault due to loss of channel one processor.
BR7 | U1 | 7 | 5150 | 2014-01-13 08:05 | 2014-01-14 13:30 | 29.4167 | 29.4167 | 5030.25 |  |  |  | 0 | 172 | 171 | Gas Turbine - Turning Gear And Motor | Unit will not stay on rotor barring.
BR7 | U1 | 12 | 5049 | 2014-02-10 17:14 | 2014-02-10 19:34 | 2.3333 | 2.3333 | 399 |  |  |  | 0 | 172 | 171 | Other Gas Turbine Fuel System Problems | Issue with pressure regulators in reducing station.
BR7 | [5 empty] | 36.8333 | 36.8333 | 6298.5
BR8 | MO | 4 | 5111 | 2014-01-13 07:46 | 2014-01-13 09:25 | 1.65 | 1.65 | 211.2 |  |  |  | 0 | 129 | 128 | Gas Turbine - Lube Oil Pumps | Check DC brushes on emergency lube oil equipment
BR8 | MO | 13 | 5111 | 2014-02-19 12:10 | 2014-02-19 12:35 | 0.41667 | 0.41667 | 53.3333 |  |  |  | 0 | 129 | 128 | Gas Turbine - Lube Oil Pumps | Check brushes on DC lube oil pumps
BR8 | MO | 15 | 5160 | 2014-02-20 12:35 | 2014-02-20 13:00 | 0.41667 | 0.41667 | 53.3333 |  |  |  | 0 | 129 | 128 | Gas Turbine - Cooling And Seal Air System | Check brushes on DC mantling air fan
BR8 | MO | 17 | 5272 | 2014-02-28 08:24 | 2014-02-28 15:30 | 7.1 | 7.1 | 908.8 |  |  |  | 0 | 129 | 128 | Gas Turbine - Boroscope Inspection | Eddy Current Inspection of R3 blade and boroscope of trubine.
BR8 | [5 empty] | 9.5833 | 9.5833 | 1226.6667
BR9 | U1 | 3 | 5140 | 2014-01-07 09:33 | 2014-01-07 10:36 | 1.05 | 1.05 | 144.9 |  |  |  | 0 | 139 | 138 | Gas Turbine - Battery And Charger System | Both battery chargers indicated failure. Failure was caused by low output current
BR9 | MO | 5 | 5111 | 2014-01-13 09:25 | 2014-01-13 10:22 | 0.95 | 0.95 | 131.1 |  |  |  | 0 | 139 | 138 | Gas Turbine - Lube Oil Pumps | Check brushes on DC lube oil pumps
BR9 | MO | 12 | 5160 | 2014-02-20 13:00 | 2014-02-20 17:04 | 4.0667 | 4.0667 | 561.2 |  |  |  | 0 | 139 | 138 | Gas Turbine - Cooling And Seal Air System | Changed brushes on DC mantling air fan.
BR9 | MO | 12 | 5160 | 2014-02-20 13:00 | 2014-02-20 17:04 | 4.07 | [5 empty] | 0 | 139 | 138 | Gas Turbine - Cooling And Seal Air System | F590Changed brushes on DC mantling air fan.
BR9 | MO | 14 | 5272 | 2014-02-25 06:59 | 2014-02-25 20:03 | 13.07 | [5 empty] | 0 | 139 | 138 | Gas Turbine - Boroscope Inspection | F590Eddy current inspection of R3 blade and boroscope of turbine section.
BR9 | [5 empty] | 23.2067 | 6.0667 | 837.2
BR10 | MO | 4 | 5111 | 2014-01-13 10:22 | 2014-01-13 11:18 | 0.93333 | 0.93333 | 128.8 |  |  |  | 0 | 139 | 138 | Gas Turbine - Lube Oil Pumps | Outage to check brushes on DC lube oil pumps.
BR10 | MO | 10 | 5160 | 2014-02-20 17:04 | 2014-02-20 19:28 | 2.4 | 2.4 | 331.2 |  |  |  | 0 | 139 | 138 | Gas Turbine - Cooling And Seal Air System | Check brushes on DC mantling air fan.
BR10 | MO | 12 | 5272 | 2014-02-28 10:48 | 2014-03-02 13:50 | 51.0333 | 51.0333 | 7042.6 |  |  |  | 0 | 139 | 138 | Gas Turbine - Boroscope Inspection | Eddy current inspection of R3 blade and boroscope of turbine section.
BR10 | [5 empty] | 54.3667 | 54.3667 | 7502.6
BR11 | U1 | 3 | 5017 | 2014-01-06 17:57 | 2014-01-06 19:14 | 1.2833 | 1.2833 | 164.2667 |  |  |  | 0 | 129 | 128 | Low Pressure Compressor Bleed Valves | Loose limit switch on blow off valve caused unit to trip.
BR11 | MO | 6 | 5111 | 2014-01-13 12:32 | 2014-01-13 13:45 | 1.2167 | 1.2167 | 155.7333 |  |  |  | 0 | 129 | 128 | Gas Turbine - Lube Oil Pumps | Outage to check brushes on DC lube oil pumps
BR11 | MO | 8 | 5108 | 2014-01-14 08:00 | 2014-01-14 13:54 | 5.9 | 5.9 | 755.2 |  |  |  | 0 | 129 | 128 | Gas Turbine - High Engine Exhaust Temperature | Outage to replace TAT probe. Two thermocouples not working
BR11 | MO | 11 | 5160 | 2014-01-16 14:00 | 2014-01-16 18:57 | 4.95 | 4.95 | 633.6 |  |  |  | 0 | 129 | 128 | Gas Turbine - Cooling And Seal Air System | Leak of water into control air off the compressor
BR11 | U1 | 16 | 5017 | 2014-01-30 03:36 | 2014-01-30 07:40 | 4.0667 | 4.0667 | 520.5333 |  |  |  | 0 | 129 | 128 | Low Pressure Compressor Bleed Valves | Loose limit switch on compressor blow off valve
BR11 | MO | 19 | 5160 | 2014-02-20 19:28 | 2014-02-20 21:16 | 1.8 | 1.8 | 230.4 |  |  |  | 0 | 129 | 128 | Gas Turbine - Cooling And Seal Air System | Checked brushes on DC mantling air system.
BR11 | MO | 21 | 5272 | 2014-02-26 07:11 | 2014-02-26 16:18 | 9.1167 | 9.1167 | 1166.9333 |  |  |  | 0 | 129 | 128 | Gas Turbine - Boroscope Inspection | Eddy current inspection of R3 blade and boroscope inspection of turbine section.
BR11 | [5 empty] | 28.3333 | 28.3333 | 3626.6667
CR11 | U1 | 2 | 5130 | 2014-01-06 20:13 | 2014-01-07 09:05 | 12.8667 | 12.8667 | 180.1333 |  |  |  | 0 | 14 | 14 | Gas Turbine - Starting System (including Motor) | Broken terminal on battery cable causing Cane Run 11 starting diesel to be unable
CR11 | U1 | 5 | 5110 | 2014-01-21 10:51 | 2014-01-21 12:24 | 1.55 | 1.55 | 21.7 |  |  |  | 0 | 14 | 14 | Gas Turbine - Lube Oil System - General | Lube oil temperature to low.
CR11 | U1 | 9 | 3840 | 2014-02-03 00:42 | 2014-02-03 09:37 | 8.9167 | 8.9167 | 124.8333 |  |  |  | 0 | 14 | 14 | Service Air Compressors | Clutch air compressor pumping up slowly - probably due to the weather.
CR11 | [5 empty] | 23.3333 | 23.3333 | 326.6667
HA1 | SF | 2 | 5160 | 2014-01-06 21:22 | 2014-01-14 13:14 | 183.8667 | 183.8667 | 2574.1333 |  |  |  | 0 | 14 | 14 | Gas Turbine - Cooling And Seal Air System | Busted glycol line on radiator. Failed to ignite on start up.
HA1 | U1 | 4 | 5120 | 2014-01-16 12:31 | 2014-01-17 14:09 | 25.6333 | 25.6333 | 358.8667 |  |  |  | 0 | 14 | 14 | Gas Turbine - Hydraulic Oil System | Oil leak on diesel starting engine.
HA1 | U1 | 5 | 5108 | 2014-01-17 14:23 | 2014-01-20 14:33 | 72.1667 | 72.1667 | 1010.3333 |  |  |  | 0 | 14 | 14 | Gas Turbine - High Engine Exhaust Temperature | Lost two exhaust gas thermocouples during run.
HA1 | U1 | 7 | 5050 | 2014-01-30 06:30 | 2014-01-30 07:01 | 0.51667 | 0.51667 | 7.2333 |  |  |  | 0 | 14 | 14 | Gas Turbine - Ignition System | Ignition torch failed to light
HA1 | U1 | 9 | 3611 | 2014-02-08 02:53 | 2014-02-08 19:05 | 16.2 | 16.2 | 194.4 |  |  |  | 0 | 12 | 12 | Switchyard Circuit Breakers | Loss of power to 138KV sub.
HF1 | [5 empty] | 298.3833 | 298.3833 | 4144.9667
HA2 | U1 | 4 | 3611 | 2014-02-08 02:53 | 2014-02-08 19:05 | 16.2 | 16.2 | 194.4 |  |  |  | 0 | 12 | 12 | Switchyard Circuit Breakers | Loss power to 138KV bus in substation
HA2 | MO | 6 | 5111 | 2014-02-19 11:20 | 2014-02-19 12:20 | 1 | 1 | 12 |  |  |  | 0 | 12 | 12 | Gas Turbine - Lube Oil Pumps | Inspect brushes and repair coupling for DC lube oil pump.
HF2 | [5 empty] | 17.2 | 17.2 | 206.4
PR11 | U1 | 2 | 9130 | 2014-01-30 07:00 | 2014-01-31 09:20 | 26.3333 | 26.3333 | 316 |  |  |  | 0 | 12 | 12 | Lack Of Fuel (outside Management Control) | Fuel supply not available.
PR11 | [5 empty] | 26.3333 | 26.3333 | 316
PR12 | U1 | 2 | 9130 | 2014-01-30 07:00 | 2014-01-31 09:20 | 26.3333 | 26.3333 | 605.6667 |  |  |  | 0 | 23 | 23 | Lack Of Fuel (outside Management Control) | Fuel supply not available.
PR12 | U1 | 4 | 5170 | 2014-02-19 10:25 | 2014-03-01 | 229.5833 | 229.5833 | 5280.4167 |  |  |  | 0 | 23 | 23 | Gas Turbine - Cooling Water System | Fire pump that supplies cooling water locked up.
PR12 | [5 empty] | 255.9167 | 255.9167 | 5886.0833
PR13 | U1 | 2 | 9130 | 2014-01-30 07:00 | 2014-01-31 09:20 | 26.3333 | 26.3333 | 3871 |  |  |  | 0 | 148 | 147 | Lack Of Fuel (outside Management Control) | Fuel supply not available.
PR13 | PO | 4 | 4720 | 2014-02-15 06:08 | 2014-03-01 | 329.8667 | 329.8667 | 57726.6667 |  |  |  | 0 | 176 | 175 | Generator Synchronization Equipment | Generator synchronization equipment modifications. Replacing all generator protec
PR13 | [5 empty] | 356.2 | 356.2 | 61597.6667
TC5 | U1 | 2 | 5240 | 2014-01-03 11:04 | 2014-01-03 13:20 | 2.2667 | 2.2667 | 398.9333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fire Detection And Extinguishing Sys | Unit tripped on fire protection alarm due to condensation within fire protection p
TC5 | U1 | 4 | 5246 | 2014-01-06 12:15 | 2014-01-06 14:08 | 1.8833 | 1.8833 | 331.4667 |  |  |  | 0 | 180 | 176 | Gas Turbine Control System - Hardware Problems.... | Unit tripped on high exhaust temperature differential from a failed control system
TC5 | U1 | 6 | 5246 | 2014-01-07 01:25 | 2014-01-07 05:50 | 4.4167 | 4.4167 | 777.3333 |  |  |  | 0 | 180 | 176 | Gas Turbine Control System - Hardware Problems.... | Forced outage due to compressor inlet thermocouple disagreement from a failed cont
TC5 | U1 | 12 | 5079 | 2014-02-11 06:16 | 2014-02-11 08:35 | 2.3167 | 2.3167 | 407.7333 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
TC5 | SF | 14 | 5130 | 2014-02-17 06:28 | 2014-02-17 06:40 | 0.2 | 0.2 | 35.2 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to issue with LCI.
TC5 | U1 | 16 | 5130 | 2014-02-17 10:43 | 2014-02-17 11:57 | 1.2333 | 1.2333 | 217.0667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage to change out resistivity probe on the cooling system for the LCI.
TC5 | SF | 18 | 5130 | 2014-02-17 17:45 | 2014-02-17 20:14 | 2.4833 | 2.4833 | 437.0667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to low resistivity in the cooling water for the LCI. Changed
TC5 | [5 empty] | 14.8 | 14.8 | 2604.8
TC6 | U1 | 4 | 5079 | 2014-01-06 02:17 | 2014-01-06 03:50 | 1.55 | 1.55 | 272.8 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to a lean blowout.
TC6 | U1 | 6 | 5041 | 2014-01-06 13:52 | 2014-01-06 14:46 | 0.9 | 0.9 | 158.4 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Unit tripped due to a fuel gas valve (worker valve) not controlling properly.
TC6 | U1 | 8 | 5016 | 2014-01-07 01:25 | 2014-01-07 05:49 | 4.4 | 4.4 | 774.4 |  |  |  | 0 | 180 | 176 | High Pressure Compressor - Bleed Valves | Forced outage due to compressor bleed valve frozen closed.
TC6 | U1 | 10 | 5048 | 2014-01-21 16:35 | 2014-01-21 17:24 | 0.81667 | 0.81667 | 128.2167 |  |  |  | 0 | 160 | 157 | Gas Fuel System with controls and instruments | Forced outage due to combustion instrumentation issues.
TC6 | U1 | 11 | 5048 | 2014-01-21 17:32 | 2014-01-21 20:01 | 2.4833 | 2.4833 | 389.8833 |  |  |  | 0 | 160 | 157 | Gas Fuel System with controls and instruments | Forced outage due to combustion instrumentation issues.
TC6 | U1 | 12 | 5079 | 2014-01-22 00:08 | 2014-01-22 04:20 | 4.2 | 4.2 | 659.4 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Forced outage due to flameout.
TC6 | SF | 13 | 5016 | 2014-01-22 04:20 | 2014-01-22 05:55 | 1.5833 | 1.5833 | 248.5833 |  |  |  | 0 | 160 | 157 | High Pressure Compressor - Bleed Valves | Startup failure due to frozen compressor bleed valve.
TC6 | SF | 14 | 5016 | 2014-01-22 05:55 | 2014-01-22 06:45 | 0.83333 | 0.83333 | 130.8333 |  |  |  | 0 | 160 | 157 | High Pressure Compressor - Bleed Valves | Startup failure due to frozen compressor bleed valve.
TC6 | U1 | 15 | 5079 | 2014-01-23 11:39 | 2014-01-23 12:04 | 0.41667 | 0.41667 | 65.4167 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Forced outage due to combustion issue.
TC6 | SF | 17 | 5041 | 2014-01-23 16:56 | 2014-01-23 17:21 | 0.41667 | 0.41667 | 65.4167 |  |  |  | 0 | 160 | 157 | Gas Turbine - Fuel Piping And Valves | Startup failure due to issue with fuel gas valve.
TC6 | U1 | 18 | 5079 | 2014-01-23 17:30 | 2014-01-23 18:00 | 0.5 | 0.5 | 78.5 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Forced outage due to combustion issue.
TC6 | U1 | 19 | 5079 | 2014-01-23 18:18 | 2014-01-23 18:49 | 0.51667 | 0.51667 | 81.1167 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Forced outage due to combustion issue.
TC6 | U1 | 20 | 5250 | 2014-01-24 04:29 | 2014-01-24 10:13 | 5.7333 | 5.7333 | 900.1333 |  |  |  | 0 | 160 | 157 | Other Controls And Instrument Problems | Forced outage due to erratic thermocouple signals from T Processor.
TC6 | SF | 22 | 5041 | 2014-01-24 10:30 | 2014-01-24 11:08 | 0.63333 | 0.63333 | 99.4333 |  |  |  | 0 | 160 | 157 | Gas Turbine - Fuel Piping And Valves | Startup failure due to issue with fuel gas valve.
TC6 | MO | 23 | 5041 | 2014-01-25 12:06 | 2014-01-25 16:20 | 4.2333 | 4.2333 | 664.6333 |  |  |  | 0 | 160 | 157 | Gas Turbine - Fuel Piping And Valves | Maintenance outage to prepare unit for tuning.
TC6 | U1 | 25 | 5048 | 2014-01-27 11:27 | 2014-01-27 14:05 | 2.6333 | 2.6333 | 413.4333 |  |  |  | 0 | 160 | 157 | Gas Fuel System with controls and instruments | Unit tripped due to frozen sensing line to 96GN transmitter.
TC6 | MO | 30 | 5041 | 2014-02-04 11:33 | 2014-02-04 15:52 | 4.3167 | 4.3167 | 759.7333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Maintenance outage to change controller on Fuel Gas Worker Valve.
TC6 | U1 | 33 | 5079 | 2014-02-11 06:16 | 2014-02-11 06:58 | 0.7 | 0.7 | 123.2 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
TC6 | U1 | 34 | 5079 | 2014-02-11 08:29 | 2014-02-11 09:45 | 1.2667 | 1.2667 | 222.9333 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
TC6 | [5 empty] | 38.1333 | 38.1333 | 6236.4667
TC7 | U1 | 2 | 5048 | 2014-01-03 05:14 | 2014-01-03 06:52 | 1.6333 | 1.6333 | 287.4667 |  |  |  | 0 | 180 | 176 | Gas Fuel System with controls and instruments | Forced outage due to Hazardous Gas alarm.
TC7 | U1 | 4 | 5041 | 2014-01-05 14:07 | 2014-01-05 15:36 | 1.4833 | 1.4833 | 261.0667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Forced outage due to fuel gas valve (SRV).
TC7 | U1 | 8 | 5160 | 2014-02-05 16:03 | 2014-02-05 16:08 | 0.083333 | 0.083333 | 14.6667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Unit rolled back to FSNL due to issue with pressure switch on Exhaust Frame Blower
TC7 | U1 | 9 | 5160 | 2014-02-05 16:09 | 2014-02-05 16:17 | 0.13333 | 0.13333 | 23.4667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Unit rolled back to FSNL due to issue with pressure switch on Exhaust Frame Blower
TC7 | [5 empty] | 3.3333 | 3.3333 | 586.6667
TC8 | U1 | 2 | 5130 | 2014-01-03 05:21 | 2014-01-04 00:26 | 19.0833 | 19.0833 | 3358.6667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to issue with 89SS.
TC8 | SF | 5 | 5130 | 2014-01-05 19:28 | 2014-01-06 15:58 | 20.5 | 20.5 | 3608 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to issue with 89SS.
TC8 | U1 | 9 | 3869 | 2014-01-10 14:00 | 2014-01-14 13:28 | 95.4667 | 95.4667 | 16802.1333 |  |  |  | 0 | 180 | 176 | Other Fire Protection System Problems | Forced outage due to issue with Fire Protection System.
TC8 | U1 | 15 | 5041 | 2014-01-30 06:34 | 2014-01-30 07:49 | 1.25 | 1.25 | 196.25 |  |  |  | 0 | 160 | 157 | Gas Turbine - Fuel Piping And Valves | Forced outage to reset lifted safety valve that occurred due to fuel gas pressure
TC8 | [5 empty] | 136.3 | 136.3 | 23965.05
TC9 | SF | 3 | 5130 | 2014-01-03 | 2014-01-03 20:51 | 20.85 | 20.85 | 3669.6 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to issue with 89SS.
TC9 | U1 | 7 | 5130 | 2014-01-06 02:27 | 2014-01-06 02:57 | 0.5 | 0.5 | 88 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to issue with 89SS.
TC9 | D1 | 17 | 5041 | 2014-02-07 10:00 | 2014-02-07 12:38 | 2.6333 | 1.463 | 257.4815 |  |  |  | 80 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Derate to 80 MWs due to issue with worker fuel gas valve.
TC9 | U1 | 15 | 5041 | 2014-02-07 12:38 | 2014-02-07 15:35 | 2.95 | 2.95 | 519.2 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Forced outage to address pressure swings due to worker fuel gas valve.
TC9 | SF | 20 | 5130 | 2014-02-26 02:38 | 2014-02-26 03:45 | 1.1167 | 1.1167 | 196.5333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to 89SS on TC10 failing to open.
TC9 | U1 | 22 | 5160 | 2014-02-26 19:14 | 2014-02-26 19:15 | 0.016667 | 0.016667 | 2.9333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Forced outage from load runback due to issue with Exhaust Frame Blower.
TC9 | [5 empty] | 28.0667 | 26.8963 | 4733.7481
TC10 | U1 | 2 | 5016 | 2014-01-03 05:21 | 2014-01-03 07:03 | 1.7 | 1.7 | 299.2 |  |  |  | 0 | 180 | 176 | High Pressure Compressor - Bleed Valves | Forced outage due to compressor bleed valve frozen shut.
TC10 | SF | 13 | 5079 | 2014-01-22 00:45 | 2014-01-22 04:02 | 3.2833 | 3.2833 | 515.4833 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Failed to ignite during startup.
TC10 | U1 | 25 | 5130 | 2014-02-26 02:38 | 2014-02-26 03:45 | 1.1167 | 1.1167 | 196.5333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to 89SS failing to open.
TC10 | [5 empty] | 6.1 | 6.1 | 1011.2167
Z1 | U1 | 2 | 9130 | 2014-01-30 07:00 | 2014-01-31 09:20 | 26.3333 | 26.3333 | 368.6667 |  |  |  | 0 | 14 | 14 | Lack Of Fuel (outside Management Control) | Fuel supply not available.
ZN1 | [5 empty] | 26.3333 | 26.3333 | 368.6667

## FEB-14 Impact By System
Dated: 03/03/14 15:00 hours | [16 empty] | EAF | EUOR | EFOR
Denominator
Unit | Event | Event | Cause | Event | Event | Evt. | Equiv. | MWH | EAF | EUOR | EFOR |  |  |  | Event | Event
Name | Type | No | Code | Start | End | Hrs | Dur Hrs | Lost | Lost | Impact | Impact | GAC | GMC | NMC | Cause | Description | 8163240 | 7889119.6965 | 7609319.473
TC2 | PO | 20 | 360 | 2014-02-08 03:21 | 2014-03-01 | 500.65 | 500.65 | 285370.5 | 3.496% |  |  | 0 | 607 | 570 | Burners | TC2 began the planned outage for the replacement of all 30 burners. This effort i
CR6 | MO | 3 | 1070 | 2014-01-09 20:23 | 2014-01-17 04:37 | 176.2333 | 176.2333 | 42296 | 0.5181% | 0.5361% |  | 0 | 261 | 240 | Reheater Tube Leaks | Boiler Leak Repair - A tube within the RH Pendants was discovered to be cracked,
CR6 | MO | 14 | 4240 | 2014-02-17 15:01 | 2014-02-23 22:51 | 151.8333 | 151.8333 | 36440 | 0.4464% | 0.4619% |  | 0 | 261 | 240 | Lp Turbine Bearings | The #3 and #4 turbine bearings were removed. The #3 was found OK and was polished
GH3 | MO | 3 | 1455 | 2014-01-10 11:31 | 2014-01-13 03:25 | 63.9 | 63.9 | 30799.8 | 0.3773% | 0.3904% |  | 0 | 527 | 482 | 3-2 Induced Draft Fan Trip | Unit derated to minimum load due to 3-2 ID Fan tripping on
BR3 | U1 | 8 | 339 | 2014-01-30 03:57 | 2014-02-01 16:05 | 60.1333 | 60.1333 | 24895.2 | 0.305% | 0.3156% | 0.3272% | 0 | 457 | 414 | Pulverizer System Puff | 3-5 Mill puff causing D corner burner damage and associated boiler tube leak.
TC1 | U1 | 15 | 3344 | 2014-01-14 10:39 | 2014-01-16 22:16 | 59.6167 | 59.6167 | 22833.1833 | 0.2797% | 0.2894% | 0.3001% | 0 | 410 | 383 | Deaerator Heater Head Leak | Leak in the deaerator heater head was discovered. Unit was taken offline to repair
MC1 | MO | 41 | 1488 | 2014-02-18 22:26 | 2014-02-21 22:16 | 71.8333 | 71.8333 | 21765.5 | 0.2666% | 0.2759% |  | 0 | 330 | 303 | Air Heater Dirty | Air Heater Wash
GH3 | MO | 11 | 1455 | 2014-01-30 14:13 | 2014-02-01 09:26 | 43.2167 | 43.2167 | 20830.4333 | 0.2552% | 0.264% |  | 0 | 527 | 482 | Induced Draft Fans OB Bearing | Unit 3 has been running with 3-2 ID Fan OB Fan bearing having periodi
MC2 | MO | 57 | 1050 | 2014-02-15 00:32 | 2014-02-17 22:00 | 69.4667 | 69.4667 | 20770.5333 | 0.2544% | 0.2633% |  | 0 | 330 | 299 | Second Superheater Leaks | Boiler Tube Leak - Second Superheater
GH3 | U1 | 7 | 1040 | 2014-01-25 03:33 | 2014-01-26 19:21 | 39.8 | 39.8 | 19183.6 | 0.235% | 0.2432% | 0.2521% | 0 | 527 | 482 | Superheater Tube Leaks | Unit was taken off line after developing a boiler tube leak in the Prim
GH1 | MO | 6 | 1060 | 2014-02-01 15:04 | 2014-02-03 01:27 | 34.3833 | 34.3833 | 16538.3833 | 0.2026% | 0.2096% |  | 0 | 517 | 481 | First Reheater Leaks | Unit 1 had been running with a tube leak, located around IK #6, for s
GH3 | D1 | 2 | 1455 | 2014-01-08 06:15 | 2014-01-10 11:31 | 53.2667 | 33.0516 | 15930.8774 | 0.1952% | 0.2019% | 0.2094% | 200 | 527 | 482 | 3-2 Induced Draft Fan Out Of Service | Unit running with 3-2 ID fan out of service.
MC2 | MO | 4 | 1000 | 2014-01-02 10:39 | 2014-01-04 11:51 | 49.2 | 49.2 | 14710.8 | 0.1802% | 0.1865% |  | 0 | 330 | 299 | Furnace Wall Tube Leaks | Boiler Tube Leak - Waterwall
GH3 | MO | 9 | 1455 | 2014-01-26 20:47 | 2014-01-27 22:30 | 25.7167 | 25.7167 | 12395.4333 | 0.1518% | 0.1571% |  | 0 | 527 | 482 | 3-2 Induced Draft Fan OB Bearing | Unit was taken off line to replace 3-2 ID Fan OB bearing.
MC2 | MO | 67 | 1000 | 2014-02-24 09:31 | 2014-02-25 19:47 | 34.2667 | 34.2667 | 10245.7333 | 0.1255% | 0.1299% |  | 0 | 330 | 299 | Furnace Wall Leaks | Boiler Tube Leak - Waterwall
GH1 | MO | 12 | 1060 | 2014-02-22 14:49 | 2014-02-23 11:03 | 20.2333 | 20.2333 | 9732.2333 | 0.1192% | 0.1234% |  | 0 | 517 | 481 | First Reheater Leaks | A leak was detected in Reheater pendant section of the boiler. Dispa
BR2 | MO | 15 | 8560 | 2014-02-28 12:26 | 2014-03-02 18:19 | 53.88 | 53.88 | 9051.84 | 0.1109% | 0.1147% |  | 0 | 180 | 168 | Electrostatic Precipitator Problems | Precipitator fields out of service and tube leak repair
BR3 | MO | 4 | 740 | 2014-01-11 10:37 | 2014-01-12 04:08 | 17.5167 | 17.5167 | 7251.9 | 0.08884% | 0.09192% |  | 0 | 457 | 414 | 3-1 Boiler Recirculation Pump Replacement | Replace 3-1 BCWP
CR6 | U2 | 1 | 1070 | 2014-01-03 11:03 | 2014-01-04 17:05 | 30.0333 | 30.0333 | 7208 | 0.0883% | 0.09137% | 0.09473% | 0 | 261 | 240 | Reheater Tube Leaks | Boiler Tube Leak - A tube leak was discovered in the RH Pendants.
CR4 | MO | 9 | 8100 | 2014-02-16 11:30 | 2014-02-18 04:28 | 40.9667 | 40.9667 | 6349.8333 | 0.07779% | 0.08049% |  | 0 | 168 | 155 | Wet Scrubber/absorber Tower Or Module | Flue gas desulfurization module cleaning.
CR5 | U2 | 7 | 1060 | 2014-02-07 10:51 | 2014-02-09 | 37.15 | 37.15 | 6241.2 | 0.07645% | 0.07911% | 0.08202% | 0 | 181 | 168 | First Reheater Leaks | Reheat boiler tube leak - cracked. Total of 6 leaks - 1 dutchman & 4 padwelds.
MC1 | SF | 42 | 4261 | 2014-02-21 22:16 | 2014-02-22 17:58 | 19.7 | 19.7 | 5969.1 | 0.07312% | 0.07566% | 0.07844% | 0 | 330 | 303 | Turbine Control Valves | Turbine #2 & #3 Control Valves - Cleaned Servovalves
BR2 | MO | 11 | 3110 | 2014-02-21 22:13 | 2014-02-23 02:07 | 27.9 | 27.9 | 4687.2 | 0.05742% | 0.05941% |  | 0 | 180 | 168 | Condenser Tube Leaks | Repair condenser tube leak and other misc. issues 6522386
MC2 | SF | 58 | 380 | 2014-02-17 22:00 | 2014-02-18 13:40 | 15.6667 | 15.6667 | 4684.3333 | 0.05738% | 0.05938% | 0.06156% | 0 | 330 | 299 | Light-off (Igniter) Systems | Gas Igniter Issues
GH3 | PD | 17 | 9510 | 2014-02-15 22:00 | 2014-02-16 13:04 | 15.0667 | 9.3488 | 4506.1055 | 0.0552% |  |  | 200 | 527 | 482 | Plant Modific. Strictly For Compliance W/ Reg. Req | KBR electrical tie-in for Bag House and ID fan.
GH3 | U1 | 1 | 1455 | 2014-01-07 21:20 | 2014-01-08 06:15 | 8.9167 | 8.9167 | 4297.8333 | 0.05265% | 0.05448% | 0.05648% | 0 | 527 | 482 | 3-2 Induced Draft Fan OB Bearing | 3-2 ID fan tripped on high vibration on OB fan bearing. This caused
MC2 | U1 | 24 | 4267 | 2014-01-25 22:11 | 2014-01-26 12:32 | 14.35 | 14.35 | 4290.65 | 0.05256% | 0.05439% | 0.05639% | 0 | 330 | 299 | Turbine Control Valve Testing Trip | Turbine Control Valve Test - Trip
TC1 | U1 | 12 | 9900 | 2014-01-11 21:03 | 2014-01-12 07:57 | 10.9 | 10.9 | 4174.7 | 0.05114% | 0.05292% | 0.05486% | 0 | 410 | 383 | Operator Error | During load drop, operator error in valve closing caused the TDBFP main extraction
BR2 | D1 | 13 | 3410 | 2014-02-24 08:24 | 2014-02-26 20:00 | 59.6 | 24.8333 | 4172 | 0.05111% | 0.05288% | 0.05483% | 105 | 180 | 168 | Feedwater Pump OB Bearing | 2-2 BFP OB bearing hot 6546733
CR4 | MO | 11 | 4261 | 2014-02-18 22:14 | 2014-02-20 00:32 | 26.3 | 26.3 | 4076.5 | 0.04994% | 0.05167% |  | 0 | 168 | 155 | Turbine Control Valves | Governor valve sticking at 155 MW. Lubrication issues. CSS cleaned hardened grea
CR5 | SF | 8 | 8560 | 2014-02-09 | 2014-02-10 00:12 | 24.2 | 24.2 | 4065.6 | 0.0498% | 0.05153% | 0.05343% | 0 | 181 | 168 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
MC2 | D1 | 27 | 1850 | 2014-01-26 06:15 | 2014-01-27 08:08 | 25.8833 | 13.3338 | 3986.8177 | 0.04884% | 0.05054% | 0.05239% | 160 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
GR4 | U1 | 27 | 1050 | 2014-02-07 04:42 | 2014-02-08 17:57 | 37.25 | 37.25 | 3650.5 | 0.04472% | 0.04627% | 0.04797% | 0 | 105 | 98 | Second Superheater Leaks | Ops discovered leak in B5 Sec SH Section at 0344, unit was removed from service in
BR3 | D1 | 10 | 3414 | 2014-02-21 22:08 | 2014-02-22 23:58 | 25.8333 | 8.5923 | 3557.1991 | 0.04358% | 0.04509% | 0.04675% | 305 | 457 | 414 | Feedwater Pump Local Controls | 3-2 BFPT LP governor valve indication 6545010
TC2 | NC | 16 | 1190 | 2014-02-01 00:01 | 2014-02-01 06:15 | 6.2333 | 6.2333 | 3553 |  |  |  | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate at 550 MW to conduct boiler OEM recommended deslag. Unit av
GH3 | D1 | 20 | 1400 | 2014-02-18 10:26 | 2014-02-25 04:00 | 161.5667 | 7.0513 | 3398.725 | 0.04163% | 0.04308% | 0.04467% | 504 | 527 | 482 | Forced Draft Fans | FD fans were topping out.
GR3 | U3 | 2 | 1050 | 2014-01-12 21:48 | 2014-01-14 18:35 | 44.7833 | 44.7833 | 3179.6167 | 0.03895% | 0.0403% | 0.04179% | 0 | 75 | 71 | Second Superheater Leaks | GR3 taken out of service due to Sec SH tube leak. Dispatch was notified at 2200
BR2 | D1 | 7 | 310 | 2014-02-16 17:57 | 2014-02-19 12:47 | 66.83 | 18.5639 | 3118.7333 | 0.0382% | 0.03953% | 0.04099% | 130 | 180 | 168 | Pulverizer Mills | Broken coal mill shaft 2-2 mill 6543464
TC2 | D1 | 1 | 3439 | 2014-01-01 | 2014-01-04 02:00 | 74 | 5.2422 | 2988.0395 | 0.0366% | 0.03788% | 0.03927% | 564 | 607 | 570 | High Pressure Heater Head Leaks | 7A FWH is out of service due to a heater head leak and unit derate required until
GR4 | MO | 8 | 1050 | 2014-01-09 10:36 | 2014-01-10 16:22 | 29.7667 | 29.7667 | 2917.1333 | 0.03573% | 0.03698% | 0.03834% | 0 | 105 | 98 | Second Superheater Leaks | GR4 taken O/S in an orderly manner for repair of a tube leak in the DR Sec SH Sect
MC1 | NC | 43 | 1850 | 2014-02-22 17:58 | 2014-02-23 03:16 | 9.3 | 9.3 | 2817.9 |  |  |  | 0 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Warm Start Up
MC4 | D1 | 18 | 1710 | 2014-02-04 14:30 | 2014-02-19 06:00 | 351.5 | 4.6867 | 2277.72 | 0.0279% | 0.02887% | 0.02993% | 518 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issues
MC1 | D1 | 18 | 4261 | 2014-02-01 21:20 | 2014-02-02 08:50 | 11.5 | 7.3182 | 2217.4091 | 0.02716% | 0.02811% | 0.02914% | 120 | 330 | 303 | Turbine Control Valves | Turbine #2 Control Valve - Stuck Closed
MC2 | U1 | 35 | 3149 | 2014-02-01 23:37 | 2014-02-02 06:35 | 6.9667 | 6.9667 | 2083.0333 | 0.02552% | 0.0264% | 0.02737% | 0 | 330 | 299 | Condenser Loss of Vacuum | Condenser Vacuum Trip
TC2 | D1 | 4 | 8000 | 2014-01-11 05:23 | 2014-01-11 19:09 | 13.7667 | 3.3793 | 1926.1993 | 0.0236% | 0.02442% | 0.02531% | 458 | 607 | 570 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup
CR5 | U1 | 10 | 1475 | 2014-02-21 04:01 | 2014-02-21 14:53 | 10.8667 | 10.8667 | 1825.6 | 0.02236% | 0.02314% | 0.02399% | 0 | 181 | 168 | Induced Draft Fan Controls | 5A ID Fan trip - Replaced I/O PCB and batteries in Sigma controller and reset faul
TC2 | D1 | 5 | 8000 | 2014-01-11 19:09 | 2014-01-12 02:45 | 7.6 | 3.0926 | 1762.7743 | 0.02159% | 0.02234% | 0.02317% | 360 | 607 | 570 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup
MC2 | D1 | 26 | 1850 | 2014-01-26 18:32 | 2014-01-27 06:15 | 11.7167 | 5.8583 | 1751.6417 | 0.02146% | 0.0222% | 0.02302% | 165 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC3 | D4 | 36 | 876 | 2014-02-25 20:00 | 2014-02-26 04:28 | 8.4667 | 4.1633 | 1640.3316 | 0.02009% | 0.02079% |  | 215 | 423 | 394 | Soot Blower Controls | Sootblower Regulator - Rebuilt
GH1 | D1 | 8 | 250 | 2014-02-09 16:20 | 2014-02-09 19:43 | 3.3833 | 2.9449 | 1416.4845 | 0.01735% | 0.01795% | 0.01862% | 67 | 517 | 481 | Pulverizer Feeders | 1-4 Feeder belt bound up.
GH3 | D1 | 14 | 9650 | 2014-02-05 15:00 | 2014-02-05 19:50 | 4.8333 | 2.9257 | 1410.1777 | 0.01727% | 0.01787% | 0.01853% | 208 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | SF | 4 | 4609 | 2014-01-13 03:25 | 2014-01-13 06:19 | 2.9 | 2.9 | 1397.8 | 0.01712% | 0.01772% | 0.01837% | 0 | 527 | 482 | Other Exciter Problems | During the previous event, the unit had been rolled up to synchronise spe
BR2 | D1 | 8 | 310 | 2014-02-19 12:47 | 2014-02-20 22:00 | 33.22 | 8.305 | 1395.24 | 0.01709% | 0.01769% | 0.01834% | 135 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
GH3 | D1 | 10 | 1455 | 2014-01-28 11:27 | 2014-01-30 14:13 | 50.7667 | 2.6009 | 1253.6573 | 0.01536% | 0.01589% | 0.01648% | 500 | 527 | 482 | Induced Draft Fans | 3-2 ID Fan IB bearing running 9+ mils vibration. OB fan bearing
MC2 | D1 | 7 | 1850 | 2014-01-05 05:35 | 2014-01-06 01:00 | 19.4167 | 4.1187 | 1231.4874 | 0.01509% | 0.01561% | 0.01618% | 260 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
GR4 | PD | 13 | 345 | 2014-01-11 22:02 | 2014-01-14 13:24 | 63.3667 | 12.0698 | 1182.8444 | 0.01449% |  |  | 85 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
BR2 | D1 | 12 | 310 | 2014-02-23 08:51 | 2014-02-24 08:24 | 23.55 | 6.5417 | 1099 | 0.01346% | 0.01393% | 0.01444% | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
MC3 | D1 | 20 | 250 | 2014-02-07 18:02 | 2014-02-08 05:30 | 11.4667 | 2.6566 | 1046.6925 | 0.01282% | 0.01327% | 0.01376% | 325 | 423 | 394 | Pulverizer Feeders | 3C Coal Feeder - Replace Speed Sensor
TC2 | D1 | 14 | 9610 | 2014-01-20 01:45 | 2014-01-20 16:30 | 14.75 | 1.8286 | 1042.2807 | 0.01277% | 0.01321% | 0.0137% | 531.75 | 607 | 570 | Nox Stack Emissions - Fossil Steam Units | High NOx readings required unit derate to avoid exceedance. Mill configuration ma
GR4 | D1 | 17 | 8551 | 2014-01-13 12:40 | 2014-01-15 08:51 | 44.1833 | 10.5198 | 1030.9444 | 0.01263% | 0.01307% | 0.01355% | 80 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets.
GH3 | D1 | 16 | 9650 | 2014-02-15 11:22 | 2014-02-15 14:52 | 3.5 | 2.0721 | 998.7552 | 0.01223% | 0.01266% | 0.01313% | 215 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
MC2 | D1 | 12 | 1850 | 2014-01-07 12:15 | 2014-01-08 09:50 | 21.5833 | 3.2702 | 977.7904 | 0.01198% | 0.01239% | 0.01285% | 280 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC3 | D1 | 23 | 310 | 2014-02-09 21:52 | 2014-02-10 07:58 | 10.1 | 2.4593 | 968.9792 | 0.01187% | 0.01228% | 0.01273% | 320 | 423 | 394 | Pulverizer Mills | 3C Primary Air Fan Housing InspectionRepair Suction Box & Hot Air Damper Linkage
MC2 | D1 | 6 | 1850 | 2014-01-04 21:11 | 2014-01-05 05:35 | 8.4 | 3.1818 | 951.3636 | 0.01165% | 0.01206% | 0.0125% | 205 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
CR4 | D1 | 8 | 8560 | 2014-02-09 | 2014-02-09 11:42 | 11.7 | 6.1286 | 949.9286 | 0.01164% | 0.01204% | 0.01248% | 80 | 168 | 155 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
TC1 | D1 | 10 | 8000 | 2014-01-11 05:23 | 2014-01-11 19:09 | 13.7667 | 2.4176 | 925.9259 | 0.01134% | 0.01174% | 0.01217% | 338 | 410 | 383 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup
GH4 | U1 | 7 | 250 | 2014-02-09 03:51 | 2014-02-09 05:38 | 1.7833 | 1.7833 | 875.6167 | 0.01073% | 0.0111% | 0.01151% | 0 | 534 | 491 | Pulverizer Feeders | 4-6 Mill Feeder coal inlet plugged causing controls to see this feeder as
CR5 | D4 | 3 | 3416 | 2014-01-24 23:00 | 2014-01-25 07:25 | 8.4167 | 5.1616 | 867.1492 | 0.01062% | 0.01099% |  | 70 | 181 | 168 | Other Feedwater Pump Problems | 51 boiler feed pump maintenance.
MC1 | U1 | 10 | 800 | 2014-01-18 08:33 | 2014-01-18 11:21 | 2.8 | 2.8 | 848.4 | 0.01039% | 0.01075% | 0.01115% | 0 | 330 | 303 | Boiler Drums And Drum Internals | High Drum Level Trip due to Turbine #2 Control Valve Issue, Replaced Fast Acting S
MC4 | D4 | 22 | 8160 | 2014-02-17 20:00 | 2014-02-18 00:24 | 4.4 | 1.6343 | 794.2629 | 0.00973% | 0.01007% |  | 330 | 525 | 486 | Wet Scrubber Mist Eliminators/demisters & Washdown | FGD Demister Wash Line - Relocation
CR6 | D1 | 2 | 310 | 2014-01-05 02:54 | 2014-01-05 19:35 | 16.6833 | 3.26 | 782.3908 | 0.009584% | 0.009917% | 0.01028% | 210 | 261 | 240 | Pulverizer Mills | 6C coal mill roller maintenance.
MC1 | D4 | 5 | 310 | 2014-01-13 22:00 | 2014-01-14 07:17 | 9.2833 | 2.5318 | 767.1409 | 0.009398% | 0.009724% |  | 240 | 330 | 303 | Pulverizer Mills | 1D Coal Mill & Feeder - Inspection
MC2 | D1 | 1 | 250 | 2014-01-01 | 2014-01-01 10:30 | 10.5 | 2.5455 | 761.0909 | 0.009323% | 0.009647% | 0.01% | 250 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Replace Belt
MC4 | D1 | 7 | 250 | 2014-01-08 21:55 | 2014-01-09 05:00 | 7.0833 | 1.5516 | 754.0714 | 0.009237% | 0.009558% | 0.00991% | 410 | 525 | 486 | Pulverizer Feeders | 4A Coal Feeder - VFD Beck Drive Bad Card
MC3 | D4 | 35 | 310 | 2014-02-24 23:00 | 2014-02-25 06:39 | 7.65 | 1.8628 | 733.9298 | 0.008991% | 0.009303% |  | 320 | 423 | 394 | Pulverizer Mills | 3C Coal Mill Pyrite Hopper - Replace Top Gate
BR2 | PD | 9 | 3410 | 2014-02-20 22:00 | 2014-02-21 09:00 | 11 | 4.2778 | 718.6667 | 0.008804% |  |  | 110 | 180 | 168 | Feedwater Pump | Repair 2-2 BFP drain valve 6532228
MC1 | D1 | 40 | 1488 | 2014-02-17 09:00 | 2014-02-18 22:26 | 37.4333 | 2.2687 | 687.4121 | 0.008421% | 0.008713% | 0.009034% | 310 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC2 | D4 | 38 | 310 | 2014-02-02 22:00 | 2014-02-03 06:25 | 8.4167 | 2.2955 | 686.3409 | 0.008408% | 0.0087% |  | 240 | 330 | 299 | Pulverizer Mills | 2A Coal Mill - Inspection
MC2 | D4 | 15 | 250 | 2014-01-09 21:02 | 2014-01-10 04:09 | 7.1167 | 2.2644 | 677.0538 | 0.008294% | 0.008582% |  | 225 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Calibration
GH3 | D1 | 19 | 9650 | 2014-02-17 13:35 | 2014-02-18 10:26 | 20.85 | 1.3847 | 667.4374 | 0.008176% | 0.00846% | 0.008771% | 492 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | H2SO4 out of limit for probe pluggage.
MC2 | D1 | 56 | 1160 | 2014-02-14 11:25 | 2014-02-15 00:32 | 13.1167 | 2.1861 | 653.6472 | 0.008007% | 0.008285% | 0.00859% | 275 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
BR2 | D1 | 10 | 310 | 2014-02-21 09:00 | 2014-02-21 22:13 | 13.22 | 3.6722 | 616.9333 | 0.007557% | 0.00782% | 0.008108% | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
TC1 | D1 | 18 | 280 | 2014-01-17 16:45 | 2014-01-17 19:40 | 2.9167 | 1.5793 | 604.8598 | 0.00741% | 0.007667% | 0.007949% | 188 | 410 | 383 | Pulverizer Fires | Additional fire in the 1D mill after fires in the 1A, 1B, and 1C mills
CR6 | D1 | 9 | 8560 | 2014-02-09 | 2014-02-09 06:50 | 6.8333 | 2.5134 | 603.2184 | 0.007389% | 0.007646% | 0.007927% | 165 | 261 | 240 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
MC1 | D4 | 7 | 250 | 2014-01-15 23:00 | 2014-01-16 06:17 | 7.2833 | 1.9864 | 601.8682 | 0.007373% | 0.007629% |  | 240 | 330 | 303 | Pulverizer Feeders | 1B Coal Feeder - Calibration & Mill Inspection
MC4 | D1 | 9 | 360 | 2014-01-12 02:48 | 2014-01-12 09:33 | 6.75 | 1.2214 | 593.6143 | 0.007272% | 0.007524% | 0.007801% | 430 | 525 | 486 | Burners | 4B Mill - Fire, 4B1 Burner Blanked Off
BR2 | D1 | 6 | 310 | 2014-02-16 06:34 | 2014-02-16 17:57 | 11.3833 | 3.4782 | 584.3444 | 0.007158% | 0.007407% | 0.007679% | 125 | 180 | 168 | Pulverizer Mills | 2-2 mill shaft broken
GH2 | PD | 4 | 344 | 2014-01-17 23:30 | 2014-01-18 11:44 | 12.2333 | 1.1777 | 561.7479 | 0.006881% |  |  | 460 | 509 | 477 | Pulverizer Inspection | 2-6 Mill off for gear box inspection.
CR5 | D4 | 1 | 250 | 2014-01-09 19:40 | 2014-01-10 04:37 | 8.95 | 3.2635 | 548.274 | 0.006716% | 0.00695% |  | 115 | 181 | 168 | Pulverizer Feeders | 5C1 coal feeder repair - changing out a roller bearing.
MC3 | D4 | 4 | 360 | 2014-01-15 03:06 | 2014-01-15 08:13 | 5.1167 | 1.3669 | 538.5443 | 0.006597% | 0.006826% |  | 310 | 423 | 394 | Burners | 3C Mill - Coal Burner Logic Change
GR4 | D1 | 24 | 8551 | 2014-01-24 12:00 | 2014-02-05 11:55 | 287.9167 | 5.4841 | 537.4444 | 0.006584% | 0.006812% | 0.007063% | 103 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded o
BR3 | PD | 9 | 3412 | 2014-02-04 22:00 | 2014-02-05 01:52 | 3.8667 | 1.2438 | 514.9182 | 0.006308% |  |  | 310 | 457 | 414 | Feedwater Pump Drive - Steam Turbine | Collecting 3-2 BFP vibration data
MC1 | D4 | 14 | 250 | 2014-01-20 22:08 | 2014-01-21 04:20 | 6.2 | 1.6909 | 512.3455 | 0.006276% | 0.006494% |  | 240 | 330 | 303 | Pulverizer Feeders | 1A Coal Feeder - Calibration & Mill Inspection
MC1 | D4 | 6 | 310 | 2014-01-14 22:34 | 2014-01-15 04:42 | 6.1333 | 1.6727 | 506.8364 | 0.006209% | 0.006424% |  | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Inspection
MC4 | D1 | 26 | 1710 | 2014-02-21 10:13 | 2014-03-01 | 181.7833 | 1.0388 | 504.8383 | 0.006184% | 0.006399% | 0.006634% | 522 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
MC3 | D1 | 22 | 360 | 2014-02-09 10:50 | 2014-02-09 16:36 | 5.7667 | 1.2678 | 499.5324 | 0.006119% | 0.006332% | 0.006565% | 330 | 423 | 394 | Burners | 3C Mill - 3C10 Coal Burner High Temperature
MC2 | D1 | 37 | 1850 | 2014-02-02 14:15 | 2014-02-02 22:00 | 7.75 | 1.6439 | 491.5379 | 0.006021% | 0.006231% | 0.00646% | 260 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 25 | 310 | 2014-01-26 12:32 | 2014-01-26 18:32 | 6 | 1.6364 | 489.2727 | 0.005994% | 0.006202% | 0.00643% | 240 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Explosion, Ductwork Repair
MC1 | D1 | 23 | 1160 | 2014-02-08 08:27 | 2014-02-08 15:05 | 6.6333 | 1.6081 | 487.2485 | 0.005969% | 0.006176% | 0.006403% | 250 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC4 | D4 | 16 | 310 | 2014-02-02 23:00 | 2014-02-03 03:55 | 4.9167 | 0.98333 | 477.9 | 0.005854% | 0.006058% |  | 420 | 525 | 486 | Pulverizer Mills | 4C Coal Mill - Inspection
MC3 | D1 | 13 | 300 | 2014-01-23 17:19 | 2014-01-23 23:03 | 5.7333 | 1.1928 | 469.9436 | 0.005757% | 0.005957% | 0.006176% | 335 | 423 | 394 | Pulverizer Motors and Drives | 3C Coal Mill Motor - Failed to Start, Breaker Issue
MC2 | D4 | 42 | 310 | 2014-02-04 23:00 | 2014-02-05 04:45 | 5.75 | 1.5682 | 468.8864 | 0.005744% | 0.005943% |  | 240 | 330 | 299 | Pulverizer Mills | 2B Coal Mill - Inspection
CR5 | U1 | 2 | 1470 | 2014-01-11 19:43 | 2014-01-11 22:26 | 2.7167 | 2.7167 | 456.4 | 0.005591% | 0.005785% | 0.005998% | 0 | 181 | 168 | Induced Draft Fan Motors and Drives | 5A induced draft fan tripped due to bad thyrister card causing unit to trip.
MC3 | D4 | 24 | 250 | 2014-02-10 11:00 | 2014-02-10 16:05 | 5.0833 | 1.1176 | 440.3392 | 0.005394% | 0.005582% |  | 330 | 423 | 394 | Pulverizer Feeders | 3C Coal Feeder - Calibration
GH4 | MO | 3 | 1000 | 2014-01-01 | 2014-01-01 00:53 | 0.88333 | 0.88333 | 433.7167 | 0.005313% | 0.005498% |  | 0 | 534 | 491 | Furnace Wall Leaks | Unit 4 developed a tube leak on 8 2/3 floor on the south side of the
MC1 | D4 | 8 | 250 | 2014-01-16 23:00 | 2014-01-17 04:14 | 5.2333 | 1.4273 | 432.4636 | 0.005298% | 0.005482% |  | 240 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Calibration & Mill Inspection
MC4 | D1 | 15 | 310 | 2014-01-30 02:30 | 2014-01-30 06:55 | 4.4167 | 0.88333 | 429.3 | 0.005259% | 0.005442% | 0.005642% | 420 | 525 | 486 | Pulverizer Mills | 4E Coal Mill - Primary Air Fan Flow Issues
GH3 | D1 | 8 | 1455 | 2014-01-26 19:21 | 2014-01-26 20:47 | 1.4333 | 0.88937 | 428.6782 | 0.005251% | 0.005434% | 0.005634% | 200 | 527 | 482 | Induced Draft Fans | Load Reduction #4Unit 3 was derated during startup when 3-2 ID Fan OB bearing fail
MC2 | D4 | 41 | 310 | 2014-02-03 23:00 | 2014-02-04 04:15 | 5.25 | 1.4318 | 428.1136 | 0.005244% | 0.005427% |  | 240 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Adjust Rollers & Inspection
MC1 | D4 | 34 | 310 | 2014-02-13 22:00 | 2014-02-14 03:00 | 5 | 1.3636 | 413.1818 | 0.005061% | 0.005237% |  | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Inspection
MC3 | D4 | 28 | 8160 | 2014-02-17 20:00 | 2014-02-18 00:46 | 4.7667 | 1.048 | 412.9083 | 0.005058% | 0.005234% |  | 330 | 423 | 394 | Wet Scrubber Mist Eliminators/demisters & Washdown | FGD Demister Wash Line - Relocation
GH1 | PD | 9 | 250 | 2014-02-10 09:00 | 2014-02-10 15:33 | 6.55 | 0.84884 | 408.2918 | 0.005002% |  |  | 450 | 517 | 481 | Pulverizer Feeders | 1-4 Mill off to replace feeder discharge pipe pluggage detector.
MC4 | D1 | 17 | 360 | 2014-02-03 03:55 | 2014-02-03 06:08 | 2.2167 | 0.82333 | 400.14 | 0.004902% | 0.005072% | 0.005259% | 330 | 525 | 486 | Burners | 4B Mill - 4B3 Coal Burner High Temperature4C Coal Mill - Inspection
MC4 | D1 | 4 | 380 | 2014-01-06 06:40 | 2014-01-06 08:55 | 2.25 | 0.79286 | 385.3286 | 0.00472% | 0.004884% | 0.005064% | 340 | 525 | 486 | Light-off (Igniter) Systems (Including Fuel Supply) | 4B & 4C Mills - Gas Igniter Issues
GH2 | D1 | 11 | 340 | 2014-02-17 06:24 | 2014-02-17 14:00 | 7.6 | 0.80629 | 384.5988 | 0.004711% | 0.004875% | 0.005054% | 455 | 509 | 477 | Other Pulverizer Problems | Removed 2-4 Mill from service for journal issue.
MC2 | D1 | 8 | 1850 | 2014-01-06 01:00 | 2014-01-06 09:28 | 8.4667 | 1.2828 | 383.5657 | 0.004699% | 0.004862% | 0.005041% | 280 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D4 | 20 | 310 | 2014-01-19 23:30 | 2014-01-20 04:26 | 4.9333 | 1.2707 | 379.9414 | 0.004654% | 0.004816% |  | 245 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Inspection
CR4 | D4 | 4 | 255 | 2014-01-19 21:00 | 2014-01-20 06:24 | 9.4 | 2.406 | 372.9226 | 0.004568% | 0.004727% |  | 125 | 168 | 155 | Pulverizer Feeder Coal Scales | 4C2 Feeder Belt Repair
TC1 | D1 | 11 | 8000 | 2014-01-11 19:09 | 2014-01-11 21:03 | 1.9 | 0.94537 | 362.0751 | 0.004435% | 0.00459% | 0.004758% | 206 | 410 | 383 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup
MC2 | D1 | 48 | 1160 | 2014-02-08 05:30 | 2014-02-08 07:35 | 2.0833 | 1.1995 | 358.649 | 0.004393% | 0.004546% | 0.004713% | 140 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC3 | D4 | 12 | 360 | 2014-01-20 21:00 | 2014-01-21 00:55 | 3.9167 | 0.90741 | 357.5185 | 0.00438% | 0.004532% |  | 325 | 423 | 394 | Burners | 3A & 3D Mills - Coal Burner Logic Change Over
GH1 | D1 | 5 | 250 | 2014-01-28 21:25 | 2014-01-29 04:05 | 6.6667 | 0.73501 | 353.5397 | 0.004331% | 0.004481% | 0.004646% | 460 | 517 | 481 | Pulverizer Feeders | 1-4 Feeder belt was torn when cleanout conveyor failed.
MC4 | D1 | 5 | 380 | 2014-01-06 08:55 | 2014-01-06 12:30 | 3.5833 | 0.71667 | 348.3 | 0.004267% | 0.004415% | 0.004577% | 420 | 525 | 486 | Light-off (Igniter) Systems (Including Fuel Supply) | 4C Mill - Gas Vent Valve Stuck Open
CR6 | D1 | 12 | 250 | 2014-02-16 04:54 | 2014-02-16 12:17 | 7.3833 | 1.4427 | 346.2529 | 0.004242% | 0.004389% | 0.00455% | 210 | 261 | 240 | Pulverizer Feeders | 6B feeder belt torn. Repaired & put back in service.
GH2 | D1 | 12 | 250 | 2014-02-19 05:20 | 2014-02-19 11:30 | 6.1667 | 0.7148 | 340.9597 | 0.004177% | 0.004322% | 0.004481% | 450 | 509 | 477 | Pulverizer Feeders | 2-6 Feeder off to replace the belt.
MC4 | D1 | 1 | 360 | 2014-01-01 | 2014-01-01 03:30 | 3.5 | 0.7 | 340.2 | 0.004167% | 0.004312% | 0.004471% | 420 | 525 | 486 | Burners | 4C Mill - 4C7 & 4C9 Burners High Temperature
MC2 | D4 | 16 | 250 | 2014-01-13 00:35 | 2014-01-13 05:00 | 4.4167 | 1.1376 | 340.1503 | 0.004167% | 0.004312% |  | 245 | 330 | 299 | Pulverizer Feeders | 2D Coal Feeder - Calibration
MC1 | D4 | 48 | 310 | 2014-02-27 22:00 | 2014-02-28 02:02 | 4.0333 | 1.1 | 333.3 | 0.004083% | 0.004225% |  | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Inspection & Adjust Rollers
GR4 | D1 | 26 | 338 | 2014-02-04 22:14 | 2014-02-05 11:55 | 13.6833 | 3.2579 | 319.2778 | 0.003911% | 0.004047% | 0.004196% | 80 | 105 | 98 | Pulverizer Control Systems (Temp and Pressure) | 5-3 PA Fan control jack would not react to input from PA Controller.
CR5 | D4 | 6 | 344 | 2014-02-04 23:00 | 2014-02-05 05:00 | 6 | 1.8564 | 311.8674 | 0.00382% | 0.003953% |  | 125 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
BR3 | PD | 2 | 310 | 2014-01-09 21:20 | 2014-01-10 00:33 | 3.2167 | 0.75314 | 311.7985 | 0.00382% | 0.003952% | 0.004098% | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
CR4 | D4 | 13 | 310 | 2014-02-28 22:00 | 2014-03-01 06:51 | 8.85 | 2.0018 | 310.2768 | 0.003801% | 0.003933% |  | 130 | 168 | 155 | Pulverizer Mills | 4A Mill inspection
TC2 | D1 | 6 | 8650 | 2014-01-17 19:30 | 2014-01-17 22:15 | 2.75 | 0.54366 | 309.8847 | 0.003796% | 0.003928% | 0.004072% | 487 | 607 | 570 | Baghouse Systems - General | The bags in the baghouse are deteriorating ... holes in the bags
MC2 | D1 | 29 | 310 | 2014-01-27 09:55 | 2014-01-27 13:56 | 4.0167 | 1.0346 | 309.3442 | 0.003789% | 0.003921% | 0.004065% | 245 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Ductwork Repair
GH2 | D1 | 10 | 250 | 2014-02-15 03:20 | 2014-02-15 10:00 | 6.6667 | 0.64178 | 306.1297 | 0.00375% | 0.00388% | 0.004023% | 460 | 509 | 477 | Pulverizer Feeders | 2-1 Feeder control issue.
MC2 | D1 | 60 | 1850 | 2014-02-18 22:15 | 2014-02-19 02:00 | 3.75 | 1.0227 | 305.7955 | 0.003746% | 0.003876% | 0.004019% | 240 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
CR5 | D4 | 4 | 344 | 2014-02-02 23:00 | 2014-02-03 04:50 | 5.8333 | 1.8048 | 303.2044 | 0.003714% | 0.003843% | 0.003985% | 125 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
GH2 | D1 | 13 | 344 | 2014-02-24 23:55 | 2014-02-25 06:30 | 6.5833 | 0.63376 | 302.303 | 0.003703% | 0.003832% | 0.003973% | 460 | 509 | 477 | Pulverizer Inspection | 2-6 Mill off to inspect the grinding section.
MC1 | D4 | 4 | 310 | 2014-01-09 21:26 | 2014-01-10 01:17 | 3.85 | 0.99167 | 300.475 | 0.003681% | 0.003809% |  | 245 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Roller Adjustment
GH3 | D1 | 22 | 250 | 2014-02-20 13:50 | 2014-02-20 16:25 | 2.5833 | 0.62255 | 300.0686 | 0.003676% | 0.003804% | 0.003943% | 400 | 527 | 482 | Pulverizer Feeders | 3-3 Feeder controls.
MC1 | D1 | 9 | 4261 | 2014-01-17 21:42 | 2014-01-18 08:33 | 10.85 | 0.98636 | 298.8682 | 0.003661% | 0.003788% | 0.003928% | 300 | 330 | 303 | Turbine Control Valves | Turbine #2 Control Valve - Would Not Open during Valve Test
GH1 | D1 | 4 | 344 | 2014-01-27 06:00 | 2014-01-27 11:33 | 5.55 | 0.6119 | 294.3218 | 0.003605% | 0.003731% | 0.003868% | 460 | 517 | 481 | Pulverizer Inspection | 1-6 Mill off to inspect grinding section.
BR3 | PD | 6 | 310 | 2014-01-14 21:35 | 2014-01-15 00:37 | 3.0333 | 0.71021 | 294.0276 | 0.003602% |  |  | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
BR2 | D1 | 4 | 310 | 2014-02-11 20:04 | 2014-02-12 02:17 | 6.2167 | 1.7269 | 290.1111 | 0.003554% | 0.003677% | 0.003813% | 130 | 180 | 168 | Pulverizer Mills | 2-4 mill west door broken spring bolt
MC2 | D1 | 14 | 1850 | 2014-01-08 12:15 | 2014-01-09 09:35 | 21.3333 | 0.9697 | 289.9394 | 0.003552% | 0.003675% | 0.00381% | 315 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
GH4 | PD | 6 | 3416 | 2014-02-08 23:00 | 2014-02-09 00:20 | 1.3333 | 0.58427 | 286.8764 | 0.003514% |  |  | 300 | 534 | 491 | Other Feedwater Pump Problems | Planned derate to inspect 4-2 BFP leak. Derate was planned with
MC3 | D1 | 32 | 360 | 2014-02-22 14:45 | 2014-02-22 16:15 | 1.5 | 0.71986 | 283.6241 | 0.003474% | 0.003595% | 0.003727% | 220 | 423 | 394 | Burners | 3D Mill - 3D1 Coal Burner High Temperature3B Mill - 3B7 Coal Burner Fire
GH3 | D1 | 15 | 9650 | 2014-02-15 04:41 | 2014-02-15 07:07 | 2.4333 | 0.5864 | 282.6453 | 0.003462% | 0.003583% | 0.003714% | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
CR5 | D4 | 5 | 344 | 2014-02-03 23:00 | 2014-02-04 04:55 | 5.9167 | 1.6671 | 280.0773 | 0.003431% | 0.00355% |  | 130 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
CR4 | D1 | 3 | 250 | 2014-01-09 19:11 | 2014-01-10 02:13 | 7.0333 | 1.8002 | 279.0308 | 0.003418% | 0.003537% | 0.003667% | 125 | 168 | 155 | Pulverizer Feeders | 4A feeder belt broke. Repaired same.
GR4 | D1 | 15 | 8551 | 2014-01-12 00:59 | 2014-01-12 12:30 | 11.5167 | 2.7421 | 268.7222 | 0.003292% | 0.003406% | 0.003531% | 80 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets.
MC1 | D4 | 21 | 250 | 2014-02-06 | 2014-02-06 03:12 | 3.2 | 0.87273 | 264.4364 | 0.003239% | 0.003352% |  | 240 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Repair Discharge Flapper
BR3 | PD | 7 | 310 | 2014-01-15 21:57 | 2014-01-16 00:40 | 2.7167 | 0.63607 | 263.3324 | 0.003226% |  |  | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
MC4 | D1 | 24 | 1710 | 2014-02-19 17:42 | 2014-02-21 10:13 | 40.5167 | 0.54022 | 262.548 | 0.003216% | 0.003328% | 0.00345% | 518 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
BR3 | PD | 1 | 310 | 2014-01-08 22:33 | 2014-01-09 01:15 | 2.7 | 0.63217 | 261.7168 | 0.003206% |  |  | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
BR3 | D1 | 12 | 3414 | 2014-02-25 05:51 | 2014-02-25 07:39 | 1.8 | 0.61838 | 256.0096 | 0.003136% | 0.003245% | 0.003364% | 300 | 457 | 414 | Feedwater Pump Local Controls | 3-2 BFP LP gov. servo problems 6546920
GR4 | D1 | 23 | 8551 | 2014-01-20 18:30 | 2014-01-24 12:00 | 89.5 | 2.5571 | 250.6 | 0.00307% | 0.003177% | 0.003293% | 102 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded o
GR4 | PD | 12 | 345 | 2014-01-11 06:15 | 2014-01-11 22:02 | 15.7833 | 2.5554 | 250.4289 | 0.003068% |  |  | 88 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
GH1 | D1 | 11 | 344 | 2014-02-21 08:30 | 2014-02-21 12:30 | 4 | 0.51838 | 249.3385 | 0.003054% | 0.003161% | 0.003277% | 450 | 517 | 481 | Pulverizer Inspection | 1-6 Mill off to inspect grinding section.
GH2 | PD | 2 | 344 | 2014-01-14 23:43 | 2014-01-15 04:11 | 4.4667 | 0.51775 | 246.9654 | 0.003025% |  |  | 450 | 509 | 477 | Pulverizer Inspection | 2-6 Mill off to inspect and repair spring can shaft.
MC1 | D1 | 39 | 1488 | 2014-02-16 06:20 | 2014-02-17 09:00 | 26.6667 | 0.80808 | 244.8485 | 0.002999% | 0.003104% | 0.003218% | 320 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
BR3 | PD | 5 | 310 | 2014-01-13 22:00 | 2014-01-14 00:29 | 2.4833 | 0.58144 | 240.7149 | 0.002949% |  |  | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
MC1 | D1 | 37 | 250 | 2014-02-14 06:50 | 2014-02-14 12:00 | 5.1667 | 0.78283 | 237.197 | 0.002906% | 0.003007% | 0.003117% | 280 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor GearboxGas Guns in Service
MC3 | D1 | 2 | 360 | 2014-01-05 23:16 | 2014-01-06 02:00 | 2.7333 | 0.60095 | 236.7726 | 0.0029% | 0.003001% | 0.003112% | 330 | 423 | 394 | Burners | 3A Mill - Burners High Temperature
CR4 | D4 | 5 | 344 | 2014-01-20 09:52 | 2014-01-20 16:35 | 6.7167 | 1.5192 | 235.4831 | 0.002885% | 0.002985% |  | 130 | 168 | 155 | Pulverizer Inspection | 4C mill making noise - made roller adjustment after removing debris buildup on journal
TC2 | D1 | 17 | 310 | 2014-02-02 16:30 | 2014-02-02 19:00 | 2.5 | 0.40259 | 229.479 | 0.002811% | 0.002909% | 0.003016% | 509.25 | 607 | 570 | Pulverizer Mills | The 2D mill was performing poorly and was taken off-line to investigate. Some mil
MC2 | D1 | 28 | 1850 | 2014-01-27 08:08 | 2014-01-27 09:55 | 1.7833 | 0.75657 | 226.2131 | 0.002771% | 0.002867% | 0.002973% | 190 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
CR6 | D1 | 11 | 4240 | 2014-02-11 08:00 | 2014-02-11 14:00 | 6 | 0.94253 | 226.2069 | 0.002771% | 0.002867% | 0.002973% | 220 | 261 | 240 | Lp Turbine Bearings | #4 Turbine bearing temperature running high.
MC2 | D1 | 32 | 310 | 2014-01-27 16:39 | 2014-01-27 20:39 | 4 | 0.72727 | 217.4545 | 0.002664% | 0.002756% | 0.002858% | 270 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Ductwork Repair
MC3 | D4 | 1 | 310 | 2014-01-01 23:20 | 2014-01-02 01:35 | 2.25 | 0.54787 | 215.8617 | 0.002644% | 0.002736% |  | 320 | 423 | 394 | Pulverizer Mills | 3A Coal Mill - Inspection
GH2 | D1 | 14 | 280 | 2014-02-27 07:34 | 2014-02-27 12:11 | 4.6167 | 0.44443 | 211.9948 | 0.002597% | 0.002687% | 0.002786% | 460 | 509 | 477 | Pulverizer Fires | Load was reduced due to a fire in 2-1 Mill.
BR2 | PD | 1 | 310 | 2014-01-02 22:00 | 2014-01-03 02:00 | 4 | 1.2222 | 205.3333 | 0.002515% |  |  | 125 | 180 | 168 | Pulverizer Mills | Inspect 2-3 mill gearbox
CR6 | D1 | 6 | 344 | 2014-01-20 13:08 | 2014-01-20 18:00 | 4.8667 | 0.7645 | 183.4789 | 0.002248% | 0.002326% | 0.002411% | 220 | 261 | 240 | Pulverizer Inspection | 6D coal mill making noise. Removed metal from journal shield area of mill.
GH3 | D1 | 6 | 9290 | 2014-01-24 23:19 | 2014-01-25 03:33 | 4.2333 | 0.37755 | 181.9771 | 0.002229% | 0.002307% | 0.002392% | 480 | 527 | 482 | Other Fuel Quality Problems | Load Reduction #3Derate was reported as a coal quality issue. Actually, we were b
TC2 | D1 | 8 | 9620 | 2014-01-18 11:25 | 2014-01-18 14:00 | 2.5833 | 0.31919 | 181.9399 | 0.002229% | 0.002306% | 0.002391% | 532 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | High particulate matter readings required derate to avoid an exceedance.
TC1 | D1 | 7 | 590 | 2014-01-08 12:00 | 2014-01-08 17:26 | 5.4333 | 0.46382 | 177.6435 | 0.002176% | 0.002252% | 0.002335% | 375 | 410 | 383 | Desuperheater/Attemperator Valves | The SH Spray control valve was leaking and required a unit derate to accomplish th
TC2 | D1 | 12 | 9620 | 2014-01-19 10:29 | 2014-01-19 13:00 | 2.5167 | 0.31096 | 177.2446 | 0.002171% | 0.002247% | 0.002329% | 532 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | High particulate readings required unit derate to avoid an exceedance
GH1 | PD | 13 | 344 | 2014-02-24 13:42 | 2014-02-24 16:59 | 3.2833 | 0.36199 | 174.1183 | 0.002133% |  |  | 460 | 517 | 481 | Pulverizer Inspection | 1-1 Mill off to inspect grinding section.
MC1 | D1 | 35 | 250 | 2014-02-14 03:00 | 2014-02-14 05:05 | 2.0833 | 0.56818 | 172.1591 | 0.002109% | 0.002182% | 0.002262% | 240 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor Gearbox
MC3 | D1 | 31 | 360 | 2014-02-22 09:20 | 2014-02-22 11:18 | 1.9667 | 0.43239 | 170.3608 | 0.002087% | 0.002159% | 0.002239% | 330 | 423 | 394 | Burners | 3C Mill - 3C3 Coal Burner High Temperature
TC2 | D1 | 13 | 9620 | 2014-01-19 17:50 | 2014-01-19 20:15 | 2.4167 | 0.2986 | 170.2018 | 0.002085% | 0.002157% | 0.002237% | 532 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | High particulate readings required unit derate to avoid an exceedance
MC3 | D1 | 14 | 360 | 2014-01-23 22:08 | 2014-01-23 23:03 | 0.91667 | 0.42908 | 169.0567 | 0.002071% | 0.002143% | 0.002222% | 225 | 423 | 394 | Burners | 3D Mill - 3D7 Coal Burner High Temperature
TC2 | D1 | 7 | 8650 | 2014-01-18 04:15 | 2014-01-18 05:45 | 1.5 | 0.29654 | 169.028 | 0.002071% | 0.002143% | 0.002221% | 487 | 607 | 570 | Baghouse Systems - General | The bags in the baghouse are deteriorating ... holes in the bags
CR6 | U1 | 4 | 1700 | 2014-01-17 06:00 | 2014-01-17 06:42 | 0.7 | 0.7 | 168 | 0.002058% | 0.00213% | 0.002208% | 0 | 261 | 240 | Feedwater Controls | Low drum level - high boiler pressure
MC1 | D1 | 31 | 1488 | 2014-02-12 22:45 | 2014-02-13 07:26 | 8.6833 | 0.52626 | 159.4576 | 0.001953% | 0.002021% | 0.002096% | 310 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC2 | D1 | 22 | 250 | 2014-01-24 05:33 | 2014-01-24 07:30 | 1.95 | 0.53182 | 159.0136 | 0.001948% | 0.002016% | 0.00209% | 240 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Plugged, Frozen Coal
MC4 | D1 | 27 | 4460 | 2014-02-23 04:00 | 2014-02-23 04:33 | 0.55 | 0.31952 | 155.2886 | 0.001902% | 0.001968% | 0.002041% | 220 | 525 | 486 | Turbine Overspeed Trip Test | Turbine Overspeed Test - Linkage Stuck
MC2 | D1 | 44 | 250 | 2014-02-05 05:48 | 2014-02-05 07:56 | 2.1333 | 0.51717 | 154.6343 | 0.001894% | 0.00196% | 0.002032% | 250 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Wet Coal
BR1 | PD | 3 | 310 | 2014-02-20 22:00 | 2014-02-21 03:39 | 5.65 | 1.4373 | 153.789 | 0.001884% |  |  | 85 | 114 | 107 | Pulverizer Mills | 1-3 mill inspection
MC2 | D1 | 49 | 1160 | 2014-02-08 07:35 | 2014-02-08 09:28 | 1.8833 | 0.51364 | 153.5773 | 0.001881% | 0.001947% | 0.002018% | 240 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
GH1 | PD | 2 | 344 | 2014-01-14 23:37 | 2014-01-15 02:30 | 2.8833 | 0.31789 | 152.9059 | 0.001873% |  |  | 460 | 517 | 481 | Pulverizer Inspection | 1-6 Mill off to inspect and clean air flow transmitters.
BR2 | PD | 3 | 344 | 2014-01-13 09:44 | 2014-01-13 12:15 | 2.5167 | 0.9088 | 152.6778 | 0.00187% |  |  | 115 | 180 | 168 | Pulverizer Inspection | Inspect 2-3 mill concerning thrust bearing issue
GH1 | PD | 3 | 340 | 2014-01-16 21:57 | 2014-01-17 00:49 | 2.8667 | 0.31605 | 152.0221 | 0.001862% |  |  | 460 | 517 | 481 | Other Pulverizer Problems | 1-1 Mill journal replacement.
CR6 | D4 | 5 | 344 | 2014-01-20 07:54 | 2014-01-20 11:54 | 4 | 0.62835 | 150.8046 | 0.001847% | 0.001912% |  | 220 | 261 | 240 | Pulverizer Inspection | 6A coal mill making noise. Removed a piece of metal from journal shield area of mill
GH2 | PD | 8 | 340 | 2014-02-13 23:00 | 2014-02-14 02:11 | 3.1833 | 0.30645 | 146.1769 | 0.001791% |  |  | 460 | 509 | 477 | Other Pulverizer Problems | 2-5 Mill off to replace pyrite scraper.
TC1 | D1 | 6 | 280 | 2014-01-07 17:25 | 2014-01-07 21:08 | 3.7167 | 0.38073 | 145.8202 | 0.001786% | 0.001848% | 0.001916% | 368 | 410 | 383 | Pulverizer Fires | Derate required due to A & B coal mill fires.
MC2 | D1 | 70 | 1850 | 2014-02-26 11:21 | 2014-02-26 15:29 | 4.1333 | 0.46343 | 138.5669 | 0.001697% | 0.001756% | 0.001821% | 293 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | D1 | 27 | 1488 | 2014-02-11 10:00 | 2014-02-12 10:30 | 24.5 | 0.44545 | 134.9727 | 0.001653% | 0.001711% | 0.001774% | 324 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
GH3 | D1 | 13 | 9650 | 2014-02-05 14:10 | 2014-02-05 15:00 | 0.83333 | 0.27989 | 134.9051 | 0.001653% | 0.00171% | 0.001773% | 350 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
CR4 | D1 | 10 | 4261 | 2014-02-18 11:05 | 2014-02-18 22:14 | 11.15 | 0.8628 | 133.7336 | 0.001638% | 0.001695% | 0.001757% | 155 | 168 | 155 | Turbine Control Valves | Governor valve sticking at 155 MW. Lubrication issues.
GR4 | D1 | 6 | 310 | 2014-01-08 09:10 | 2014-01-08 13:30 | 4.3333 | 1.3619 | 133.4667 | 0.001635% | 0.001692% | 0.001754% | 72 | 105 | 98 | Pulverizer Mills | A Sluice Water line on the Conveyor Floor had frozen and burst. When it thawed it
BR1 | PD | 2 | 310 | 2014-02-19 22:00 | 2014-02-20 02:51 | 4.85 | 1.2338 | 132.0136 | 0.001617% |  |  | 85 | 114 | 107 | Pulverizer Mills | 1-1 & 1-4 mill inspection
TC1 | D1 | 28 | 310 | 2014-02-10 10:00 | 2014-02-10 13:58 | 3.9667 | 0.33862 | 129.6907 | 0.001589% | 0.001644% | 0.001704% | 375 | 410 | 383 | Pulverizer Mills | Derate required due to fire on the 1D coal mill.
GH2 | D1 | 3 | 9650 | 2014-01-15 19:30 | 2014-01-15 21:03 | 1.55 | 0.27102 | 129.2773 | 0.001584% | 0.001639% | 0.001699% | 420 | 509 | 477 | Other Stack Or Exhaust Emissions -fossil Stm Unit | H2SO4 in high alarm. Dropped load to investigate. Blower for ou
MC1 | D1 | 36 | 250 | 2014-02-14 05:05 | 2014-02-14 06:50 | 1.75 | 0.42424 | 128.5455 | 0.001575% | 0.001629% | 0.001689% | 250 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor Gearbox
TC1 | D1 | 13 | 280 | 2014-01-13 06:39 | 2014-01-13 10:33 | 3.9 | 0.33293 | 127.511 | 0.001562% | 0.001616% | 0.001676% | 375 | 410 | 383 | Pulverizer Fires | Unit derate due to two coal mill issues: 1E mill had a fire that needed to be put out
TC1 | D1 | 5 | 280 | 2014-01-04 05:09 | 2014-01-04 08:18 | 3.15 | 0.33037 | 126.5301 | 0.00155% | 0.001604% | 0.001663% | 367 | 410 | 383 | Pulverizer Fires | Derate due to fires in the D coal mill and the E coal mill was unavailable for a m
GR3 | U1 | 13 | 580 | 2014-02-22 23:25 | 2014-02-23 01:09 | 1.7333 | 1.7333 | 123.0667 | 0.001508% | 0.00156% | 0.001617% | 0 | 75 | 71 | Desuperheater/Attemperator Piping | While GR3 was off line on Reserve, Ops discovered a leak in B4 Attemperator supply
MC2 | D1 | 61 | 1850 | 2014-02-19 02:00 | 2014-02-19 04:15 | 2.25 | 0.40909 | 122.3182 | 0.001498% | 0.00155% | 0.001607% | 270 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 11 | 250 | 2014-01-07 05:45 | 2014-01-07 07:15 | 1.5 | 0.40909 | 122.3182 | 0.001498% | 0.00155% | 0.001607% | 240 | 330 | 299 | Pulverizer Feeders | 2A Coal Feeder - Plugged, Frozen/Wet Coal
MC1 | D1 | 20 | 250 | 2014-02-05 07:28 | 2014-02-05 09:30 | 2.0333 | 0.40051 | 121.353 | 0.001487% | 0.001538% | 0.001595% | 265 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Wet Coal
GH4 | D1 | 5 | 9650 | 2014-02-03 00:50 | 2014-02-03 01:48 | 0.96667 | 0.24257 | 119.1027 | 0.001459% | 0.00151% | 0.001565% | 400 | 534 | 491 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
MC2 | D1 | 64 | 1850 | 2014-02-19 08:50 | 2014-02-19 21:41 | 12.85 | 0.38939 | 116.4288 | 0.001426% | 0.001476% | 0.00153% | 320 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC3 | D1 | 21 | 360 | 2014-02-09 09:05 | 2014-02-09 10:25 | 1.3333 | 0.29314 | 115.4988 | 0.001415% | 0.001464% | 0.001518% | 330 | 423 | 394 | Burners | 3C Mill - 3C3 Coal Burner High Temperature
MC3 | D1 | 29 | 360 | 2014-02-21 14:09 | 2014-02-21 15:29 | 1.3333 | 0.29314 | 115.4988 | 0.001415% | 0.001464% | 0.001518% | 330 | 423 | 394 | Burners | 3D Mill - 3D1 Coal Burner High Temperature
CR4 | D1 | 1 | 8280 | 2014-01-07 21:20 | 2014-01-07 23:43 | 2.3833 | 0.7377 | 114.3433 | 0.001401% | 0.001449% | 0.001503% | 116 | 168 | 155 | Wet Scrubber - Reagent Feed Piping | Reactive feed line from supply pump frozen.
MC1 | D1 | 30 | 1488 | 2014-02-12 10:30 | 2014-02-12 22:45 | 12.25 | 0.37121 | 112.4773 | 0.001378% | 0.001426% | 0.001478% | 320 | 330 | 303 | Air Heater (Regenerative) | 1A Air heater - High Differential
MC2 | D1 | 62 | 1850 | 2014-02-19 04:15 | 2014-02-19 07:00 | 2.75 | 0.375 | 112.125 | 0.001374% | 0.001421% | 0.001474% | 285 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | D1 | 17 | 250 | 2014-01-24 07:43 | 2014-01-24 09:04 | 1.35 | 0.36818 | 111.5591 | 0.001367% | 0.001414% | 0.001466% | 240 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen Coal
MC1 | D1 | 1 | 8280 | 2014-01-07 07:15 | 2014-01-07 08:58 | 1.7167 | 0.36414 | 110.3348 | 0.001352% | 0.001399% | 0.00145% | 260 | 330 | 303 | Wet Scrubber - Reagent Feed Piping | FGD Reactant Feed Line - Leak
GH2 | PD | 7 | 344 | 2014-02-06 23:00 | 2014-02-07 01:24 | 2.4 | 0.23104 | 110.2067 | 0.00135% |  |  | 460 | 509 | 477 | Pulverizer Inspection | 2-2 Mill was removed from service to inspect due to high differen
MC2 | D1 | 21 | 250 | 2014-01-23 22:08 | 2014-01-23 23:28 | 1.3333 | 0.36364 | 108.7273 | 0.001332% | 0.001378% | 0.001429% | 240 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Plugged, Frozen Coal
MC3 | D4 | 10 | 310 | 2014-01-17 04:00 | 2014-01-17 05:15 | 1.25 | 0.27482 | 108.2801 | 0.001326% | 0.001373% |  | 330 | 423 | 394 | Pulverizer Mills | 3B Mill - Coal Burner Logic Change
MC1 | D1 | 38 | 1488 | 2014-02-15 06:54 | 2014-02-16 06:20 | 23.4333 | 0.35505 | 107.5803 | 0.001318% | 0.001364% | 0.001414% | 325 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC2 | D1 | 30 | 310 | 2014-01-27 13:56 | 2014-01-27 15:52 | 1.9333 | 0.35152 | 105.103 | 0.001288% | 0.001332% | 0.001381% | 270 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Ductwork Repair
BR2 | D1 | 2 | 310 | 2014-01-11 18:55 | 2014-01-11 21:25 | 2.5 | 0.625 | 105 | 0.001286% | 0.001331% | 0.00138% | 135 | 180 | 168 | Pulverizer Mills | Repair 2-2 mill broken spring bolt
GH2 | D1 | 1 | 9650 | 2014-01-06 11:20 | 2014-01-06 12:00 | 0.66667 | 0.21218 | 101.2102 | 0.00124% | 0.001283% | 0.00133% | 347 | 509 | 477 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Lost SO3 mitigation system. Air pressure / injection causing H2S
MC2 | D1 | 10 | 1850 | 2014-01-06 19:00 | 2014-01-06 22:36 | 3.6 | 0.32727 | 97.8545 | 0.001199% | 0.00124% | 0.001286% | 300 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC4 | D4 | 6 | 360 | 2014-01-08 21:00 | 2014-01-08 21:55 | 0.91667 | 0.20079 | 97.5857 | 0.001195% | 0.001237% |  | 410 | 525 | 486 | Burners | 4B Mill - Coal Burners Inspection
MC2 | D1 | 40 | 1850 | 2014-02-03 10:23 | 2014-02-03 21:05 | 10.7 | 0.32424 | 96.9485 | 0.001188% | 0.001229% | 0.001274% | 320 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC3 | D1 | 16 | 360 | 2014-01-24 23:56 | 2014-01-25 01:35 | 1.65 | 0.24574 | 96.8234 | 0.001186% | 0.001227% | 0.001272% | 360 | 423 | 394 | Burners | 3D Mill - 3D10 Coal Burner High Temperature
MC2 | D1 | 39 | 1700 | 2014-02-03 08:15 | 2014-02-03 10:23 | 2.1333 | 0.32323 | 96.6465 | 0.001184% | 0.001225% | 0.00127% | 280 | 330 | 299 | Feedwater Controls | Feedwater Flow Issue
MC3 | D1 | 34 | 360 | 2014-02-22 19:25 | 2014-02-22 20:28 | 1.05 | 0.23085 | 90.9553 | 0.001114% | 0.001153% | 0.001195% | 330 | 423 | 394 | Burners | 3D Mill - 3D2 Coal Burner High Temperature
MC2 | D1 | 2 | 1850 | 2014-01-01 10:30 | 2014-01-01 15:30 | 5 | 0.30303 | 90.6061 | 0.00111% | 0.001148% | 0.001191% | 310 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
GH2 | D1 | 6 | 312 | 2014-02-01 14:40 | 2014-02-01 18:00 | 3.3333 | 0.18991 | 90.5894 | 0.00111% | 0.001148% | 0.001191% | 480 | 509 | 477 | Pulverizer Mill Classifiers | 2-1 Mill not grinding, took off for inspection.
BR1 | PD | 5 | 310 | 2014-02-27 | 2014-02-27 02:28 | 2.4667 | 0.84386 | 90.293 | 0.001106% |  |  | 75 | 114 | 107 | Pulverizer Mills | 1-2 mill inspection
MC3 | D1 | 26 | 360 | 2014-02-15 11:11 | 2014-02-15 12:43 | 1.5333 | 0.22837 | 89.9773 | 0.001102% | 0.001141% | 0.001182% | 360 | 423 | 394 | Burners | 3C Mill - 3C1 & 3C3 Coal Burners High Temperature
GH1 | D1 | 14 | 320 | 2014-02-25 11:17 | 2014-02-25 12:57 | 1.6667 | 0.18375 | 88.3849 | 0.001083% | 0.00112% | 0.001162% | 460 | 517 | 481 | Foreign Object in Mill | 1-3 Mill had a noise in the pyrite section. Removed the mill to
TC1 | D1 | 17 | 280 | 2014-01-17 16:00 | 2014-01-17 16:45 | 0.75 | 0.22866 | 87.5762 | 0.001073% | 0.00111% | 0.001151% | 285 | 410 | 383 | Pulverizer Fires | Additional fire in the 1C mill following 1A and 1B mill fires
MC2 | D1 | 9 | 1850 | 2014-01-06 09:28 | 2014-01-06 19:00 | 9.5333 | 0.28889 | 86.3778 | 0.001058% | 0.001095% | 0.001135% | 320 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
GH4 | D1 | 2 | 250 | 2014-01-07 03:55 | 2014-01-07 04:36 | 0.68333 | 0.17147 | 84.1933 | 0.001031% | 0.001067% | 0.001106% | 400 | 534 | 491 | Pulverizer Feeders | 4-4 Feeder tripped.
MC2 | D1 | 3 | 250 | 2014-01-02 04:15 | 2014-01-02 05:24 | 1.15 | 0.27879 | 83.3576 | 0.001021% | 0.001057% | 0.001095% | 250 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Belt Slipping
MC1 | D1 | 2 | 250 | 2014-01-07 16:50 | 2014-01-07 18:06 | 1.2667 | 0.26869 | 81.4121 | 0.0009973% | 0.001032% | 0.00107% | 260 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen/Wet Coal
MC3 | D1 | 19 | 360 | 2014-01-31 08:09 | 2014-01-31 09:12 | 1.05 | 0.20603 | 81.1752 | 0.0009944% | 0.001029% | 0.001067% | 340 | 423 | 394 | Burners | 3C Mill - 3C2 Coal Burner High Temperature
MC1 | D1 | 32 | 1488 | 2014-02-13 07:26 | 2014-02-13 22:00 | 14.5667 | 0.26485 | 80.2491 | 0.0009831% | 0.001017% | 0.001055% | 324 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | D1 | 3 | 250 | 2014-01-08 05:45 | 2014-01-08 06:43 | 0.96667 | 0.26364 | 79.8818 | 0.0009786% | 0.001013% | 0.00105% | 240 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen/Wet Coal
GR4 | PD | 9 | 345 | 2014-01-10 19:25 | 2014-01-11 03:57 | 8.5333 | 0.8127 | 79.6444 | 0.0009756% |  |  | 95 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
MC2 | D1 | 13 | 1850 | 2014-01-08 09:50 | 2014-01-08 12:15 | 2.4167 | 0.25631 | 76.6376 | 0.0009388% | 0.0009714% | 0.001007% | 295 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 43 | 250 | 2014-02-05 03:53 | 2014-02-05 04:29 | 0.6 | 0.25455 | 76.1091 | 0.0009323% | 0.0009647% | 0.001% | 190 | 330 | 299 | Pulverizer Feeders | 2A Coal Feeder - Wet Coal
MC4 | D1 | 8 | 310 | 2014-01-09 07:00 | 2014-01-09 08:38 | 1.6333 | 0.15556 | 75.6 | 0.0009261% | 0.0009583% | 0.0009935% | 475 | 525 | 486 | Pulverizer Mills | 4A Coal Mill - Breaker Issue
GH3 | D1 | 21 | 9650 | 2014-02-20 12:30 | 2014-02-20 13:05 | 0.58333 | 0.15164 | 73.0927 | 0.0008954% | 0.0009265% | 0.0009606% | 390 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH1 | D1 | 1 | 9270 | 2014-01-08 07:48 | 2014-01-08 09:10 | 1.3667 | 0.15068 | 72.4756 | 0.0008878% | 0.0009187% | 0.0009525% | 460 | 517 | 481 | Wet Coal | Feeder plugged due to wet coal and this tripped the mill.
MC3 | D4 | 5 | 360 | 2014-01-15 08:13 | 2014-01-15 09:42 | 1.4833 | 0.17884 | 70.4636 | 0.0008632% | 0.0008932% |  | 372 | 423 | 394 | Burners | 3C Mill - Coal Burner Logic Testing
GH3 | D1 | 12 | 9650 | 2014-02-02 20:10 | 2014-02-02 20:45 | 0.58333 | 0.14058 | 67.7574 | 0.00083% | 0.0008589% | 0.0008905% | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | 3-2B SO3 injection blower pressure sensing line came off causing
MC3 | D1 | 8 | 360 | 2014-01-15 12:09 | 2014-01-15 13:13 | 1.0667 | 0.17147 | 67.5606 | 0.0008276% | 0.0008564% | 0.0008879% | 355 | 423 | 394 | Burners | 3D Mill - 3D7 Coal Burner High Temperature
GH2 | PD | 9 | 340 | 2014-02-14 02:11 | 2014-02-14 03:39 | 1.4667 | 0.14119 | 67.3485 | 0.000825% |  |  | 460 | 509 | 477 | Other Pulverizer Problems | 2-6 Mill off to inspect grinding section and classifiers.
TC1 | D1 | 14 | 280 | 2014-01-14 08:36 | 2014-01-14 10:39 | 2.05 | 0.175 | 67.025 | 0.0008211% | 0.0008496% | 0.0008808% | 375 | 410 | 383 | Pulverizer Fires | Derate due to fire in the 1B Coal Mill.
MC3 | D1 | 33 | 360 | 2014-02-22 16:15 | 2014-02-22 17:00 | 0.75 | 0.16489 | 64.9681 | 0.0007959% | 0.0008235% | 0.0008538% | 330 | 423 | 394 | Burners | 3D Mill - 3D1 Coal Burner High Temperature
MC2 | D1 | 31 | 310 | 2014-01-27 15:52 | 2014-01-27 16:39 | 0.78333 | 0.21364 | 63.8773 | 0.0007825% | 0.0008097% | 0.0008395% | 240 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Ductwork Repair
BR1 | PD | 1 | 260 | 2014-01-03 | 2014-01-03 02:00 | 2 | 0.59649 | 63.8246 | 0.0007819% |  |  | 80 | 114 | 107 | Primary Air Fan | 1-3 mil primary air fan housing leak repair
MC3 | D1 | 30 | 360 | 2014-02-21 18:21 | 2014-02-21 19:10 | 0.81667 | 0.16024 | 63.1362 | 0.0007734% | 0.0008003% | 0.0008297% | 340 | 423 | 394 | Burners | 3A Mill - 3A4 Coal Burner High Temperature
GH1 | D1 | 7 | 250 | 2014-02-07 12:35 | 2014-02-07 13:45 | 1.1667 | 0.12863 | 61.8694 | 0.0007579% | 0.0007842% | 0.0008131% | 460 | 517 | 481 | Pulverizer Feeders | Metal hung in 1-4 mill feeder.
TC2 | D1 | 10 | 9620 | 2014-01-18 18:10 | 2014-01-18 19:15 | 1.0833 | 0.10708 | 61.0379 | 0.0007477% | 0.0007737% | 0.0008021% | 547 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | The bags in the baghouse are deteriorating … holes in the bags
GH3 | D1 | 18 | 1455 | 2014-02-17 10:50 | 2014-02-17 12:00 | 1.1667 | 0.12619 | 60.8216 | 0.0007451% | 0.000771% | 0.0007993% | 470 | 527 | 482 | Induced Draft Fans | ID Fans out the top. Reduced load to swap mills.
BR1 | PD | 4 | 1400 | 2014-02-26 23:00 | 2014-02-27 | 1 | 0.5614 | 60.0702 | 0.0007359% |  |  | 50 | 114 | 107 | Forced Draft Fans | Repair leaking cooler hose 1-1 FD Fan
GR4 | D1 | 16 | 8551 | 2014-01-12 12:30 | 2014-01-12 14:38 | 2.1333 | 0.60952 | 59.7333 | 0.0007317% | 0.0007572% | 0.000785% | 75 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets. Derate increased
MC3 | D1 | 11 | 360 | 2014-01-20 08:37 | 2014-01-20 09:20 | 0.71667 | 0.14909 | 58.7429 | 0.0007196% | 0.0007446% | 0.000772% | 335 | 423 | 394 | Burners | 3C Mill - 3C3 Coal Burner High Temperature
MC3 | D1 | 17 | 360 | 2014-01-28 09:43 | 2014-01-28 10:42 | 0.98333 | 0.14645 | 57.7028 | 0.0007069% | 0.0007314% | 0.0007583% | 360 | 423 | 394 | Burners | 3C Mill - 3C2 Coal Burner High Temperature
GR3 | D1 | 6 | 9630 | 2014-02-11 09:40 | 2014-02-11 13:13 | 3.55 | 0.80467 | 57.1313 | 0.0006999% | 0.0007242% | 0.0007508% | 58 | 75 | 71 | Opacity - Fossil Steam Units | Continuation of previous event. GR3 derate increased to blow soot and clean boile
MC1 | D1 | 13 | 1850 | 2014-01-18 16:36 | 2014-01-18 18:40 | 2.0667 | 0.18788 | 56.9273 | 0.0006974% | 0.0007216% | 0.0007481% | 300 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
CR6 | D1 | 7 | 250 | 2014-02-07 01:12 | 2014-02-07 02:10 | 0.96667 | 0.22593 | 54.2222 | 0.0006642% | 0.0006873% | 0.0007126% | 200 | 261 | 240 | Pulverizer Feeders | D1 feeder plugged due to torn belt.
MC2 | D1 | 46 | 1850 | 2014-02-05 09:43 | 2014-02-05 13:25 | 3.7 | 0.17939 | 53.6388 | 0.0006571% | 0.0006799% | 0.0007049% | 314 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
TC1 | D1 | 3 | 280 | 2014-01-03 09:40 | 2014-01-03 11:31 | 1.85 | 0.13988 | 53.5733 | 0.0006563% | 0.0006791% | 0.000704% | 379 | 410 | 383 | Pulverizer Fires | Derate due to fires in the B and D coal mills.
CR6 | D1 | 8 | 250 | 2014-02-08 00:05 | 2014-02-08 01:13 | 1.1333 | 0.22146 | 53.1494 | 0.0006511% | 0.0006737% | 0.0006985% | 210 | 261 | 240 | Pulverizer Feeders | D2 feeder plugged due to wet coal.
MC3 | D1 | 27 | 360 | 2014-02-15 13:28 | 2014-02-15 14:20 | 0.86667 | 0.12908 | 50.8567 | 0.000623% | 0.0006446% | 0.0006683% | 360 | 423 | 394 | Burners | 3A Mill - 3A4 Coal Burner High Temperature
GR4 | D1 | 14 | 8551 | 2014-01-11 22:02 | 2014-01-11 23:49 | 1.7833 | 0.50952 | 49.9333 | 0.0006117% | 0.0006329% | 0.0006562% | 75 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing loss of two half cabinets.
CR6 | D1 | 16 | 9600 | 2014-02-28 08:35 | 2014-02-28 09:53 | 1.3 | 0.20421 | 49.0115 | 0.0006004% | 0.0006213% | 0.0006441% | 220 | 261 | 240 | So2 Stack Emissions - Fossil Steam Units | Dropped load an additional 20 MW to remain in SO2 compliance . Unit now at 220 MW
MC2 | D1 | 66 | 250 | 2014-02-24 00:16 | 2014-02-24 03:46 | 3.5 | 0.15909 | 47.5682 | 0.0005827% | 0.000603% | 0.0006251% | 315 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Plugged, Foreign Material
MC1 | D1 | 25 | 1488 | 2014-02-10 23:05 | 2014-02-11 06:25 | 7.3333 | 0.15556 | 47.1333 | 0.0005774% | 0.0005974% | 0.0006194% | 323 | 330 | 303 | Air Heater (Regenerative) | Air Heater - High Differential
MC2 | D1 | 69 | 1850 | 2014-02-26 05:39 | 2014-02-26 11:21 | 5.7 | 0.15545 | 46.4809 | 0.0005694% | 0.0005892% | 0.0006108% | 321 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | D1 | 44 | 1850 | 2014-02-23 03:16 | 2014-02-23 04:11 | 0.91667 | 0.15278 | 46.2917 | 0.0005671% | 0.0005868% | 0.0006084% | 275 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | D1 | 16 | 250 | 2014-01-24 03:08 | 2014-01-24 03:45 | 0.61667 | 0.14949 | 45.297 | 0.0005549% | 0.0005742% | 0.0005953% | 250 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen Coal
MC2 | D1 | 65 | 1850 | 2014-02-20 02:40 | 2014-02-20 08:09 | 5.4833 | 0.14955 | 44.7141 | 0.0005477% | 0.0005668% | 0.0005876% | 321 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
GH1 | D1 | 10 | 9650 | 2014-02-13 07:23 | 2014-02-13 09:08 | 1.75 | 0.091393 | 43.9599 | 0.0005385% | 0.0005572% | 0.0005777% | 490 | 517 | 481 | Other Stack Or Exhaust Emissions -fossil Stm Unit | U1 H2SO4 was high. Dropped load to keep it in compliance.
GR4 | D1 | 22 | 8551 | 2014-01-20 09:20 | 2014-01-20 18:30 | 9.1667 | 0.43651 | 42.7778 | 0.000524% | 0.0005422% | 0.0005622% | 100 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded o
GR4 | D1 | 20 | 8551 | 2014-01-17 20:13 | 2014-01-18 00:33 | 4.3333 | 0.4127 | 40.4444 | 0.0004954% | 0.0005127% | 0.0005315% | 95 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded
MC2 | D1 | 45 | 1850 | 2014-02-05 07:56 | 2014-02-05 09:43 | 1.7833 | 0.1351 | 40.3952 | 0.0004948% | 0.000512% | 0.0005309% | 305 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 63 | 1850 | 2014-02-19 07:00 | 2014-02-19 08:50 | 1.8333 | 0.13333 | 39.8667 | 0.0004884% | 0.0005053% | 0.0005239% | 306 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
GR4 | D1 | 3 | 9630 | 2014-01-04 07:34 | 2014-01-04 16:06 | 8.5333 | 0.40635 | 39.8222 | 0.0004878% | 0.0005048% | 0.0005233% | 100 | 105 | 98 | Opacity - Fossil Steam Units | Load reduced on GR4 due to Opacity issues.
TC1 | D1 | 29 | 310 | 2014-02-11 22:17 | 2014-02-11 23:30 | 1.2167 | 0.10386 | 39.7791 | 0.0004873% | 0.0005042% | 0.0005228% | 375 | 410 | 383 | Pulverizer Mills | Derate required due to high temperature on the 1B coal mill.
TC1 | D1 | 4 | 280 | 2014-01-04 02:47 | 2014-01-04 03:56 | 1.15 | 0.098171 | 37.5994 | 0.0004606% | 0.0004766% | 0.0004941% | 375 | 410 | 383 | Pulverizer Fires | Derate due to fire in the D coal mill.
CR6 | D1 | 10 | 340 | 2014-02-09 06:50 | 2014-02-09 07:15 | 0.41667 | 0.15326 | 36.7816 | 0.0004506% | 0.0004662% | 0.0004834% | 165 | 261 | 240 | Other Pulverizer Problems | Support fuel unavailable due to loss of communication between precipitator & DCS.
GR4 | D1 | 19 | 8551 | 2014-01-16 10:36 | 2014-01-16 14:30 | 3.9 | 0.37143 | 36.4 | 0.0004459% | 0.0004614% | 0.0004784% | 95 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets.
MC1 | D1 | 12 | 1850 | 2014-01-18 15:45 | 2014-01-18 16:36 | 0.85 | 0.11591 | 35.1205 | 0.0004302% | 0.0004452% | 0.0004615% | 285 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC3 | D1 | 18 | 360 | 2014-01-28 16:30 | 2014-01-28 17:05 | 0.58333 | 0.086879 | 34.2305 | 0.0004193% | 0.0004339% | 0.0004498% | 360 | 423 | 394 | Burners | 3B Mill - 3B6 Coal Burner High Temperature
MC4 | D1 | 28 | 1520 | 2014-02-25 08:16 | 2014-02-25 09:00 | 0.73333 | 0.069841 | 33.9429 | 0.0004158% | 0.0004302% | 0.0004461% | 475 | 525 | 486 | Flue Gas Dampers (Except Recirculation) | 4A Economizer Outlet Damper - Failed to Open Completely
BR2 | D1 | 5 | 310 | 2014-02-14 18:23 | 2014-02-14 19:11 | 0.8 | 0.2 | 33.6 | 0.0004116% | 0.0004259% | 0.0004416% | 135 | 180 | 168 | Pulverizer Mills | 2-4 hot air damper not making limit
MC4 | D1 | 3 | 380 | 2014-01-06 05:40 | 2014-01-06 05:48 | 0.13333 | 0.068571 | 33.3257 | 0.0004082% | 0.0004224% | 0.000438% | 255 | 525 | 486 | Light-off (Igniter) Systems (Including Fuel Supply) | 4C Mill - Gas Igniter Issue
MC1 | D1 | 22 | 1160 | 2014-02-08 07:15 | 2014-02-08 08:27 | 1.2 | 0.10909 | 33.0545 | 0.0004049% | 0.000419% | 0.0004344% | 300 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC1 | D1 | 26 | 1488 | 2014-02-11 06:25 | 2014-02-11 10:00 | 3.5833 | 0.10859 | 32.9015 | 0.000403% | 0.000417% | 0.0004324% | 320 | 330 | 303 | Air Heater (Regenerative) | Air Heater - High Differential
MC1 | D1 | 46 | 1850 | 2014-02-23 04:39 | 2014-02-23 05:36 | 0.95 | 0.10076 | 30.5295 | 0.000374% | 0.000387% | 0.0004012% | 295 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC3 | D1 | 15 | 300 | 2014-01-23 23:03 | 2014-01-23 23:23 | 0.33333 | 0.073286 | 28.8747 | 0.0003537% | 0.000366% | 0.0003795% | 330 | 423 | 394 | Pulverizer Motors and Drives | 3C Coal Mill Motor - Failed to Start, Breaker Issue
GR4 | D1 | 5 | 9630 | 2014-01-08 05:00 | 2014-01-08 08:04 | 3.0667 | 0.29206 | 28.6222 | 0.0003506% | 0.0003628% | 0.0003761% | 95 | 105 | 98 | Opacity - Fossil Steam Units | GR4 load reduction to avoid opacity exceedances. B5 has a tube leak and we have a
GH2 | D1 | 5 | 280 | 2014-01-18 13:37 | 2014-01-18 14:14 | 0.61667 | 0.059365 | 28.317 | 0.0003469% | 0.0003589% | 0.0003721% | 460 | 509 | 477 | Pulverizer Fires | 2-6 Mill off due to fire in the pyrite line.
TC2 | D1 | 9 | 9620 | 2014-01-18 17:55 | 2014-01-18 18:10 | 0.25 | 0.049423 | 28.1713 | 0.0003451% | 0.0003571% | 0.0003702% | 487 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | The bags in the baghouse are deteriorating … holes in the bags
GR3 | D1 | 7 | 9630 | 2014-02-11 13:13 | 2014-02-11 17:20 | 4.1167 | 0.38422 | 27.2798 | 0.0003342% | 0.0003458% | 0.0003585% | 68 | 75 | 71 | Opacity - Fossil Steam Units | Continuation of previous event. GR3/B4 soot blowing completed, raised load as muc
GR4 | D1 | 25 | 263 | 2014-02-01 21:38 | 2014-02-01 22:48 | 1.1667 | 0.27778 | 27.2222 | 0.0003335% | 0.0003451% | 0.0003577% | 80 | 105 | 98 | Primary Air Fan Drives | 5-2 PA Fan Control Jack Minimum Stop failed to disengage. I&E found and repaired
GR4 | D1 | 21 | 8551 | 2014-01-18 17:09 | 2014-01-18 22:26 | 5.2833 | 0.25159 | 24.6556 | 0.000302% | 0.0003125% | 0.000324% | 100 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result ot two half cabinets grounded
MC1 | D1 | 15 | 250 | 2014-01-24 02:53 | 2014-01-24 03:08 | 0.25 | 0.079545 | 24.1023 | 0.0002953% | 0.0003055% | 0.0003167% | 225 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen Coal
MC3 | D1 | 25 | 360 | 2014-02-10 19:42 | 2014-02-10 19:57 | 0.25 | 0.060875 | 23.9846 | 0.0002938% | 0.000304% | 0.0003152% | 320 | 423 | 394 | Burners | 3D Mill - 3D4 Coal Burner High Temperature
GR4 | D1 | 1 | 9630 | 2014-01-02 12:20 | 2014-01-02 15:10 | 2.8333 | 0.24286 | 23.8 | 0.0002916% | 0.0003017% | 0.0003128% | 96 | 105 | 98 | Opacity - Fossil Steam Units | Load reduced on GR4 to blow soot and to stay within 3 hr Particulate limit
TC1 | D1 | 19 | 280 | 2014-01-17 19:40 | 2014-01-17 20:08 | 0.46667 | 0.056911 | 21.7967 | 0.000267% | 0.0002763% | 0.0002864% | 360 | 410 | 383 | Pulverizer Fires | Some of the mills were returned to service. However, unit derate was still necessary
GH4 | PD | 8 | 250 | 2014-02-25 03:58 | 2014-02-25 05:33 | 1.5833 | 0.041511 | 20.3817 | 0.0002497% |  |  | 520 | 534 | 491 | Pulverizer Feeders | Boiler exit gas was high due to both top mills being in service w
GR4 | D1 | 18 | 8551 | 2014-01-16 02:31 | 2014-01-16 06:41 | 4.1667 | 0.19841 | 19.4444 | 0.0002382% | 0.0002465% | 0.0002555% | 100 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets.
MC1 | D1 | 45 | 1850 | 2014-02-23 04:11 | 2014-02-23 04:39 | 0.46667 | 0.063636 | 19.2818 | 0.0002362% | 0.0002444% | 0.0002534% | 285 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
GR3 | PD | 11 | 346 | 2014-02-19 22:00 | 2014-02-19 23:20 | 1.3333 | 0.26667 | 18.9333 | 0.0002319% |  |  | 60 | 75 | 71 | Pulverizer Pyrite Removal System | 4-4 Pulv Pyrite Trap running heavy. Maint found Pyrite Swing Gaate stuck in the op
GR3 | D1 | 1 | 250 | 2014-01-07 13:15 | 2014-01-07 14:15 | 1 | 0.26667 | 18.9333 | 0.0002319% | 0.00024% | 0.0002488% | 55 | 75 | 71 | Pulverizer Feeders | 4-4 Feeder plugged with coal and ice.
TC1 | D1 | 16 | 280 | 2014-01-17 15:20 | 2014-01-17 16:00 | 0.66667 | 0.043902 | 16.8146 | 0.000206% | 0.0002131% | 0.000221% | 383 | 410 | 383 | Pulverizer Fires | Fires in the 1A and 1B coal mills required unit derate.
GR4 | D1 | 28 | 9630 | 2014-02-13 14:41 | 2014-02-13 16:28 | 1.7833 | 0.16984 | 16.6444 | 0.0002039% | 0.000211% | 0.0002187% | 95 | 105 | 98 | Opacity - Fossil Steam Units | GR4 derated due to opacity, blowing soot to clean up the boiler.
GR4 | PD | 11 | 345 | 2014-01-11 05:23 | 2014-01-11 06:15 | 0.86667 | 0.16508 | 16.1778 | 0.0001982% |  |  | 85 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
GR4 | PD | 10 | 345 | 2014-01-11 03:57 | 2014-01-11 05:23 | 1.4333 | 0.16381 | 16.0533 | 0.0001967% |  |  | 93 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
MC4 | D1 | 19 | 310 | 2014-02-07 06:50 | 2014-02-07 07:05 | 0.25 | 0.030952 | 15.0429 | 0.0001843% | 0.0001907% | 0.0001977% | 460 | 525 | 486 | Pulverizer Mills | 4B Coal Mill - Swing Valve & Ignitor Gas Valve Issues
MC4 | D1 | 20 | 250 | 2014-02-11 09:10 | 2014-02-11 09:20 | 0.16667 | 0.030159 | 14.6571 | 0.0001796% | 0.0001858% | 0.0001926% | 430 | 525 | 486 | Pulverizer Feeders | 4C Coal Feeder - Microprocessor Issue
MC4 | D1 | 2 | 4261 | 2014-01-02 11:34 | 2014-01-02 12:11 | 0.61667 | 0.029365 | 14.2714 | 0.0001748% | 0.0001809% | 0.0001876% | 500 | 525 | 486 | Turbine Control Valves | Turbine Control Valves - EHC Issue
GH3 | D1 | 5 | 1455 | 2014-01-21 23:18 | 2014-01-22 01:31 | 2.2167 | 0.029443 | 14.1917 | 0.0001738% | 0.0001799% | 0.0001865% | 520 | 527 | 482 | Induced Draft Fans | Load was reduced when 3-1 ID Fan blade position feedback failed,
TC1 | D1 | 27 | 310 | 2014-02-10 07:22 | 2014-02-10 07:45 | 0.38333 | 0.032724 | 12.5331 | 0.0001535% | 0.0001589% | 0.0001647% | 375 | 410 | 383 | Pulverizer Mills | Derate on TC1 to 500 MW's due to D coal mill fire. Additional issue with the E co
GR4 | D1 | 7 | 9630 | 2014-01-08 13:30 | 2014-01-08 17:55 | 4.4167 | 0.12619 | 12.3667 | 0.0001515% | 0.0001568% | 0.0001625% | 102 | 105 | 98 | Opacity - Fossil Steam Units | GR4 load reduction to avoid opacity exceedances. B5 has a tube leak and we have a
MC2 | D1 | 71 | 1850 | 2014-02-26 15:29 | 2014-02-26 16:46 | 1.2833 | 0.035 | 10.465 | 0.0001282% | 0.0001327% | 0.0001375% | 321 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
TC2 | D1 | 18 | 1455 | 2014-02-04 15:45 | 2014-02-04 16:15 | 0.5 | 0.015651 | 8.9209 | 0.0001093% | 0.0001131% | 0.0001172% | 588 | 607 | 570 | Induced Draft Fans | Derate required on the unit due to ID fan stall alarms. Required derate to avoid
CR6 | D1 | 15 | 9600 | 2014-02-28 08:13 | 2014-02-28 08:35 | 0.36667 | 0.029502 | 7.0805 | 8.674e-05% | 8.975e-05% | 9.305e-05% | 240 | 261 | 240 | So2 Stack Emissions - Fossil Steam Units | Dropped load to keep SO2 in compliance.
GR3 | D1 | 4 | 9630 | 2014-02-11 08:17 | 2014-02-11 09:18 | 1.0167 | 0.094889 | 6.7371 | 8.253e-05% | 8.54e-05% | 8.854e-05% | 68 | 75 | 71 | Opacity - Fossil Steam Units | Load reduced on GR3 due to high opacity.
GR3 | D1 | 9 | 9630 | 2014-02-12 08:20 | 2014-02-12 09:30 | 1.1667 | 0.093333 | 6.6267 | 8.118e-05% | 8.4e-05% | 8.709e-05% | 69 | 75 | 71 | Opacity - Fossil Steam Units | GR3 derate decreased from Event #8 due to high opacity.
GR3 | D1 | 10 | 9630 | 2014-02-12 09:30 | 2014-02-12 11:00 | 1.5 | 0.08 | 5.68 | 6.958e-05% | 7.2e-05% | 7.465e-05% | 71 | 75 | 71 | Opacity - Fossil Steam Units | GR3 Derate reduction from Event #9 due to high opacity.
GR3 | D1 | 8 | 9630 | 2014-02-12 07:40 | 2014-02-12 08:20 | 0.66667 | 0.08 | 5.68 | 6.958e-05% | 7.2e-05% | 7.465e-05% | 66 | 75 | 71 | Opacity - Fossil Steam Units | GR3 load reduced due to high opacity.
GR4 | D1 | 2 | 9630 | 2014-01-04 05:51 | 2014-01-04 06:41 | 0.83333 | 0.039683 | 3.8889 | 4.764e-05% | 4.929e-05% | 5.111e-05% | 100 | 105 | 98 | Opacity - Fossil Steam Units | Load reduced on GR4 due to Opacity issues.
GR3 | D1 | 3 | 340 | 2014-01-23 18:56 | 2014-01-23 19:09 | 0.21667 | 0.043333 | 3.0767 | 3.769e-05% | 3.9e-05% | 4.043e-05% | 60 | 75 | 71 | Other Pulverizer Problems | 4-4 Pulverizer Pyrite Trap plugged. Pulv O/S to clear trap.
GR4 | D1 | 4 | 9630 | 2014-01-04 16:06 | 2014-01-04 17:34 | 1.4667 | 0.027937 | 2.7378 | 3.354e-05% | 3.47e-05% | 3.598e-05% | 103 | 105 | 98 | Opacity - Fossil Steam Units | GR4 Derate reduced from 5MW to 2MW due to Opacity issues.
GR3 | D1 | 5 | 9630 | 2014-02-11 09:18 | 2014-02-11 09:40 | 0.36667 | 0.024444 | 1.7356 | 2.126e-05% | 2.2e-05% | 2.281e-05% | 70 | 75 | 71 | Opacity - Fossil Steam Units | GR3 derate reduction from event #4. Derate due to igh opacity.
MC4 | NC | 14 | 1160 | 2014-01-26 11:35 | 2014-01-27 05:50 | 18.25 | [5 empty] | 0 | 525 | 486 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC1 | NC | 29 | 8460 | 2014-02-12 07:00 | 2014-02-12 22:45 | 15.75 | [5 empty] | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
MC4 | NC | 10 | 1160 | 2014-01-18 21:00 | 2014-01-19 07:41 | 10.6833 | [5 empty] | 0 | 525 | 486 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 68 | 1850 | 2014-02-25 19:47 | 2014-02-26 05:39 | 9.8667 | [5 empty] | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Hot Start Up
MC4 | NC | 11 | 8825 | 2014-01-22 10:35 | 2014-01-22 20:00 | 9.4167 | [5 empty] | 0 | 525 | 486 | Other Scr Problems | SCR Flow Test @ Full Load
MC2 | NC | 5 | 1850 | 2014-01-04 11:51 | 2014-01-04 21:11 | 9.3333 | [5 empty] | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Warm Start Up
CR4 | NC | 2 | 1150 | 2014-01-08 21:00 | 2014-01-09 06:07 | 9.1167 | [5 empty] | 0 | 168 | 155 | Second Superheater Slagging or Fouling | Boiler deslag. Full load available if needed.
MC3 | NC | 6 | 1990 | 2014-01-14 08:00 | 2014-01-14 16:40 | 8.6667 | [5 empty] | 0 | 423 | 394 | Boiler Performance Testing | Full Load Winter Capability Test
CR4 | NC | 6 | 1150 | 2014-01-24 21:30 | 2014-01-25 06:09 | 8.65 | [5 empty] | 0 | 168 | 155 | Second Superheater Slagging or Fouling | Boiler deslag. Full load available if needed.
MC2 | NC | 59 | 1850 | 2014-02-18 13:40 | 2014-02-18 22:15 | 8.5833 | [5 empty] | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Warm Start Up
TC1 | NC | 9 | 1489 | 2014-01-10 06:30 | 2014-01-10 15:00 | 8.5 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | A 525 MW minimum limit was set on the unit to accomplish air heater slip testing.
MC1 | NC | 33 | 8460 | 2014-02-13 13:40 | 2014-02-13 22:00 | 8.3333 | [5 empty] | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
MC2 | NC | 19 | 1160 | 2014-01-18 21:05 | 2014-01-19 05:00 | 7.9167 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 23 | 1160 | 2014-01-24 23:00 | 2014-01-25 06:50 | 7.8333 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 36 | 1850 | 2014-02-02 06:35 | 2014-02-02 14:15 | 7.6667 | [5 empty] | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Hot Start Up
TC1 | NC | 25 | 1489 | 2014-01-31 13:00 | 2014-01-31 20:00 | 7 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running & good for full load with a 525 MW limit set for ammonia slip mit
TC1 | NC | 147 | 1489 | 2014-01-31 13:00 | 2014-01-31 20:00 | 7 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running and good for full load with a 525 MW limit set for ammonia slip m
MC2 | NC | 54 | 1160 | 2014-02-12 22:00 | 2014-02-13 04:50 | 6.8333 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
CR4 | NC | 7 | 1150 | 2014-01-30 21:45 | 2014-01-31 04:30 | 6.75 | [5 empty] | 0 | 168 | 155 | Second Superheater Slagging or Fouling | Boiler deslag. Full load availabe if needed.
MC2 | NC | 18 | 1160 | 2014-01-17 22:15 | 2014-01-18 05:00 | 6.75 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC4 | NC | 23 | 4490 | 2014-02-19 06:00 | 2014-02-19 12:30 | 6.5 | [5 empty] | 0 | 525 | 486 | Turbine Performance Testing | Full Load Capability Test
MC2 | NC | 47 | 1160 | 2014-02-07 23:00 | 2014-02-08 05:30 | 6.5 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC4 | NC | 12 | 8825 | 2014-01-23 08:47 | 2014-01-23 15:10 | 6.3833 | [5 empty] | 0 | 525 | 486 | Other Scr Problems | SCR Flow Test @ Full Load
MC1 | NC | 47 | 4490 | 2014-02-27 07:00 | 2014-02-27 13:18 | 6.3 | [5 empty] | 0 | 330 | 303 | Turbine Performance Testing | Capability Test - Full Load
TC2 | NC | 11 | 1190 | 2014-01-19 | 2014-01-19 06:15 | 6.25 | [5 empty] | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate to conduct boiler OEM recommended deslag.
MC2 | NC | 51 | 1160 | 2014-02-09 21:12 | 2014-02-10 03:17 | 6.0833 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC1 | NC | 24 | 1160 | 2014-02-08 22:00 | 2014-02-09 04:00 | 6 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 50 | 1160 | 2014-02-08 22:00 | 2014-02-09 04:00 | 6 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
TC1 | NC | 1 | 1489 | 2014-01-02 09:00 | 2014-01-02 15:00 | 6 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Holding the unit above 525 MW's for Air Heater Slip Testing to be conducted.
TC1 | NC | 8 | 1489 | 2014-01-09 07:00 | 2014-01-09 13:00 | 6 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | A 525 MW minimum limit was set on the unit to accomplish air heater slip testing.
TC1 | NC | 30 | 9999 | 2014-02-19 08:00 | 2014-02-19 14:00 | 6 | [5 empty] | 0 | 410 | 383 | Total Unit Performance Testing | Test run at full load to maintain high temperatures for unit testing.
TC2 | NC | 15 | 1190 | 2014-01-26 12:00 | 2014-01-26 18:00 | 6 | [5 empty] | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate at 561 MW to conduct boiler OEM recommended deslag. Unit av
TC1 | NC | 21 | 1489 | 2014-01-21 18:00 | 2014-01-21 23:59 | 5.9833 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running and good for full load but with a 525 MW limit set for ammonia slip
MC2 | NC | 34 | 1160 | 2014-01-30 22:15 | 2014-01-31 04:00 | 5.75 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC4 | NC | 13 | 8825 | 2014-01-24 12:20 | 2014-01-24 18:02 | 5.7 | [5 empty] | 0 | 525 | 486 | Other Scr Problems | SCR Flow Test - Full Load
TC1 | NC | 26 | 9999 | 2014-02-05 10:45 | 2014-02-05 16:26 | 5.6833 | [5 empty] | 0 | 410 | 383 | Total Unit Performance Testing | Unit running and good for full load, this non-curtailing event was for the complet
TC2 | NC | 3 | 1190 | 2014-01-11 | 2014-01-11 05:23 | 5.3833 | [5 empty] | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate at 561MW for boiler OEM recommended weekly deslag.
MC1 | NC | 19 | 1160 | 2014-02-04 23:00 | 2014-02-05 04:15 | 5.25 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater. Full load available if needed.
MC2 | NC | 55 | 8460 | 2014-02-13 08:00 | 2014-02-13 13:11 | 5.1833 | [5 empty] | 0 | 330 | 299 | Wet Scrubber Testing | Particulate Matter Testing - Full Load
TC2 | NC | 2 | 1190 | 2014-01-04 12:00 | 2014-01-04 17:00 | 5 | [5 empty] | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate due to boiler OEM recommended deslag, unit available to retu
MC2 | NC | 17 | 1160 | 2014-01-16 23:00 | 2014-01-17 04:00 | 5 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC4 | NC | 25 | 1160 | 2014-02-20 23:00 | 2014-02-21 04:00 | 5 | [5 empty] | 0 | 525 | 486 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 33 | 1160 | 2014-01-29 21:00 | 2014-01-30 01:55 | 4.9167 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater. Full load available if needed.
TC1 | NC | 2 | 1489 | 2014-01-03 05:00 | 2014-01-03 09:40 | 4.6667 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Holding load above 525 MW's for ammonia slip testing for the air heaters.
TC1 | NC | 24 | 1489 | 2014-01-29 10:00 | 2014-01-29 14:37 | 4.6167 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running and good for full load but with a 525 MW limit set for ammonia sl
CR4 | NC | 12 | 9999 | 2014-02-24 09:40 | 2014-02-24 14:12 | 4.5333 | [5 empty] | 0 | 168 | 155 | Total Unit Performance Testing | Full Load winter capability test.
MC1 | NC | 11 | 1850 | 2014-01-18 11:21 | 2014-01-18 15:45 | 4.4 | [5 empty] | 0 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Very Hot Start Up
MC4 | NC | 21 | 1160 | 2014-02-12 23:59 | 2014-02-13 04:20 | 4.35 | [5 empty] | 0 | 525 | 486 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 52 | 8460 | 2014-02-11 08:00 | 2014-02-11 12:20 | 4.3333 | [5 empty] | 0 | 330 | 299 | Wet Scrubber Testing | Particulate Matter Testing - Full Load
MC2 | NC | 53 | 1160 | 2014-02-11 12:21 | 2014-02-11 16:30 | 4.15 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
BR3 | NC | 11 | 1710 | 2014-02-24 22:00 | 2014-02-25 02:05 | 4.0833 | [5 empty] | 0 | 457 | 414 | Combustion/Steam Condition Controls | Combustion tuning 6544234
CR5 | NC | 9 | 9999 | 2014-02-13 10:00 | 2014-02-13 14:00 | 4 | [5 empty] | 0 | 181 | 168 | Total Unit Performance Testing | Full load winter capability test.
MC3 | NC | 9 | 8460 | 2014-01-15 13:14 | 2014-01-15 16:42 | 3.4667 | [5 empty] | 0 | 423 | 394 | Wet Scrubber Testing | Full Load RATA Test
MC1 | NC | 28 | 8460 | 2014-02-11 12:45 | 2014-02-11 16:00 | 3.25 | [5 empty] | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
MC3 | NC | 3 | 8460 | 2014-01-15 | 2014-01-15 03:06 | 3.1 | [5 empty] | 0 | 423 | 394 | Wet Scrubber Testing | Mid Flow RATA Test
CR6 | NC | 13 | 4240 | 2014-02-17 12:00 | 2014-02-17 15:01 | 3.0167 | [5 empty] | 0 | 261 | 240 | Lp Turbine Bearings | Turbine cool down in prep for removing #3 & #4 turbine bearing during maintenance
MC3 | NC | 7 | 8460 | 2014-01-15 09:42 | 2014-01-15 12:09 | 2.45 | [5 empty] | 0 | 423 | 394 | Wet Scrubber Testing | Full Load RATA Test
TC1 | NC | 22 | 1489 | 2014-01-29 06:00 | 2014-01-29 08:00 | 2 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running and good for full load but with a 525 MW limit set for ammonia sl
TC1 | NC | 23 | 9999 | 2014-01-29 08:00 | 2014-01-29 10:00 | 2 | [5 empty] | 0 | 410 | 383 | Total Unit Performance Testing | Unit was running and requested full load production to allow for the full-load tes
TC1 | NC | 20 | 4267 | 2014-01-19 01:00 | 2014-01-19 01:30 | 0.5 | [5 empty] | 0 | 410 | 383 | Turbine Control Valve Testing | Weekly valve check on the unit, Unit available to return to full load if required
[9 empty] | 9.856% | 6.435% | 2.933%
PR13 | PO | 4 | 4720 | 2014-02-15 06:08 | 2014-03-01 | 329.8667 | 329.8667 | 57726.6667 |  |  |  | 0 | 176 | 175 | Generator Synchronization Equipment | Generator synchronization equipment modifications. Replacing all generator protec
TC8 | U1 | 9 | 3869 | 2014-01-10 14:00 | 2014-01-14 13:28 | 95.4667 | 95.4667 | 16802.1333 |  |  |  | 0 | 180 | 176 | Other Fire Protection System Problems | Forced outage due to issue with Fire Protection System.
BR10 | MO | 12 | 5272 | 2014-02-28 10:48 | 2014-03-02 13:50 | 51.0333 | 51.0333 | 7042.6 |  |  |  | 0 | 139 | 138 | Gas Turbine - Boroscope Inspection | Eddy current inspection of R3 blade and boroscope of turbine section.
PR12 | U1 | 4 | 5170 | 2014-02-19 10:25 | 2014-03-01 | 229.5833 | 229.5833 | 5280.4167 |  |  |  | 0 | 23 | 23 | Gas Turbine - Cooling Water System | Fire pump that supplies cooling water locked up.
BR7 | U1 | 7 | 5150 | 2014-01-13 08:05 | 2014-01-14 13:30 | 29.4167 | 29.4167 | 5030.25 |  |  |  | 0 | 172 | 171 | Gas Turbine - Turning Gear And Motor | Unit will not stay on rotor barring.
PR13 | U1 | 2 | 9130 | 2014-01-30 07:00 | 2014-01-31 09:20 | 26.3333 | 26.3333 | 3871 |  |  |  | 0 | 148 | 147 | Lack Of Fuel (outside Management Control) | Fuel supply not available.
TC9 | SF | 3 | 5130 | 2014-01-03 | 2014-01-03 20:51 | 20.85 | 20.85 | 3669.6 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to issue with 89SS.
TC8 | SF | 5 | 5130 | 2014-01-05 19:28 | 2014-01-06 15:58 | 20.5 | 20.5 | 3608 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to issue with 89SS.
TC8 | U1 | 2 | 5130 | 2014-01-03 05:21 | 2014-01-04 00:26 | 19.0833 | 19.0833 | 3358.6667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to issue with 89SS.
HA1 | SF | 2 | 5160 | 2014-01-06 21:22 | 2014-01-14 13:14 | 183.8667 | 183.8667 | 2574.1333 |  |  |  | 0 | 14 | 14 | Gas Turbine - Cooling And Seal Air System | Busted glycol line on radiator. Failed to ignite on start up.
BR11 | MO | 21 | 5272 | 2014-02-26 07:11 | 2014-02-26 16:18 | 9.1167 | 9.1167 | 1166.9333 |  |  |  | 0 | 129 | 128 | Gas Turbine - Boroscope Inspection | Eddy current inspection of R3 blade and boroscope inspection of turbine section.
HA1 | U1 | 5 | 5108 | 2014-01-17 14:23 | 2014-01-20 14:33 | 72.1667 | 72.1667 | 1010.3333 |  |  |  | 0 | 14 | 14 | Gas Turbine - High Engine Exhaust Temperature | Lost two exhaust gas thermocouples during run.
BR8 | MO | 17 | 5272 | 2014-02-28 08:24 | 2014-02-28 15:30 | 7.1 | 7.1 | 908.8 |  |  |  | 0 | 129 | 128 | Gas Turbine - Boroscope Inspection | Eddy Current Inspection of R3 blade and boroscope of trubine.
TC6 | U1 | 20 | 5250 | 2014-01-24 04:29 | 2014-01-24 10:13 | 5.7333 | 5.7333 | 900.1333 |  |  |  | 0 | 160 | 157 | Other Controls And Instrument Problems | Forced outage due to erratic thermocouple signals from T Processor.
BR5 | MO | 12 | 5272 | 2014-02-27 06:55 | 2014-02-27 14:53 | 7.9667 | 7.9667 | 892.2667 |  |  |  | 0 | 113 | 112 | Gas Turbine - Boroscope Inspection | Eddy Current Inspection of R3 blade
BR7 | U1 | 4 | 4700 | 2014-01-04 06:11 | 2014-01-04 11:16 | 5.0833 | 5.0833 | 869.25 |  |  |  | 0 | 172 | 171 | Generator Voltage Control | AVR Fault due to loss of channel one processor.
TC5 | U1 | 6 | 5246 | 2014-01-07 01:25 | 2014-01-07 05:50 | 4.4167 | 4.4167 | 777.3333 |  |  |  | 0 | 180 | 176 | Gas Turbine Control System - Hardware Problems.... | Forced outage due to compressor inlet thermocouple disagreement from a failed cont
TC6 | U1 | 8 | 5016 | 2014-01-07 01:25 | 2014-01-07 05:49 | 4.4 | 4.4 | 774.4 |  |  |  | 0 | 180 | 176 | High Pressure Compressor - Bleed Valves | Forced outage due to compressor bleed valve frozen closed.
TC6 | MO | 30 | 5041 | 2014-02-04 11:33 | 2014-02-04 15:52 | 4.3167 | 4.3167 | 759.7333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Maintenance outage to change controller on Fuel Gas Worker Valve.
BR11 | MO | 8 | 5108 | 2014-01-14 08:00 | 2014-01-14 13:54 | 5.9 | 5.9 | 755.2 |  |  |  | 0 | 129 | 128 | Gas Turbine - High Engine Exhaust Temperature | Outage to replace TAT probe. Two thermocouples not working
TC6 | MO | 23 | 5041 | 2014-01-25 12:06 | 2014-01-25 16:20 | 4.2333 | 4.2333 | 664.6333 |  |  |  | 0 | 160 | 157 | Gas Turbine - Fuel Piping And Valves | Maintenance outage to prepare unit for tuning.
TC6 | U1 | 12 | 5079 | 2014-01-22 00:08 | 2014-01-22 04:20 | 4.2 | 4.2 | 659.4 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Forced outage due to flameout.
BR11 | MO | 11 | 5160 | 2014-01-16 14:00 | 2014-01-16 18:57 | 4.95 | 4.95 | 633.6 |  |  |  | 0 | 129 | 128 | Gas Turbine - Cooling And Seal Air System | Leak of water into control air off the compressor
PR12 | U1 | 2 | 9130 | 2014-01-30 07:00 | 2014-01-31 09:20 | 26.3333 | 26.3333 | 605.6667 |  |  |  | 0 | 23 | 23 | Lack Of Fuel (outside Management Control) | Fuel supply not available.
BR9 | MO | 12 | 5160 | 2014-02-20 13:00 | 2014-02-20 17:04 | 4.0667 | 4.0667 | 561.2 |  |  |  | 0 | 139 | 138 | Gas Turbine - Cooling And Seal Air System | Changed brushes on DC mantling air fan.
BR5 | MO | 10 | 5048 | 2014-02-18 08:00 | 2014-02-18 12:46 | 4.7667 | 4.7667 | 533.8667 |  |  |  | 0 | 113 | 112 | Gas Fuel System with controls and instruments | Inspect orifice, calibrate transmitter for fuel gas system flow meter.
BR11 | U1 | 16 | 5017 | 2014-01-30 03:36 | 2014-01-30 07:40 | 4.0667 | 4.0667 | 520.5333 |  |  |  | 0 | 129 | 128 | Low Pressure Compressor Bleed Valves | Loose limit switch on compressor blow off valve
TC9 | U1 | 15 | 5041 | 2014-02-07 12:38 | 2014-02-07 15:35 | 2.95 | 2.95 | 519.2 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Forced outage to address pressure swings due to worker fuel gas valve.
TC10 | SF | 13 | 5079 | 2014-01-22 00:45 | 2014-01-22 04:02 | 3.2833 | 3.2833 | 515.4833 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Failed to ignite during startup.
BR5 | U1 | 2 | 5054 | 2014-01-06 08:23 | 2014-01-06 11:47 | 3.4 | 3.4 | 442 |  |  |  | 0 | 131 | 130 | Water Injection System | Instrument measuring DP across water injection control started to freeze. Operato
TC5 | SF | 18 | 5130 | 2014-02-17 17:45 | 2014-02-17 20:14 | 2.4833 | 2.4833 | 437.0667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to low resistivity in the cooling water for the LCI. Changed
TC6 | U1 | 25 | 5048 | 2014-01-27 11:27 | 2014-01-27 14:05 | 2.6333 | 2.6333 | 413.4333 |  |  |  | 0 | 160 | 157 | Gas Fuel System with controls and instruments | Unit tripped due to frozen sensing line to 96GN transmitter.
TC5 | U1 | 12 | 5079 | 2014-02-11 06:16 | 2014-02-11 08:35 | 2.3167 | 2.3167 | 407.7333 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
BR7 | U1 | 12 | 5049 | 2014-02-10 17:14 | 2014-02-10 19:34 | 2.3333 | 2.3333 | 399 |  |  |  | 0 | 172 | 171 | Other Gas Turbine Fuel System Problems | Issue with pressure regulators in reducing station.
TC5 | U1 | 2 | 5240 | 2014-01-03 11:04 | 2014-01-03 13:20 | 2.2667 | 2.2667 | 398.9333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fire Detection And Extinguishing Sys | Unit tripped on fire protection alarm due to condensation within fire protection p
TC6 | U1 | 11 | 5048 | 2014-01-21 17:32 | 2014-01-21 20:01 | 2.4833 | 2.4833 | 389.8833 |  |  |  | 0 | 160 | 157 | Gas Fuel System with controls and instruments | Forced outage due to combustion instrumentation issues.
Z1 | U1 | 2 | 9130 | 2014-01-30 07:00 | 2014-01-31 09:20 | 26.3333 | 26.3333 | 368.6667 |  |  |  | 0 | 14 | 14 | Lack Of Fuel (outside Management Control) | Fuel supply not available.
HA1 | U1 | 4 | 5120 | 2014-01-16 12:31 | 2014-01-17 14:09 | 25.6333 | 25.6333 | 358.8667 |  |  |  | 0 | 14 | 14 | Gas Turbine - Hydraulic Oil System | Oil leak on diesel starting engine.
TC5 | U1 | 4 | 5246 | 2014-01-06 12:15 | 2014-01-06 14:08 | 1.8833 | 1.8833 | 331.4667 |  |  |  | 0 | 180 | 176 | Gas Turbine Control System - Hardware Problems.... | Unit tripped on high exhaust temperature differential from a failed control system
BR10 | MO | 10 | 5160 | 2014-02-20 17:04 | 2014-02-20 19:28 | 2.4 | 2.4 | 331.2 |  |  |  | 0 | 139 | 138 | Gas Turbine - Cooling And Seal Air System | Check brushes on DC mantling air fan.
PR11 | U1 | 2 | 9130 | 2014-01-30 07:00 | 2014-01-31 09:20 | 26.3333 | 26.3333 | 316 |  |  |  | 0 | 12 | 12 | Lack Of Fuel (outside Management Control) | Fuel supply not available.
TC10 | U1 | 2 | 5016 | 2014-01-03 05:21 | 2014-01-03 07:03 | 1.7 | 1.7 | 299.2 |  |  |  | 0 | 180 | 176 | High Pressure Compressor - Bleed Valves | Forced outage due to compressor bleed valve frozen shut.
TC7 | U1 | 2 | 5048 | 2014-01-03 05:14 | 2014-01-03 06:52 | 1.6333 | 1.6333 | 287.4667 |  |  |  | 0 | 180 | 176 | Gas Fuel System with controls and instruments | Forced outage due to Hazardous Gas alarm.
TC6 | U1 | 4 | 5079 | 2014-01-06 02:17 | 2014-01-06 03:50 | 1.55 | 1.55 | 272.8 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to a lean blowout.
TC7 | U1 | 4 | 5041 | 2014-01-05 14:07 | 2014-01-05 15:36 | 1.4833 | 1.4833 | 261.0667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Forced outage due to fuel gas valve (SRV).
TC9 | D1 | 17 | 5041 | 2014-02-07 10:00 | 2014-02-07 12:38 | 2.6333 | 1.463 | 257.4815 |  |  |  | 80 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Derate to 80 MWs due to issue with worker fuel gas valve.
BR6 | MO | 10 | 5048 | 2014-02-04 06:30 | 2014-02-04 08:00 | 1.5 | 1.5 | 256.5 |  |  |  | 0 | 172 | 171 | Gas Fuel System with controls and instruments | Change cable for fuel gas flow meter RTD.
TC6 | SF | 13 | 5016 | 2014-01-22 04:20 | 2014-01-22 05:55 | 1.5833 | 1.5833 | 248.5833 |  |  |  | 0 | 160 | 157 | High Pressure Compressor - Bleed Valves | Startup failure due to frozen compressor bleed valve.
BR11 | MO | 19 | 5160 | 2014-02-20 19:28 | 2014-02-20 21:16 | 1.8 | 1.8 | 230.4 |  |  |  | 0 | 129 | 128 | Gas Turbine - Cooling And Seal Air System | Checked brushes on DC mantling air system.
TC6 | U1 | 34 | 5079 | 2014-02-11 08:29 | 2014-02-11 09:45 | 1.2667 | 1.2667 | 222.9333 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
BR6 | U1 | 7 | 5109 | 2014-01-23 13:31 | 2014-01-23 14:49 | 1.3 | 1.3 | 222.3 |  |  |  | 0 | 172 | 171 | Other Gas Turbine Exhaust Problems | Loss TC on TAT2 readings. TC reading was coming in and out of service
TC5 | U1 | 16 | 5130 | 2014-02-17 10:43 | 2014-02-17 11:57 | 1.2333 | 1.2333 | 217.0667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage to change out resistivity probe on the cooling system for the LCI.
BR8 | MO | 4 | 5111 | 2014-01-13 07:46 | 2014-01-13 09:25 | 1.65 | 1.65 | 211.2 |  |  |  | 0 | 129 | 128 | Gas Turbine - Lube Oil Pumps | Check DC brushes on emergency lube oil equipment
TC9 | SF | 20 | 5130 | 2014-02-26 02:38 | 2014-02-26 03:45 | 1.1167 | 1.1167 | 196.5333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to 89SS on TC10 failing to open.
TC10 | U1 | 25 | 5130 | 2014-02-26 02:38 | 2014-02-26 03:45 | 1.1167 | 1.1167 | 196.5333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to 89SS failing to open.
TC8 | U1 | 15 | 5041 | 2014-01-30 06:34 | 2014-01-30 07:49 | 1.25 | 1.25 | 196.25 |  |  |  | 0 | 160 | 157 | Gas Turbine - Fuel Piping And Valves | Forced outage to reset lifted safety valve that occurred due to fuel gas pressure
HA1 | U1 | 9 | 3611 | 2014-02-08 02:53 | 2014-02-08 19:05 | 16.2 | 16.2 | 194.4 |  |  |  | 0 | 12 | 12 | Switchyard Circuit Breakers | Loss of power to 138KV sub.
HA2 | U1 | 4 | 3611 | 2014-02-08 02:53 | 2014-02-08 19:05 | 16.2 | 16.2 | 194.4 |  |  |  | 0 | 12 | 12 | Switchyard Circuit Breakers | Loss power to 138KV bus in substation
CR11 | U1 | 2 | 5130 | 2014-01-06 20:13 | 2014-01-07 09:05 | 12.8667 | 12.8667 | 180.1333 |  |  |  | 0 | 14 | 14 | Gas Turbine - Starting System (including Motor) | Broken terminal on battery cable causing Cane Run 11 starting diesel to be unable
BR11 | U1 | 3 | 5017 | 2014-01-06 17:57 | 2014-01-06 19:14 | 1.2833 | 1.2833 | 164.2667 |  |  |  | 0 | 129 | 128 | Low Pressure Compressor Bleed Valves | Loose limit switch on blow off valve caused unit to trip.
TC6 | U1 | 6 | 5041 | 2014-01-06 13:52 | 2014-01-06 14:46 | 0.9 | 0.9 | 158.4 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Unit tripped due to a fuel gas valve (worker valve) not controlling properly.
BR11 | MO | 6 | 5111 | 2014-01-13 12:32 | 2014-01-13 13:45 | 1.2167 | 1.2167 | 155.7333 |  |  |  | 0 | 129 | 128 | Gas Turbine - Lube Oil Pumps | Outage to check brushes on DC lube oil pumps
BR9 | U1 | 3 | 5140 | 2014-01-07 09:33 | 2014-01-07 10:36 | 1.05 | 1.05 | 144.9 |  |  |  | 0 | 139 | 138 | Gas Turbine - Battery And Charger System | Both battery chargers indicated failure. Failure was caused by low output current
BR6 | SF | 2 | 4810 | 2014-01-02 16:13 | 2014-01-02 17:03 | 0.83333 | 0.83333 | 142.5 |  |  |  | 0 | 172 | 171 | Generator Output Breaker | Generator circuit breaker loss of 120VAC control power prevented the unit from sta
BR9 | MO | 5 | 5111 | 2014-01-13 09:25 | 2014-01-13 10:22 | 0.95 | 0.95 | 131.1 |  |  |  | 0 | 139 | 138 | Gas Turbine - Lube Oil Pumps | Check brushes on DC lube oil pumps
TC6 | SF | 14 | 5016 | 2014-01-22 05:55 | 2014-01-22 06:45 | 0.83333 | 0.83333 | 130.8333 |  |  |  | 0 | 160 | 157 | High Pressure Compressor - Bleed Valves | Startup failure due to frozen compressor bleed valve.
BR10 | MO | 4 | 5111 | 2014-01-13 10:22 | 2014-01-13 11:18 | 0.93333 | 0.93333 | 128.8 |  |  |  | 0 | 139 | 138 | Gas Turbine - Lube Oil Pumps | Outage to check brushes on DC lube oil pumps.
TC6 | U1 | 10 | 5048 | 2014-01-21 16:35 | 2014-01-21 17:24 | 0.81667 | 0.81667 | 128.2167 |  |  |  | 0 | 160 | 157 | Gas Fuel System with controls and instruments | Forced outage due to combustion instrumentation issues.
CR11 | U1 | 9 | 3840 | 2014-02-03 00:42 | 2014-02-03 09:37 | 8.9167 | 8.9167 | 124.8333 |  |  |  | 0 | 14 | 14 | Service Air Compressors | Clutch air compressor pumping up slowly - probably due to the weather.
TC6 | U1 | 33 | 5079 | 2014-02-11 06:16 | 2014-02-11 06:58 | 0.7 | 0.7 | 123.2 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
TC6 | SF | 22 | 5041 | 2014-01-24 10:30 | 2014-01-24 11:08 | 0.63333 | 0.63333 | 99.4333 |  |  |  | 0 | 160 | 157 | Gas Turbine - Fuel Piping And Valves | Startup failure due to issue with fuel gas valve.
TC9 | U1 | 7 | 5130 | 2014-01-06 02:27 | 2014-01-06 02:57 | 0.5 | 0.5 | 88 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to issue with 89SS.
TC6 | U1 | 19 | 5079 | 2014-01-23 18:18 | 2014-01-23 18:49 | 0.51667 | 0.51667 | 81.1167 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Forced outage due to combustion issue.
TC6 | U1 | 18 | 5079 | 2014-01-23 17:30 | 2014-01-23 18:00 | 0.5 | 0.5 | 78.5 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Forced outage due to combustion issue.
TC6 | U1 | 15 | 5079 | 2014-01-23 11:39 | 2014-01-23 12:04 | 0.41667 | 0.41667 | 65.4167 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Forced outage due to combustion issue.
TC6 | SF | 17 | 5041 | 2014-01-23 16:56 | 2014-01-23 17:21 | 0.41667 | 0.41667 | 65.4167 |  |  |  | 0 | 160 | 157 | Gas Turbine - Fuel Piping And Valves | Startup failure due to issue with fuel gas valve.
BR8 | MO | 13 | 5111 | 2014-02-19 12:10 | 2014-02-19 12:35 | 0.41667 | 0.41667 | 53.3333 |  |  |  | 0 | 129 | 128 | Gas Turbine - Lube Oil Pumps | Check brushes on DC lube oil pumps
BR8 | MO | 15 | 5160 | 2014-02-20 12:35 | 2014-02-20 13:00 | 0.41667 | 0.41667 | 53.3333 |  |  |  | 0 | 129 | 128 | Gas Turbine - Cooling And Seal Air System | Check brushes on DC mantling air fan
TC5 | SF | 14 | 5130 | 2014-02-17 06:28 | 2014-02-17 06:40 | 0.2 | 0.2 | 35.2 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to issue with LCI.
TC7 | U1 | 9 | 5160 | 2014-02-05 16:09 | 2014-02-05 16:17 | 0.13333 | 0.13333 | 23.4667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Unit rolled back to FSNL due to issue with pressure switch on Exhaust Frame Blower
CR11 | U1 | 5 | 5110 | 2014-01-21 10:51 | 2014-01-21 12:24 | 1.55 | 1.55 | 21.7 |  |  |  | 0 | 14 | 14 | Gas Turbine - Lube Oil System - General | Lube oil temperature to low.
TC7 | U1 | 8 | 5160 | 2014-02-05 16:03 | 2014-02-05 16:08 | 0.083333 | 0.083333 | 14.6667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Unit rolled back to FSNL due to issue with pressure switch on Exhaust Frame Blower
HA2 | MO | 6 | 5111 | 2014-02-19 11:20 | 2014-02-19 12:20 | 1 | 1 | 12 |  |  |  | 0 | 12 | 12 | Gas Turbine - Lube Oil Pumps | Inspect brushes and repair coupling for DC lube oil pump.
HA1 | U1 | 7 | 5050 | 2014-01-30 06:30 | 2014-01-30 07:01 | 0.51667 | 0.51667 | 7.2333 |  |  |  | 0 | 14 | 14 | Gas Turbine - Ignition System | Ignition torch failed to light
TC9 | U1 | 22 | 5160 | 2014-02-26 19:14 | 2014-02-26 19:15 | 0.016667 | 0.016667 | 2.9333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Forced outage from load runback due to issue with Exhaust Frame Blower.
BR9 | MO | 14 | 5272 | 2014-02-25 06:59 | 2014-02-25 20:03 | 13.07 | [5 empty] | 0 | 139 | 138 | Gas Turbine - Boroscope Inspection | F590Eddy current inspection of R3 blade and boroscope of turbine section.
BR9 | MO | 12 | 5160 | 2014-02-20 13:00 | 2014-02-20 17:04 | 4.07 | [5 empty] | 0 | 139 | 138 | Gas Turbine - Cooling And Seal Air System | F590Changed brushes on DC mantling air fan.

## FEB-14 Impact By Cause Code
Unit | Event | Event | Cause | Event | Event | Event | Equiv. | MWH | EAF | EUOR | EFOR | Unit | Unit | Unit | Event | Event
Name | Type | No | Code | Start | End | Hours | Hours | Lost | Lost | Impact | Impact | GAC | GMC | NMC | Cause | Description
|  |  | (0000-0009) |  |  | 0 | 0 | 0 | 0% | 0% | 0%
TC2 | PO | 20 | 360 | 2014-02-08 03:21 | 2014-03-01 | 500.65 | 500.65 | 285370.5 | 3.496% |  |  | 0 | 607 | 570 | Burners | TC2 began the planned outage for the replacement of all 30 burners. This effort i
|  |  | (0010-0130) |  | Fuel Handling | 500.65 | 500.65 | 285370.5 | 3.496% | 0% | 0%
|  |  | (0500-1999) |  | Boiler | 0 | 0 | 0 | 0% | 0% | 0%
0
0
|  |  | (3110-3999) |  | Balance Of Plant | 0 | 0 | 0 | 0% | 0% | 0%
|  |  | (4000-4499) |  | Steam Turbine | 0 | 0 | 0 | 0% | 0% | 0%
0
0
|  |  | (4500-4899) |  | Generator | 0 | 0 | 0 | 0% | 0% | 0%
|  |  | (8000-8835) |  | Pollution Control Equip. | 0 | 0 | 0 | 0% | 0% | 0%
|  |  | (0010-0130) |  | Fuel Handling | 0 | 0 | 0 | 0% | 0% | 0%
0
MC2 | D1 | 1 | 250 | 2014-01-01 | 2014-01-01 10:30 | 10.5 | 2.5455 | 761.0909 | 0.009323% | 0.009647% | 0.01% | 250 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Replace Belt
MC2 | D1 | 3 | 250 | 2014-01-02 04:15 | 2014-01-02 05:24 | 1.15 | 0.27879 | 83.3576 | 0.001021% | 0.001057% | 0.001095% | 250 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Belt Slipping
GH4 | D1 | 2 | 250 | 2014-01-07 03:55 | 2014-01-07 04:36 | 0.68333 | 0.17147 | 84.1933 | 0.001031% | 0.001067% | 0.001106% | 400 | 534 | 491 | Pulverizer Feeders | 4-4 Feeder tripped.
MC2 | D1 | 11 | 250 | 2014-01-07 05:45 | 2014-01-07 07:15 | 1.5 | 0.40909 | 122.3182 | 0.001498% | 0.00155% | 0.001607% | 240 | 330 | 299 | Pulverizer Feeders | 2A Coal Feeder - Plugged, Frozen/Wet Coal
GR3 | D1 | 1 | 250 | 2014-01-07 13:15 | 2014-01-07 14:15 | 1 | 0.26667 | 18.9333 | 0.0002319% | 0.00024% | 0.0002488% | 55 | 75 | 71 | Pulverizer Feeders | 4-4 Feeder plugged with coal and ice.
MC1 | D1 | 2 | 250 | 2014-01-07 16:50 | 2014-01-07 18:06 | 1.2667 | 0.26869 | 81.4121 | 0.0009973% | 0.001032% | 0.00107% | 260 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen/Wet Coal
MC1 | D1 | 3 | 250 | 2014-01-08 05:45 | 2014-01-08 06:43 | 0.96667 | 0.26364 | 79.8818 | 0.0009786% | 0.001013% | 0.00105% | 240 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen/Wet Coal
MC4 | D1 | 7 | 250 | 2014-01-08 21:55 | 2014-01-09 05:00 | 7.0833 | 1.5516 | 754.0714 | 0.009237% | 0.009558% | 0.00991% | 410 | 525 | 486 | Pulverizer Feeders | 4A Coal Feeder - VFD Beck Drive Bad Card
CR4 | D1 | 3 | 250 | 2014-01-09 19:11 | 2014-01-10 02:13 | 7.0333 | 1.8002 | 279.0308 | 0.003418% | 0.003537% | 0.003667% | 125 | 168 | 155 | Pulverizer Feeders | 4A feeder belt broke. Repaired same.
CR5 | D4 | 1 | 250 | 2014-01-09 19:40 | 2014-01-10 04:37 | 8.95 | 3.2635 | 548.274 | 0.006716% | 0.00695% |  | 115 | 181 | 168 | Pulverizer Feeders | 5C1 coal feeder repair - changing out a roller bearing.
MC2 | D4 | 15 | 250 | 2014-01-09 21:02 | 2014-01-10 04:09 | 7.1167 | 2.2644 | 677.0538 | 0.008294% | 0.008582% |  | 225 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Calibration
MC2 | D4 | 16 | 250 | 2014-01-13 00:35 | 2014-01-13 05:00 | 4.4167 | 1.1376 | 340.1503 | 0.004167% | 0.004312% |  | 245 | 330 | 299 | Pulverizer Feeders | 2D Coal Feeder - Calibration
MC1 | D4 | 7 | 250 | 2014-01-15 23:00 | 2014-01-16 06:17 | 7.2833 | 1.9864 | 601.8682 | 0.007373% | 0.007629% |  | 240 | 330 | 303 | Pulverizer Feeders | 1B Coal Feeder - Calibration & Mill Inspection
MC1 | D4 | 8 | 250 | 2014-01-16 23:00 | 2014-01-17 04:14 | 5.2333 | 1.4273 | 432.4636 | 0.005298% | 0.005482% |  | 240 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Calibration & Mill Inspection
MC1 | D4 | 14 | 250 | 2014-01-20 22:08 | 2014-01-21 04:20 | 6.2 | 1.6909 | 512.3455 | 0.006276% | 0.006494% |  | 240 | 330 | 303 | Pulverizer Feeders | 1A Coal Feeder - Calibration & Mill Inspection
MC2 | D1 | 21 | 250 | 2014-01-23 22:08 | 2014-01-23 23:28 | 1.3333 | 0.36364 | 108.7273 | 0.001332% | 0.001378% | 0.001429% | 240 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Plugged, Frozen Coal
MC1 | D1 | 15 | 250 | 2014-01-24 02:53 | 2014-01-24 03:08 | 0.25 | 0.079545 | 24.1023 | 0.0002953% | 0.0003055% | 0.0003167% | 225 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen Coal
MC1 | D1 | 16 | 250 | 2014-01-24 03:08 | 2014-01-24 03:45 | 0.61667 | 0.14949 | 45.297 | 0.0005549% | 0.0005742% | 0.0005953% | 250 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen Coal
MC2 | D1 | 22 | 250 | 2014-01-24 05:33 | 2014-01-24 07:30 | 1.95 | 0.53182 | 159.0136 | 0.001948% | 0.002016% | 0.00209% | 240 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Plugged, Frozen Coal
MC1 | D1 | 17 | 250 | 2014-01-24 07:43 | 2014-01-24 09:04 | 1.35 | 0.36818 | 111.5591 | 0.001367% | 0.001414% | 0.001466% | 240 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Plugged, Frozen Coal
GH1 | D1 | 5 | 250 | 2014-01-28 21:25 | 2014-01-29 04:05 | 6.6667 | 0.73501 | 353.5397 | 0.004331% | 0.004481% | 0.004646% | 460 | 517 | 481 | Pulverizer Feeders | 1-4 Feeder belt was torn when cleanout conveyor failed.
MC2 | D1 | 43 | 250 | 2014-02-05 03:53 | 2014-02-05 04:29 | 0.6 | 0.25455 | 76.1091 | 0.0009323% | 0.0009647% | 0.001% | 190 | 330 | 299 | Pulverizer Feeders | 2A Coal Feeder - Wet Coal
MC2 | D1 | 44 | 250 | 2014-02-05 05:48 | 2014-02-05 07:56 | 2.1333 | 0.51717 | 154.6343 | 0.001894% | 0.00196% | 0.002032% | 250 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Wet Coal
MC1 | D1 | 20 | 250 | 2014-02-05 07:28 | 2014-02-05 09:30 | 2.0333 | 0.40051 | 121.353 | 0.001487% | 0.001538% | 0.001595% | 265 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Wet Coal
MC1 | D4 | 21 | 250 | 2014-02-06 | 2014-02-06 03:12 | 3.2 | 0.87273 | 264.4364 | 0.003239% | 0.003352% |  | 240 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Repair Discharge Flapper
CR6 | D1 | 7 | 250 | 2014-02-07 01:12 | 2014-02-07 02:10 | 0.96667 | 0.22593 | 54.2222 | 0.0006642% | 0.0006873% | 0.0007126% | 200 | 261 | 240 | Pulverizer Feeders | D1 feeder plugged due to torn belt.
GH1 | D1 | 7 | 250 | 2014-02-07 12:35 | 2014-02-07 13:45 | 1.1667 | 0.12863 | 61.8694 | 0.0007579% | 0.0007842% | 0.0008131% | 460 | 517 | 481 | Pulverizer Feeders | Metal hung in 1-4 mill feeder.
MC3 | D1 | 20 | 250 | 2014-02-07 18:02 | 2014-02-08 05:30 | 11.4667 | 2.6566 | 1046.6925 | 0.01282% | 0.01327% | 0.01376% | 325 | 423 | 394 | Pulverizer Feeders | 3C Coal Feeder - Replace Speed Sensor
CR6 | D1 | 8 | 250 | 2014-02-08 00:05 | 2014-02-08 01:13 | 1.1333 | 0.22146 | 53.1494 | 0.0006511% | 0.0006737% | 0.0006985% | 210 | 261 | 240 | Pulverizer Feeders | D2 feeder plugged due to wet coal.
GH4 | U1 | 7 | 250 | 2014-02-09 03:51 | 2014-02-09 05:38 | 1.7833 | 1.7833 | 875.6167 | 0.01073% | 0.0111% | 0.01151% | 0 | 534 | 491 | Pulverizer Feeders | 4-6 Mill Feeder coal inlet plugged causing controls to see this feeder as
GH1 | D1 | 8 | 250 | 2014-02-09 16:20 | 2014-02-09 19:43 | 3.3833 | 2.9449 | 1416.4845 | 0.01735% | 0.01795% | 0.01862% | 67 | 517 | 481 | Pulverizer Feeders | 1-4 Feeder belt bound up.
GH1 | PD | 9 | 250 | 2014-02-10 09:00 | 2014-02-10 15:33 | 6.55 | 0.84884 | 408.2918 | 0.005002% |  |  | 450 | 517 | 481 | Pulverizer Feeders | 1-4 Mill off to replace feeder discharge pipe pluggage detector.
MC3 | D4 | 24 | 250 | 2014-02-10 11:00 | 2014-02-10 16:05 | 5.0833 | 1.1176 | 440.3392 | 0.005394% | 0.005582% |  | 330 | 423 | 394 | Pulverizer Feeders | 3C Coal Feeder - Calibration
MC4 | D1 | 20 | 250 | 2014-02-11 09:10 | 2014-02-11 09:20 | 0.16667 | 0.030159 | 14.6571 | 0.0001796% | 0.0001858% | 0.0001926% | 430 | 525 | 486 | Pulverizer Feeders | 4C Coal Feeder - Microprocessor Issue
MC1 | D1 | 35 | 250 | 2014-02-14 03:00 | 2014-02-14 05:05 | 2.0833 | 0.56818 | 172.1591 | 0.002109% | 0.002182% | 0.002262% | 240 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor Gearbox
MC1 | D1 | 36 | 250 | 2014-02-14 05:05 | 2014-02-14 06:50 | 1.75 | 0.42424 | 128.5455 | 0.001575% | 0.001629% | 0.001689% | 250 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor Gearbox
MC1 | D1 | 37 | 250 | 2014-02-14 06:50 | 2014-02-14 12:00 | 5.1667 | 0.78283 | 237.197 | 0.002906% | 0.003007% | 0.003117% | 280 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor GearboxGas Guns in Service
GH2 | D1 | 10 | 250 | 2014-02-15 03:20 | 2014-02-15 10:00 | 6.6667 | 0.64178 | 306.1297 | 0.00375% | 0.00388% | 0.004023% | 460 | 509 | 477 | Pulverizer Feeders | 2-1 Feeder control issue.
CR6 | D1 | 12 | 250 | 2014-02-16 04:54 | 2014-02-16 12:17 | 7.3833 | 1.4427 | 346.2529 | 0.004242% | 0.004389% | 0.00455% | 210 | 261 | 240 | Pulverizer Feeders | 6B feeder belt torn. Repaired & put back in service.
GH2 | D1 | 12 | 250 | 2014-02-19 05:20 | 2014-02-19 11:30 | 6.1667 | 0.7148 | 340.9597 | 0.004177% | 0.004322% | 0.004481% | 450 | 509 | 477 | Pulverizer Feeders | 2-6 Feeder off to replace the belt.
GH3 | D1 | 22 | 250 | 2014-02-20 13:50 | 2014-02-20 16:25 | 2.5833 | 0.62255 | 300.0686 | 0.003676% | 0.003804% | 0.003943% | 400 | 527 | 482 | Pulverizer Feeders | 3-3 Feeder controls.
MC2 | D1 | 66 | 250 | 2014-02-24 00:16 | 2014-02-24 03:46 | 3.5 | 0.15909 | 47.5682 | 0.0005827% | 0.000603% | 0.0006251% | 315 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Plugged, Foreign Material
GH4 | PD | 8 | 250 | 2014-02-25 03:58 | 2014-02-25 05:33 | 1.5833 | 0.041511 | 20.3817 | 0.0002497% |  |  | 520 | 534 | 491 | Pulverizer Feeders | Boiler exit gas was high due to both top mills being in service w
CR4 | D4 | 4 | 255 | 2014-01-19 21:00 | 2014-01-20 06:24 | 9.4 | 2.406 | 372.9226 | 0.004568% | 0.004727% |  | 125 | 168 | 155 | Pulverizer Feeder Coal Scales | 4C2 Feeder Belt Repair
BR1 | PD | 1 | 260 | 2014-01-03 | 2014-01-03 02:00 | 2 | 0.59649 | 63.8246 | 0.0007819% |  |  | 80 | 114 | 107 | Primary Air Fan | 1-3 mil primary air fan housing leak repair
GR4 | D1 | 25 | 263 | 2014-02-01 21:38 | 2014-02-01 22:48 | 1.1667 | 0.27778 | 27.2222 | 0.0003335% | 0.0003451% | 0.0003577% | 80 | 105 | 98 | Primary Air Fan Drives | 5-2 PA Fan Control Jack Minimum Stop failed to disengage. I&E found and repaired
TC1 | D1 | 3 | 280 | 2014-01-03 09:40 | 2014-01-03 11:31 | 1.85 | 0.13988 | 53.5733 | 0.0006563% | 0.0006791% | 0.000704% | 379 | 410 | 383 | Pulverizer Fires | Derate due to fires in the B and D coal mills.
TC1 | D1 | 4 | 280 | 2014-01-04 02:47 | 2014-01-04 03:56 | 1.15 | 0.098171 | 37.5994 | 0.0004606% | 0.0004766% | 0.0004941% | 375 | 410 | 383 | Pulverizer Fires | Derate due to fire in the D coal mill.
TC1 | D1 | 5 | 280 | 2014-01-04 05:09 | 2014-01-04 08:18 | 3.15 | 0.33037 | 126.5301 | 0.00155% | 0.001604% | 0.001663% | 367 | 410 | 383 | Pulverizer Fires | Derate due to fires in the D coal mill and the E coal mill was unavailable for a m
TC1 | D1 | 6 | 280 | 2014-01-07 17:25 | 2014-01-07 21:08 | 3.7167 | 0.38073 | 145.8202 | 0.001786% | 0.001848% | 0.001916% | 368 | 410 | 383 | Pulverizer Fires | Derate required due to A & B coal mill fires.
TC1 | D1 | 13 | 280 | 2014-01-13 06:39 | 2014-01-13 10:33 | 3.9 | 0.33293 | 127.511 | 0.001562% | 0.001616% | 0.001676% | 375 | 410 | 383 | Pulverizer Fires | Unit derate due to two coal mill issues: 1E mill had a fire that needed to be put out
TC1 | D1 | 14 | 280 | 2014-01-14 08:36 | 2014-01-14 10:39 | 2.05 | 0.175 | 67.025 | 0.0008211% | 0.0008496% | 0.0008808% | 375 | 410 | 383 | Pulverizer Fires | Derate due to fire in the 1B Coal Mill.
TC1 | D1 | 16 | 280 | 2014-01-17 15:20 | 2014-01-17 16:00 | 0.66667 | 0.043902 | 16.8146 | 0.000206% | 0.0002131% | 0.000221% | 383 | 410 | 383 | Pulverizer Fires | Fires in the 1A and 1B coal mills required unit derate.
TC1 | D1 | 17 | 280 | 2014-01-17 16:00 | 2014-01-17 16:45 | 0.75 | 0.22866 | 87.5762 | 0.001073% | 0.00111% | 0.001151% | 285 | 410 | 383 | Pulverizer Fires | Additional fire in the 1C mill following 1A and 1B mill fires
TC1 | D1 | 18 | 280 | 2014-01-17 16:45 | 2014-01-17 19:40 | 2.9167 | 1.5793 | 604.8598 | 0.00741% | 0.007667% | 0.007949% | 188 | 410 | 383 | Pulverizer Fires | Additional fire in the 1D mill after fires in the 1A, 1B, and 1C mills
TC1 | D1 | 19 | 280 | 2014-01-17 19:40 | 2014-01-17 20:08 | 0.46667 | 0.056911 | 21.7967 | 0.000267% | 0.0002763% | 0.0002864% | 360 | 410 | 383 | Pulverizer Fires | Some of the mills were returned to service. However, unit derate was still necessary
GH2 | D1 | 5 | 280 | 2014-01-18 13:37 | 2014-01-18 14:14 | 0.61667 | 0.059365 | 28.317 | 0.0003469% | 0.0003589% | 0.0003721% | 460 | 509 | 477 | Pulverizer Fires | 2-6 Mill off due to fire in the pyrite line.
GH2 | D1 | 14 | 280 | 2014-02-27 07:34 | 2014-02-27 12:11 | 4.6167 | 0.44443 | 211.9948 | 0.002597% | 0.002687% | 0.002786% | 460 | 509 | 477 | Pulverizer Fires | Load was reduced due to a fire in 2-1 Mill.
MC3 | D1 | 13 | 300 | 2014-01-23 17:19 | 2014-01-23 23:03 | 5.7333 | 1.1928 | 469.9436 | 0.005757% | 0.005957% | 0.006176% | 335 | 423 | 394 | Pulverizer Motors and Drives | 3C Coal Mill Motor - Failed to Start, Breaker Issue
MC3 | D1 | 15 | 300 | 2014-01-23 23:03 | 2014-01-23 23:23 | 0.33333 | 0.073286 | 28.8747 | 0.0003537% | 0.000366% | 0.0003795% | 330 | 423 | 394 | Pulverizer Motors and Drives | 3C Coal Mill Motor - Failed to Start, Breaker Issue
MC3 | D4 | 1 | 310 | 2014-01-01 23:20 | 2014-01-02 01:35 | 2.25 | 0.54787 | 215.8617 | 0.002644% | 0.002736% |  | 320 | 423 | 394 | Pulverizer Mills | 3A Coal Mill - Inspection
BR2 | PD | 1 | 310 | 2014-01-02 22:00 | 2014-01-03 02:00 | 4 | 1.2222 | 205.3333 | 0.002515% |  |  | 125 | 180 | 168 | Pulverizer Mills | Inspect 2-3 mill gearbox
CR6 | D1 | 2 | 310 | 2014-01-05 02:54 | 2014-01-05 19:35 | 16.6833 | 3.26 | 782.3908 | 0.009584% | 0.009917% | 0.01028% | 210 | 261 | 240 | Pulverizer Mills | 6C coal mill roller maintenance.
GR4 | D1 | 6 | 310 | 2014-01-08 09:10 | 2014-01-08 13:30 | 4.3333 | 1.3619 | 133.4667 | 0.001635% | 0.001692% | 0.001754% | 72 | 105 | 98 | Pulverizer Mills | A Sluice Water line on the Conveyor Floor had frozen and burst. When it thawed it
BR3 | PD | 1 | 310 | 2014-01-08 22:33 | 2014-01-09 01:15 | 2.7 | 0.63217 | 261.7168 | 0.003206% |  |  | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
MC4 | D1 | 8 | 310 | 2014-01-09 07:00 | 2014-01-09 08:38 | 1.6333 | 0.15556 | 75.6 | 0.0009261% | 0.0009583% | 0.0009935% | 475 | 525 | 486 | Pulverizer Mills | 4A Coal Mill - Breaker Issue
BR3 | PD | 2 | 310 | 2014-01-09 21:20 | 2014-01-10 00:33 | 3.2167 | 0.75314 | 311.7985 | 0.00382% | 0.003952% | 0.004098% | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
MC1 | D4 | 4 | 310 | 2014-01-09 21:26 | 2014-01-10 01:17 | 3.85 | 0.99167 | 300.475 | 0.003681% | 0.003809% |  | 245 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Roller Adjustment
BR2 | D1 | 2 | 310 | 2014-01-11 18:55 | 2014-01-11 21:25 | 2.5 | 0.625 | 105 | 0.001286% | 0.001331% | 0.00138% | 135 | 180 | 168 | Pulverizer Mills | Repair 2-2 mill broken spring bolt
MC1 | D4 | 5 | 310 | 2014-01-13 22:00 | 2014-01-14 07:17 | 9.2833 | 2.5318 | 767.1409 | 0.009398% | 0.009724% |  | 240 | 330 | 303 | Pulverizer Mills | 1D Coal Mill & Feeder - Inspection
BR3 | PD | 5 | 310 | 2014-01-13 22:00 | 2014-01-14 00:29 | 2.4833 | 0.58144 | 240.7149 | 0.002949% |  |  | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
BR3 | PD | 6 | 310 | 2014-01-14 21:35 | 2014-01-15 00:37 | 3.0333 | 0.71021 | 294.0276 | 0.003602% |  |  | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
MC1 | D4 | 6 | 310 | 2014-01-14 22:34 | 2014-01-15 04:42 | 6.1333 | 1.6727 | 506.8364 | 0.006209% | 0.006424% |  | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Inspection
BR3 | PD | 7 | 310 | 2014-01-15 21:57 | 2014-01-16 00:40 | 2.7167 | 0.63607 | 263.3324 | 0.003226% |  |  | 350 | 457 | 414 | Pulverizer Mills | Adjust 3-4 mill riffle elements
MC3 | D4 | 10 | 310 | 2014-01-17 04:00 | 2014-01-17 05:15 | 1.25 | 0.27482 | 108.2801 | 0.001326% | 0.001373% |  | 330 | 423 | 394 | Pulverizer Mills | 3B Mill - Coal Burner Logic Change
MC2 | D4 | 20 | 310 | 2014-01-19 23:30 | 2014-01-20 04:26 | 4.9333 | 1.2707 | 379.9414 | 0.004654% | 0.004816% |  | 245 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Inspection
MC2 | D1 | 25 | 310 | 2014-01-26 12:32 | 2014-01-26 18:32 | 6 | 1.6364 | 489.2727 | 0.005994% | 0.006202% | 0.00643% | 240 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Explosion, Ductwork Repair
MC2 | D1 | 29 | 310 | 2014-01-27 09:55 | 2014-01-27 13:56 | 4.0167 | 1.0346 | 309.3442 | 0.003789% | 0.003921% | 0.004065% | 245 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Ductwork Repair
MC2 | D1 | 30 | 310 | 2014-01-27 13:56 | 2014-01-27 15:52 | 1.9333 | 0.35152 | 105.103 | 0.001288% | 0.001332% | 0.001381% | 270 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Ductwork Repair
MC2 | D1 | 31 | 310 | 2014-01-27 15:52 | 2014-01-27 16:39 | 0.78333 | 0.21364 | 63.8773 | 0.0007825% | 0.0008097% | 0.0008395% | 240 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Ductwork Repair
MC2 | D1 | 32 | 310 | 2014-01-27 16:39 | 2014-01-27 20:39 | 4 | 0.72727 | 217.4545 | 0.002664% | 0.002756% | 0.002858% | 270 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Ductwork Repair
MC4 | D1 | 15 | 310 | 2014-01-30 02:30 | 2014-01-30 06:55 | 4.4167 | 0.88333 | 429.3 | 0.005259% | 0.005442% | 0.005642% | 420 | 525 | 486 | Pulverizer Mills | 4E Coal Mill - Primary Air Fan Flow Issues
TC2 | D1 | 17 | 310 | 2014-02-02 16:30 | 2014-02-02 19:00 | 2.5 | 0.40259 | 229.479 | 0.002811% | 0.002909% | 0.003016% | 509.25 | 607 | 570 | Pulverizer Mills | The 2D mill was performing poorly and was taken off-line to investigate. Some mil
MC2 | D4 | 38 | 310 | 2014-02-02 22:00 | 2014-02-03 06:25 | 8.4167 | 2.2955 | 686.3409 | 0.008408% | 0.0087% |  | 240 | 330 | 299 | Pulverizer Mills | 2A Coal Mill - Inspection
MC4 | D4 | 16 | 310 | 2014-02-02 23:00 | 2014-02-03 03:55 | 4.9167 | 0.98333 | 477.9 | 0.005854% | 0.006058% |  | 420 | 525 | 486 | Pulverizer Mills | 4C Coal Mill - Inspection
MC2 | D4 | 41 | 310 | 2014-02-03 23:00 | 2014-02-04 04:15 | 5.25 | 1.4318 | 428.1136 | 0.005244% | 0.005427% |  | 240 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Adjust Rollers & Inspection
MC2 | D4 | 42 | 310 | 2014-02-04 23:00 | 2014-02-05 04:45 | 5.75 | 1.5682 | 468.8864 | 0.005744% | 0.005943% |  | 240 | 330 | 299 | Pulverizer Mills | 2B Coal Mill - Inspection
MC4 | D1 | 19 | 310 | 2014-02-07 06:50 | 2014-02-07 07:05 | 0.25 | 0.030952 | 15.0429 | 0.0001843% | 0.0001907% | 0.0001977% | 460 | 525 | 486 | Pulverizer Mills | 4B Coal Mill - Swing Valve & Ignitor Gas Valve Issues
MC3 | D1 | 23 | 310 | 2014-02-09 21:52 | 2014-02-10 07:58 | 10.1 | 2.4593 | 968.9792 | 0.01187% | 0.01228% | 0.01273% | 320 | 423 | 394 | Pulverizer Mills | 3C Primary Air Fan Housing InspectionRepair Suction Box & Hot Air Damper Linkage
TC1 | D1 | 27 | 310 | 2014-02-10 07:22 | 2014-02-10 07:45 | 0.38333 | 0.032724 | 12.5331 | 0.0001535% | 0.0001589% | 0.0001647% | 375 | 410 | 383 | Pulverizer Mills | Derate on TC1 to 500 MW's due to D coal mill fire. Additional issue with the E co
TC1 | D1 | 28 | 310 | 2014-02-10 10:00 | 2014-02-10 13:58 | 3.9667 | 0.33862 | 129.6907 | 0.001589% | 0.001644% | 0.001704% | 375 | 410 | 383 | Pulverizer Mills | Derate required due to fire on the 1D coal mill.
BR2 | D1 | 4 | 310 | 2014-02-11 20:04 | 2014-02-12 02:17 | 6.2167 | 1.7269 | 290.1111 | 0.003554% | 0.003677% | 0.003813% | 130 | 180 | 168 | Pulverizer Mills | 2-4 mill west door broken spring bolt
TC1 | D1 | 29 | 310 | 2014-02-11 22:17 | 2014-02-11 23:30 | 1.2167 | 0.10386 | 39.7791 | 0.0004873% | 0.0005042% | 0.0005228% | 375 | 410 | 383 | Pulverizer Mills | Derate required due to high temperature on the 1B coal mill.
MC1 | D4 | 34 | 310 | 2014-02-13 22:00 | 2014-02-14 03:00 | 5 | 1.3636 | 413.1818 | 0.005061% | 0.005237% |  | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Inspection
BR2 | D1 | 5 | 310 | 2014-02-14 18:23 | 2014-02-14 19:11 | 0.8 | 0.2 | 33.6 | 0.0004116% | 0.0004259% | 0.0004416% | 135 | 180 | 168 | Pulverizer Mills | 2-4 hot air damper not making limit
BR2 | D1 | 6 | 310 | 2014-02-16 06:34 | 2014-02-16 17:57 | 11.3833 | 3.4782 | 584.3444 | 0.007158% | 0.007407% | 0.007679% | 125 | 180 | 168 | Pulverizer Mills | 2-2 mill shaft broken
BR2 | D1 | 7 | 310 | 2014-02-16 17:57 | 2014-02-19 12:47 | 66.83 | 18.5639 | 3118.7333 | 0.0382% | 0.03953% | 0.04099% | 130 | 180 | 168 | Pulverizer Mills | Broken coal mill shaft 2-2 mill 6543464
BR2 | D1 | 8 | 310 | 2014-02-19 12:47 | 2014-02-20 22:00 | 33.22 | 8.305 | 1395.24 | 0.01709% | 0.01769% | 0.01834% | 135 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
BR1 | PD | 2 | 310 | 2014-02-19 22:00 | 2014-02-20 02:51 | 4.85 | 1.2338 | 132.0136 | 0.001617% |  |  | 85 | 114 | 107 | Pulverizer Mills | 1-1 & 1-4 mill inspection
BR1 | PD | 3 | 310 | 2014-02-20 22:00 | 2014-02-21 03:39 | 5.65 | 1.4373 | 153.789 | 0.001884% |  |  | 85 | 114 | 107 | Pulverizer Mills | 1-3 mill inspection
BR2 | D1 | 10 | 310 | 2014-02-21 09:00 | 2014-02-21 22:13 | 13.22 | 3.6722 | 616.9333 | 0.007557% | 0.00782% | 0.008108% | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
BR2 | D1 | 12 | 310 | 2014-02-23 08:51 | 2014-02-24 08:24 | 23.55 | 6.5417 | 1099 | 0.01346% | 0.01393% | 0.01444% | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
MC3 | D4 | 35 | 310 | 2014-02-24 23:00 | 2014-02-25 06:39 | 7.65 | 1.8628 | 733.9298 | 0.008991% | 0.009303% |  | 320 | 423 | 394 | Pulverizer Mills | 3C Coal Mill Pyrite Hopper - Replace Top Gate
BR1 | PD | 5 | 310 | 2014-02-27 | 2014-02-27 02:28 | 2.4667 | 0.84386 | 90.293 | 0.001106% |  |  | 75 | 114 | 107 | Pulverizer Mills | 1-2 mill inspection
MC1 | D4 | 48 | 310 | 2014-02-27 22:00 | 2014-02-28 02:02 | 4.0333 | 1.1 | 333.3 | 0.004083% | 0.004225% |  | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Inspection & Adjust Rollers
CR4 | D4 | 13 | 310 | 2014-02-28 22:00 | 2014-03-01 06:51 | 8.85 | 2.0018 | 310.2768 | 0.003801% | 0.003933% |  | 130 | 168 | 155 | Pulverizer Mills | 4A Mill inspection
GH2 | D1 | 6 | 312 | 2014-02-01 14:40 | 2014-02-01 18:00 | 3.3333 | 0.18991 | 90.5894 | 0.00111% | 0.001148% | 0.001191% | 480 | 509 | 477 | Pulverizer Mill Classifiers | 2-1 Mill not grinding, took off for inspection.
GH1 | D1 | 14 | 320 | 2014-02-25 11:17 | 2014-02-25 12:57 | 1.6667 | 0.18375 | 88.3849 | 0.001083% | 0.00112% | 0.001162% | 460 | 517 | 481 | Foreign Object in Mill | 1-3 Mill had a noise in the pyrite section. Removed the mill to
GR4 | D1 | 26 | 338 | 2014-02-04 22:14 | 2014-02-05 11:55 | 13.6833 | 3.2579 | 319.2778 | 0.003911% | 0.004047% | 0.004196% | 80 | 105 | 98 | Pulverizer Control Systems (Temp and Pressure) | 5-3 PA Fan control jack would not react to input from PA Controller.
BR3 | U1 | 8 | 339 | 2014-01-30 03:57 | 2014-02-01 16:05 | 60.1333 | 60.1333 | 24895.2 | 0.305% | 0.3156% | 0.3272% | 0 | 457 | 414 | Pulverizer System Puff | 3-5 Mill puff causing D corner burner damage and associated boiler tube leak.
GH1 | PD | 3 | 340 | 2014-01-16 21:57 | 2014-01-17 00:49 | 2.8667 | 0.31605 | 152.0221 | 0.001862% |  |  | 460 | 517 | 481 | Other Pulverizer Problems | 1-1 Mill journal replacement.
GR3 | D1 | 3 | 340 | 2014-01-23 18:56 | 2014-01-23 19:09 | 0.21667 | 0.043333 | 3.0767 | 3.769e-05% | 3.9e-05% | 4.043e-05% | 60 | 75 | 71 | Other Pulverizer Problems | 4-4 Pulverizer Pyrite Trap plugged. Pulv O/S to clear trap.
CR6 | D1 | 10 | 340 | 2014-02-09 06:50 | 2014-02-09 07:15 | 0.41667 | 0.15326 | 36.7816 | 0.0004506% | 0.0004662% | 0.0004834% | 165 | 261 | 240 | Other Pulverizer Problems | Support fuel unavailable due to loss of communication between precipitator & DCS.
GH2 | PD | 8 | 340 | 2014-02-13 23:00 | 2014-02-14 02:11 | 3.1833 | 0.30645 | 146.1769 | 0.001791% |  |  | 460 | 509 | 477 | Other Pulverizer Problems | 2-5 Mill off to replace pyrite scraper.
GH2 | PD | 9 | 340 | 2014-02-14 02:11 | 2014-02-14 03:39 | 1.4667 | 0.14119 | 67.3485 | 0.000825% |  |  | 460 | 509 | 477 | Other Pulverizer Problems | 2-6 Mill off to inspect grinding section and classifiers.
GH2 | D1 | 11 | 340 | 2014-02-17 06:24 | 2014-02-17 14:00 | 7.6 | 0.80629 | 384.5988 | 0.004711% | 0.004875% | 0.005054% | 455 | 509 | 477 | Other Pulverizer Problems | Removed 2-4 Mill from service for journal issue.
BR2 | PD | 3 | 344 | 2014-01-13 09:44 | 2014-01-13 12:15 | 2.5167 | 0.9088 | 152.6778 | 0.00187% |  |  | 115 | 180 | 168 | Pulverizer Inspection | Inspect 2-3 mill concerning thrust bearing issue
GH1 | PD | 2 | 344 | 2014-01-14 23:37 | 2014-01-15 02:30 | 2.8833 | 0.31789 | 152.9059 | 0.001873% |  |  | 460 | 517 | 481 | Pulverizer Inspection | 1-6 Mill off to inspect and clean air flow transmitters.
GH2 | PD | 2 | 344 | 2014-01-14 23:43 | 2014-01-15 04:11 | 4.4667 | 0.51775 | 246.9654 | 0.003025% |  |  | 450 | 509 | 477 | Pulverizer Inspection | 2-6 Mill off to inspect and repair spring can shaft.
GH2 | PD | 4 | 344 | 2014-01-17 23:30 | 2014-01-18 11:44 | 12.2333 | 1.1777 | 561.7479 | 0.006881% |  |  | 460 | 509 | 477 | Pulverizer Inspection | 2-6 Mill off for gear box inspection.
CR6 | D4 | 5 | 344 | 2014-01-20 07:54 | 2014-01-20 11:54 | 4 | 0.62835 | 150.8046 | 0.001847% | 0.001912% |  | 220 | 261 | 240 | Pulverizer Inspection | 6A coal mill making noise. Removed a piece of metal from journal shield area of mill
CR4 | D4 | 5 | 344 | 2014-01-20 09:52 | 2014-01-20 16:35 | 6.7167 | 1.5192 | 235.4831 | 0.002885% | 0.002985% |  | 130 | 168 | 155 | Pulverizer Inspection | 4C mill making noise - made roller adjustment after removing debris buildup on journal
CR6 | D1 | 6 | 344 | 2014-01-20 13:08 | 2014-01-20 18:00 | 4.8667 | 0.7645 | 183.4789 | 0.002248% | 0.002326% | 0.002411% | 220 | 261 | 240 | Pulverizer Inspection | 6D coal mill making noise. Removed metal from journal shield area of mill.
GH1 | D1 | 4 | 344 | 2014-01-27 06:00 | 2014-01-27 11:33 | 5.55 | 0.6119 | 294.3218 | 0.003605% | 0.003731% | 0.003868% | 460 | 517 | 481 | Pulverizer Inspection | 1-6 Mill off to inspect grinding section.
CR5 | D4 | 4 | 344 | 2014-02-02 23:00 | 2014-02-03 04:50 | 5.8333 | 1.8048 | 303.2044 | 0.003714% | 0.003843% | 0.003985% | 125 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
CR5 | D4 | 5 | 344 | 2014-02-03 23:00 | 2014-02-04 04:55 | 5.9167 | 1.6671 | 280.0773 | 0.003431% | 0.00355% |  | 130 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
CR5 | D4 | 6 | 344 | 2014-02-04 23:00 | 2014-02-05 05:00 | 6 | 1.8564 | 311.8674 | 0.00382% | 0.003953% |  | 125 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
GH2 | PD | 7 | 344 | 2014-02-06 23:00 | 2014-02-07 01:24 | 2.4 | 0.23104 | 110.2067 | 0.00135% |  |  | 460 | 509 | 477 | Pulverizer Inspection | 2-2 Mill was removed from service to inspect due to high differen
GH1 | D1 | 11 | 344 | 2014-02-21 08:30 | 2014-02-21 12:30 | 4 | 0.51838 | 249.3385 | 0.003054% | 0.003161% | 0.003277% | 450 | 517 | 481 | Pulverizer Inspection | 1-6 Mill off to inspect grinding section.
GH1 | PD | 13 | 344 | 2014-02-24 13:42 | 2014-02-24 16:59 | 3.2833 | 0.36199 | 174.1183 | 0.002133% |  |  | 460 | 517 | 481 | Pulverizer Inspection | 1-1 Mill off to inspect grinding section.
GH2 | D1 | 13 | 344 | 2014-02-24 23:55 | 2014-02-25 06:30 | 6.5833 | 0.63376 | 302.303 | 0.003703% | 0.003832% | 0.003973% | 460 | 509 | 477 | Pulverizer Inspection | 2-6 Mill off to inspect the grinding section.
GR4 | PD | 9 | 345 | 2014-01-10 19:25 | 2014-01-11 03:57 | 8.5333 | 0.8127 | 79.6444 | 0.0009756% |  |  | 95 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
GR4 | PD | 10 | 345 | 2014-01-11 03:57 | 2014-01-11 05:23 | 1.4333 | 0.16381 | 16.0533 | 0.0001967% |  |  | 93 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
GR4 | PD | 11 | 345 | 2014-01-11 05:23 | 2014-01-11 06:15 | 0.86667 | 0.16508 | 16.1778 | 0.0001982% |  |  | 85 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
GR4 | PD | 12 | 345 | 2014-01-11 06:15 | 2014-01-11 22:02 | 15.7833 | 2.5554 | 250.4289 | 0.003068% |  |  | 88 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
GR4 | PD | 13 | 345 | 2014-01-11 22:02 | 2014-01-14 13:24 | 63.3667 | 12.0698 | 1182.8444 | 0.01449% |  |  | 85 | 105 | 98 | Pulverizer Overhaul | Maint discovered a broken lower race on 5-3 Pulv during inspection.
GR3 | PD | 11 | 346 | 2014-02-19 22:00 | 2014-02-19 23:20 | 1.3333 | 0.26667 | 18.9333 | 0.0002319% |  |  | 60 | 75 | 71 | Pulverizer Pyrite Removal System | 4-4 Pulv Pyrite Trap running heavy. Maint found Pyrite Swing Gaate stuck in the op
MC4 | D1 | 1 | 360 | 2014-01-01 | 2014-01-01 03:30 | 3.5 | 0.7 | 340.2 | 0.004167% | 0.004312% | 0.004471% | 420 | 525 | 486 | Burners | 4C Mill - 4C7 & 4C9 Burners High Temperature
MC3 | D1 | 2 | 360 | 2014-01-05 23:16 | 2014-01-06 02:00 | 2.7333 | 0.60095 | 236.7726 | 0.0029% | 0.003001% | 0.003112% | 330 | 423 | 394 | Burners | 3A Mill - Burners High Temperature
MC4 | D4 | 6 | 360 | 2014-01-08 21:00 | 2014-01-08 21:55 | 0.91667 | 0.20079 | 97.5857 | 0.001195% | 0.001237% |  | 410 | 525 | 486 | Burners | 4B Mill - Coal Burners Inspection
MC4 | D1 | 9 | 360 | 2014-01-12 02:48 | 2014-01-12 09:33 | 6.75 | 1.2214 | 593.6143 | 0.007272% | 0.007524% | 0.007801% | 430 | 525 | 486 | Burners | 4B Mill - Fire, 4B1 Burner Blanked Off
MC3 | D4 | 4 | 360 | 2014-01-15 03:06 | 2014-01-15 08:13 | 5.1167 | 1.3669 | 538.5443 | 0.006597% | 0.006826% |  | 310 | 423 | 394 | Burners | 3C Mill - Coal Burner Logic Change
MC3 | D4 | 5 | 360 | 2014-01-15 08:13 | 2014-01-15 09:42 | 1.4833 | 0.17884 | 70.4636 | 0.0008632% | 0.0008932% |  | 372 | 423 | 394 | Burners | 3C Mill - Coal Burner Logic Testing
MC3 | D1 | 8 | 360 | 2014-01-15 12:09 | 2014-01-15 13:13 | 1.0667 | 0.17147 | 67.5606 | 0.0008276% | 0.0008564% | 0.0008879% | 355 | 423 | 394 | Burners | 3D Mill - 3D7 Coal Burner High Temperature
MC3 | D1 | 11 | 360 | 2014-01-20 08:37 | 2014-01-20 09:20 | 0.71667 | 0.14909 | 58.7429 | 0.0007196% | 0.0007446% | 0.000772% | 335 | 423 | 394 | Burners | 3C Mill - 3C3 Coal Burner High Temperature
MC3 | D4 | 12 | 360 | 2014-01-20 21:00 | 2014-01-21 00:55 | 3.9167 | 0.90741 | 357.5185 | 0.00438% | 0.004532% |  | 325 | 423 | 394 | Burners | 3A & 3D Mills - Coal Burner Logic Change Over
MC3 | D1 | 14 | 360 | 2014-01-23 22:08 | 2014-01-23 23:03 | 0.91667 | 0.42908 | 169.0567 | 0.002071% | 0.002143% | 0.002222% | 225 | 423 | 394 | Burners | 3D Mill - 3D7 Coal Burner High Temperature
MC3 | D1 | 16 | 360 | 2014-01-24 23:56 | 2014-01-25 01:35 | 1.65 | 0.24574 | 96.8234 | 0.001186% | 0.001227% | 0.001272% | 360 | 423 | 394 | Burners | 3D Mill - 3D10 Coal Burner High Temperature
MC3 | D1 | 17 | 360 | 2014-01-28 09:43 | 2014-01-28 10:42 | 0.98333 | 0.14645 | 57.7028 | 0.0007069% | 0.0007314% | 0.0007583% | 360 | 423 | 394 | Burners | 3C Mill - 3C2 Coal Burner High Temperature
MC3 | D1 | 18 | 360 | 2014-01-28 16:30 | 2014-01-28 17:05 | 0.58333 | 0.086879 | 34.2305 | 0.0004193% | 0.0004339% | 0.0004498% | 360 | 423 | 394 | Burners | 3B Mill - 3B6 Coal Burner High Temperature
MC3 | D1 | 19 | 360 | 2014-01-31 08:09 | 2014-01-31 09:12 | 1.05 | 0.20603 | 81.1752 | 0.0009944% | 0.001029% | 0.001067% | 340 | 423 | 394 | Burners | 3C Mill - 3C2 Coal Burner High Temperature
MC4 | D1 | 17 | 360 | 2014-02-03 03:55 | 2014-02-03 06:08 | 2.2167 | 0.82333 | 400.14 | 0.004902% | 0.005072% | 0.005259% | 330 | 525 | 486 | Burners | 4B Mill - 4B3 Coal Burner High Temperature4C Coal Mill - Inspection
MC3 | D1 | 21 | 360 | 2014-02-09 09:05 | 2014-02-09 10:25 | 1.3333 | 0.29314 | 115.4988 | 0.001415% | 0.001464% | 0.001518% | 330 | 423 | 394 | Burners | 3C Mill - 3C3 Coal Burner High Temperature
MC3 | D1 | 22 | 360 | 2014-02-09 10:50 | 2014-02-09 16:36 | 5.7667 | 1.2678 | 499.5324 | 0.006119% | 0.006332% | 0.006565% | 330 | 423 | 394 | Burners | 3C Mill - 3C10 Coal Burner High Temperature
MC3 | D1 | 25 | 360 | 2014-02-10 19:42 | 2014-02-10 19:57 | 0.25 | 0.060875 | 23.9846 | 0.0002938% | 0.000304% | 0.0003152% | 320 | 423 | 394 | Burners | 3D Mill - 3D4 Coal Burner High Temperature
MC3 | D1 | 26 | 360 | 2014-02-15 11:11 | 2014-02-15 12:43 | 1.5333 | 0.22837 | 89.9773 | 0.001102% | 0.001141% | 0.001182% | 360 | 423 | 394 | Burners | 3C Mill - 3C1 & 3C3 Coal Burners High Temperature
MC3 | D1 | 27 | 360 | 2014-02-15 13:28 | 2014-02-15 14:20 | 0.86667 | 0.12908 | 50.8567 | 0.000623% | 0.0006446% | 0.0006683% | 360 | 423 | 394 | Burners | 3A Mill - 3A4 Coal Burner High Temperature
MC3 | D1 | 29 | 360 | 2014-02-21 14:09 | 2014-02-21 15:29 | 1.3333 | 0.29314 | 115.4988 | 0.001415% | 0.001464% | 0.001518% | 330 | 423 | 394 | Burners | 3D Mill - 3D1 Coal Burner High Temperature
MC3 | D1 | 30 | 360 | 2014-02-21 18:21 | 2014-02-21 19:10 | 0.81667 | 0.16024 | 63.1362 | 0.0007734% | 0.0008003% | 0.0008297% | 340 | 423 | 394 | Burners | 3A Mill - 3A4 Coal Burner High Temperature
MC3 | D1 | 31 | 360 | 2014-02-22 09:20 | 2014-02-22 11:18 | 1.9667 | 0.43239 | 170.3608 | 0.002087% | 0.002159% | 0.002239% | 330 | 423 | 394 | Burners | 3C Mill - 3C3 Coal Burner High Temperature
MC3 | D1 | 32 | 360 | 2014-02-22 14:45 | 2014-02-22 16:15 | 1.5 | 0.71986 | 283.6241 | 0.003474% | 0.003595% | 0.003727% | 220 | 423 | 394 | Burners | 3D Mill - 3D1 Coal Burner High Temperature3B Mill - 3B7 Coal Burner Fire
MC3 | D1 | 33 | 360 | 2014-02-22 16:15 | 2014-02-22 17:00 | 0.75 | 0.16489 | 64.9681 | 0.0007959% | 0.0008235% | 0.0008538% | 330 | 423 | 394 | Burners | 3D Mill - 3D1 Coal Burner High Temperature
MC3 | D1 | 34 | 360 | 2014-02-22 19:25 | 2014-02-22 20:28 | 1.05 | 0.23085 | 90.9553 | 0.001114% | 0.001153% | 0.001195% | 330 | 423 | 394 | Burners | 3D Mill - 3D2 Coal Burner High Temperature
MC4 | D1 | 3 | 380 | 2014-01-06 05:40 | 2014-01-06 05:48 | 0.13333 | 0.068571 | 33.3257 | 0.0004082% | 0.0004224% | 0.000438% | 255 | 525 | 486 | Light-off (Igniter) Systems (Including Fuel Supply) | 4C Mill - Gas Igniter Issue
MC4 | D1 | 4 | 380 | 2014-01-06 06:40 | 2014-01-06 08:55 | 2.25 | 0.79286 | 385.3286 | 0.00472% | 0.004884% | 0.005064% | 340 | 525 | 486 | Light-off (Igniter) Systems (Including Fuel Supply) | 4B & 4C Mills - Gas Igniter Issues
MC4 | D1 | 5 | 380 | 2014-01-06 08:55 | 2014-01-06 12:30 | 3.5833 | 0.71667 | 348.3 | 0.004267% | 0.004415% | 0.004577% | 420 | 525 | 486 | Light-off (Igniter) Systems (Including Fuel Supply) | 4C Mill - Gas Vent Valve Stuck Open
MC2 | SF | 58 | 380 | 2014-02-17 22:00 | 2014-02-18 13:40 | 15.6667 | 15.6667 | 4684.3333 | 0.05738% | 0.05938% | 0.06156% | 0 | 330 | 299 | Light-off (Igniter) Systems | Gas Igniter Issues
0
|  |  | (0200-0480) |  | Fuel Firing | 867.7367 | 255.1655 | 76562.6189 | 0.9379% | 0.9012% | 0.7719%
0
GR3 | U1 | 13 | 580 | 2014-02-22 23:25 | 2014-02-23 01:09 | 1.7333 | 1.7333 | 123.0667 | 0.001508% | 0.00156% | 0.001617% | 0 | 75 | 71 | Desuperheater/Attemperator Piping | While GR3 was off line on Reserve, Ops discovered a leak in B4 Attemperator supply
TC1 | D1 | 7 | 590 | 2014-01-08 12:00 | 2014-01-08 17:26 | 5.4333 | 0.46382 | 177.6435 | 0.002176% | 0.002252% | 0.002335% | 375 | 410 | 383 | Desuperheater/Attemperator Valves | The SH Spray control valve was leaking and required a unit derate to accomplish th
BR3 | MO | 4 | 740 | 2014-01-11 10:37 | 2014-01-12 04:08 | 17.5167 | 17.5167 | 7251.9 | 0.08884% | 0.09192% |  | 0 | 457 | 414 | 3-1 Boiler Recirculation Pump Replacement | Replace 3-1 BCWP
MC1 | U1 | 10 | 800 | 2014-01-18 08:33 | 2014-01-18 11:21 | 2.8 | 2.8 | 848.4 | 0.01039% | 0.01075% | 0.01115% | 0 | 330 | 303 | Boiler Drums And Drum Internals | High Drum Level Trip due to Turbine #2 Control Valve Issue, Replaced Fast Acting S
MC3 | D4 | 36 | 876 | 2014-02-25 20:00 | 2014-02-26 04:28 | 8.4667 | 4.1633 | 1640.3316 | 0.02009% | 0.02079% |  | 215 | 423 | 394 | Soot Blower Controls | Sootblower Regulator - Rebuilt
GH4 | MO | 3 | 1000 | 2014-01-01 | 2014-01-01 00:53 | 0.88333 | 0.88333 | 433.7167 | 0.005313% | 0.005498% |  | 0 | 534 | 491 | Furnace Wall Leaks | Unit 4 developed a tube leak on 8 2/3 floor on the south side of the
MC2 | MO | 4 | 1000 | 2014-01-02 10:39 | 2014-01-04 11:51 | 49.2 | 49.2 | 14710.8 | 0.1802% | 0.1865% |  | 0 | 330 | 299 | Furnace Wall Tube Leaks | Boiler Tube Leak - Waterwall
MC2 | MO | 67 | 1000 | 2014-02-24 09:31 | 2014-02-25 19:47 | 34.2667 | 34.2667 | 10245.7333 | 0.1255% | 0.1299% |  | 0 | 330 | 299 | Furnace Wall Leaks | Boiler Tube Leak - Waterwall
GH3 | U1 | 7 | 1040 | 2014-01-25 03:33 | 2014-01-26 19:21 | 39.8 | 39.8 | 19183.6 | 0.235% | 0.2432% | 0.2521% | 0 | 527 | 482 | Superheater Tube Leaks | Unit was taken off line after developing a boiler tube leak in the Prim
GR4 | MO | 8 | 1050 | 2014-01-09 10:36 | 2014-01-10 16:22 | 29.7667 | 29.7667 | 2917.1333 | 0.03573% | 0.03698% | 0.03834% | 0 | 105 | 98 | Second Superheater Leaks | GR4 taken O/S in an orderly manner for repair of a tube leak in the DR Sec SH Sect
GR3 | U3 | 2 | 1050 | 2014-01-12 21:48 | 2014-01-14 18:35 | 44.7833 | 44.7833 | 3179.6167 | 0.03895% | 0.0403% | 0.04179% | 0 | 75 | 71 | Second Superheater Leaks | GR3 taken out of service due to Sec SH tube leak. Dispatch was notified at 2200
GR4 | U1 | 27 | 1050 | 2014-02-07 04:42 | 2014-02-08 17:57 | 37.25 | 37.25 | 3650.5 | 0.04472% | 0.04627% | 0.04797% | 0 | 105 | 98 | Second Superheater Leaks | Ops discovered leak in B5 Sec SH Section at 0344, unit was removed from service in
MC2 | MO | 57 | 1050 | 2014-02-15 00:32 | 2014-02-17 22:00 | 69.4667 | 69.4667 | 20770.5333 | 0.2544% | 0.2633% |  | 0 | 330 | 299 | Second Superheater Leaks | Boiler Tube Leak - Second Superheater
GH1 | MO | 6 | 1060 | 2014-02-01 15:04 | 2014-02-03 01:27 | 34.3833 | 34.3833 | 16538.3833 | 0.2026% | 0.2096% |  | 0 | 517 | 481 | First Reheater Leaks | Unit 1 had been running with a tube leak, located around IK #6, for s
CR5 | U2 | 7 | 1060 | 2014-02-07 10:51 | 2014-02-09 | 37.15 | 37.15 | 6241.2 | 0.07645% | 0.07911% | 0.08202% | 0 | 181 | 168 | First Reheater Leaks | Reheat boiler tube leak - cracked. Total of 6 leaks - 1 dutchman & 4 padwelds.
GH1 | MO | 12 | 1060 | 2014-02-22 14:49 | 2014-02-23 11:03 | 20.2333 | 20.2333 | 9732.2333 | 0.1192% | 0.1234% |  | 0 | 517 | 481 | First Reheater Leaks | A leak was detected in Reheater pendant section of the boiler. Dispa
CR6 | U2 | 1 | 1070 | 2014-01-03 11:03 | 2014-01-04 17:05 | 30.0333 | 30.0333 | 7208 | 0.0883% | 0.09137% | 0.09473% | 0 | 261 | 240 | Reheater Tube Leaks | Boiler Tube Leak - A tube leak was discovered in the RH Pendants.
CR6 | MO | 3 | 1070 | 2014-01-09 20:23 | 2014-01-17 04:37 | 176.2333 | 176.2333 | 42296 | 0.5181% | 0.5361% |  | 0 | 261 | 240 | Reheater Tube Leaks | Boiler Leak Repair - A tube within the RH Pendants was discovered to be cracked,
CR4 | NC | 2 | 1150 | 2014-01-08 21:00 | 2014-01-09 06:07 | 9.1167 | [5 empty] | 0 | 168 | 155 | Second Superheater Slagging or Fouling | Boiler deslag. Full load available if needed.
CR4 | NC | 6 | 1150 | 2014-01-24 21:30 | 2014-01-25 06:09 | 8.65 | [5 empty] | 0 | 168 | 155 | Second Superheater Slagging or Fouling | Boiler deslag. Full load available if needed.
CR4 | NC | 7 | 1150 | 2014-01-30 21:45 | 2014-01-31 04:30 | 6.75 | [5 empty] | 0 | 168 | 155 | Second Superheater Slagging or Fouling | Boiler deslag. Full load availabe if needed.
MC2 | NC | 17 | 1160 | 2014-01-16 23:00 | 2014-01-17 04:00 | 5 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 18 | 1160 | 2014-01-17 22:15 | 2014-01-18 05:00 | 6.75 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC4 | NC | 10 | 1160 | 2014-01-18 21:00 | 2014-01-19 07:41 | 10.6833 | [5 empty] | 0 | 525 | 486 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 19 | 1160 | 2014-01-18 21:05 | 2014-01-19 05:00 | 7.9167 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 23 | 1160 | 2014-01-24 23:00 | 2014-01-25 06:50 | 7.8333 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC4 | NC | 14 | 1160 | 2014-01-26 11:35 | 2014-01-27 05:50 | 18.25 | [5 empty] | 0 | 525 | 486 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 33 | 1160 | 2014-01-29 21:00 | 2014-01-30 01:55 | 4.9167 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater. Full load available if needed.
MC2 | NC | 34 | 1160 | 2014-01-30 22:15 | 2014-01-31 04:00 | 5.75 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC1 | NC | 19 | 1160 | 2014-02-04 23:00 | 2014-02-05 04:15 | 5.25 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater. Full load available if needed.
MC2 | NC | 47 | 1160 | 2014-02-07 23:00 | 2014-02-08 05:30 | 6.5 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | D1 | 48 | 1160 | 2014-02-08 05:30 | 2014-02-08 07:35 | 2.0833 | 1.1995 | 358.649 | 0.004393% | 0.004546% | 0.004713% | 140 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC1 | D1 | 22 | 1160 | 2014-02-08 07:15 | 2014-02-08 08:27 | 1.2 | 0.10909 | 33.0545 | 0.0004049% | 0.000419% | 0.0004344% | 300 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC2 | D1 | 49 | 1160 | 2014-02-08 07:35 | 2014-02-08 09:28 | 1.8833 | 0.51364 | 153.5773 | 0.001881% | 0.001947% | 0.002018% | 240 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC1 | D1 | 23 | 1160 | 2014-02-08 08:27 | 2014-02-08 15:05 | 6.6333 | 1.6081 | 487.2485 | 0.005969% | 0.006176% | 0.006403% | 250 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC1 | NC | 24 | 1160 | 2014-02-08 22:00 | 2014-02-09 04:00 | 6 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 50 | 1160 | 2014-02-08 22:00 | 2014-02-09 04:00 | 6 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 51 | 1160 | 2014-02-09 21:12 | 2014-02-10 03:17 | 6.0833 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 53 | 1160 | 2014-02-11 12:21 | 2014-02-11 16:30 | 4.15 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 54 | 1160 | 2014-02-12 22:00 | 2014-02-13 04:50 | 6.8333 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC4 | NC | 21 | 1160 | 2014-02-12 23:59 | 2014-02-13 04:20 | 4.35 | [5 empty] | 0 | 525 | 486 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | D1 | 56 | 1160 | 2014-02-14 11:25 | 2014-02-15 00:32 | 13.1167 | 2.1861 | 653.6472 | 0.008007% | 0.008285% | 0.00859% | 275 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC4 | NC | 25 | 1160 | 2014-02-20 23:00 | 2014-02-21 04:00 | 5 | [5 empty] | 0 | 525 | 486 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
TC2 | NC | 2 | 1190 | 2014-01-04 12:00 | 2014-01-04 17:00 | 5 | [5 empty] | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate due to boiler OEM recommended deslag, unit available to retu
TC2 | NC | 3 | 1190 | 2014-01-11 | 2014-01-11 05:23 | 5.3833 | [5 empty] | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate at 561MW for boiler OEM recommended weekly deslag.
TC2 | NC | 11 | 1190 | 2014-01-19 | 2014-01-19 06:15 | 6.25 | [5 empty] | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate to conduct boiler OEM recommended deslag.
TC2 | NC | 15 | 1190 | 2014-01-26 12:00 | 2014-01-26 18:00 | 6 | [5 empty] | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate at 561 MW to conduct boiler OEM recommended deslag. Unit av
TC2 | NC | 16 | 1190 | 2014-02-01 00:01 | 2014-02-01 06:15 | 6.2333 | 6.2333 | 3553 |  |  |  | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate at 550 MW to conduct boiler OEM recommended deslag. Unit av
GH3 | D1 | 20 | 1400 | 2014-02-18 10:26 | 2014-02-25 04:00 | 161.5667 | 7.0513 | 3398.725 | 0.04163% | 0.04308% | 0.04467% | 504 | 527 | 482 | Forced Draft Fans | FD fans were topping out.
BR1 | PD | 4 | 1400 | 2014-02-26 23:00 | 2014-02-27 | 1 | 0.5614 | 60.0702 | 0.0007359% |  |  | 50 | 114 | 107 | Forced Draft Fans | Repair leaking cooler hose 1-1 FD Fan
GH3 | U1 | 1 | 1455 | 2014-01-07 21:20 | 2014-01-08 06:15 | 8.9167 | 8.9167 | 4297.8333 | 0.05265% | 0.05448% | 0.05648% | 0 | 527 | 482 | 3-2 Induced Draft Fan OB Bearing | 3-2 ID fan tripped on high vibration on OB fan bearing. This caused
GH3 | D1 | 2 | 1455 | 2014-01-08 06:15 | 2014-01-10 11:31 | 53.2667 | 33.0516 | 15930.8774 | 0.1952% | 0.2019% | 0.2094% | 200 | 527 | 482 | 3-2 Induced Draft Fan Out Of Service | Unit running with 3-2 ID fan out of service.
GH3 | MO | 3 | 1455 | 2014-01-10 11:31 | 2014-01-13 03:25 | 63.9 | 63.9 | 30799.8 | 0.3773% | 0.3904% |  | 0 | 527 | 482 | 3-2 Induced Draft Fan Trip | Unit derated to minimum load due to 3-2 ID Fan tripping on
GH3 | D1 | 5 | 1455 | 2014-01-21 23:18 | 2014-01-22 01:31 | 2.2167 | 0.029443 | 14.1917 | 0.0001738% | 0.0001799% | 0.0001865% | 520 | 527 | 482 | Induced Draft Fans | Load was reduced when 3-1 ID Fan blade position feedback failed,
GH3 | D1 | 8 | 1455 | 2014-01-26 19:21 | 2014-01-26 20:47 | 1.4333 | 0.88937 | 428.6782 | 0.005251% | 0.005434% | 0.005634% | 200 | 527 | 482 | Induced Draft Fans | Load Reduction #4Unit 3 was derated during startup when 3-2 ID Fan OB bearing fail
GH3 | MO | 9 | 1455 | 2014-01-26 20:47 | 2014-01-27 22:30 | 25.7167 | 25.7167 | 12395.4333 | 0.1518% | 0.1571% |  | 0 | 527 | 482 | 3-2 Induced Draft Fan OB Bearing | Unit was taken off line to replace 3-2 ID Fan OB bearing.
GH3 | D1 | 10 | 1455 | 2014-01-28 11:27 | 2014-01-30 14:13 | 50.7667 | 2.6009 | 1253.6573 | 0.01536% | 0.01589% | 0.01648% | 500 | 527 | 482 | Induced Draft Fans | 3-2 ID Fan IB bearing running 9+ mils vibration. OB fan bearing
GH3 | MO | 11 | 1455 | 2014-01-30 14:13 | 2014-02-01 09:26 | 43.2167 | 43.2167 | 20830.4333 | 0.2552% | 0.264% |  | 0 | 527 | 482 | Induced Draft Fans OB Bearing | Unit 3 has been running with 3-2 ID Fan OB Fan bearing having periodi
TC2 | D1 | 18 | 1455 | 2014-02-04 15:45 | 2014-02-04 16:15 | 0.5 | 0.015651 | 8.9209 | 0.0001093% | 0.0001131% | 0.0001172% | 588 | 607 | 570 | Induced Draft Fans | Derate required on the unit due to ID fan stall alarms. Required derate to avoid
GH3 | D1 | 18 | 1455 | 2014-02-17 10:50 | 2014-02-17 12:00 | 1.1667 | 0.12619 | 60.8216 | 0.0007451% | 0.000771% | 0.0007993% | 470 | 527 | 482 | Induced Draft Fans | ID Fans out the top. Reduced load to swap mills.
CR5 | U1 | 2 | 1470 | 2014-01-11 19:43 | 2014-01-11 22:26 | 2.7167 | 2.7167 | 456.4 | 0.005591% | 0.005785% | 0.005998% | 0 | 181 | 168 | Induced Draft Fan Motors and Drives | 5A induced draft fan tripped due to bad thyrister card causing unit to trip.
CR5 | U1 | 10 | 1475 | 2014-02-21 04:01 | 2014-02-21 14:53 | 10.8667 | 10.8667 | 1825.6 | 0.02236% | 0.02314% | 0.02399% | 0 | 181 | 168 | Induced Draft Fan Controls | 5A ID Fan trip - Replaced I/O PCB and batteries in Sigma controller and reset faul
MC1 | D1 | 25 | 1488 | 2014-02-10 23:05 | 2014-02-11 06:25 | 7.3333 | 0.15556 | 47.1333 | 0.0005774% | 0.0005974% | 0.0006194% | 323 | 330 | 303 | Air Heater (Regenerative) | Air Heater - High Differential
MC1 | D1 | 26 | 1488 | 2014-02-11 06:25 | 2014-02-11 10:00 | 3.5833 | 0.10859 | 32.9015 | 0.000403% | 0.000417% | 0.0004324% | 320 | 330 | 303 | Air Heater (Regenerative) | Air Heater - High Differential
MC1 | D1 | 27 | 1488 | 2014-02-11 10:00 | 2014-02-12 10:30 | 24.5 | 0.44545 | 134.9727 | 0.001653% | 0.001711% | 0.001774% | 324 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | D1 | 30 | 1488 | 2014-02-12 10:30 | 2014-02-12 22:45 | 12.25 | 0.37121 | 112.4773 | 0.001378% | 0.001426% | 0.001478% | 320 | 330 | 303 | Air Heater (Regenerative) | 1A Air heater - High Differential
MC1 | D1 | 31 | 1488 | 2014-02-12 22:45 | 2014-02-13 07:26 | 8.6833 | 0.52626 | 159.4576 | 0.001953% | 0.002021% | 0.002096% | 310 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | D1 | 32 | 1488 | 2014-02-13 07:26 | 2014-02-13 22:00 | 14.5667 | 0.26485 | 80.2491 | 0.0009831% | 0.001017% | 0.001055% | 324 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | D1 | 38 | 1488 | 2014-02-15 06:54 | 2014-02-16 06:20 | 23.4333 | 0.35505 | 107.5803 | 0.001318% | 0.001364% | 0.001414% | 325 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | D1 | 39 | 1488 | 2014-02-16 06:20 | 2014-02-17 09:00 | 26.6667 | 0.80808 | 244.8485 | 0.002999% | 0.003104% | 0.003218% | 320 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | D1 | 40 | 1488 | 2014-02-17 09:00 | 2014-02-18 22:26 | 37.4333 | 2.2687 | 687.4121 | 0.008421% | 0.008713% | 0.009034% | 310 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | MO | 41 | 1488 | 2014-02-18 22:26 | 2014-02-21 22:16 | 71.8333 | 71.8333 | 21765.5 | 0.2666% | 0.2759% |  | 0 | 330 | 303 | Air Heater Dirty | Air Heater Wash
TC1 | NC | 1 | 1489 | 2014-01-02 09:00 | 2014-01-02 15:00 | 6 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Holding the unit above 525 MW's for Air Heater Slip Testing to be conducted.
TC1 | NC | 2 | 1489 | 2014-01-03 05:00 | 2014-01-03 09:40 | 4.6667 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Holding load above 525 MW's for ammonia slip testing for the air heaters.
TC1 | NC | 8 | 1489 | 2014-01-09 07:00 | 2014-01-09 13:00 | 6 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | A 525 MW minimum limit was set on the unit to accomplish air heater slip testing.
TC1 | NC | 9 | 1489 | 2014-01-10 06:30 | 2014-01-10 15:00 | 8.5 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | A 525 MW minimum limit was set on the unit to accomplish air heater slip testing.
TC1 | NC | 21 | 1489 | 2014-01-21 18:00 | 2014-01-21 23:59 | 5.9833 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running and good for full load but with a 525 MW limit set for ammonia slip
TC1 | NC | 22 | 1489 | 2014-01-29 06:00 | 2014-01-29 08:00 | 2 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running and good for full load but with a 525 MW limit set for ammonia sl
TC1 | NC | 24 | 1489 | 2014-01-29 10:00 | 2014-01-29 14:37 | 4.6167 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running and good for full load but with a 525 MW limit set for ammonia sl
TC1 | NC | 25 | 1489 | 2014-01-31 13:00 | 2014-01-31 20:00 | 7 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running & good for full load with a 525 MW limit set for ammonia slip mit
TC1 | NC | 147 | 1489 | 2014-01-31 13:00 | 2014-01-31 20:00 | 7 | [5 empty] | 0 | 410 | 383 | Air Heater (Heat Pipe; Plate-type) | Unit was running and good for full load with a 525 MW limit set for ammonia slip m
MC4 | D1 | 28 | 1520 | 2014-02-25 08:16 | 2014-02-25 09:00 | 0.73333 | 0.069841 | 33.9429 | 0.0004158% | 0.0004302% | 0.0004461% | 475 | 525 | 486 | Flue Gas Dampers (Except Recirculation) | 4A Economizer Outlet Damper - Failed to Open Completely
CR6 | U1 | 4 | 1700 | 2014-01-17 06:00 | 2014-01-17 06:42 | 0.7 | 0.7 | 168 | 0.002058% | 0.00213% | 0.002208% | 0 | 261 | 240 | Feedwater Controls | Low drum level - high boiler pressure
MC2 | D1 | 39 | 1700 | 2014-02-03 08:15 | 2014-02-03 10:23 | 2.1333 | 0.32323 | 96.6465 | 0.001184% | 0.001225% | 0.00127% | 280 | 330 | 299 | Feedwater Controls | Feedwater Flow Issue
MC4 | D1 | 18 | 1710 | 2014-02-04 14:30 | 2014-02-19 06:00 | 351.5 | 4.6867 | 2277.72 | 0.0279% | 0.02887% | 0.02993% | 518 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issues
MC4 | D1 | 24 | 1710 | 2014-02-19 17:42 | 2014-02-21 10:13 | 40.5167 | 0.54022 | 262.548 | 0.003216% | 0.003328% | 0.00345% | 518 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
MC4 | D1 | 26 | 1710 | 2014-02-21 10:13 | 2014-03-01 | 181.7833 | 1.0388 | 504.8383 | 0.006184% | 0.006399% | 0.006634% | 522 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
BR3 | NC | 11 | 1710 | 2014-02-24 22:00 | 2014-02-25 02:05 | 4.0833 | [5 empty] | 0 | 457 | 414 | Combustion/Steam Condition Controls | Combustion tuning 6544234
MC2 | D1 | 2 | 1850 | 2014-01-01 10:30 | 2014-01-01 15:30 | 5 | 0.30303 | 90.6061 | 0.00111% | 0.001148% | 0.001191% | 310 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | NC | 5 | 1850 | 2014-01-04 11:51 | 2014-01-04 21:11 | 9.3333 | [5 empty] | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Warm Start Up
MC2 | D1 | 6 | 1850 | 2014-01-04 21:11 | 2014-01-05 05:35 | 8.4 | 3.1818 | 951.3636 | 0.01165% | 0.01206% | 0.0125% | 205 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 7 | 1850 | 2014-01-05 05:35 | 2014-01-06 01:00 | 19.4167 | 4.1187 | 1231.4874 | 0.01509% | 0.01561% | 0.01618% | 260 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 8 | 1850 | 2014-01-06 01:00 | 2014-01-06 09:28 | 8.4667 | 1.2828 | 383.5657 | 0.004699% | 0.004862% | 0.005041% | 280 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 9 | 1850 | 2014-01-06 09:28 | 2014-01-06 19:00 | 9.5333 | 0.28889 | 86.3778 | 0.001058% | 0.001095% | 0.001135% | 320 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 10 | 1850 | 2014-01-06 19:00 | 2014-01-06 22:36 | 3.6 | 0.32727 | 97.8545 | 0.001199% | 0.00124% | 0.001286% | 300 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 12 | 1850 | 2014-01-07 12:15 | 2014-01-08 09:50 | 21.5833 | 3.2702 | 977.7904 | 0.01198% | 0.01239% | 0.01285% | 280 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 13 | 1850 | 2014-01-08 09:50 | 2014-01-08 12:15 | 2.4167 | 0.25631 | 76.6376 | 0.0009388% | 0.0009714% | 0.001007% | 295 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 14 | 1850 | 2014-01-08 12:15 | 2014-01-09 09:35 | 21.3333 | 0.9697 | 289.9394 | 0.003552% | 0.003675% | 0.00381% | 315 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | NC | 11 | 1850 | 2014-01-18 11:21 | 2014-01-18 15:45 | 4.4 | [5 empty] | 0 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Very Hot Start Up
MC1 | D1 | 12 | 1850 | 2014-01-18 15:45 | 2014-01-18 16:36 | 0.85 | 0.11591 | 35.1205 | 0.0004302% | 0.0004452% | 0.0004615% | 285 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | D1 | 13 | 1850 | 2014-01-18 16:36 | 2014-01-18 18:40 | 2.0667 | 0.18788 | 56.9273 | 0.0006974% | 0.0007216% | 0.0007481% | 300 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 27 | 1850 | 2014-01-26 06:15 | 2014-01-27 08:08 | 25.8833 | 13.3338 | 3986.8177 | 0.04884% | 0.05054% | 0.05239% | 160 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 26 | 1850 | 2014-01-26 18:32 | 2014-01-27 06:15 | 11.7167 | 5.8583 | 1751.6417 | 0.02146% | 0.0222% | 0.02302% | 165 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 28 | 1850 | 2014-01-27 08:08 | 2014-01-27 09:55 | 1.7833 | 0.75657 | 226.2131 | 0.002771% | 0.002867% | 0.002973% | 190 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | NC | 36 | 1850 | 2014-02-02 06:35 | 2014-02-02 14:15 | 7.6667 | [5 empty] | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Hot Start Up
MC2 | D1 | 37 | 1850 | 2014-02-02 14:15 | 2014-02-02 22:00 | 7.75 | 1.6439 | 491.5379 | 0.006021% | 0.006231% | 0.00646% | 260 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 40 | 1850 | 2014-02-03 10:23 | 2014-02-03 21:05 | 10.7 | 0.32424 | 96.9485 | 0.001188% | 0.001229% | 0.001274% | 320 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 45 | 1850 | 2014-02-05 07:56 | 2014-02-05 09:43 | 1.7833 | 0.1351 | 40.3952 | 0.0004948% | 0.000512% | 0.0005309% | 305 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 46 | 1850 | 2014-02-05 09:43 | 2014-02-05 13:25 | 3.7 | 0.17939 | 53.6388 | 0.0006571% | 0.0006799% | 0.0007049% | 314 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | NC | 59 | 1850 | 2014-02-18 13:40 | 2014-02-18 22:15 | 8.5833 | [5 empty] | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Warm Start Up
MC2 | D1 | 60 | 1850 | 2014-02-18 22:15 | 2014-02-19 02:00 | 3.75 | 1.0227 | 305.7955 | 0.003746% | 0.003876% | 0.004019% | 240 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 61 | 1850 | 2014-02-19 02:00 | 2014-02-19 04:15 | 2.25 | 0.40909 | 122.3182 | 0.001498% | 0.00155% | 0.001607% | 270 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 62 | 1850 | 2014-02-19 04:15 | 2014-02-19 07:00 | 2.75 | 0.375 | 112.125 | 0.001374% | 0.001421% | 0.001474% | 285 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 63 | 1850 | 2014-02-19 07:00 | 2014-02-19 08:50 | 1.8333 | 0.13333 | 39.8667 | 0.0004884% | 0.0005053% | 0.0005239% | 306 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 64 | 1850 | 2014-02-19 08:50 | 2014-02-19 21:41 | 12.85 | 0.38939 | 116.4288 | 0.001426% | 0.001476% | 0.00153% | 320 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 65 | 1850 | 2014-02-20 02:40 | 2014-02-20 08:09 | 5.4833 | 0.14955 | 44.7141 | 0.0005477% | 0.0005668% | 0.0005876% | 321 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | NC | 43 | 1850 | 2014-02-22 17:58 | 2014-02-23 03:16 | 9.3 | 9.3 | 2817.9 |  |  |  | 0 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Warm Start Up
MC1 | D1 | 44 | 1850 | 2014-02-23 03:16 | 2014-02-23 04:11 | 0.91667 | 0.15278 | 46.2917 | 0.0005671% | 0.0005868% | 0.0006084% | 275 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | D1 | 45 | 1850 | 2014-02-23 04:11 | 2014-02-23 04:39 | 0.46667 | 0.063636 | 19.2818 | 0.0002362% | 0.0002444% | 0.0002534% | 285 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | D1 | 46 | 1850 | 2014-02-23 04:39 | 2014-02-23 05:36 | 0.95 | 0.10076 | 30.5295 | 0.000374% | 0.000387% | 0.0004012% | 295 | 330 | 303 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | NC | 68 | 1850 | 2014-02-25 19:47 | 2014-02-26 05:39 | 9.8667 | [5 empty] | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Hot Start Up
MC2 | D1 | 69 | 1850 | 2014-02-26 05:39 | 2014-02-26 11:21 | 5.7 | 0.15545 | 46.4809 | 0.0005694% | 0.0005892% | 0.0006108% | 321 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 70 | 1850 | 2014-02-26 11:21 | 2014-02-26 15:29 | 4.1333 | 0.46343 | 138.5669 | 0.001697% | 0.001756% | 0.001821% | 293 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 71 | 1850 | 2014-02-26 15:29 | 2014-02-26 16:46 | 1.2833 | 0.035 | 10.465 | 0.0001282% | 0.0001327% | 0.0001375% | 321 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC3 | NC | 6 | 1990 | 2014-01-14 08:00 | 2014-01-14 16:40 | 8.6667 | [5 empty] | 0 | 423 | 394 | Boiler Performance Testing | Full Load Winter Capability Test
0
|  |  | (0500-1999) |  | Boiler | 2391.8833 | 975.416 | 305641.2657 | 3.666% | 3.793% | 1.18%
0
BR2 | MO | 11 | 3110 | 2014-02-21 22:13 | 2014-02-23 02:07 | 27.9 | 27.9 | 4687.2 | 0.05742% | 0.05941% |  | 0 | 180 | 168 | Condenser Tube Leaks | Repair condenser tube leak and other misc. issues 6522386
MC2 | U1 | 35 | 3149 | 2014-02-01 23:37 | 2014-02-02 06:35 | 6.9667 | 6.9667 | 2083.0333 | 0.02552% | 0.0264% | 0.02737% | 0 | 330 | 299 | Condenser Loss of Vacuum | Condenser Vacuum Trip
TC1 | U1 | 15 | 3344 | 2014-01-14 10:39 | 2014-01-16 22:16 | 59.6167 | 59.6167 | 22833.1833 | 0.2797% | 0.2894% | 0.3001% | 0 | 410 | 383 | Deaerator Heater Head Leak | Leak in the deaerator heater head was discovered. Unit was taken offline to repair
BR2 | PD | 9 | 3410 | 2014-02-20 22:00 | 2014-02-21 09:00 | 11 | 4.2778 | 718.6667 | 0.008804% |  |  | 110 | 180 | 168 | Feedwater Pump | Repair 2-2 BFP drain valve 6532228
BR2 | D1 | 13 | 3410 | 2014-02-24 08:24 | 2014-02-26 20:00 | 59.6 | 24.8333 | 4172 | 0.05111% | 0.05288% | 0.05483% | 105 | 180 | 168 | Feedwater Pump OB Bearing | 2-2 BFP OB bearing hot 6546733
BR3 | PD | 9 | 3412 | 2014-02-04 22:00 | 2014-02-05 01:52 | 3.8667 | 1.2438 | 514.9182 | 0.006308% |  |  | 310 | 457 | 414 | Feedwater Pump Drive - Steam Turbine | Collecting 3-2 BFP vibration data
BR3 | D1 | 10 | 3414 | 2014-02-21 22:08 | 2014-02-22 23:58 | 25.8333 | 8.5923 | 3557.1991 | 0.04358% | 0.04509% | 0.04675% | 305 | 457 | 414 | Feedwater Pump Local Controls | 3-2 BFPT LP governor valve indication 6545010
BR3 | D1 | 12 | 3414 | 2014-02-25 05:51 | 2014-02-25 07:39 | 1.8 | 0.61838 | 256.0096 | 0.003136% | 0.003245% | 0.003364% | 300 | 457 | 414 | Feedwater Pump Local Controls | 3-2 BFP LP gov. servo problems 6546920
CR5 | D4 | 3 | 3416 | 2014-01-24 23:00 | 2014-01-25 07:25 | 8.4167 | 5.1616 | 867.1492 | 0.01062% | 0.01099% |  | 70 | 181 | 168 | Other Feedwater Pump Problems | 51 boiler feed pump maintenance.
GH4 | PD | 6 | 3416 | 2014-02-08 23:00 | 2014-02-09 00:20 | 1.3333 | 0.58427 | 286.8764 | 0.003514% |  |  | 300 | 534 | 491 | Other Feedwater Pump Problems | Planned derate to inspect 4-2 BFP leak. Derate was planned with
TC2 | D1 | 1 | 3439 | 2014-01-01 | 2014-01-04 02:00 | 74 | 5.2422 | 2988.0395 | 0.0366% | 0.03788% | 0.03927% | 564 | 607 | 570 | High Pressure Heater Head Leaks | 7A FWH is out of service due to a heater head leak and unit derate required until
0
|  |  | (3110-3999) |  | Balance Of Plant | 280.3333 | 145.0369 | 42964.2754 | 0.5263% | 0.5253% | 0.4717%
0
CR6 | D1 | 11 | 4240 | 2014-02-11 08:00 | 2014-02-11 14:00 | 6 | 0.94253 | 226.2069 | 0.002771% | 0.002867% | 0.002973% | 220 | 261 | 240 | Lp Turbine Bearings | #4 Turbine bearing temperature running high.
CR6 | NC | 13 | 4240 | 2014-02-17 12:00 | 2014-02-17 15:01 | 3.0167 | [5 empty] | 0 | 261 | 240 | Lp Turbine Bearings | Turbine cool down in prep for removing #3 & #4 turbine bearing during maintenance
CR6 | MO | 14 | 4240 | 2014-02-17 15:01 | 2014-02-23 22:51 | 151.8333 | 151.8333 | 36440 | 0.4464% | 0.4619% |  | 0 | 261 | 240 | Lp Turbine Bearings | The #3 and #4 turbine bearings were removed. The #3 was found OK and was polished
MC4 | D1 | 2 | 4261 | 2014-01-02 11:34 | 2014-01-02 12:11 | 0.61667 | 0.029365 | 14.2714 | 0.0001748% | 0.0001809% | 0.0001876% | 500 | 525 | 486 | Turbine Control Valves | Turbine Control Valves - EHC Issue
MC1 | D1 | 9 | 4261 | 2014-01-17 21:42 | 2014-01-18 08:33 | 10.85 | 0.98636 | 298.8682 | 0.003661% | 0.003788% | 0.003928% | 300 | 330 | 303 | Turbine Control Valves | Turbine #2 Control Valve - Would Not Open during Valve Test
MC1 | D1 | 18 | 4261 | 2014-02-01 21:20 | 2014-02-02 08:50 | 11.5 | 7.3182 | 2217.4091 | 0.02716% | 0.02811% | 0.02914% | 120 | 330 | 303 | Turbine Control Valves | Turbine #2 Control Valve - Stuck Closed
CR4 | D1 | 10 | 4261 | 2014-02-18 11:05 | 2014-02-18 22:14 | 11.15 | 0.8628 | 133.7336 | 0.001638% | 0.001695% | 0.001757% | 155 | 168 | 155 | Turbine Control Valves | Governor valve sticking at 155 MW. Lubrication issues.
CR4 | MO | 11 | 4261 | 2014-02-18 22:14 | 2014-02-20 00:32 | 26.3 | 26.3 | 4076.5 | 0.04994% | 0.05167% |  | 0 | 168 | 155 | Turbine Control Valves | Governor valve sticking at 155 MW. Lubrication issues. CSS cleaned hardened grea
MC1 | SF | 42 | 4261 | 2014-02-21 22:16 | 2014-02-22 17:58 | 19.7 | 19.7 | 5969.1 | 0.07312% | 0.07566% | 0.07844% | 0 | 330 | 303 | Turbine Control Valves | Turbine #2 & #3 Control Valves - Cleaned Servovalves
TC1 | NC | 20 | 4267 | 2014-01-19 01:00 | 2014-01-19 01:30 | 0.5 | [5 empty] | 0 | 410 | 383 | Turbine Control Valve Testing | Weekly valve check on the unit, Unit available to return to full load if required
MC2 | U1 | 24 | 4267 | 2014-01-25 22:11 | 2014-01-26 12:32 | 14.35 | 14.35 | 4290.65 | 0.05256% | 0.05439% | 0.05639% | 0 | 330 | 299 | Turbine Control Valve Testing Trip | Turbine Control Valve Test - Trip
MC4 | D1 | 27 | 4460 | 2014-02-23 04:00 | 2014-02-23 04:33 | 0.55 | 0.31952 | 155.2886 | 0.001902% | 0.001968% | 0.002041% | 220 | 525 | 486 | Turbine Overspeed Trip Test | Turbine Overspeed Test - Linkage Stuck
MC4 | NC | 23 | 4490 | 2014-02-19 06:00 | 2014-02-19 12:30 | 6.5 | [5 empty] | 0 | 525 | 486 | Turbine Performance Testing | Full Load Capability Test
MC1 | NC | 47 | 4490 | 2014-02-27 07:00 | 2014-02-27 13:18 | 6.3 | [5 empty] | 0 | 330 | 303 | Turbine Performance Testing | Capability Test - Full Load
0
|  |  | (4000-4499) |  | Steam Turbine | 269.1667 | 222.6421 | 53822.0278 | 0.6593% | 0.6822% | 0.1749%
0
GH3 | SF | 4 | 4609 | 2014-01-13 03:25 | 2014-01-13 06:19 | 2.9 | 2.9 | 1397.8 | 0.01712% | 0.01772% | 0.01837% | 0 | 527 | 482 | Other Exciter Problems | During the previous event, the unit had been rolled up to synchronise spe
0
|  |  | (4500-4899) |  | Generator | 2.9 | 2.9 | 1397.8 | 0.01712% | 0.01772% | 0.01837%
TC2 | D1 | 4 | 8000 | 2014-01-11 05:23 | 2014-01-11 19:09 | 13.7667 | 3.3793 | 1926.1993 | 0.0236% | 0.02442% | 0.02531% | 458 | 607 | 570 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup
TC1 | D1 | 10 | 8000 | 2014-01-11 05:23 | 2014-01-11 19:09 | 13.7667 | 2.4176 | 925.9259 | 0.01134% | 0.01174% | 0.01217% | 338 | 410 | 383 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup
TC2 | D1 | 5 | 8000 | 2014-01-11 19:09 | 2014-01-12 02:45 | 7.6 | 3.0926 | 1762.7743 | 0.02159% | 0.02234% | 0.02317% | 360 | 607 | 570 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup
TC1 | D1 | 11 | 8000 | 2014-01-11 19:09 | 2014-01-11 21:03 | 1.9 | 0.94537 | 362.0751 | 0.004435% | 0.00459% | 0.004758% | 206 | 410 | 383 | Chemical Feed Storage; Mill Feeders And Conveyors | Reactant supply C Limestone conveyor belt broke and issues with running backup
CR4 | MO | 9 | 8100 | 2014-02-16 11:30 | 2014-02-18 04:28 | 40.9667 | 40.9667 | 6349.8333 | 0.07779% | 0.08049% |  | 0 | 168 | 155 | Wet Scrubber/absorber Tower Or Module | Flue gas desulfurization module cleaning.
MC4 | D4 | 22 | 8160 | 2014-02-17 20:00 | 2014-02-18 00:24 | 4.4 | 1.6343 | 794.2629 | 0.00973% | 0.01007% |  | 330 | 525 | 486 | Wet Scrubber Mist Eliminators/demisters & Washdown | FGD Demister Wash Line - Relocation
MC3 | D4 | 28 | 8160 | 2014-02-17 20:00 | 2014-02-18 00:46 | 4.7667 | 1.048 | 412.9083 | 0.005058% | 0.005234% |  | 330 | 423 | 394 | Wet Scrubber Mist Eliminators/demisters & Washdown | FGD Demister Wash Line - Relocation
MC1 | D1 | 1 | 8280 | 2014-01-07 07:15 | 2014-01-07 08:58 | 1.7167 | 0.36414 | 110.3348 | 0.001352% | 0.001399% | 0.00145% | 260 | 330 | 303 | Wet Scrubber - Reagent Feed Piping | FGD Reactant Feed Line - Leak
CR4 | D1 | 1 | 8280 | 2014-01-07 21:20 | 2014-01-07 23:43 | 2.3833 | 0.7377 | 114.3433 | 0.001401% | 0.001449% | 0.001503% | 116 | 168 | 155 | Wet Scrubber - Reagent Feed Piping | Reactive feed line from supply pump frozen.
MC3 | NC | 3 | 8460 | 2014-01-15 | 2014-01-15 03:06 | 3.1 | [5 empty] | 0 | 423 | 394 | Wet Scrubber Testing | Mid Flow RATA Test
MC3 | NC | 7 | 8460 | 2014-01-15 09:42 | 2014-01-15 12:09 | 2.45 | [5 empty] | 0 | 423 | 394 | Wet Scrubber Testing | Full Load RATA Test
MC3 | NC | 9 | 8460 | 2014-01-15 13:14 | 2014-01-15 16:42 | 3.4667 | [5 empty] | 0 | 423 | 394 | Wet Scrubber Testing | Full Load RATA Test
MC2 | NC | 52 | 8460 | 2014-02-11 08:00 | 2014-02-11 12:20 | 4.3333 | [5 empty] | 0 | 330 | 299 | Wet Scrubber Testing | Particulate Matter Testing - Full Load
MC1 | NC | 28 | 8460 | 2014-02-11 12:45 | 2014-02-11 16:00 | 3.25 | [5 empty] | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
MC1 | NC | 29 | 8460 | 2014-02-12 07:00 | 2014-02-12 22:45 | 15.75 | [5 empty] | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
MC2 | NC | 55 | 8460 | 2014-02-13 08:00 | 2014-02-13 13:11 | 5.1833 | [5 empty] | 0 | 330 | 299 | Wet Scrubber Testing | Particulate Matter Testing - Full Load
MC1 | NC | 33 | 8460 | 2014-02-13 13:40 | 2014-02-13 22:00 | 8.3333 | [5 empty] | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
GR4 | D1 | 14 | 8551 | 2014-01-11 22:02 | 2014-01-11 23:49 | 1.7833 | 0.50952 | 49.9333 | 0.0006117% | 0.0006329% | 0.0006562% | 75 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing loss of two half cabinets.
GR4 | D1 | 15 | 8551 | 2014-01-12 00:59 | 2014-01-12 12:30 | 11.5167 | 2.7421 | 268.7222 | 0.003292% | 0.003406% | 0.003531% | 80 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets.
GR4 | D1 | 16 | 8551 | 2014-01-12 12:30 | 2014-01-12 14:38 | 2.1333 | 0.60952 | 59.7333 | 0.0007317% | 0.0007572% | 0.000785% | 75 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets. Derate increased
GR4 | D1 | 17 | 8551 | 2014-01-13 12:40 | 2014-01-15 08:51 | 44.1833 | 10.5198 | 1030.9444 | 0.01263% | 0.01307% | 0.01355% | 80 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets.
GR4 | D1 | 18 | 8551 | 2014-01-16 02:31 | 2014-01-16 06:41 | 4.1667 | 0.19841 | 19.4444 | 0.0002382% | 0.0002465% | 0.0002555% | 100 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets.
GR4 | D1 | 19 | 8551 | 2014-01-16 10:36 | 2014-01-16 14:30 | 3.9 | 0.37143 | 36.4 | 0.0004459% | 0.0004614% | 0.0004784% | 95 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | Broken wire in B5 Precip causing the loss of two half cabinets.
GR4 | D1 | 20 | 8551 | 2014-01-17 20:13 | 2014-01-18 00:33 | 4.3333 | 0.4127 | 40.4444 | 0.0004954% | 0.0005127% | 0.0005315% | 95 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded
GR4 | D1 | 21 | 8551 | 2014-01-18 17:09 | 2014-01-18 22:26 | 5.2833 | 0.25159 | 24.6556 | 0.000302% | 0.0003125% | 0.000324% | 100 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result ot two half cabinets grounded
GR4 | D1 | 22 | 8551 | 2014-01-20 09:20 | 2014-01-20 18:30 | 9.1667 | 0.43651 | 42.7778 | 0.000524% | 0.0005422% | 0.0005622% | 100 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded o
GR4 | D1 | 23 | 8551 | 2014-01-20 18:30 | 2014-01-24 12:00 | 89.5 | 2.5571 | 250.6 | 0.00307% | 0.003177% | 0.003293% | 102 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded o
GR4 | D1 | 24 | 8551 | 2014-01-24 12:00 | 2014-02-05 11:55 | 287.9167 | 5.4841 | 537.4444 | 0.006584% | 0.006812% | 0.007063% | 103 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded o
CR5 | SF | 8 | 8560 | 2014-02-09 | 2014-02-10 00:12 | 24.2 | 24.2 | 4065.6 | 0.0498% | 0.05153% | 0.05343% | 0 | 181 | 168 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
CR4 | D1 | 8 | 8560 | 2014-02-09 | 2014-02-09 11:42 | 11.7 | 6.1286 | 949.9286 | 0.01164% | 0.01204% | 0.01248% | 80 | 168 | 155 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
CR6 | D1 | 9 | 8560 | 2014-02-09 | 2014-02-09 06:50 | 6.8333 | 2.5134 | 603.2184 | 0.007389% | 0.007646% | 0.007927% | 165 | 261 | 240 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
BR2 | MO | 15 | 8560 | 2014-02-28 12:26 | 2014-03-02 18:19 | 53.88 | 53.88 | 9051.84 | 0.1109% | 0.1147% |  | 0 | 180 | 168 | Electrostatic Precipitator Problems | Precipitator fields out of service and tube leak repair
TC2 | D1 | 6 | 8650 | 2014-01-17 19:30 | 2014-01-17 22:15 | 2.75 | 0.54366 | 309.8847 | 0.003796% | 0.003928% | 0.004072% | 487 | 607 | 570 | Baghouse Systems - General | The bags in the baghouse are deteriorating ... holes in the bags
TC2 | D1 | 7 | 8650 | 2014-01-18 04:15 | 2014-01-18 05:45 | 1.5 | 0.29654 | 169.028 | 0.002071% | 0.002143% | 0.002221% | 487 | 607 | 570 | Baghouse Systems - General | The bags in the baghouse are deteriorating ... holes in the bags
MC4 | NC | 11 | 8825 | 2014-01-22 10:35 | 2014-01-22 20:00 | 9.4167 | [5 empty] | 0 | 525 | 486 | Other Scr Problems | SCR Flow Test @ Full Load
MC4 | NC | 12 | 8825 | 2014-01-23 08:47 | 2014-01-23 15:10 | 6.3833 | [5 empty] | 0 | 525 | 486 | Other Scr Problems | SCR Flow Test @ Full Load
MC4 | NC | 13 | 8825 | 2014-01-24 12:20 | 2014-01-24 18:02 | 5.7 | [5 empty] | 0 | 525 | 486 | Other Scr Problems | SCR Flow Test - Full Load
0
|  |  | (8000-8835) |  | Pollution Control Equip. | 723.38 | 166.2406 | 30269.2568 | 0.3708% | 0.3837% | 0.1795%
GH1 | D1 | 1 | 9270 | 2014-01-08 07:48 | 2014-01-08 09:10 | 1.3667 | 0.15068 | 72.4756 | 0.0008878% | 0.0009187% | 0.0009525% | 460 | 517 | 481 | Wet Coal | Feeder plugged due to wet coal and this tripped the mill.
GH3 | D1 | 6 | 9290 | 2014-01-24 23:19 | 2014-01-25 03:33 | 4.2333 | 0.37755 | 181.9771 | 0.002229% | 0.002307% | 0.002392% | 480 | 527 | 482 | Other Fuel Quality Problems | Load Reduction #3Derate was reported as a coal quality issue. Actually, we were b
|  |  | (9000-9340) |  | External | 5.6 | 0.52822 | 254.4527 | 0.003117% | 0.003225% | 0.003344%
GH3 | PD | 17 | 9510 | 2014-02-15 22:00 | 2014-02-16 13:04 | 15.0667 | 9.3488 | 4506.1055 | 0.0552% |  |  | 200 | 527 | 482 | Plant Modific. Strictly For Compliance W/ Reg. Req | KBR electrical tie-in for Bag House and ID fan.
CR6 | D1 | 15 | 9600 | 2014-02-28 08:13 | 2014-02-28 08:35 | 0.36667 | 0.029502 | 7.0805 | 8.674e-05% | 8.975e-05% | 9.305e-05% | 240 | 261 | 240 | So2 Stack Emissions - Fossil Steam Units | Dropped load to keep SO2 in compliance.
CR6 | D1 | 16 | 9600 | 2014-02-28 08:35 | 2014-02-28 09:53 | 1.3 | 0.20421 | 49.0115 | 0.0006004% | 0.0006213% | 0.0006441% | 220 | 261 | 240 | So2 Stack Emissions - Fossil Steam Units | Dropped load an additional 20 MW to remain in SO2 compliance . Unit now at 220 MW
TC2 | D1 | 14 | 9610 | 2014-01-20 01:45 | 2014-01-20 16:30 | 14.75 | 1.8286 | 1042.2807 | 0.01277% | 0.01321% | 0.0137% | 531.75 | 607 | 570 | Nox Stack Emissions - Fossil Steam Units | High NOx readings required unit derate to avoid exceedance. Mill configuration ma
TC2 | D1 | 8 | 9620 | 2014-01-18 11:25 | 2014-01-18 14:00 | 2.5833 | 0.31919 | 181.9399 | 0.002229% | 0.002306% | 0.002391% | 532 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | High particulate matter readings required derate to avoid an exceedance.
TC2 | D1 | 9 | 9620 | 2014-01-18 17:55 | 2014-01-18 18:10 | 0.25 | 0.049423 | 28.1713 | 0.0003451% | 0.0003571% | 0.0003702% | 487 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | The bags in the baghouse are deteriorating … holes in the bags
TC2 | D1 | 10 | 9620 | 2014-01-18 18:10 | 2014-01-18 19:15 | 1.0833 | 0.10708 | 61.0379 | 0.0007477% | 0.0007737% | 0.0008021% | 547 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | The bags in the baghouse are deteriorating … holes in the bags
TC2 | D1 | 12 | 9620 | 2014-01-19 10:29 | 2014-01-19 13:00 | 2.5167 | 0.31096 | 177.2446 | 0.002171% | 0.002247% | 0.002329% | 532 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | High particulate readings required unit derate to avoid an exceedance
TC2 | D1 | 13 | 9620 | 2014-01-19 17:50 | 2014-01-19 20:15 | 2.4167 | 0.2986 | 170.2018 | 0.002085% | 0.002157% | 0.002237% | 532 | 607 | 570 | Particulate Stack Emissions - Fossil Steam Units | High particulate readings required unit derate to avoid an exceedance
GR4 | D1 | 1 | 9630 | 2014-01-02 12:20 | 2014-01-02 15:10 | 2.8333 | 0.24286 | 23.8 | 0.0002916% | 0.0003017% | 0.0003128% | 96 | 105 | 98 | Opacity - Fossil Steam Units | Load reduced on GR4 to blow soot and to stay within 3 hr Particulate limit
GR4 | D1 | 2 | 9630 | 2014-01-04 05:51 | 2014-01-04 06:41 | 0.83333 | 0.039683 | 3.8889 | 4.764e-05% | 4.929e-05% | 5.111e-05% | 100 | 105 | 98 | Opacity - Fossil Steam Units | Load reduced on GR4 due to Opacity issues.
GR4 | D1 | 3 | 9630 | 2014-01-04 07:34 | 2014-01-04 16:06 | 8.5333 | 0.40635 | 39.8222 | 0.0004878% | 0.0005048% | 0.0005233% | 100 | 105 | 98 | Opacity - Fossil Steam Units | Load reduced on GR4 due to Opacity issues.
GR4 | D1 | 4 | 9630 | 2014-01-04 16:06 | 2014-01-04 17:34 | 1.4667 | 0.027937 | 2.7378 | 3.354e-05% | 3.47e-05% | 3.598e-05% | 103 | 105 | 98 | Opacity - Fossil Steam Units | GR4 Derate reduced from 5MW to 2MW due to Opacity issues.
GR4 | D1 | 5 | 9630 | 2014-01-08 05:00 | 2014-01-08 08:04 | 3.0667 | 0.29206 | 28.6222 | 0.0003506% | 0.0003628% | 0.0003761% | 95 | 105 | 98 | Opacity - Fossil Steam Units | GR4 load reduction to avoid opacity exceedances. B5 has a tube leak and we have a
GR4 | D1 | 7 | 9630 | 2014-01-08 13:30 | 2014-01-08 17:55 | 4.4167 | 0.12619 | 12.3667 | 0.0001515% | 0.0001568% | 0.0001625% | 102 | 105 | 98 | Opacity - Fossil Steam Units | GR4 load reduction to avoid opacity exceedances. B5 has a tube leak and we have a
GR3 | D1 | 4 | 9630 | 2014-02-11 08:17 | 2014-02-11 09:18 | 1.0167 | 0.094889 | 6.7371 | 8.253e-05% | 8.54e-05% | 8.854e-05% | 68 | 75 | 71 | Opacity - Fossil Steam Units | Load reduced on GR3 due to high opacity.
GR3 | D1 | 5 | 9630 | 2014-02-11 09:18 | 2014-02-11 09:40 | 0.36667 | 0.024444 | 1.7356 | 2.126e-05% | 2.2e-05% | 2.281e-05% | 70 | 75 | 71 | Opacity - Fossil Steam Units | GR3 derate reduction from event #4. Derate due to igh opacity.
GR3 | D1 | 6 | 9630 | 2014-02-11 09:40 | 2014-02-11 13:13 | 3.55 | 0.80467 | 57.1313 | 0.0006999% | 0.0007242% | 0.0007508% | 58 | 75 | 71 | Opacity - Fossil Steam Units | Continuation of previous event. GR3 derate increased to blow soot and clean boile
GR3 | D1 | 7 | 9630 | 2014-02-11 13:13 | 2014-02-11 17:20 | 4.1167 | 0.38422 | 27.2798 | 0.0003342% | 0.0003458% | 0.0003585% | 68 | 75 | 71 | Opacity - Fossil Steam Units | Continuation of previous event. GR3/B4 soot blowing completed, raised load as muc
GR3 | D1 | 8 | 9630 | 2014-02-12 07:40 | 2014-02-12 08:20 | 0.66667 | 0.08 | 5.68 | 6.958e-05% | 7.2e-05% | 7.465e-05% | 66 | 75 | 71 | Opacity - Fossil Steam Units | GR3 load reduced due to high opacity.
GR3 | D1 | 9 | 9630 | 2014-02-12 08:20 | 2014-02-12 09:30 | 1.1667 | 0.093333 | 6.6267 | 8.118e-05% | 8.4e-05% | 8.709e-05% | 69 | 75 | 71 | Opacity - Fossil Steam Units | GR3 derate decreased from Event #8 due to high opacity.
GR3 | D1 | 10 | 9630 | 2014-02-12 09:30 | 2014-02-12 11:00 | 1.5 | 0.08 | 5.68 | 6.958e-05% | 7.2e-05% | 7.465e-05% | 71 | 75 | 71 | Opacity - Fossil Steam Units | GR3 Derate reduction from Event #9 due to high opacity.
GR4 | D1 | 28 | 9630 | 2014-02-13 14:41 | 2014-02-13 16:28 | 1.7833 | 0.16984 | 16.6444 | 0.0002039% | 0.000211% | 0.0002187% | 95 | 105 | 98 | Opacity - Fossil Steam Units | GR4 derated due to opacity, blowing soot to clean up the boiler.
GH2 | D1 | 1 | 9650 | 2014-01-06 11:20 | 2014-01-06 12:00 | 0.66667 | 0.21218 | 101.2102 | 0.00124% | 0.001283% | 0.00133% | 347 | 509 | 477 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Lost SO3 mitigation system. Air pressure / injection causing H2S
GH2 | D1 | 3 | 9650 | 2014-01-15 19:30 | 2014-01-15 21:03 | 1.55 | 0.27102 | 129.2773 | 0.001584% | 0.001639% | 0.001699% | 420 | 509 | 477 | Other Stack Or Exhaust Emissions -fossil Stm Unit | H2SO4 in high alarm. Dropped load to investigate. Blower for ou
GH3 | D1 | 12 | 9650 | 2014-02-02 20:10 | 2014-02-02 20:45 | 0.58333 | 0.14058 | 67.7574 | 0.00083% | 0.0008589% | 0.0008905% | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | 3-2B SO3 injection blower pressure sensing line came off causing
GH4 | D1 | 5 | 9650 | 2014-02-03 00:50 | 2014-02-03 01:48 | 0.96667 | 0.24257 | 119.1027 | 0.001459% | 0.00151% | 0.001565% | 400 | 534 | 491 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | D1 | 13 | 9650 | 2014-02-05 14:10 | 2014-02-05 15:00 | 0.83333 | 0.27989 | 134.9051 | 0.001653% | 0.00171% | 0.001773% | 350 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | D1 | 14 | 9650 | 2014-02-05 15:00 | 2014-02-05 19:50 | 4.8333 | 2.9257 | 1410.1777 | 0.01727% | 0.01787% | 0.01853% | 208 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH1 | D1 | 10 | 9650 | 2014-02-13 07:23 | 2014-02-13 09:08 | 1.75 | 0.091393 | 43.9599 | 0.0005385% | 0.0005572% | 0.0005777% | 490 | 517 | 481 | Other Stack Or Exhaust Emissions -fossil Stm Unit | U1 H2SO4 was high. Dropped load to keep it in compliance.
GH3 | D1 | 15 | 9650 | 2014-02-15 04:41 | 2014-02-15 07:07 | 2.4333 | 0.5864 | 282.6453 | 0.003462% | 0.003583% | 0.003714% | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | D1 | 16 | 9650 | 2014-02-15 11:22 | 2014-02-15 14:52 | 3.5 | 2.0721 | 998.7552 | 0.01223% | 0.01266% | 0.01313% | 215 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | D1 | 19 | 9650 | 2014-02-17 13:35 | 2014-02-18 10:26 | 20.85 | 1.3847 | 667.4374 | 0.008176% | 0.00846% | 0.008771% | 492 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | H2SO4 out of limit for probe pluggage.
GH3 | D1 | 21 | 9650 | 2014-02-20 12:30 | 2014-02-20 13:05 | 0.58333 | 0.15164 | 73.0927 | 0.0008954% | 0.0009265% | 0.0009606% | 390 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
|  |  | (9504-9720) |  | Reg., Safety, Envrn. | 114.2 | 23.721 | 10490.1473 | 0.1285% | 0.07585% | 0.07864%
TC1 | U1 | 12 | 9900 | 2014-01-11 21:03 | 2014-01-12 07:57 | 10.9 | 10.9 | 4174.7 | 0.05114% | 0.05292% | 0.05486% | 0 | 410 | 383 | Operator Error | During load drop, operator error in valve closing caused the TDBFP main extraction
TC1 | NC | 23 | 9999 | 2014-01-29 08:00 | 2014-01-29 10:00 | 2 | [5 empty] | 0 | 410 | 383 | Total Unit Performance Testing | Unit was running and requested full load production to allow for the full-load tes
TC1 | NC | 26 | 9999 | 2014-02-05 10:45 | 2014-02-05 16:26 | 5.6833 | [5 empty] | 0 | 410 | 383 | Total Unit Performance Testing | Unit running and good for full load, this non-curtailing event was for the complet
CR5 | NC | 9 | 9999 | 2014-02-13 10:00 | 2014-02-13 14:00 | 4 | [5 empty] | 0 | 181 | 168 | Total Unit Performance Testing | Full load winter capability test.
TC1 | NC | 30 | 9999 | 2014-02-19 08:00 | 2014-02-19 14:00 | 6 | [5 empty] | 0 | 410 | 383 | Total Unit Performance Testing | Test run at full load to maintain high temperatures for unit testing.
CR4 | NC | 12 | 9999 | 2014-02-24 09:40 | 2014-02-24 14:12 | 4.5333 | [5 empty] | 0 | 168 | 155 | Total Unit Performance Testing | Full Load winter capability test.
|  |  | (9900-9999) |  | Per., and Proced. Errors | 33.1167 | 10.9 | 4174.7 | 0.05114% | 0.05292% | 0.05486%
All Steam | [5 empty] | 5188.9667 | 2303.2003 | 810947.0447 | 9.856% | 6.435% | 2.933%
PR13 | PO | 4 | 4720 | 2014-02-15 06:08 | 2014-03-01 | 329.8667 | 329.8667 | 57726.6667 |  |  |  | 0 | 176 | 175 | Generator Synchronization Equipment | Generator synchronization equipment modifications. Replacing all generator protec
|  |  | (4500-4899) |  | Generator | 329.8667 | 329.8667 | 57726.6667 | 0% | 0% | 0%
|  |  | (5000-5299) |  | Gas Turbine | 0 | 0 | 0 | 0% | 0% | 0%
HA1 | U1 | 9 | 3611 | 2014-02-08 02:53 | 2014-02-08 19:05 | 16.2 | 16.2 | 194.4 |  |  |  | 0 | 12 | 12 | Switchyard Circuit Breakers | Loss of power to 138KV sub.
HA2 | U1 | 4 | 3611 | 2014-02-08 02:53 | 2014-02-08 19:05 | 16.2 | 16.2 | 194.4 |  |  |  | 0 | 12 | 12 | Switchyard Circuit Breakers | Loss power to 138KV bus in substation
CR11 | U1 | 9 | 3840 | 2014-02-03 00:42 | 2014-02-03 09:37 | 8.9167 | 8.9167 | 124.8333 |  |  |  | 0 | 14 | 14 | Service Air Compressors | Clutch air compressor pumping up slowly - probably due to the weather.
TC8 | U1 | 9 | 3869 | 2014-01-10 14:00 | 2014-01-14 13:28 | 95.4667 | 95.4667 | 16802.1333 |  |  |  | 0 | 180 | 176 | Other Fire Protection System Problems | Forced outage due to issue with Fire Protection System.
|  |  | (3110-3999) |  | Balance Of Plant | 136.7833 | 136.7833 | 17315.7667 | 0% | 0% | 0%
BR7 | U1 | 4 | 4700 | 2014-01-04 06:11 | 2014-01-04 11:16 | 5.0833 | 5.0833 | 869.25 |  |  |  | 0 | 172 | 171 | Generator Voltage Control | AVR Fault due to loss of channel one processor.
BR6 | SF | 2 | 4810 | 2014-01-02 16:13 | 2014-01-02 17:03 | 0.83333 | 0.83333 | 142.5 |  |  |  | 0 | 172 | 171 | Generator Output Breaker | Generator circuit breaker loss of 120VAC control power prevented the unit from sta
|  |  | (4500-4899) |  | Generator | 5.9167 | 5.9167 | 1011.75 | 0% | 0% | 0%
TC10 | U1 | 2 | 5016 | 2014-01-03 05:21 | 2014-01-03 07:03 | 1.7 | 1.7 | 299.2 |  |  |  | 0 | 180 | 176 | High Pressure Compressor - Bleed Valves | Forced outage due to compressor bleed valve frozen shut.
TC6 | U1 | 8 | 5016 | 2014-01-07 01:25 | 2014-01-07 05:49 | 4.4 | 4.4 | 774.4 |  |  |  | 0 | 180 | 176 | High Pressure Compressor - Bleed Valves | Forced outage due to compressor bleed valve frozen closed.
TC6 | SF | 13 | 5016 | 2014-01-22 04:20 | 2014-01-22 05:55 | 1.5833 | 1.5833 | 248.5833 |  |  |  | 0 | 160 | 157 | High Pressure Compressor - Bleed Valves | Startup failure due to frozen compressor bleed valve.
TC6 | SF | 14 | 5016 | 2014-01-22 05:55 | 2014-01-22 06:45 | 0.83333 | 0.83333 | 130.8333 |  |  |  | 0 | 160 | 157 | High Pressure Compressor - Bleed Valves | Startup failure due to frozen compressor bleed valve.
BR11 | U1 | 3 | 5017 | 2014-01-06 17:57 | 2014-01-06 19:14 | 1.2833 | 1.2833 | 164.2667 |  |  |  | 0 | 129 | 128 | Low Pressure Compressor Bleed Valves | Loose limit switch on blow off valve caused unit to trip.
BR11 | U1 | 16 | 5017 | 2014-01-30 03:36 | 2014-01-30 07:40 | 4.0667 | 4.0667 | 520.5333 |  |  |  | 0 | 129 | 128 | Low Pressure Compressor Bleed Valves | Loose limit switch on compressor blow off valve
TC7 | U1 | 4 | 5041 | 2014-01-05 14:07 | 2014-01-05 15:36 | 1.4833 | 1.4833 | 261.0667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Forced outage due to fuel gas valve (SRV).
TC6 | U1 | 6 | 5041 | 2014-01-06 13:52 | 2014-01-06 14:46 | 0.9 | 0.9 | 158.4 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Unit tripped due to a fuel gas valve (worker valve) not controlling properly.
TC6 | SF | 17 | 5041 | 2014-01-23 16:56 | 2014-01-23 17:21 | 0.41667 | 0.41667 | 65.4167 |  |  |  | 0 | 160 | 157 | Gas Turbine - Fuel Piping And Valves | Startup failure due to issue with fuel gas valve.
TC6 | SF | 22 | 5041 | 2014-01-24 10:30 | 2014-01-24 11:08 | 0.63333 | 0.63333 | 99.4333 |  |  |  | 0 | 160 | 157 | Gas Turbine - Fuel Piping And Valves | Startup failure due to issue with fuel gas valve.
TC6 | MO | 23 | 5041 | 2014-01-25 12:06 | 2014-01-25 16:20 | 4.2333 | 4.2333 | 664.6333 |  |  |  | 0 | 160 | 157 | Gas Turbine - Fuel Piping And Valves | Maintenance outage to prepare unit for tuning.
TC8 | U1 | 15 | 5041 | 2014-01-30 06:34 | 2014-01-30 07:49 | 1.25 | 1.25 | 196.25 |  |  |  | 0 | 160 | 157 | Gas Turbine - Fuel Piping And Valves | Forced outage to reset lifted safety valve that occurred due to fuel gas pressure
TC6 | MO | 30 | 5041 | 2014-02-04 11:33 | 2014-02-04 15:52 | 4.3167 | 4.3167 | 759.7333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Maintenance outage to change controller on Fuel Gas Worker Valve.
TC9 | D1 | 17 | 5041 | 2014-02-07 10:00 | 2014-02-07 12:38 | 2.6333 | 1.463 | 257.4815 |  |  |  | 80 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Derate to 80 MWs due to issue with worker fuel gas valve.
TC9 | U1 | 15 | 5041 | 2014-02-07 12:38 | 2014-02-07 15:35 | 2.95 | 2.95 | 519.2 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Forced outage to address pressure swings due to worker fuel gas valve.
TC7 | U1 | 2 | 5048 | 2014-01-03 05:14 | 2014-01-03 06:52 | 1.6333 | 1.6333 | 287.4667 |  |  |  | 0 | 180 | 176 | Gas Fuel System with controls and instruments | Forced outage due to Hazardous Gas alarm.
TC6 | U1 | 10 | 5048 | 2014-01-21 16:35 | 2014-01-21 17:24 | 0.81667 | 0.81667 | 128.2167 |  |  |  | 0 | 160 | 157 | Gas Fuel System with controls and instruments | Forced outage due to combustion instrumentation issues.
TC6 | U1 | 11 | 5048 | 2014-01-21 17:32 | 2014-01-21 20:01 | 2.4833 | 2.4833 | 389.8833 |  |  |  | 0 | 160 | 157 | Gas Fuel System with controls and instruments | Forced outage due to combustion instrumentation issues.
TC6 | U1 | 25 | 5048 | 2014-01-27 11:27 | 2014-01-27 14:05 | 2.6333 | 2.6333 | 413.4333 |  |  |  | 0 | 160 | 157 | Gas Fuel System with controls and instruments | Unit tripped due to frozen sensing line to 96GN transmitter.
BR6 | MO | 10 | 5048 | 2014-02-04 06:30 | 2014-02-04 08:00 | 1.5 | 1.5 | 256.5 |  |  |  | 0 | 172 | 171 | Gas Fuel System with controls and instruments | Change cable for fuel gas flow meter RTD.
BR5 | MO | 10 | 5048 | 2014-02-18 08:00 | 2014-02-18 12:46 | 4.7667 | 4.7667 | 533.8667 |  |  |  | 0 | 113 | 112 | Gas Fuel System with controls and instruments | Inspect orifice, calibrate transmitter for fuel gas system flow meter.
BR7 | U1 | 12 | 5049 | 2014-02-10 17:14 | 2014-02-10 19:34 | 2.3333 | 2.3333 | 399 |  |  |  | 0 | 172 | 171 | Other Gas Turbine Fuel System Problems | Issue with pressure regulators in reducing station.
HA1 | U1 | 7 | 5050 | 2014-01-30 06:30 | 2014-01-30 07:01 | 0.51667 | 0.51667 | 7.2333 |  |  |  | 0 | 14 | 14 | Gas Turbine - Ignition System | Ignition torch failed to light
BR5 | U1 | 2 | 5054 | 2014-01-06 08:23 | 2014-01-06 11:47 | 3.4 | 3.4 | 442 |  |  |  | 0 | 131 | 130 | Water Injection System | Instrument measuring DP across water injection control started to freeze. Operato
TC6 | U1 | 4 | 5079 | 2014-01-06 02:17 | 2014-01-06 03:50 | 1.55 | 1.55 | 272.8 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to a lean blowout.
TC6 | U1 | 12 | 5079 | 2014-01-22 00:08 | 2014-01-22 04:20 | 4.2 | 4.2 | 659.4 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Forced outage due to flameout.
TC10 | SF | 13 | 5079 | 2014-01-22 00:45 | 2014-01-22 04:02 | 3.2833 | 3.2833 | 515.4833 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Failed to ignite during startup.
TC6 | U1 | 15 | 5079 | 2014-01-23 11:39 | 2014-01-23 12:04 | 0.41667 | 0.41667 | 65.4167 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Forced outage due to combustion issue.
TC6 | U1 | 18 | 5079 | 2014-01-23 17:30 | 2014-01-23 18:00 | 0.5 | 0.5 | 78.5 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Forced outage due to combustion issue.
TC6 | U1 | 19 | 5079 | 2014-01-23 18:18 | 2014-01-23 18:49 | 0.51667 | 0.51667 | 81.1167 |  |  |  | 0 | 160 | 157 | Other Gas Turbine Combustor Problems | Forced outage due to combustion issue.
TC5 | U1 | 12 | 5079 | 2014-02-11 06:16 | 2014-02-11 08:35 | 2.3167 | 2.3167 | 407.7333 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
TC6 | U1 | 33 | 5079 | 2014-02-11 06:16 | 2014-02-11 06:58 | 0.7 | 0.7 | 123.2 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
TC6 | U1 | 34 | 5079 | 2014-02-11 08:29 | 2014-02-11 09:45 | 1.2667 | 1.2667 | 222.9333 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
BR11 | MO | 8 | 5108 | 2014-01-14 08:00 | 2014-01-14 13:54 | 5.9 | 5.9 | 755.2 |  |  |  | 0 | 129 | 128 | Gas Turbine - High Engine Exhaust Temperature | Outage to replace TAT probe. Two thermocouples not working
HA1 | U1 | 5 | 5108 | 2014-01-17 14:23 | 2014-01-20 14:33 | 72.1667 | 72.1667 | 1010.3333 |  |  |  | 0 | 14 | 14 | Gas Turbine - High Engine Exhaust Temperature | Lost two exhaust gas thermocouples during run.
BR6 | U1 | 7 | 5109 | 2014-01-23 13:31 | 2014-01-23 14:49 | 1.3 | 1.3 | 222.3 |  |  |  | 0 | 172 | 171 | Other Gas Turbine Exhaust Problems | Loss TC on TAT2 readings. TC reading was coming in and out of service
CR11 | U1 | 5 | 5110 | 2014-01-21 10:51 | 2014-01-21 12:24 | 1.55 | 1.55 | 21.7 |  |  |  | 0 | 14 | 14 | Gas Turbine - Lube Oil System - General | Lube oil temperature to low.
BR8 | MO | 4 | 5111 | 2014-01-13 07:46 | 2014-01-13 09:25 | 1.65 | 1.65 | 211.2 |  |  |  | 0 | 129 | 128 | Gas Turbine - Lube Oil Pumps | Check DC brushes on emergency lube oil equipment
BR9 | MO | 5 | 5111 | 2014-01-13 09:25 | 2014-01-13 10:22 | 0.95 | 0.95 | 131.1 |  |  |  | 0 | 139 | 138 | Gas Turbine - Lube Oil Pumps | Check brushes on DC lube oil pumps
BR10 | MO | 4 | 5111 | 2014-01-13 10:22 | 2014-01-13 11:18 | 0.93333 | 0.93333 | 128.8 |  |  |  | 0 | 139 | 138 | Gas Turbine - Lube Oil Pumps | Outage to check brushes on DC lube oil pumps.
BR11 | MO | 6 | 5111 | 2014-01-13 12:32 | 2014-01-13 13:45 | 1.2167 | 1.2167 | 155.7333 |  |  |  | 0 | 129 | 128 | Gas Turbine - Lube Oil Pumps | Outage to check brushes on DC lube oil pumps
HA2 | MO | 6 | 5111 | 2014-02-19 11:20 | 2014-02-19 12:20 | 1 | 1 | 12 |  |  |  | 0 | 12 | 12 | Gas Turbine - Lube Oil Pumps | Inspect brushes and repair coupling for DC lube oil pump.
BR8 | MO | 13 | 5111 | 2014-02-19 12:10 | 2014-02-19 12:35 | 0.41667 | 0.41667 | 53.3333 |  |  |  | 0 | 129 | 128 | Gas Turbine - Lube Oil Pumps | Check brushes on DC lube oil pumps
HA1 | U1 | 4 | 5120 | 2014-01-16 12:31 | 2014-01-17 14:09 | 25.6333 | 25.6333 | 358.8667 |  |  |  | 0 | 14 | 14 | Gas Turbine - Hydraulic Oil System | Oil leak on diesel starting engine.
TC9 | SF | 3 | 5130 | 2014-01-03 | 2014-01-03 20:51 | 20.85 | 20.85 | 3669.6 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to issue with 89SS.
TC8 | U1 | 2 | 5130 | 2014-01-03 05:21 | 2014-01-04 00:26 | 19.0833 | 19.0833 | 3358.6667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to issue with 89SS.
TC8 | SF | 5 | 5130 | 2014-01-05 19:28 | 2014-01-06 15:58 | 20.5 | 20.5 | 3608 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to issue with 89SS.
TC9 | U1 | 7 | 5130 | 2014-01-06 02:27 | 2014-01-06 02:57 | 0.5 | 0.5 | 88 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to issue with 89SS.
CR11 | U1 | 2 | 5130 | 2014-01-06 20:13 | 2014-01-07 09:05 | 12.8667 | 12.8667 | 180.1333 |  |  |  | 0 | 14 | 14 | Gas Turbine - Starting System (including Motor) | Broken terminal on battery cable causing Cane Run 11 starting diesel to be unable
TC5 | SF | 14 | 5130 | 2014-02-17 06:28 | 2014-02-17 06:40 | 0.2 | 0.2 | 35.2 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to issue with LCI.
TC5 | U1 | 16 | 5130 | 2014-02-17 10:43 | 2014-02-17 11:57 | 1.2333 | 1.2333 | 217.0667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage to change out resistivity probe on the cooling system for the LCI.
TC5 | SF | 18 | 5130 | 2014-02-17 17:45 | 2014-02-17 20:14 | 2.4833 | 2.4833 | 437.0667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to low resistivity in the cooling water for the LCI. Changed
TC9 | SF | 20 | 5130 | 2014-02-26 02:38 | 2014-02-26 03:45 | 1.1167 | 1.1167 | 196.5333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to 89SS on TC10 failing to open.
TC10 | U1 | 25 | 5130 | 2014-02-26 02:38 | 2014-02-26 03:45 | 1.1167 | 1.1167 | 196.5333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to 89SS failing to open.
BR9 | U1 | 3 | 5140 | 2014-01-07 09:33 | 2014-01-07 10:36 | 1.05 | 1.05 | 144.9 |  |  |  | 0 | 139 | 138 | Gas Turbine - Battery And Charger System | Both battery chargers indicated failure. Failure was caused by low output current
BR7 | U1 | 7 | 5150 | 2014-01-13 08:05 | 2014-01-14 13:30 | 29.4167 | 29.4167 | 5030.25 |  |  |  | 0 | 172 | 171 | Gas Turbine - Turning Gear And Motor | Unit will not stay on rotor barring.
HA1 | SF | 2 | 5160 | 2014-01-06 21:22 | 2014-01-14 13:14 | 183.8667 | 183.8667 | 2574.1333 |  |  |  | 0 | 14 | 14 | Gas Turbine - Cooling And Seal Air System | Busted glycol line on radiator. Failed to ignite on start up.
BR11 | MO | 11 | 5160 | 2014-01-16 14:00 | 2014-01-16 18:57 | 4.95 | 4.95 | 633.6 |  |  |  | 0 | 129 | 128 | Gas Turbine - Cooling And Seal Air System | Leak of water into control air off the compressor
TC7 | U1 | 8 | 5160 | 2014-02-05 16:03 | 2014-02-05 16:08 | 0.083333 | 0.083333 | 14.6667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Unit rolled back to FSNL due to issue with pressure switch on Exhaust Frame Blower
TC7 | U1 | 9 | 5160 | 2014-02-05 16:09 | 2014-02-05 16:17 | 0.13333 | 0.13333 | 23.4667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Unit rolled back to FSNL due to issue with pressure switch on Exhaust Frame Blower
BR8 | MO | 15 | 5160 | 2014-02-20 12:35 | 2014-02-20 13:00 | 0.41667 | 0.41667 | 53.3333 |  |  |  | 0 | 129 | 128 | Gas Turbine - Cooling And Seal Air System | Check brushes on DC mantling air fan
BR9 | MO | 12 | 5160 | 2014-02-20 13:00 | 2014-02-20 17:04 | 4.0667 | 4.0667 | 561.2 |  |  |  | 0 | 139 | 138 | Gas Turbine - Cooling And Seal Air System | Changed brushes on DC mantling air fan.
BR9 | MO | 12 | 5160 | 2014-02-20 13:00 | 2014-02-20 17:04 | 4.07 | [5 empty] | 0 | 139 | 138 | Gas Turbine - Cooling And Seal Air System | F590Changed brushes on DC mantling air fan.
BR10 | MO | 10 | 5160 | 2014-02-20 17:04 | 2014-02-20 19:28 | 2.4 | 2.4 | 331.2 |  |  |  | 0 | 139 | 138 | Gas Turbine - Cooling And Seal Air System | Check brushes on DC mantling air fan.
BR11 | MO | 19 | 5160 | 2014-02-20 19:28 | 2014-02-20 21:16 | 1.8 | 1.8 | 230.4 |  |  |  | 0 | 129 | 128 | Gas Turbine - Cooling And Seal Air System | Checked brushes on DC mantling air system.
TC9 | U1 | 22 | 5160 | 2014-02-26 19:14 | 2014-02-26 19:15 | 0.016667 | 0.016667 | 2.9333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Forced outage from load runback due to issue with Exhaust Frame Blower.
PR12 | U1 | 4 | 5170 | 2014-02-19 10:25 | 2014-03-01 | 229.5833 | 229.5833 | 5280.4167 |  |  |  | 0 | 23 | 23 | Gas Turbine - Cooling Water System | Fire pump that supplies cooling water locked up.
TC5 | U1 | 2 | 5240 | 2014-01-03 11:04 | 2014-01-03 13:20 | 2.2667 | 2.2667 | 398.9333 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fire Detection And Extinguishing Sys | Unit tripped on fire protection alarm due to condensation within fire protection p
TC5 | U1 | 4 | 5246 | 2014-01-06 12:15 | 2014-01-06 14:08 | 1.8833 | 1.8833 | 331.4667 |  |  |  | 0 | 180 | 176 | Gas Turbine Control System - Hardware Problems.... | Unit tripped on high exhaust temperature differential from a failed control system
TC5 | U1 | 6 | 5246 | 2014-01-07 01:25 | 2014-01-07 05:50 | 4.4167 | 4.4167 | 777.3333 |  |  |  | 0 | 180 | 176 | Gas Turbine Control System - Hardware Problems.... | Forced outage due to compressor inlet thermocouple disagreement from a failed cont
TC6 | U1 | 20 | 5250 | 2014-01-24 04:29 | 2014-01-24 10:13 | 5.7333 | 5.7333 | 900.1333 |  |  |  | 0 | 160 | 157 | Other Controls And Instrument Problems | Forced outage due to erratic thermocouple signals from T Processor.
BR9 | MO | 14 | 5272 | 2014-02-25 06:59 | 2014-02-25 20:03 | 13.07 | [5 empty] | 0 | 139 | 138 | Gas Turbine - Boroscope Inspection | F590Eddy current inspection of R3 blade and boroscope of turbine section.
BR11 | MO | 21 | 5272 | 2014-02-26 07:11 | 2014-02-26 16:18 | 9.1167 | 9.1167 | 1166.9333 |  |  |  | 0 | 129 | 128 | Gas Turbine - Boroscope Inspection | Eddy current inspection of R3 blade and boroscope inspection of turbine section.
BR5 | MO | 12 | 5272 | 2014-02-27 06:55 | 2014-02-27 14:53 | 7.9667 | 7.9667 | 892.2667 |  |  |  | 0 | 113 | 112 | Gas Turbine - Boroscope Inspection | Eddy Current Inspection of R3 blade
BR8 | MO | 17 | 5272 | 2014-02-28 08:24 | 2014-02-28 15:30 | 7.1 | 7.1 | 908.8 |  |  |  | 0 | 129 | 128 | Gas Turbine - Boroscope Inspection | Eddy Current Inspection of R3 blade and boroscope of trubine.
BR10 | MO | 12 | 5272 | 2014-02-28 10:48 | 2014-03-02 13:50 | 51.0333 | 51.0333 | 7042.6 |  |  |  | 0 | 139 | 138 | Gas Turbine - Boroscope Inspection | Eddy current inspection of R3 blade and boroscope of turbine section.
|  |  | (5000-5299) |  | Gas Turbine | 824.6233 | 0 | 0 | 0% | 0% | 0%
|  |  | (8000-8835) |  | Pollution Control Equip. | 0 | 0 | 0 | 0% | 0% | 0%
PR13 | U1 | 2 | 9130 | 2014-01-30 07:00 | 2014-01-31 09:20 | 26.3333 | 26.3333 | 3871 |  |  |  | 0 | 148 | 147 | Lack Of Fuel (outside Management Control) | Fuel supply not available.
PR12 | U1 | 2 | 9130 | 2014-01-30 07:00 | 2014-01-31 09:20 | 26.3333 | 26.3333 | 605.6667 |  |  |  | 0 | 23 | 23 | Lack Of Fuel (outside Management Control) | Fuel supply not available.
Z1 | U1 | 2 | 9130 | 2014-01-30 07:00 | 2014-01-31 09:20 | 26.3333 | 26.3333 | 368.6667 |  |  |  | 0 | 14 | 14 | Lack Of Fuel (outside Management Control) | Fuel supply not available.
PR11 | U1 | 2 | 9130 | 2014-01-30 07:00 | 2014-01-31 09:20 | 26.3333 | 26.3333 | 316 |  |  |  | 0 | 12 | 12 | Lack Of Fuel (outside Management Control) | Fuel supply not available.
|  |  | (9000-9340) |  | External | 105.3333 | 105.3333 | 5161.3333 | 0% | 0% | 0%
|  |  | (9504-9720) |  | Reg., Safety, Envrn. | 0 | 0 | 0 | 0% | 0% | 0%
|  |  | (9504-9720) |  | Reg., Safety, Envrn. | 0 | 0 | 0 | 0% | 0% | 0%
|  |  | (9900-9999) |  | Per., and Proced. Errors | 0 | 0 | 0 | 0% | 0% | 0%

## FEB-14 BTF Impact By Cause Code
Outage | Unit | Event | Event | Cause | Event | Event | Event | Equiv. | MWH | EAF | EUOR | EFOR | Unit | Unit | Unit | Event | Event
Count | Name | Type | No | Code | Start | End | Hours | Hours | Lost | Lost | Impact | Impact | GAC | GMC | NMC | Cause | Description
0
1 | GH4 | MO | 3 | 1000 | 2014-01-01 | 2014-01-01 00:53 | 0.88333 | 0.88333 | 433.7167 | 0.005313% | 0.005498% |  | 0 | 534 | 491 | Furnace Wall Leaks | Unit 4 developed a tube leak on 8 2/3 floor on the south side of the
2 | MC2 | MO | 4 | 1000 | 2014-01-02 10:39 | 2014-01-04 11:51 | 49.2 | 49.2 | 14710.8 | 0.1802% | 0.1865% |  | 0 | 330 | 299 | Furnace Wall Tube Leaks | Boiler Tube Leak - Waterwall
3 | MC2 | MO | 67 | 1000 | 2014-02-24 09:31 | 2014-02-25 19:47 | 34.2667 | 34.2667 | 10245.7333 | 0.1255% | 0.1299% |  | 0 | 330 | 299 | Furnace Wall Leaks | Boiler Tube Leak - Waterwall
0
3 |  |  |  | (1000-1030) |  | Waterwall BTF | 84.35 | 84.35 | 25390.25 | 0.311% | 0.3218% | 0%
0
1 | GH3 | U1 | 7 | 1040 | 2014-01-25 03:33 | 2014-01-26 19:21 | 39.8 | 39.8 | 19183.6 | 0.235% | 0.2432% | 0.2521% | 0 | 527 | 482 | Superheater Tube Leaks | Unit was taken off line after developing a boiler tube leak in the Prim
2 | GR4 | MO | 8 | 1050 | 2014-01-09 10:36 | 2014-01-10 16:22 | 29.7667 | 29.7667 | 2917.1333 | 0.03573% | 0.03698% | 0.03834% | 0 | 105 | 98 | Second Superheater Leaks | GR4 taken O/S in an orderly manner for repair of a tube leak in the DR Sec SH Sect
3 | GR3 | U3 | 2 | 1050 | 2014-01-12 21:48 | 2014-01-14 18:35 | 44.7833 | 44.7833 | 3179.6167 | 0.03895% | 0.0403% | 0.04179% | 0 | 75 | 71 | Second Superheater Leaks | GR3 taken out of service due to Sec SH tube leak. Dispatch was notified at 2200
4 | GR4 | U1 | 27 | 1050 | 2014-02-07 04:42 | 2014-02-08 17:57 | 37.25 | 37.25 | 3650.5 | 0.04472% | 0.04627% | 0.04797% | 0 | 105 | 98 | Second Superheater Leaks | Ops discovered leak in B5 Sec SH Section at 0344, unit was removed from service in
5 | MC2 | MO | 57 | 1050 | 2014-02-15 00:32 | 2014-02-17 22:00 | 69.4667 | 69.4667 | 20770.5333 | 0.2544% | 0.2633% |  | 0 | 330 | 299 | Second Superheater Leaks | Boiler Tube Leak - Second Superheater
0
5 |  |  |  | (1035-1050) |  | Superheater BTF | 221.0667 | 221.0667 | 49701.3833 | 0.6088% | 0.63% | 0.3802%
0
1 | GH1 | MO | 6 | 1060 | 2014-02-01 15:04 | 2014-02-03 01:27 | 34.3833 | 34.3833 | 16538.3833 | 0.2026% | 0.2096% |  | 0 | 517 | 481 | First Reheater Leaks | Unit 1 had been running with a tube leak, located around IK #6, for s
2 | CR5 | U2 | 7 | 1060 | 2014-02-07 10:51 | 2014-02-09 | 37.15 | 37.15 | 6241.2 | 0.07645% | 0.07911% | 0.08202% | 0 | 181 | 168 | First Reheater Leaks | Reheat boiler tube leak - cracked. Total of 6 leaks - 1 dutchman & 4 padwelds.
3 | GH1 | MO | 12 | 1060 | 2014-02-22 14:49 | 2014-02-23 11:03 | 20.2333 | 20.2333 | 9732.2333 | 0.1192% | 0.1234% |  | 0 | 517 | 481 | First Reheater Leaks | A leak was detected in Reheater pendant section of the boiler. Dispa
4 | CR6 | U2 | 1 | 1070 | 2014-01-03 11:03 | 2014-01-04 17:05 | 30.0333 | 30.0333 | 7208 | 0.0883% | 0.09137% | 0.09473% | 0 | 261 | 240 | Reheater Tube Leaks | Boiler Tube Leak - A tube leak was discovered in the RH Pendants.
5 | CR6 | MO | 3 | 1070 | 2014-01-09 20:23 | 2014-01-17 04:37 | 176.2333 | 176.2333 | 42296 | 0.5181% | 0.5361% |  | 0 | 261 | 240 | Reheater Tube Leaks | Boiler Leak Repair - A tube within the RH Pendants was discovered to be cracked,
0
5 |  |  |  | (1060-1070) |  | Reheater BTF | 298.0333 | 298.0333 | 82015.8167 | 1.005% | 1.04% | 0.1767%
0
0
0 |  |  |  | (1080-1099) |  | Economizer BTF | 0 | 0 | 0 | 0% | 0% | 0%
13 | All Steam |  |  |  |  | All BTF | 603.45 | 603.45 | 157107.45 | 1.925% | 1.991% | 0.5569%
46000%
| D1 | 50 | 346 | 2011-09-09 14:18 | 2011-09-09 17:09 | 2.85 | 0.40714 | 189.7286 |  |  |  | 420 | 490 | 466 | PULVERIZER PYRITE REMOVAL SYSTEM | Load Reduction #412-1 Mill pyrite section plugged.
| D1 | 51 | 350 | 2011-09-09 17:16 | 2011-09-10 16:30 | 23.2333 | 1.8966 | 883.815 |  |  |  | 450 | 490 | 466 | PULVERIZED FUEL AND AIR PIPING (PULVERIZER TO WIND BOX) | Load Reduction #422-1 Mill C burner line fire.
| D1 | 52 | 250 | 2011-09-10 00:38 | 2011-09-10 04:33 | 3.9167 | 0.51956 | 242.1139 |  |  |  | 425 | 490 | 466 | PULVERIZER FEEDERS | Load Reduction #432-3 Feeder had a bad carrier roll.
| D1 | 53 | 410 | 2011-09-12 13:05 | 2011-09-12 13:26 | 0.35 | 0.075 | 34.95 |  |  |  | 385 | 490 | 466 | OTHER DUCT BURNER PROBLEMS | Load Reduction #442-2 Mill 'C' burner temperature got hot. Took mill off to inspe
| D1 | 54 | 3410 | 2011-09-15 07:38 | 2011-09-15 08:34 | 0.93333 | 0.34286 | 159.7714 |  |  |  | 310 | 490 | 466 | FEEDWATER PUMP | Load Reduction #452-2 BFP inboard oil seal lost its seal and was leaking oil.
| MO | 55 | 1488 | 2011-09-23 22:03 | 2011-09-26 20:01 | 69.9667 | 69.9667 | 32604.4667 |  |  |  | 0 | 490 | 466 | AIR HEATER (REGENERATIVE) | Outage #10The unit was running with known seal damage on the air heaters. Removed
| PD | 56 | 8100 | 2011-09-26 05:16 | 2011-09-26 22:19 | 17.05 | 6.4372 | 2999.7561 |  |  |  | 305 | 490 | 466 | WET SCRUBBER/ABSORBER TOWER OR MODULE | Load Reduction #462-1 and 2-2 Absorber towers were out of service for maintenance
| D1 | 57 | 338 | 2011-09-29 14:27 | 2011-09-29 20:27 | 6 | 0.12245 | 57.0612 |  |  |  | 480 | 490 | 466 | PULVERIZER CONTROL SYSTEMS (TEMPERATURE AND PRESSURE) | Load Reduction #472-6 Mill bow differential transmitter failed due to water in the

## FEB-14 Summary By Cause Code
NERC GADS UNPLANNED EVENT IMPACT
BY CAUSE CODE GROUP
FEBRUARY-YTD 2014
|  |  | MWH (system) | EAF (system) | EUOR (system) | EFOR (system)
| Range | Cause Code Group | Lost | Lost | Impact | Impact
| 0010-0130 | Fuel Handling | 0 | 0% | 0% | 0%
| 0200-0480 | Fuel Firing | 76562.6189 | 0.9379% | 0.9012% | 0.7719%
| 0500-1999 | Boiler (all) | 305641.2657 | 3.666% | 3.793% | 1.18%
| 3110-3999 | Balance Of Plant | 42964.2754 | 0.5263% | 0.5253% | 0.4717%
| 4000-4499 | Steam Turbine | 53822.0278 | 0.6593% | 0.6822% | 0.1749%
| 4500-4899 | Generator | 1397.8 | 0.01712% | 0.01772% | 0.01837%
| 8000-8835 | Pollution Control Equipment | 30269.2568 | 0.3708% | 0.3837% | 0.1795%
| 9000-9340 | External | 254.4527 | 0.003117% | 0.003225% | 0.003344%
| 9504-9720 | Reg., Safety, & Environmental | 10490.1473 | 0.1285% | 0.07585% | 0.07864%
| 9900-9999 | Personnel Or Procedural Errors | 4174.7 | 0.05114% | 0.05292% | 0.05486%
|  |  | 525576.5447 | 6.36% | 6.435% | 2.933%
Note: This data may not
match KPI values as this data
includes overlapping events.
Boiler Tube Failures ( # 13 outages)
| 1000-1020 | Waterwall (# 3 outage) | 25390.25 | 0.311% | 0.3218% | 0%
| 1030-1050 | Superheater (# 5 outages) | 49701.3833 | 0.6088% | 0.63% | 0.3802%
| 1060-1070 | Reheater (# 5 outages) | 82015.8167 | 1.005% | 1.04% | 0.1767%
| 1080-1099 | Economizer (# 0 outage) | 0 | 0% | 0% | 0%
|  |  | 157107.45 | 1.925% | 1.991% | 0.5569%
|  |  | 29.89% | 30.26% | 30.95% | 18.99%
|  |  | of Total | of Total | of Total | of Total
|  |  | MWH(lost) | EAF(lost) | EUOR(lost) | EFOR(lost)
|  |  | MWH (system) | EAF (system) | EUOR (system) | EFOR (system)
| Range | Cause Code Group | Lost | Lost | Impact | Impact
1 | 0500-1999 | Boiler (non-BTF) | 148533.8157 | 1.742% | 1.801% | 0.6232%
2 | 1060-1070 | Reheater (# 2 outages) | 82015.8167 | 1.005% | 1.04% | 0.1767%
3 | 0200-0480 | Fuel Firing | 76562.6189 | 0.9379% | 0.9012% | 0.7719%
4 | 4000-4499 | Steam Turbine | 53822.0278 | 0.6593% | 0.6822% | 0.1749%
5 | 1030-1050 | Superheater (# 3 outages) | 49701.3833 | 0.6088% | 0.63% | 0.3802%
|  |  | 410635.6624 | 4.952% | 5.054% | 2.127%
|  |  | 78.13% | 77.86% | 78.55% | 72.51%
|  |  | of Total | of Total | of Total | of Total
|  |  | MWH(lost) | EAF(lost) | EUOR(lost) | EFOR(lost)