## Interim Report
REGULATED (LG&E and KU) POWER GENERATION
CAPACITY WEIGHTED INTERIM EAF and EFOR REPORT
[7 empty] | FEBRUARY | 1 st | THROUGH |  | 16 |  |  | th
|  | 2014 |  |  |  |  | 2/17/2014
|  | Winter | [16 empty] | 16
Station | Unit | NDC | FOH | EFDH | EMOH | EPOH |  | AH | RH | SH |  | Efor Num. | Efor Den. | EFOR | UU Num. | UU Den. | EUOR | Eaf Num. | Eaf Den. | EAF | UU
Brown | 1 | 107 | 0 | 0 | 0 | 0 |  | 384 | 0 | 384 |  | 0 | 41088 | 0% | 0 | 41088 | 0% | 41088 | 41088 | 100% | 0%
Brown | 2 | 168 | 0 | 3.407 | 0 | 0 |  | 384 | 0 | 384 |  | 572.376 | 64512 | 0.8872% | 572.376 | 64512 | 0.8872% | 63939.624 | 64512 | 99.11% | 0.8872%
Brown | 3 | 414 | 16.083 | 0 | 0 | 1.244 |  | 367.917 | 0 | 367.917 |  | 6658.362 | 158976 | 4.188% | 6658.362 | 158976 | 4.188% | 152317.638 | 158976 | 95.81% | 4.188%
Brown | 5 | 130 | 0 | 0 | 0 | 0 |  | 384 | 325.65 | 58.35 |  | 0 | 7585.5 | 0% | 0 | 7585.5 | 0% | 49920 | 49920 | 100% | 0%
Brown | 6 | 171 | 0 | 0 | 1.5 | 0 |  | 382.5 | 184.267 | 198.233 |  | 0 | 33897.843 | 0% | 256.5 | 34154.343 | 0.751% | 65407.5 | 65664 | 99.61% | 0.3906%
Brown | 7 | 171 | 2.333 | 0 | 0 | 0 |  | 381.667 | 203.483 | 178.184 |  | 398.943 | 30868.407 | 1.292% | 398.943 | 30868.407 | 1.292% | 65265.057 | 65664 | 99.39% | 0.6076%
Brown | 8 | 128 | 0 | 0 | 0 | 0 |  | 384 | 368.867 | 15.133 |  | 0 | 1937.024 | 0% | 0 | 1937.024 | 0% | 49152 | 49152 | 100% | 0%
Brown | 9 | 138 | 0 | 0 | 0 | 0 |  | 384 | 370.317 | 13.683 |  | 0 | 1888.254 | 0% | 0 | 1888.254 | 0% | 52992 | 52992 | 100% | 0%
Brown | 10 | 138 | 0 | 0 | 0 | 0 |  | 384 | 370.25 | 13.75 |  | 0 | 1897.5 | 0% | 0 | 1897.5 | 0% | 52992 | 52992 | 100% | 0%
Brown | 11 | 128 | 0 | 0 | 0 | 0 |  | 384 | 378.667 | 5.333 |  | 0 | 682.624 | 0% | 0 | 682.624 | 0% | 49152 | 49152 | 100% | 0%
Brown | (steam) | 689 | 16.083 | 3.407 | 0 | 1.244 |  | 1135.917 | 0 | 1135.917 |  | 7230.738 | 264576 | 2.733% | 7230.738 | 264576 | 2.733% | 257345.262 | 264576 | 97.27% | 2.733%
Brown | (fossil) | 1693 | 18.416 | 3.407 | 1.5 | 1.244 |  | 3820.084 | 2201.501 | 1618.583 |  | 7629.681 | 343333.152 | 2.222% | 7886.181 | 343589.652 | 2.295% | 642225.819 | 650112 | 98.79% | 1.213%
Cane Run | 4 | 155 | 0 | 6.129 | 12.5 | 0 |  | 371.5 | 0 | 371.5 |  | 949.995 | 57582.5 | 1.65% | 2887.495 | 59520 | 4.851% | 56632.505 | 59520 | 95.15% | 4.851%
Cane Run | 5 | 168 | 61.35 | 0 | 5.328 | 0 |  | 322.65 | 0 | 322.65 |  | 10306.8 | 64512 | 15.98% | 11201.904 | 65407.104 | 17.13% | 54205.2 | 64512 | 84.02% | 17.36%
Cane Run | 6 | 240 | 0 | 5.499 | 0 | 0 |  | 384 | 0 | 384 |  | 1319.76 | 92160 | 1.432% | 1319.76 | 92160 | 1.432% | 90840.24 | 92160 | 98.57% | 1.432%
Cane Run | 11 | 14 | 8.917 | 0 | 0 | 0 |  | 375.083 | 375.083 | 1e-11 |  | 124.838 | 124.838 | 100% | 124.838 | 124.838 | 100% | 5251.162 | 5376 | 97.68% | 2.322%
Cane Run | (steam) | 563 | 61.35 | 11.628 | 17.828 | 0 |  | 1078.15 | 0 | 1078.15 |  | 12576.555 | 214254.5 | 5.87% | 15409.159 | 217087.104 | 7.098% | 201677.945 | 216192 | 93.29% | 7.128%
Cane Run | (fossil) | 577 | 70.267 | 11.628 | 17.828 | 0 |  | 1453.233 | 375.083 | 1078.15 |  | 12701.393 | 214379.338 | 5.925% | 15533.997 | 217211.942 | 7.152% | 206929.107 | 221568 | 93.39% | 7.011%
Ghent | 1 | 481 | 0 | 3.165 | 34.383 | 0.849 |  | 349.617 | 0 | 349.617 |  | 1522.365 | 168165.777 | 0.9053% | 18060.588 | 184704 | 9.778% | 166643.412 | 184704 | 90.22% | 9.778%
Ghent | 2 | 477 | 0 | 0.832 | 0 | 0.679 |  | 384 | 0 | 384 |  | 396.864 | 183168 | 0.2167% | 396.864 | 183168 | 0.2167% | 182771.136 | 183168 | 99.78% | 0.2167%
Ghent | 3 | 482 | 0 | 6.005 | 43.217 | 9.349 |  | 374.567 | 0 | 374.567 |  | 2894.41 | 180541.294 | 1.603% | 23725.004 | 201371.888 | 11.78% | 177646.884 | 185088 | 95.98% | 12.82%
Ghent | 4 | 491 | 1.783 | 0.243 | 0 | 0.584 |  | 382.217 | 0 | 382.217 |  | 994.766 | 188544 | 0.5276% | 994.766 | 188544 | 0.5276% | 187549.234 | 188544 | 99.47% | 0.5276%
Ghent | (steam) | 1931 | 1.783 | 10.245 | 77.6 | 11.461 |  | 1490.401 | 0 | 1490.401 |  | 5808.405 | 720419.071 | 0.8063% | 43177.222 | 757787.888 | 5.698% | 714610.666 | 741504 | 96.37% | 5.823%
Ghent | (fossil) | 1931 | 1.783 | 10.245 | 77.6 | 11.461 |  | 1490.401 | 0 | 1490.401 |  | 5808.405 | 720419.071 | 0.8063% | 43177.222 | 757787.888 | 5.698% | 714610.666 | 741504 | 96.37% | 5.823%
Green River | 3 | 71 | 0 | 1.562 | 0 | 0 |  | 384 | 0 | 384 |  | 110.902 | 27264 | 0.4068% | 110.902 | 27264 | 0.4068% | 27153.098 | 27264 | 99.59% | 0.4068%
Green River | 4 | 98 | 37.25 | 5.478 | 0 | 0 |  | 346.75 | 0 | 346.75 |  | 4187.344 | 37632 | 11.13% | 4187.344 | 37632 | 11.13% | 33444.656 | 37632 | 88.87% | 11.13%
Green River | (steam) | 169 | 37.25 | 7.04 | 0 | 0 |  | 730.75 | 0 | 730.75 |  | 4298.246 | 64896 | 6.623% | 4298.246 | 64896 | 6.623% | 60597.754 | 64896 | 93.38% | 6.623%
Green River | (fossil) | 169 | 37.25 | 7.04 | 0 | 0 |  | 730.75 | 0 | 730.75 |  | 4298.246 | 64896 | 6.623% | 4298.246 | 64896 | 6.623% | 60597.754 | 64896 | 93.38% | 6.623%
Haefling | 1 | 14 | 16.2 | 0 | 0 | 0 |  | 367.8 | 367.8 | 1e-11 |  | 226.8 | 226.8 | 100% | 226.8 | 226.8 | 100% | 5149.2 | 5376 | 95.78% | 4.219%
Haefling | 2 | 14 | 16.2 | 0 | 0 | 0 |  | 367.8 | 367.8 | 1e-11 |  | 226.8 | 226.8 | 100% | 226.8 | 226.8 | 100% | 5149.2 | 5376 | 95.78% | 4.219%
Haefling | (steam) | 0 | - | - | - | - |  | - | - | - |  |  |  | - |  |  | - |  |  | - | -
Haefling | (fossil) | 28 | 32.4 | 0 | 0 | 0 |  | 735.6 | 735.6 | 2e-11 |  | 453.6 | 453.6 | 100% | 453.6 | 453.6 | 100% | 10298.4 | 10752 | 95.78% | 4.219%
Mill Creek | 1 | 303 | 0 | 13.973 | 2.236 | 0 |  | 384 | 0 | 384 |  | 4233.819 | 116352 | 3.639% | 4911.327 | 117029.508 | 4.197% | 112118.181 | 116352 | 96.36% | 4.221%
Mill Creek | 2 | 299 | 6.967 | 7.113 | 52.762 | 0 |  | 329.567 | 0 | 329.567 |  | 4209.92 | 100623.666 | 4.184% | 19985.758 | 116399.504 | 17.17% | 96413.746 | 114816 | 83.97% | 17.41%
Mill Creek | 3 | 394 | 0 | 7.095 | 1.108 | 0 |  | 384 | 0 | 384 |  | 2795.43 | 151296 | 1.848% | 3231.982 | 151732.552 | 2.13% | 148500.57 | 151296 | 98.15% | 2.136%
Mill Creek | 4 | 486 | 0 | 4.846 | 0.953 | 0 |  | 384 | 0 | 384 |  | 2355.156 | 186624 | 1.262% | 2818.314 | 187087.158 | 1.506% | 184268.844 | 186624 | 98.74% | 1.51%
Mill Creek | (steam) | 1482 | 6.967 | 33.027 | 57.059 | 0 |  | 1481.567 | 0 | 1481.567 |  | 13594.325 | 554895.666 | 2.45% | 30947.381 | 572248.722 | 5.408% | 541301.341 | 569088 | 95.12% | 5.438%
Mill Creek | (fossil) | 1482 | 6.967 | 33.027 | 57.059 | 0 |  | 1481.567 | 0 | 1481.567 |  | 13594.325 | 554895.666 | 2.45% | 30947.381 | 572248.722 | 5.408% | 541301.341 | 569088 | 95.12% | 5.438%
Paddys Run | 11 | 13 | 0 | 0 | 0 | 0 |  | 384 | 384 | 1e-11 |  | 0 | 1.3e-10 | 0% | 0 | 1.3e-10 | 0% | 4992 | 4992 | 100% | 0%
Paddys Run | 12 | 28 | 0 | 0 | 0 | 0 |  | 384 | 384 | 1e-11 |  | 0 | 2.8e-10 | 0% | 0 | 2.8e-10 | 0% | 10752 | 10752 | 100% | 0%
Paddys Run | 13 | 175 | 0 | 0 | 0 | 41.867 |  | 342.133 | 342.133 | 1e-11 |  | 0 | 1.75e-09 | 0% | 0 | 1.75e-09 | 0% | 59873.275 | 67200 | 89.1% | 0%
Paddys Run | (steam) | 0 | - | - | - | - |  | - | - | - |  |  |  | - |  |  | - |  |  | - | -
Paddys Run | (fossil) | 216 | 0 | 0 | 0 | 41.867 |  | 1110.133 | 1110.133 | 3e-11 |  | 0 | 2.16e-09 | 0% | 0 | 2.16e-09 | 0% | 75617.275 | 82944 | 91.17% | 0%
Trimble Co. | 1 (@ 75%) | 383 | 0 | 0.475 | 0 | 0 |  | 384 | 0 | 384 |  | 181.925 | 147072 | 0.1237% | 181.925 | 147072 | 0.1237% | 146890.075 | 147072 | 99.88% | 0.1237%
Trimble Co. | 2 (@75%) | 570 | 0 | 0.418 | 0 | 212.65 |  | 171.35 | 0 | 171.35 |  | 238.26 | 97669.5 | 0.2439% | 238.26 | 97669.5 | 0.2439% | 97431.24 | 218880 | 44.51% | 0.1089%
Trimble Co. | 5 | 176 | 2.317 | 0 | 0 | 0 |  | 381.683 | 272.067 | 109.616 |  | 407.792 | 19700.208 | 2.07% | 407.792 | 19700.208 | 2.07% | 67176.208 | 67584 | 99.4% | 0.6034%
Trimble Co. | 6 | 176 | 1.967 | 0 | 4.317 | 0 |  | 377.717 | 260.417 | 117.3 |  | 346.192 | 20990.992 | 1.649% | 1105.984 | 21750.784 | 5.085% | 66478.192 | 67584 | 98.36% | 1.636%
Trimble Co. | 7 | 176 | 0.217 | 0 | 0 | 0 |  | 383.783 | 246.217 | 137.566 |  | 38.192 | 24249.808 | 0.1575% | 38.192 | 24249.808 | 0.1575% | 67545.808 | 67584 | 99.94% | 0.05651%
Trimble Co. | 8 | 176 | 0 | 0 | 0 | 0 |  | 384 | 339.117 | 44.883 |  | 0 | 7899.408 | 0% | 0 | 7899.408 | 0% | 67584 | 67584 | 100% | 0%
Trimble Co. | 9 | 176 | 2.95 | 1.463 | 0 | 0 |  | 381.05 | 238.683 | 142.367 |  | 776.688 | 25575.792 | 3.037% | 776.688 | 25575.792 | 3.037% | 66807.312 | 67584 | 98.85% | 1.149%
Trimble Co. | 10 | 176 | 0 | 0 | 0 | 0 |  | 384 | 315.567 | 68.433 |  | 0 | 12044.208 | 0% | 0 | 12044.208 | 0% | 67584 | 67584 | 100% | 0%
Trimble Co. | (steam) | 953 | 0 | 0.893 | 0 | 212.65 |  | 555.35 | 0 | 555.35 |  | 420.185 | 244741.5 | 0.1717% | 420.185 | 244741.5 | 0.1717% | 244321.315 | 365952 | 66.76% | 0.1148%
Trimble Co. | (fossil) | 2009 | 7.451 | 2.356 | 4.317 | 212.65 |  | 2847.583 | 1672.068 | 1175.515 |  | 1989.049 | 355201.916 | 0.56% | 2748.841 | 355961.708 | 0.7722% | 647496.835 | 771456 | 83.93% | 0.3563%
Tyrone | 3 | 0 | [9 empty] | 0 | 0 |  | 0 | 0 |  | 0 | 0
Tyrone | (steam) | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
Tyrone | (fossil) | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0
Zorn | 1 | 16 | 0 | 0 | 0 | 0 |  | 384 | 384 | 1e-11 |  | 0 | 1.6e-10 | 0% | 0 | 1.6e-10 | 0% | 6144 | 6144 | 100% | 0%
Zorn | (steam) | 0 | 0 | 0 | 0 | 0 |  | 384 | 384 | - |  |  |  | - |  |  | - |  |  | - | -
Zorn | (fossil) | 16 | 0 | 0 | 0 | 0 |  | 384 | 384 | 1e-11 |  | 0 | 1.6e-10 | 0% | 0 | 1.6e-10 | 0% | 6144 | 6144 | 100% | 0%
KU | (steam) | 2789 | 55.116 | 20.692 | 77.6 | 12.705 |  | 3357.068 | 0 | 3357.068 |  | 17337.389 | 1049891.071 | 1.651% | 54706.206 | 1087259.888 | 5.032% | 1032553.682 | 1070976 | 96.41% | 5.108%
KU | (fossil) | 3821 | 89.849 | 20.692 | 79.1 | 12.705 |  | 6776.835 | 2937.101 | 3839.734 |  | 18189.932 | 1129101.823 | 1.611% | 55815.249 | 1166727.14 | 4.784% | 1427732.639 | 1467264 | 97.31% | 3.804%
[8 empty] | FEBRUARY Steam Targets | [5 empty] | 5.24% |  |  | 7.42% |  |  | 89.07% | 6.38%
LG&E | (steam) | 2998 | 68.317 | 45.548 | 74.887 | 212.65 |  | 3499.067 | 384 | 3115.067 |  | 26591.065 | 1013891.666 | 2.623% | 46776.725 | 1034077.326 | 4.524% | 987300.601 | 1151232 | 85.76% | 4.063%
LG&E | (fossil) | 4300 | 84.685 | 47.011 | 79.204 | 254.517 |  | 7276.516 | 3541.284 | 3735.232 |  | 28284.767 | 1124476.92 | 2.515% | 49230.219 | 1145422.372 | 4.298% | 1477488.558 | 1651200 | 89.48% | 2.981%
[8 empty] | FEBRUARY Steam Targets | [5 empty] | 5.04% |  |  | 7.19% |  |  | 76.28% | 5.97%
Reg'd. Gen. | (steam) | 5787 | 123.433 | 66.24 | 152.487 | 225.355 |  | 6856.135 | 384 | 6472.135 |  | 43928.454 | 2063782.737 | 2.129% | 101482.931 | 2121337.214 | 4.784% | 2019854.283 | 2222208 | 90.89% | 4.567%
Reg'd. Gen. | (fossil) | 8121 | 174.534 | 67.703 | 158.304 | 267.222 |  | 14053.351 | 6478.385 | 7574.966 |  | 46474.699 | 2253578.743 | 2.062% | 105045.468 | 2312149.512 | 4.543% | 2905221.197 | 3118464 | 93.16% | 3.369%
[14 empty] | versus |  |  | versus |  |  | versus | versus
[8 empty] | FEBRUARY Steam Targets | [5 empty] | 5.14% |  |  | 7.3% |  |  | 82.45% | 6.17%
[8 empty] | 2014 Steam Targets | [5 empty] | 5.14% |  |  | 7.3% |  |  | 83.11% | 6.17%

## EAF & EFOR Contributors
REGULATED (LG&E and KU) POWER GENERATION
CAPACITY WEIGHTED INTERIM EAF and EFOR REPORT
[5 empty] | FEBRUARY | 1 st | THRU |  | 16 | st
Impact |  |  | Evt. |  |  | Equiv. |  | EFOR | EAF | MWH
Order | Unit | NDC | No. | Start Date | End Date | Hrs. |  | (Impact) | (Lost) | (Lost) | Type | Event Descrption
1 | GH1 | 481 | 6 | 2014-02-01 15:04 | 2014-02-03 01:27 | 34.3833 |  |  | 0.8001% | 16538.3833 | MO | First Reheater Leaks
2 | MC2 | 299 | 57 | 2014-02-15 00:32 | 2014-02-17 | 47.4667 |  |  | 0.6866% | 14192.5333 | MO | Second Superheater Leaks
3 | BR3 | 414 | 8 | 2014-02-01 | 2014-02-01 16:05 | 16.0833 |  | 0.3226% | 0.3221% | 6658.5 | U1 | Pulverizer Puff Boiler Damage
4 | CR5 | 168 | 7 | 2014-02-07 10:51 | 2014-02-09 | 37.15 |  | 0.3024% | 0.3019% | 6241.2 | U2 | First Reheater Leaks
5 | GH3 | 482 | 11 | 2014-02-01 | 2014-02-01 09:26 | 9.4333 |  |  | 0.22% | 4546.8667 | MO | Induced Draft Fan Bearings
6 | GH3 | 482 | 17 | 2014-02-15 22:00 | 2014-02-16 13:04 | 9.3488 |  |  | 0.218% | 4506.1055 | PD | Plant Modifications For Baghouse
7 | CR5 | 168 | 8 | 2014-02-09 | 2014-02-10 00:12 | 24.2 |  | 0.197% | 0.1967% | 4065.6 | SF | Electrostatic Precipitator Problems
8 | GR4 | 98 | 27 | 2014-02-07 04:42 | 2014-02-08 17:57 | 37.25 |  | 0.1769% | 0.1766% | 3650.5 | U1 | Second Superheater Leaks
9 | MC1 | 303 | 18 | 2014-02-01 21:20 | 2014-02-02 08:50 | 7.3182 |  | 0.1074% | 0.1073% | 2217.4091 | D1 | Turbine Control Valve Stuck
10 | MC2 | 299 | 35 | 2014-02-01 23:37 | 2014-02-02 06:35 | 6.9667 |  | 0.1009% | 0.1008% | 2083.0333 | U1 | Condenser Loss of Vacuum
[6 empty] | 229.6003 |  | 1.207% | 3.13% | 64700.1313
[8 empty] | 56.72% | 34.37%
[8 empty] | of the | of the
[6 empty] | total EFOR(steam) impact |  | 2.129% | 9.106% | total lost EAF(steam)

## Event List By Unit
Unit | Event | Event | Cause | Event | Event | Evt. | Equiv. | MWH |  |  |  | Event | Event
Name | Type | No | Code | Start | End | Hrs | Dur Hrs | Lost | GAC | GMC | NMC | Cause | Description
[10 empty] | 114 | 107
BR1 | [5 empty] | 0 | 0 | 0
D4
PD
BR2 | D1 | 4 | 310 | 2014-02-11 20:04 | 2014-02-12 02:17 | 6.2167 | 1.7269 | 290.1111 | 130 | 180 | 168 | Pulverizer Mills | 2-4 mill west door broken spring bolt
BR2 | D1 | 5 | 310 | 2014-02-16 17:57 | 2014-02-17 | 6.05 | 1.6806 | 282.3333 | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill
[10 empty] | 180 | 168
BR2 | [5 empty] | 12.2667 | 3.4074 | 572.4444
D4
PD
BR3 | U1 | 8 | 339 | 2014-01-30 03:57 | 2014-02-01 16:05 | 60.1333 | 60.1333 | 24895.2 | 0 | 457 | 414 | Pulverizer System Puff | 3-5 Mill puff causing D corner burner damage and associated boiler tube leak.
BR3 | PD | 9 | 3412 | 2014-02-04 22:00 | 2014-02-05 01:52 | 3.8667 | 1.2438 | 514.9182 | 310 | 457 | 414 | Feedwater Pump Drive - Steam Turbine | Collecting 3-2 BFP vibration data
[10 empty] | 457 | 414
BR3 | [5 empty] | 64 | 61.3771 | 25410.1182
D4
| PD |  |  |  |  | 3.8667 | 1.2438 | 514.9182
CR4 | D1 | 8 | 8560 | 2014-02-09 | 2014-02-09 11:42 | 11.7 | 6.1286 | 949.9286 | 80 | 168 | 155 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
CR4 | MO | 9 | 8100 | 2014-02-16 11:30 | 2014-02-17 | 12.5 | 12.5 | 1937.5 | 0 | 168 | 155 | Wet Scrubber/absorber Tower Or Module | Flue gas desulfurization module cleaning.
[10 empty] | 168 | 155
CR4 | [5 empty] | 24.2 | 18.6286 | 2887.4286
D4
PD
CR5 | D4 | 4 | 344 | 2014-02-02 23:00 | 2014-02-03 04:50 | 5.8333 | 1.8048 | 303.2044 | 125 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
CR5 | D4 | 5 | 344 | 2014-02-03 23:00 | 2014-02-04 04:55 | 5.9167 | 1.6671 | 280.0773 | 130 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
CR5 | D4 | 6 | 344 | 2014-02-04 23:00 | 2014-02-05 05:00 | 6 | 1.8564 | 311.8674 | 125 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
CR5 | U2 | 7 | 1060 | 2014-02-07 10:51 | 2014-02-09 | 37.15 | 37.15 | 6241.2 | 0 | 181 | 168 | First Reheater Leaks | Reheat boiler tube leak - cracked. Total of 6 leaks - 1 dutchman & 4 padwelds.
CR5 | SF | 8 | 8560 | 2014-02-09 | 2014-02-10 00:12 | 24.2 | 24.2 | 4065.6 | 0 | 181 | 168 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
CR5 | NC | 9 | 9999 | 2014-02-13 10:00 | 2014-02-13 14:00 | 4 |  |  | 0 | 181 | 168 | Total Unit Performance Testing | Full load winter capability test.
[10 empty] | 181 | 168
CR5 | [5 empty] | 83.1 | 66.6783 | 11201.9492
| D4 |  |  |  |  | 17.75 | 5.3283 | 895.1492
PD
CR6 | D1 | 7 | 250 | 2014-02-07 01:12 | 2014-02-07 02:10 | 0.96667 | 0.22593 | 54.2222 | 200 | 261 | 240 | Pulverizer Feeders | D1 feeder plugged due to torn belt.
CR6 | D1 | 8 | 250 | 2014-02-08 00:05 | 2014-02-08 01:13 | 1.1333 | 0.22146 | 53.1494 | 210 | 261 | 240 | Pulverizer Feeders | D2 feeder plugged due to wet coal.
CR6 | D1 | 9 | 8560 | 2014-02-09 | 2014-02-09 06:50 | 6.8333 | 2.5134 | 603.2184 | 165 | 261 | 240 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
CR6 | D1 | 10 | 340 | 2014-02-09 06:50 | 2014-02-09 07:15 | 0.41667 | 0.15326 | 36.7816 | 165 | 261 | 240 | Other Pulverizer Problems | Support fuel unavailable due to loss of communication between precipitator & DCS.
CR6 | D1 | 11 | 4240 | 2014-02-11 08:00 | 2014-02-11 14:00 | 6 | 0.94253 | 226.2069 | 220 | 261 | 240 | Lp Turbine Bearings | #4 Turbine bearing temperature running high.
CR6 | D1 | 12 | 250 | 2014-02-16 04:54 | 2014-02-16 12:17 | 7.3833 | 1.4427 | 346.2529 | 210 | 261 | 240 | Pulverizer Feeders | 6B feeder belt torn. Repaired & put back in service.
[10 empty] | 261 | 240
CR6 | [5 empty] | 22.7333 | 5.4993 | 1319.8314
D4
PD
GH1 | MO | 6 | 1060 | 2014-02-01 15:04 | 2014-02-03 01:27 | 34.3833 | 34.3833 | 16538.3833 | 0 | 517 | 481 | First Reheater Leaks | Unit 1 had been running with a tube leak, located around IK #6, for s
GH1 | D1 | 7 | 250 | 2014-02-07 12:35 | 2014-02-07 13:45 | 1.1667 | 0.12863 | 61.8694 | 460 | 517 | 481 | Pulverizer Feeders | Metal hung in 1-4 mill feeder.
GH1 | D1 | 8 | 250 | 2014-02-09 16:20 | 2014-02-09 19:43 | 3.3833 | 2.9449 | 1416.4845 | 67 | 517 | 481 | Pulverizer Feeders | 1-4 Feeder belt bound up.
GH1 | PD | 9 | 250 | 2014-02-10 09:00 | 2014-02-10 15:33 | 6.55 | 0.84884 | 408.2918 | 450 | 517 | 481 | Pulverizer Feeders | 1-4 Mill off to replace feeder discharge pipe pluggage detector.
GH1 | D1 | 10 | 9650 | 2014-02-13 07:23 | 2014-02-13 09:08 | 1.75 | 0.091393 | 43.9599 | 490 | 517 | 481 | Other Stack Or Exhaust Emissions -fossil Stm Unit | U1 H2SO4 was high. Dropped load to keep it in compliance.
[10 empty] | 517 | 481
GH1 | [5 empty] | 47.2333 | 38.3971 | 18468.9889
D4
| PD |  |  |  |  | 6.55 | 0.84884 | 408.2918
GH2 | D1 | 6 | 312 | 2014-02-01 14:40 | 2014-02-01 18:00 | 3.3333 | 0.18991 | 90.5894 | 480 | 509 | 477 | Pulverizer Mill Classifiers | 2-1 Mill not grinding, took off for inspection.
GH2 | PD | 7 | 344 | 2014-02-06 23:00 | 2014-02-07 01:24 | 2.4 | 0.23104 | 110.2067 | 460 | 509 | 477 | Pulverizer Inspection | 2-2 Mill was removed from service to inspect due to high differen
GH2 | PD | 8 | 340 | 2014-02-13 23:00 | 2014-02-14 02:11 | 3.1833 | 0.30645 | 146.1769 | 460 | 509 | 477 | Other Pulverizer Problems | 2-5 Mill off to replace pyrite scraper.
GH2 | PD | 9 | 340 | 2014-02-14 02:11 | 2014-02-14 03:39 | 1.4667 | 0.14119 | 67.3485 | 460 | 509 | 477 | Other Pulverizer Problems | 2-6 Mill off to inspect grinding section and classifiers.
GH2 | D1 | 10 | 250 | 2014-02-15 03:20 | 2014-02-15 10:00 | 6.6667 | 0.64178 | 306.1297 | 460 | 509 | 477 | Pulverizer Feeders | 2-1 Feeder control issue.
[10 empty] | 509 | 477
GH2 | [5 empty] | 17.05 | 1.5104 | 720.4512
D4
| PD |  |  |  |  | 7.05 | 0.67868 | 323.7321
GH3 | MO | 11 | 1455 | 2014-01-30 14:13 | 2014-02-01 09:26 | 43.2167 | 43.2167 | 20830.4333 | 0 | 527 | 482 | Induced Draft Fans | Unit 3 has been running with 3-2 ID Fan OB Fan bearing having periodi
GH3 | D1 | 12 | 9650 | 2014-02-02 20:10 | 2014-02-02 20:45 | 0.58333 | 0.14058 | 67.7574 | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | 3-2B SO3 injection blower pressure sensing line came off causing
GH3 | D1 | 13 | 9650 | 2014-02-05 14:10 | 2014-02-05 15:00 | 0.83333 | 0.27989 | 134.9051 | 350 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | D1 | 14 | 9650 | 2014-02-05 15:00 | 2014-02-05 19:50 | 4.8333 | 2.9257 | 1410.1777 | 208 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | D1 | 15 | 9650 | 2014-02-15 04:41 | 2014-02-15 07:07 | 2.4333 | 0.5864 | 282.6453 | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | D1 | 16 | 9650 | 2014-02-15 11:22 | 2014-02-15 14:52 | 3.5 | 2.0721 | 998.7552 | 215 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH3 | PD | 17 | 9510 | 2014-02-15 22:00 | 2014-02-16 13:04 | 15.0667 | 9.3488 | 4506.1055 | 200 | 527 | 482 | Plant Modific. Strictly For Compliance W/ Reg. Req | KBR electrical tie-in for Bag House and ID fan.
[10 empty] | 527 | 482
GH3 | [5 empty] | 70.4667 | 58.5701 | 28230.7796
D4
| PD |  |  |  |  | 15.0667 | 9.3488 | 4506.1055
GH4 | D1 | 5 | 9650 | 2014-02-03 00:50 | 2014-02-03 01:48 | 0.96667 | 0.24257 | 119.1027 | 400 | 534 | 491 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
GH4 | PD | 6 | 3416 | 2014-02-08 23:00 | 2014-02-09 00:20 | 1.3333 | 0.58427 | 286.8764 | 300 | 534 | 491 | Other Feedwater Pump Problems | Planned derate to inspect 4-2 BFP leak. Derate was planned with
GH4 | U1 | 7 | 250 | 2014-02-09 03:51 | 2014-02-09 05:38 | 1.7833 | 1.7833 | 875.6167 | 0 | 534 | 491 | Pulverizer Feeders | 4-6 Mill Feeder coal inlet plugged causing controls to see this feeder as
[10 empty] | 534 | 491
GH4 | [5 empty] | 4.0833 | 2.6102 | 1281.5958
D4
PD
GR3 | D1 | 4 | 9630 | 2014-02-11 08:17 | 2014-02-11 09:18 | 1.0167 | 0.094889 | 6.7371 | 68 | 75 | 71 | Opacity - Fossil Steam Units | Load reduced on GR3 due to high opacity.
GR3 | D1 | 5 | 9630 | 2014-02-11 09:18 | 2014-02-11 09:40 | 0.36667 | 0.024444 | 1.7356 | 70 | 75 | 71 | Opacity - Fossil Steam Units | GR3 derate reduction from event #4. Derate due to igh opacity.
GR3 | D1 | 6 | 9630 | 2014-02-11 09:40 | 2014-02-11 13:13 | 3.55 | 0.80467 | 57.1313 | 58 | 75 | 71 | Opacity - Fossil Steam Units | Continuation of previous event. GR3 derate increased to blow soot and clean boile
GR3 | D1 | 7 | 9630 | 2014-02-11 13:13 | 2014-02-11 17:20 | 4.1167 | 0.38422 | 27.2798 | 68 | 75 | 71 | Opacity - Fossil Steam Units | Continuation of previous event. GR3/B4 soot blowing completed, raised load as muc
GR3 | D1 | 8 | 9630 | 2014-02-12 07:40 | 2014-02-12 08:20 | 0.66667 | 0.08 | 5.68 | 66 | 75 | 71 | Opacity - Fossil Steam Units | GR3 load reduced due to high opacity.
GR3 | D1 | 9 | 9630 | 2014-02-12 08:20 | 2014-02-12 09:30 | 1.1667 | 0.093333 | 6.6267 | 69 | 75 | 71 | Opacity - Fossil Steam Units | GR3 derate decreased from Event #8 due to high opacity.
GR3 | D1 | 10 | 9630 | 2014-02-12 09:30 | 2014-02-12 11:00 | 1.5 | 0.08 | 5.68 | 71 | 75 | 71 | Opacity - Fossil Steam Units | GR3 Derate reduction from Event #9 due to high opacity.
[10 empty] | 75 | 71
GR3 | [5 empty] | 12.3833 | 1.5616 | 110.8704
D4
PD
GR4 | D1 | 24 | 8551 | 2014-01-24 12:00 | 2014-02-05 11:55 | 287.9167 | 5.4841 | 537.4444 | 103 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded o
GR4 | D1 | 25 | 263 | 2014-02-01 21:38 | 2014-02-01 22:48 | 1.1667 | 0.27778 | 27.2222 | 80 | 105 | 98 | Primary Air Fan Drives | 5-2 PA Fan Control Jack Minimum Stop failed to disengage. I&E found and repaired
GR4 | D1 | 26 | 338 | 2014-02-04 22:14 | 2014-02-05 11:55 | 13.6833 | 3.2579 | 319.2778 | 80 | 105 | 98 | Pulverizer Control Systems (Temp and Pressure) | 5-3 PA Fan control jack would not react to input from PA Controller.
GR4 | U1 | 27 | 1050 | 2014-02-07 04:42 | 2014-02-08 17:57 | 37.25 | 37.25 | 3650.5 | 0 | 105 | 98 | Second Superheater Leaks | Ops discovered leak in B5 Sec SH Section at 0344, unit was removed from service in
GR4 | D1 | 28 | 9630 | 2014-02-13 14:41 | 2014-02-13 16:28 | 1.7833 | 0.16984 | 16.6444 | 95 | 105 | 98 | Opacity - Fossil Steam Units | GR4 derated due to opacity, blowing soot to clean up the boiler.
[10 empty] | 105 | 98
GR4 | [5 empty] | 341.8 | 46.4397 | 4551.0889
D4
PD
MC1 | D1 | 18 | 4261 | 2014-02-01 21:20 | 2014-02-02 08:50 | 11.5 | 7.3182 | 2217.4091 | 120 | 330 | 303 | Turbine Control Valves | Turbine #2 Control Valve - Stuck Closed
MC1 | NC | 19 | 1160 | 2014-02-04 23:00 | 2014-02-05 04:15 | 5.25 |  |  | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater. Full load available if needed.
MC1 | D1 | 20 | 250 | 2014-02-05 07:28 | 2014-02-05 09:30 | 2.0333 | 0.40051 | 121.353 | 265 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Wet Coal
MC1 | D4 | 21 | 250 | 2014-02-06 | 2014-02-06 03:12 | 3.2 | 0.87273 | 264.4364 | 240 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Repair Discharge Flapper
MC1 | D1 | 22 | 1160 | 2014-02-08 07:15 | 2014-02-08 08:27 | 1.2 | 0.10909 | 33.0545 | 300 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC1 | D1 | 23 | 1160 | 2014-02-08 08:27 | 2014-02-08 15:05 | 6.6333 | 1.6081 | 487.2485 | 250 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC1 | NC | 24 | 1160 | 2014-02-08 22:00 | 2014-02-09 04:00 | 6 |  |  | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC1 | D1 | 25 | 1488 | 2014-02-10 23:05 | 2014-02-11 06:25 | 7.3333 | 0.15556 | 47.1333 | 323 | 330 | 303 | Air Heater (Regenerative) | Air Heater - High Differential
MC1 | D1 | 26 | 1488 | 2014-02-11 06:25 | 2014-02-11 10:00 | 3.5833 | 0.10859 | 32.9015 | 320 | 330 | 303 | Air Heater (Regenerative) | Air Heater - High Differential
MC1 | D1 | 27 | 1488 | 2014-02-11 10:00 | 2014-02-12 10:30 | 24.5 | 0.44545 | 134.9727 | 324 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | NC | 28 | 8460 | 2014-02-11 12:45 | 2014-02-11 16:00 | 3.25 |  |  | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
MC1 | NC | 29 | 8460 | 2014-02-12 07:00 | 2014-02-12 22:45 | 15.75 |  |  | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
MC1 | D1 | 30 | 1488 | 2014-02-12 10:30 | 2014-02-12 22:45 | 12.25 | 0.37121 | 112.4773 | 320 | 330 | 303 | Air Heater (Regenerative) | 1A Air heater - High Differential
MC1 | D1 | 31 | 1488 | 2014-02-12 22:45 | 2014-02-13 07:26 | 8.6833 | 0.52626 | 159.4576 | 310 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | D1 | 32 | 1488 | 2014-02-13 07:26 | 2014-02-13 22:00 | 14.5667 | 0.26485 | 80.2491 | 324 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | NC | 33 | 8460 | 2014-02-13 13:40 | 2014-02-13 22:00 | 8.3333 |  |  | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
MC1 | D4 | 34 | 310 | 2014-02-13 22:00 | 2014-02-14 03:00 | 5 | 1.3636 | 413.1818 | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Inspection
MC1 | D1 | 35 | 250 | 2014-02-14 03:00 | 2014-02-14 05:05 | 2.0833 | 0.56818 | 172.1591 | 240 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor Gearbox
MC1 | D1 | 36 | 250 | 2014-02-14 05:05 | 2014-02-14 06:50 | 1.75 | 0.42424 | 128.5455 | 250 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor Gearbox
MC1 | D1 | 37 | 250 | 2014-02-14 06:50 | 2014-02-14 12:00 | 5.1667 | 0.78283 | 237.197 | 280 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor GearboxGas Guns in Service
MC1 | D1 | 38 | 1488 | 2014-02-15 06:54 | 2014-02-16 06:20 | 23.4333 | 0.35505 | 107.5803 | 325 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | D1 | 39 | 1488 | 2014-02-16 06:20 | 2014-02-17 | 17.6667 | 0.53535 | 162.2121 | 320 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
[10 empty] | 330 | 303
MC1 | [5 empty] | 189.1667 | 16.2098 | 4911.5688
| D4 |  |  |  |  | 8.2 | 2.2364 | 677.6182
PD
MC2 | U1 | 35 | 3149 | 2014-02-01 23:37 | 2014-02-02 06:35 | 6.9667 | 6.9667 | 2083.0333 | 0 | 330 | 299 | Condenser Loss of Vacuum | Condenser Vacuum Trip
MC2 | NC | 36 | 1850 | 2014-02-02 06:35 | 2014-02-02 14:15 | 7.6667 |  |  | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Hot Start Up
MC2 | D1 | 37 | 1850 | 2014-02-02 14:15 | 2014-02-02 22:00 | 7.75 | 1.6439 | 491.5379 | 260 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D4 | 38 | 310 | 2014-02-02 22:00 | 2014-02-03 06:25 | 8.4167 | 2.2955 | 686.3409 | 240 | 330 | 299 | Pulverizer Mills | 2A Coal Mill - Inspection
MC2 | D1 | 39 | 1700 | 2014-02-03 08:15 | 2014-02-03 10:23 | 2.1333 | 0.32323 | 96.6465 | 280 | 330 | 299 | Feedwater Controls | Feedwater Flow Issue
MC2 | D1 | 40 | 1850 | 2014-02-03 10:23 | 2014-02-03 21:05 | 10.7 | 0.32424 | 96.9485 | 320 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D4 | 41 | 310 | 2014-02-03 23:00 | 2014-02-04 04:15 | 5.25 | 1.4318 | 428.1136 | 240 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Adjust Rollers & Inspection
MC2 | D4 | 42 | 310 | 2014-02-04 23:00 | 2014-02-05 04:45 | 5.75 | 1.5682 | 468.8864 | 240 | 330 | 299 | Pulverizer Mills | 2B Coal Mill - Inspection
MC2 | D1 | 43 | 250 | 2014-02-05 03:53 | 2014-02-05 04:29 | 0.6 | 0.25455 | 76.1091 | 190 | 330 | 299 | Pulverizer Feeders | 2A Coal Feeder - Wet Coal
MC2 | D1 | 44 | 250 | 2014-02-05 05:48 | 2014-02-05 07:56 | 2.1333 | 0.51717 | 154.6343 | 250 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Wet Coal
MC2 | D1 | 45 | 1850 | 2014-02-05 07:56 | 2014-02-05 09:43 | 1.7833 | 0.1351 | 40.3952 | 305 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 46 | 1850 | 2014-02-05 09:43 | 2014-02-05 13:25 | 3.7 | 0.17939 | 53.6388 | 314 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | NC | 47 | 1160 | 2014-02-07 23:00 | 2014-02-08 05:30 | 6.5 |  |  | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | D1 | 48 | 1160 | 2014-02-08 05:30 | 2014-02-08 07:35 | 2.0833 | 1.1995 | 358.649 | 140 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | D1 | 49 | 1160 | 2014-02-08 07:35 | 2014-02-08 09:28 | 1.8833 | 0.51364 | 153.5773 | 240 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC2 | NC | 50 | 1160 | 2014-02-08 22:00 | 2014-02-09 04:00 | 6 |  |  | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 51 | 1160 | 2014-02-09 21:12 | 2014-02-10 03:17 | 6.0833 |  |  | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 52 | 8460 | 2014-02-11 08:00 | 2014-02-11 12:20 | 4.3333 |  |  | 0 | 330 | 299 | Wet Scrubber Testing | Particulate Matter Testing - Full Load
MC2 | NC | 53 | 1160 | 2014-02-11 12:21 | 2014-02-11 16:30 | 4.15 |  |  | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 54 | 1160 | 2014-02-12 22:00 | 2014-02-13 04:50 | 6.8333 |  |  | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 55 | 8460 | 2014-02-13 08:00 | 2014-02-13 13:11 | 5.1833 |  |  | 0 | 330 | 299 | Wet Scrubber Testing | Particulate Matter Testing - Full Load
MC2 | D1 | 56 | 1160 | 2014-02-14 11:25 | 2014-02-15 00:32 | 13.1167 | 2.1861 | 653.6472 | 275 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC2 | MO | 57 | 1050 | 2014-02-15 00:32 | 2014-02-17 | 47.4667 | 47.4667 | 14192.5333 | 0 | 330 | 299 | Second Superheater Leaks | Boiler Tube Leak - Second Superheater
[10 empty] | 330 | 299
MC2 | [5 empty] | 166.4833 | 67.0057 | 20034.6913
| D4 |  |  |  |  | 19.4167 | 5.2955 | 1583.3409
PD
MC3 | D1 | 20 | 250 | 2014-02-07 18:02 | 2014-02-08 05:30 | 11.4667 | 2.6357 | 1033.1956 | 325 | 422 | 392 | Pulverizer Feeders | 3C Coal Feeder - Replace Speed Sensor
MC3 | D1 | 21 | 360 | 2014-02-09 09:05 | 2014-02-09 10:25 | 1.3333 | 0.29068 | 113.9463 | 330 | 422 | 392 | Burners | 3C Mill - 3C3 Coal Burner High Temperature
MC3 | D1 | 22 | 360 | 2014-02-09 10:50 | 2014-02-09 16:36 | 5.7667 | 1.2572 | 492.8177 | 330 | 422 | 392 | Burners | 3C Mill - 3C10 Coal Burner High Temperature
MC3 | D1 | 23 | 310 | 2014-02-09 21:52 | 2014-02-10 07:58 | 10.1 | 2.4412 | 956.963 | 320 | 422 | 392 | Pulverizer Mills | 3C Primary Air Fan Housing InspectionRepair Suction Box & Hot Air Damper Linkage
MC3 | D4 | 24 | 250 | 2014-02-10 11:00 | 2014-02-10 16:05 | 5.0833 | 1.1082 | 434.4202 | 330 | 422 | 392 | Pulverizer Feeders | 3C Coal Feeder - Calibration
MC3 | D1 | 25 | 360 | 2014-02-10 19:42 | 2014-02-10 19:57 | 0.25 | 0.060427 | 23.6872 | 320 | 422 | 392 | Burners | 3D Mill - 3D4 Coal Burner High Temperature
MC3 | D1 | 26 | 360 | 2014-02-15 11:11 | 2014-02-15 12:43 | 1.5333 | 0.22528 | 88.3084 | 360 | 422 | 392 | Burners | 3C Mill - 3C1 & 3C3 Coal Burners High Temperature
MC3 | D1 | 27 | 360 | 2014-02-15 13:28 | 2014-02-15 14:20 | 0.86667 | 0.12733 | 49.9134 | 360 | 422 | 392 | Burners | 3A Mill - 3A4 Coal Burner High Temperature
MC3 | [5 empty] | 36.4 | 8.1461 | 3193.2518
| D4 |  |  |  |  | 5.0833 | 1.1082 | 434.4202
PD
MC4 | D4 | 16 | 310 | 2014-02-02 23:00 | 2014-02-03 03:55 | 4.9167 | 0.95313 | 458.4579 | 420 | 521 | 481 | Pulverizer Mills | 4C Coal Mill - Inspection
MC4 | D1 | 17 | 360 | 2014-02-03 03:55 | 2014-02-03 06:08 | 2.2167 | 0.81264 | 390.8779 | 330 | 521 | 481 | Burners | 4B Mill - 4B3 Coal Burner High Temperature4C Coal Mill - Inspection
MC4 | D1 | 18 | 1710 | 2014-02-04 14:30 | 2014-02-17 | 297.5 | 1.7131 | 823.9779 | 518 | 521 | 481 | Combustion/Steam Condition Controls | Max Steam Flow Issues
MC4 | D1 | 19 | 310 | 2014-02-07 06:50 | 2014-02-07 07:05 | 0.25 | 0.029271 | 14.0792 | 460 | 521 | 481 | Pulverizer Mills | 4B Coal Mill - Swing Valve & Ignitor Gas Valve Issues
MC4 | D1 | 20 | 250 | 2014-02-11 09:10 | 2014-02-11 09:20 | 0.16667 | 0.029111 | 14.0022 | 430 | 521 | 481 | Pulverizer Feeders | 4C Coal Feeder - Microprocessor Issue
MC4 | NC | 21 | 1160 | 2014-02-12 23:59 | 2014-02-13 04:20 | 4.35 |  |  | 0 | 521 | 481 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC4 | [5 empty] | 309.4 | 3.5372 | 1701.3952
| D4 |  |  |  |  | 4.9167 | 0.95313 | 458.4579
PD
TC1 | NC | 26 | 9999 | 2014-02-05 10:45 | 2014-02-05 16:26 | 5.6833 |  |  | 0 | 410 | 383 | Total Unit Performance Testing | Unit running and good for full load, this non-curtailing event was for the complet
TC1 | D1 | 27 | 310 | 2014-02-10 07:22 | 2014-02-10 07:45 | 0.38333 | 0.032724 | 12.5331 | 375 | 410 | 383 | Pulverizer Mills | Derate on TC1 to 500 MW's due to D coal mill fire. Additional issue with the E co
TC1 | D1 | 28 | 310 | 2014-02-10 10:00 | 2014-02-10 13:58 | 3.9667 | 0.33862 | 129.6907 | 375 | 410 | 383 | Pulverizer Mills | Derate required due to fire on the 1D coal mill.
TC1 | D1 | 29 | 310 | 2014-02-11 22:17 | 2014-02-11 23:30 | 1.2167 | 0.10386 | 39.7791 | 375 | 410 | 383 | Pulverizer Mills | Derate required due to high temperature on the 1B coal mill.
[10 empty] | 410 | 383
TC1 | [5 empty] | 11.25 | 0.4752 | 182.0028
D4
PD
TC2 | NC | 16 | 1190 | 2014-02-01 00:01 | 2014-02-01 06:15 | 6.2333 | 6.2333 | 3553 | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate at 550 MW to conduct boiler OEM recommended deslag. Unit av
TC2 | D1 | 17 | 310 | 2014-02-02 16:30 | 2014-02-02 19:00 | 2.5 | 0.40259 | 229.479 | 509.25 | 607 | 570 | Pulverizer Mills | The 2D mill was performing poorly and was taken off-line to investigate. Some mil
TC2 | D1 | 18 | 1455 | 2014-02-04 15:45 | 2014-02-04 16:15 | 0.5 | 0.015651 | 8.9209 | 588 | 607 | 570 | Induced Draft Fans | Derate required on the unit due to ID fan stall alarms. Required derate to avoid
TC2 | PO | 20 | 360 | 2014-02-08 03:21 | 2014-02-17 | 212.65 | 212.65 | 121210.5 | 0 | 607 | 570 | Burners | TC2 began the planned outage for the replacement of all 30 burners. This effort i
[10 empty] | 607 | 570
TC2 | [5 empty] | 221.8833 | 219.3016 | 125001.8999
D4
PD
[10 empty] | 131 | 130
BR5 | [5 empty] | 0 | 0 | 0
BR6 | MO | 10 | 5048 | 2014-02-04 06:30 | 2014-02-04 08:00 | 1.5 | 1.5 | 256.5 | 0 | 172 | 171 | Gas Fuel System with controls and instruments | Change cable for fuel gas flow meter RTD.
[10 empty] | 172 | 171
BR6 | [5 empty] | 1.5 | 1.5 | 256.5
BR7 | U1 | 12 | 5049 | 2014-02-10 17:14 | 2014-02-10 19:34 | 2.3333 | 2.3333 | 399 | 0 | 172 | 171 | Other Gas Turbine Fuel System Problems | Issue with pressure regulators in reducing station.
[10 empty] | 172 | 171
BR7 | [5 empty] | 2.3333 | 2.3333 | 399
[10 empty] | 129 | 128
BR8 | [5 empty] | 0 | 0 | 0
[10 empty] | 139 | 138
BR9 | [5 empty] | 0 | 0 | 0
[10 empty] | 139 | 138
BR10 | [5 empty] | 0 | 0 | 0
[10 empty] | 129 | 128
BR11 | [5 empty] | 0 | 0 | 0
CR11 | U1 | 9 | 3840 | 2014-02-03 00:42 | 2014-02-03 09:37 | 8.9167 | 8.9167 | 124.8333 | 0 | 14 | 14 | Service Air Compressors | Clutch air compressor pumping up slowly - probably due to the weather.
[10 empty] | 14 | 14
CR11 | [5 empty] | 8.9167 | 8.9167 | 124.8333
HA1 | U1 | 9 | 3611 | 2014-02-08 02:53 | 2014-02-08 19:05 | 16.2 | 16.2 | 194.4 | 0 | 12 | 12 | Switchyard Circuit Breakers | Loss of power to 138KV sub.
[10 empty] | 12 | 12
HF1 | [5 empty] | 16.2 | 16.2 | 194.4
HA2 | U1 | 4 | 3611 | 2014-02-08 02:53 | 2014-02-08 19:05 | 16.2 | 16.2 | 194.4 | 0 | 12 | 12 | Switchyard Circuit Breakers | Loss power to 138KV bus in substation
[10 empty] | 12 | 12
HF2 | [5 empty] | 16.2 | 16.2 | 194.4
[10 empty] | 13 | 13
PR11 | [5 empty] | 0 | 0 | 0
[10 empty] | 28 | 28
PR12 | [5 empty] | 0 | 0 | 0
PR13 | PO | 4 | 4720 | 2014-02-15 06:08 | 2014-02-17 | 41.8667 | 41.8667 | 7326.6667 | 0 | 176 | 175 | Generator Synchronization Equipment | Generator synchronization equipment modifications. Replacing all generator protec
[10 empty] | 176 | 175
PR13 | [5 empty] | 41.8667 | 41.8667 | 7326.6667
TC5 | U1 | 12 | 5079 | 2014-02-11 06:16 | 2014-02-11 08:35 | 2.3167 | 2.3167 | 407.7333 | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
TC5 | SF | 14 | 5130 | 2014-02-17 06:28 | 2014-02-17 06:40 | 0.2 | 0.2 | 35.2 | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to issue with LCI.
[10 empty] | 180 | 176
TC5 | [5 empty] | 2.5167 | 2.5167 | 442.9333
[10 empty] | 180 | 176
TC6 | MO | 30 | 5041 | 2014-02-04 11:33 | 2014-02-04 15:52 | 4.3167 | 4.3167 | 759.7333 | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Maintenance outage to change controller on Fuel Gas Worker Valve.
TC6 | U1 | 33 | 5079 | 2014-02-11 06:16 | 2014-02-11 06:58 | 0.7 | 0.7 | 123.2 | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
TC6 | U1 | 34 | 5079 | 2014-02-11 08:29 | 2014-02-11 09:45 | 1.2667 | 1.2667 | 222.9333 | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
[10 empty] | 180 | 176
TC6 | [5 empty] | 6.2833 | 6.2833 | 1105.8667
TC7 | U1 | 8 | 5160 | 2014-02-05 16:03 | 2014-02-05 16:08 | 0.083333 | 0.083333 | 14.6667 | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Unit rolled back to FSNL due to issue with pressure switch on Exhaust Frame Blower
TC7 | U1 | 9 | 5160 | 2014-02-05 16:09 | 2014-02-05 16:17 | 0.13333 | 0.13333 | 23.4667 | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Unit rolled back to FSNL due to issue with pressure switch on Exhaust Frame Blower
[10 empty] | 180 | 176
TC7 | [5 empty] | 0.21667 | 0.21667 | 38.1333
[10 empty] | 180 | 176
TC8 | [5 empty] | 0 | 0 | 0
TC9 | D1 | 17 | 5041 | 2014-02-07 10:00 | 2014-02-07 12:38 | 2.6333 | 1.463 | 257.4815 | 80 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Derate to 80 MWs due to issue with worker fuel gas valve.
TC9 | U1 | 15 | 5041 | 2014-02-07 12:38 | 2014-02-07 15:35 | 2.95 | 2.95 | 519.2 | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Forced outage to address pressure swings due to worker fuel gas valve.
[10 empty] | 180 | 176
TC9 | [5 empty] | 5.5833 | 4.413 | 776.6815
[10 empty] | 180 | 176
TC10 | [5 empty] | 0 | 0 | 0
[10 empty] | 16 | 16
ZN1 | [5 empty] | 0 | 0 | 0

## Event List By Impact
Unit | Event | Event | Cause | Event | Event | Evt. | Equiv. | MWH |  |  |  | Event | Event
Name | Type | No | Code | Start | End | Hrs | Dur Hrs | Lost | GAC | GMC | NMC | Cause | Description
TC2 | PO | 20 | 360 | 2014-02-08 03:21 | 2014-02-17 | 212.65 | 212.65 | 121210.5 | 0 | 607 | 570 | Burners | TC2 began the planned outage for the replacement of all 30 burners. This effort i
GH1 | MO | 6 | 1060 | 2014-02-01 15:04 | 2014-02-03 01:27 | 34.3833 | 34.3833 | 16538.3833 | 0 | 517 | 481 | First Reheater Leaks | Unit 1 had been running with a tube leak, located around IK #6, for s
MC2 | MO | 57 | 1050 | 2014-02-15 00:32 | 2014-02-17 | 47.4667 | 47.4667 | 14192.5333 | 0 | 330 | 299 | Second Superheater Leaks | Boiler Tube Leak - Second Superheater
BR3 | U1 | 8 | 339 | 2014-02-01 | 2014-02-01 16:05 | 16.0833 | 16.0833 | 6658.5 | 0 | 457 | 414 | Pulverizer Puff Boiler Damage | 3-5 Mill puff causing D corner burner damage and associated boiler tube leak.
CR5 | U2 | 7 | 1060 | 2014-02-07 10:51 | 2014-02-09 | 37.15 | 37.15 | 6241.2 | 0 | 181 | 168 | First Reheater Leaks | Reheat boiler tube leak - cracked. Total of 6 leaks - 1 dutchman & 4 padwelds.
GH3 | MO | 11 | 1455 | 2014-02-01 | 2014-02-01 09:26 | 9.4333 | 9.4333 | 4546.8667 | 0 | 527 | 482 | Induced Draft Fan Bearings | Unit 3 has been running with 3-2 ID Fan OB Fan bearing having periodi
GH3 | PD | 17 | 9510 | 2014-02-15 22:00 | 2014-02-16 13:04 | 15.0667 | 9.3488 | 4506.1055 | 200 | 527 | 482 | Plant Modifications For Baghouse | KBR electrical tie-in for Bag House and ID fan.
CR5 | SF | 8 | 8560 | 2014-02-09 | 2014-02-10 00:12 | 24.2 | 24.2 | 4065.6 | 0 | 181 | 168 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
GR4 | U1 | 27 | 1050 | 2014-02-07 04:42 | 2014-02-08 17:57 | 37.25 | 37.25 | 3650.5 | 0 | 105 | 98 | Second Superheater Leaks | Ops discovered leak in B5 Sec SH Section at 0344, unit was removed from service in
MC1 | D1 | 18 | 4261 | 2014-02-01 21:20 | 2014-02-02 08:50 | 11.5 | 7.3182 | 2217.4091 | 120 | 330 | 303 | Turbine Control Valve Stuck | Turbine #2 Control Valve - Stuck Closed
MC2 | U1 | 35 | 3149 | 2014-02-01 23:37 | 2014-02-02 06:35 | 6.9667 | 6.9667 | 2083.0333 | 0 | 330 | 299 | Condenser Loss of Vacuum | Condenser Vacuum Trip
CR4 | MO | 9 | 8100 | 2014-02-16 11:30 | 2014-02-17 | 12.5 | 12.5 | 1937.5 | 0 | 168 | 155 | Wet Scrubber Absorber Cleaning | Flue gas desulfurization module cleaning.
GH1 | D1 | 8 | 250 | 2014-02-09 16:20 | 2014-02-09 19:43 | 3.3833 | 2.9449 | 1416.4845 | 67 | 517 | 481 | Pulverizer Feeders | 1-4 Feeder belt bound up.
GH3 | D1 | 14 | 9650 | 2014-02-05 15:00 | 2014-02-05 19:50 | 4.8333 | 2.9257 | 1410.1777 | 208 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
MC3 | D1 | 20 | 250 | 2014-02-07 18:02 | 2014-02-08 05:30 | 11.4667 | 2.6357 | 1033.1956 | 325 | 422 | 392 | Pulverizer Feeders | 3C Coal Feeder - Replace Speed Sensor
GH3 | D1 | 16 | 9650 | 2014-02-15 11:22 | 2014-02-15 14:52 | 3.5 | 2.0721 | 998.7552 | 215 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
MC3 | D1 | 23 | 310 | 2014-02-09 21:52 | 2014-02-10 07:58 | 10.1 | 2.4412 | 956.963 | 320 | 422 | 392 | Pulverizer Mills | 3C Primary Air Fan Housing InspectionRepair Suction Box & Hot Air Damper Linkage
CR4 | D1 | 8 | 8560 | 2014-02-09 | 2014-02-09 11:42 | 11.7 | 6.1286 | 949.9286 | 80 | 168 | 155 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
GH4 | U1 | 7 | 250 | 2014-02-09 03:51 | 2014-02-09 05:38 | 1.7833 | 1.7833 | 875.6167 | 0 | 534 | 491 | Pulverizer Feeders | 4-6 Mill Feeder coal inlet plugged causing controls to see this feeder as
MC4 | D1 | 18 | 1710 | 2014-02-04 14:30 | 2014-02-17 | 297.5 | 1.7131 | 823.9779 | 518 | 521 | 481 | Combustion/Steam Condition Controls | Max Steam Flow Issues
MC2 | D4 | 38 | 310 | 2014-02-02 22:00 | 2014-02-03 06:25 | 8.4167 | 2.2955 | 686.3409 | 240 | 330 | 299 | Pulverizer Mills | 2A Coal Mill - Inspection
MC2 | D1 | 56 | 1160 | 2014-02-14 11:25 | 2014-02-15 00:32 | 13.1167 | 2.1861 | 653.6472 | 275 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
CR6 | D1 | 9 | 8560 | 2014-02-09 | 2014-02-09 06:50 | 6.8333 | 2.5134 | 603.2184 | 165 | 261 | 240 | Electrostatic Precipitator Problems | Loss of communication between DCS & precipitator.
BR3 | PD | 9 | 3412 | 2014-02-04 22:00 | 2014-02-05 01:52 | 3.8667 | 1.2438 | 514.9182 | 310 | 457 | 414 | Feedwater Pump Drive - Steam Turbine | Collecting 3-2 BFP vibration data
MC3 | D1 | 22 | 360 | 2014-02-09 10:50 | 2014-02-09 16:36 | 5.7667 | 1.2572 | 492.8177 | 330 | 422 | 392 | Burners | 3C Mill - 3C10 Coal Burner High Temperature
MC2 | D1 | 37 | 1850 | 2014-02-02 14:15 | 2014-02-02 22:00 | 7.75 | 1.6439 | 491.5379 | 260 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC1 | D1 | 23 | 1160 | 2014-02-08 08:27 | 2014-02-08 15:05 | 6.6333 | 1.6081 | 487.2485 | 250 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC2 | D4 | 42 | 310 | 2014-02-04 23:00 | 2014-02-05 04:45 | 5.75 | 1.5682 | 468.8864 | 240 | 330 | 299 | Pulverizer Mills | 2B Coal Mill - Inspection
MC4 | D4 | 16 | 310 | 2014-02-02 23:00 | 2014-02-03 03:55 | 4.9167 | 0.95313 | 458.4579 | 420 | 521 | 481 | Pulverizer Mills | 4C Coal Mill - Inspection
MC3 | D4 | 24 | 250 | 2014-02-10 11:00 | 2014-02-10 16:05 | 5.0833 | 1.1082 | 434.4202 | 330 | 422 | 392 | Pulverizer Feeders | 3C Coal Feeder - Calibration
MC2 | D4 | 41 | 310 | 2014-02-03 23:00 | 2014-02-04 04:15 | 5.25 | 1.4318 | 428.1136 | 240 | 330 | 299 | Pulverizer Mills | 2D Coal Mill - Adjust Rollers & Inspection
MC1 | D4 | 34 | 310 | 2014-02-13 22:00 | 2014-02-14 03:00 | 5 | 1.3636 | 413.1818 | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Inspection
GH1 | PD | 9 | 250 | 2014-02-10 09:00 | 2014-02-10 15:33 | 6.55 | 0.84884 | 408.2918 | 450 | 517 | 481 | Pulverizer Feeders | 1-4 Mill off to replace feeder discharge pipe pluggage detector.
MC4 | D1 | 17 | 360 | 2014-02-03 03:55 | 2014-02-03 06:08 | 2.2167 | 0.81264 | 390.8779 | 330 | 521 | 481 | Burners | 4B Mill - 4B3 Coal Burner High Temperature4C Coal Mill - Inspection
MC2 | D1 | 48 | 1160 | 2014-02-08 05:30 | 2014-02-08 07:35 | 2.0833 | 1.1995 | 358.649 | 140 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
CR6 | D1 | 12 | 250 | 2014-02-16 04:54 | 2014-02-16 12:17 | 7.3833 | 1.4427 | 346.2529 | 210 | 261 | 240 | Pulverizer Feeders | 6B feeder belt torn. Repaired & put back in service.
GR4 | D1 | 26 | 338 | 2014-02-04 22:14 | 2014-02-05 11:55 | 13.6833 | 3.2579 | 319.2778 | 80 | 105 | 98 | Pulverizer Control Systems (Temp and Pressure) | 5-3 PA Fan control jack would not react to input from PA Controller.
CR5 | D4 | 6 | 344 | 2014-02-04 23:00 | 2014-02-05 05:00 | 6 | 1.8564 | 311.8674 | 125 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
GH2 | D1 | 10 | 250 | 2014-02-15 03:20 | 2014-02-15 10:00 | 6.6667 | 0.64178 | 306.1297 | 460 | 509 | 477 | Pulverizer Feeders | 2-1 Feeder control issue.
CR5 | D4 | 4 | 344 | 2014-02-02 23:00 | 2014-02-03 04:50 | 5.8333 | 1.8048 | 303.2044 | 125 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
BR2 | D1 | 4 | 310 | 2014-02-11 20:04 | 2014-02-12 02:17 | 6.2167 | 1.7269 | 290.1111 | 130 | 180 | 168 | Pulverizer Mills | 2-4 mill west door broken spring bolt
GH4 | PD | 6 | 3416 | 2014-02-08 23:00 | 2014-02-09 00:20 | 1.3333 | 0.58427 | 286.8764 | 300 | 534 | 491 | Other Feedwater Pump Problems | Planned derate to inspect 4-2 BFP leak. Derate was planned with
GH3 | D1 | 15 | 9650 | 2014-02-15 04:41 | 2014-02-15 07:07 | 2.4333 | 0.5864 | 282.6453 | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
BR2 | D1 | 5 | 310 | 2014-02-16 17:57 | 2014-02-17 | 6.05 | 1.6806 | 282.3333 | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill
CR5 | D4 | 5 | 344 | 2014-02-03 23:00 | 2014-02-04 04:55 | 5.9167 | 1.6671 | 280.0773 | 130 | 181 | 168 | Pulverizer Inspection | 5A mill inspection.
MC1 | D4 | 21 | 250 | 2014-02-06 | 2014-02-06 03:12 | 3.2 | 0.87273 | 264.4364 | 240 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Repair Discharge Flapper
MC1 | D1 | 37 | 250 | 2014-02-14 06:50 | 2014-02-14 12:00 | 5.1667 | 0.78283 | 237.197 | 280 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor GearboxGas Guns in Service
TC2 | D1 | 17 | 310 | 2014-02-02 16:30 | 2014-02-02 19:00 | 2.5 | 0.40259 | 229.479 | 509.25 | 607 | 570 | Pulverizer Mills | The 2D mill was performing poorly and was taken off-line to investigate. Some mil
CR6 | D1 | 11 | 4240 | 2014-02-11 08:00 | 2014-02-11 14:00 | 6 | 0.94253 | 226.2069 | 220 | 261 | 240 | Lp Turbine Bearings | #4 Turbine bearing temperature running high.
GR4 | D1 | 24 | 8551 | 2014-02-01 | 2014-02-05 11:55 | 107.9167 | 2.0556 | 201.4444 | 103 | 105 | 98 | Electrostatic Precipitator Field Out Of Service | GR4 load reduced due to opacity issues as a result of two half cabinets grounded o
MC1 | D1 | 35 | 250 | 2014-02-14 03:00 | 2014-02-14 05:05 | 2.0833 | 0.56818 | 172.1591 | 240 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor Gearbox
MC1 | D1 | 39 | 1488 | 2014-02-16 06:20 | 2014-02-17 | 17.6667 | 0.53535 | 162.2121 | 320 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC1 | D1 | 31 | 1488 | 2014-02-12 22:45 | 2014-02-13 07:26 | 8.6833 | 0.52626 | 159.4576 | 310 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC2 | D1 | 44 | 250 | 2014-02-05 05:48 | 2014-02-05 07:56 | 2.1333 | 0.51717 | 154.6343 | 250 | 330 | 299 | Pulverizer Feeders | 2B Coal Feeder - Wet Coal
MC2 | D1 | 49 | 1160 | 2014-02-08 07:35 | 2014-02-08 09:28 | 1.8833 | 0.51364 | 153.5773 | 240 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
GH2 | PD | 8 | 340 | 2014-02-13 23:00 | 2014-02-14 02:11 | 3.1833 | 0.30645 | 146.1769 | 460 | 509 | 477 | Other Pulverizer Problems | 2-5 Mill off to replace pyrite scraper.
MC1 | D1 | 27 | 1488 | 2014-02-11 10:00 | 2014-02-12 10:30 | 24.5 | 0.44545 | 134.9727 | 324 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
GH3 | D1 | 13 | 9650 | 2014-02-05 14:10 | 2014-02-05 15:00 | 0.83333 | 0.27989 | 134.9051 | 350 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
TC1 | D1 | 28 | 310 | 2014-02-10 10:00 | 2014-02-10 13:58 | 3.9667 | 0.33862 | 129.6907 | 375 | 410 | 383 | Pulverizer Mills | Derate required due to fire on the 1D coal mill.
MC1 | D1 | 36 | 250 | 2014-02-14 05:05 | 2014-02-14 06:50 | 1.75 | 0.42424 | 128.5455 | 250 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Replace Clean Out Conveyor Gearbox
MC1 | D1 | 20 | 250 | 2014-02-05 07:28 | 2014-02-05 09:30 | 2.0333 | 0.40051 | 121.353 | 265 | 330 | 303 | Pulverizer Feeders | 1C Coal Feeder - Wet Coal
GH4 | D1 | 5 | 9650 | 2014-02-03 00:50 | 2014-02-03 01:48 | 0.96667 | 0.24257 | 119.1027 | 400 | 534 | 491 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit.
MC3 | D1 | 21 | 360 | 2014-02-09 09:05 | 2014-02-09 10:25 | 1.3333 | 0.29068 | 113.9463 | 330 | 422 | 392 | Burners | 3C Mill - 3C3 Coal Burner High Temperature
MC1 | D1 | 30 | 1488 | 2014-02-12 10:30 | 2014-02-12 22:45 | 12.25 | 0.37121 | 112.4773 | 320 | 330 | 303 | Air Heater (Regenerative) | 1A Air heater - High Differential
GH2 | PD | 7 | 344 | 2014-02-06 23:00 | 2014-02-07 01:24 | 2.4 | 0.23104 | 110.2067 | 460 | 509 | 477 | Pulverizer Inspection | 2-2 Mill was removed from service to inspect due to high differen
MC1 | D1 | 38 | 1488 | 2014-02-15 06:54 | 2014-02-16 06:20 | 23.4333 | 0.35505 | 107.5803 | 325 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC2 | D1 | 40 | 1850 | 2014-02-03 10:23 | 2014-02-03 21:05 | 10.7 | 0.32424 | 96.9485 | 320 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC2 | D1 | 39 | 1700 | 2014-02-03 08:15 | 2014-02-03 10:23 | 2.1333 | 0.32323 | 96.6465 | 280 | 330 | 299 | Feedwater Controls | Feedwater Flow Issue
GH2 | D1 | 6 | 312 | 2014-02-01 14:40 | 2014-02-01 18:00 | 3.3333 | 0.18991 | 90.5894 | 480 | 509 | 477 | Pulverizer Mill Classifiers | 2-1 Mill not grinding, took off for inspection.
MC3 | D1 | 26 | 360 | 2014-02-15 11:11 | 2014-02-15 12:43 | 1.5333 | 0.22528 | 88.3084 | 360 | 422 | 392 | Burners | 3C Mill - 3C1 & 3C3 Coal Burners High Temperature
MC1 | D1 | 32 | 1488 | 2014-02-13 07:26 | 2014-02-13 22:00 | 14.5667 | 0.26485 | 80.2491 | 324 | 330 | 303 | Air Heater (Regenerative) | 1A Air Heater - High Differential
MC2 | D1 | 43 | 250 | 2014-02-05 03:53 | 2014-02-05 04:29 | 0.6 | 0.25455 | 76.1091 | 190 | 330 | 299 | Pulverizer Feeders | 2A Coal Feeder - Wet Coal
GH3 | D1 | 12 | 9650 | 2014-02-02 20:10 | 2014-02-02 20:45 | 0.58333 | 0.14058 | 67.7574 | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | 3-2B SO3 injection blower pressure sensing line came off causing
GH2 | PD | 9 | 340 | 2014-02-14 02:11 | 2014-02-14 03:39 | 1.4667 | 0.14119 | 67.3485 | 460 | 509 | 477 | Other Pulverizer Problems | 2-6 Mill off to inspect grinding section and classifiers.
GH1 | D1 | 7 | 250 | 2014-02-07 12:35 | 2014-02-07 13:45 | 1.1667 | 0.12863 | 61.8694 | 460 | 517 | 481 | Pulverizer Feeders | Metal hung in 1-4 mill feeder.
GR3 | D1 | 6 | 9630 | 2014-02-11 09:40 | 2014-02-11 13:13 | 3.55 | 0.80467 | 57.1313 | 58 | 75 | 71 | Opacity - Fossil Steam Units | Continuation of previous event. GR3 derate increased to blow soot and clean boile
CR6 | D1 | 7 | 250 | 2014-02-07 01:12 | 2014-02-07 02:10 | 0.96667 | 0.22593 | 54.2222 | 200 | 261 | 240 | Pulverizer Feeders | D1 feeder plugged due to torn belt.
MC2 | D1 | 46 | 1850 | 2014-02-05 09:43 | 2014-02-05 13:25 | 3.7 | 0.17939 | 53.6388 | 314 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
CR6 | D1 | 8 | 250 | 2014-02-08 00:05 | 2014-02-08 01:13 | 1.1333 | 0.22146 | 53.1494 | 210 | 261 | 240 | Pulverizer Feeders | D2 feeder plugged due to wet coal.
MC3 | D1 | 27 | 360 | 2014-02-15 13:28 | 2014-02-15 14:20 | 0.86667 | 0.12733 | 49.9134 | 360 | 422 | 392 | Burners | 3A Mill - 3A4 Coal Burner High Temperature
MC1 | D1 | 25 | 1488 | 2014-02-10 23:05 | 2014-02-11 06:25 | 7.3333 | 0.15556 | 47.1333 | 323 | 330 | 303 | Air Heater (Regenerative) | Air Heater - High Differential
GH1 | D1 | 10 | 9650 | 2014-02-13 07:23 | 2014-02-13 09:08 | 1.75 | 0.091393 | 43.9599 | 490 | 517 | 481 | Other Stack Or Exhaust Emissions -fossil Stm Unit | U1 H2SO4 was high. Dropped load to keep it in compliance.
MC2 | D1 | 45 | 1850 | 2014-02-05 07:56 | 2014-02-05 09:43 | 1.7833 | 0.1351 | 40.3952 | 305 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
TC1 | D1 | 29 | 310 | 2014-02-11 22:17 | 2014-02-11 23:30 | 1.2167 | 0.10386 | 39.7791 | 375 | 410 | 383 | Pulverizer Mills | Derate required due to high temperature on the 1B coal mill.
CR6 | D1 | 10 | 340 | 2014-02-09 06:50 | 2014-02-09 07:15 | 0.41667 | 0.15326 | 36.7816 | 165 | 261 | 240 | Other Pulverizer Problems | Support fuel unavailable due to loss of communication between precipitator & DCS.
MC1 | D1 | 22 | 1160 | 2014-02-08 07:15 | 2014-02-08 08:27 | 1.2 | 0.10909 | 33.0545 | 300 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Slag - First Reheater
MC1 | D1 | 26 | 1488 | 2014-02-11 06:25 | 2014-02-11 10:00 | 3.5833 | 0.10859 | 32.9015 | 320 | 330 | 303 | Air Heater (Regenerative) | Air Heater - High Differential
GR3 | D1 | 7 | 9630 | 2014-02-11 13:13 | 2014-02-11 17:20 | 4.1167 | 0.38422 | 27.2798 | 68 | 75 | 71 | Opacity - Fossil Steam Units | Continuation of previous event. GR3/B4 soot blowing completed, raised load as muc
GR4 | D1 | 25 | 263 | 2014-02-01 21:38 | 2014-02-01 22:48 | 1.1667 | 0.27778 | 27.2222 | 80 | 105 | 98 | Primary Air Fan Drives | 5-2 PA Fan Control Jack Minimum Stop failed to disengage. I&E found and repaired
MC3 | D1 | 25 | 360 | 2014-02-10 19:42 | 2014-02-10 19:57 | 0.25 | 0.060427 | 23.6872 | 320 | 422 | 392 | Burners | 3D Mill - 3D4 Coal Burner High Temperature
GR4 | D1 | 28 | 9630 | 2014-02-13 14:41 | 2014-02-13 16:28 | 1.7833 | 0.16984 | 16.6444 | 95 | 105 | 98 | Opacity - Fossil Steam Units | GR4 derated due to opacity, blowing soot to clean up the boiler.
MC4 | D1 | 19 | 310 | 2014-02-07 06:50 | 2014-02-07 07:05 | 0.25 | 0.029271 | 14.0792 | 460 | 521 | 481 | Pulverizer Mills | 4B Coal Mill - Swing Valve & Ignitor Gas Valve Issues
MC4 | D1 | 20 | 250 | 2014-02-11 09:10 | 2014-02-11 09:20 | 0.16667 | 0.029111 | 14.0022 | 430 | 521 | 481 | Pulverizer Feeders | 4C Coal Feeder - Microprocessor Issue
TC1 | D1 | 27 | 310 | 2014-02-10 07:22 | 2014-02-10 07:45 | 0.38333 | 0.032724 | 12.5331 | 375 | 410 | 383 | Pulverizer Mills | Derate on TC1 to 500 MW's due to D coal mill fire. Additional issue with the E co
TC2 | D1 | 18 | 1455 | 2014-02-04 15:45 | 2014-02-04 16:15 | 0.5 | 0.015651 | 8.9209 | 588 | 607 | 570 | Induced Draft Fans | Derate required on the unit due to ID fan stall alarms. Required derate to avoid
GR3 | D1 | 4 | 9630 | 2014-02-11 08:17 | 2014-02-11 09:18 | 1.0167 | 0.094889 | 6.7371 | 68 | 75 | 71 | Opacity - Fossil Steam Units | Load reduced on GR3 due to high opacity.
GR3 | D1 | 9 | 9630 | 2014-02-12 08:20 | 2014-02-12 09:30 | 1.1667 | 0.093333 | 6.6267 | 69 | 75 | 71 | Opacity - Fossil Steam Units | GR3 derate decreased from Event #8 due to high opacity.
GR3 | D1 | 10 | 9630 | 2014-02-12 09:30 | 2014-02-12 11:00 | 1.5 | 0.08 | 5.68 | 71 | 75 | 71 | Opacity - Fossil Steam Units | GR3 Derate reduction from Event #9 due to high opacity.
GR3 | D1 | 8 | 9630 | 2014-02-12 07:40 | 2014-02-12 08:20 | 0.66667 | 0.08 | 5.68 | 66 | 75 | 71 | Opacity - Fossil Steam Units | GR3 load reduced due to high opacity.
GR3 | D1 | 5 | 9630 | 2014-02-11 09:18 | 2014-02-11 09:40 | 0.36667 | 0.024444 | 1.7356 | 70 | 75 | 71 | Opacity - Fossil Steam Units | GR3 derate reduction from event #4. Derate due to igh opacity.
MC1 | NC | 29 | 8460 | 2014-02-12 07:00 | 2014-02-12 22:45 | 15.75 |  |  | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
MC1 | NC | 33 | 8460 | 2014-02-13 13:40 | 2014-02-13 22:00 | 8.3333 |  |  | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
MC2 | NC | 36 | 1850 | 2014-02-02 06:35 | 2014-02-02 14:15 | 7.6667 |  |  | 0 | 330 | 299 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Hot Start Up
MC2 | NC | 54 | 1160 | 2014-02-12 22:00 | 2014-02-13 04:50 | 6.8333 |  |  | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 47 | 1160 | 2014-02-07 23:00 | 2014-02-08 05:30 | 6.5 |  |  | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
TC2 | NC | 16 | 1190 | 2014-02-01 00:01 | 2014-02-01 06:15 | 6.2333 |  |  | 0 | 607 | 570 | Other Tube Slagging or Fouling | Non-curtailing derate at 550 MW to conduct boiler OEM recommended deslag. Unit av
MC2 | NC | 51 | 1160 | 2014-02-09 21:12 | 2014-02-10 03:17 | 6.0833 |  |  | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC1 | NC | 24 | 1160 | 2014-02-08 22:00 | 2014-02-09 04:00 | 6 |  |  | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 50 | 1160 | 2014-02-08 22:00 | 2014-02-09 04:00 | 6 |  |  | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
TC1 | NC | 26 | 9999 | 2014-02-05 10:45 | 2014-02-05 16:26 | 5.6833 |  |  | 0 | 410 | 383 | Total Unit Performance Testing | Unit running and good for full load, this non-curtailing event was for the complet
MC1 | NC | 19 | 1160 | 2014-02-04 23:00 | 2014-02-05 04:15 | 5.25 |  |  | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater. Full load available if needed.
MC2 | NC | 55 | 8460 | 2014-02-13 08:00 | 2014-02-13 13:11 | 5.1833 |  |  | 0 | 330 | 299 | Wet Scrubber Testing | Particulate Matter Testing - Full Load
MC4 | NC | 21 | 1160 | 2014-02-12 23:59 | 2014-02-13 04:20 | 4.35 |  |  | 0 | 521 | 481 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 52 | 8460 | 2014-02-11 08:00 | 2014-02-11 12:20 | 4.3333 |  |  | 0 | 330 | 299 | Wet Scrubber Testing | Particulate Matter Testing - Full Load
MC2 | NC | 53 | 1160 | 2014-02-11 12:21 | 2014-02-11 16:30 | 4.15 |  |  | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
CR5 | NC | 9 | 9999 | 2014-02-13 10:00 | 2014-02-13 14:00 | 4 |  |  | 0 | 181 | 168 | Total Unit Performance Testing | Full load winter capability test.
MC1 | NC | 28 | 8460 | 2014-02-11 12:45 | 2014-02-11 16:00 | 3.25 |  |  | 0 | 330 | 303 | Wet Scrubber Testing | Particulate Matter Testing
[10 empty] | 607 | 570
PR13 | PO | 4 | 4720 | 2014-02-15 06:08 | 2014-02-17 | 41.8667 | 41.8667 | 7326.6667 | 0 | 176 | 175 | Generator Synchronization Equipment | Generator synchronization equipment modifications. Replacing all generator protec
TC6 | MO | 30 | 5041 | 2014-02-04 11:33 | 2014-02-04 15:52 | 4.3167 | 4.3167 | 759.7333 | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Maintenance outage to change controller on Fuel Gas Worker Valve.
TC9 | U1 | 15 | 5041 | 2014-02-07 12:38 | 2014-02-07 15:35 | 2.95 | 2.95 | 519.2 | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Forced outage to address pressure swings due to worker fuel gas valve.
TC5 | U1 | 12 | 5079 | 2014-02-11 06:16 | 2014-02-11 08:35 | 2.3167 | 2.3167 | 407.7333 | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
BR7 | U1 | 12 | 5049 | 2014-02-10 17:14 | 2014-02-10 19:34 | 2.3333 | 2.3333 | 399 | 0 | 172 | 171 | Other Gas Turbine Fuel System Problems | Issue with pressure regulators in reducing station.
TC9 | D1 | 17 | 5041 | 2014-02-07 10:00 | 2014-02-07 12:38 | 2.6333 | 1.463 | 257.4815 | 80 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Derate to 80 MWs due to issue with worker fuel gas valve.
BR6 | MO | 10 | 5048 | 2014-02-04 06:30 | 2014-02-04 08:00 | 1.5 | 1.5 | 256.5 | 0 | 172 | 171 | Gas Fuel System with controls and instruments | Change cable for fuel gas flow meter RTD.
TC6 | U1 | 34 | 5079 | 2014-02-11 08:29 | 2014-02-11 09:45 | 1.2667 | 1.2667 | 222.9333 | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
HA1 | U1 | 9 | 3611 | 2014-02-08 02:53 | 2014-02-08 19:05 | 16.2 | 16.2 | 194.4 | 0 | 12 | 12 | Switchyard Circuit Breakers | Loss of power to 138KV sub.
HA2 | U1 | 4 | 3611 | 2014-02-08 02:53 | 2014-02-08 19:05 | 16.2 | 16.2 | 194.4 | 0 | 12 | 12 | Switchyard Circuit Breakers | Loss power to 138KV bus in substation
CR11 | U1 | 9 | 3840 | 2014-02-03 00:42 | 2014-02-03 09:37 | 8.9167 | 8.9167 | 124.8333 | 0 | 14 | 14 | Service Air Compressors | Clutch air compressor pumping up slowly - probably due to the weather.
TC6 | U1 | 33 | 5079 | 2014-02-11 06:16 | 2014-02-11 06:58 | 0.7 | 0.7 | 123.2 | 0 | 180 | 176 | Other Gas Turbine Combustor Problems | Unit tripped due to flameout.
TC5 | SF | 14 | 5130 | 2014-02-17 06:28 | 2014-02-17 06:40 | 0.2 | 0.2 | 35.2 | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to issue with LCI.
TC7 | U1 | 9 | 5160 | 2014-02-05 16:09 | 2014-02-05 16:17 | 0.13333 | 0.13333 | 23.4667 | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Unit rolled back to FSNL due to issue with pressure switch on Exhaust Frame Blower
TC7 | U1 | 8 | 5160 | 2014-02-05 16:03 | 2014-02-05 16:08 | 0.083333 | 0.083333 | 14.6667 | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Unit rolled back to FSNL due to issue with pressure switch on Exhaust Frame Blower
[10 empty] | 180 | 176

## e-mail table
| EFOR(steam) |  |  |  | EUOR(steam)
| Actual | Target | Var. # | Var. % | Actual | Target | Var. # | Var. %
Brown | 2.733% | 7.299% | -4.566% | -62.56% | 2.733% | 10.06% | -7.323% | -72.82%
Cane Run | 5.87% | 7.101% | -1.231% | -17.33% | 7.098% | 9.614% | -2.515% | -26.17%
Ghent | 0.8063% | 5% | -4.193% | -83.87% | 5.698% | 7.079% | -1.381% | -19.51%
Green River | 6.623% | 5.601% | 1.022% | 18.26% | 6.623% | 7.979% | -1.355% | -16.99%
Mill Creek | 2.45% | 4.997% | -2.547% | -50.97% | 5.408% | 7.076% | -1.668% | -23.57%
Trimble Co | 0.1717% | 3.899% | -3.727% | -95.6% | 0.1717% | 5.952% | -5.78% | -97.12%
TOTAL(stm) | 2.129% | 5.14% | -3.012% | -58.59% | 4.784% | 7.305% | -2.521% | -34.51%
EUOR(steam)
| Actual | Target | Var. # | Var. %
Brown | 2.733% | 10.06% | -7.323% | -72.82%
Cane Run | 7.098% | 9.614% | -2.515% | -26.17%
Ghent | 5.698% | 7.079% | -1.381% | -19.51%
Green River | 6.623% | 7.979% | -1.355% | -16.99%
Mill Creek | 5.408% | 7.076% | -1.668% | -23.57%
Trimble Co | 0.1717% | 5.952% | -5.78% | -97.12%
TOTAL(stm) | 4.784% | 7.305% | -2.521% | -34.51%
EAF(steam)
| Actual | Target | Var. # | Var. %
Brown | 97.27% | 93.1% | 4.166% | 4.474%
Cane Run | 93.29% | 92.23% | 1.056% | 1.145%
Ghent | 96.37% | 87.3% | 9.074% | 10.39%
Green River | 93.38% | 93.1% | 0.2788% | 0.2995%
Mill Creek | 95.12% | 92.91% | 2.205% | 2.374%
Trimble Co | 66.76% | 40.69% | 26.07% | 64.06%
TOTAL(stm) | 90.89% | 82.45% | 8.439% | 10.23%

## EFOR Contribution By Station
REGULATED (LG&E and KU) POWER GENERATION
CAPACITY WEIGHTED INTERIM EAF and EFOR REPORT
| FEBRUARY | 1 st | THROUGH |  | 16 | th
EFOR CONTRIBUTION BY UNIT
Station |  | Equiv. Hrs. |  | EFOR (Contribution) | % Of Total EFOR
0%
0%
|  | 0 |  | 0% | 0%

## Notes
Data come from query: CFC - Monthly Interim Rept - All Lg Units (adj dates) in MiCroGADS_Gold_Database
Color Coding | EventStart | EventEnd
D1 | 2011-10-01 | 2011-10-17
D3 |  | 2011-11-01
D4
IR
ME
MO
NC
PD
PO
SF
U1
U3