## Sheet1
DOOSAN MINI OUTAGE WORK SCOPE - 29-JUN-14 TO 04-JUL-14
# | Description | Forecast | Doosan Owner
1 | EC-SBR/Petrochem looking at burner front and PF splash plate insulation to reduce burner front temperatures | f/c = 03-Jul-14 for 1 burner on C row as Master Template f/c = TBC for balance of 29 (Post outage activity) | IK
2 | Doosan to Issue updated 5 pair oil gun tip testing program for cold start | f/c = 03-Jul-14…draft copy issued 2nd July 14 for review & comment by All | IK
3 | Review Economiser Feed Piping supports in cold position and cut & re-weld the stubs to address the issue of the valves bottoming out on level 6? | All NDE complete for re-welded stubs…procedure issued 02-Jul-14 for re-setting the piping supports, work to commence 03-Jul-14 ..f/c = 05-Jul-14 with insulation 'make good' to be completed post outage | RE / MW
3a | Need Bechtel confirmation that supports in their piping scope are correctly loaded | Bechtel action
3b | Verify support supporting the Economizer inlet line adjacent to the check valve is loaded correctly - The support number is 31311SSC001 | f/c survey = 03-Jul-14 as part of action plan issued for item # 3 | RE / MW
3c | Look to install Buckstay Markers | f/c = 03-Jul-14 as part of action plan issued for item # 3 | RE / MW
4 | Issue our email re Drain Pipe From the Small Start-up Vessel to the Boiler Drains Vessel (# 2-BLS-L879) and effect any repairs / check movement back in cold position | f/c response = 02-Jul-14..action plan issued for review 2nd July '14..work to commence and complete the reposition two pipe clamps 03-Jul-14, with insulation 'make good' to be completed post outage | CS /SH
5 | Logic updates
5a (8) | Doosan review and revision of logic associated with release of GAH soot blower system to warm pipework and blow GAH (enthalpy steam quality release set point) | 02-Jul-14: Logic implemented and LG&E comments returned to Crawley re DPII PLC address details | SH
5b (9) (16) | Following a review Doosan recommend switching off the Optimum damper position up to 80% Unit load and returning to a minimum crossover duct pressure of 2.6 “ wc. It will be a site activity to optimise the final minimum crossover duct pressure and the fuel rate to release the Optimum Damper Position Controller. | 02-Jul-14: Logic mtg held with LG&E and proposed changes are approved with the understanding that the crossover duct pressure setpoint will be raised in manual if we encounter issues with emissions during restart | SH
5c (10) | Doosan recommend that the new Enthalpy f(x) Set Point for sliding pressure mode mentioned in the e-mail sent by Kevin Maunder on 28-Jun-14, RE: 07292 TC2 - Logic Mark up re High Spray Flows and Enthalpy Control is implemented during the outage | 02-Jul-14: Logic mtg held with LG&E and approved implementing a move of 50% of the proposed value change. We will be restarting on 100% Riverview and will evaluate further with the unit on-line | SH
5d (11) | Doosan to review the cross-over duct pressure configuration modifications, testing and tuning suggested by David Lee to negate the Hydrojet impact on wind box / furnace pressure changes and if agreed recommend to LGE-KU for implementation | 02-Jul-14: Logic mtg held with LG&E and approve installing the proposed logic now without making it active. Upon the unit’s return to service, we will evaluate how the logic will perform if activated | SH
5e (12) | Ron Gratton to summarise revisions required to the DPII logic following the commissioning of the GAH soot blower steam system Doosan to verify that the GAH soot blower steam system operating philosophy is consistent with the finally commisioned system | Post outage activity | RG
5f (13) | Doosan to verify implementation of "Following Each MFT There Is a Period (5 minutes) During Which All Dampers Are Frozen", logic sheets issued by Chris Dukes on 30-Jun-14 | 01-Jul-14: Steve Hammond, Confirmed implementation as intended. | SH
5g (14) | LGE-KU to review and approve for implementation the fuel oil pressure control logic mark up sent by Paul Reynolds on 18-Jun-14, "07292A - Trimble County, Oil Gun Igniters, FUEL OIL PRESSURE CONTROL LOGIC MODIFICATION" | 02-Jul-14: Logic implemented and LG&E have issued sheets to Crawley for verification | SH
5h (15) | Doosan to review recent O2 dip seen when changing coal mills and recommend a logic revision to ensure this does not re-cur | 02-Jul-14: Logic implemented, Crawley have confirmed implementation as intended. | SH
6 | Verify thermocouple wiring to D3 PF upper and D4 PF lower is correct | 30Jun-14: Alan London, Thermocouples – D3 PF upper & D4 PF lower were removed, checked back to DCS at ambient. T/C heated and temperature rise noted. T/C replaced and reading close to others in the same location. E5 SA tip upper was found defective and was replaced. | JH/ AL
7 | Finalise Beck drive power / DCS cable routing on burner decks and replace all ‘nylon cable ties’ with metal P clips, as per Phil Rabe’s request last week..survey complete & materials on order | Materials on order and to be completed as post outage activity | RE / MW
8 | Reconcile and test flame scanners and check for faults / confirm how many are serviceable | 30-Jun-14: Alan London, Current known stock of flame scanners is: Coal – 6 x new scanners, Oil – 2 x new scanners and 1 x used. Others are being recovered from the I&E workshop for testing. | JH/ AL
9 | Doosan to investigate A3, B4 and C3 oil scanners | 01-Jul-14: Justin Heath, A3 & B4 flame monitors had their test cables removed and original ‘used’ cables re-fitted. Function checked and settings backed to Profile 0 / Set (High Load). C3 oil flame monitor has been fitted with a new cable. Functionality checks performed and settings backed to Profile 0 / Set (High Load). | JH/ AL
10 | Doosan to repair and refit Cegrit assemblies | f/c = 03-Jul-14….mechanically installed and power cable to be installed 03-Jul-14 | GJ
11 | Set mills A,B, D, & F core air damper minimum closed stops (to same position as C & E) | 01-Jul-14: Advised complete by Ron Gratton | RG
12 | Look to fit all upgrade hardened PF Orifice plates – Materials in the stores | Mechanically complete and Crawley to Issue size + location sheet and/or include in IO&M f/c = 04 Jul-14 | SH
13 | Complete OFA damper bearing and test point insulation | f/c = 04-Jul-14 Current status one coner complete, 3 corners WIP | RE / MW
14 | Complete installation of new valves on level 16 condensate pots and cap on vent line - Action EC-SBR & Mistras | Welding & NDE completed 02-Jul-14 | RE / IK
15 | OFA Port Rod adjustments – to eliminate the length variations that currently exist | Colour coded handles to be re-painted…Materials on order and to be completed as post outage activity | RE
16 | Complete fitting the PA / SA test probes | 01-Jul-14: Advised complete by Gareth Jones & scaffolds being removed | GJ
17 | Survey the GAH pipework system and supports now the unit has gone through start to hot and now back to cold and note if any issues with supports / pipe movements i.e. level 14 down to 2 | 01-Jul-14: David Farrow, This has been walked down from the 16th to the 2nd floor examining all supports / guides and spring hangers for the correct movement, or fouling etc. Nothing untoward was observed. | DF
18 | Survey F row PF lines re movement on lower cans back to cold positions | 01-Jul-14: David Farrow, This has been examined and the constant load supports have moved towards the cold set position to varying degrees. 01-Jul-14: David Bingham, Crawley Engineering have reviewed and believe that adjusting the pipework back to cold set position will have little benefit as during the next hot condition the same effect will happen again. | DF
19 | Take unit cold position readings on all the access ladders on the burner decks and mark on the ladders as completed with the unit in the hot position | Now complete with all Cold & Hot measurements marked on ladders…look to fit plate 3 position movement indicators f/c = 03-Jul-14 | DF
20 | Can we repair bound up Mech. Stops on CA damper - A row, investigate if we source spares parts ASAP from Tyco / MacJunkin? | Materials on order due by 8th July and to be completed as post outage activity | IK
21 | Take photo's of burner and OFA throats - Site access via 'dance floor' doors, LGE-KU to open and shut on completion | 01-Jul-14 both B&V and Bechtel photo's issued to all and further burner photos taken by Doosan issued 02 July '14 | RE
22 | LGE-KU to check out CO probes - A side as we understand from Devin that one appears to be flat lining? | LGE-KU action
23 | LGE-KU to look at A3 fuel oil valve | LGE-KU action
24 | LGE-KU to carry out further overhaul of purge air valves subject to repair kit availability - Rick Powell checking | LGE-KU action
25 | Doosan to issue revised copy of our D-NOx burner optimisation test program phases 1 – 7 to LGE-KU and Bechtel | f/c = 04-Jul-14 | JS / SH
26 | Doosan to demobilise Storm & FERCo personnel on 30-Jun-14, Storm to remobilise for dirty air testing, FERCo to remobilse Monday week | Demobilisation action complete | GJ
27 | Look at overall impact to our latest program as issued at the end of last week | f/c = 03-Jul-14 | AMac
28 | Gas Biasing Dampers - complete blade tip to tip measurements | LGE-KU action with Doosan support to re-set... f/c = 03-Jul-14
29 | Clean Burners / Decks from previous PF leaks - Burner #'s A1, B3, D3 & F1 | f/c = 04 Jul-14 but can be completed as post outage activity | RE / IK
30 | Clean Burner fronts / boiler cladding ledges - all elevations - Petrochem | f/c = 04-Jul-14 | RE / MW
31 | Complete modifications to boiler front lagging re PF pipe support clashes x 2 locations on A row - Petrochem | Completed 02-Jul-14 | RE / IK
32 | Modify Purge air pipe / PF support clash on A1 burner | Completed 02-Jul-14 | RE / IK
33 | Complete welding to toe plate on burner deck and remove misc wire support A Row | Completed nightshift 01 Jul-14 | RE / IK
34 | Test / check SCR Sonic horns & open SCR doors and review ash build up re new sweep system in place | LGE-KU action
35 | Open APH doors & inspect tops of baskets following lime injenction | Inspection completed all clean, some debris on top of the baskets
36 | Test / Check HP Spraywater suspect T/C on 6th level north wall previously reading 40 deg low | LGE-KU action f/c = 02 Jul-14
37 | F4 PF pipework clash with instrument air - A deck | 01-Jul-14: Advised complete by Rob Elliott | RE
38 | Complete transfer of LG&E burner inventory from warehouse B | f/c = 04-Jul-14…current status Ignitor parts, burner gaskets & T/C's still to move | MC / IK
39 | Level 4 Scanner / DCS room - clean out outage debris | f/c = 03-Jul -14 | RE / MW
40 | Investigate NW corner OFA suspected duct leak | Completed internal duct inspections and underside duct survey, no weld defects / gaps found | MW
41 | Clean tops of SA ducting - top burner deck re previously underside of the OFA ducting was re-lagged - Petrochem | f/c = 04-Jul-14 | RE / MW
42 | SA Ducting insulation interference with C4 PF pipe hanger on the 5th Floor - Petrochem | f/c = 03-Jul -14 | RE / MW
43 | F1 Burner PF scanner cooling air hose interference with core air insulation jacket | Completed 02-Jul-14 | RE / MW
44 | Burner A4 Core air pipe interference with burner F3 PF pipe support hanger rod | f/c = 03-Jul -14 | RE / MW