## LGEData
SorF | UnitName | EventType | EventNo | CauseCode | EventStart | EventEnd | Duration_Hrs | Cause | eventDescription
F | TC1 | U1 | 12 | 9900 | 2014-01-11 21:03 | 2014-01-12 07:57 | 10.9 | Operator Error | F820During load drop, operator error in valve closing caused the TDBFP main extraction
S | TC10 | MO | 121 | 5130 | 2013-12-18 08:37 | 2013-12-18 20:45 | 12.13 | Gas Turbine - Starting System (including Motor) | F340Maintenance outage to address 89SS issues.
F | TC10 | U1 | 123 | 5130 | 2013-12-19 01:23 | 2013-12-19 16:07 | 14.73 | Gas Turbine - Starting System (including Motor) | F340Forced outage due to 89SS issue.
S | TC10 | MO | 62 | 5130 | 2014-04-10 08:28 | 2014-04-10 16:05 | 7.62 | Gas Turbine - Starting System (including Motor) | F340Adjustment made to TC9 and TC10 89SS cam limit switches.
S | TC10 | SF | 78 | 5130 | 41757.2625 | 41757.541 | 6.68 | Gas Turbine - Starting System (including Motor) | F34089SS failed to disengage, Adjustments made to linkage.
S | TC2 | PO | 20 | 360 | 2014-02-08 03:21 | 2014-05-26 | 2564.65 | Burners | F610TC2 began the planned outage for the replacement of all 30 burners. This effort i
F | TC8 | U1 | 9 | 3869 | 2014-01-10 14:00 | 2014-01-14 13:28 | 95.47 | Other Fire Protection System Problems | F660Forced outage due to issue with Fire Protection System.