## LGEData
SorF | UnitName | EventType | EventNo | CauseCode | EventStart | EventEnd | Duration_Hrs | Cause | eventDescription | Response
F | TC1 | U1 | 12 | 9900 | 2014-01-11 21:03 | 2014-01-12 07:57 | 10.9 | Operator Error | F820During load drop, operator error in valve closing caused the TDBFP main extraction | Unit load was dropped due to system load conditions. When dropping load the operator intended to take the 1A TDBFP out of service. The low pressure steam supply valve to the turbine needed to be closed and a close was initiated on 1MOV-003 (the common steam supply to both the 1A and 1B TDBFPTs) instead of 1MOV-002, which would have isolated the 1A BFPT only. The DCS graphics show valve 1MOV-003 on both the 1A and 1B feed pump screens, and did not represent a line crossing over to the other feed pump. The DCS graphics have since been updated and all unit operators have been tailgated.
S | TC10 | MO | 121 | 5130 | 2013-12-18 08:37 | 2013-12-18 20:45 | 12.13 | Gas Turbine - Starting System (including Motor) | F340Maintenance outage to address 89SS issues. | all of these outages were similar in nature and were caused by the gas turbine electrical startup drive mechanically operated disconnect switches. Over time the switches became worn and out of alignment. Multiple adjustments and tightening of linkages were required to address the issue. In addition to adjustment of the mechanical linkages and limits, a variable speed drive for the motor operator was adjusted to prevent over driving the disconnect blade into the reciever. This has further helped with binding issues.
F | TC10 | U1 | 123 | 5130 | 2013-12-19 01:23 | 2013-12-19 16:07 | 14.73 | Gas Turbine - Starting System (including Motor) | F340Forced outage due to 89SS issue.
S | TC10 | MO | 62 | 5130 | 2014-04-10 08:28 | 2014-04-10 16:05 | 7.62 | Gas Turbine - Starting System (including Motor) | F340Adjustment made to TC9 and TC10 89SS cam limit switches.
S | TC10 | SF | 78 | 5130 | 41757.2625 | 41757.541 | 6.68 | Gas Turbine - Starting System (including Motor) | F34089SS failed to disengage, Adjustments made to linkage.
S | TC2 | PO | 20 | 360 | 2014-02-08 03:21 | 2014-05-26 | 2564.65 | Burners | F610TC2 began the planned outage for the replacement of all 30 burners. This effort i | This work was to address emmissions issues and reliability issues which have occurred since TC2 was constructed. While previous attempts to solve issues with the burners were performed, they involved modifications to the originally supplied burners and had limited sucess. The burner installed during this outage was a newly designed burner with more control features along with a new burner throat. The new burner has performed much better from an emmissions standpoint, and has yet to experience an issue with burner overheating. Final testing and tuning of the current burner is on track to be completed in October of this year. The burner replacement was on schedule.
F | TC8 | U1 | 9 | 3869 | 2014-01-10 14:00 | 2014-01-14 13:28 | 95.47 | Other Fire Protection System Problems | F660Forced outage due to issue with Fire Protection System. | The C02 fire protection system was out of service due to issues with the cooling system on the fire protection. The cooling system failed and allowed the c02 to heat up and expand. When the c02 expands the system will vent off using a safety valve to protect the storage tank. We had the HVAC repair company make repairs to the cooling system (Installed a new thermal expansion valve) and recharge the system with Freon. When the cooling system was back up and running we ordered c02 to refill the system and make the unit back available. We will not run the units when the c02 system is below 4% in the tank; it requires a minimum of 4% to extinguish a fire in any one compartment area in case of emergency.