## MAR-14 Impact By Unit
Dated: 04/01/14 14:00 hours | [16 empty] | EAF | EUOR | EFOR
Denominator
Unit | Event | Event | Cause | Event | Event | Evt. | Equiv. | MWH | EAF | EUOR | EFOR |  |  |  | Event | Event
Name | Type | No | Code | Start | End | Hrs | Dur Hrs | Lost | Lost | Impact | Impact | GAC | GMC | NMC | Cause | Description | 4289160 | 3227171.1845 | 3206756.3455
BR1 | D1 | 6 | 280 | 2014-03-04 09:56 | 2014-03-04 13:25 | 3.4833 | 1.0389 | 110.1222 | 0.002567% | 0.003412% | 0.003434% | 80 | 114 | 106 | Pulverizer Fires | 1-3 mill pyrite fire 6548834
BR1 | NC | 7 | 9656 | 2014-03-11 11:42 | 2014-03-11 16:08 | 4.4333 | [5 empty] | 0 | 114 | 106 | Other stack or exhaust emissions testing - fossil | Low load RATA testing
BR1 | D1 | 8 | 310 | 2014-03-13 10:15 | 2014-03-13 13:45 | 3.5 | 1.0439 | 110.6491 | 0.00258% | 0.003429% | 0.00345% | 80 | 114 | 106 | Pulverizer Mills | 1-4 mill tripped due to air flow issues 6552310
BR1 | D1 | 9 | 310 | 2014-03-17 06:32 | 2014-03-17 07:27 | 0.91667 | 0.23319 | 24.7178 | 0.0005763% | 0.0007659% | 0.0007708% | 85 | 114 | 106 | Pulverizer Mills | 1-4 mill air flow erratic 6552310
BR1 | D1 | 10 | 9205 | 2014-03-18 08:37 | 2014-03-18 10:37 | 2 | 0.12281 | 13.0175 | 0.0003035% | 0.0004034% | 0.0004059% | 107 | 114 | 106 | Poor quality fuel; heat content | Limited by coal quality
BR1 | D1 | 11 | 9205 | 2014-03-18 10:37 | 2014-03-18 10:51 | 0.23333 | 0.0040936 | 0.43392 | 1.012e-05% | 1.345e-05% | 1.353e-05% | 112 | 114 | 106 | Poor quality fuel; heat content | Limited by coal quality
[13 empty] | 114 | 107
BR1 | [5 empty] | 14.5667 | 2.4428 | 258.9406 | 0.006037% | 0.008024% | 0.008075%
D4
PD
BR2 | MO | 15 | 8560 | 2014-02-28 12:26 | 2014-03-02 18:19 | 53.8833 | 53.8833 | 9052.4 | 0.2111% | 0.2805% |  | 0 | 180 | 168 | Electrostatic Precipitator Problems | Precipitator fields out of service and tube leak repair 6546848
BR2 | D1 | 16 | 310 | 2014-03-02 20:15 | 2014-03-03 07:22 | 11.1167 | 3.088 | 518.7778 | 0.0121% | 0.01608% | 0.01618% | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
BR2 | D1 | 17 | 3410 | 2014-03-03 07:22 | 2014-03-06 16:50 | 81.4667 | 33.9444 | 5702.6667 | 0.133% | 0.1767% | 0.1778% | 105 | 180 | 168 | Feedwater Pump | 2-2 BFP oil leak 6546733
BR2 | D1 | 18 | 310 | 2014-03-06 16:50 | 2014-03-06 19:00 | 2.1667 | 0.60185 | 101.1111 | 0.002357% | 0.003133% | 0.003153% | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
BR2 | PD | 19 | 310 | 2014-03-06 19:00 | 2014-03-08 07:40 | 36.6667 | 10.1852 | 1711.1111 | 0.03989% |  |  | 130 | 180 | 168 | Pulverizer Mills | 2-3 mill thrust bearing replacement 6529384
BR2 | U1 | 20 | 1040 | 2014-03-10 14:50 | 2014-03-11 21:09 | 30.3167 | 30.3167 | 5093.2 | 0.1187% | 0.1578% | 0.1588% | 0 | 180 | 168 | First Superheater Leaks | Tube leak in boiler penthouse area. 6550561
BR2 | D1 | 21 | 350 | 2014-03-27 09:06 | 2014-03-27 10:05 | 0.98333 | 0.1912 | 32.1222 | 0.0007489% | 0.0009954% | 0.001002% | 145 | 180 | 168 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | 2-2 mill burner line temperature high
BR2 | D1 | 22 | 350 | 2014-03-27 10:31 | 2014-03-27 13:13 | 2.7 | 0.525 | 88.2 | 0.002056% | 0.002733% | 0.00275% | 145 | 180 | 168 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | 2-2 mill burner line temperature high
BR2 | D1 | 23 | 350 | 2014-03-27 14:25 | 2014-03-27 14:47 | 0.36667 | 0.071296 | 11.9778 | 0.0002793% | 0.0003712% | 0.0003735% | 145 | 180 | 168 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | Inspect 2-1A burner line for pluggage
[13 empty] | 180 | 168
BR2 | [5 empty] | 219.6667 | 132.8069 | 22311.5667 | 0.5202% | 0.6383% | 0.3601%
D4
PD
BR3 | NC | 13 | 9656 | 2014-03-11 11:42 | 2014-03-11 13:51 | 2.15 | [5 empty] | 0 | 457 | 414 | Other stack or exhaust emissions testing - fossil | Low load RATA testing
BR3 | D1 | 14 | 310 | 2014-03-11 13:51 | 2014-03-11 15:36 | 1.75 | 0.40974 | 169.6313 | 0.003955% | 0.005256% | 0.00529% | 350 | 457 | 414 | Pulverizer Mills | 3-1 mill broken spring bolt 6550819
BR3 | NC | 15 | 9656 | 2014-03-11 15:36 | 2014-03-11 16:08 | 0.53333 | [5 empty] | 0 | 457 | 414 | Other stack or exhaust emissions testing - fossil | Low load RATA testing
BR3 | NC | 16 | 9656 | 2014-03-12 08:45 | 2014-03-12 20:38 | 11.8833 | [5 empty] | 0 | 457 | 414 | Other stack or exhaust emissions testing - fossil | RATA testing at 425 mw.
BR3 | NC | 17 | 9656 | 2014-03-13 12:30 | 2014-03-13 17:00 | 4.5 | [5 empty] | 0 | 457 | 414 | Other stack or exhaust emissions testing - fossil | RATA testing at 425 mw.
BR3 | D1 | 18 | 740 | 2014-03-17 14:15 | 2014-03-18 | 9.75 | 0.57604 | 238.4803 | 0.00556% | 0.00739% | 0.007437% | 430 | 457 | 414 | Boiler Recirculation Pumps | 3-1 BCWP out of service
BR3 | D1 | 19 | 740 | 2014-03-19 10:13 | 2014-03-19 10:32 | 0.31667 | 0.27717 | 114.7484 | 0.002675% | 0.003556% | 0.003578% | 57 | 457 | 414 | Boiler Recirculation Pumps | Boiler trip due to BCWP differential pressure
BR3 | U1 | 20 | 740 | 2014-03-19 10:32 | 2014-03-19 12:29 | 1.95 | 1.95 | 807.3 | 0.01882% | 0.02502% | 0.02517% | 0 | 457 | 414 | Boiler Recirculation Pumps | Boiler trip due to BCWP differential pressure
BR3 | D1 | 21 | 310 | 2014-03-19 21:47 | 2014-03-19 23:04 | 1.2833 | 0.30047 | 124.3963 | 0.0029% | 0.003855% | 0.003879% | 350 | 457 | 414 | Pulverizer Mills | 3-5 mill explosion
BR3 | U1 | 22 | 310 | 2014-03-19 23:04 | 2014-03-21 06:05 | 31.0167 | 31.0167 | 12840.9 | 0.2994% | 0.3979% | 0.4004% | 0 | 457 | 414 | Pulverizer Mills | 3-5 mill explosion, damage inspection and repair
BR3 | D1 | 23 | 310 | 2014-03-21 11:20 | 2014-03-21 16:28 | 5.1333 | 1.3142 | 544.0884 | 0.01269% | 0.01686% | 0.01697% | 340 | 457 | 414 | Pulverizer Mills | 3-5 mill post explosion calibrations and inspections
BR3 | D1 | 24 | 310 | 2014-03-21 16:28 | 2014-03-24 10:30 | 66.0333 | 5.3462 | 2213.3449 | 0.0516% | 0.06858% | 0.06902% | 420 | 457 | 414 | Pulverizer Mills | High exhauster to furnance pressure due to 3-5D burner out of service.
BR3 | D1 | 25 | 310 | 2014-03-24 10:30 | 2014-03-24 10:43 | 0.21667 | 0.057841 | 23.9462 | 0.0005583% | 0.000742% | 0.0007467% | 335 | 457 | 414 | Pulverizer Mills | 3-3 mill exhauster bearing high vibration
BR3 | D1 | 26 | 310 | 2014-03-24 10:43 | 2014-03-25 07:04 | 20.35 | 1.6476 | 682.1035 | 0.0159% | 0.02114% | 0.02127% | 420 | 457 | 414 | Pulverizer Mills | High exhauster to furnance pressure due to 3-5D burner out of service.
BR3 | D1 | 27 | 350 | 2014-03-25 07:04 | 2014-03-25 11:00 | 3.9333 | 1.05 | 434.7151 | 0.01014% | 0.01347% | 0.01356% | 335 | 457 | 414 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | 3-5A burner line coal leak
BR3 | D1 | 28 | 350 | 2014-03-25 11:00 | 2014-03-25 12:06 | 1.1 | 0.26958 | 111.6079 | 0.002602% | 0.003458% | 0.00348% | 345 | 457 | 414 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | 3-5A burner line coal leak
BR3 | D1 | 29 | 310 | 2014-03-25 12:06 | 2014-03-28 23:33 | 83.45 | 6.7563 | 2797.1271 | 0.06521% | 0.08667% | 0.08723% | 420 | 457 | 414 | Pulverizer Mills | High exhauster to furnance pressure due to 3-5D burner out of service.
BR3 | PO | 30 | 1801 | 2014-03-28 23:33 | 2014-04-01 | 72.4497 | 72.4497 | 29994.185 | 0.6993% |  |  | 0 | 457 | 414 | Minor Boiler Overhaul (less than 720 Hours) | Planned spring outage
[13 empty] | 457 | 414
BR3 | [5 empty] | 317.7997 | 123.4217 | 51096.5743 | 1.191% | 0.6539% | 0.6581%
D4
PD
CR4 | D4 | 13 | 344 | 2014-02-28 22:00 | 2014-03-01 06:51 | 8.85 | 2.0018 | 310.2768 | 0.007234% | 0.009615% |  | 130 | 168 | 155 | Pulverizer Inspection | 4A Mill inspection
CR4 | D4 | 14 | 315 | 2014-03-05 23:09 | 2014-03-06 01:25 | 2.2667 | 0.5127 | 79.4683 | 0.001853% | 0.002462% |  | 130 | 168 | 155 | Pulverizer Coal Level Controls | 4A Mill - broken purge air line on bowl differential pressure indication was repa
CR4 | D1 | 15 | 310 | 2014-03-10 06:35 | 2014-03-11 00:58 | 18.3833 | 4.7053 | 729.315 | 0.017% | 0.0226% | 0.02274% | 125 | 168 | 155 | Pulverizer Mills | 4C Coal mill (roller) - #3 journal bad bearing
CR4 | NC | 16 | 1160 | 2014-03-18 22:30 | 2014-03-19 03:50 | 5.3333 | [5 empty] | 0 | 168 | 155 | First Reheater Slagging or Fouling | Boiler deslag
CR4 | NC | 17 | 1160 | 2014-03-19 22:00 | 2014-03-20 03:20 | 5.3333 | [5 empty] | 0 | 168 | 155 | First Reheater Slagging or Fouling | Boiler deslag
CR4 | D1 | 18 | 8000 | 2014-03-23 20:18 | 2014-03-23 20:29 | 0.18333 | 0.041468 | 6.4276 | 0.0001499% | 0.0001992% | 0.0002004% | 130 | 168 | 155 | Chemical Feed Storage; Mill Feeders And Conveyors | B LST tank solids buildup
CR4 | MO | 19 | 3110 | 2014-03-24 20:40 | 2014-03-25 18:55 | 22.25 | 22.25 | 3448.75 | 0.08041% | 0.1069% |  | 0 | 168 | 155 | Condenser Tube Leaks | Unit removed from service due to high silica. Root cause is from condenser tube l
CR4 | D1 | 20 | 1160 | 2014-03-26 22:00 | 2014-03-27 03:15 | 5.25 | 2.75 | 426.25 | 0.009938% | 0.01321% | 0.01329% | 80 | 168 | 155 | First Reheater Slagging or Fouling | Load limit to clean up boiler slag around the 7R and 5R retract area.
CR4 | NC | 21 | 1160 | 2014-03-27 23:00 | 2014-03-28 04:10 | 5.1667 | [5 empty] | 0 | 168 | 155 | First Reheater Slagging or Fouling | Load limit to clean up boiler slag around the 7R and 5R retract area.
[13 empty] | 168 | 155
CR4 | [5 empty] | 73.0167 | 32.2612 | 5000.4876 | 0.1166% | 0.1549% | 0.03624%
D4
PD
CR5 | D4 | 11 | 1980 | 2014-03-06 21:15 | 2014-03-06 22:56 | 1.6833 | 0.28831 | 48.4354 | 0.001129% | 0.001501% |  | 150 | 181 | 168 | Boiler Safety Valve Test | Precision Services testing & inspecting safety valves
CR5 | PO | 12 | 1060 | 2014-03-07 12:53 | 2014-03-15 23:00 | 202.1167 | 202.1167 | 33955.6 | 0.7917% |  |  | 0 | 181 | 168 | First Reheater Leaks | Boiler tube inspection and repairs. Three reheat leaks were discovered upon inspe
CR5 | MO | 13 | 1160 | 2014-03-18 10:07 | 2014-03-19 16:52 | 30.75 | 30.75 | 5166 | 0.1204% | 0.1601% |  | 0 | 181 | 168 | First Reheater Slagging or Fouling | Replaced 1 reheat tube with dutchman.
CR5 | D1 | 14 | 344 | 2014-03-21 23:21 | 2014-03-22 01:35 | 2.2333 | 0.62928 | 105.7193 | 0.002465% | 0.003276% | 0.003297% | 130 | 181 | 168 | Pulverizer Inspection | Checked 5B coal mill air chamber for buildup.
CR5 | D1 | 15 | 8000 | 2014-03-23 20:16 | 2014-03-23 20:29 | 0.21667 | 0.025138 | 4.2232 | 9.846e-05% | 0.0001309% | 0.0001317% | 160 | 181 | 168 | Chemical Feed Storage; Mill Feeders And Conveyors | B LST tank solids buildup
[13 empty] | 181 | 168
CR5 | [5 empty] | 237 | 233.8094 | 39279.9779 | 0.9158% | 0.165% | 0.003428%
D4
PD
CR6 | D1 | 17 | 310 | 2014-03-05 14:16 | 2014-03-05 20:35 | 6.3167 | 1.4763 | 354.3142 | 0.008261% | 0.01098% | 0.01105% | 200 | 261 | 240 | Pulverizer Mills | 6A Mill broken mill sweep - replaced damaged parts.
CR6 | D1 | 18 | 8199 | 2014-03-08 05:11 | 2014-03-08 08:18 | 3.1167 | 0.52542 | 126.0996 | 0.00294% | 0.003907% | 0.003932% | 217 | 261 | 240 | Other Wet Scrubber Problems | SO2 excursion during load pickup. Contributing factors were the 6B reaction tank
CR6 | D1 | 19 | 310 | 2014-03-08 15:15 | 2014-03-09 09:27 | 18.2 | 3.905 | 937.1954 | 0.02185% | 0.02904% | 0.02923% | 205 | 261 | 240 | Pulverizer Mills | 6D Mill - #2 journal broken shaft
CR6 | D1 | 20 | 8110 | 2014-03-10 10:15 | 2014-03-10 12:13 | 1.9667 | 0.30894 | 74.1456 | 0.001729% | 0.002298% | 0.002312% | 220 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
CR6 | D1 | 21 | 8110 | 2014-03-10 20:31 | 2014-03-10 21:11 | 0.66667 | 0.05364 | 12.8736 | 0.0003001% | 0.0003989% | 0.0004015% | 240 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
CR6 | D1 | 22 | 8110 | 2014-03-11 06:11 | 2014-03-11 07:36 | 1.4167 | 0.16826 | 40.3831 | 0.0009415% | 0.001251% | 0.001259% | 230 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
CR6 | D1 | 23 | 8110 | 2014-03-11 07:36 | 2014-03-11 09:26 | 1.8333 | 0.35824 | 85.977 | 0.002005% | 0.002664% | 0.002681% | 210 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
CR6 | D1 | 24 | 8110 | 2014-03-11 09:26 | 2014-03-11 11:18 | 1.8667 | 0.72235 | 173.364 | 0.004042% | 0.005372% | 0.005406% | 160 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
CR6 | U1 | 25 | 8100 | 2014-03-11 11:19 | 2014-03-12 19:03 | 31.7333 | 31.7333 | 7616 | 0.1776% | 0.236% | 0.2375% | 0 | 261 | 240 | Wet Scrubber/absorber Tower Or Module | FGD module cleaning - solids buildup in module spray header, resulting from incons
CR6 | D1 | 26 | 3415 | 2014-03-13 04:58 | 2014-03-13 05:55 | 0.95 | 0.40402 | 96.9655 | 0.002261% | 0.003005% | 0.003024% | 150 | 261 | 240 | Feedwater Pump/Drive Lube Oil System | Lube oil pressure indication low
CR6 | NC | 27 | 1980 | 2014-03-13 21:13 | 2014-03-14 00:18 | 3.0833 | [5 empty] | 0 | 261 | 240 | Boiler Safety Valve Test | Electrostatic boiler valve safety testing (pre outage).
CR6 | PO | 28 | 8199 | 2014-03-14 23:44 | 2014-03-30 19:27 | 379.7167 | 379.7167 | 91132 | 2.125% |  |  | 0 | 261 | 240 | Other Wet Scrubber Problems | Total replacement of thickener tank center well ring.
CR6 | U1 | 29 | 3669 | 2014-03-31 08:13 | 2014-03-31 13:34 | 5.35 | 5.35 | 1284 | 0.02994% | 0.03979% | 0.04004% | 0 | 261 | 240 | Other 4000-7000-volt Problems | I/E personnel inadvertently cold transfered the 4KV A Buse power supply.
CR6 | D1 | 30 | 310 | 2014-03-31 20:24 | 2014-04-01 | 3.5997 | 0.56547 | 135.7137 | 0.003164% | 0.004205% | 0.004232% | 220 | 261 | 240 | Pulverizer Mills | 6C Coal Mill explosion during post unit trip. Burning mill out.
[13 empty] | 261 | 240
CR6 | [5 empty] | 459.8164 | 425.2876 | 102069.0317 | 2.38% | 0.3389% | 0.3411%
D4
PD
GH1 | D1 | 16 | 250 | 2014-03-03 16:05 | 2014-03-03 22:16 | 6.1833 | 0.68172 | 327.908 | 0.007645% | 0.01016% | 0.01023% | 460 | 517 | 481 | Pulverizer Feeders | 1-3 Feeder belt failed. Removed from service to replace belt.
GH1 | U1 | 17 | 1000 | 2014-03-05 00:42 | 2014-03-05 23:00 | 22.3 | 22.3 | 10726.3 | 0.2501% | 0.3324% | 0.3345% | 0 | 517 | 481 | Furnace Wall Leaks | Water water tube leak blew out on the upper slope of the boiler about 15
GH1 | D1 | 18 | 346 | 2014-03-17 07:42 | 2014-03-17 12:14 | 4.5333 | 0.49981 | 240.407 | 0.005605% | 0.007449% | 0.007497% | 460 | 517 | 481 | Pulverizer Pyrite Removal System | 1-3 Mill out of service to inspect pyrite section.
GH1 | PO | 19 | 1812 | 2014-03-21 21:30 | 2014-04-01 | 242.4997 | 242.4997 | 116642.3664 | 2.719% |  |  | 0 | 517 | 481 | Boiler Inspections - Scheduled or Routine | Unit 1 scheduled for a Planned Spring Outage. Removed the unit from
[13 empty] | 517 | 481
GH1 | [5 empty] | 275.5164 | 265.9813 | 127936.9814 | 2.983% | 0.35% | 0.3522%
D4
PD
GH2 | PD | 15 | 345 | 2014-03-06 12:00 | 2014-03-07 22:07 | 34.1167 | 3.2843 | 1566.6186 | 0.03653% |  |  | 460 | 509 | 477 | Pulverizer Overhaul | 2-4 Mill out of service for scheduled overhaul.
GH2 | PO | 16 | 1812 | 2014-03-07 22:07 | 2014-03-21 11:04 | 324.95 | 324.95 | 155001.15 | 3.614% |  |  | 0 | 509 | 477 | Boiler Inspections - Scheduled or Routine | Unit 2 scheduled for Planned Spring Outage. Removed the unit
GH2 | PD | 17 | 345 | 2014-03-21 11:05 | 2014-03-27 12:02 | 144.95 | 13.9539 | 6656.0243 | 0.1552% |  |  | 460 | 509 | 477 | Pulverizer Overhaul | 2-4 Mill out of service for overhaul.
GH2 | D1 | 18 | 1850 | 2014-03-21 19:34 | 2014-03-22 06:10 | 10.6 | 3.3112 | 1579.4417 | 0.03682% | 0.04894% | 0.04925% | 350 | 509 | 477 | Boiler Water Condition (not Feedwater Water Quality) | Boiler water chemistry - high silica during start up.
GH2 | D1 | 19 | 890 | 2014-03-29 11:16 | 2014-03-29 15:40 | 4.4 | 0.76935 | 366.9807 | 0.008556% | 0.01137% | 0.01144% | 420 | 509 | 477 | Bottom Ash Systems (Wet or Dry) | Unit 2 was derated due to wet ash system pluggage.
[13 empty] | 509 | 477
GH2 | [5 empty] | 519.0167 | 346.2688 | 165170.2152 | 3.851% | 0.06031% | 0.0607%
D4
PD
GH3 | PD | 23 | 9650 | 2014-02-28 22:30 | 2014-03-01 03:08 | 4.6333 | 2.6112 | 1258.5962 | 0.02934% |  |  | 230 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. Working on sorbent blower.
GH3 | D1 | 24 | 9650 | 2014-03-02 18:15 | 2014-03-02 21:00 | 2.75 | 0.82448 | 397.3985 | 0.009265% | 0.01231% | 0.01239% | 369 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. Low level on Silo feeding outlet i
GH3 | D1 | 25 | 9650 | 2014-03-05 07:08 | 2014-03-05 08:03 | 0.91667 | 0.25569 | 123.2438 | 0.002873% | 0.003819% | 0.003843% | 380 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | H2SO4 running high due to outlet injection probe pluggage. Redu
GH3 | D1 | 26 | 9650 | 2014-03-05 17:28 | 2014-03-06 01:30 | 8.0333 | 1.1738 | 565.7479 | 0.01319% | 0.01753% | 0.01764% | 450 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2S04 within limit. Outlet injection lines plugged.
GH3 | D1 | 27 | 9650 | 2014-03-07 04:20 | 2014-03-07 06:05 | 1.75 | 0.42173 | 203.2723 | 0.004739% | 0.006299% | 0.006339% | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. 3-2B Blow through valve drive chain
GH3 | D1 | 28 | 9650 | 2014-03-07 07:30 | 2014-03-07 08:00 | 0.5 | 0.011385 | 5.4877 | 0.0001279% | 0.00017% | 0.0001711% | 515 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2S04 within limit. 3-2 Blow through drive chain valve
GH3 | D1 | 29 | 1400 | 2014-03-07 19:29 | 2014-03-07 23:10 | 3.6833 | 0.069892 | 33.6882 | 0.0007854% | 0.001044% | 0.001051% | 517 | 527 | 482 | Forced Draft Fans | FD fans out the top.
GH3 | D1 | 30 | 1400 | 2014-03-08 19:35 | 2014-03-09 05:28 | 9.8833 | 0.16879 | 81.3546 | 0.001897% | 0.002521% | 0.002537% | 518 | 527 | 482 | Forced Draft Fans | FD Fans out the top.
GH3 | D1 | 31 | 280 | 2014-03-13 22:40 | 2014-03-13 23:45 | 1.0833 | 0.1994 | 96.1104 | 0.002241% | 0.002978% | 0.002997% | 430 | 527 | 482 | Pulverizer Fires | 3-5 Mill fire.
GH3 | D1 | 32 | 9650 | 2014-03-14 03:36 | 2014-03-14 05:18 | 1.7 | 0.03871 | 18.6581 | 0.000435% | 0.0005782% | 0.0005818% | 515 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limits, ID Fan Injection Outlets plugged.
GH3 | D1 | 33 | 1400 | 2014-03-14 05:18 | 2014-03-14 09:57 | 4.65 | 0.017647 | 8.5059 | 0.0001983% | 0.0002636% | 0.0002652% | 525 | 527 | 482 | Forced Draft Fans | FD Fan Limit, 3-1 FD Fan Inlet Vane needs attention.
GH3 | D1 | 34 | 9650 | 2014-03-14 09:57 | 2014-03-14 11:08 | 1.1833 | 0.08308 | 40.0447 | 0.0009336% | 0.001241% | 0.001249% | 490 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO3 within limit. ID Fan Outlet Injection plugged.
GH3 | D1 | 35 | 1400 | 2014-03-14 11:08 | 2014-03-14 12:26 | 1.3 | 0.017268 | 8.323 | 0.000194% | 0.0002579% | 0.0002595% | 520 | 527 | 482 | Forced Draft Fans | FD Fan Limit, 3-1 ID Fan Vane needs attention.
GH3 | D1 | 36 | 9650 | 2014-03-14 12:26 | 2014-03-15 05:15 | 16.8167 | 2.3294 | 1122.7917 | 0.02618% | 0.03479% | 0.03501% | 454 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. ID Fan Outlet Injection plugged.
GH3 | D1 | 37 | 9650 | 2014-03-15 06:24 | 2014-03-15 10:54 | 4.5 | 0.31594 | 152.2827 | 0.00355% | 0.004719% | 0.004749% | 490 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. ID Faan Outlet Injection plugged.
GH3 | D1 | 38 | 9650 | 2014-03-17 09:30 | 2014-03-17 11:03 | 1.55 | 0.37353 | 180.0412 | 0.004198% | 0.005579% | 0.005614% | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2So4 within limit. 3-2B Drop Through Rotary valve driv
GH3 | D1 | 39 | 1400 | 2014-03-19 06:00 | 2014-03-20 07:00 | 25 | 0.80645 | 388.7097 | 0.009063% | 0.01204% | 0.01212% | 510 | 527 | 482 | Forced Draft Fans | FD Fan limit, 3-1 FD Fan Inlet Vane needs attention.
GH3 | D1 | 40 | 280 | 2014-03-25 08:39 | 2014-03-25 09:56 | 1.2833 | 0.15098 | 72.7725 | 0.001697% | 0.002255% | 0.002269% | 465 | 527 | 482 | Pulverizer Fires | 3-5 Mill fire in top of the mill.
GH3 | D1 | 41 | 9650 | 2014-03-25 11:38 | 2014-03-25 12:35 | 0.95 | 0.1388 | 66.9038 | 0.00156% | 0.002073% | 0.002086% | 450 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit. Inlet probes were plug
GH3 | PD | 42 | 855 | 2014-03-26 22:00 | 2014-03-27 00:36 | 2.6 | 0.20721 | 99.8755 | 0.002329% |  |  | 485 | 527 | 482 | Boiler Drum Relief/Safety Valves | Precision to set drum safeties.
GH3 | PO | 43 | 1800 | 2014-03-28 22:07 | 2014-04-01 | 73.8831 | 73.8831 | 35611.6328 | 0.8303% |  |  | 0 | 527 | 482 | Major Boiler Overhaul (720 Hours or Longer) | Unit 3 is scheduled for a Planned Spring Outage. Removed the unit fr
[13 empty] | 527 | 482
GH3 | [5 empty] | 168.6497 | 84.0984 | 40535.4411 | 0.9451% | 0.1105% | 0.1112%
D4
PD
GH4 | D1 | 9 | 9650 | 2014-03-05 17:35 | 2014-03-05 18:09 | 0.56667 | 0.089139 | 43.767 | 0.00102% | 0.001356% | 0.001365% | 450 | 534 | 491 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Temporary lime silo plugged at mixer.
GH4 | D1 | 10 | 9650 | 2014-03-05 20:48 | 2014-03-05 22:01 | 1.2167 | 0.077466 | 38.0356 | 0.0008868% | 0.001179% | 0.001186% | 500 | 534 | 491 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Temporary lime silo plugged at mixer.
GH4 | D1 | 11 | 3440 | 2014-03-24 08:44 | 2014-03-26 02:30 | 41.7667 | 1.7989 | 883.279 | 0.02059% | 0.02737% | 0.02754% | 511 | 534 | 491 | High Pressure Heater Tube Leaks | HP heaters are out of service to repair a tube leak in 'G' HP hea
GH4 | D1 | 12 | 4499 | 2014-03-26 06:30 | 2014-04-01 | 137.4997 | 1.03 | 505.7106 | 0.01179% | 0.01567% | 0.01577% | 530 | 534 | 491 | Other Miscellaneous Steam Turbine Problems | Turbine performance due to copper deposition.
[13 empty] | 534 | 491
GH4 | [5 empty] | 181.0497 | 2.9955 | 1470.7922 | 0.03429% | 0.04558% | 0.04587%
D4
PD
GR3 | NC | 15 | 3190 | 2014-03-08 07:45 | 2014-03-08 12:49 | 5.0667 | [5 empty] | 0 | 75 | 71 | Condensing System Air Leakage | Conco Services helium testing GR3 for air inleakage.
GR3 | MO | 16 | 782 | 2014-03-08 13:20 | 2014-03-09 02:33 | 13.2167 | 13.2167 | 938.3833 | 0.02188% | 0.02908% |  | 0 | 75 | 71 | Headers and Caps | GR3 off line on Maint Outage for lower waterwall hand hole cap leak repair. Also
GR3 | U1 | 18 | 3441 | 2014-03-10 02:39 | 2014-03-10 03:21 | 0.7 | 0.7 | 49.7 | 0.001159% | 0.00154% | 0.00155% | 0 | 75 | 71 | Other High Pressure Heater Problems | GR3 tripped due to high level in 3-4 HP Heater shortly after startup.
GR3 | PD | 19 | 346 | 2014-03-18 22:10 | 2014-03-19 04:20 | 6.1667 | 1.5622 | 110.9178 | 0.002586% |  |  | 56 | 75 | 71 | Pulverizer Pyrite Removal System | Maint replacing 4-4 Pulv Pyrite inside gate.
GR3 | D1 | 20 | 346 | 2014-03-19 09:00 | 2014-03-19 11:17 | 2.2833 | 0.57844 | 41.0696 | 0.0009575% | 0.001273% | 0.001281% | 56 | 75 | 71 | Pulverizer Pyrite Removal System | 4-4 Pulv O/S for adjustments to Pulv pyrite inside gate.
GR3 | D1 | 21 | 250 | 2014-03-31 07:32 | 2014-03-31 08:21 | 0.81667 | 0.21778 | 15.4622 | 0.0003605% | 0.0004791% | 0.0004822% | 55 | 75 | 71 | Pulverizer Feeders | GR3 load reduction to clean out 4-2 Feeder. Plugged with wet coal.
[13 empty] | 75 | 71
GR3 | [5 empty] | 28.25 | 16.2751 | 1155.5329 | 0.02694% | 0.03237% | 0.003313%
D4
PD
GR4 | D1 | 29 | 9630 | 2014-03-12 04:45 | 2014-03-12 05:31 | 0.76667 | 0.073016 | 7.1556 | 0.0001668% | 0.0002217% | 0.0002231% | 95 | 105 | 98 | Opacity - Fossil Steam Units | GR4 load reduced due to opacity limitations.
GR4 | NC | 30 | 3112 | 2014-03-20 09:30 | 2014-03-20 10:00 | 0.5 | [5 empty] | 0 | 105 | 98 | Condenser Tube Fouling Tube Side | GR4 load reduction for condenser backwash.
GR4 | D1 | 31 | 9630 | 2014-03-28 21:33 | 2014-03-29 01:15 | 3.7 | 0.185 | 17.205 | 0.0004011% | 0.0005331% | 0.0005365% | 95 | 100 | 93 | Opacity - Fossil Steam Units | GR4 load reduction to blow soot due to frequent opacity spikes.
GR4 | D1 | 32 | 9630 | 2014-03-29 04:06 | 2014-03-29 05:40 | 1.5667 | 0.047 | 4.371 | 0.0001019% | 0.0001354% | 0.0001363% | 97 | 100 | 93 | Opacity - Fossil Steam Units | GR4 load reduction due to opacity. Ops has found a waterwall tube leak in B5.
GR4 | U1 | 33 | 1000 | 2014-03-29 05:40 | 2014-03-30 04:03 | 22.3833 | 22.3833 | 2081.65 | 0.04853% | 0.0645% | 0.06491% | 0 | 100 | 93 | Furnace Wall Leaks | Ops verified a waterwall tube leak in B5 at 0408, reported to Dispatch at 0413. O
GR4 | D1 | 34 | 250 | 2014-03-30 17:34 | 2014-03-30 17:59 | 0.41667 | 0.083333 | 7.75 | 0.0001807% | 0.0002401% | 0.0002417% | 80 | 100 | 93 | Pulverizer Feeders | GR4 load reduction due to 5-1 Feeder plugged with wet coal.
GR4 | D1 | 35 | 250 | 2014-03-30 21:39 | 2014-03-30 22:50 | 1.1833 | 0.5325 | 49.5225 | 0.001155% | 0.001535% | 0.001544% | 55 | 100 | 93 | Pulverizer Feeders | 5-2 Pulv O/S due to plugged feeder pipe, shortly afterwards lost coal feed to 5-4
GR4 | D1 | 36 | 250 | 2014-03-30 22:50 | 2014-03-30 23:07 | 0.28333 | 0.070833 | 6.5875 | 0.0001536% | 0.0002041% | 0.0002054% | 75 | 100 | 93 | Pulverizer Feeders | Contunuation of Event #35, derate reduced when 5-4 Pulv was returned to service.
[13 empty] | 105 | 98
GR4 | [5 empty] | 30.8 | 23.375 | 2174.2416 | 0.05069% | 0.06737% | 0.0678%
D4
PD
MC1 | NC | 49 | 1160 | 2014-03-05 23:20 | 2014-03-06 01:00 | 1.6667 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC1 | NC | 50 | 1160 | 2014-03-06 22:45 | 2014-03-07 03:30 | 4.75 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC1 | NC | 51 | 1160 | 2014-03-07 13:45 | 2014-03-07 17:40 | 3.9167 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC1 | D4 | 52 | 310 | 2014-03-11 21:30 | 2014-03-12 03:40 | 6.1667 | 1.6818 | 509.5909 | 0.01188% | 0.01579% |  | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Adjust Rollers & Mill Inspection1B Coal Feeder - Replace Integrat
MC1 | NC | 53 | 1160 | 2014-03-16 00:30 | 2014-03-16 05:41 | 5.1833 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC1 | D4 | 54 | 250 | 2014-03-19 23:00 | 2014-03-20 04:15 | 5.25 | [5 empty] | 240 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Repair Skirt
MC1 | D1 | 55 | 360 | 2014-03-22 13:40 | 2014-03-22 14:10 | 0.5 | 0.13636 | 41.3182 | 0.0009633% | 0.00128% | 0.001288% | 240 | 330 | 303 | Burners | 1B Mill - 1B4 Coal Burner High Temperature
[13 empty] | 330 | 303
MC1 | [5 empty] | 27.4333 | 1.8182 | 550.9091 | 0.01284% | 0.01707% | 0.001288%
D4
PD
MC2 | NC | 72 | 1160 | 2014-03-04 23:30 | 2014-03-05 04:30 | 5 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 73 | 4490 | 2014-03-05 06:00 | 2014-03-05 12:05 | 6.0833 | [5 empty] | 0 | 330 | 299 | Turbine Performance Testing | Capability Test - Full Load
MC2 | NC | 74 | 1160 | 2014-03-06 00:30 | 2014-03-06 01:00 | 0.5 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 75 | 1160 | 2014-03-06 22:45 | 2014-03-07 03:20 | 4.5833 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | D1 | 76 | 1455 | 2014-03-07 05:45 | 2014-03-07 07:23 | 1.6333 | 0.089091 | 26.6382 | 0.0006211% | 0.0008254% | 0.0008307% | 312 | 330 | 299 | Induced Draft Fans | 2B Induced Draft Fan - Run Back
MC2 | D1 | 77 | 1455 | 2014-03-07 07:23 | 2014-03-07 11:52 | 4.4833 | 0.095101 | 28.4352 | 0.000663% | 0.0008811% | 0.0008867% | 323 | 330 | 299 | Induced Draft Fans | 2B Induced Draft Fan - Run Back
MC2 | NC | 78 | 1160 | 2014-03-07 13:45 | 2014-03-07 17:40 | 3.9167 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 79 | 1160 | 2014-03-15 23:00 | 2014-03-16 04:47 | 5.7833 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 80 | 1160 | 2014-03-16 22:30 | 2014-03-17 03:45 | 5.25 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | D4 | 81 | 310 | 2014-03-24 23:00 | 2014-03-25 02:09 | 3.15 | 0.85909 | 256.8682 | 0.005989% | 0.00796% |  | 240 | 330 | 299 | Pulverizer Mills | 2C Coal Mill - Bowl Differential Reference Line Repair
MC2 | NC | 82 | 1160 | 2014-03-25 22:45 | 2014-03-26 03:30 | 4.75 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 83 | 1160 | 2014-03-30 22:35 | 2014-03-31 03:04 | 4.4833 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | D4 | 84 | 1160 | 2014-03-31 22:00 | 2014-04-01 | 1.9997 | 1.1514 | 344.2552 | 0.008026% | 0.01067% |  | 140 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
[13 empty] | 330 | 299
MC2 | [5 empty] | 51.6164 | 2.1946 | 656.1968 | 0.0153% | 0.02033% | 0.001717%
D4
PD
MC3 | D1 | 37 | 310 | 2014-03-05 05:15 | 2014-03-05 05:48 | 0.55 | 0.11442 | 45.0818 | 0.001051% | 0.001397% | 0.001406% | 335 | 423 | 394 | Pulverizer Mills | 3A Coal Mill - Breaker Issue
MC3 | D4 | 38 | 8160 | 2014-03-08 23:30 | 2014-03-09 06:36 | 7.1 | 1.6449 | 648.0974 | 0.01511% | 0.02008% |  | 325 | 423 | 394 | Wet Scrubber Mist Eliminators/demisters & Washdown | FGD Mist Eliminator - Wash Line Tie In
MC3 | D1 | 39 | 260 | 2014-03-23 17:17 | 2014-03-23 19:18 | 2.0167 | 0.49106 | 193.476 | 0.004511% | 0.005995% | 0.006033% | 320 | 423 | 394 | Primary Air Fan | 3C Primary Air Fan Outboard Bearing - High Temperature, Changed Oil
MC3 | D1 | 40 | 380 | 2014-03-24 03:18 | 2014-03-24 03:51 | 0.55 | 0.062411 | 24.5901 | 0.0005733% | 0.000762% | 0.0007668% | 375 | 423 | 394 | Light-off (Igniter) Systems (Including Fuel Supply) | 3D Coal Mill - 3D2 Lighter Could Not Get in Service
[13 empty] | 423 | 394
MC3 | [5 empty] | 10.2167 | 2.3128 | 911.2453 | 0.02125% | 0.02824% | 0.008206%
| D4 |  |  |  |  | 7.1 | 1.6449 | 648.0974
PD
MC4 | D1 | 26 | 1710 | 2014-02-21 10:13 | 2014-03-04 06:41 | 260.4667 | 1.4884 | 723.3531 | 0.01686% | 0.02241% | 0.02256% | 522 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
MC4 | D1 | 29 | 250 | 2014-03-01 19:00 | 2014-03-01 22:35 | 3.5833 | 0.64841 | 315.1286 | 0.007347% | 0.009765% | 0.009827% | 430 | 525 | 486 | Pulverizer Feeders | 4C Coal Feeder - Loose Connection @ Control Board
MC4 | D1 | 30 | 360 | 2014-03-02 11:41 | 2014-03-02 12:14 | 0.55 | 0.08381 | 40.7314 | 0.0009496% | 0.001262% | 0.00127% | 445 | 525 | 486 | Burners | 4B Mill - 4B7 Coal Burner High Temperature
MC4 | D1 | 31 | 1710 | 2014-03-04 08:45 | 2014-03-12 18:14 | 201.4833 | 1.1513 | 559.548 | 0.01305% | 0.01734% | 0.01745% | 522 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
MC4 | D1 | 32 | 876 | 2014-03-07 23:20 | 2014-03-08 03:55 | 4.5833 | 1.7897 | 869.7857 | 0.02028% | 0.02695% | 0.02712% | 320 | 525 | 486 | Soot Blower Controls | Sootblower Regulator - Repair Positioner
MC4 | D4 | 33 | 8160 | 2014-03-08 23:30 | 2014-03-09 06:36 | 7.1 | 2.5019 | 1215.9257 | 0.02835% | 0.03768% |  | 340 | 525 | 486 | Wet Scrubber Mist Eliminators/demisters & Washdown | FGD Mist Eliminator - Wash Line Tie In
MC4 | D1 | 34 | 1710 | 2014-03-13 06:15 | 2014-03-14 23:47 | 41.5333 | 0.23733 | 115.344 | 0.002689% | 0.003574% | 0.003597% | 522 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
MC4 | PO | 35 | 1801 | 2014-03-14 23:47 | 2014-03-30 19:15 | 379.4667 | 379.4667 | 184420.8 | 4.3% |  |  | 0 | 525 | 486 | Minor Boiler Overhaul (less than 720 Hours) | Planned 2 Week Outage
MC4 | NC | 36 | 1850 | 2014-03-30 19:15 | 2014-03-31 19:30 | 24.25 | [5 empty] | 0 | 525 | 486 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Cold Start Up
MC4 | D1 | 37 | 1850 | 2014-03-31 19:30 | 2014-04-01 | 4.4997 | 1.6285 | 791.4369 | 0.01845% | 0.02452% | 0.02468% | 335 | 525 | 486 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
[13 empty] | 525 | 486
MC4 | [5 empty] | 927.5164 | 388.996 | 189052.0534 | 4.408% | 0.1435% | 0.1065%
| D4 |  |  |  |  | 7.1 | 2.5019 | 1215.9257
PD
TC1 | NC | 31 | 510 | 2014-03-02 01:00 | 2014-03-02 01:20 | 0.33333 | [5 empty] | 0 | 410 | 383 | Main Steam Relief/Safety Valves | Non-curtailing derate for a planned, weekly valve check. Unit was available to re
TC1 | U1 | 32 | 1471 | 2014-03-06 01:06 | 2014-03-06 12:48 | 11.7 | 11.7 | 4481.1 | 0.1045% | 0.1389% | 0.1397% | 0 | 410 | 383 | Induced Draft Fan Motors - Variable Speed | The VFD on the 1B ID fan sent a false alarm due to a low-low cooling supply alarm
TC1 | D1 | 33 | 280 | 2014-03-09 09:00 | 2014-03-09 10:15 | 1.25 | 0.10671 | 40.8689 | 0.0009528% | 0.001266% | 0.001274% | 375 | 410 | 383 | Pulverizer Fires | TC1 D coal mill had a fire and required a derate.
TC1 | D1 | 34 | 310 | 2014-03-09 10:15 | 2014-03-09 12:45 | 2.5 | 0.21341 | 81.7378 | 0.001906% | 0.002533% | 0.002549% | 375 | 410 | 383 | Pulverizer Mills | TC1 D coal mill breaker had an issue requiring replacement.
TC1 | D1 | 35 | 340 | 2014-03-13 08:15 | 2014-03-13 10:20 | 2.0833 | 0.13974 | 53.5188 | 0.001248% | 0.001658% | 0.001669% | 382.5 | 410 | 383 | Other Pulverizer Problems | The 1D Mill discharge valve was behaving erratically affecting mill control.
TC1 | D1 | 36 | 280 | 2014-03-13 10:20 | 2014-03-13 10:46 | 0.43333 | 0.088516 | 33.9017 | 0.0007904% | 0.001051% | 0.001057% | 326.25 | 410 | 383 | Pulverizer Fires | 1B mill fire required unit derate until OOS mill could be started
TC1 | D1 | 37 | 340 | 2014-03-13 10:46 | 2014-03-13 11:30 | 0.73333 | 0.049187 | 18.8386 | 0.0004392% | 0.0005838% | 0.0005875% | 382.5 | 410 | 383 | Other Pulverizer Problems | 1D mill discharge valve was operating erratically affecting mill control.
TC1 | D1 | 38 | 340 | 2014-03-14 14:00 | 2014-03-14 16:15 | 2.25 | 0.15091 | 57.8003 | 0.001348% | 0.001791% | 0.001802% | 382.5 | 410 | 383 | Other Pulverizer Problems | 1D coal mill discharge valve was operating erratically affecting mill control. Ad
TC1 | D1 | 39 | 3412 | 2014-03-15 01:55 | 2014-03-15 08:50 | 6.9167 | 0.27414 | 104.9942 | 0.002448% | 0.003253% | 0.003274% | 393.75 | 410 | 383 | Feedwater Pump Drive - Steam Turbine | The 1A TDBFP had an emergency governor trip removing it from service.
TC1 | D1 | 40 | 3412 | 2014-03-15 11:32 | 2014-03-15 13:33 | 2.0167 | 0.079929 | 30.6128 | 0.0007137% | 0.0009486% | 0.0009546% | 393.75 | 410 | 383 | Feedwater Pump Drive - Steam Turbine | The 1A TDBFP had an oil leak which required removal from service to repair.
TC1 | D1 | 41 | 280 | 2014-03-17 18:20 | 2014-03-17 21:55 | 3.5833 | 0.14202 | 54.3946 | 0.001268% | 0.001686% | 0.001696% | 393.75 | 410 | 383 | Pulverizer Fires | 1B Coal Mill had a fire and required removal from service and unit derate.
TC1 | NC | 42 | 1100 | 2014-03-29 | 2014-03-29 05:00 | 5 | [5 empty] | 0 | 410 | 383 | Furnace Wall Slagging or Fouling | Non-curtailing derate was placed on the unit to complete a planned boiler deslag.
[13 empty] | 410 | 383
TC1 | [5 empty] | 38.8 | 12.9446 | 4957.7676 | 0.1156% | 0.1536% | 0.1546%
D4
PD
TC2 | PO | 20 | 360 | 2014-02-08 03:21 | 2014-04-01 | 1244.6497 | 1244.6497 | 709450.3417 | 16.54% |  |  | 0 | 607 | 570 | Burners | TC2 began the planned outage for the replacement of all 30 burners. This effort i
[13 empty] | 607 | 570
TC2 | [5 empty] | 1244.6497 | 1244.6497 | 709450.3417 | 16.54% | 0% | 0%
D4
PD
KU - LG&E | [8 empty] | 34.13% | 2.988% | 2.32%
[13 empty] | 131 | 130
BR5 | [5 empty] | 0 | 0 | 0
BR6 | U1 | 18 | 5160 | 2014-03-05 13:12 | 2014-03-05 14:45 | 1.55 | 1.55 | 265.05 |  |  |  | 0 | 172 | 171 | Gas Turbine - Cooling And Seal Air System | Leak on water injection lance on HP quench vessel.
BR6 | U1 | 21 | 5160 | 2014-03-13 08:59 | 2014-03-14 17:25 | 32.4333 | 32.4333 | 5546.1 |  |  |  | 0 | 172 | 171 | Gas Turbine - Cooling And Seal Air System | Air Leak on HP quench cooler.
BR6 | PO | 24 | 5272 | 2014-03-21 22:06 | 2014-04-01 | 241.8997 | 241.8997 | 41364.8525 |  |  |  | 0 | 172 | 171 | Gas Turbine - Boroscope Inspection | Annual Planned outage: Boroscope Inspection, Fuel Oil Stop valves installed, Fuel
[13 empty] | 172 | 171
BR6 | [5 empty] | 275.8831 | 275.8831 | 47176.0025
BR7 | MO | 25 | 5041 | 2014-03-21 22:06 | 2014-03-22 16:00 | 17.9 | 17.9 | 3060.9 |  |  |  | 0 | 172 | 171 | Gas Turbine - Fuel Piping And Valves | Outage to install fuel flexibility standpipes.
BR7 | U1 | 27 | 5160 | 2014-03-24 04:51 | 2014-03-24 06:53 | 2.0333 | 2.0333 | 347.7 |  |  |  | 0 | 172 | 171 | Gas Turbine - Cooling And Seal Air System | Tripped unit due to high temperature on HP quench system. Problem looks to be tha
BR7 | PO | 30 | 5272 | 2014-03-29 13:48 | 2014-04-01 | 58.1997 | 58.1997 | 9952.1525 |  |  |  | 0 | 172 | 171 | Gas Turbine - Boroscope Inspection | Planned outage for opportunity inspection.
[13 empty] | 172 | 171
BR7 | [5 empty] | 78.1331 | 78.1331 | 13360.7525
BR8 | U1 | 23 | 5016 | 2014-03-31 05:56 | 2014-03-31 06:05 | 0.15 | 0.15 | 19.2 |  |  |  | 0 | 129 | 128 | High Pressure Compressor - Bleed Valves | Trip due to compressor blow off valve not being closed. Unit tripped immediately
[13 empty] | 129 | 128
BR8 | [5 empty] | 0.15 | 0.15 | 19.2
BR9 | U1 | 17 | 5246 | 2014-03-04 09:27 | 2014-03-04 10:06 | 0.65 | 0.65 | 89.7 |  |  |  | 0 | 139 | 138 | Gas Turbine Control System - Hardware Problems.... | Unit tripped when unit 11's MOS opened.
[13 empty] | 139 | 138
BR9 | [5 empty] | 0.65 | 0.65 | 89.7
BR10 | MO | 12 | 5272 | 2014-02-28 10:48 | 2014-03-02 13:50 | 51.0333 | 51.0333 | 7042.6 |  |  |  | 0 | 139 | 138 | Gas Turbine - Boroscope Inspection | Eddy current inspection of R3 blade and boroscope of turbine section.
[13 empty] | 139 | 138
BR10 | [5 empty] | 51.0333 | 51.0333 | 7042.6
BR11 | SF | 27 | 5041 | 2014-03-19 10:23 | 2014-03-19 12:46 | 2.3833 | 2.3833 | 305.0667 |  |  |  | 0 | 129 | 128 | Gas Turbine - Fuel Piping And Valves | Control Gas Valve swinging during start up.
[13 empty] | 129 | 128
BR11 | [5 empty] | 2.3833 | 2.3833 | 305.0667
CR11 | MO | 11 | 5130 | 2014-03-20 06:30 | 2014-03-20 13:03 | 6.55 | 6.55 | 91.7 |  |  |  | 0 | 14 | 14 | Gas Turbine - Starting System (including Motor) | Annual servicing of the diesel enginees. Changing oil and filters, checking hoses
[13 empty] | 14 | 14
CR11 | [5 empty] | 6.55 | 6.55 | 91.7
[13 empty] | 12 | 12
HF1 | [5 empty] | 0 | 0 | 0
[13 empty] | 12 | 12
HF2 | [5 empty] | 0 | 0 | 0
PR11 | MO | 4 | 5130 | 2014-03-19 07:00 | 2014-03-19 10:50 | 3.8333 | 3.8333 | 49.8333 |  |  |  | 0 | 13 | 13 | Gas Turbine - Starting System (including Motor) | Annual servicing of the diesel engines. Changing oil and filters, checking hoses,
[13 empty] | 13 | 13
PR11 | [5 empty] | 3.8333 | 3.8333 | 49.8333
PR12 | U1 | 4 | 5170 | 2014-02-19 10:25 | 2014-03-06 13:33 | 363.1333 | 363.1333 | 10167.7333 |  |  |  | 0 | 28 | 28 | Gas Turbine - Cooling Water System | Fire pump that supplies cooling water locked up.
PR12 | U1 | 6 | 5250 | 2014-03-11 11:34 | 2014-03-12 10:22 | 22.8 | 22.8 | 638.4 |  |  |  | 0 | 28 | 28 | Other Controls And Instrument Problems | The Active Speed Probe is having erratic readings.
[13 empty] | 28 | 28
PR12 | [5 empty] | 385.9333 | 385.9333 | 10806.1333
PR13 | PO | 4 | 4720 | 2014-02-15 06:08 | 2014-03-03 08:25 | 386.2833 | 386.2833 | 67599.5833 |  |  |  | 0 | 176 | 175 | Generator Synchronization Equipment | Generator synchronization equipment modifications. Replacing all generator protec
PR13 | U1 | 5 | 3860 | 2014-03-03 08:25 | 2014-03-06 13:33 | 77.1333 | 77.1333 | 13498.3333 |  |  |  | 0 | 176 | 175 | Fire Protection System Pumps | GSU and aux transformer fire pump is seized up.
PR13 | MO | 6 | 4720 | 2014-03-06 13:33 | 2014-03-07 11:04 | 21.5167 | 21.5167 | 3765.4167 |  |  |  | 0 | 176 | 175 | Generator Synchronization Equipment | Relay testing is needed to complete scope of work for previous Planned Outage.
PR13 | MO | 7 | 4720 | 2014-03-07 11:31 | 2014-03-07 11:59 | 0.46667 | 0.46667 | 81.6667 |  |  |  | 0 | 176 | 175 | Generator Synchronization Equipment | Relay testing is needed to complete scope of work for previous Planned Outage.
PR13 | MO | 9 | 3629 | 2014-03-21 06:00 | 2014-03-21 14:25 | 8.4167 | 8.4167 | 1472.9167 |  |  |  | 0 | 176 | 175 | Other Switchyard or High Voltage System Problems | Carded the buse to remove jumpers for isolation purposes to replace the buse work.
PR13 | SF | 11 | 4610 | 2014-03-25 05:45 | 2014-03-25 06:24 | 0.65 | 0.65 | 113.75 |  |  |  | 0 | 176 | 175 | Hydrogen Cooling System Piping And Valves | Hydrogen fill valve was frozen and would not open when needed.
[13 empty] | 176 | 175
PR13 | [5 empty] | 494.4667 | 494.4667 | 86531.6667
TC5 | SF | 23 | 5016 | 2014-03-02 21:40 | 2014-03-03 01:59 | 4.3167 | 4.3167 | 759.7333 |  |  |  | 0 | 180 | 176 | High Pressure Compressor - Bleed Valves | Startup failure due to issue with compressor bleed valve.
TC5 | U1 | 43 | 5049 | 2014-03-28 05:45 | 2014-03-28 06:14 | 0.48333 | 0.48333 | 85.0667 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Fuel System Problems | Forced outage due to over temperature of the fuel gas heater.
[13 empty] | 180 | 176
TC5 | [5 empty] | 4.8 | 4.8 | 844.8
TC6 | SF | 46 | 5041 | 2014-03-18 05:26 | 2014-03-18 05:50 | 0.4 | 0.4 | 70.4 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Startup failure due to gas valves not controlling properly.
TC6 | U1 | 53 | 5049 | 2014-03-28 05:45 | 2014-03-28 06:14 | 0.48333 | 0.48333 | 85.0667 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Fuel System Problems | Forced outage due to over temperature of fuel gas heater.
[13 empty] | 180 | 176
TC6 | [5 empty] | 0.88333 | 0.88333 | 155.4667
TC7 | SF | 18 | 5041 | 2014-03-02 21:40 | 2014-03-02 21:51 | 0.18333 | 0.18333 | 32.2667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Startup failure due to high hazardous gas alarm.
[13 empty] | 180 | 176
TC7 | [5 empty] | 0.18333 | 0.18333 | 32.2667
[13 empty] | 180 | 176
TC8 | [5 empty] | 0 | 0 | 0
TC9 | MO | 27 | 5160 | 2014-03-07 06:41 | 2014-03-07 12:37 | 5.9333 | 5.9333 | 1044.2667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Maintenance outage to replace exhaust frame blower motor.
TC9 | SF | 30 | 5130 | 2014-03-16 18:25 | 2014-03-16 20:27 | 2.0333 | 2.0333 | 357.8667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to 89SS not disengaging on TC10.
TC9 | SF | 33 | 3631 | 2014-03-18 05:09 | 2014-03-18 06:54 | 1.75 | 1.75 | 308 |  |  |  | 0 | 180 | 176 | 400-700-volt Circuit Breakers | Startup failure due to TC9 MCC #2 feed breaker opening cutting power to inservice
[13 empty] | 180 | 176
TC9 | [5 empty] | 9.7167 | 9.7167 | 1710.1333
TC10 | U1 | 29 | 5130 | 2014-03-08 08:03 | 2014-03-08 08:50 | 0.78333 | 0.78333 | 137.8667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to 89SS failing to disengage.
TC10 | U1 | 33 | 5130 | 2014-03-16 18:25 | 2014-03-16 20:27 | 2.0333 | 2.0333 | 357.8667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to 89SS failing to disengage.
TC10 | U1 | 37 | 3631 | 2014-03-18 06:09 | 2014-03-18 06:19 | 0.16667 | 0.16667 | 29.3333 |  |  |  | 0 | 180 | 176 | 400-700-volt Circuit Breakers | Forced outage due to TC9 MCC #2 feed breaker opening. Control power to TC9/10 LCI
TC10 | U1 | 41 | 5130 | 2014-03-20 08:30 | 2014-03-20 09:03 | 0.55 | 0.55 | 96.8 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to issue with 89SS.
[13 empty] | 180 | 176
TC10 | [5 empty] | 3.5333 | 3.5333 | 621.8667
Z1 | MO | 4 | 5130 | 2014-03-21 06:30 | 2014-03-21 10:35 | 4.0833 | 4.0833 | 65.3333 |  |  |  | 0 | 16 | 16 | Gas Turbine - Starting System (including Motor) | Annual servicing of the diesel engines. Changing oil and filters, checking hoses,
[13 empty] | 16 | 16
ZN1 | [5 empty] | 4.0833 | 4.0833 | 65.3333

## MAR-14 Impact By System
Dated: 04/01/14 14:00 hours | [16 empty] | EAF | EUOR | EFOR
Denominator
Unit | Event | Event | Cause | Event | Event | Evt. | Equiv. | MWH | EAF | EUOR | EFOR |  |  |  | Event | Event
Name | Type | No | Code | Start | End | Hrs | Dur Hrs | Lost | Lost | Impact | Impact | GAC | GMC | NMC | Cause | Description | 4289160 | 3227171.1845 | 3206756.3455
TC2 | PO | 20 | 360 | 2014-02-08 03:21 | 2014-04-01 | 1244.6497 | 1244.6497 | 709450.3417 | 16.54% |  |  | 0 | 607 | 570 | Burners | TC2 began the planned outage for the replacement of all 30 burners. This effort i
MC4 | PO | 35 | 1801 | 2014-03-14 23:47 | 2014-03-30 19:15 | 379.4667 | 379.4667 | 184420.8 | 4.3% |  |  | 0 | 525 | 486 | Minor Boiler Overhaul (less than 720 Hours) | Planned 2 Week Outage
GH2 | PO | 16 | 1812 | 2014-03-07 22:07 | 2014-03-21 11:04 | 324.95 | 324.95 | 155001.15 | 3.614% |  |  | 0 | 509 | 477 | Boiler Inspections - Scheduled or Routine | Unit 2 scheduled for Planned Spring Outage. Removed the unit
GH1 | PO | 19 | 1812 | 2014-03-21 21:30 | 2014-04-01 | 242.4997 | 242.4997 | 116642.3664 | 2.719% |  |  | 0 | 517 | 481 | Boiler Inspections - Scheduled or Routine | Unit 1 scheduled for a Planned Spring Outage. Removed the unit from
CR6 | PO | 28 | 8199 | 2014-03-14 23:44 | 2014-03-30 19:27 | 379.7167 | 379.7167 | 91132 | 2.125% |  |  | 0 | 261 | 240 | Other Wet Scrubber Problems | Total replacement of thickener tank center well ring.
GH3 | PO | 43 | 1800 | 2014-03-28 22:07 | 2014-04-01 | 73.8831 | 73.8831 | 35611.6328 | 0.8303% |  |  | 0 | 527 | 482 | Major Boiler Overhaul (720 Hours or Longer) | Unit 3 is scheduled for a Planned Spring Outage. Removed the unit fr
CR5 | PO | 12 | 1060 | 2014-03-07 12:53 | 2014-03-15 23:00 | 202.1167 | 202.1167 | 33955.6 | 0.7917% |  |  | 0 | 181 | 168 | First Reheater Leaks | Boiler tube inspection and repairs. Three reheat leaks were discovered upon inspe
BR3 | PO | 30 | 1801 | 2014-03-28 23:33 | 2014-04-01 | 72.4497 | 72.4497 | 29994.185 | 0.6993% |  |  | 0 | 457 | 414 | Minor Boiler Overhaul (less than 720 Hours) | Planned spring outage
BR3 | U1 | 22 | 310 | 2014-03-19 23:04 | 2014-03-21 06:05 | 31.0167 | 31.0167 | 12840.9 | 0.2994% | 0.3979% | 0.4004% | 0 | 457 | 414 | 3-5 Coal Mill Explosion Repair | 3-5 mill explosion, damage inspection and repair
GH1 | U1 | 17 | 1000 | 2014-03-05 00:42 | 2014-03-05 23:00 | 22.3 | 22.3 | 10726.3 | 0.2501% | 0.3324% | 0.3345% | 0 | 517 | 481 | Furnace Wall Tube Leaks | Water water tube leak blew out on the upper slope of the boiler about 15
BR2 | MO | 15 | 8560 | 2014-02-28 12:26 | 2014-03-02 18:19 | 53.8833 | 53.8833 | 9052.4 | 0.2111% | 0.2805% |  | 0 | 180 | 168 | Electrostatic Precipitator Fields Out | Precipitator fields out of service and tube leak repair 6546848
CR6 | U1 | 25 | 8100 | 2014-03-11 11:19 | 2014-03-12 19:03 | 31.7333 | 31.7333 | 7616 | 0.1776% | 0.236% | 0.2375% | 0 | 261 | 240 | FGD Absorber Module Cleaning | FGD module cleaning - solids buildup in module spray header, resulting from incons
GH2 | PD | 17 | 345 | 2014-03-21 11:05 | 2014-03-27 12:02 | 144.95 | 13.9539 | 6656.0243 | 0.1552% |  |  | 460 | 509 | 477 | 2-4 Coal Mill Overhaul | 2-4 Mill out of service for overhaul.
BR2 | D1 | 17 | 3410 | 2014-03-03 07:22 | 2014-03-06 16:50 | 81.4667 | 33.9444 | 5702.6667 | 0.133% | 0.1767% | 0.1778% | 105 | 180 | 168 | 2-2 Boiler Feedwater Pump Oil Leak | 2-2 BFP oil leak 6546733
CR5 | MO | 13 | 1160 | 2014-03-18 10:07 | 2014-03-19 16:52 | 30.75 | 30.75 | 5166 | 0.1204% | 0.1601% |  | 0 | 181 | 168 | First Reheater Slagging and Fouling | Replaced 1 reheat tube with dutchman.
BR2 | U1 | 20 | 1040 | 2014-03-10 14:50 | 2014-03-11 21:09 | 30.3167 | 30.3167 | 5093.2 | 0.1187% | 0.1578% | 0.1588% | 0 | 180 | 168 | First Superheater Tube Leaks | Tube leak in boiler penthouse area. 6550561
TC1 | U1 | 32 | 1471 | 2014-03-06 01:06 | 2014-03-06 12:48 | 11.7 | 11.7 | 4481.1 | 0.1045% | 0.1389% | 0.1397% | 0 | 410 | 383 | ID Fan Motors - Variable Speed Drive | The VFD on the 1B ID fan sent a false alarm due to a low-low cooling supply alarm
CR4 | MO | 19 | 3110 | 2014-03-24 20:40 | 2014-03-25 18:55 | 22.25 | 22.25 | 3448.75 | 0.08041% | 0.1069% |  | 0 | 168 | 155 | Condenser Tube Leaks | Unit removed from service due to high silica. Root cause is from condenser tube l
BR3 | D1 | 29 | 310 | 2014-03-25 12:06 | 2014-03-28 23:33 | 83.45 | 6.7563 | 2797.1271 | 0.06521% | 0.08667% | 0.08723% | 420 | 457 | 414 | 3-5 Coal Mill Exhauster Pressure | High exhauster to furnance pressure due to 3-5D burner out of service.
BR3 | D1 | 24 | 310 | 2014-03-21 16:28 | 2014-03-24 10:30 | 66.0333 | 5.3462 | 2213.3449 | 0.0516% | 0.06858% | 0.06902% | 420 | 457 | 414 | 3-5 Coal Mill Exhauster Pressure | High exhauster to furnance pressure due to 3-5D burner out of service.
GR4 | U1 | 33 | 1000 | 2014-03-29 05:40 | 2014-03-30 04:03 | 22.3833 | 22.3833 | 2081.65 | 0.04853% | 0.0645% | 0.06491% | 0 | 100 | 93 | Furnace Wall Tube Leaks | Ops verified a waterwall tube leak in B5 at 0408, reported to Dispatch at 0413. O
BR2 | PD | 19 | 310 | 2014-03-06 19:00 | 2014-03-08 07:40 | 36.6667 | 10.1852 | 1711.1111 | 0.03989% |  |  | 130 | 180 | 168 | 2-3 Coal Mill Thrust Bearing | 2-3 mill thrust bearing replacement 6529384
GH2 | D1 | 18 | 1850 | 2014-03-21 19:34 | 2014-03-22 06:10 | 10.6 | 3.3112 | 1579.4417 | 0.03682% | 0.04894% | 0.04925% | 350 | 509 | 477 | Boiler Water Condition | Boiler water chemistry - high silica during start up.
GH2 | PD | 15 | 345 | 2014-03-06 12:00 | 2014-03-07 22:07 | 34.1167 | 3.2843 | 1566.6186 | 0.03653% |  |  | 460 | 509 | 477 | 2-4 Pulverizer Overhaul | 2-4 Mill out of service for scheduled overhaul.
CR6 | U1 | 29 | 3669 | 2014-03-31 08:13 | 2014-03-31 13:34 | 5.35 | 5.35 | 1284 | 0.02994% | 0.03979% | 0.04004% | 0 | 261 | 240 | Other 4000-7000-volt Problems | I/E personnel inadvertently cold transfered the 4KV A Buse power supply.
GH3 | PD | 23 | 9650 | 2014-02-28 22:30 | 2014-03-01 03:08 | 4.6333 | 2.6112 | 1258.5962 | 0.02934% |  |  | 230 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. Working on sorbent blower.
MC4 | D4 | 33 | 8160 | 2014-03-08 23:30 | 2014-03-09 06:36 | 7.1 | 2.5019 | 1215.9257 | 0.02835% | 0.03768% |  | 340 | 525 | 486 | Wet Scrubber Mist Eliminators/demisters & Washdown | FGD Mist Eliminator - Wash Line Tie In
GH3 | D1 | 36 | 9650 | 2014-03-14 12:26 | 2014-03-15 05:15 | 16.8167 | 2.3294 | 1122.7917 | 0.02618% | 0.03479% | 0.03501% | 454 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. ID Fan Outlet Injection plugged.
GR3 | MO | 16 | 782 | 2014-03-08 13:20 | 2014-03-09 02:33 | 13.2167 | 13.2167 | 938.3833 | 0.02188% | 0.02908% |  | 0 | 75 | 71 | Headers and Caps | GR3 off line on Maint Outage for lower waterwall hand hole cap leak repair. Also
CR6 | D1 | 19 | 310 | 2014-03-08 15:15 | 2014-03-09 09:27 | 18.2 | 3.905 | 937.1954 | 0.02185% | 0.02904% | 0.02923% | 205 | 261 | 240 | Pulverizer Mills | 6D Mill - #2 journal broken shaft
GH4 | D1 | 11 | 3440 | 2014-03-24 08:44 | 2014-03-26 02:30 | 41.7667 | 1.7989 | 883.279 | 0.02059% | 0.02737% | 0.02754% | 511 | 534 | 491 | High Pressure Heater Tube Leaks | HP heaters are out of service to repair a tube leak in 'G' HP hea
MC4 | D1 | 32 | 876 | 2014-03-07 23:20 | 2014-03-08 03:55 | 4.5833 | 1.7897 | 869.7857 | 0.02028% | 0.02695% | 0.02712% | 320 | 525 | 486 | Soot Blower Controls | Sootblower Regulator - Repair Positioner
BR3 | U1 | 20 | 740 | 2014-03-19 10:32 | 2014-03-19 12:29 | 1.95 | 1.95 | 807.3 | 0.01882% | 0.02502% | 0.02517% | 0 | 457 | 414 | Boiler Recirculation Pumps | Boiler trip due to BCWP differential pressure
MC4 | D1 | 37 | 1850 | 2014-03-31 19:30 | 2014-04-01 | 4.4997 | 1.6285 | 791.4369 | 0.01845% | 0.02452% | 0.02468% | 335 | 525 | 486 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
CR4 | D1 | 15 | 310 | 2014-03-10 06:35 | 2014-03-11 00:58 | 18.3833 | 4.7053 | 729.315 | 0.017% | 0.0226% | 0.02274% | 125 | 168 | 155 | Pulverizer Mills | 4C Coal mill (roller) - #3 journal bad bearing
MC4 | D1 | 26 | 1710 | 2014-02-21 10:13 | 2014-03-04 06:41 | 260.4667 | 1.4884 | 723.3531 | 0.01686% | 0.02241% | 0.02256% | 522 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
BR3 | D1 | 26 | 310 | 2014-03-24 10:43 | 2014-03-25 07:04 | 20.35 | 1.6476 | 682.1035 | 0.0159% | 0.02114% | 0.02127% | 420 | 457 | 414 | Pulverizer Mills | High exhauster to furnance pressure due to 3-5D burner out of service.
MC3 | D4 | 38 | 8160 | 2014-03-08 23:30 | 2014-03-09 06:36 | 7.1 | 1.6449 | 648.0974 | 0.01511% | 0.02008% |  | 325 | 423 | 394 | Wet Scrubber Mist Eliminators/demisters & Washdown | FGD Mist Eliminator - Wash Line Tie In
GH3 | D1 | 26 | 9650 | 2014-03-05 17:28 | 2014-03-06 01:30 | 8.0333 | 1.1738 | 565.7479 | 0.01319% | 0.01753% | 0.01764% | 450 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2S04 within limit. Outlet injection lines plugged.
MC4 | D1 | 31 | 1710 | 2014-03-04 08:45 | 2014-03-12 18:14 | 201.4833 | 1.1513 | 559.548 | 0.01305% | 0.01734% | 0.01745% | 522 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
BR3 | D1 | 23 | 310 | 2014-03-21 11:20 | 2014-03-21 16:28 | 5.1333 | 1.3142 | 544.0884 | 0.01269% | 0.01686% | 0.01697% | 340 | 457 | 414 | Pulverizer Mills | 3-5 mill post explosion calibrations and inspections
BR2 | D1 | 16 | 310 | 2014-03-02 20:15 | 2014-03-03 07:22 | 11.1167 | 3.088 | 518.7778 | 0.0121% | 0.01608% | 0.01618% | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
MC1 | D4 | 52 | 310 | 2014-03-11 21:30 | 2014-03-12 03:40 | 6.1667 | 1.6818 | 509.5909 | 0.01188% | 0.01579% |  | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Adjust Rollers & Mill Inspection1B Coal Feeder - Replace Integrat
GH4 | D1 | 12 | 4499 | 2014-03-26 06:30 | 2014-04-01 | 137.4997 | 1.03 | 505.7106 | 0.01179% | 0.01567% | 0.01577% | 530 | 534 | 491 | Other Miscellaneous Steam Turbine Problems | Turbine performance due to copper deposition.
BR3 | D1 | 27 | 350 | 2014-03-25 07:04 | 2014-03-25 11:00 | 3.9333 | 1.05 | 434.7151 | 0.01014% | 0.01347% | 0.01356% | 335 | 457 | 414 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | 3-5A burner line coal leak
MC1 | D4 | 54 | 250 | 2014-03-19 23:00 | 2014-03-20 04:15 | 5.25 | 1.4318 | 433.8409 | 0.01011% | 0.01344% |  | 240 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Repair Skirt
CR4 | D1 | 20 | 1160 | 2014-03-26 22:00 | 2014-03-27 03:15 | 5.25 | 2.75 | 426.25 | 0.009938% | 0.01321% | 0.01329% | 80 | 168 | 155 | First Reheater Slagging or Fouling | Load limit to clean up boiler slag around the 7R and 5R retract area.
GH3 | D1 | 24 | 9650 | 2014-03-02 18:15 | 2014-03-02 21:00 | 2.75 | 0.82448 | 397.3985 | 0.009265% | 0.01231% | 0.01239% | 369 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. Low level on Silo feeding outlet i
GH3 | D1 | 39 | 1400 | 2014-03-19 06:00 | 2014-03-20 07:00 | 25 | 0.80645 | 388.7097 | 0.009063% | 0.01204% | 0.01212% | 510 | 527 | 482 | Forced Draft Fans | FD Fan limit, 3-1 FD Fan Inlet Vane needs attention.
GH2 | D1 | 19 | 890 | 2014-03-29 11:16 | 2014-03-29 15:40 | 4.4 | 0.76935 | 366.9807 | 0.008556% | 0.01137% | 0.01144% | 420 | 509 | 477 | Bottom Ash Systems (Wet or Dry) | Unit 2 was derated due to wet ash system pluggage.
CR6 | D1 | 17 | 310 | 2014-03-05 14:16 | 2014-03-05 20:35 | 6.3167 | 1.4763 | 354.3142 | 0.008261% | 0.01098% | 0.01105% | 200 | 261 | 240 | Pulverizer Mills | 6A Mill broken mill sweep - replaced damaged parts.
MC2 | D4 | 84 | 1160 | 2014-03-31 22:00 | 2014-04-01 | 1.9997 | 1.1514 | 344.2552 | 0.008026% | 0.01067% |  | 140 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
GH1 | D1 | 16 | 250 | 2014-03-03 16:05 | 2014-03-03 22:16 | 6.1833 | 0.68172 | 327.908 | 0.007645% | 0.01016% | 0.01023% | 460 | 517 | 481 | Pulverizer Feeders | 1-3 Feeder belt failed. Removed from service to replace belt.
MC4 | D1 | 29 | 250 | 2014-03-01 19:00 | 2014-03-01 22:35 | 3.5833 | 0.64841 | 315.1286 | 0.007347% | 0.009765% | 0.009827% | 430 | 525 | 486 | Pulverizer Feeders | 4C Coal Feeder - Loose Connection @ Control Board
CR4 | D4 | 13 | 344 | 2014-02-28 22:00 | 2014-03-01 06:51 | 8.85 | 2.0018 | 310.2768 | 0.007234% | 0.009615% |  | 130 | 168 | 155 | Pulverizer Inspection | 4A Mill inspection
MC2 | D4 | 81 | 310 | 2014-03-24 23:00 | 2014-03-25 02:09 | 3.15 | 0.85909 | 256.8682 | 0.005989% | 0.00796% |  | 240 | 330 | 299 | Pulverizer Mills | 2C Coal Mill - Bowl Differential Reference Line Repair
GH1 | D1 | 18 | 346 | 2014-03-17 07:42 | 2014-03-17 12:14 | 4.5333 | 0.49981 | 240.407 | 0.005605% | 0.007449% | 0.007497% | 460 | 517 | 481 | Pulverizer Pyrite Removal System | 1-3 Mill out of service to inspect pyrite section.
BR3 | D1 | 18 | 740 | 2014-03-17 14:15 | 2014-03-18 | 9.75 | 0.57604 | 238.4803 | 0.00556% | 0.00739% | 0.007437% | 430 | 457 | 414 | Boiler Recirculation Pumps | 3-1 BCWP out of service
GH3 | D1 | 27 | 9650 | 2014-03-07 04:20 | 2014-03-07 06:05 | 1.75 | 0.42173 | 203.2723 | 0.004739% | 0.006299% | 0.006339% | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. 3-2B Blow through valve drive chain
MC3 | D1 | 39 | 260 | 2014-03-23 17:17 | 2014-03-23 19:18 | 2.0167 | 0.49106 | 193.476 | 0.004511% | 0.005995% | 0.006033% | 320 | 423 | 394 | Primary Air Fan | 3C Primary Air Fan Outboard Bearing - High Temperature, Changed Oil
GH3 | D1 | 38 | 9650 | 2014-03-17 09:30 | 2014-03-17 11:03 | 1.55 | 0.37353 | 180.0412 | 0.004198% | 0.005579% | 0.005614% | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2So4 within limit. 3-2B Drop Through Rotary valve driv
CR6 | D1 | 24 | 8110 | 2014-03-11 09:26 | 2014-03-11 11:18 | 1.8667 | 0.72235 | 173.364 | 0.004042% | 0.005372% | 0.005406% | 160 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
BR3 | D1 | 14 | 310 | 2014-03-11 13:51 | 2014-03-11 15:36 | 1.75 | 0.40974 | 169.6313 | 0.003955% | 0.005256% | 0.00529% | 350 | 457 | 414 | Pulverizer Mills | 3-1 mill broken spring bolt 6550819
GH3 | D1 | 37 | 9650 | 2014-03-15 06:24 | 2014-03-15 10:54 | 4.5 | 0.31594 | 152.2827 | 0.00355% | 0.004719% | 0.004749% | 490 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. ID Faan Outlet Injection plugged.
CR6 | D1 | 30 | 310 | 2014-03-31 20:24 | 2014-04-01 | 3.5997 | 0.56547 | 135.7137 | 0.003164% | 0.004205% | 0.004232% | 220 | 261 | 240 | Pulverizer Mills | 6C Coal Mill explosion during post unit trip. Burning mill out.
CR6 | D1 | 18 | 8199 | 2014-03-08 05:11 | 2014-03-08 08:18 | 3.1167 | 0.52542 | 126.0996 | 0.00294% | 0.003907% | 0.003932% | 217 | 261 | 240 | Other Wet Scrubber Problems | SO2 excursion during load pickup. Contributing factors were the 6B reaction tank
BR3 | D1 | 21 | 310 | 2014-03-19 21:47 | 2014-03-19 23:04 | 1.2833 | 0.30047 | 124.3963 | 0.0029% | 0.003855% | 0.003879% | 350 | 457 | 414 | Pulverizer Mills | 3-5 mill explosion
GH3 | D1 | 25 | 9650 | 2014-03-05 07:08 | 2014-03-05 08:03 | 0.91667 | 0.25569 | 123.2438 | 0.002873% | 0.003819% | 0.003843% | 380 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | H2SO4 running high due to outlet injection probe pluggage. Redu
MC4 | D1 | 34 | 1710 | 2014-03-13 06:15 | 2014-03-14 23:47 | 41.5333 | 0.23733 | 115.344 | 0.002689% | 0.003574% | 0.003597% | 522 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
BR3 | D1 | 19 | 740 | 2014-03-19 10:13 | 2014-03-19 10:32 | 0.31667 | 0.27717 | 114.7484 | 0.002675% | 0.003556% | 0.003578% | 57 | 457 | 414 | Boiler Recirculation Pumps | Boiler trip due to BCWP differential pressure
BR3 | D1 | 28 | 350 | 2014-03-25 11:00 | 2014-03-25 12:06 | 1.1 | 0.26958 | 111.6079 | 0.002602% | 0.003458% | 0.00348% | 345 | 457 | 414 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | 3-5A burner line coal leak
GR3 | PD | 19 | 346 | 2014-03-18 22:10 | 2014-03-19 04:20 | 6.1667 | 1.5622 | 110.9178 | 0.002586% |  |  | 56 | 75 | 71 | Pulverizer Pyrite Removal System | Maint replacing 4-4 Pulv Pyrite inside gate.
BR1 | D1 | 8 | 310 | 2014-03-13 10:15 | 2014-03-13 13:45 | 3.5 | 1.0439 | 110.6491 | 0.00258% | 0.003429% | 0.00345% | 80 | 114 | 106 | Pulverizer Mills | 1-4 mill tripped due to air flow issues 6552310
BR1 | D1 | 6 | 280 | 2014-03-04 09:56 | 2014-03-04 13:25 | 3.4833 | 1.0389 | 110.1222 | 0.002567% | 0.003412% | 0.003434% | 80 | 114 | 106 | Pulverizer Fires | 1-3 mill pyrite fire 6548834
CR5 | D1 | 14 | 344 | 2014-03-21 23:21 | 2014-03-22 01:35 | 2.2333 | 0.62928 | 105.7193 | 0.002465% | 0.003276% | 0.003297% | 130 | 181 | 168 | Pulverizer Inspection | Checked 5B coal mill air chamber for buildup.
TC1 | D1 | 39 | 3412 | 2014-03-15 01:55 | 2014-03-15 08:50 | 6.9167 | 0.27414 | 104.9942 | 0.002448% | 0.003253% | 0.003274% | 393.75 | 410 | 383 | Feedwater Pump Drive - Steam Turbine | The 1A TDBFP had an emergency governor trip removing it from service.
BR2 | D1 | 18 | 310 | 2014-03-06 16:50 | 2014-03-06 19:00 | 2.1667 | 0.60185 | 101.1111 | 0.002357% | 0.003133% | 0.003153% | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
GH3 | PD | 42 | 855 | 2014-03-26 22:00 | 2014-03-27 00:36 | 2.6 | 0.20721 | 99.8755 | 0.002329% |  |  | 485 | 527 | 482 | Boiler Drum Relief/Safety Valves | Precision to set drum safeties.
CR6 | D1 | 26 | 3415 | 2014-03-13 04:58 | 2014-03-13 05:55 | 0.95 | 0.40402 | 96.9655 | 0.002261% | 0.003005% | 0.003024% | 150 | 261 | 240 | Feedwater Pump/Drive Lube Oil System | Lube oil pressure indication low
GH3 | D1 | 31 | 280 | 2014-03-13 22:40 | 2014-03-13 23:45 | 1.0833 | 0.1994 | 96.1104 | 0.002241% | 0.002978% | 0.002997% | 430 | 527 | 482 | Pulverizer Fires | 3-5 Mill fire.
BR2 | D1 | 22 | 350 | 2014-03-27 10:31 | 2014-03-27 13:13 | 2.7 | 0.525 | 88.2 | 0.002056% | 0.002733% | 0.00275% | 145 | 180 | 168 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | 2-2 mill burner line temperature high
CR6 | D1 | 23 | 8110 | 2014-03-11 07:36 | 2014-03-11 09:26 | 1.8333 | 0.35824 | 85.977 | 0.002005% | 0.002664% | 0.002681% | 210 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
TC1 | D1 | 34 | 310 | 2014-03-09 10:15 | 2014-03-09 12:45 | 2.5 | 0.21341 | 81.7378 | 0.001906% | 0.002533% | 0.002549% | 375 | 410 | 383 | Pulverizer Mills | TC1 D coal mill breaker had an issue requiring replacement.
GH3 | D1 | 30 | 1400 | 2014-03-08 19:35 | 2014-03-09 05:28 | 9.8833 | 0.16879 | 81.3546 | 0.001897% | 0.002521% | 0.002537% | 518 | 527 | 482 | Forced Draft Fans | FD Fans out the top.
CR4 | D4 | 14 | 315 | 2014-03-05 23:09 | 2014-03-06 01:25 | 2.2667 | 0.5127 | 79.4683 | 0.001853% | 0.002462% |  | 130 | 168 | 155 | Pulverizer Coal Level Controls | 4A Mill - broken purge air line on bowl differential pressure indication was repa
CR6 | D1 | 20 | 8110 | 2014-03-10 10:15 | 2014-03-10 12:13 | 1.9667 | 0.30894 | 74.1456 | 0.001729% | 0.002298% | 0.002312% | 220 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
GH3 | D1 | 40 | 280 | 2014-03-25 08:39 | 2014-03-25 09:56 | 1.2833 | 0.15098 | 72.7725 | 0.001697% | 0.002255% | 0.002269% | 465 | 527 | 482 | Pulverizer Fires | 3-5 Mill fire in top of the mill.
GH3 | D1 | 41 | 9650 | 2014-03-25 11:38 | 2014-03-25 12:35 | 0.95 | 0.1388 | 66.9038 | 0.00156% | 0.002073% | 0.002086% | 450 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit. Inlet probes were plug
TC1 | D1 | 38 | 340 | 2014-03-14 14:00 | 2014-03-14 16:15 | 2.25 | 0.15091 | 57.8003 | 0.001348% | 0.001791% | 0.001802% | 382.5 | 410 | 383 | Other Pulverizer Problems | 1D coal mill discharge valve was operating erratically affecting mill control. Ad
TC1 | D1 | 41 | 280 | 2014-03-17 18:20 | 2014-03-17 21:55 | 3.5833 | 0.14202 | 54.3946 | 0.001268% | 0.001686% | 0.001696% | 393.75 | 410 | 383 | Pulverizer Fires | 1B Coal Mill had a fire and required removal from service and unit derate.
TC1 | D1 | 35 | 340 | 2014-03-13 08:15 | 2014-03-13 10:20 | 2.0833 | 0.13974 | 53.5188 | 0.001248% | 0.001658% | 0.001669% | 382.5 | 410 | 383 | Other Pulverizer Problems | The 1D Mill discharge valve was behaving erratically affecting mill control.
GR3 | U1 | 18 | 3441 | 2014-03-10 02:39 | 2014-03-10 03:21 | 0.7 | 0.7 | 49.7 | 0.001159% | 0.00154% | 0.00155% | 0 | 75 | 71 | Other High Pressure Heater Problems | GR3 tripped due to high level in 3-4 HP Heater shortly after startup.
GR4 | D1 | 35 | 250 | 2014-03-30 21:39 | 2014-03-30 22:50 | 1.1833 | 0.5325 | 49.5225 | 0.001155% | 0.001535% | 0.001544% | 55 | 100 | 93 | Pulverizer Feeders | 5-2 Pulv O/S due to plugged feeder pipe, shortly afterwards lost coal feed to 5-4
CR5 | D4 | 11 | 1980 | 2014-03-06 21:15 | 2014-03-06 22:56 | 1.6833 | 0.28831 | 48.4354 | 0.001129% | 0.001501% |  | 150 | 181 | 168 | Boiler Safety Valve Test | Precision Services testing & inspecting safety valves
MC3 | D1 | 37 | 310 | 2014-03-05 05:15 | 2014-03-05 05:48 | 0.55 | 0.11442 | 45.0818 | 0.001051% | 0.001397% | 0.001406% | 335 | 423 | 394 | Pulverizer Mills | 3A Coal Mill - Breaker Issue
GH4 | D1 | 9 | 9650 | 2014-03-05 17:35 | 2014-03-05 18:09 | 0.56667 | 0.089139 | 43.767 | 0.00102% | 0.001356% | 0.001365% | 450 | 534 | 491 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Temporary lime silo plugged at mixer.
MC1 | D1 | 55 | 360 | 2014-03-22 13:40 | 2014-03-22 14:10 | 0.5 | 0.13636 | 41.3182 | 0.0009633% | 0.00128% | 0.001288% | 240 | 330 | 303 | Burners | 1B Mill - 1B4 Coal Burner High Temperature
GR3 | D1 | 20 | 346 | 2014-03-19 09:00 | 2014-03-19 11:17 | 2.2833 | 0.57844 | 41.0696 | 0.0009575% | 0.001273% | 0.001281% | 56 | 75 | 71 | Pulverizer Pyrite Removal System | 4-4 Pulv O/S for adjustments to Pulv pyrite inside gate.
TC1 | D1 | 33 | 280 | 2014-03-09 09:00 | 2014-03-09 10:15 | 1.25 | 0.10671 | 40.8689 | 0.0009528% | 0.001266% | 0.001274% | 375 | 410 | 383 | Pulverizer Fires | TC1 D coal mill had a fire and required a derate.
MC4 | D1 | 30 | 360 | 2014-03-02 11:41 | 2014-03-02 12:14 | 0.55 | 0.08381 | 40.7314 | 0.0009496% | 0.001262% | 0.00127% | 445 | 525 | 486 | Burners | 4B Mill - 4B7 Coal Burner High Temperature
CR6 | D1 | 22 | 8110 | 2014-03-11 06:11 | 2014-03-11 07:36 | 1.4167 | 0.16826 | 40.3831 | 0.0009415% | 0.001251% | 0.001259% | 230 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
GH3 | D1 | 34 | 9650 | 2014-03-14 09:57 | 2014-03-14 11:08 | 1.1833 | 0.08308 | 40.0447 | 0.0009336% | 0.001241% | 0.001249% | 490 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO3 within limit. ID Fan Outlet Injection plugged.
GH4 | D1 | 10 | 9650 | 2014-03-05 20:48 | 2014-03-05 22:01 | 1.2167 | 0.077466 | 38.0356 | 0.0008868% | 0.001179% | 0.001186% | 500 | 534 | 491 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Temporary lime silo plugged at mixer.
TC1 | D1 | 36 | 280 | 2014-03-13 10:20 | 2014-03-13 10:46 | 0.43333 | 0.088516 | 33.9017 | 0.0007904% | 0.001051% | 0.001057% | 326.25 | 410 | 383 | Pulverizer Fires | 1B mill fire required unit derate until OOS mill could be started
GH3 | D1 | 29 | 1400 | 2014-03-07 19:29 | 2014-03-07 23:10 | 3.6833 | 0.069892 | 33.6882 | 0.0007854% | 0.001044% | 0.001051% | 517 | 527 | 482 | Forced Draft Fans | FD fans out the top.
BR2 | D1 | 21 | 350 | 2014-03-27 09:06 | 2014-03-27 10:05 | 0.98333 | 0.1912 | 32.1222 | 0.0007489% | 0.0009954% | 0.001002% | 145 | 180 | 168 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | 2-2 mill burner line temperature high
TC1 | D1 | 40 | 3412 | 2014-03-15 11:32 | 2014-03-15 13:33 | 2.0167 | 0.079929 | 30.6128 | 0.0007137% | 0.0009486% | 0.0009546% | 393.75 | 410 | 383 | Feedwater Pump Drive - Steam Turbine | The 1A TDBFP had an oil leak which required removal from service to repair.
MC2 | D1 | 77 | 1455 | 2014-03-07 07:23 | 2014-03-07 11:52 | 4.4833 | 0.095101 | 28.4352 | 0.000663% | 0.0008811% | 0.0008867% | 323 | 330 | 299 | Induced Draft Fans | 2B Induced Draft Fan - Run Back
MC2 | D1 | 76 | 1455 | 2014-03-07 05:45 | 2014-03-07 07:23 | 1.6333 | 0.089091 | 26.6382 | 0.0006211% | 0.0008254% | 0.0008307% | 312 | 330 | 299 | Induced Draft Fans | 2B Induced Draft Fan - Run Back
BR1 | D1 | 9 | 310 | 2014-03-17 06:32 | 2014-03-17 07:27 | 0.91667 | 0.23319 | 24.7178 | 0.0005763% | 0.0007659% | 0.0007708% | 85 | 114 | 106 | Pulverizer Mills | 1-4 mill air flow erratic 6552310
MC3 | D1 | 40 | 380 | 2014-03-24 03:18 | 2014-03-24 03:51 | 0.55 | 0.062411 | 24.5901 | 0.0005733% | 0.000762% | 0.0007668% | 375 | 423 | 394 | Light-off (Igniter) Systems (Including Fuel Supply) | 3D Coal Mill - 3D2 Lighter Could Not Get in Service
BR3 | D1 | 25 | 310 | 2014-03-24 10:30 | 2014-03-24 10:43 | 0.21667 | 0.057841 | 23.9462 | 0.0005583% | 0.000742% | 0.0007467% | 335 | 457 | 414 | Pulverizer Mills | 3-3 mill exhauster bearing high vibration
TC1 | D1 | 37 | 340 | 2014-03-13 10:46 | 2014-03-13 11:30 | 0.73333 | 0.049187 | 18.8386 | 0.0004392% | 0.0005838% | 0.0005875% | 382.5 | 410 | 383 | Other Pulverizer Problems | 1D mill discharge valve was operating erratically affecting mill control.
GH3 | D1 | 32 | 9650 | 2014-03-14 03:36 | 2014-03-14 05:18 | 1.7 | 0.03871 | 18.6581 | 0.000435% | 0.0005782% | 0.0005818% | 515 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limits, ID Fan Injection Outlets plugged.
GR4 | D1 | 31 | 9630 | 2014-03-28 21:33 | 2014-03-29 01:15 | 3.7 | 0.185 | 17.205 | 0.0004011% | 0.0005331% | 0.0005365% | 95 | 100 | 93 | Opacity - Fossil Steam Units | GR4 load reduction to blow soot due to frequent opacity spikes.
GR3 | D1 | 21 | 250 | 2014-03-31 07:32 | 2014-03-31 08:21 | 0.81667 | 0.21778 | 15.4622 | 0.0003605% | 0.0004791% | 0.0004822% | 55 | 75 | 71 | Pulverizer Feeders | GR3 load reduction to clean out 4-2 Feeder. Plugged with wet coal.
BR1 | D1 | 10 | 9205 | 2014-03-18 08:37 | 2014-03-18 10:37 | 2 | 0.12281 | 13.0175 | 0.0003035% | 0.0004034% | 0.0004059% | 107 | 114 | 106 | Poor quality fuel; heat content | Limited by coal quality
CR6 | D1 | 21 | 8110 | 2014-03-10 20:31 | 2014-03-10 21:11 | 0.66667 | 0.05364 | 12.8736 | 0.0003001% | 0.0003989% | 0.0004015% | 240 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
BR2 | D1 | 23 | 350 | 2014-03-27 14:25 | 2014-03-27 14:47 | 0.36667 | 0.071296 | 11.9778 | 0.0002793% | 0.0003712% | 0.0003735% | 145 | 180 | 168 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | Inspect 2-1A burner line for pluggage
GH3 | D1 | 33 | 1400 | 2014-03-14 05:18 | 2014-03-14 09:57 | 4.65 | 0.017647 | 8.5059 | 0.0001983% | 0.0002636% | 0.0002652% | 525 | 527 | 482 | Forced Draft Fans | FD Fan Limit, 3-1 FD Fan Inlet Vane needs attention.
GH3 | D1 | 35 | 1400 | 2014-03-14 11:08 | 2014-03-14 12:26 | 1.3 | 0.017268 | 8.323 | 0.000194% | 0.0002579% | 0.0002595% | 520 | 527 | 482 | Forced Draft Fans | FD Fan Limit, 3-1 ID Fan Vane needs attention.
GR4 | D1 | 34 | 250 | 2014-03-30 17:34 | 2014-03-30 17:59 | 0.41667 | 0.083333 | 7.75 | 0.0001807% | 0.0002401% | 0.0002417% | 80 | 100 | 93 | Pulverizer Feeders | GR4 load reduction due to 5-1 Feeder plugged with wet coal.
GR4 | D1 | 29 | 9630 | 2014-03-12 04:45 | 2014-03-12 05:31 | 0.76667 | 0.073016 | 7.1556 | 0.0001668% | 0.0002217% | 0.0002231% | 95 | 105 | 98 | Opacity - Fossil Steam Units | GR4 load reduced due to opacity limitations.
GR4 | D1 | 36 | 250 | 2014-03-30 22:50 | 2014-03-30 23:07 | 0.28333 | 0.070833 | 6.5875 | 0.0001536% | 0.0002041% | 0.0002054% | 75 | 100 | 93 | Pulverizer Feeders | Contunuation of Event #35, derate reduced when 5-4 Pulv was returned to service.
CR4 | D1 | 18 | 8000 | 2014-03-23 20:18 | 2014-03-23 20:29 | 0.18333 | 0.041468 | 6.4276 | 0.0001499% | 0.0001992% | 0.0002004% | 130 | 168 | 155 | Chemical Feed Storage; Mill Feeders And Conveyors | B LST tank solids buildup
GH3 | D1 | 28 | 9650 | 2014-03-07 07:30 | 2014-03-07 08:00 | 0.5 | 0.011385 | 5.4877 | 0.0001279% | 0.00017% | 0.0001711% | 515 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2S04 within limit. 3-2 Blow through drive chain valve
GR4 | D1 | 32 | 9630 | 2014-03-29 04:06 | 2014-03-29 05:40 | 1.5667 | 0.047 | 4.371 | 0.0001019% | 0.0001354% | 0.0001363% | 97 | 100 | 93 | Opacity - Fossil Steam Units | GR4 load reduction due to opacity. Ops has found a waterwall tube leak in B5.
CR5 | D1 | 15 | 8000 | 2014-03-23 20:16 | 2014-03-23 20:29 | 0.21667 | 0.025138 | 4.2232 | 9.846e-05% | 0.0001309% | 0.0001317% | 160 | 181 | 168 | Chemical Feed Storage; Mill Feeders And Conveyors | B LST tank solids buildup
BR1 | D1 | 11 | 9205 | 2014-03-18 10:37 | 2014-03-18 10:51 | 0.23333 | 0.0040936 | 0.43392 | 1.012e-05% | 1.345e-05% | 1.353e-05% | 112 | 114 | 106 | Poor quality fuel; heat content | Limited by coal quality
MC4 | NC | 36 | 1850 | 2014-03-30 19:15 | 2014-03-31 19:30 | 24.25 | [5 empty] | 0 | 525 | 486 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Cold Start Up
BR3 | NC | 16 | 9656 | 2014-03-12 08:45 | 2014-03-12 20:38 | 11.8833 | [5 empty] | 0 | 457 | 414 | Other stack or exhaust emissions testing - fossil | RATA testing at 425 mw.
MC2 | NC | 73 | 4490 | 2014-03-05 06:00 | 2014-03-05 12:05 | 6.0833 | [5 empty] | 0 | 330 | 299 | Turbine Performance Testing | Capability Test - Full Load
MC2 | NC | 79 | 1160 | 2014-03-15 23:00 | 2014-03-16 04:47 | 5.7833 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
CR4 | NC | 17 | 1160 | 2014-03-19 22:00 | 2014-03-20 03:20 | 5.3333 | [5 empty] | 0 | 168 | 155 | First Reheater Slagging or Fouling | Boiler deslag
CR4 | NC | 16 | 1160 | 2014-03-18 22:30 | 2014-03-19 03:50 | 5.3333 | [5 empty] | 0 | 168 | 155 | First Reheater Slagging or Fouling | Boiler deslag
MC2 | NC | 80 | 1160 | 2014-03-16 22:30 | 2014-03-17 03:45 | 5.25 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC1 | NC | 53 | 1160 | 2014-03-16 00:30 | 2014-03-16 05:41 | 5.1833 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
CR4 | NC | 21 | 1160 | 2014-03-27 23:00 | 2014-03-28 04:10 | 5.1667 | [5 empty] | 0 | 168 | 155 | First Reheater Slagging or Fouling | Load limit to clean up boiler slag around the 7R and 5R retract area.
GR3 | NC | 15 | 3190 | 2014-03-08 07:45 | 2014-03-08 12:49 | 5.0667 | [5 empty] | 0 | 75 | 71 | Condensing System Air Leakage | Conco Services helium testing GR3 for air inleakage.
MC2 | NC | 72 | 1160 | 2014-03-04 23:30 | 2014-03-05 04:30 | 5 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
TC1 | NC | 42 | 1100 | 2014-03-29 | 2014-03-29 05:00 | 5 | [5 empty] | 0 | 410 | 383 | Furnace Wall Slagging or Fouling | Non-curtailing derate was placed on the unit to complete a planned boiler deslag.
MC1 | NC | 50 | 1160 | 2014-03-06 22:45 | 2014-03-07 03:30 | 4.75 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 82 | 1160 | 2014-03-25 22:45 | 2014-03-26 03:30 | 4.75 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 75 | 1160 | 2014-03-06 22:45 | 2014-03-07 03:20 | 4.5833 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
BR3 | NC | 17 | 9656 | 2014-03-13 12:30 | 2014-03-13 17:00 | 4.5 | [5 empty] | 0 | 457 | 414 | Other stack or exhaust emissions testing - fossil | RATA testing at 425 mw.
MC2 | NC | 83 | 1160 | 2014-03-30 22:35 | 2014-03-31 03:04 | 4.4833 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
BR1 | NC | 7 | 9656 | 2014-03-11 11:42 | 2014-03-11 16:08 | 4.4333 | [5 empty] | 0 | 114 | 106 | Other stack or exhaust emissions testing - fossil | Low load RATA testing
MC1 | NC | 51 | 1160 | 2014-03-07 13:45 | 2014-03-07 17:40 | 3.9167 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 78 | 1160 | 2014-03-07 13:45 | 2014-03-07 17:40 | 3.9167 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
CR6 | NC | 27 | 1980 | 2014-03-13 21:13 | 2014-03-14 00:18 | 3.0833 | [5 empty] | 0 | 261 | 240 | Boiler Safety Valve Test | Electrostatic boiler valve safety testing (pre outage).
BR3 | NC | 13 | 9656 | 2014-03-11 11:42 | 2014-03-11 13:51 | 2.15 | [5 empty] | 0 | 457 | 414 | Other stack or exhaust emissions testing - fossil | Low load RATA testing
MC1 | NC | 49 | 1160 | 2014-03-05 23:20 | 2014-03-06 01:00 | 1.6667 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
BR3 | NC | 15 | 9656 | 2014-03-11 15:36 | 2014-03-11 16:08 | 0.53333 | [5 empty] | 0 | 457 | 414 | Other stack or exhaust emissions testing - fossil | Low load RATA testing
GR4 | NC | 30 | 3112 | 2014-03-20 09:30 | 2014-03-20 10:00 | 0.5 | [5 empty] | 0 | 105 | 98 | Condenser Tube Fouling Tube Side | GR4 load reduction for condenser backwash.
MC2 | NC | 74 | 1160 | 2014-03-06 00:30 | 2014-03-06 01:00 | 0.5 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
TC1 | NC | 31 | 510 | 2014-03-02 01:00 | 2014-03-02 01:20 | 0.33333 | [5 empty] | 0 | 410 | 383 | Main Steam Relief/Safety Valves | Non-curtailing derate for a planned, weekly valve check. Unit was available to re
[13 empty] | 607 | 570
KU - LG&E | [8 empty] | 17.07% | 1.501% | 1.16%
PR13 | PO | 4 | 4720 | 2014-02-15 06:08 | 2014-03-03 08:25 | 386.2833 | 386.2833 | 67599.5833 |  |  |  | 0 | 176 | 175 | Generator Synchronization Equipment | Generator synchronization equipment modifications. Replacing all generator protec
BR6 | PO | 24 | 5272 | 2014-03-21 22:06 | 2014-04-01 | 241.8997 | 241.8997 | 41364.8525 |  |  |  | 0 | 172 | 171 | Gas Turbine - Boroscope Inspection | Annual Planned outage: Boroscope Inspection, Fuel Oil Stop valves installed, Fuel
BR7 | PO | 30 | 5272 | 2014-03-29 13:48 | 2014-04-01 | 58.1997 | 58.1997 | 9952.1525 |  |  |  | 0 | 172 | 171 | Gas Turbine - Boroscope Inspection | Planned outage for opportunity inspection.
PR13 | U1 | 5 | 3860 | 2014-03-03 08:25 | 2014-03-06 13:33 | 77.1333 | 77.1333 | 13498.3333 |  |  |  | 0 | 176 | 175 | Fire Protection System Pumps | GSU and aux transformer fire pump is seized up.
PR12 | U1 | 4 | 5170 | 2014-02-19 10:25 | 2014-03-06 13:33 | 363.1333 | 363.1333 | 10167.7333 |  |  |  | 0 | 28 | 28 | Gas Turbine - Cooling Water System | Fire pump that supplies cooling water locked up.
BR10 | MO | 12 | 5272 | 2014-02-28 10:48 | 2014-03-02 13:50 | 51.0333 | 51.0333 | 7042.6 |  |  |  | 0 | 139 | 138 | Gas Turbine - Boroscope Inspection | Eddy current inspection of R3 blade and boroscope of turbine section.
BR6 | U1 | 21 | 5160 | 2014-03-13 08:59 | 2014-03-14 17:25 | 32.4333 | 32.4333 | 5546.1 |  |  |  | 0 | 172 | 171 | Gas Turbine - Cooling And Seal Air System | Air Leak on HP quench cooler.
PR13 | MO | 6 | 4720 | 2014-03-06 13:33 | 2014-03-07 11:04 | 21.5167 | 21.5167 | 3765.4167 |  |  |  | 0 | 176 | 175 | Generator Synchronization Equipment | Relay testing is needed to complete scope of work for previous Planned Outage.
BR7 | MO | 25 | 5041 | 2014-03-21 22:06 | 2014-03-22 16:00 | 17.9 | 17.9 | 3060.9 |  |  |  | 0 | 172 | 171 | Gas Turbine - Fuel Piping And Valves | Outage to install fuel flexibility standpipes.
PR13 | MO | 9 | 3629 | 2014-03-21 06:00 | 2014-03-21 14:25 | 8.4167 | 8.4167 | 1472.9167 |  |  |  | 0 | 176 | 175 | Other Switchyard or High Voltage System Problems | Carded the buse to remove jumpers for isolation purposes to replace the buse work.
TC9 | MO | 27 | 5160 | 2014-03-07 06:41 | 2014-03-07 12:37 | 5.9333 | 5.9333 | 1044.2667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Maintenance outage to replace exhaust frame blower motor.
TC5 | SF | 23 | 5016 | 2014-03-02 21:40 | 2014-03-03 01:59 | 4.3167 | 4.3167 | 759.7333 |  |  |  | 0 | 180 | 176 | High Pressure Compressor - Bleed Valves | Startup failure due to issue with compressor bleed valve.
PR12 | U1 | 6 | 5250 | 2014-03-11 11:34 | 2014-03-12 10:22 | 22.8 | 22.8 | 638.4 |  |  |  | 0 | 28 | 28 | Other Controls And Instrument Problems | The Active Speed Probe is having erratic readings.
TC9 | SF | 30 | 5130 | 2014-03-16 18:25 | 2014-03-16 20:27 | 2.0333 | 2.0333 | 357.8667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to 89SS not disengaging on TC10.
TC10 | U1 | 33 | 5130 | 2014-03-16 18:25 | 2014-03-16 20:27 | 2.0333 | 2.0333 | 357.8667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to 89SS failing to disengage.
BR7 | U1 | 27 | 5160 | 2014-03-24 04:51 | 2014-03-24 06:53 | 2.0333 | 2.0333 | 347.7 |  |  |  | 0 | 172 | 171 | Gas Turbine - Cooling And Seal Air System | Tripped unit due to high temperature on HP quench system. Problem looks to be tha
TC9 | SF | 33 | 3631 | 2014-03-18 05:09 | 2014-03-18 06:54 | 1.75 | 1.75 | 308 |  |  |  | 0 | 180 | 176 | 400-700-volt Circuit Breakers | Startup failure due to TC9 MCC #2 feed breaker opening cutting power to inservice
BR11 | SF | 27 | 5041 | 2014-03-19 10:23 | 2014-03-19 12:46 | 2.3833 | 2.3833 | 305.0667 |  |  |  | 0 | 129 | 128 | Gas Turbine - Fuel Piping And Valves | Control Gas Valve swinging during start up.
BR6 | U1 | 18 | 5160 | 2014-03-05 13:12 | 2014-03-05 14:45 | 1.55 | 1.55 | 265.05 |  |  |  | 0 | 172 | 171 | Gas Turbine - Cooling And Seal Air System | Leak on water injection lance on HP quench vessel.
TC10 | U1 | 29 | 5130 | 2014-03-08 08:03 | 2014-03-08 08:50 | 0.78333 | 0.78333 | 137.8667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to 89SS failing to disengage.
PR13 | SF | 11 | 4610 | 2014-03-25 05:45 | 2014-03-25 06:24 | 0.65 | 0.65 | 113.75 |  |  |  | 0 | 176 | 175 | Hydrogen Cooling System Piping And Valves | Hydrogen fill valve was frozen and would not open when needed.
TC10 | U1 | 41 | 5130 | 2014-03-20 08:30 | 2014-03-20 09:03 | 0.55 | 0.55 | 96.8 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to issue with 89SS.
CR11 | MO | 11 | 5130 | 2014-03-20 06:30 | 2014-03-20 13:03 | 6.55 | 6.55 | 91.7 |  |  |  | 0 | 14 | 14 | Gas Turbine - Starting System (including Motor) | Annual servicing of the diesel enginees. Changing oil and filters, checking hoses
BR9 | U1 | 17 | 5246 | 2014-03-04 09:27 | 2014-03-04 10:06 | 0.65 | 0.65 | 89.7 |  |  |  | 0 | 139 | 138 | Gas Turbine Control System - Hardware Problems.... | Unit tripped when unit 11's MOS opened.
TC5 | U1 | 43 | 5049 | 2014-03-28 05:45 | 2014-03-28 06:14 | 0.48333 | 0.48333 | 85.0667 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Fuel System Problems | Forced outage due to over temperature of the fuel gas heater.
TC6 | U1 | 53 | 5049 | 2014-03-28 05:45 | 2014-03-28 06:14 | 0.48333 | 0.48333 | 85.0667 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Fuel System Problems | Forced outage due to over temperature of fuel gas heater.
PR13 | MO | 7 | 4720 | 2014-03-07 11:31 | 2014-03-07 11:59 | 0.46667 | 0.46667 | 81.6667 |  |  |  | 0 | 176 | 175 | Generator Synchronization Equipment | Relay testing is needed to complete scope of work for previous Planned Outage.
TC6 | SF | 46 | 5041 | 2014-03-18 05:26 | 2014-03-18 05:50 | 0.4 | 0.4 | 70.4 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Startup failure due to gas valves not controlling properly.
Z1 | MO | 4 | 5130 | 2014-03-21 06:30 | 2014-03-21 10:35 | 4.0833 | 4.0833 | 65.3333 |  |  |  | 0 | 16 | 16 | Gas Turbine - Starting System (including Motor) | Annual servicing of the diesel engines. Changing oil and filters, checking hoses,
PR11 | MO | 4 | 5130 | 2014-03-19 07:00 | 2014-03-19 10:50 | 3.8333 | 3.8333 | 49.8333 |  |  |  | 0 | 13 | 13 | Gas Turbine - Starting System (including Motor) | Annual servicing of the diesel engines. Changing oil and filters, checking hoses,
TC7 | SF | 18 | 5041 | 2014-03-02 21:40 | 2014-03-02 21:51 | 0.18333 | 0.18333 | 32.2667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Startup failure due to high hazardous gas alarm.
TC10 | U1 | 37 | 3631 | 2014-03-18 06:09 | 2014-03-18 06:19 | 0.16667 | 0.16667 | 29.3333 |  |  |  | 0 | 180 | 176 | 400-700-volt Circuit Breakers | Forced outage due to TC9 MCC #2 feed breaker opening. Control power to TC9/10 LCI
BR8 | U1 | 23 | 5016 | 2014-03-31 05:56 | 2014-03-31 06:05 | 0.15 | 0.15 | 19.2 |  |  |  | 0 | 129 | 128 | High Pressure Compressor - Bleed Valves | Trip due to compressor blow off valve not being closed. Unit tripped immediately
[13 empty] | 16 | 16

## MAR-14 Impact By Cause Code
Unit | Event | Event | Cause | Event | Event | Event | Equiv. | MWH | EAF | EUOR | EFOR | Unit | Unit | Unit | Event | Event
Name | Type | No | Code | Start | End | Hours | Hours | Lost | Lost | Impact | Impact | GAC | GMC | NMC | Cause | Description
|  |  | (0000-0009) |  |  | 0 | 0 | 0 | 0% | 0% | 0%
TC2 | PO | 20 | 360 | 2014-02-08 03:21 | 2014-04-01 | 1244.6497 | 1244.6497 | 709450.3417 | 16.54% |  |  | 0 | 607 | 570 | Burners | TC2 began the planned outage for the replacement of all 30 burners. This effort i
|  |  | (0200-0480) |  | Fuel Firing | 0 | 0 | 0 | 0% | 0% | 0%
CR5 | PO | 12 | 1060 | 2014-03-07 12:53 | 2014-03-15 23:00 | 202.1167 | 202.1167 | 33955.6 | 0.7917% |  |  | 0 | 181 | 168 | First Reheater Leaks | Boiler tube inspection and repairs. Three reheat leaks were discovered upon inspe
GH3 | PO | 43 | 1800 | 2014-03-28 22:07 | 2014-04-01 | 73.8831 | 73.8831 | 35611.6328 | 0.8303% |  |  | 0 | 527 | 482 | Major Boiler Overhaul (720 Hours or Longer) | Unit 3 is scheduled for a Planned Spring Outage. Removed the unit fr
MC4 | PO | 35 | 1801 | 2014-03-14 23:47 | 2014-03-30 19:15 | 379.4667 | 379.4667 | 184420.8 | 4.3% |  |  | 0 | 525 | 486 | Minor Boiler Overhaul (less than 720 Hours) | Planned 2 Week Outage
BR3 | PO | 30 | 1801 | 2014-03-28 23:33 | 2014-04-01 | 72.4497 | 72.4497 | 29994.185 | 0.6993% |  |  | 0 | 457 | 414 | Minor Boiler Overhaul (less than 720 Hours) | Planned spring outage
GH2 | PO | 16 | 1812 | 2014-03-07 22:07 | 2014-03-21 11:04 | 324.95 | 324.95 | 155001.15 | 3.614% |  |  | 0 | 509 | 477 | Boiler Inspections - Scheduled or Routine | Unit 2 scheduled for Planned Spring Outage. Removed the unit
GH1 | PO | 19 | 1812 | 2014-03-21 21:30 | 2014-04-01 | 242.4997 | 242.4997 | 116642.3664 | 2.719% |  |  | 0 | 517 | 481 | Boiler Inspections - Scheduled or Routine | Unit 1 scheduled for a Planned Spring Outage. Removed the unit from
|  |  | (0500-1999) |  | Boiler | 1295.3658 | 1295.3658 | 555625.7342 | 12.95% | 0% | 0%
0
0
|  |  | (3110-3999) |  | Balance Of Plant | 0 | 0 | 0 | 0% | 0% | 0%
|  |  | (4000-4499) |  | Steam Turbine | 0 | 0 | 0 | 0% | 0% | 0%
0
0
|  |  | (4500-4899) |  | Generator | 0 | 0 | 0 | 0% | 0% | 0%
CR6 | PO | 28 | 8199 | 2014-03-14 23:44 | 2014-03-30 19:27 | 379.7167 | 379.7167 | 91132 | 2.125% |  |  | 0 | 261 | 240 | Other Wet Scrubber Problems | Total replacement of thickener tank center well ring.
|  |  | (8000-8835) |  | Pollution Control Equip. | 0 | 0 | 0 | 2.125% | 0% | 0%
|  |  | (0010-0130) |  | Fuel Handling | 0 | 0 | 0 | 0% | 0% | 0%
0
MC1 | D4 | 54 | 250 | 2014-03-19 23:00 | 2014-03-20 04:15 | 5.25 | 1.4318 | 433.8409 | 0.01011% | 0.01344% |  | 240 | 330 | 303 | Pulverizer Feeders | 1D Coal Feeder - Repair Skirt
GH1 | D1 | 16 | 250 | 2014-03-03 16:05 | 2014-03-03 22:16 | 6.1833 | 0.68172 | 327.908 | 0.007645% | 0.01016% | 0.01023% | 460 | 517 | 481 | Pulverizer Feeders | 1-3 Feeder belt failed. Removed from service to replace belt.
MC4 | D1 | 29 | 250 | 2014-03-01 19:00 | 2014-03-01 22:35 | 3.5833 | 0.64841 | 315.1286 | 0.007347% | 0.009765% | 0.009827% | 430 | 525 | 486 | Pulverizer Feeders | 4C Coal Feeder - Loose Connection @ Control Board
GR4 | D1 | 35 | 250 | 2014-03-30 21:39 | 2014-03-30 22:50 | 1.1833 | 0.5325 | 49.5225 | 0.001155% | 0.001535% | 0.001544% | 55 | 100 | 93 | Pulverizer Feeders | 5-2 Pulv O/S due to plugged feeder pipe, shortly afterwards lost coal feed to 5-4
GR3 | D1 | 21 | 250 | 2014-03-31 07:32 | 2014-03-31 08:21 | 0.81667 | 0.21778 | 15.4622 | 0.0003605% | 0.0004791% | 0.0004822% | 55 | 75 | 71 | Pulverizer Feeders | GR3 load reduction to clean out 4-2 Feeder. Plugged with wet coal.
GR4 | D1 | 34 | 250 | 2014-03-30 17:34 | 2014-03-30 17:59 | 0.41667 | 0.083333 | 7.75 | 0.0001807% | 0.0002401% | 0.0002417% | 80 | 100 | 93 | Pulverizer Feeders | GR4 load reduction due to 5-1 Feeder plugged with wet coal.
GR4 | D1 | 36 | 250 | 2014-03-30 22:50 | 2014-03-30 23:07 | 0.28333 | 0.070833 | 6.5875 | 0.0001536% | 0.0002041% | 0.0002054% | 75 | 100 | 93 | Pulverizer Feeders | Contunuation of Event #35, derate reduced when 5-4 Pulv was returned to service.
MC3 | D1 | 39 | 260 | 2014-03-23 17:17 | 2014-03-23 19:18 | 2.0167 | 0.49106 | 193.476 | 0.004511% | 0.005995% | 0.006033% | 320 | 423 | 394 | Primary Air Fan | 3C Primary Air Fan Outboard Bearing - High Temperature, Changed Oil
BR1 | D1 | 6 | 280 | 2014-03-04 09:56 | 2014-03-04 13:25 | 3.4833 | 1.0389 | 110.1222 | 0.002567% | 0.003412% | 0.003434% | 80 | 114 | 106 | Pulverizer Fires | 1-3 mill pyrite fire 6548834
GH3 | D1 | 31 | 280 | 2014-03-13 22:40 | 2014-03-13 23:45 | 1.0833 | 0.1994 | 96.1104 | 0.002241% | 0.002978% | 0.002997% | 430 | 527 | 482 | Pulverizer Fires | 3-5 Mill fire.
GH3 | D1 | 40 | 280 | 2014-03-25 08:39 | 2014-03-25 09:56 | 1.2833 | 0.15098 | 72.7725 | 0.001697% | 0.002255% | 0.002269% | 465 | 527 | 482 | Pulverizer Fires | 3-5 Mill fire in top of the mill.
TC1 | D1 | 41 | 280 | 2014-03-17 18:20 | 2014-03-17 21:55 | 3.5833 | 0.14202 | 54.3946 | 0.001268% | 0.001686% | 0.001696% | 393.75 | 410 | 383 | Pulverizer Fires | 1B Coal Mill had a fire and required removal from service and unit derate.
TC1 | D1 | 33 | 280 | 2014-03-09 09:00 | 2014-03-09 10:15 | 1.25 | 0.10671 | 40.8689 | 0.0009528% | 0.001266% | 0.001274% | 375 | 410 | 383 | Pulverizer Fires | TC1 D coal mill had a fire and required a derate.
TC1 | D1 | 36 | 280 | 2014-03-13 10:20 | 2014-03-13 10:46 | 0.43333 | 0.088516 | 33.9017 | 0.0007904% | 0.001051% | 0.001057% | 326.25 | 410 | 383 | Pulverizer Fires | 1B mill fire required unit derate until OOS mill could be started
BR3 | U1 | 22 | 310 | 2014-03-19 23:04 | 2014-03-21 06:05 | 31.0167 | 31.0167 | 12840.9 | 0.2994% | 0.3979% | 0.4004% | 0 | 457 | 414 | 3-5 Coal Mill Explosion Repair | 3-5 mill explosion, damage inspection and repair
BR3 | D1 | 29 | 310 | 2014-03-25 12:06 | 2014-03-28 23:33 | 83.45 | 6.7563 | 2797.1271 | 0.06521% | 0.08667% | 0.08723% | 420 | 457 | 414 | 3-5 Coal Mill Exhauster Pressure | High exhauster to furnance pressure due to 3-5D burner out of service.
BR3 | D1 | 24 | 310 | 2014-03-21 16:28 | 2014-03-24 10:30 | 66.0333 | 5.3462 | 2213.3449 | 0.0516% | 0.06858% | 0.06902% | 420 | 457 | 414 | 3-5 Coal Mill Exhauster Pressure | High exhauster to furnance pressure due to 3-5D burner out of service.
BR2 | PD | 19 | 310 | 2014-03-06 19:00 | 2014-03-08 07:40 | 36.6667 | 10.1852 | 1711.1111 | 0.03989% |  |  | 130 | 180 | 168 | 2-3 Coal Mill Thrust Bearing | 2-3 mill thrust bearing replacement 6529384
CR6 | D1 | 19 | 310 | 2014-03-08 15:15 | 2014-03-09 09:27 | 18.2 | 3.905 | 937.1954 | 0.02185% | 0.02904% | 0.02923% | 205 | 261 | 240 | Pulverizer Mills | 6D Mill - #2 journal broken shaft
CR4 | D1 | 15 | 310 | 2014-03-10 06:35 | 2014-03-11 00:58 | 18.3833 | 4.7053 | 729.315 | 0.017% | 0.0226% | 0.02274% | 125 | 168 | 155 | Pulverizer Mills | 4C Coal mill (roller) - #3 journal bad bearing
BR3 | D1 | 26 | 310 | 2014-03-24 10:43 | 2014-03-25 07:04 | 20.35 | 1.6476 | 682.1035 | 0.0159% | 0.02114% | 0.02127% | 420 | 457 | 414 | Pulverizer Mills | High exhauster to furnance pressure due to 3-5D burner out of service.
BR3 | D1 | 23 | 310 | 2014-03-21 11:20 | 2014-03-21 16:28 | 5.1333 | 1.3142 | 544.0884 | 0.01269% | 0.01686% | 0.01697% | 340 | 457 | 414 | Pulverizer Mills | 3-5 mill post explosion calibrations and inspections
BR2 | D1 | 16 | 310 | 2014-03-02 20:15 | 2014-03-03 07:22 | 11.1167 | 3.088 | 518.7778 | 0.0121% | 0.01608% | 0.01618% | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
MC1 | D4 | 52 | 310 | 2014-03-11 21:30 | 2014-03-12 03:40 | 6.1667 | 1.6818 | 509.5909 | 0.01188% | 0.01579% |  | 240 | 330 | 303 | Pulverizer Mills | 1A Coal Mill - Adjust Rollers & Mill Inspection1B Coal Feeder - Replace Integrat
CR6 | D1 | 17 | 310 | 2014-03-05 14:16 | 2014-03-05 20:35 | 6.3167 | 1.4763 | 354.3142 | 0.008261% | 0.01098% | 0.01105% | 200 | 261 | 240 | Pulverizer Mills | 6A Mill broken mill sweep - replaced damaged parts.
MC2 | D4 | 81 | 310 | 2014-03-24 23:00 | 2014-03-25 02:09 | 3.15 | 0.85909 | 256.8682 | 0.005989% | 0.00796% |  | 240 | 330 | 299 | Pulverizer Mills | 2C Coal Mill - Bowl Differential Reference Line Repair
BR3 | D1 | 14 | 310 | 2014-03-11 13:51 | 2014-03-11 15:36 | 1.75 | 0.40974 | 169.6313 | 0.003955% | 0.005256% | 0.00529% | 350 | 457 | 414 | Pulverizer Mills | 3-1 mill broken spring bolt 6550819
CR6 | D1 | 30 | 310 | 2014-03-31 20:24 | 2014-04-01 | 3.5997 | 0.56547 | 135.7137 | 0.003164% | 0.004205% | 0.004232% | 220 | 261 | 240 | Pulverizer Mills | 6C Coal Mill explosion during post unit trip. Burning mill out.
BR3 | D1 | 21 | 310 | 2014-03-19 21:47 | 2014-03-19 23:04 | 1.2833 | 0.30047 | 124.3963 | 0.0029% | 0.003855% | 0.003879% | 350 | 457 | 414 | Pulverizer Mills | 3-5 mill explosion
BR1 | D1 | 8 | 310 | 2014-03-13 10:15 | 2014-03-13 13:45 | 3.5 | 1.0439 | 110.6491 | 0.00258% | 0.003429% | 0.00345% | 80 | 114 | 106 | Pulverizer Mills | 1-4 mill tripped due to air flow issues 6552310
BR2 | D1 | 18 | 310 | 2014-03-06 16:50 | 2014-03-06 19:00 | 2.1667 | 0.60185 | 101.1111 | 0.002357% | 0.003133% | 0.003153% | 130 | 180 | 168 | Pulverizer Mills | Broken shaft 2-2 mill 6543464
TC1 | D1 | 34 | 310 | 2014-03-09 10:15 | 2014-03-09 12:45 | 2.5 | 0.21341 | 81.7378 | 0.001906% | 0.002533% | 0.002549% | 375 | 410 | 383 | Pulverizer Mills | TC1 D coal mill breaker had an issue requiring replacement.
MC3 | D1 | 37 | 310 | 2014-03-05 05:15 | 2014-03-05 05:48 | 0.55 | 0.11442 | 45.0818 | 0.001051% | 0.001397% | 0.001406% | 335 | 423 | 394 | Pulverizer Mills | 3A Coal Mill - Breaker Issue
BR1 | D1 | 9 | 310 | 2014-03-17 06:32 | 2014-03-17 07:27 | 0.91667 | 0.23319 | 24.7178 | 0.0005763% | 0.0007659% | 0.0007708% | 85 | 114 | 106 | Pulverizer Mills | 1-4 mill air flow erratic 6552310
BR3 | D1 | 25 | 310 | 2014-03-24 10:30 | 2014-03-24 10:43 | 0.21667 | 0.057841 | 23.9462 | 0.0005583% | 0.000742% | 0.0007467% | 335 | 457 | 414 | Pulverizer Mills | 3-3 mill exhauster bearing high vibration
CR4 | D4 | 14 | 315 | 2014-03-05 23:09 | 2014-03-06 01:25 | 2.2667 | 0.5127 | 79.4683 | 0.001853% | 0.002462% |  | 130 | 168 | 155 | Pulverizer Coal Level Controls | 4A Mill - broken purge air line on bowl differential pressure indication was repa
TC1 | D1 | 38 | 340 | 2014-03-14 14:00 | 2014-03-14 16:15 | 2.25 | 0.15091 | 57.8003 | 0.001348% | 0.001791% | 0.001802% | 382.5 | 410 | 383 | Other Pulverizer Problems | 1D coal mill discharge valve was operating erratically affecting mill control. Ad
TC1 | D1 | 35 | 340 | 2014-03-13 08:15 | 2014-03-13 10:20 | 2.0833 | 0.13974 | 53.5188 | 0.001248% | 0.001658% | 0.001669% | 382.5 | 410 | 383 | Other Pulverizer Problems | The 1D Mill discharge valve was behaving erratically affecting mill control.
TC1 | D1 | 37 | 340 | 2014-03-13 10:46 | 2014-03-13 11:30 | 0.73333 | 0.049187 | 18.8386 | 0.0004392% | 0.0005838% | 0.0005875% | 382.5 | 410 | 383 | Other Pulverizer Problems | 1D mill discharge valve was operating erratically affecting mill control.
CR4 | D4 | 13 | 344 | 2014-02-28 22:00 | 2014-03-01 06:51 | 8.85 | 2.0018 | 310.2768 | 0.007234% | 0.009615% |  | 130 | 168 | 155 | Pulverizer Inspection | 4A Mill inspection
CR5 | D1 | 14 | 344 | 2014-03-21 23:21 | 2014-03-22 01:35 | 2.2333 | 0.62928 | 105.7193 | 0.002465% | 0.003276% | 0.003297% | 130 | 181 | 168 | Pulverizer Inspection | Checked 5B coal mill air chamber for buildup.
GH2 | PD | 17 | 345 | 2014-03-21 11:05 | 2014-03-27 12:02 | 144.95 | 13.9539 | 6656.0243 | 0.1552% |  |  | 460 | 509 | 477 | 2-4 Coal Mill Overhaul | 2-4 Mill out of service for overhaul.
GH2 | PD | 15 | 345 | 2014-03-06 12:00 | 2014-03-07 22:07 | 34.1167 | 3.2843 | 1566.6186 | 0.03653% |  |  | 460 | 509 | 477 | 2-4 Pulverizer Overhaul | 2-4 Mill out of service for scheduled overhaul.
GH1 | D1 | 18 | 346 | 2014-03-17 07:42 | 2014-03-17 12:14 | 4.5333 | 0.49981 | 240.407 | 0.005605% | 0.007449% | 0.007497% | 460 | 517 | 481 | Pulverizer Pyrite Removal System | 1-3 Mill out of service to inspect pyrite section.
GR3 | PD | 19 | 346 | 2014-03-18 22:10 | 2014-03-19 04:20 | 6.1667 | 1.5622 | 110.9178 | 0.002586% |  |  | 56 | 75 | 71 | Pulverizer Pyrite Removal System | Maint replacing 4-4 Pulv Pyrite inside gate.
GR3 | D1 | 20 | 346 | 2014-03-19 09:00 | 2014-03-19 11:17 | 2.2833 | 0.57844 | 41.0696 | 0.0009575% | 0.001273% | 0.001281% | 56 | 75 | 71 | Pulverizer Pyrite Removal System | 4-4 Pulv O/S for adjustments to Pulv pyrite inside gate.
BR3 | D1 | 27 | 350 | 2014-03-25 07:04 | 2014-03-25 11:00 | 3.9333 | 1.05 | 434.7151 | 0.01014% | 0.01347% | 0.01356% | 335 | 457 | 414 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | 3-5A burner line coal leak
BR3 | D1 | 28 | 350 | 2014-03-25 11:00 | 2014-03-25 12:06 | 1.1 | 0.26958 | 111.6079 | 0.002602% | 0.003458% | 0.00348% | 345 | 457 | 414 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | 3-5A burner line coal leak
BR2 | D1 | 22 | 350 | 2014-03-27 10:31 | 2014-03-27 13:13 | 2.7 | 0.525 | 88.2 | 0.002056% | 0.002733% | 0.00275% | 145 | 180 | 168 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | 2-2 mill burner line temperature high
BR2 | D1 | 21 | 350 | 2014-03-27 09:06 | 2014-03-27 10:05 | 0.98333 | 0.1912 | 32.1222 | 0.0007489% | 0.0009954% | 0.001002% | 145 | 180 | 168 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | 2-2 mill burner line temperature high
BR2 | D1 | 23 | 350 | 2014-03-27 14:25 | 2014-03-27 14:47 | 0.36667 | 0.071296 | 11.9778 | 0.0002793% | 0.0003712% | 0.0003735% | 145 | 180 | 168 | Pulverized Fuel and Air Piping (Pulverizer to Wind Box) | Inspect 2-1A burner line for pluggage
MC1 | D1 | 55 | 360 | 2014-03-22 13:40 | 2014-03-22 14:10 | 0.5 | 0.13636 | 41.3182 | 0.0009633% | 0.00128% | 0.001288% | 240 | 330 | 303 | Burners | 1B Mill - 1B4 Coal Burner High Temperature
MC4 | D1 | 30 | 360 | 2014-03-02 11:41 | 2014-03-02 12:14 | 0.55 | 0.08381 | 40.7314 | 0.0009496% | 0.001262% | 0.00127% | 445 | 525 | 486 | Burners | 4B Mill - 4B7 Coal Burner High Temperature
MC3 | D1 | 40 | 380 | 2014-03-24 03:18 | 2014-03-24 03:51 | 0.55 | 0.062411 | 24.5901 | 0.0005733% | 0.000762% | 0.0007668% | 375 | 423 | 394 | Light-off (Igniter) Systems (Including Fuel Supply) | 3D Coal Mill - 3D2 Lighter Could Not Get in Service
0
|  |  | (0200-0480) |  | Fuel Firing | 574.4664 | 107.1579 | 36695.4895 | 0.8555% | 0.8258% | 0.7815%
0
TC1 | NC | 31 | 510 | 2014-03-02 01:00 | 2014-03-02 01:20 | 0.33333 | [5 empty] | 0 | 410 | 383 | Main Steam Relief/Safety Valves | Non-curtailing derate for a planned, weekly valve check. Unit was available to re
BR3 | U1 | 20 | 740 | 2014-03-19 10:32 | 2014-03-19 12:29 | 1.95 | 1.95 | 807.3 | 0.01882% | 0.02502% | 0.02517% | 0 | 457 | 414 | Boiler Recirculation Pumps | Boiler trip due to BCWP differential pressure
BR3 | D1 | 18 | 740 | 2014-03-17 14:15 | 2014-03-18 | 9.75 | 0.57604 | 238.4803 | 0.00556% | 0.00739% | 0.007437% | 430 | 457 | 414 | Boiler Recirculation Pumps | 3-1 BCWP out of service
BR3 | D1 | 19 | 740 | 2014-03-19 10:13 | 2014-03-19 10:32 | 0.31667 | 0.27717 | 114.7484 | 0.002675% | 0.003556% | 0.003578% | 57 | 457 | 414 | Boiler Recirculation Pumps | Boiler trip due to BCWP differential pressure
GR3 | MO | 16 | 782 | 2014-03-08 13:20 | 2014-03-09 02:33 | 13.2167 | 13.2167 | 938.3833 | 0.02188% | 0.02908% |  | 0 | 75 | 71 | Headers and Caps | GR3 off line on Maint Outage for lower waterwall hand hole cap leak repair. Also
GH3 | PD | 42 | 855 | 2014-03-26 22:00 | 2014-03-27 00:36 | 2.6 | 0.20721 | 99.8755 | 0.002329% |  |  | 485 | 527 | 482 | Boiler Drum Relief/Safety Valves | Precision to set drum safeties.
MC4 | D1 | 32 | 876 | 2014-03-07 23:20 | 2014-03-08 03:55 | 4.5833 | 1.7897 | 869.7857 | 0.02028% | 0.02695% | 0.02712% | 320 | 525 | 486 | Soot Blower Controls | Sootblower Regulator - Repair Positioner
GH2 | D1 | 19 | 890 | 2014-03-29 11:16 | 2014-03-29 15:40 | 4.4 | 0.76935 | 366.9807 | 0.008556% | 0.01137% | 0.01144% | 420 | 509 | 477 | Bottom Ash Systems (Wet or Dry) | Unit 2 was derated due to wet ash system pluggage.
GH1 | U1 | 17 | 1000 | 2014-03-05 00:42 | 2014-03-05 23:00 | 22.3 | 22.3 | 10726.3 | 0.2501% | 0.3324% | 0.3345% | 0 | 517 | 481 | Furnace Wall Tube Leaks | Water water tube leak blew out on the upper slope of the boiler about 15
GR4 | U1 | 33 | 1000 | 2014-03-29 05:40 | 2014-03-30 04:03 | 22.3833 | 22.3833 | 2081.65 | 0.04853% | 0.0645% | 0.06491% | 0 | 100 | 93 | Furnace Wall Tube Leaks | Ops verified a waterwall tube leak in B5 at 0408, reported to Dispatch at 0413. O
BR2 | U1 | 20 | 1040 | 2014-03-10 14:50 | 2014-03-11 21:09 | 30.3167 | 30.3167 | 5093.2 | 0.1187% | 0.1578% | 0.1588% | 0 | 180 | 168 | First Superheater Tube Leaks | Tube leak in boiler penthouse area. 6550561
TC1 | NC | 42 | 1100 | 2014-03-29 | 2014-03-29 05:00 | 5 | [5 empty] | 0 | 410 | 383 | Furnace Wall Slagging or Fouling | Non-curtailing derate was placed on the unit to complete a planned boiler deslag.
CR5 | MO | 13 | 1160 | 2014-03-18 10:07 | 2014-03-19 16:52 | 30.75 | 30.75 | 5166 | 0.1204% | 0.1601% |  | 0 | 181 | 168 | First Reheater Slagging and Fouling | Replaced 1 reheat tube with dutchman.
CR4 | D1 | 20 | 1160 | 2014-03-26 22:00 | 2014-03-27 03:15 | 5.25 | 2.75 | 426.25 | 0.009938% | 0.01321% | 0.01329% | 80 | 168 | 155 | First Reheater Slagging or Fouling | Load limit to clean up boiler slag around the 7R and 5R retract area.
MC2 | D4 | 84 | 1160 | 2014-03-31 22:00 | 2014-04-01 | 1.9997 | 1.1514 | 344.2552 | 0.008026% | 0.01067% |  | 140 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 79 | 1160 | 2014-03-15 23:00 | 2014-03-16 04:47 | 5.7833 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
CR4 | NC | 17 | 1160 | 2014-03-19 22:00 | 2014-03-20 03:20 | 5.3333 | [5 empty] | 0 | 168 | 155 | First Reheater Slagging or Fouling | Boiler deslag
CR4 | NC | 16 | 1160 | 2014-03-18 22:30 | 2014-03-19 03:50 | 5.3333 | [5 empty] | 0 | 168 | 155 | First Reheater Slagging or Fouling | Boiler deslag
MC2 | NC | 80 | 1160 | 2014-03-16 22:30 | 2014-03-17 03:45 | 5.25 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC1 | NC | 53 | 1160 | 2014-03-16 00:30 | 2014-03-16 05:41 | 5.1833 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
CR4 | NC | 21 | 1160 | 2014-03-27 23:00 | 2014-03-28 04:10 | 5.1667 | [5 empty] | 0 | 168 | 155 | First Reheater Slagging or Fouling | Load limit to clean up boiler slag around the 7R and 5R retract area.
MC2 | NC | 72 | 1160 | 2014-03-04 23:30 | 2014-03-05 04:30 | 5 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC1 | NC | 50 | 1160 | 2014-03-06 22:45 | 2014-03-07 03:30 | 4.75 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 82 | 1160 | 2014-03-25 22:45 | 2014-03-26 03:30 | 4.75 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC2 | NC | 75 | 1160 | 2014-03-06 22:45 | 2014-03-07 03:20 | 4.5833 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 83 | 1160 | 2014-03-30 22:35 | 2014-03-31 03:04 | 4.4833 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First ReheaterFull Load Available as Needed
MC1 | NC | 51 | 1160 | 2014-03-07 13:45 | 2014-03-07 17:40 | 3.9167 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 78 | 1160 | 2014-03-07 13:45 | 2014-03-07 17:40 | 3.9167 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC1 | NC | 49 | 1160 | 2014-03-05 23:20 | 2014-03-06 01:00 | 1.6667 | [5 empty] | 0 | 330 | 303 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
MC2 | NC | 74 | 1160 | 2014-03-06 00:30 | 2014-03-06 01:00 | 0.5 | [5 empty] | 0 | 330 | 299 | First Reheater Slagging or Fouling | Boiler Deslag - First Reheater
GH3 | D1 | 39 | 1400 | 2014-03-19 06:00 | 2014-03-20 07:00 | 25 | 0.80645 | 388.7097 | 0.009063% | 0.01204% | 0.01212% | 510 | 527 | 482 | Forced Draft Fans | FD Fan limit, 3-1 FD Fan Inlet Vane needs attention.
GH3 | D1 | 30 | 1400 | 2014-03-08 19:35 | 2014-03-09 05:28 | 9.8833 | 0.16879 | 81.3546 | 0.001897% | 0.002521% | 0.002537% | 518 | 527 | 482 | Forced Draft Fans | FD Fans out the top.
GH3 | D1 | 29 | 1400 | 2014-03-07 19:29 | 2014-03-07 23:10 | 3.6833 | 0.069892 | 33.6882 | 0.0007854% | 0.001044% | 0.001051% | 517 | 527 | 482 | Forced Draft Fans | FD fans out the top.
GH3 | D1 | 33 | 1400 | 2014-03-14 05:18 | 2014-03-14 09:57 | 4.65 | 0.017647 | 8.5059 | 0.0001983% | 0.0002636% | 0.0002652% | 525 | 527 | 482 | Forced Draft Fans | FD Fan Limit, 3-1 FD Fan Inlet Vane needs attention.
GH3 | D1 | 35 | 1400 | 2014-03-14 11:08 | 2014-03-14 12:26 | 1.3 | 0.017268 | 8.323 | 0.000194% | 0.0002579% | 0.0002595% | 520 | 527 | 482 | Forced Draft Fans | FD Fan Limit, 3-1 ID Fan Vane needs attention.
MC2 | D1 | 77 | 1455 | 2014-03-07 07:23 | 2014-03-07 11:52 | 4.4833 | 0.095101 | 28.4352 | 0.000663% | 0.0008811% | 0.0008867% | 323 | 330 | 299 | Induced Draft Fans | 2B Induced Draft Fan - Run Back
MC2 | D1 | 76 | 1455 | 2014-03-07 05:45 | 2014-03-07 07:23 | 1.6333 | 0.089091 | 26.6382 | 0.0006211% | 0.0008254% | 0.0008307% | 312 | 330 | 299 | Induced Draft Fans | 2B Induced Draft Fan - Run Back
TC1 | U1 | 32 | 1471 | 2014-03-06 01:06 | 2014-03-06 12:48 | 11.7 | 11.7 | 4481.1 | 0.1045% | 0.1389% | 0.1397% | 0 | 410 | 383 | ID Fan Motors - Variable Speed Drive | The VFD on the 1B ID fan sent a false alarm due to a low-low cooling supply alarm
MC4 | D1 | 26 | 1710 | 2014-02-21 10:13 | 2014-03-04 06:41 | 260.4667 | 1.4884 | 723.3531 | 0.01686% | 0.02241% | 0.02256% | 522 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
MC4 | D1 | 31 | 1710 | 2014-03-04 08:45 | 2014-03-12 18:14 | 201.4833 | 1.1513 | 559.548 | 0.01305% | 0.01734% | 0.01745% | 522 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
MC4 | D1 | 34 | 1710 | 2014-03-13 06:15 | 2014-03-14 23:47 | 41.5333 | 0.23733 | 115.344 | 0.002689% | 0.003574% | 0.003597% | 522 | 525 | 486 | Combustion/Steam Condition Controls | Max Steam Flow Issue
GH2 | D1 | 18 | 1850 | 2014-03-21 19:34 | 2014-03-22 06:10 | 10.6 | 3.3112 | 1579.4417 | 0.03682% | 0.04894% | 0.04925% | 350 | 509 | 477 | Boiler Water Condition | Boiler water chemistry - high silica during start up.
MC4 | D1 | 37 | 1850 | 2014-03-31 19:30 | 2014-04-01 | 4.4997 | 1.6285 | 791.4369 | 0.01845% | 0.02452% | 0.02468% | 335 | 525 | 486 | Boiler Water Condition (not Feedwater Water Quality) | High Silica
MC4 | NC | 36 | 1850 | 2014-03-30 19:15 | 2014-03-31 19:30 | 24.25 | [5 empty] | 0 | 525 | 486 | Boiler Water Condition (not Feedwater Water Quality) | High Silica @ Cold Start Up
CR5 | D4 | 11 | 1980 | 2014-03-06 21:15 | 2014-03-06 22:56 | 1.6833 | 0.28831 | 48.4354 | 0.001129% | 0.001501% |  | 150 | 181 | 168 | Boiler Safety Valve Test | Precision Services testing & inspecting safety valves
CR6 | NC | 27 | 1980 | 2014-03-13 21:13 | 2014-03-14 00:18 | 3.0833 | [5 empty] | 0 | 261 | 240 | Boiler Safety Valve Test | Electrostatic boiler valve safety testing (pre outage).
0
|  |  | (0500-1999) |  | Boiler | 830.6994 | 149.5067 | 36147.5229 | 0.8428% | 1.117% | 0.9215%
0
CR4 | MO | 19 | 3110 | 2014-03-24 20:40 | 2014-03-25 18:55 | 22.25 | 22.25 | 3448.75 | 0.08041% | 0.1069% |  | 0 | 168 | 155 | Condenser Tube Leaks | Unit removed from service due to high silica. Root cause is from condenser tube l
GR4 | NC | 30 | 3112 | 2014-03-20 09:30 | 2014-03-20 10:00 | 0.5 | [5 empty] | 0 | 105 | 98 | Condenser Tube Fouling Tube Side | GR4 load reduction for condenser backwash.
GR3 | NC | 15 | 3190 | 2014-03-08 07:45 | 2014-03-08 12:49 | 5.0667 | [5 empty] | 0 | 75 | 71 | Condensing System Air Leakage | Conco Services helium testing GR3 for air inleakage.
BR2 | D1 | 17 | 3410 | 2014-03-03 07:22 | 2014-03-06 16:50 | 81.4667 | 33.9444 | 5702.6667 | 0.133% | 0.1767% | 0.1778% | 105 | 180 | 168 | 2-2 Boiler Feedwater Pump Oil Leak | 2-2 BFP oil leak 6546733
TC1 | D1 | 39 | 3412 | 2014-03-15 01:55 | 2014-03-15 08:50 | 6.9167 | 0.27414 | 104.9942 | 0.002448% | 0.003253% | 0.003274% | 393.75 | 410 | 383 | Feedwater Pump Drive - Steam Turbine | The 1A TDBFP had an emergency governor trip removing it from service.
TC1 | D1 | 40 | 3412 | 2014-03-15 11:32 | 2014-03-15 13:33 | 2.0167 | 0.079929 | 30.6128 | 0.0007137% | 0.0009486% | 0.0009546% | 393.75 | 410 | 383 | Feedwater Pump Drive - Steam Turbine | The 1A TDBFP had an oil leak which required removal from service to repair.
CR6 | D1 | 26 | 3415 | 2014-03-13 04:58 | 2014-03-13 05:55 | 0.95 | 0.40402 | 96.9655 | 0.002261% | 0.003005% | 0.003024% | 150 | 261 | 240 | Feedwater Pump/Drive Lube Oil System | Lube oil pressure indication low
GH4 | D1 | 11 | 3440 | 2014-03-24 08:44 | 2014-03-26 02:30 | 41.7667 | 1.7989 | 883.279 | 0.02059% | 0.02737% | 0.02754% | 511 | 534 | 491 | High Pressure Heater Tube Leaks | HP heaters are out of service to repair a tube leak in 'G' HP hea
GR3 | U1 | 18 | 3441 | 2014-03-10 02:39 | 2014-03-10 03:21 | 0.7 | 0.7 | 49.7 | 0.001159% | 0.00154% | 0.00155% | 0 | 75 | 71 | Other High Pressure Heater Problems | GR3 tripped due to high level in 3-4 HP Heater shortly after startup.
CR6 | U1 | 29 | 3669 | 2014-03-31 08:13 | 2014-03-31 13:34 | 5.35 | 5.35 | 1284 | 0.02994% | 0.03979% | 0.04004% | 0 | 261 | 240 | Other 4000-7000-volt Problems | I/E personnel inadvertently cold transfered the 4KV A Buse power supply.
0
|  |  | (3110-3999) |  | Balance Of Plant | 166.9833 | 64.8015 | 11600.9681 | 0.2705% | 0.3595% | 0.2542%
0
MC2 | NC | 73 | 4490 | 2014-03-05 06:00 | 2014-03-05 12:05 | 6.0833 | [5 empty] | 0 | 330 | 299 | Turbine Performance Testing | Capability Test - Full Load
GH4 | D1 | 12 | 4499 | 2014-03-26 06:30 | 2014-04-01 | 137.4997 | 1.03 | 505.7106 | 0.01179% | 0.01567% | 0.01577% | 530 | 534 | 491 | Other Miscellaneous Steam Turbine Problems | Turbine performance due to copper deposition.
0
|  |  | (4000-4499) |  | Steam Turbine | 143.5831 | 1.03 | 505.7106 | 0.01179% | 0.01567% | 0.01577%
0
0
|  |  | (4500-4899) |  | Generator | 0 | 0 | 0 | 0% | 0% | 0%
CR4 | D1 | 18 | 8000 | 2014-03-23 20:18 | 2014-03-23 20:29 | 0.18333 | 0.041468 | 6.4276 | 0.0001499% | 0.0001992% | 0.0002004% | 130 | 168 | 155 | Chemical Feed Storage; Mill Feeders And Conveyors | B LST tank solids buildup
CR5 | D1 | 15 | 8000 | 2014-03-23 20:16 | 2014-03-23 20:29 | 0.21667 | 0.025138 | 4.2232 | 9.846e-05% | 0.0001309% | 0.0001317% | 160 | 181 | 168 | Chemical Feed Storage; Mill Feeders And Conveyors | B LST tank solids buildup
CR6 | U1 | 25 | 8100 | 2014-03-11 11:19 | 2014-03-12 19:03 | 31.7333 | 31.7333 | 7616 | 0.1776% | 0.236% | 0.2375% | 0 | 261 | 240 | FGD Absorber Module Cleaning | FGD module cleaning - solids buildup in module spray header, resulting from incons
CR6 | D1 | 24 | 8110 | 2014-03-11 09:26 | 2014-03-11 11:18 | 1.8667 | 0.72235 | 173.364 | 0.004042% | 0.005372% | 0.005406% | 160 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
CR6 | D1 | 23 | 8110 | 2014-03-11 07:36 | 2014-03-11 09:26 | 1.8333 | 0.35824 | 85.977 | 0.002005% | 0.002664% | 0.002681% | 210 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
CR6 | D1 | 20 | 8110 | 2014-03-10 10:15 | 2014-03-10 12:13 | 1.9667 | 0.30894 | 74.1456 | 0.001729% | 0.002298% | 0.002312% | 220 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
CR6 | D1 | 22 | 8110 | 2014-03-11 06:11 | 2014-03-11 07:36 | 1.4167 | 0.16826 | 40.3831 | 0.0009415% | 0.001251% | 0.001259% | 230 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
CR6 | D1 | 21 | 8110 | 2014-03-10 20:31 | 2014-03-10 21:11 | 0.66667 | 0.05364 | 12.8736 | 0.0003001% | 0.0003989% | 0.0004015% | 240 | 261 | 240 | Wet Scrubber - Spray Nozzles | Solids buildup in module spray header, resulting from inconsistent PH control.
MC4 | D4 | 33 | 8160 | 2014-03-08 23:30 | 2014-03-09 06:36 | 7.1 | 2.5019 | 1215.9257 | 0.02835% | 0.03768% |  | 340 | 525 | 486 | Wet Scrubber Mist Eliminators/demisters & Washdown | FGD Mist Eliminator - Wash Line Tie In
MC3 | D4 | 38 | 8160 | 2014-03-08 23:30 | 2014-03-09 06:36 | 7.1 | 1.6449 | 648.0974 | 0.01511% | 0.02008% |  | 325 | 423 | 394 | Wet Scrubber Mist Eliminators/demisters & Washdown | FGD Mist Eliminator - Wash Line Tie In
CR6 | D1 | 18 | 8199 | 2014-03-08 05:11 | 2014-03-08 08:18 | 3.1167 | 0.52542 | 126.0996 | 0.00294% | 0.003907% | 0.003932% | 217 | 261 | 240 | Other Wet Scrubber Problems | SO2 excursion during load pickup. Contributing factors were the 6B reaction tank
BR2 | MO | 15 | 8560 | 2014-02-28 12:26 | 2014-03-02 18:19 | 53.8833 | 53.8833 | 9052.4 | 0.2111% | 0.2805% |  | 0 | 180 | 168 | Electrostatic Precipitator Fields Out | Precipitator fields out of service and tube leak repair 6546848
0
|  |  | (8000-8835) |  | Pollution Control Equip. | 111.0833 | 91.9669 | 19055.9168 | 0.4443% | 0.5905% | 0.2538%
BR1 | D1 | 10 | 9205 | 2014-03-18 08:37 | 2014-03-18 10:37 | 2 | 0.12281 | 13.0175 | 0.0003035% | 0.0004034% | 0.0004059% | 107 | 114 | 106 | Poor quality fuel; heat content | Limited by coal quality
BR1 | D1 | 11 | 9205 | 2014-03-18 10:37 | 2014-03-18 10:51 | 0.23333 | 0.0040936 | 0.43392 | 1.012e-05% | 1.345e-05% | 1.353e-05% | 112 | 114 | 106 | Poor quality fuel; heat content | Limited by coal quality
|  |  | (9000-9340) |  | External | 2.2333 | 0.1269 | 13.4515 | 0.0003136% | 0.0004168% | 0.0004195%
GR4 | D1 | 31 | 9630 | 2014-03-28 21:33 | 2014-03-29 01:15 | 3.7 | 0.185 | 17.205 | 0.0004011% | 0.0005331% | 0.0005365% | 95 | 100 | 93 | Opacity - Fossil Steam Units | GR4 load reduction to blow soot due to frequent opacity spikes.
GR4 | D1 | 29 | 9630 | 2014-03-12 04:45 | 2014-03-12 05:31 | 0.76667 | 0.073016 | 7.1556 | 0.0001668% | 0.0002217% | 0.0002231% | 95 | 105 | 98 | Opacity - Fossil Steam Units | GR4 load reduced due to opacity limitations.
GR4 | D1 | 32 | 9630 | 2014-03-29 04:06 | 2014-03-29 05:40 | 1.5667 | 0.047 | 4.371 | 0.0001019% | 0.0001354% | 0.0001363% | 97 | 100 | 93 | Opacity - Fossil Steam Units | GR4 load reduction due to opacity. Ops has found a waterwall tube leak in B5.
GH3 | PD | 23 | 9650 | 2014-02-28 22:30 | 2014-03-01 03:08 | 4.6333 | 2.6112 | 1258.5962 | 0.02934% |  |  | 230 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. Working on sorbent blower.
GH3 | D1 | 36 | 9650 | 2014-03-14 12:26 | 2014-03-15 05:15 | 16.8167 | 2.3294 | 1122.7917 | 0.02618% | 0.03479% | 0.03501% | 454 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. ID Fan Outlet Injection plugged.
GH3 | D1 | 26 | 9650 | 2014-03-05 17:28 | 2014-03-06 01:30 | 8.0333 | 1.1738 | 565.7479 | 0.01319% | 0.01753% | 0.01764% | 450 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2S04 within limit. Outlet injection lines plugged.
GH3 | D1 | 24 | 9650 | 2014-03-02 18:15 | 2014-03-02 21:00 | 2.75 | 0.82448 | 397.3985 | 0.009265% | 0.01231% | 0.01239% | 369 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. Low level on Silo feeding outlet i
GH3 | D1 | 27 | 9650 | 2014-03-07 04:20 | 2014-03-07 06:05 | 1.75 | 0.42173 | 203.2723 | 0.004739% | 0.006299% | 0.006339% | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. 3-2B Blow through valve drive chain
GH3 | D1 | 38 | 9650 | 2014-03-17 09:30 | 2014-03-17 11:03 | 1.55 | 0.37353 | 180.0412 | 0.004198% | 0.005579% | 0.005614% | 400 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2So4 within limit. 3-2B Drop Through Rotary valve driv
GH3 | D1 | 37 | 9650 | 2014-03-15 06:24 | 2014-03-15 10:54 | 4.5 | 0.31594 | 152.2827 | 0.00355% | 0.004719% | 0.004749% | 490 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limit. ID Faan Outlet Injection plugged.
GH3 | D1 | 25 | 9650 | 2014-03-05 07:08 | 2014-03-05 08:03 | 0.91667 | 0.25569 | 123.2438 | 0.002873% | 0.003819% | 0.003843% | 380 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | H2SO4 running high due to outlet injection probe pluggage. Redu
GH3 | D1 | 41 | 9650 | 2014-03-25 11:38 | 2014-03-25 12:35 | 0.95 | 0.1388 | 66.9038 | 0.00156% | 0.002073% | 0.002086% | 450 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Reduced load to keep H2SO4 within limit. Inlet probes were plug
GH4 | D1 | 9 | 9650 | 2014-03-05 17:35 | 2014-03-05 18:09 | 0.56667 | 0.089139 | 43.767 | 0.00102% | 0.001356% | 0.001365% | 450 | 534 | 491 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Temporary lime silo plugged at mixer.
GH3 | D1 | 34 | 9650 | 2014-03-14 09:57 | 2014-03-14 11:08 | 1.1833 | 0.08308 | 40.0447 | 0.0009336% | 0.001241% | 0.001249% | 490 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO3 within limit. ID Fan Outlet Injection plugged.
GH4 | D1 | 10 | 9650 | 2014-03-05 20:48 | 2014-03-05 22:01 | 1.2167 | 0.077466 | 38.0356 | 0.0008868% | 0.001179% | 0.001186% | 500 | 534 | 491 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Temporary lime silo plugged at mixer.
GH3 | D1 | 32 | 9650 | 2014-03-14 03:36 | 2014-03-14 05:18 | 1.7 | 0.03871 | 18.6581 | 0.000435% | 0.0005782% | 0.0005818% | 515 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2SO4 within limits, ID Fan Injection Outlets plugged.
GH3 | D1 | 28 | 9650 | 2014-03-07 07:30 | 2014-03-07 08:00 | 0.5 | 0.011385 | 5.4877 | 0.0001279% | 0.00017% | 0.0001711% | 515 | 527 | 482 | Other Stack Or Exhaust Emissions -fossil Stm Unit | Keeping H2S04 within limit. 3-2 Blow through drive chain valve
BR3 | NC | 16 | 9656 | 2014-03-12 08:45 | 2014-03-12 20:38 | 11.8833 | [5 empty] | 0 | 457 | 414 | Other stack or exhaust emissions testing - fossil | RATA testing at 425 mw.
BR3 | NC | 17 | 9656 | 2014-03-13 12:30 | 2014-03-13 17:00 | 4.5 | [5 empty] | 0 | 457 | 414 | Other stack or exhaust emissions testing - fossil | RATA testing at 425 mw.
BR1 | NC | 7 | 9656 | 2014-03-11 11:42 | 2014-03-11 16:08 | 4.4333 | [5 empty] | 0 | 114 | 106 | Other stack or exhaust emissions testing - fossil | Low load RATA testing
BR3 | NC | 13 | 9656 | 2014-03-11 11:42 | 2014-03-11 13:51 | 2.15 | [5 empty] | 0 | 457 | 414 | Other stack or exhaust emissions testing - fossil | Low load RATA testing
BR3 | NC | 15 | 9656 | 2014-03-11 15:36 | 2014-03-11 16:08 | 0.53333 | [5 empty] | 0 | 457 | 414 | Other stack or exhaust emissions testing - fossil | Low load RATA testing
|  |  | (9504-9720) |  | Reg., Safety, Envrn. | 76.6 | 9.0494 | 4245.0028 | 0.09897% | 0.09254% | 0.09313%
|  |  | (9900-9999) |  | Per., and Proced. Errors | 0 | 0 | 0 | 0% | 0% | 0%
All Steam | [5 empty] | 4013.1979 | 2531.1883 | 1064180.9672 | 25.87% | 3.001% | 2.32%
PR13 | PO | 4 | 4720 | 2014-02-15 06:08 | 2014-03-03 08:25 | 386.2833 | 386.2833 | 67599.5833 |  |  |  | 0 | 176 | 175 | Generator Synchronization Equipment | Generator synchronization equipment modifications. Replacing all generator protec
|  |  | (4500-4899) |  | Generator | 386.2833 | 386.2833 | 67599.5833 | 0% | 0% | 0%
BR6 | PO | 24 | 5272 | 2014-03-21 22:06 | 2014-04-01 | 241.8997 | 241.8997 | 41364.8525 |  |  |  | 0 | 172 | 171 | Gas Turbine - Boroscope Inspection | Annual Planned outage: Boroscope Inspection, Fuel Oil Stop valves installed, Fuel
BR7 | PO | 30 | 5272 | 2014-03-29 13:48 | 2014-04-01 | 58.1997 | 58.1997 | 9952.1525 |  |  |  | 0 | 172 | 171 | Gas Turbine - Boroscope Inspection | Planned outage for opportunity inspection.
|  |  | (5000-5299) |  | Gas Turbine | 300.0994 | 300.0994 | 51317.005 | 0% | 0% | 0%
PR13 | MO | 9 | 3629 | 2014-03-21 06:00 | 2014-03-21 14:25 | 8.4167 | 8.4167 | 1472.9167 |  |  |  | 0 | 176 | 175 | Other Switchyard or High Voltage System Problems | Carded the buse to remove jumpers for isolation purposes to replace the buse work.
TC9 | SF | 33 | 3631 | 2014-03-18 05:09 | 2014-03-18 06:54 | 1.75 | 1.75 | 308 |  |  |  | 0 | 180 | 176 | 400-700-volt Circuit Breakers | Startup failure due to TC9 MCC #2 feed breaker opening cutting power to inservice
TC10 | U1 | 37 | 3631 | 2014-03-18 06:09 | 2014-03-18 06:19 | 0.16667 | 0.16667 | 29.3333 |  |  |  | 0 | 180 | 176 | 400-700-volt Circuit Breakers | Forced outage due to TC9 MCC #2 feed breaker opening. Control power to TC9/10 LCI
PR13 | U1 | 5 | 3860 | 2014-03-03 08:25 | 2014-03-06 13:33 | 77.1333 | 77.1333 | 13498.3333 |  |  |  | 0 | 176 | 175 | Fire Protection System Pumps | GSU and aux transformer fire pump is seized up.
|  |  | (3110-3999) |  | Balance Of Plant | 87.4667 | 87.4667 | 15308.5833 | 0% | 0% | 0%
PR13 | SF | 11 | 4610 | 2014-03-25 05:45 | 2014-03-25 06:24 | 0.65 | 0.65 | 113.75 |  |  |  | 0 | 176 | 175 | Hydrogen Cooling System Piping And Valves | Hydrogen fill valve was frozen and would not open when needed.
PR13 | MO | 6 | 4720 | 2014-03-06 13:33 | 2014-03-07 11:04 | 21.5167 | 21.5167 | 3765.4167 |  |  |  | 0 | 176 | 175 | Generator Synchronization Equipment | Relay testing is needed to complete scope of work for previous Planned Outage.
PR13 | MO | 7 | 4720 | 2014-03-07 11:31 | 2014-03-07 11:59 | 0.46667 | 0.46667 | 81.6667 |  |  |  | 0 | 176 | 175 | Generator Synchronization Equipment | Relay testing is needed to complete scope of work for previous Planned Outage.
|  |  | (4500-4899) |  | Generator | 22.6333 | 22.6333 | 3960.8333 | 0% | 0% | 0%
TC5 | SF | 23 | 5016 | 2014-03-02 21:40 | 2014-03-03 01:59 | 4.3167 | 4.3167 | 759.7333 |  |  |  | 0 | 180 | 176 | High Pressure Compressor - Bleed Valves | Startup failure due to issue with compressor bleed valve.
BR8 | U1 | 23 | 5016 | 2014-03-31 05:56 | 2014-03-31 06:05 | 0.15 | 0.15 | 19.2 |  |  |  | 0 | 129 | 128 | High Pressure Compressor - Bleed Valves | Trip due to compressor blow off valve not being closed. Unit tripped immediately
BR7 | MO | 25 | 5041 | 2014-03-21 22:06 | 2014-03-22 16:00 | 17.9 | 17.9 | 3060.9 |  |  |  | 0 | 172 | 171 | Gas Turbine - Fuel Piping And Valves | Outage to install fuel flexibility standpipes.
BR11 | SF | 27 | 5041 | 2014-03-19 10:23 | 2014-03-19 12:46 | 2.3833 | 2.3833 | 305.0667 |  |  |  | 0 | 129 | 128 | Gas Turbine - Fuel Piping And Valves | Control Gas Valve swinging during start up.
TC6 | SF | 46 | 5041 | 2014-03-18 05:26 | 2014-03-18 05:50 | 0.4 | 0.4 | 70.4 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Startup failure due to gas valves not controlling properly.
TC7 | SF | 18 | 5041 | 2014-03-02 21:40 | 2014-03-02 21:51 | 0.18333 | 0.18333 | 32.2667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Fuel Piping And Valves | Startup failure due to high hazardous gas alarm.
TC5 | U1 | 43 | 5049 | 2014-03-28 05:45 | 2014-03-28 06:14 | 0.48333 | 0.48333 | 85.0667 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Fuel System Problems | Forced outage due to over temperature of the fuel gas heater.
TC6 | U1 | 53 | 5049 | 2014-03-28 05:45 | 2014-03-28 06:14 | 0.48333 | 0.48333 | 85.0667 |  |  |  | 0 | 180 | 176 | Other Gas Turbine Fuel System Problems | Forced outage due to over temperature of fuel gas heater.
TC9 | SF | 30 | 5130 | 2014-03-16 18:25 | 2014-03-16 20:27 | 2.0333 | 2.0333 | 357.8667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Startup failure due to 89SS not disengaging on TC10.
TC10 | U1 | 33 | 5130 | 2014-03-16 18:25 | 2014-03-16 20:27 | 2.0333 | 2.0333 | 357.8667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to 89SS failing to disengage.
TC10 | U1 | 29 | 5130 | 2014-03-08 08:03 | 2014-03-08 08:50 | 0.78333 | 0.78333 | 137.8667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to 89SS failing to disengage.
TC10 | U1 | 41 | 5130 | 2014-03-20 08:30 | 2014-03-20 09:03 | 0.55 | 0.55 | 96.8 |  |  |  | 0 | 180 | 176 | Gas Turbine - Starting System (including Motor) | Forced outage due to issue with 89SS.
CR11 | MO | 11 | 5130 | 2014-03-20 06:30 | 2014-03-20 13:03 | 6.55 | 6.55 | 91.7 |  |  |  | 0 | 14 | 14 | Gas Turbine - Starting System (including Motor) | Annual servicing of the diesel enginees. Changing oil and filters, checking hoses
Z1 | MO | 4 | 5130 | 2014-03-21 06:30 | 2014-03-21 10:35 | 4.0833 | 4.0833 | 65.3333 |  |  |  | 0 | 16 | 16 | Gas Turbine - Starting System (including Motor) | Annual servicing of the diesel engines. Changing oil and filters, checking hoses,
PR11 | MO | 4 | 5130 | 2014-03-19 07:00 | 2014-03-19 10:50 | 3.8333 | 3.8333 | 49.8333 |  |  |  | 0 | 13 | 13 | Gas Turbine - Starting System (including Motor) | Annual servicing of the diesel engines. Changing oil and filters, checking hoses,
BR6 | U1 | 21 | 5160 | 2014-03-13 08:59 | 2014-03-14 17:25 | 32.4333 | 32.4333 | 5546.1 |  |  |  | 0 | 172 | 171 | Gas Turbine - Cooling And Seal Air System | Air Leak on HP quench cooler.
TC9 | MO | 27 | 5160 | 2014-03-07 06:41 | 2014-03-07 12:37 | 5.9333 | 5.9333 | 1044.2667 |  |  |  | 0 | 180 | 176 | Gas Turbine - Cooling And Seal Air System | Maintenance outage to replace exhaust frame blower motor.
BR7 | U1 | 27 | 5160 | 2014-03-24 04:51 | 2014-03-24 06:53 | 2.0333 | 2.0333 | 347.7 |  |  |  | 0 | 172 | 171 | Gas Turbine - Cooling And Seal Air System | Tripped unit due to high temperature on HP quench system. Problem looks to be tha
BR6 | U1 | 18 | 5160 | 2014-03-05 13:12 | 2014-03-05 14:45 | 1.55 | 1.55 | 265.05 |  |  |  | 0 | 172 | 171 | Gas Turbine - Cooling And Seal Air System | Leak on water injection lance on HP quench vessel.
PR12 | U1 | 4 | 5170 | 2014-02-19 10:25 | 2014-03-06 13:33 | 363.1333 | 363.1333 | 10167.7333 |  |  |  | 0 | 28 | 28 | Gas Turbine - Cooling Water System | Fire pump that supplies cooling water locked up.
BR9 | U1 | 17 | 5246 | 2014-03-04 09:27 | 2014-03-04 10:06 | 0.65 | 0.65 | 89.7 |  |  |  | 0 | 139 | 138 | Gas Turbine Control System - Hardware Problems.... | Unit tripped when unit 11's MOS opened.
PR12 | U1 | 6 | 5250 | 2014-03-11 11:34 | 2014-03-12 10:22 | 22.8 | 22.8 | 638.4 |  |  |  | 0 | 28 | 28 | Other Controls And Instrument Problems | The Active Speed Probe is having erratic readings.
BR10 | MO | 12 | 5272 | 2014-02-28 10:48 | 2014-03-02 13:50 | 51.0333 | 51.0333 | 7042.6 |  |  |  | 0 | 139 | 138 | Gas Turbine - Boroscope Inspection | Eddy current inspection of R3 blade and boroscope of turbine section.
|  |  | (5000-5299) |  | Gas Turbine | 525.7333 | 0 | 0 | 0% | 0% | 0%
|  |  | (8000-8835) |  | Pollution Control Equip. | 0 | 0 | 0 | 0% | 0% | 0%
|  |  | (9000-9340) |  | External | 0 | 0 | 0 | 0% | 0% | 0%
|  |  | (9504-9720) |  | Reg., Safety, Envrn. | 0 | 0 | 0 | 0% | 0% | 0%
|  |  | (9504-9720) |  | Reg., Safety, Envrn. | 0 | 0 | 0 | 0% | 0% | 0%
|  |  | (9900-9999) |  | Per., and Proced. Errors | 0 | 0 | 0 | 0% | 0% | 0%

## MAR-14 BTF Impact By Cause Code
Outage | Unit | Event | Event | Cause | Event | Event | Event | Equiv. | MWH | EAF | EUOR | EFOR | Unit | Unit | Unit | Event | Event
Count | Name | Type | No | Code | Start | End | Hours | Hours | Lost | Lost | Impact | Impact | GAC | GMC | NMC | Cause | Description
0
1 | GH1 | U1 | 17 | 1000 | 2014-03-05 00:42 | 2014-03-05 23:00 | 22.3 | 22.3 | 10726.3 | 0.2501% | 0.3324% | 0.3345% | 0 | 517 | 481 | Furnace Wall Tube Leaks | Water water tube leak blew out on the upper slope of the boiler about 15
2 | GR4 | U1 | 33 | 1000 | 2014-03-29 05:40 | 2014-03-30 04:03 | 22.3833 | 22.3833 | 2081.65 | 0.04853% | 0.0645% | 0.06491% | 0 | 100 | 93 | Furnace Wall Tube Leaks | Ops verified a waterwall tube leak in B5 at 0408, reported to Dispatch at 0413. O
0
2 |  |  |  | (1000-1030) |  | Waterwall BTF | 44.6833 | 44.6833 | 12807.95 | 0.2986% | 0.3969% | 0.3994%
0
1 | BR2 | U1 | 20 | 1040 | 2014-03-10 14:50 | 2014-03-11 21:09 | 30.3167 | 30.3167 | 5093.2 | 0.1187% | 0.1578% | 0.1588% | 0 | 180 | 168 | First Superheater Tube Leaks | Tube leak in boiler penthouse area. 6550561
0
1 |  |  |  | (1035-1050) |  | Superheater BTF | 30.3167 | 30.3167 | 5093.2 | 0.1187% | 0.1578% | 0.1588%
0
0
0 |  |  |  | (1060-1070) |  | Reheater BTF | 0 | 0 | 0 | 0% | 0% | 0%
0
0
0 |  |  |  | (1080-1099) |  | Economizer BTF | 0 | 0 | 0 | 0% | 0% | 0%
3 | All Steam |  |  |  |  | All BTF | 75 | 75 | 17901.15 | 0.4174% | 0.5547% | 0.5582%
46000%
| D1 | 50 | 346 | 2011-09-09 14:18 | 2011-09-09 17:09 | 2.85 | 0.40714 | 189.7286 |  |  |  | 420 | 490 | 466 | PULVERIZER PYRITE REMOVAL SYSTEM | Load Reduction #412-1 Mill pyrite section plugged.
| D1 | 51 | 350 | 2011-09-09 17:16 | 2011-09-10 16:30 | 23.2333 | 1.8966 | 883.815 |  |  |  | 450 | 490 | 466 | PULVERIZED FUEL AND AIR PIPING (PULVERIZER TO WIND BOX) | Load Reduction #422-1 Mill C burner line fire.
| D1 | 52 | 250 | 2011-09-10 00:38 | 2011-09-10 04:33 | 3.9167 | 0.51956 | 242.1139 |  |  |  | 425 | 490 | 466 | PULVERIZER FEEDERS | Load Reduction #432-3 Feeder had a bad carrier roll.
| D1 | 53 | 410 | 2011-09-12 13:05 | 2011-09-12 13:26 | 0.35 | 0.075 | 34.95 |  |  |  | 385 | 490 | 466 | OTHER DUCT BURNER PROBLEMS | Load Reduction #442-2 Mill 'C' burner temperature got hot. Took mill off to inspe
| D1 | 54 | 3410 | 2011-09-15 07:38 | 2011-09-15 08:34 | 0.93333 | 0.34286 | 159.7714 |  |  |  | 310 | 490 | 466 | FEEDWATER PUMP | Load Reduction #452-2 BFP inboard oil seal lost its seal and was leaking oil.
| MO | 55 | 1488 | 2011-09-23 22:03 | 2011-09-26 20:01 | 69.9667 | 69.9667 | 32604.4667 |  |  |  | 0 | 490 | 466 | AIR HEATER (REGENERATIVE) | Outage #10The unit was running with known seal damage on the air heaters. Removed
| PD | 56 | 8100 | 2011-09-26 05:16 | 2011-09-26 22:19 | 17.05 | 6.4372 | 2999.7561 |  |  |  | 305 | 490 | 466 | WET SCRUBBER/ABSORBER TOWER OR MODULE | Load Reduction #462-1 and 2-2 Absorber towers were out of service for maintenance
| D1 | 57 | 338 | 2011-09-29 14:27 | 2011-09-29 20:27 | 6 | 0.12245 | 57.0612 |  |  |  | 480 | 490 | 466 | PULVERIZER CONTROL SYSTEMS (TEMPERATURE AND PRESSURE) | Load Reduction #472-6 Mill bow differential transmitter failed due to water in the

## MAR-14 Summary By Cause Code
NERC GADS UNPLANNED EVENT IMPACT
BY CAUSE CODE GROUP
MARCH 2014
|  |  | MWH (system) | EAF (system) | EUOR (system) | EFOR (system)
| Range | Cause Code Group | Lost | Lost | Impact | Impact
| 0010-0130 | Fuel Handling | 0 | 0% | 0% | 0%
| 0200-0480 | Fuel Firing | 36695.4895 | 0.8555% | 0.8258% | 0.7815%
| 0500-1999 | Boiler (all) | 36147.5229 | 0.8428% | 1.117% | 0.9215%
| 3110-3999 | Balance Of Plant | 11600.9681 | 0.2705% | 0.3595% | 0.2542%
| 4000-4499 | Steam Turbine | 505.7106 | 0.01179% | 0.01567% | 0.01577%
| 4500-4899 | Generator | 0 | 0% | 0% | 0%
| 8000-8835 | Pollution Control Equipment | 19055.9168 | 0.4443% | 0.5905% | 0.2538%
| 9000-9340 | External | 13.4515 | 0.0003136% | 0.0004168% | 0.0004195%
| 9504-9720 | Reg., Safety, & Environmental | 4245.0028 | 0.09897% | 0.09254% | 0.09313%
| 9900-9999 | Personnel Or Procedural Errors | 0 | 0% | 0% | 0%
|  |  | 108264.0622 | 2.524% | 3.001% | 2.32%
Note: This data may not
match KPI values as this data
includes overlapping events.
Boiler Tube Failures ( # 3 outages)
| 1000-1020 | Waterwall (# 2 outage) | 12807.95 | 0.2986% | 0.3969% | 0.3994%
| 1030-1050 | Superheater (# 1 outages) | 5093.2 | 0.1187% | 0.1578% | 0.1588%
| 1060-1070 | Reheater (# - outages) | 0 | 0% | 0% | 0%
| 1080-1099 | Economizer (# -- outage) | 0 | 0% | 0% | 0%
|  |  | 17901.15 | 0.4174% | 0.5547% | 0.5582%
|  |  | 16.53% | 16.53% | 18.48% | 24.06%
|  |  | of Total | of Total | of Total | of Total
|  |  | MWH(lost) | EAF(lost) | EUOR(lost) | EFOR(lost)
|  |  | MWH (system) | EAF (system) | EUOR (system) | EFOR (system)
| Range | Cause Code Group | Lost | Lost | Impact | Impact
1 | 0200-0480 | Fuel Firing | 36695.4895 | 0.8555% | 0.8258% | 0.7815%
2 | 8000-8835 | Pollution Control Equipment | 19055.9168 | 0.4443% | 0.5905% | 0.2538%
3 | 0500-1999 | Boiler (non-BTF) | 18246.3729 | 0.4254% | 0.5623% | 0.3633%
4 | 1000-1020 | Waterwall (# 2 outage) | 12807.95 | 0.2986% | 0.3969% | 0.3994%
5 | 3110-3999 | Balance Of Plant | 11600.9681 | 0.2705% | 0.3595% | 0.2542%
|  |  | 61711.2078 | 1.439% | 1.909% | 1.271%
|  |  | 57% | 57% | 63.61% | 54.76%
|  |  | of Total | of Total | of Total | of Total
|  |  | MWH(lost) | EAF(lost) | EUOR(lost) | EFOR(lost)