## Sheet1
DOOSAN MINI OUTAGE WORK SCOPE - 29-JUN-14 TO 04-JUL-14
# | Description | Forecast
1 | EC/Petrochem looking at burner front and PF splash plate insulation to reduce burner front temperatures | f/c = 04-Jul-14 for one burner
2 | Doosan to Issue updated 5 pair oil gun tip testing program for cold start | f/c = 02-Jul-14
3 | Review Economiser Feed Piping supports in cold position and are we going to cut & re-weld the stubs to address the issue of the valves bottoming out on level 6? Action SBR & Mistras | f/c start is 01-Jul-14
3a | Need Bechtel confirmation that supports in their piping scope are correctly loaded | Bechtel action
3b | Verify support supporting the Economizer inlet line adjacent to the check valve is loaded correctly - The support number is 31311SSC001 | f/c survey = 01-Jul-14
4 | Issue our email re Drain Pipe From the Small Start-up Vessel to the Boiler Drains Vessel (# 2-BLS-L879) and effect any repairs / check movement back in cold position | f/c response = 02-Jul-14
5 | Logic updates - Separate list to be issued upon completion of review | f/c = 01-Jul-14
6 | Verify thermocouple wiring to D3 PF upper and D4 PF lower is correct | f/c =30-Jun-14
7 | Finalise Beck drive power / DCS cable routing on burner decks and replace all ‘nylon cable ties’ with metal P clips, as per Phil Rabe’s request last week | f/c = 04-Jul-14
8 | Reconcile and test flame scanners and check for faults / confirm how many are serviceable | f/c =30-Jun-14
9 | Doosan to investigate A3, B4 and C3 oil scanners | f/c = 01-Jul-14
10 | Doosan to repair and refit Cegrit assemblies | f/c = 01-Jul-14
11 | Set mills A,B, D, & F core air damper minimum closed stops (to same position as C & E) | f/c = 02-Jul-14
12 | Look to fit all upgrade hardened PF Orifice plates – Materials in the stores | f/c = 04-Jul-14
13 | Complete OFA damper bearing and test point insulation | f/c = 03-Jul-14
14 | Complete installation of new valves on level 16 condensate pots and cap on vent line - Action SBR & Mistras | f/c balance of materials = 01-Jul-14 f/c complete = 03-Jul-14
15 | OFA Port Rod adjustments – to eliminate the length variations that current exist | f/c = 01-Jul-14
16 | Complete fitting the PA / SA test probes | f/c = 04-Jul-14
17 | Survey the GAH pipework system and supports now the unit has gone through start to hot and now back to cold and note if any issues with supports / pipe movements i.e. level 14 down to 2 | f/c = 01-Jul-14
18 | Survey F row PF lines re movement on lower cans back to cold positions | f/c = 01-Jul-14
19 | Take unit cold position readings on all the access ladders on the burner decks and mark on the ladders as completed with the unit in the hot position | f/c = 01-Jul-14
20 | Can we repair bound up Mech. Stops on CA damper - A row, investigate if we source spares parts ASAP from Tyco / MacJunkin? | Under investigation to see whether possible in time frame
21 | Take photo's of burner and OFA throats - Site access via 'dance floor' doors, LGE-KU to open and shut on completion | f/c = 01-Jul-14
22 | LGE-KU to check out CO probes as understand from my discussions with Devin that one appears to be flat lining? | LGE-KU action
23 | LGE-KU to look at A3 fuel oil valve | LGE-KU action
24 | LGE-KU to carry out further overhaul of purge air valves subject to repair kit availability - Rick Powell checking | LGE-KU action
25 | Doosan to issue revised copy of our D-NOx burner optimisation test program phases 1 – 7 to LGE-KU and Bechtel | f/c = 04-Jul-14
26 | Doosan to demobilise Storm & FERCo personnel on 30-Jun-14, Storm to remobilise for dirty air testing, FERCo to remobilse Monday week | f/c = 04-Jul-14
27 | Look at overall impact to our latest program as issued at the end of last week | f/c = 03-Jul-14