## To Go Activities
2014-01-08
| # | Description | Start | Finish | Remarks
LOGIC/TUNING DCS UPDATES
| 8.25 | List of all logic mods and latest rev (include the red lines). |  | On-going, current is 07-Oct-13 | Latest list issued via S. Hammond 07-Oct-13 (WCAH Logic revision noted by Chris Dukes added).
| 8.32 | REVISED LOGIC TO BE ISSUED
| 59.1.6.1 | Mill Temperature Control Logic - Option 1 (Temperature Kicker, move HAD and CAD both initially). Variable gain/integral added to all mills as of 24-Jul-13, switch from slow to fast gain at 33% feedrate. |  | 24 MW/min successful at 55% ODP Doosan: 59% ODP for repeat 24MW/Min ramp - 08-Oct-13 (A) | 12 MW/min successfully achieved 18-Aug-13. 24 MW/min successfully achieved 24~25-Aug-13. Doosan requests 59% ODP & LGE to repeat the 24MW/min ramp. Doosan to confirm ramp steps, Bechtel confirmed smaller increments acceptable per test procedure (80 - 100% ok). Doosan agreed verbally (06-Nov-13) and via e-mail 17-Nov-13.
| 79 | Provide Summary Report of Mill Swings and final resolution. |  | f/c = 23-Dec-13 (A) | Summary report of mill swings and final resolution to be provided once PA flow measurement resolved - thought to be the cause. (F mill HAD position feedback off by 5%, add to LGE outage work order). Summary report issued 23-Dec-13.
ACTION ITEMS
| 62 | ID FAN STALL
| 62.8 | Revise Stall Alarm curve. |  | 16-Aug-13 (A) Alternative curves f/c = 22-Jan-14 | Doosan to develop alternative Stall alarm curves that follow fan curve, have available if needed. Doosan recommends to maintain existing stall lines via S. Hammond 16-Aug-13.
FURNACE HYDROJETS
| 62.7.4 | Pressure Drop Analysis (Replace Check Valves). |  | f/c = 18-Dec-13 (Subject to unit availability) | Check Valve, Water Hammer and Pipe Support correction - Closed. Doosan to repeat pressure measurements and confirm that the new check valve is working as expected once the tuning is completed by DPII, f/c = 18-Dec-13 (Subject to unit availability)
| 83 | AIR FLOW TRAVERSE TESTING
| 83.8 | SA - Recommendations on k factors/logic. |  | DPS response sent 25-Oct-13 (A) | K factor recommendations issued 30-Jul-13 (Doosan recommends to keep as-is). Bechtel response 30-Jul-13, 01-Aug-13 and 02-Oct-13.
| 83.8.1 | Restart procedure to include methodology for checking the SA K factors |  | f/c = TBC | Doosan to update restart procedure.
MISCELLANEOUS
WN-441 | 84.2 | WCAH Data Sheet. |  | Design Agreed in Principle Issue of current DS 19-Nov-13 (A) | LGE requests final design data sheets. PO placed with Armstrong, f/c delivery 31-Jan-14. GA drawings issued 08-Oct-13 (A).
| 84.2.2.1 | Doosan response to LGE WCAH Racking Sketches comments. |  | f/c = 24-Jan-14 | Doosan to progress on completion of laser scanning.
WN-0443 | 91 | Ammonia Pumping Skid - Mod to permit starting of idle pump. |  | Mod during Spring outage | Bechtel progressing modifications with Aether.
LGE Action | 92 | ID fan Hydraulic Cylinder Failure - Logic mod requested (applies to FD fans also). |  | 04-Oct-13 (A) | C. Dukes recommended Solution of 13-May-13. DPS concern issued 04-Oct-13 with logic mod for approval to implement. C. Dukes ok with logic, 07-Nov-13.
| 96 | SCR SO3 & PLUGGAGE ISSUE (OPEN ITEMS) |  |  | See Restart Recommendations, S. Hammond e-mail 16-May-13.
| 96.1 | Evaluate Additional vs improved sonic horns. |  | Outage Inspection Report 07-Oct-13 (A). Recommendation sent 26-Nov-13 (A) | Recommendation provided 11/26/13 via S. Hammond.
| 97 | FURNACE FEGT
| 97.1 | Double Frequency of 4 Platen Lowers (IK 9,10, 19,20). Flux Sensor Recommendations. |  | f/c = 17-Dec-13 (A) | LGE addressing logic issue with Diamond. Seq 10/20 logic issues, brings in faults/alarms. 17-Dec-13: Doosan recommends to review the data again following a confirmed period of operation (minimum 2 days' operation at steady load without mill changes) with 4 hourly cycles of the lower platen sootblowers.
| 98 | Mill Seal Air Damper Leakage. |  | 09-Nov-13 (A) Comments 20-Nov-13 (A) Responses | Doosan to proceed with Effox damper. Address damper seal attachment - Seal will be both bonded and mechanically attached to the blade, details on drawing, issued 08-Jan-14 (A).
| 99 | Alstom Mill Wing Tip Modification - Verfiy required or not. |  | f/c = 16-Dec-13 (A) | Mill E wing tip mods complete, removed 1", resulted in excessive coal spillage. LG&E replaced the wing tip during mini outage, PA flow set at +15% to reduce coal spillage. As per conference call on 16-Dec-13, Mill E clearance between the vane wheel and air restriction ring to be inspected, f/c 16-Dec-13, and Mill F wing tips to be trimmed, f/c w/c 23-Dec-13.
WN- | 101 | Coal Pipe Purge Procedures - Verify Current Requirements. |  | Joint LGE/Doosan walk down required | LGE/Doosan to walk down week of Nov. 4th. LGE agrees to stop purge on mills D and F, verify no deposits during Spring 2014 outage. LGE requests means to verify no steam leakage.
| 103 | Manual Update. |  | Electronic: 22-Nov-13 Hardcopy: f/c = Jan~Feb-14 | Hard Copies - ID fan stall purge system, Burner T/C alarms, …etc. - delivered to TC2 on 11-Dec-13 (With Ron G) and agreed with Jim Craft / Michelle Griffith that update will take place late Jan-14/early Feb-14.
| 106 | Commissioning Records Package. |  | f/c = TBC | Doosan to package commissioning records and submit to Bechtel/LGE.
| 109 | Lime Injection Upstream of Air Heater. |  | f/c = TBC | Evaluate possibilitiy of Testing one month prior to outage. Joint walkdown with Mark Thomas held 13-Nov-13. Conference call on 11-Dec-13, Lances and splitters forecast to be delivered TC2 w/c 06-Jan-14, LGE-KU looking at injection skid and hoses for hook up. Follow up call w/c 16-Dec-13.
| 110 | Coal Pipe Manometer Data/Analysis. |  | Ongoing Current data set issued 17-Dec-13 | 1st data set to be sent 11/6/13. Plan for a set of readings once per week taken using a digital manometer. 1st set of readings taken 14-Oct-13.
WATCH ITEMS
| 2.2.7.2 | Borescope PF Pipe Inspection |  | 07-May-13 (A) | Move to Spring 2014 Outage List for verification. No deposits found, RCA updated - 07-May-13 (A).
| 8.12 | Revised SA Crossover f(x) Logic | ??? | f/c = ??? | Optimize Curve - On-going. On new curve, Target = 6 inwc
| 8.13 | Revised Part Load 02 f(x) curve | 2012-08-01 | 2012-08-19 | Need low load operation f/c ramps 14-Aug-13 to 19-Aug-13
| 8.23 | Engr Function to change stoich air by up to 3% |  | Watch | See 01-May-13 Meeting minutes. To be left at current +2%. Review if cross - limit alarms reoccur upon startup, reduce cross limit margin to 0.5 kpph
| 8.31 | Mill outlet Temp change to 150 F |  | 2013-02-01 | Pending additional fuel testing.
| 8.32.8 | Increasing Mill Exit Setpoint during mill startup |  | Watch | See C. Dukes suggested Logic changes for startup vs operation, 26-Jun-13 (change tuning after 30% load)
| 8.32.11 | S/A Damper balancing Logic |  | f/c = ?? | Leave as-is, with operator bias station. See S. Montgomery reply 12/19. Increases demand on already busy controllers and CFD suggests its not needed.
| 8.33 | O2 Trim Limits - Limited by 0.88 Stoich |  | 13-Aug-13 (A) | LGE has chosen to keep as-is due to CO concerns. Currently at 0.89, Doosan recommends to lower to 0.87 via S. Hammond email of 13-Aug-13
| 32 | NOx at SCR stack reading | 2012-07-02 | Watch | Watch after SCR/Ammonia tuning completed. 8.18
| 38 | Finalize Mill Classifier speed (due to increase in mill load line, at 76 rpm) |  | f/c=??? | Mill A 72rpm=67% Mill A=78rpm = 75.7%. Finalize classifier speed curve once PA flow is finalized. Put all Mills @ 76rpm
| 63 | Training on the dampers optimum position setting for the operators |  | f/c | LGE to develop list of needed training.
| 71 | PURGE MILL CONTENTS TO FURNACE AFTER STEAM INERT |  |  | Meeting held 17-Sep-12; Meeting scheduled for 28-Nov-12
| 71.1 | Confirm Insurers/legal okay with LGE accepting responsibility with the NFPA criteria |  |  | LGE action
| 71.2 | Doosan to confirm no other barriers to implementing purge to furnace |  |  | Define what load conditions must exist prior to purging to furnace, no of oil burners in service for example
| 75.9 | Mill Clear Out Check Sheets |  |  | Move to Watch item. Doosan to complete check sheets
| 83.2 | PA -Venturis - PA Fan Upgrade Options |  |  | Options presented in Renfrew - Move to watch item
Spring 2014 Outage Items
| 62.4 | Modify stall sensing ports per Howden recommendations |  | 28-Aug-13 (A) Further analysis required | Doosan evaluating whether to insulate piping. See D. Groom analysis 28-Aug-13. Results show below ADP, Doosan further evaluating. Open Issue - Heating for purge air - See DPS e-mail 04-Apr-13, purge air temperature to be monitored at restart. Doosan provided commissioning records for purge air system, Manual updates required.. Taps inspected during Sep-13 mini outage and minimal build up observed. To be re-inspected during 2014 outage and if required cleaned and the pipe insulated.
TESTING (Pending Completion of Optimization)
LGE Action | 4 | Fly Ash Removal Test |  | 2013-11-20 | Rescheduled to Dec. 5th or 6th.
LGE Action | 5 | Bottom Ash Removal Test |  | Prelim Tests on-going, official test f/c = ??? | Alstom witnessed 8 hour test 05-Sep-13. Successful test. Alstom evaluating hydaulic pressures on restart.
CLOSED ITEMS
| 1 | F Row Burner Inspection | 2013-02-15 | 2013-02-22 | Target is 2/15, no later than 2/22. Inspection Completed. See Doosan presentation 2/21
| 1 | Check-Out Back to DCS | 2012-04-25 | 2012-05-21 | Burner Thermocouples ~ 130 I/O. Will finish when C3 and E1 burners are reinstalled
| 1.5 | Address B low flow alarm (microwave instrument) | 2012-07-06 | ??? | Bruce Provided instrument instructions, I&C to verify calibration. Bruce to get with Rick P.
Forney / Coen | 2 | Flame Scanner; Inspect mounting and amplifier settings, Adjust gain and discrimination Set up oil Igniters/Scanner | 2012-05-21 | 2012-08-14 | Complete. 33 (28 + 5) longer air tubes on site as of 7/25. Doosan to install during outage
| 2 | Doosan to perform metallurgy test on sampling of deformed Core Air Tubes to determine if correct material was provided |  | 2012-12-07 | Lab test results confirm mat'l is HR120
| 2.1 | Doosan to evaluate atomizing air cooling to be applied to all rows? C and F only currently. |  | 8/20 e-mail via R. Gratton | Atomizing Air Cooling Logic requested to be applied to all burner by R. Gratton 8/20/2012. Coen Report Rec'd, released to work other burners. B-Row complete working all other rows as can Logic for Remaining Rows??
| 2.1 | Oil Gun Tip Failures |  |  | Watch added air consumption
| 2.2 | Coal Scanner Setup - Verify flame dropout timer - 3 or 4 seconds |  | 9/5 (A) | Replies provided 9/5 (A). 1. Forney to provide site specific set up procedure, 2. code references for dropout times. 3. Doosan to arrange Forney on-site prior to shutdown - back on site for restart
| 2.2.1 | Track Scanner Setup/Completeness |  | 11/13/2012 (A) | Two Oil Guns on B row allowed oil injection to a dark furnace. Three ignitors on B row have oil flame signal dropping out. Pending Forney Report for partial scope. Additional rows to be addressed on startup. see 2.2.3.4
| 2.2.1.1 | Doosan to consider alternative scanner Suppliers/equipment |  | ???
| 2.2.2 | LGE may Trial alternate designed scanner |  | 10/12(A) | John Grist provided recommendations 10/12
| 2.2.3 | Forney to submit scanner tuning procedures for Trimble |  | 10/18/2012 (A) | Channel "B" clarificaiton reqeusted. 10/29
WN-0325 | 2.2.3.1 | Forney Scanners - Retune on Restart |  | f/c = At Restart (5/26) | Forney on site 5/26 to monitor through 40% load. No issues reported. Forney Released. Doosan to respond to warranty notice.
LGE Action | 2.2.4 | Add Fibre Optics for Scanners | 2012-12-02 | on-going | LGE agrees to close. Guide Tube did not recieve sufficient cooling air. Currently on original scanners. on-going evaluation (D Row) - All 5 with heat damage week of Jan 15th LGE-KU to confirm current status and whether item can be closed.
Hitachi | 2.2.4 | Dark Check - Clarify load point when it can be omitted (>40% load?) |  | 10/22 (A) | Dark Check changed from 50% to 40%. Major Issue - Can't pass dark check due to "seeing" opposite wall oil flame
| 2.2.5 | Scanner/Ignitor Mtg to address Issues | 2012-11-06 |  | Meeting held on 11/14 @ 1:00
| 2.2.5 | Logic Check - Verify BMS logic aligns with requested load limits on dark check |  | 10/22 (A) | Doosan verified logic is correct and up to date
| 2.2.6 | Bannjo Failure Initial Root Cause Analysis |  | 12/20/2012(A) | 5 banjos being replaced (all CCW); 30 burners - refractory being added in gap; Draft issued on 11/27; Final RCA issued 12/20
| 2.2.7 | PF Pipe - Coal Layout - Root Cause Analysis | 2012-11-21 | 12/07/2012(A) | Meeting held 11/28; Single pipe purge to be completed during restart; Updated procedure for single pipe purge?
| 2.2.7.1 | Single Pipe Purge - Every 720 Hours |  | 2013-02-15 | Run Time Logic proposed 2/4. Changed from 500 to 720 hours per S. Hammond 1/18 e-mail. Doosan provided logic 2/12 (A), implementation confirmed.
| 2.2.7.2 | Borescope PF Pipe Inspection |  | 05/07/13 (A) | Move to Spring 2014 Outage List for verification. No deposits found, RCA updated - 05/07/13 (A).
| 2.2.7.2 | Borescope PF Pipe Inspection |  | 05/07/13 (A) | Move to Spring 2014 Outage List for verification. No deposits found, RCA updated - 05/07/13 (A).
| 2.2.7.3 | Steam Inerting - Review of steam Qty |  | 2013-02-15 | Updated Philosophy sent 1/11. Comments provided 1/18. DPS responded 2/14/13, item closed pending boroscope inspection
| 2.2.8 | Banjo Replacements for Owner Spares |  | f/c = 05/20/13 Delivery | Delivered 20May13
| 3 | Doosan to review material grade and next order of core air spare parts is to be appropriate material grade |  | Complete | DPS notes that HR160 has a higher resistance to oxidation but on examination of the data sheets, inferior mechanical properties than HR120. DPS conclusion is therefore to remain with the HR120.
Bechtel | 3 | CA Tube Insulation |  | 2012-07-14 | 50% complete. (E row 100% complete)
| 4 | Doosan to perform and submit a RCA for banjo casing liner cracks |  | 2012-12-01 | DPS engineer on site 11/8/2012 to determine RCA
| 4 | Motor Run in | 2012-05-21 | 2012-05-21
Hitachi | 5 | Check-Outs and Start-up | 2012-05-21 | 2012-05-23
| 5 | PAC Lances pluggage |  | watch | None reported in last two weeks, operations verified no pluggage
| 6 | A3 T/A damper is locked |  |  | Corrected during 9/29 Economizer Tube leak outage
| 6 | AFCU Skid Tuning | 2012-06-25 | 2012-07-02 | Logic to be tuned item same as 8.15
| 7 | Doosan to arrange a joint Alstom/Doosan/LGE/Bechtel meeting to discuss mill clear out issues |  | 11/28/2012 (A) | Joint meeting planned for 2:00 PM 11/28
| 7 | Function Test | 2012-05-23 | 2012-05-25 | On coal.
Emerson | 8 | DCS Update Tuning | 2012-05-24 | 2012-07-09 | On going. Mill tuning.
| 8.1 | Sonic Horn logic |  | ?? | Complete
| 8.1 | BCP Cooling Water Temperature Logic |  | ?? | Complete
| 8.2 | Coal Quality factor |  | 10/27(A) | S. Hammond e-mail 10/27; LGE action - agree or provide comments
| 8.2 | Sonic Horn Graphic |  | ?? | Complete
| 8.3 | (Air Balance - Recheck after Beck Changes) |  | Move to Watch | RDL's balanced 10/6. Windbox rows balanced side to side week of 9/25
| 8.3 | Pressure Switches Associated with the New Layer 3 Sonic Horns Air Supply |  | ?? | Complete
| 8.4 | Pressure Switch Graphic |  | ?? | Complete
| 8.5 | Catalyst layer 3 Graphic |  | ?? | Complete
| 8.6 | AFCU Skid: The flow transmitters tagged 2SCRFT710 AND 2SCRFT711 are to be re-ranged to 0-800lb/hr. |  | ?? | Complete
| 8.7 | AFCU Skid: The ammonia flow control loop required correction to the ammonia demand molecular weight and the boiler heat input. |  | ?? | Complete
| 8.8 | FD Fan Intake Damper Control Logic |  | ?? | Complete
| 8.9 | PF Failure to Ignite Logic |  | ?? | Complete
| 8.11 | O2 Auto Trim Minimum Limit Logic | ??? | 2012-07-02 | Fine tuning w/Emerson DCS Engineer (David Lee on site as of 6/25)
| 8.11.1 | O2 Trim - OFA Only |  | f/c = ??? | See 5/1 Meeting Minutes - O2 Trim being implemented for S/A AND OFA.
| 8.11.2 | Analysis of the O2 Trim Change |  | Preliminary analysis provided; Further review and assessment 1/10/13 | Is this better or worse than old logic? Revert to prior logic?
LGE Action | 8.14 | Ammonia Control Logic - Outlet Lbs/MMBtu Control Monitor/Tuning | 2013-06-09 | f/c = 13-Sep-13 | Per P. Rabe, tuning acceptable 8/21/13. Tuning Report submitted 8/13 for Review. Comments requested by 30-Aug-13
LGE Action | 8.14.1 | Percent Removal Logic for ammonia | 2013-06-09 | f/c = 13-Sep-13 | Per P. Rabe, tuning acceptable 8/21/13. Tuning Report submitted 8/13 for Review. Comments requested by 30-Aug-13
| 8.15 | Ammonia Control Logic - Percent Removal Logic | ??? | 2012-07-13 | Bechtel sent to LGE to respond. Doosan advised this would be a scope change.
| 8.16 | B-2 & F-1 Temp over 1100 trip of Mill | 2012-06-13 | 2012-06-25 | Flame temp traverses initiated, discuss @ meeting 6/20
| 8.17 | Purge Logic: |  | 2012-07-06 | - SAME AS ITEM 50.1 Logic mod provided 6/26 - Single pipe purge didn’t work, PA damper logic issue. LGE to review. - Doosan to advise Criteria for when it can be implemented (load? Min no. mills?) LGE requests Procedure
| 8.18 | SCR Optimization |  |  | Moved to below
| 8.18 | SCR Optimization Procedure |  | 7/9(A) | Revised Draft issued 7/9
LGE Action | 8.18.1 | SCR Tuning Results |  | 14-Aug-13(A) Update 21-Sep-13 (A) | P. Rabe confirmed to close 10/30. Bechtel/LGE to review updated version. See Bechtel Questons sent 14-Aug-13. See Fuel Tech report submitted via S. Hammond 14-Aug-13
| 8.19 | Finalize Stoichiometry Curve (Phase 5) | 2013-06-24 | 7/29/2013 (A) | See S. Hammond response 7/29 advising to keep Stoichiometry as is, BZS = 1.0.
| 8.21 | S/Heat Reheat damper logic change |  | f/c = TBD | R.Gratton reported 8/15 tuning is complete. LGE okay with status. Will be relooked at during winter rating (809 MW's starting Oct. 1st)
LGE Action | 8.22 | OFA Logic change (6 mill operating-min demand) |  | 2013-08-02 | Logic changes acceptable Per P. Rabe 7/26/2013. Resent 7/3/2013. S. Hammond e-mail 10/27; LGE action - agree or provide comments. LGE-KU action
| 8.24 | Implement single pipe purge logic |  | 2012-07-31 | Completed and tested 7/31
| 8.26 | Eliminate Feedwater Bias |  | 11/9/2012 (A) | Friday Nov. 9th proposed, 10:00 AM
| 8.27 | Min Cooling Position for Windbox Dampers (logic and control to balance flow rate) |  | 12/08/2012 (A) | Top Rows at 28%, middle at 25%, bottom at 21% per S. Hammond 12/8
| 8.27.1 | Verify Burner OOS temps are acceptable |  | 22-Aug-13 (A) C & F mills, E mill (29-Aug-13), remainder by TBC | All verified as acceptable per R. Gratton on10/30. F(x) logic provided via S. Hammond 22-Aug-13 for top two rows. Will evaluate and then decide if other mills receive as well. C & F = 38%, A & D Row = 34%, B & E Row = 29%
| 8.28 | Core Air Dampers 100% Open OOS |  | 10/1 (A) Logic Implemented = ?? | Doosan incorporated Comments
| 8.32 | Optimum Damper Positions, P/A |  |  | Attempted 55 percent 10/9, didn't work, reverted back to 50 percent.
| 8.33 | GAH S/A Bypass Damper Logic |  | 1/29/13 (A 2/1/13 Implemented | Updated Logic provided 1/29. Correct discrepancies between A and B sides. Doosan issued logic 1/16
| 8.34 | Fuel Oil Pressure Logic |  |  | R. Gratton confirmed working acceptably. S. Montgomery replies 1/24
| 8.23.1 | Update System Descriptions for Logic Changes |  | 12/11/2012 (A) | Draft Operating Philosophy issued 11/22; Issued final on 12/11
| 8.25.1 | List for all tuning parameter changes |  | 2012-10-09
| 8.26.1 | Update FW Bias Logic |  | 11/12/2012 (A)
| 8.28.1 | Verify acceptable temps achieved (Core Air Tubes) |  | 2013-08-20 | See core Air Temp Report issued 8/20 via S. Hammond. Doosan recommends temp are acceptable.
| 8.29 | Optimum Damper Positions, S/A |  | Following Spring 2014 Outage | S. Hammond reply 8/14 - To be performed during restart on De-Nox burners. Move to Restart Activities
| 8.32.1 | Venturi - Eliminate Auto Purge |  | 12/4/2012 (A) | Currently being drafted, to be issued on 11/27; Issued on 12/4; DPS proposed totally removing the PA flow purge logic. LG&E rejected this. DPS /LG&E to agree modifications removing the purge solenoid logic but enabling the operator to freeze the flow signal during a manual purge.
| 8.32.10 | Plant Trip during shutdown - review feedwater control logic |  | Close? | A. Stano confirmed demand did not change, but speed dropped from 3,000 to 2,400 rpm. LGE checking oil filters and further troubleshooting.
| 8.32.2 | Venturi - Add third Thermocouple | 2013-06-01 | 07/18/13 (A) | LGE in agreement per P. Rabe 7/26/2013. See Doosan Reply dated 7/18 summarizing traverse data and recommendation to change the temp diff alarm to 60F.
| 8.32.3 | Venturi - Revise flow vs DP |  | 12/5/2012 (A) | Issued 12/5
| 8.32.4 | SA Flow - Revise flow vs DP, rerange xmtrs |  |  | Restart on existing xmtrs ranging
LGE Action | 8.32.4.1 | SA Flow - Evaluate alternate HP port - Rerange xmtrs if pursue |  | 2013-02-15 | Doosan to evaluate traverse test results. DPS issued comparative data and summary 2/14. All have agreed to remove the existing tubing and plug ports
| 8.32.5 | Pyrite Removal - Revise logic for semi dry clearout |  | on-going | Implemented after scraper pins replaced. Logic Worked Successfully on D mill, updates required for fault handling
| 8.32.5.1 | Update Semi Dry Logic to address Fault Clearing, apply to remaining Mills |  | A, B, E to go, f/c/ = ??? | Semi - Dry Logic implemented on all mills.
| 8.32.5.2 | Update Ops procedure for semi dry clearout |  | 3/12/13 (A) | D. Groom issued 3/12(A)
| 8.32.6 | Pyrite Removal - Revise logic for wet clearout |  | 12/5/2012 (A) | Issued 12/5
| 8.32.7 | Mill Shutdown - Finalize CAD 70 vs 50% | 2012-12-03 | 2013-02-01 | Finalized at 50%. Working acceptably per R. Gratton
| 8.32.9 | Logic Priority List |  | 12/14/2012 (A) | To be completed before return to service and which could follow. This will include the logic change for the 10% Burner Overfire Alarm. This was requested by Phil Rabe to assist in eliminating/reducing nuisance alarms.
| 8.33 | O2 Trim Limits - Limited by 0.88 Stoich |  | 13-Aug-13 (A) | LGE has chosen to keep as-is due to CO concerns. Currently at 0.89, Doosan recommends to lower to 0.87 via S. Hammond email of 8/13. Move to watch item
| 8.34 | Classifier rejects to Manual during "some" start sequences |  | 07-Aug-13(A) | See R. Gratton recommendation of 8/7 to change BTSC to 68 rpm.
| 8.35 | Instability when Mill seal air limits hit (LGE requests raising ACET to 200F) |  | 15-Oct-13 (A) | See C. Dukes 9/26 email, ACET changed to 203 F, switch and tuning parameters changed. Doosan recommends changing back to 195 F ACET post spring outage.
LGE/Doosan Commissiong Action | 8.36 | OFA FRont to Rear Bias Logic |  | Additional bias being reviewed on site. | Move to watch item per 8/21/13 meeting. M. Slaugter suggested additional bias may be needed with C mill IS, F mill OOS. R. Boone tuning. LGE agrees to implement per P. Rabe 7/31. C Row OOS = 5%, F Row OOS = 2.5%
|  | Feedwater Bias Tracking |  | 2012-11-12 | See S. Montgomery 11/12
|  | S/Heater Drain Valve Logic - Correct Pulse |  | 2012-11-26 | Approved by Doosan 11/26
| 10 | Straight line Plot (sq ft (DP x Density) vs. Flow) | 2012-05-20 | 2012-06-23 | MTG held 6/20, Straight line plots provided in mtg handout
| 10 | Doosan to provide ops training after issuance of revised control philosophy |  | One shift to complete | Training Material provided 5/15
| 11 | Doosan to issue a detailed startup plan. The plan is to include logic checks. |  | 11/21/12 (A) | Schedule and procedures are in progress
| 12 | Doosan to provide proposal for redundancy for ID Fan Stall warning |  | Complete | Stall warning has no redundancy but revised system for stall protection has same redundancy as existing system i.e. production is from 2 out of 3 probes/transmitters
| 12 | Calibrate & Test SA Flows (COLD) | 2012-05-20 | 2012-05-24 | Completed
| 13 | Calibrate & Test SA Flows (HOT) | 2012-06-09 | 2012-06-16 | Testing Complete
| 14 | Aerofoil inspections D/G/E (Pressure) | 2012-06-05 |  | Complete
| 15 | The Hydrojet Water Pumps common discharge pipe hangers |  | 2012-06-12 | Complete/Bechtel
| 15.1 | #4 Hydrojet cool/seal air low overheated |  | Warranty | Filters cleaned 6/12/12 , alarms out, move to Warranty SCR inlet duct
| 16 | Lube Oil Cooler |  |  | Complete
| 17 | D Recycle Exp Joints |  |  | Complete
| 19 | Monitor SSC thermal growth design mod. | 2012-06-15 |  | Done no issues f/c 6/01/12
| 20 | AH sootblower with air set up. Need min./max trim. | f/c = ??? | Watch | No issues reported on 9/30 Restart (following economizer tube leak outage)
| 21 | Expansion for econ vent | 2012-11-25 | Outage | Moved to Warranty
| 22 | New AIG DP Gages |  | 2012-07-10 | Working - 10 manifold on site 7/6/2012 , need additional 8 manifolds - 2 - 5 week delivery.
| 23 | Spark Rod parts LGE to light Ing., and trouble shoot other issues with light off | 2012-06-01 | 2012-07-10 | Need final drawing - S. Hammond to issue drawing on Friday 7/6/12
| 23 | Spark Rods/Scanners/Ignitors |  | Watch | 22-Jun-13 Mill A Start - A5 oil @ 9%
| 24 | Mill PA Traverse Test "D" Mill | 2012-06-09 |  | closed
| 25 | Test Mill Cool functions | 2012-06-16 | No longer being pursued as remedy for core air tube overheating | Data provided to Crawley. Mill temps above 200 F. Increase Tempering Air Flow. F Mill HAD Seals require replacement. Test again once damper/drive setup complete. Doosan to update written instructions once finalized. Not in service at this time.
| 25.1 | 30 minute timer |  | 2012-07-11 | Logic mod provided 6/26 - Under Review by LGE. Mitch to review.
| 26 | Air Heater Sootblower pressures - resize cold end orifice |  |  | closed?
| 27 | Verify Sootblowing at 1300psi |  |  | Doosan verified 300deg F of superheat
| 30 | FD fan balance on Air Flow |  |  | Acceptable
| 31 | WESP Wash Water |  | 2012-06-13 | logic does not permit auto operation until 650 MW's. SESS reply sent 6/13
| 33 | Issue Daily Plan of Activities w/look a head |  | 6/20/12 | Doosan is issuing Daily Plan
| 34.1 | AIR HEATER SOOTBLOWING STEAM QUALITY |  |  | Change to 300 F superheat. Doosan to verify installation dates
| 34.1.1 | Issue Tie-in Design for November Outage |  | 10/23 (A) | SMR - 107
| 34.1.2 | Material orders placed |  | 2013-03-15 | on-going as engineering is completed
| 34.1.3 | Engineering for review
| 34.1.3.1 | P&ID |  | f/c = ??? | Revised P&ID's issued for comment on 04/15/13. LGE and Bechtel comments provided 4/18, Docs returned 5/10 and 5/13
| 34.1.3.2 | Valve Spec |  | PCV - purchased PSV - T&c's to be finalized | PCV- 1/18(A). DPS requires PCV feedback to size PSV.
| 34.1.3.3 | Piping Drawings |  | 11-Jun-13 (A) | Relief Valve Vent Stacks submmitted 6/11. To be reviewed and commented on.
| 34.1.4 | Delivery of all components |  | f/c = 02-Oct-13 f/c = 13-Nov-13 | Latest on site date for bulk of materials Latest on site date for trimmer steel and supports
|  | Safety Valve |  | f/c = 02-Oct-13 | PO placed - Dresser
|  | Control Valve |  | f/c = 30-Sep-13 | PO placed - CCI
|  | HP Isolation Valves |  | f/c = 05-Sep-13 | PO placed - Briggs Valcon/VTI
|  | LP Isolation Valves |  | f/c = 07-Sep-13 f/c = 27-Sep-13 | PO placed - Wm Powell PO placed - Pentair (Tyco)
|  | Poppet Valves |  | f/c = 23-Sep-13 | PO placed - Alstom
|  | Piping |  | f/c 03-Oct-13 | PO placed - APP (To be Site run by Mech subcon'r)
|  | Hangers/Support Steel |  |  | RFQ to be issued on completion of design
|  | Instrumentation - Pressure Gauges |  | f/c = 05-Sep-13 | PO placed - Ashcroft
|  | Instrumentation - Pressure Transmitters |  | 20-Aug-13 (A) | Delivered - Rosemount
|  | Instrumentation - Flow measurement |  | f/c PO = 06 Sept | Quote rec'd and under evaluation
|  | Instrumentation - Thermocouples |  | f/c PO = 30-Aug-13 | LGE agreed to allow strap-ons to be used
|  | Electrical Design Documents |  | After final docs | Electrical ECN by Bechtel, f/c = following design docs
|  | Cable |  |  | Bechtel provided BOM 14-Aug-13
|  | Logic |  |  | Doosan and DPII logic
| 34.2 | Send Air Heater Baskets for Analysis |  | 11/2/2012 Alstom report received | See G. Davidson e-mail 10/28. Alstom f/c 6 weeks to complete analysis. Alstom Test Procedure provided S. Hammond 8/24
| 35 | 300kpph OFA Need modified test plan | 2012-06-14 | 2012-06-22 | Doosan able to complete the traverse
| 36 | Mill Curve Load increase (at +10%) | 2012-06-14 | 2012-08-14 | Place holder till finalized
| 37 | Windbox flows exceed 300kpph |  | during outage | Re-range all to 350kpph. (Completed during mini-outage, 9/13) 415AA shows bad quality
| 38.1 | Mill fineness | 2013-06-05 | 29-Jul-13 (A) | Doosan recommends keeping all mills at 76 rpm per R. Gratton 8/15/2013.
| 38.2 | Mill Air Flow Testing |  | TBD | Doosan arranging for FERCO to test - Covered under item 59.1.1
| 39 | "A" windbox retest at 55kph with oil guns in service |  | 2012-06-16 | complete testing 78 RPM
| 40 | SESS Pac/Lime Injection |  | 2012-06-19 | Tues 1pm schedule call
| 41 | Need max flow limits in ammonia |  |  | Doosan provided updated limits of 600kpph
| 42 | Core Air T/C temp data |  | Full load | Need Decision on Core Air Tube Cooling. Distributed data 7/5 and 6/20 - results ok. Relook at Full Load
| 44 | Burner T/C alarms |  | 2012-06-26 | Revised Alarm Sheet issued 6/25
| 44.1 | Update DCS for revised Alarm limits | 2012-06-25 |  | Rick Boone to update in DCS.
| 45 | Evaluate Condenser back pressure |  | 2012-06-25 | LGE working, will be complete 6/26
| 45.1 | Seal Leakoff Issue - Seal Leakoff Pressure running high, Control Valve wide open |  |  | Perf Test Results Distributed, investigation of leakoff source underway
| 46 | Multiple Burner T/C Failures - OEM to replace |  | 2012-09-08 | All pulled and replaced. Send batch back to OEM for replacements.
| 46.1 | IF run out of spares, recommend placement strategy |  |  | Secondary Air 1st?, PF upper next, PF lower?
| 47 | Cross Over Duct Pressure - Evaluate why Air Heater Outlet lower than main duct |  | ??? | Doosan Considers not to be an issue
| 48 | Burner Purge Procedure - Advise if Oil is to be started |  | 2012-06-22 | Doosan Recommends Against the use of oil
| 49 | Furnace Camera arr June 27th |  |  | Demo by OEM on 6/27
| 50 | HP Steam Temp Excursion during PF Purge - Address if logic mod req'd to address the added, unmeasured fuel |  |  | Meeting held 6/25 -
| 50.1 | Mill/PF Pipe Purge - Direct to Furnace |  | 2012-08-15 | Identify Criteria for when this can be done
| 50.2 | Review MS Spray Water logic | Set up Mtg | 2012-08-15 | Bechtel and Doosan to review
| 50.3 | MS Spray Water Source - Verify sufficient pressure available | AM 10:00 | 2012-08-15 | review events of June 1st
| 50.4 | Feedwater Bias - Clarify use/criteria |  | 2012-08-15 | reset to zero during Emerson upgrade, now at 200 kpph
| 50.5 | Boiler Max Permissible Temp |  | 9/13/2012 (A) | See S. Hammond E-mail of 9/13 with recommended inspection locations.
| 50.6 | Max Main Steam Pipe Temp |  | 2012-08-15 | identify max temp
| 51 | SCR Outlet NOx - Monitor Ammonia in ash |  | Watch | 0.035 lbs/MMBtu recommended low limit, up to 16 ppm thus far 7/11
| 51 | Provide Operations Guidance on NOx Control |  | 2012-06-25 | Interim Guidance Issued 6/25
| 52 | Remove Mill PA Flow bias based on bowl dP |  | 2012-06-22 | Mill B bias removed. All other mill are removed. Doosan to watch
| 53 | Daily Slag Condition |  | Operations to confirm tool working | Modified rod out tool Completed. Per Doosan, working acceptably. (7) Rod out pipes on A3,A5,B1,B3,C3,C4,D4 bent by Doosan observation. LGE has identified Qty = 40.
| 53.1 | Modify/Replace Rod-Out Tubes - 14 burners |  |  | Addt'l material not available. Original qty will be modified
| 54 | Don Parker Recommendations. |  | 2012-07-20 | LGE to review - No further comments.
| 54.1.1 | Stroke B Dampers |  |  | B mill HAD hung up at 50 - 70% B mill Cold Air Damper - Stroked fine
| 54.1.2 | Check plug/bolt on Banjo for Mat'l
| 54.1.3 | Clean out Bowl DP tapping points |  | 2012-08-02
| 55 | Burner Optimization - Send out Test Plan |  | 2012-07-06 | No LGE comments Comments to Doosan 6/28
| 56 | Identify Burner Inspection Criteria | 2012-06-25 | Inspection outage | Inspection plan sent 6/26 (A3, D3, F1, B2) and rod out tubes
| 56.1 | Pull Together Burner Spare Parts Inventory |  | 2012-07-09 | Doosan Spare inventory list sent 6/29 No Prefabrication needed prior to inspection (Qty = 2),
| 57 | Identify list of work for mini-outage |  |  | See attached list - Outage Mtg planned for Monday, July 9th
| 58 | Air Htr Sootblowers - Correct Logic for Drain Valves on Steam |  | 2012-08-11 | -On LGE's outage list - N. Payne to address, correct logic. - Drains have been open via logic since December w/no header orifice. - Operation closing valve manually at moment. New thermowells f/c=8/3
| 59 | All Mills Pressure Differential Swings. Tuning on b/c mill. |  | 8/22/2012DBEL/Loetsche/Alstom Reply | Alstom to address spring tension, roll to table clearances, 70/30 blend, wing tips A,B,C PA flow=+10% (as of 7/20) D,E,F PA flow=+10% third party report
| 59.1 | Joint Doosan, Alstom, Loesche call |  | 2012-08-16 | Send out Action Items, call held 8/16
| 59.1.1 | FERCO to perform side by side air flow tests on C mill, prior to outage | 2012-08-23 | 2012-08-26 | FERCO Testing Complete - Pending Analysis and Traverse Data
| 59.1.1.1 | Analysis of FERCO Mill traverse Data |  | f/c = ??? | Other Mill traverse data to be distributed. 200 F imbalance on Mill C at high load. Doosan to recommend remedy.
| 59.1.2 | Phoenix to review FE application |  | 2012-09-09 | Phoenix Replies provided, reviewed Bechtel/LGE/Doosan 9/10
| 59.1.2.1.1 | Evaluate New Static Tapping Ports |  | On-Hold | On hold, restart with existing static ports
| 59.1.2.1.2 | Evaluate Performance of Element |  |  | FERCO on site 10/2 to retest
| 59.1.2.2 | Long Term Fixes (Venturi)
| 59.1.2.2.1 | Evaluate FT above Tapping Point |  |  | To be located above tapping point
| 59.1.2.2.2 | Evaluate Purge Pressure/Hookup |  |  | I. Torkington provided recommendation 11/19; LGE requested 3 way valve
| 59.1.2.2.3 | Replace Copper Impulse Lines |  |  | Applies to New Static Ports
| 59.1.2.2.4 | Replace or Repair Honeycomb/Element
| 59.1.2.2.5 | Replace FT's/Environmentally controlled box |  |  | CES Model 467 vs Emerson 3051
| 59.1.2.2.6 | Replace CS Impulse Lines? |  |  | Pending final location and response to 9/18 e-mail questions.
| 59.1.2.2.7 | Seal Air Pipe Mod |  |  | To allow access to dynamic rodding port
| 59.1.2.2.8 | Evaluate Pyrite Removal System |  |  | Test 9/13
| 59.1.2.2.9 | Alstom Reduce Water Flows? |  | 11/13/12 (A)
| 59.1.3 | Testing Recommendation on Purge Air System |  | 10/23 OEM on site. 10/12 CAM Unit delivery - Install on Mill C | 1. Solenoid to isolate pilot line added to all mills 2. Doosan purchased bubble tight solenoids, added to mills 3. Doosan to order complete Phoenix Purge System, del = 10/12?? 4. Finalize any temporary tubing
| 59.1.3.1 | Verify effectiveness of CAM unit, Mill C |  |  | Establish Data Collection
| 59.1.4 | Test with Purge Air Jumpered out |  |  | F mill tested - No impact, E-mill tested - No impact??
| 59.1.4 | Engage EMF Expert |  | Working | Reported no noise found on B/D/F FE FT's and T/C's. Pending verification during mill swing
| 59.1.5 | Pressure Test at Element |  | 2012-09-15 | Purge pressure increased to 90 psig out of regulator. Pressure at element 30 - 50 psig. To verify adequate purge pressure Prior to Outage (Plugged) Static = 55 psig, Dynamic = 30 psig
| 59.1.5 | Verify FT Cable Grounding/Shielding |  | Working | Place High Speed Recorder on B mill FT and VFD
| 59.1.6 | Trial Transmitter at Element |  |  | Temp S probes were responsive, confirms tubing length not an issue
| 59.1.6.01 | Test Logic - Operator Defined Mill Inlet Temp |  | 2012-08-23 | Per Doosan - No longer recommended. Limited to 350 - 450 F, keep as engineering function, test logic only
| 59.1.6.1.01 | Mill Blockage Logic - Option 2 |  |  | Doosan recommends option 1
| 59.1.6.2 | Purge Air Logic Changes | 2012-09-05 | Watch | Purge during mill inert/clearout, Implemented
| 59.1.6.3 | Purge One leg at a time? |  | If req'd
| 59.1.6.4 | Manual Purge of FE (For those mills that have purge isolated) |  |  | Auto purge in place for all mills. All Mills have modified solenoid arrangement, except F (pending materials)
| 59.1.7 | Internal Mill Inspection |  | During Outage | LGE inspected during mini-outage. No reported findings.
| 60 | T/C's at Burners - Shield/lift off hot surfaces |  | 2012-07-02
| 61 | WCAH Pressure Drop - Doosan to recommend remedy |  | f/c = ??? | No change required if x-over press</=6 in wc, single row at 1.5 inwc (26-Jul-13, BMCR)
| 62.1 | Open reheat biasing dampers |  | 2012-08-21 | After some run time on new transformer. Doosan provided min damper positions 8/21
| 62.11 | Send Stall Sensing Line liquid for Analysis |  | f/c = ??? | Sample collected 8/7
| 62.2 | Air Heater DP |  | 2012-07-16 | Doosan Expediting Alstom
| 62.5 | Upper 2 mills - higher OFA demand |  | 2012-07-26 | Doosan Engineering to evaluate
| 62.6 | Sootblowing Regime - Optimize/Evaluate |  |  | Doosan provided recommendations 7/17 Bechtel sent comments 7/24 (requested clearer criteria for "aggressive water cannon use" and identified multiple wall zones as issues
| 62.6.1 | Sootblower Effectiveness Meeting |  | Use of Boiler T/C's - Mike Smith to address | See S. Hammond reply 11/23
| 62.6.1 | Water Canon System Repairs Completed |  |  | Move to Outage item. Repairs by LGE during Sept 8 outage. Need to advise Doosan when completed. (Zone 12 heat flux reading bad, 2A hydrojet check valve found leaking causing low water flow
| 62.6.2 | Monitor New Sootblower Sequences - 1, 2 , 5; Verify effectiveness of 10/12 recommendations |  | 10/12/2012 (A) | Updated Recommendations provided 10/12 via R. Gratton e-mail.
| 62.6.2.2 | Update logic to implement 10/12 sootblowing recommendations |  | 12/4/2012 (A) 12/8 (A) | Add Alarms as to when to implement "enhanced mode"; Issued 12/4, revision 12/8
| 62.6.3 | Change graphics on water cannon screens |  |  | LGE action
| 62.6.3 | Advise Criteria for Aggressive mode cleaning |  | 10/12 (A) | Updated Sootblowing Recommendations provided 10/12
| 62.6.4 | Joint Doosan/LGE/Bechtel Sootblower meeting |  | Jan 4th (10:00 AM) Meeting with DP - LGE to advise by 1/16 on water lances | See Actions below. duplicate of 77.2 Supporting data to be issued by DPS 2/12/13. Meeting scheduled for 2/22/13. - Same as # 77.2.
| 62.7 | Stall Meeting to review calcs/operation |  | 2012-07-26 | After 7:30 mtg
| 62.7 | Hydrojet Drain line hangers |  | f/c = Run system during outage | Doosan reported hangers are funciotning properly.
| 62.7.1 | Piping |  | 12/5/2012 (A) | Issued Recommendation on 12/5 - Multiple pressure gauges added to determine location of excess DP.
| 62.7.2 | Valve Friction |  | 12/5/2012 (A) | Issued Recommendation on 12/5
| 62.7.3 | Analysis |  | 12/5/2012 (A) | Issued Recommendation on 12/5
| 62.7.5 | Recommendations on Hydrojet Supply Pump |  | f/c = 1 week after running system | Pending pressure drop analysis above - Doosan confirms issues are with the check valve, pump is acceptable.
WN-0346 | 62.7.6 | Hyrdrojet Mounting Bolt Heat Damage |  | f/c = ??? | See G. Davis response 6/18. Diamond considers center plate acceptable, offers to trial an upgrade to inconnel. Being addrssed by Warranty groups
| 62.7.6 | Diamond Power Site Visit Report |  | 3/26/13(A) | Diamond Rep made minor mod's to program, reset numerous heat flux setponits. Full report issued 3/26/2013 by S. Hammond
LGE Action | 62.9 | Review ID Fan C factor |  | 16-Aug-13 (A) | LGE/Bechtel in agreement per 8/21/13 AI mtg. Doosan recommends to maintain existing C factor per S. Hammond 8/16. Increased C factor to Howden design number 68,316 (10/26). Implemented C from 57,310 to 64,044 7/26; Need O2 measurements local to ID fan to check, G. Jones to obtain readings after restart
Bechtel | 64 | Baghouse outlet vs ID fan inlet pressure readings |  | Complete | Modify sensing line routing to add slope, meeting with SESS 10/12
LGE Action | 64.1 | Update Logic for ID fan suction pressure |  | f/c = ??? | Update ID fan setpoints. LGE elects not to change per 3/29 P. Rabe. Bechtel provided recommendation 2/20/2013
| 65 | Verify if 100% Riverview is to be tested prior to outage |  | 2012-07-31 | Identify test dates
| 66 | Establish Hold points prior to outage for flame/burner observations |  | 2012-09-14 | Post Outage Testing planned 9/14
| 66.1 | Issue to go Test Plan |  | 9/26/2012 Updated | Final Version issued by R. Gratton 9/26. Identify any load reductions for deslagging - Per R. Gratton 9/24, 3 mills/half load once per week.
| 67 | Banjo - RCA |  | 2012-12-01 | Banjo RCA Dave Anderson
| 67.1 | Doosan to trial ceramic rope in Gap Areas on Burners (qty = 15) |  | during outage | Sketch Provided, to be applied to 15 burners
| 67.2 | Document Burner As left Condition |  | 9/17/2012(A) | Photos and Defects on each burner provided to LGE
| 68 | RCA for coal in coal pipe |  | f/c = ??
| 69 | Pyrite Test on TC1 mill, burning Riverview |  | 10/5 (A) | To verify amount of pyrite/spillage on the TC1 mill setup.
| 67.1.1 | Review Prior B and A mill coal pipe testing |  | 2012-08-17 | D. Hough provided summary - Recommends no further testing is required
| 67.1.2 | Move Burner Register Settings |  | Prelim 8/28 Final - 10/1/2012 | Finalized after outage, All burners moved8/29 to S/A = 100% T/A = 60% Mill K factors changed 8/29
| 67.1.3 | Review Coal Samples |  | 2012-08-01 | Sample Analysis shows nothing abnormal
| 67.1.4 | Clear out B PA Flow Element |  | 2012-08-01 | Completed 8/1
| 67.1.5 | Review FE full scale DP = 0.6 inwc |  | 2012-08-20 | Duplicate, see 59.1.2TC1 = 3 inwc +/- in operation for venturies, others have similar DP
| 67.1.6 | Review Transmitter location - above/below tapping points |  | 2012-08-20 | Duplicate - See 59.1.2TC1 = Below
| 70 | Verify B/C mill tuning parameter changes |  | 2012-09-01 | All Mills returned to original tuning parameters. Mill B only tuning parameters returned to original settings. C to be returned after outage, Doosan to Bring Emerson back on site after outage to finalize tuning, logic changes., Detuned only HAD, not the cold
| 70.1 | Inspect B coal Mill |  | 2012-08-01 | 7/31 - Approx. 2 feet of coal in PA inlet 8/2 - No coal at inlet
| 71.3 | Questions being sent to Alstom |  | f/c = ?? | Post Steam Inert, then Dry PF discharge to pyrites followed by Water injection
Bechtel | 71.4 | Issue Test Results on Mill Swirl Water Test |  | 2012-11-28 | Test okay, no spillover of water back into inlet Duct. J. Babcock to issue.
| 71.4.1 | Review 40 kpph PA flow when OOS |  |  | A= Low, <10 kpph B= 40 kpph C = 7 to 20 kpph F = <1 kpph
| 71.4.2 | Perform "Aggressive" S/A purge |  | 2012-08-01 | Close T/A's - 60%, S/A = 100% 8/2 - Close T/A to 25% on problem burner
| 72 | Aggressive S/A Purge Procedure |  | 9/20/2012 (A) | Table Issued 8/3 - To be incorporated into Burner purge procedure
| 72.1 | Purge Any OOS mill every 3 days |  | 8/29?? | Update Procedure
| 72.1.1 | Increase Mill B load line to +15% |  | 2012-08-01 | Returned to +10%
| 72.1.2 | B-2 Oil Gun Inspection |  | 2012-08-01 | Rental unit doesn't have temp capability. Doosan cameras to arrive 8/10
| 72.1.3 | Single Pipe Purge - Measure ea coal pipe flow |  | 2012-07-31 | 114 - 117 kpph reported, no pluggage
| 72.1.4 | Determine Furnace Camera Status |  | on-going | Insufficient Cooling, won't work.
| 73 | Mill Logic - Proportional Control vs HAD controls flow, Cold Air Damper controls temp |  | Hold - Watch item | Evaluate on Restart - Suggestions sent to Doosan 8/8
| 74 | Mill - Contact Alstom to open up Pyrite Removal Opening |  | f/c = ??? | Per Doosan - This is the largest size opening offered by Alstom and consistent with another recent Alstom job. Mill B Tripped 9/19 - Under evaluation Clarification questions asked 8/17, replies sent 8/22 LGE review - 9 of last 11 had high alarms Final Mill trips (mill D and E 9/7) prior to mini outage - No high alarm
| 75 | Pyrite Rejects - Evaluate Spillage |  | 10/18 (A) | Alstom recommends after air flow/burner issues resolved. Quote Rec'd to trim wing tips, if needed. Riverview run on TC1, rejects were approx. half of other fuel, but still 6 times higher on TC1 vs TC2
| 75.1 | Wing Tip - Procedure for Adjusting |  | 14-Nov-12 (A) | See T. Smth (Alstom e-mail of 14-Nov-12)
| 75.11 | Steam Inerting Valve - Leakage |  | TBD | LGE rebuilt Valves for 2C and 2E coal mills (found with steam cuts) Steam traps on 2D and 2F inspected - found to be working properly
| 75.12 | Mill - Water Slugs - Investigate Cause |  | 7/19(A) | No slope or drainage issues found. S. H. issued Doosan summary 7/19/13. D. Brann issued summary of Bechtel pipe (5/22) and Doosan to writeup findings
| 75.12 | LGE Recommends adding low point drain |  | TBD | WN-0452 issued, need feed back from # 75.11 to understand whether there is a need or not.
| 75.13 | Investigate Upstream of Doosan Steam inerting Scope the Piping/Steam Supply |  |  | Walked down, no findings. Doosan reported 2/25 seeing water after initially dry steam while testing the semi dry logic
| 75.1.1 | Verify any leaks into Mill |  | 2012-08-03 | Operations - checked fire water, swirl water, steam inerting - No significant leaks found
| 75.2 | Revise control logic to dry clear-out of PF followed by water injection |  |  | Revised Philosophy provided 11/13. Comments sent 11/15
Bechtel | 75.3 | Increase pyrites removal system capacity |  | 4/5/13(A) | Clarifications sent to R. Donais 1/30. Alstom response sent 4/5
| 75.4 | Add air deflector at mill inlet |  |  | Adding Air Dam instead
| 75.5 | Add rod out connections at pyrites hopper outlet (Alstom to confirm) |  |  | Doosan Reply: Recommending no need for change to current system
| 75.6 | Change pyrites hopper overflow to loop seal |  | 4/5/3013(A) | Pending Doosan Reply; Alstom to quote. Alstom response sent 4/5
| 75.7 | Modify water lances in mill inlet duct (Design) |  | 1/11/13 (A) | Design Confirmed and Agreed Upon
| 75.7.1 | Modify water lances in mill inlet duct |  | f/c = TBC | Mod's completed to improve Operator Access sent 5/23 (D. Groom)
| 75.8 | Modify PA inlet duct drain |  | (A)
| 75.9 | Mill Clear Out Check Sheets |  |  | Move to Watch item. Doosan to complete check sheets
| 76 | Plant Trip during shutdown - evaluate logic | 2012-11-08 | 12/2/2012 (A) and 12/14(A) | Boiler Circ Pump - Review subcooling valve logic; Issued logic on 12/2; Philosophy agreed. Pump Motor protection revised logic issued 12/14 (based on cooling water temps)
| 77 | SCR Catalyst Sample Analysis | 2012-11-17 | 2013-03-28 | Pending results received from Hitachi. Deactivation curve updated and issued 08-Apr-13, catalyst report provided to LGE/Bechtel.
| 77 | Aggressive Mode Cleaning - Criteria for use |  | 12/15/2012(A) | Based on operations judjement to reduce FEGT balanced against thermal fatigue damage over a one month period.
| 77.1 | DPII to proivde analysis of thermal fatigue and cleaning success |  | 1/4/13 (A) | D. Groom to issue mtg notes from 1/4 mtg, send package to LGE for review of recommended water lances
| 77.2 | Send recommendation for Water lances to LGE |  | 2013-02-22 | See S. Hammond 1/29 - Minimal Benefit to FEGT/NOx. References Provided. LGE to review and advise. Meeting held 2/22/13.
| 77.2.1 | Water Lance - Follow Up Actions |  | f/c=??? | Evaluate impacts to SO3 conversions. Evaluate FEGT vs S/Ht and R/Ht spray flows. (See S. Hammond e-mail of 3/14). DPS response sent 04/08/13 - Item closed.
| 78 | BURNER THROATS
| 78 | Heat Flux Sensors Broken - Removal of the heat flux sensor from the boiler tubes on the furnace wall |  | 12/15/2012(A) | 1. Use pattern from similar zone (preferred) or 2. Use Manaul Sequence
| 78.1 | WN-0344 - Burner Tile / Quarl Inspections & any Repairs SMR0115 |  | Outage Inspection Item | comments provided 2/4 by Bechtel. Repairs being made by LGE.
| 80 | Max Burner Heat Input - Allow 10% above BMCR for 10 minutes |  | 12/10(A)/12/20(A) | See. S. Hammond e-mail of 12/10, Implemented 12/20 by C. Dukes
| 81 | PA/SA beck/damper linkage slipping |  | Outage Item | Re-set during Outage. All S/A drives/dampers retorqued and positions reverified
| 82 | PA Venturi - HP Tap not Responding |  | Venturi Testing completed | Revised PA K factors implemented approx. 6/20, Traverse Test Results distributed 6/18 via G. Jones
| 82.1 | Distibute Cold Air Venturi Test Results, Damper Characterization |  |  | Superseeded by Hot Air Flow Traverse Test
| 83.1 | PA-Venturi's (Storm) |  | f/c = ??? | A, E mills modelling completed. Turnign vanes modified at A and E mills. See item 82 above.
| 83.1 | PA - Traverse Tests | 2013-06-01 | Completed | Revised K factors implemented
| 83.3 | PA - Coal Pipe Distribution (Storm) |  | 2013-02-13 | Results distributed. Raw data issued 2/8/13. DPS issued report 2/13/13.
| 83.4 | PA - Issue Venturi Calibration Test Procedure |  | 2013-06-06 | DPS revised and reissued Mill PA test procedure
| 83.5 | PA - Schedule Addt'l coal pipe testing |  | f/c = TBC | Combustion Optimization Results issued 7/24
| 83.6 | SA - Existing Taps (FERCO) |  | 2/26/13(A) | Results to be analyzed/recommendations provided. Raw data issued 2/5/13. DPS issued FERCO report 2/26/13.
| 83.7 | SA - Update Test Procedure |  | 6/16/13 (A) | See G. Jones e-mail of 6/16
| 83.9 | PA - Response Testing of Venturis w/new HP Taps |  | 5/6 - 5-10 | Repeat of 82 - deleted
| 83.9 | SA - Alternate HP Tap |  | 2013-02-15 | Results to be analyzed/recommendations provided. DPS to issue comparative data and summary - same as # 8.32.4.1.
| 84 | WCAH Redesign (Armstrong) |  | 2013-02-21 | See Doosan reply 1/24 to freezing concerns. Meeting held 2/21/13.
| 84.1 | Test WCAH Flow |  | Outage Inspection of C.V. | 2nd WCAH flow control valve found to be plugged, similar to the B valve. Trim was replaced in spring 2013 outage
| 84.2.1 | WCAH P&ID markup |  | 14-Aug-13 (A) | P. Rabe comments sent 23-Aug-13. See Draft P&ID submitted via S. Hammond 14-Aug-13
| 84.2.1.1 | Doosan Response to LGE P&ID comments. |  | 26-Nov-13 (A) | See S. Hammond reply 12-Sep-13. Doosan responded 11/26 via S. Hammond to comments made 06-Nov-13 by P. Rabe re Position of temperature measurement and Isolating valves.
LGE Action | 84.2.2 | WCAH Racking Sketches |  | 19-Aug-13 (A) | See P. Rabe comments 8/26. Joint walkdown held W/O 29-Jul-13 (Bechtel, LGE, Doosan, Youngblood)
| 85 | Nox Outlet Probe Traverse |  | 2013-02-13 | Data to be Distributed. DPS issued test results 2/13. Further Nox distribution testing to be done post SCR modifications.
WN-0325 | 86 | COEN Ignitors - COEN to provide 35 new spark rod tips (Longer at 48 inches) |  | New spark rod tips, 5 Del'd, balance of 30 f/c = ??? | 5 on C Row. Watch on restart for approx. 2 weeks - Verify logic mods and new tips. Agreed 03-Jul-13 to move to watch item, continue with existing oil ignitors until burner mods
LGE Action | 87 | Building Vacuum |  | 2013-06-05 | Reponse Provided 6/5. Close off Inside building damper, see Doosan modified logic, monitor condensate pump performance. LGE to provide building vacuum readings taken during test. 4/16 P - Follow up clarifications requested 4/16
| 88 | OT Conversion - |  | on-going
LGE Action | 89 | RAT (13.8kV)to MAT Transfer - Unit Tripped |  | 2013-02-19 | Found issues in the transfer macro. Bechtel provided reply 2/19
| 90 | Updated Safety Valve Data Sheets |  | See AIL # 103 | Hard copy update completed - DPS to confirm status of CD's . Verify manual updates include new ID fan purge system. Final Manual update, prior to burner replacements to be issued.
LGE Action | 93 | ID Fan - Calibrate Stall Detection System (Stall Probes) |  |  | Doosan will calibrate the "new" stall warning system prior to restart - Completed, Laura to verify with Ricky stall probes have previously been calibrated.
| 94 | AIR HEATER RESTART ACTIONS |  |  | Monitor for dry steam, move Lime Injection Silo
| 94.1 | Monitor FD Fan Air Intake during Unit Operation/Rainfall |  | During Rain | - Modified Rain Hood intake superseeds this action - Close item. 6/13 Observation showed little water ingress. Similar observation 7/2 during heavy rainfall
| 94.2 | Change Air Heater Blow Pressures |  | At Restart | Cold End to 130 psig, Hot End to 160 psig, verify orifice plate size
| 94.3 | Monitor/Verify Dry Steam to Air Heater. |  | 17-Nov-13 (A) | Tell Tales in use thus far. Doosan response issued 17-Nov-13.
LGE Action | 94.4 | Relocate Temporary Lime Silo |  |  | Plan to move to the West end of building
| 94.5 | Verify ACET Logic BTSC changed to 80F |  | f/c = ??? | C. Dukes verified it has been changed to 80 F.
| 94.6 | Alstom Recommendations on Air Heater Air Cleaning |  |  | Alstom requires DRY, Isturment quality air, which is not available 245 psig Hot End- 4380 scfm 190 psig Cold End - 3460 scfm
| 94.6 | Verify min Air Inlet Temp - Alstom |  | f/c=??? | Alstom Response provided by Doosan, ACET is the governing criteria
| 95 | O2 Probes - Extend Wing O2 Probes |  | At Restart | Bring Emerson TA to site to support restart
| 96.2 | Stacks to measure SO3, Acid dew point. | 7/24 | 22-Aug-13 (A) STACs Test Report 08-Oct-13 (A) Updated Report | Stacs report and Doosan summary provided 22-Aug-13 (A) via S. Hammond. Bechtel comments sent 22-Aug-13.
| 96.3 | Hitachi Evaluation of Ash Pluggage and elevated SO3. |  | 17-Nov-13 (A) | Hitachi response provided via S. Hammond 11/17/13.
| 100 | Burner Purge Procedures - Verify Current Requirements |  | 7/19/13(A) | Doosan recommends to maintain current procedures
| 102 | Catalyst Sample Results (from Spring '13 Outage) (catalyst end of life f/c March 1st, 2015) |  | 22-Aug-13 (A) | See Hitachi report submitted via S. Hammond 14-Aug-13, revised 22-Aug-13. Plan for Meeting on catalyst Selection for Spring 2014 Outage - LG&E to replace one layer with standard height catalyst in Spring 2014 outage. Corrected report issued via S. Hammond e-mail dated 08-Oct-13.
| 104 | ID fan Insulation - Discharge Ring |  | 8/9/2013 (A) | Complete Insulation
| 105 | WCAH Racking Sketches |  |  | Covered under item 84.2.2. J. Lee, Youngblood, LGE, Bechtel to walkdown
| 107 | Optimize Ht flux sensor settings vs Load |  | 19-Aug-13 DPII to visit site | Ref. S. H. e-mail of 7/27/2013. DPII to visit site 8/19 and 8/20. LGE to assign internal "champion"
| 108 | Mini-Outage Work List |  | f/c = 10-Oct-13 | ID fan Purge System Inspection, SCR Inspection, Air Heater Wash Verifcation, Pull F row oil ignitors, A3/D3 burners?, Add coal pipe manometers
AEROFOIL
| 9 | Verification of Aerofoil calibration checks Traverse Data Integrated into k factors Finalize k factors | 2012-05-20 | 2012-07-20 | - K factors and calcs issued 7/23. Implemented 7/24. Verified Acceptable 7/25
| 11 | Summation of all Aerofoil's = Combustion Calc (Verification Step) | 2012-05-20 | 2012-07-20 | Issued 7/23
| 11.1 | Review k Factor Calc | 2012-06-25 | 2012-06-25 | k factor calc reviewed in joint mtg 6/6/26
| 25.1 | Core Air Tips - Doosan to modify 5 of LGE spares (remove venturi, add section of HR-120) |  | 2012-08-08 | 7 total on site as of 8/9. Move to outage item
| 28.1 | Contact Effox for recommendations - Pin shafts (S/A dampers - A both sides, C South side | 2012-06-25 | 2012-09-01 | Set up dampers & Beck Drives during outage. Write Up meeting minutes
| 28.2 | Meeting with Beck |  | 2012-08-17 | Follow Up Reply rec'd 8/15. Partial response rec'd 8/14. Doosan requested additional clarifications from Effox. Doosan confirms torque is adequate and recommend to stay with current stroke times (approx. 20 seconds)
| 32 | NOx at SCR stack reading | 2012-07-02 | Watch | Watch after SCR/Ammonia tuning completed. 8.18 - Move to watch item
| 34 | Air Htr temp balance and Sootblower effectiveness | f/c | 2012-08-13 | Performance Review Rec'ed 8/14
November OUTAGE ITEMS
| 1 | Burners - Replace Thermal Rope |  |  | All 30 Burners
| 2 | Burners - Weld Repairs |  |  | See Doosan List
| 3 | PA FE - Correct Connection behind seal air pipe
| 4 | PA FE - Replace temporary pipe at Transmitters
| 5 | Amstar
| 7 | Inspect supherheat/rht biasing damper E |  |  | Linkage has broken twice
| 8 | Modify Impulse lines for ID fan inlet pressure measurement