## To Go Activities
2014-02-25
| # | Description | Start | Finish | Remarks
LOGIC/TUNING DCS UPDATES
| 8.25 | List of all logic mods and latest rev (include the red lines). |  | On-going, current is 07-Oct-13 | Latest list issued via S. Hammond 07-Oct-13 (WCAH Logic revision noted by Chris Dukes added).
| 8.32 | REVISED LOGIC TO BE ISSUED
| 59.1.6.1 | Mill Temperature Control Logic - Option 1 (Temperature Kicker, move HAD and CAD both initially). Variable gain/integral added to all mills as of 24-Jul-13, switch from slow to fast gain at 33% feedrate. |  | Repeat 24MW/Min ramp with 59% ODP f/c = TBC (LGE) | 12 MW/min successfully achieved 18-Aug-13. 24 MW/min successfully achieved 24~25-Aug-13. Doosan requests 59% ODP & LGE to repeat the 24MW/min ramp. Doosan to confirm ramp steps, Bechtel confirmed smaller increments acceptable per test procedure (80 - 100% ok). Doosan agreed verbally (06-Nov-13) and via e-mail 17-Nov-13.
| 79 | Provide Summary Report of Mill Swings and final resolution. |  | f/c = 23-Dec-13 (A) | Summary report of mill swings and final resolution to be provided once PA flow measurement resolved - thought to be the cause. (F mill HAD position feedback off by 5%, add to LGE outage work order). Summary report issued 23-Dec-13. Bechtel comments to be incorporated and document reissued as a part of AIL # 106
ACTION ITEMS
| 62 | ID FAN STALL
| 62.8 | Revise Stall Alarm curve. |  | 16-Aug-13 (A) Alternative curves f/c = 07-Mar-14 | Doosan to develop alternative Stall alarm curves that follow fan curve, have available if needed. Doosan recommends to maintain existing stall lines via S. Hammond 16-Aug-13.
FURNACE HYDROJETS
| 62.7.4 | Pressure Drop Analysis (Replace Check Valves). |  | 21/22-Jan-14 (A) | Check Valve, Water Hammer and Pipe Support correction - Closed. Doosan to repeat pressure measurements and confirm that the new check valve is working as expected once the tuning is completed by DPII. DPII (Barry Petty) attended TC2 on 21/22-Jan-14, report issued and circulated on 14-Feb-14.
| 83 | AIR FLOW TRAVERSE TESTING
| 83.8 | SA - Recommendations on k factors/logic. |  | DPS response sent 25-Oct-13 (A) | K factor recommendations issued 30-Jul-13 (Doosan recommends to keep as-is). Bechtel response 30-Jul-13, 01-Aug-13 and 02-Oct-13.
| 83.8.1 | Restart procedure to include methodology for checking the SA K factors |  | f/c = TBC | Doosan to update restart procedure.
MISCELLANEOUS
| 84.2.2.1 | Doosan response to LGE WCAH Racking Sketches comments. |  | 08-Feb-14 (A) | 10-Feb-14: Rick Melloan comment re pulling of coils to be responded to. Doosan response sent 13-Feb-14.
WN-0443 | 91 | Ammonia Pumping Skid - Mod to permit starting of idle pump. |  | Mod during Spring outage | Bechtel progressing modifications with Aether.
LGE Action | 92 | ID fan Hydraulic Cylinder Failure - Logic mod requested (applies to FD fans also). |  | 04-Oct-13 (A) | C. Dukes recommended Solution of 13-May-13. DPS concern issued 04-Oct-13 with logic mod for approval to implement. C. Dukes ok with logic, 07-Nov-13. Implemented and Logic issued by Chris Dukes on 13-Feb-14 for Doosan review. 20-Feb-14 - Doosan confirmed correct implementation.
| 96 | SCR SO3 & PLUGGAGE ISSUE (OPEN ITEMS) |  |  | See Restart Recommendations, S. Hammond e-mail 16-May-13.
| 96.1 | Evaluate Additional vs improved sonic horns. |  | Outage Inspection Report 07-Oct-13 (A). Recommendation sent 26-Nov-13 (A) | Recommendation provided 11/26/13 via S. Hammond. Joint LGE/Doosan inspection at start of outage to verify ash build up and any further actions - Completed 17-Feb-14
| 97 | FURNACE FEGT
| 97.1 | Double Frequency of 4 Platen Lowers (IK 9,10, 19,20). Flux Sensor Recommendations. |  | f/c = 17-Dec-13 (A) | LGE addressing logic issue with Diamond. Seq 10/20 logic issues, brings in faults/alarms. 17-Dec-13: Doosan recommends to review the data again following a confirmed period of operation (minimum 2 days' operation at steady load without mill changes) with 4 hourly cycles of the lower platen sootblowers. LGE confirmed sequencing issues resolved with DPII support prior to start of outage. Doosan to review and comment. LGE concern re continuation of increased frequency and potential for tube erosion.
WN- | 101 | Coal Pipe Purge Procedures - Verify Current Requirements. |  | Joint LGE/Doosan walk down required | LGE/Doosan to walk down week of Nov. 4th. LGE agrees to stop purge on mills D and F, verify no deposits during Spring 2014 outage. LGE requests means to verify no steam leakage. LGE confirmed that pipe purges stopped on all mills for Jan-14 and suggested the fitting of observation windows in the duct as a means to verify no steam leakage, Doosan to review.
| 103 | Manual Update. |  | Electronic: 22-Nov-13 Hardcopy: f/c = Jan~Feb-14 | Hard Copies - ID fan stall purge system, Burner T/C alarms, …etc. - delivered to TC2 on 11-Dec-13 (With Ron G) and agreed with Jim Craft / Michelle Griffith that update will take place late Jan-14/early Feb-14.
| 106 | Commissioning Records Package. |  | f/c = End of Mar-14 | Doosan to package commissioning records and submit to Bechtel/LGE.
| 109 | Lime Injection Upstream of Air Heater. |  | f/c = TBC | Evaluate possibilitiy of Testing one month prior to outage. Joint walkdown with Mark Thomas held 13-Nov-13. Conference call on 11-Dec-13, Lances and splitters forecast to be delivered TC2 w/c 06-Jan-14, LGE looking at injection skid and hoses for hook up.
| 110 | Coal Pipe Manometer Data/Analysis. |  | Ongoing Current data set issued 17-Dec-13 | 1st data set to be sent 11/6/13. Plan for a set of readings once per week taken using a digital manometer. 1st set of readings taken 14-Oct-13. Data set distributed on 14-Feb-14. Readings being analysed by Doosan, f/c = 07-Mar-14
Spring 2014 Outage Items
| 2.2.7.2 SMR0141 | Borescope PF Pipe Inspection |  | 07-May-13 (A) | Move to Spring 2014 Outage List for verification. No deposits found, RCA updated - 07-May-13 (A).
| 62.4 SMR0127 | Modify stall sensing ports per Howden recommendations |  | 28-Aug-13 (A) Further analysis required | Doosan evaluating whether to insulate piping. See D. Groom analysis 28-Aug-13. Results show below ADP, Doosan further evaluating. Open Issue - Heating for purge air - See DPS e-mail 04-Apr-13, purge air temperature to be monitored at restart. Doosan provided commissioning records for purge air system, Manual updates required.. Taps inspected during Sep-13 mini outage and minimal build up observed. To be re-inspected during 2014 outage and if required cleaned and the pipe insulated.
| 99.1 | Alstom Mill Wing Tip Modification - Mill E investigation |  | f/c = 16-Dec-13 (A) | Mill E wing tip mods complete, removed 1", resulted in excessive coal spillage. LG&E replaced the wing tip during mini outage, PA flow set at +15% to reduce coal spillage. As per conference call on 16-Dec-13, Mill E clearance between the vane wheel and air restriction ring to be inspected, f/c 16-Dec-13. Mill E flows traversed on 30-Jan-14 and found to be correct. Inspection of Mill E required during outage, VOP's to be identified and burner pictures to be taken.
| 2014-1 SMR0095 | The replacement WCAH coils currently located on the turbine room floor have internal debris in them (rust and slag). |  | 23-Feb-14 (A) | Doosan to provide the plans for cleaning up these coils prior to placing them into service. Doosan response provided 23-Feb-14.
| 2014-2 SMR0132 | Doosan to review small threaded holes on burner front plate. |  | 23-Feb-14 (A) | Doosan response provided 23-Feb-14.
| 2014-3 SMR0127 | Doosan to review tubing to purge meters on ID fan - No expansion facility causing damage to meters |  | f/c = 28-Feb-14
WATCH ITEMS
| 8.12 | Revised SA Crossover f(x) Logic | ??? | f/c = ??? | Optimize Curve - On-going. On new curve, Target = 6 inwc
| 8.13 | Revised Part Load 02 f(x) curve | 2012-08-01 | 2012-08-19 | Need low load operation f/c ramps 14-Aug-13 to 19-Aug-13
| 8.23 | Engr Function to change stoich air by up to 3% |  | Watch | See 01-May-13 Meeting minutes. To be left at current +2%. Review if cross - limit alarms reoccur upon startup, reduce cross limit margin to 0.5 kpph
| 8.31 | Mill outlet Temp change to 150 F |  | 2013-02-01 | Pending additional fuel testing.
| 8.32.8 | Increasing Mill Exit Setpoint during mill startup |  | Watch | See C. Dukes suggested Logic changes for startup vs operation, 26-Jun-13 (change tuning after 30% load)
| 8.32.11 | S/A Damper balancing Logic |  | f/c = ?? | Leave as-is, with operator bias station. See S. Montgomery reply 12/19. Increases demand on already busy controllers and CFD suggests its not needed.
| 8.33 | O2 Trim Limits - Limited by 0.88 Stoich |  | 13-Aug-13 (A) | LGE has chosen to keep as-is due to CO concerns. Currently at 0.89, Doosan recommends to lower to 0.87 via S. Hammond email of 13-Aug-13
| 32 | NOx at SCR stack reading | 2012-07-02 | Watch | Watch after SCR/Ammonia tuning completed. 8.18
| 38 | Finalize Mill Classifier speed (due to increase in mill load line, at 76 rpm) |  | f/c=??? | Mill A 72rpm=67% Mill A=78rpm = 75.7%. Finalize classifier speed curve once PA flow is finalized. Put all Mills @ 76rpm
| 63 | Training on the dampers optimum position setting for the operators |  | f/c | LGE to develop list of needed training.
| 71 | PURGE MILL CONTENTS TO FURNACE AFTER STEAM INERT |  |  | Meeting held 17-Sep-12; Meeting scheduled for 28-Nov-12
| 71.1 | Confirm Insurers/legal okay with LGE accepting responsibility with the NFPA criteria |  |  | LGE action
| 71.2 | Doosan to confirm no other barriers to implementing purge to furnace |  |  | Define what load conditions must exist prior to purging to furnace, no of oil burners in service for example
| 75.9 | Mill Clear Out Check Sheets |  |  | Move to Watch item. Doosan to complete check sheets
| 83.2 | PA -Venturis - PA Fan Upgrade Options |  |  | Options presented in Renfrew - Move to watch item
TESTING (Pending Completion of Optimization)
LGE Action | 4 | Fly Ash Removal Test |  | 2013-11-20 | Rescheduled to Dec. 5th or 6th.
LGE Action | 5 | Bottom Ash Removal Test |  | Prelim Tests on-going, official test f/c = ??? | Alstom witnessed 8 hour test 05-Sep-13. Successful test. Alstom evaluating hydaulic pressures on restart.
CLOSED ITEMS
| 1 | F Row Burner Inspection | 2013-02-15 | 2013-02-22 | Target is 2/15, no later than 2/22. Inspection Completed. See Doosan presentation 2/21
| 1 | Check-Out Back to DCS | 2012-04-25 | 2012-05-21 | Burner Thermocouples ~ 130 I/O. Will finish when C3 and E1 burners are reinstalled
| 1.5 | Address B low flow alarm (microwave instrument) | 2012-07-06 | ??? | Bruce Provided instrument instructions, I&C to verify calibration. Bruce to get with Rick P.
Forney / Coen | 2 | Flame Scanner; Inspect mounting and amplifier settings, Adjust gain and discrimination Set up oil Igniters/Scanner | 2012-05-21 | 2012-08-14 | Complete. 33 (28 + 5) longer air tubes on site as of 7/25. Doosan to install during outage
| 2 | Doosan to perform metallurgy test on sampling of deformed Core Air Tubes to determine if correct material was provided |  | 2012-12-07 | Lab test results confirm mat'l is HR120
| 2.1 | Doosan to evaluate atomizing air cooling to be applied to all rows? C and F only currently. |  | 8/20 e-mail via R. Gratton | Atomizing Air Cooling Logic requested to be applied to all burner by R. Gratton 8/20/2012. Coen Report Rec'd, released to work other burners. B-Row complete working all other rows as can Logic for Remaining Rows??
| 2.1 | Oil Gun Tip Failures |  |  | Watch added air consumption
| 2.2 | Coal Scanner Setup - Verify flame dropout timer - 3 or 4 seconds |  | 9/5 (A) | Replies provided 9/5 (A). 1. Forney to provide site specific set up procedure, 2. code references for dropout times. 3. Doosan to arrange Forney on-site prior to shutdown - back on site for restart
| 2.2.1 | Track Scanner Setup/Completeness |  | 11/13/2012 (A) | Two Oil Guns on B row allowed oil injection to a dark furnace. Three ignitors on B row have oil flame signal dropping out. Pending Forney Report for partial scope. Additional rows to be addressed on startup. see 2.2.3.4
| 2.2.1.1 | Doosan to consider alternative scanner Suppliers/equipment |  | ???
| 2.2.2 | LGE may Trial alternate designed scanner |  | 10/12(A) | John Grist provided recommendations 10/12
| 2.2.3 | Forney to submit scanner tuning procedures for Trimble |  | 10/18/2012 (A) | Channel "B" clarificaiton reqeusted. 10/29
WN-0325 | 2.2.3.1 | Forney Scanners - Retune on Restart |  | f/c = At Restart (5/26) | Forney on site 5/26 to monitor through 40% load. No issues reported. Forney Released. Doosan to respond to warranty notice.
LGE Action | 2.2.4 | Add Fibre Optics for Scanners | 2012-12-02 | on-going | LGE agrees to close. Guide Tube did not recieve sufficient cooling air. Currently on original scanners. on-going evaluation (D Row) - All 5 with heat damage week of Jan 15th LGE to confirm current status and whether item can be closed.
Hitachi | 2.2.4 | Dark Check - Clarify load point when it can be omitted (>40% load?) |  | 10/22 (A) | Dark Check changed from 50% to 40%. Major Issue - Can't pass dark check due to "seeing" opposite wall oil flame
| 2.2.5 | Scanner/Ignitor Mtg to address Issues | 2012-11-06 |  | Meeting held on 11/14 @ 1:00
| 2.2.5 | Logic Check - Verify BMS logic aligns with requested load limits on dark check |  | 10/22 (A) | Doosan verified logic is correct and up to date
| 2.2.6 | Bannjo Failure Initial Root Cause Analysis |  | 12/20/2012(A) | 5 banjos being replaced (all CCW); 30 burners - refractory being added in gap; Draft issued on 11/27; Final RCA issued 12/20
| 2.2.7 | PF Pipe - Coal Layout - Root Cause Analysis | 2012-11-21 | 12/07/2012(A) | Meeting held 11/28; Single pipe purge to be completed during restart; Updated procedure for single pipe purge?
| 2.2.7.1 | Single Pipe Purge - Every 720 Hours |  | 2013-02-15 | Run Time Logic proposed 2/4. Changed from 500 to 720 hours per S. Hammond 1/18 e-mail. Doosan provided logic 2/12 (A), implementation confirmed.
| 2.2.7.2 | Borescope PF Pipe Inspection |  | 05/07/13 (A) | Move to Spring 2014 Outage List for verification. No deposits found, RCA updated - 05/07/13 (A).
| 2.2.7.2 | Borescope PF Pipe Inspection |  | 05/07/13 (A) | Move to Spring 2014 Outage List for verification. No deposits found, RCA updated - 05/07/13 (A).
| 2.2.7.3 | Steam Inerting - Review of steam Qty |  | 2013-02-15 | Updated Philosophy sent 1/11. Comments provided 1/18. DPS responded 2/14/13, item closed pending boroscope inspection
| 2.2.8 | Banjo Replacements for Owner Spares |  | f/c = 05/20/13 Delivery | Delivered 20May13
| 3 | Doosan to review material grade and next order of core air spare parts is to be appropriate material grade |  | Complete | DPS notes that HR160 has a higher resistance to oxidation but on examination of the data sheets, inferior mechanical properties than HR120. DPS conclusion is therefore to remain with the HR120.
Bechtel | 3 | CA Tube Insulation |  | 2012-07-14 | 50% complete. (E row 100% complete)
| 4 | Doosan to perform and submit a RCA for banjo casing liner cracks |  | 2012-12-01 | DPS engineer on site 11/8/2012 to determine RCA
| 4 | Motor Run in | 2012-05-21 | 2012-05-21
Hitachi | 5 | Check-Outs and Start-up | 2012-05-21 | 2012-05-23
| 5 | PAC Lances pluggage |  | watch | None reported in last two weeks, operations verified no pluggage
| 6 | A3 T/A damper is locked |  |  | Corrected during 9/29 Economizer Tube leak outage
| 6 | AFCU Skid Tuning | 2012-06-25 | 2012-07-02 | Logic to be tuned item same as 8.15
| 7 | Doosan to arrange a joint Alstom/Doosan/LGE/Bechtel meeting to discuss mill clear out issues |  | 11/28/2012 (A) | Joint meeting planned for 2:00 PM 11/28
| 7 | Function Test | 2012-05-23 | 2012-05-25 | On coal.
Emerson | 8 | DCS Update Tuning | 2012-05-24 | 2012-07-09 | On going. Mill tuning.
| 8.1 | Sonic Horn logic |  | ?? | Complete
| 8.1 | BCP Cooling Water Temperature Logic |  | ?? | Complete
| 8.2 | Coal Quality factor |  | 10/27(A) | S. Hammond e-mail 10/27; LGE action - agree or provide comments
| 8.2 | Sonic Horn Graphic |  | ?? | Complete
| 8.3 | (Air Balance - Recheck after Beck Changes) |  | Move to Watch | RDL's balanced 10/6. Windbox rows balanced side to side week of 9/25
| 8.3 | Pressure Switches Associated with the New Layer 3 Sonic Horns Air Supply |  | ?? | Complete
| 8.4 | Pressure Switch Graphic |  | ?? | Complete
| 8.5 | Catalyst layer 3 Graphic |  | ?? | Complete
| 8.6 | AFCU Skid: The flow transmitters tagged 2SCRFT710 AND 2SCRFT711 are to be re-ranged to 0-800lb/hr. |  | ?? | Complete
| 8.7 | AFCU Skid: The ammonia flow control loop required correction to the ammonia demand molecular weight and the boiler heat input. |  | ?? | Complete
| 8.8 | FD Fan Intake Damper Control Logic |  | ?? | Complete
| 8.9 | PF Failure to Ignite Logic |  | ?? | Complete
| 8.11 | O2 Auto Trim Minimum Limit Logic | ??? | 2012-07-02 | Fine tuning w/Emerson DCS Engineer (David Lee on site as of 6/25)
| 8.11.1 | O2 Trim - OFA Only |  | f/c = ??? | See 5/1 Meeting Minutes - O2 Trim being implemented for S/A AND OFA.
| 8.11.2 | Analysis of the O2 Trim Change |  | Preliminary analysis provided; Further review and assessment 1/10/13 | Is this better or worse than old logic? Revert to prior logic?
LGE Action | 8.14 | Ammonia Control Logic - Outlet Lbs/MMBtu Control Monitor/Tuning | 2013-06-09 | f/c = 13-Sep-13 | Per P. Rabe, tuning acceptable 8/21/13. Tuning Report submitted 8/13 for Review. Comments requested by 30-Aug-13
LGE Action | 8.14.1 | Percent Removal Logic for ammonia | 2013-06-09 | f/c = 13-Sep-13 | Per P. Rabe, tuning acceptable 8/21/13. Tuning Report submitted 8/13 for Review. Comments requested by 30-Aug-13
| 8.15 | Ammonia Control Logic - Percent Removal Logic | ??? | 2012-07-13 | Bechtel sent to LGE to respond. Doosan advised this would be a scope change.
| 8.16 | B-2 & F-1 Temp over 1100 trip of Mill | 2012-06-13 | 2012-06-25 | Flame temp traverses initiated, discuss @ meeting 6/20
| 8.17 | Purge Logic: |  | 2012-07-06 | - SAME AS ITEM 50.1 Logic mod provided 6/26 - Single pipe purge didn’t work, PA damper logic issue. LGE to review. - Doosan to advise Criteria for when it can be implemented (load? Min no. mills?) LGE requests Procedure
| 8.18 | SCR Optimization |  |  | Moved to below
| 8.18 | SCR Optimization Procedure |  | 7/9(A) | Revised Draft issued 7/9
LGE Action | 8.18.1 | SCR Tuning Results |  | 14-Aug-13(A) Update 21-Sep-13 (A) | P. Rabe confirmed to close 10/30. Bechtel/LGE to review updated version. See Bechtel Questons sent 14-Aug-13. See Fuel Tech report submitted via S. Hammond 14-Aug-13
| 8.19 | Finalize Stoichiometry Curve (Phase 5) | 2013-06-24 | 7/29/2013 (A) | See S. Hammond response 7/29 advising to keep Stoichiometry as is, BZS = 1.0.
| 8.21 | S/Heat Reheat damper logic change |  | f/c = TBD | R.Gratton reported 8/15 tuning is complete. LGE okay with status. Will be relooked at during winter rating (809 MW's starting Oct. 1st)
LGE Action | 8.22 | OFA Logic change (6 mill operating-min demand) |  | 2013-08-02 | Logic changes acceptable Per P. Rabe 7/26/2013. Resent 7/3/2013. S. Hammond e-mail 10/27; LGE action - agree or provide comments. LGE action
| 8.24 | Implement single pipe purge logic |  | 2012-07-31 | Completed and tested 7/31
| 8.26 | Eliminate Feedwater Bias |  | 11/9/2012 (A) | Friday Nov. 9th proposed, 10:00 AM
| 8.27 | Min Cooling Position for Windbox Dampers (logic and control to balance flow rate) |  | 12/08/2012 (A) | Top Rows at 28%, middle at 25%, bottom at 21% per S. Hammond 12/8
| 8.27.1 | Verify Burner OOS temps are acceptable |  | 22-Aug-13 (A) C & F mills, E mill (29-Aug-13), remainder by TBC | All verified as acceptable per R. Gratton on10/30. F(x) logic provided via S. Hammond 22-Aug-13 for top two rows. Will evaluate and then decide if other mills receive as well. C & F = 38%, A & D Row = 34%, B & E Row = 29%
| 8.28 | Core Air Dampers 100% Open OOS |  | 10/1 (A) Logic Implemented = ?? | Doosan incorporated Comments
| 8.32 | Optimum Damper Positions, P/A |  |  | Attempted 55 percent 10/9, didn't work, reverted back to 50 percent.
| 8.33 | GAH S/A Bypass Damper Logic |  | 1/29/13 (A 2/1/13 Implemented | Updated Logic provided 1/29. Correct discrepancies between A and B sides. Doosan issued logic 1/16
| 8.34 | Fuel Oil Pressure Logic |  |  | R. Gratton confirmed working acceptably. S. Montgomery replies 1/24
| 8.23.1 | Update System Descriptions for Logic Changes |  | 12/11/2012 (A) | Draft Operating Philosophy issued 11/22; Issued final on 12/11
| 8.25.1 | List for all tuning parameter changes |  | 2012-10-09
| 8.26.1 | Update FW Bias Logic |  | 11/12/2012 (A)
| 8.28.1 | Verify acceptable temps achieved (Core Air Tubes) |  | 2013-08-20 | See core Air Temp Report issued 8/20 via S. Hammond. Doosan recommends temp are acceptable.
| 8.29 | Optimum Damper Positions, S/A |  | Following Spring 2014 Outage | S. Hammond reply 8/14 - To be performed during restart on De-Nox burners. Move to Restart Activities
| 8.32.1 | Venturi - Eliminate Auto Purge |  | 12/4/2012 (A) | Currently being drafted, to be issued on 11/27; Issued on 12/4; DPS proposed totally removing the PA flow purge logic. LG&E rejected this. DPS /LG&E to agree modifications removing the purge solenoid logic but enabling the operator to freeze the flow signal during a manual purge.
| 8.32.10 | Plant Trip during shutdown - review feedwater control logic |  | Close? | A. Stano confirmed demand did not change, but speed dropped from 3,000 to 2,400 rpm. LGE checking oil filters and further troubleshooting.
| 8.32.2 | Venturi - Add third Thermocouple | 2013-06-01 | 07/18/13 (A) | LGE in agreement per P. Rabe 7/26/2013. See Doosan Reply dated 7/18 summarizing traverse data and recommendation to change the temp diff alarm to 60F.
| 8.32.3 | Venturi - Revise flow vs DP |  | 12/5/2012 (A) | Issued 12/5
| 8.32.4 | SA Flow - Revise flow vs DP, rerange xmtrs |  |  | Restart on existing xmtrs ranging
LGE Action | 8.32.4.1 | SA Flow - Evaluate alternate HP port - Rerange xmtrs if pursue |  | 2013-02-15 | Doosan to evaluate traverse test results. DPS issued comparative data and summary 2/14. All have agreed to remove the existing tubing and plug ports
| 8.32.5 | Pyrite Removal - Revise logic for semi dry clearout |  | on-going | Implemented after scraper pins replaced. Logic Worked Successfully on D mill, updates required for fault handling
| 8.32.5.1 | Update Semi Dry Logic to address Fault Clearing, apply to remaining Mills |  | A, B, E to go, f/c/ = ??? | Semi - Dry Logic implemented on all mills.
| 8.32.5.2 | Update Ops procedure for semi dry clearout |  | 3/12/13 (A) | D. Groom issued 3/12(A)
| 8.32.6 | Pyrite Removal - Revise logic for wet clearout |  | 12/5/2012 (A) | Issued 12/5
| 8.32.7 | Mill Shutdown - Finalize CAD 70 vs 50% | 2012-12-03 | 2013-02-01 | Finalized at 50%. Working acceptably per R. Gratton
| 8.32.9 | Logic Priority List |  | 12/14/2012 (A) | To be completed before return to service and which could follow. This will include the logic change for the 10% Burner Overfire Alarm. This was requested by Phil Rabe to assist in eliminating/reducing nuisance alarms.
| 8.33 | O2 Trim Limits - Limited by 0.88 Stoich |  | 13-Aug-13 (A) | LGE has chosen to keep as-is due to CO concerns. Currently at 0.89, Doosan recommends to lower to 0.87 via S. Hammond email of 8/13. Move to watch item
| 8.34 | Classifier rejects to Manual during "some" start sequences |  | 07-Aug-13(A) | See R. Gratton recommendation of 8/7 to change BTSC to 68 rpm.
| 8.35 | Instability when Mill seal air limits hit (LGE requests raising ACET to 200F) |  | 15-Oct-13 (A) | See C. Dukes 9/26 email, ACET changed to 203 F, switch and tuning parameters changed. Doosan recommends changing back to 195 F ACET post spring outage.
LGE/Doosan Commissiong Action | 8.36 | OFA FRont to Rear Bias Logic |  | Additional bias being reviewed on site. | Move to watch item per 8/21/13 meeting. M. Slaugter suggested additional bias may be needed with C mill IS, F mill OOS. R. Boone tuning. LGE agrees to implement per P. Rabe 7/31. C Row OOS = 5%, F Row OOS = 2.5%
|  | Feedwater Bias Tracking |  | 2012-11-12 | See S. Montgomery 11/12
|  | S/Heater Drain Valve Logic - Correct Pulse |  | 2012-11-26 | Approved by Doosan 11/26
| 10 | Straight line Plot (sq ft (DP x Density) vs. Flow) | 2012-05-20 | 2012-06-23 | MTG held 6/20, Straight line plots provided in mtg handout
| 10 | Doosan to provide ops training after issuance of revised control philosophy |  | One shift to complete | Training Material provided 5/15
| 11 | Doosan to issue a detailed startup plan. The plan is to include logic checks. |  | 11/21/12 (A) | Schedule and procedures are in progress
| 12 | Doosan to provide proposal for redundancy for ID Fan Stall warning |  | Complete | Stall warning has no redundancy but revised system for stall protection has same redundancy as existing system i.e. production is from 2 out of 3 probes/transmitters
| 12 | Calibrate & Test SA Flows (COLD) | 2012-05-20 | 2012-05-24 | Completed
| 13 | Calibrate & Test SA Flows (HOT) | 2012-06-09 | 2012-06-16 | Testing Complete
| 14 | Aerofoil inspections D/G/E (Pressure) | 2012-06-05 |  | Complete
| 15 | The Hydrojet Water Pumps common discharge pipe hangers |  | 2012-06-12 | Complete/Bechtel
| 15.1 | #4 Hydrojet cool/seal air low overheated |  | Warranty | Filters cleaned 6/12/12 , alarms out, move to Warranty SCR inlet duct
| 16 | Lube Oil Cooler |  |  | Complete
| 17 | D Recycle Exp Joints |  |  | Complete
| 19 | Monitor SSC thermal growth design mod. | 2012-06-15 |  | Done no issues f/c 6/01/12
| 20 | AH sootblower with air set up. Need min./max trim. | f/c = ??? | Watch | No issues reported on 9/30 Restart (following economizer tube leak outage)
| 21 | Expansion for econ vent | 2012-11-25 | Outage | Moved to Warranty
| 22 | New AIG DP Gages |  | 2012-07-10 | Working - 10 manifold on site 7/6/2012 , need additional 8 manifolds - 2 - 5 week delivery.
| 23 | Spark Rod parts LGE to light Ing., and trouble shoot other issues with light off | 2012-06-01 | 2012-07-10 | Need final drawing - S. Hammond to issue drawing on Friday 7/6/12
| 23 | Spark Rods/Scanners/Ignitors |  | Watch | 22-Jun-13 Mill A Start - A5 oil @ 9%
| 24 | Mill PA Traverse Test "D" Mill | 2012-06-09 |  | closed
| 25 | Test Mill Cool functions | 2012-06-16 | No longer being pursued as remedy for core air tube overheating | Data provided to Crawley. Mill temps above 200 F. Increase Tempering Air Flow. F Mill HAD Seals require replacement. Test again once damper/drive setup complete. Doosan to update written instructions once finalized. Not in service at this time.
| 25.1 | 30 minute timer |  | 2012-07-11 | Logic mod provided 6/26 - Under Review by LGE. Mitch to review.
| 26 | Air Heater Sootblower pressures - resize cold end orifice |  |  | closed?
| 27 | Verify Sootblowing at 1300psi |  |  | Doosan verified 300deg F of superheat
| 30 | FD fan balance on Air Flow |  |  | Acceptable
| 31 | WESP Wash Water |  | 2012-06-13 | logic does not permit auto operation until 650 MW's. SESS reply sent 6/13
| 33 | Issue Daily Plan of Activities w/look a head |  | 6/20/12 | Doosan is issuing Daily Plan
| 34.1 | AIR HEATER SOOTBLOWING STEAM QUALITY |  |  | Change to 300 F superheat. Doosan to verify installation dates
| 34.1.1 | Issue Tie-in Design for November Outage |  | 10/23 (A) | SMR - 107
| 34.1.2 | Material orders placed |  | 2013-03-15 | on-going as engineering is completed
| 34.1.3 | Engineering for review
| 34.1.3.1 | P&ID |  | f/c = ??? | Revised P&ID's issued for comment on 04/15/13. LGE and Bechtel comments provided 4/18, Docs returned 5/10 and 5/13
| 34.1.3.2 | Valve Spec |  | PCV - purchased PSV - T&c's to be finalized | PCV- 1/18(A). DPS requires PCV feedback to size PSV.
| 34.1.3.3 | Piping Drawings |  | 11-Jun-13 (A) | Relief Valve Vent Stacks submmitted 6/11. To be reviewed and commented on.
| 34.1.4 | Delivery of all components |  | f/c = 02-Oct-13 f/c = 13-Nov-13 | Latest on site date for bulk of materials Latest on site date for trimmer steel and supports
|  | Safety Valve |  | f/c = 02-Oct-13 | PO placed - Dresser
|  | Control Valve |  | f/c = 30-Sep-13 | PO placed - CCI
|  | HP Isolation Valves |  | f/c = 05-Sep-13 | PO placed - Briggs Valcon/VTI
|  | LP Isolation Valves |  | f/c = 07-Sep-13 f/c = 27-Sep-13 | PO placed - Wm Powell PO placed - Pentair (Tyco)
|  | Poppet Valves |  | f/c = 23-Sep-13 | PO placed - Alstom
|  | Piping |  | f/c 03-Oct-13 | PO placed - APP (To be Site run by Mech subcon'r)
|  | Hangers/Support Steel |  |  | RFQ to be issued on completion of design
|  | Instrumentation - Pressure Gauges |  | f/c = 05-Sep-13 | PO placed - Ashcroft
|  | Instrumentation - Pressure Transmitters |  | 20-Aug-13 (A) | Delivered - Rosemount
|  | Instrumentation - Flow measurement |  | f/c PO = 06 Sept | Quote rec'd and under evaluation
|  | Instrumentation - Thermocouples |  | f/c PO = 30-Aug-13 | LGE agreed to allow strap-ons to be used
|  | Electrical Design Documents |  | After final docs | Electrical ECN by Bechtel, f/c = following design docs
|  | Cable |  |  | Bechtel provided BOM 14-Aug-13
|  | Logic |  |  | Doosan and DPII logic
| 34.2 | Send Air Heater Baskets for Analysis |  | 11/2/2012 Alstom report received | See G. Davidson e-mail 10/28. Alstom f/c 6 weeks to complete analysis. Alstom Test Procedure provided S. Hammond 8/24
| 35 | 300kpph OFA Need modified test plan | 2012-06-14 | 2012-06-22 | Doosan able to complete the traverse
| 36 | Mill Curve Load increase (at +10%) | 2012-06-14 | 2012-08-14 | Place holder till finalized
| 37 | Windbox flows exceed 300kpph |  | during outage | Re-range all to 350kpph. (Completed during mini-outage, 9/13) 415AA shows bad quality
| 38.1 | Mill fineness | 2013-06-05 | 29-Jul-13 (A) | Doosan recommends keeping all mills at 76 rpm per R. Gratton 8/15/2013.
| 38.2 | Mill Air Flow Testing |  | TBD | Doosan arranging for FERCO to test - Covered under item 59.1.1
| 39 | "A" windbox retest at 55kph with oil guns in service |  | 2012-06-16 | complete testing 78 RPM
| 40 | SESS Pac/Lime Injection |  | 2012-06-19 | Tues 1pm schedule call
| 41 | Need max flow limits in ammonia |  |  | Doosan provided updated limits of 600kpph
| 42 | Core Air T/C temp data |  | Full load | Need Decision on Core Air Tube Cooling. Distributed data 7/5 and 6/20 - results ok. Relook at Full Load
| 44 | Burner T/C alarms |  | 2012-06-26 | Revised Alarm Sheet issued 6/25
| 44.1 | Update DCS for revised Alarm limits | 2012-06-25 |  | Rick Boone to update in DCS.
| 45 | Evaluate Condenser back pressure |  | 2012-06-25 | LGE working, will be complete 6/26
| 45.1 | Seal Leakoff Issue - Seal Leakoff Pressure running high, Control Valve wide open |  |  | Perf Test Results Distributed, investigation of leakoff source underway
| 46 | Multiple Burner T/C Failures - OEM to replace |  | 2012-09-08 | All pulled and replaced. Send batch back to OEM for replacements.
| 46.1 | IF run out of spares, recommend placement strategy |  |  | Secondary Air 1st?, PF upper next, PF lower?
| 47 | Cross Over Duct Pressure - Evaluate why Air Heater Outlet lower than main duct |  | ??? | Doosan Considers not to be an issue
| 48 | Burner Purge Procedure - Advise if Oil is to be started |  | 2012-06-22 | Doosan Recommends Against the use of oil
| 49 | Furnace Camera arr June 27th |  |  | Demo by OEM on 6/27
| 50 | HP Steam Temp Excursion during PF Purge - Address if logic mod req'd to address the added, unmeasured fuel |  |  | Meeting held 6/25 -
| 50.1 | Mill/PF Pipe Purge - Direct to Furnace |  | 2012-08-15 | Identify Criteria for when this can be done
| 50.2 | Review MS Spray Water logic | Set up Mtg | 2012-08-15 | Bechtel and Doosan to review
| 50.3 | MS Spray Water Source - Verify sufficient pressure available | AM 10:00 | 2012-08-15 | review events of June 1st
| 50.4 | Feedwater Bias - Clarify use/criteria |  | 2012-08-15 | reset to zero during Emerson upgrade, now at 200 kpph
| 50.5 | Boiler Max Permissible Temp |  | 9/13/2012 (A) | See S. Hammond E-mail of 9/13 with recommended inspection locations.
| 50.6 | Max Main Steam Pipe Temp |  | 2012-08-15 | identify max temp
| 51 | SCR Outlet NOx - Monitor Ammonia in ash |  | Watch | 0.035 lbs/MMBtu recommended low limit, up to 16 ppm thus far 7/11
| 51 | Provide Operations Guidance on NOx Control |  | 2012-06-25 | Interim Guidance Issued 6/25
| 52 | Remove Mill PA Flow bias based on bowl dP |  | 2012-06-22 | Mill B bias removed. All other mill are removed. Doosan to watch
| 53 | Daily Slag Condition |  | Operations to confirm tool working | Modified rod out tool Completed. Per Doosan, working acceptably. (7) Rod out pipes on A3,A5,B1,B3,C3,C4,D4 bent by Doosan observation. LGE has identified Qty = 40.
| 53.1 | Modify/Replace Rod-Out Tubes - 14 burners |  |  | Addt'l material not available. Original qty will be modified
| 54 | Don Parker Recommendations. |  | 2012-07-20 | LGE to review - No further comments.
| 54.1.1 | Stroke B Dampers |  |  | B mill HAD hung up at 50 - 70% B mill Cold Air Damper - Stroked fine
| 54.1.2 | Check plug/bolt on Banjo for Mat'l
| 54.1.3 | Clean out Bowl DP tapping points |  | 2012-08-02
| 55 | Burner Optimization - Send out Test Plan |  | 2012-07-06 | No LGE comments Comments to Doosan 6/28
| 56 | Identify Burner Inspection Criteria | 2012-06-25 | Inspection outage | Inspection plan sent 6/26 (A3, D3, F1, B2) and rod out tubes
| 56.1 | Pull Together Burner Spare Parts Inventory |  | 2012-07-09 | Doosan Spare inventory list sent 6/29 No Prefabrication needed prior to inspection (Qty = 2),
| 57 | Identify list of work for mini-outage |  |  | See attached list - Outage Mtg planned for Monday, July 9th
| 58 | Air Htr Sootblowers - Correct Logic for Drain Valves on Steam |  | 2012-08-11 | -On LGE's outage list - N. Payne to address, correct logic. - Drains have been open via logic since December w/no header orifice. - Operation closing valve manually at moment. New thermowells f/c=8/3
| 59 | All Mills Pressure Differential Swings. Tuning on b/c mill. |  | 8/22/2012DBEL/Loetsche/Alstom Reply | Alstom to address spring tension, roll to table clearances, 70/30 blend, wing tips A,B,C PA flow=+10% (as of 7/20) D,E,F PA flow=+10% third party report
| 59.1 | Joint Doosan, Alstom, Loesche call |  | 2012-08-16 | Send out Action Items, call held 8/16
| 59.1.1 | FERCO to perform side by side air flow tests on C mill, prior to outage | 2012-08-23 | 2012-08-26 | FERCO Testing Complete - Pending Analysis and Traverse Data
| 59.1.1.1 | Analysis of FERCO Mill traverse Data |  | f/c = ??? | Other Mill traverse data to be distributed. 200 F imbalance on Mill C at high load. Doosan to recommend remedy.
| 59.1.2 | Phoenix to review FE application |  | 2012-09-09 | Phoenix Replies provided, reviewed Bechtel/LGE/Doosan 9/10
| 59.1.2.1.1 | Evaluate New Static Tapping Ports |  | On-Hold | On hold, restart with existing static ports
| 59.1.2.1.2 | Evaluate Performance of Element |  |  | FERCO on site 10/2 to retest
| 59.1.2.2 | Long Term Fixes (Venturi)
| 59.1.2.2.1 | Evaluate FT above Tapping Point |  |  | To be located above tapping point
| 59.1.2.2.2 | Evaluate Purge Pressure/Hookup |  |  | I. Torkington provided recommendation 11/19; LGE requested 3 way valve
| 59.1.2.2.3 | Replace Copper Impulse Lines |  |  | Applies to New Static Ports
| 59.1.2.2.4 | Replace or Repair Honeycomb/Element
| 59.1.2.2.5 | Replace FT's/Environmentally controlled box |  |  | CES Model 467 vs Emerson 3051
| 59.1.2.2.6 | Replace CS Impulse Lines? |  |  | Pending final location and response to 9/18 e-mail questions.
| 59.1.2.2.7 | Seal Air Pipe Mod |  |  | To allow access to dynamic rodding port
| 59.1.2.2.8 | Evaluate Pyrite Removal System |  |  | Test 9/13
| 59.1.2.2.9 | Alstom Reduce Water Flows? |  | 11/13/12 (A)
| 59.1.3 | Testing Recommendation on Purge Air System |  | 10/23 OEM on site. 10/12 CAM Unit delivery - Install on Mill C | 1. Solenoid to isolate pilot line added to all mills 2. Doosan purchased bubble tight solenoids, added to mills 3. Doosan to order complete Phoenix Purge System, del = 10/12?? 4. Finalize any temporary tubing
| 59.1.3.1 | Verify effectiveness of CAM unit, Mill C |  |  | Establish Data Collection
| 59.1.4 | Test with Purge Air Jumpered out |  |  | F mill tested - No impact, E-mill tested - No impact??
| 59.1.4 | Engage EMF Expert |  | Working | Reported no noise found on B/D/F FE FT's and T/C's. Pending verification during mill swing
| 59.1.5 | Pressure Test at Element |  | 2012-09-15 | Purge pressure increased to 90 psig out of regulator. Pressure at element 30 - 50 psig. To verify adequate purge pressure Prior to Outage (Plugged) Static = 55 psig, Dynamic = 30 psig
| 59.1.5 | Verify FT Cable Grounding/Shielding |  | Working | Place High Speed Recorder on B mill FT and VFD
| 59.1.6 | Trial Transmitter at Element |  |  | Temp S probes were responsive, confirms tubing length not an issue
| 59.1.6.01 | Test Logic - Operator Defined Mill Inlet Temp |  | 2012-08-23 | Per Doosan - No longer recommended. Limited to 350 - 450 F, keep as engineering function, test logic only
| 59.1.6.1.01 | Mill Blockage Logic - Option 2 |  |  | Doosan recommends option 1
| 59.1.6.2 | Purge Air Logic Changes | 2012-09-05 | Watch | Purge during mill inert/clearout, Implemented
| 59.1.6.3 | Purge One leg at a time? |  | If req'd
| 59.1.6.4 | Manual Purge of FE (For those mills that have purge isolated) |  |  | Auto purge in place for all mills. All Mills have modified solenoid arrangement, except F (pending materials)
| 59.1.7 | Internal Mill Inspection |  | During Outage | LGE inspected during mini-outage. No reported findings.
| 60 | T/C's at Burners - Shield/lift off hot surfaces |  | 2012-07-02
| 61 | WCAH Pressure Drop - Doosan to recommend remedy |  | f/c = ??? | No change required if x-over press</=6 in wc, single row at 1.5 inwc (26-Jul-13, BMCR)
| 62.1 | Open reheat biasing dampers |  | 2012-08-21 | After some run time on new transformer. Doosan provided min damper positions 8/21
| 62.11 | Send Stall Sensing Line liquid for Analysis |  | f/c = ??? | Sample collected 8/7
| 62.2 | Air Heater DP |  | 2012-07-16 | Doosan Expediting Alstom
| 62.5 | Upper 2 mills - higher OFA demand |  | 2012-07-26 | Doosan Engineering to evaluate
| 62.6 | Sootblowing Regime - Optimize/Evaluate |  |  | Doosan provided recommendations 7/17 Bechtel sent comments 7/24 (requested clearer criteria for "aggressive water cannon use" and identified multiple wall zones as issues
| 62.6.1 | Sootblower Effectiveness Meeting |  | Use of Boiler T/C's - Mike Smith to address | See S. Hammond reply 11/23
| 62.6.1 | Water Canon System Repairs Completed |  |  | Move to Outage item. Repairs by LGE during Sept 8 outage. Need to advise Doosan when completed. (Zone 12 heat flux reading bad, 2A hydrojet check valve found leaking causing low water flow
| 62.6.2 | Monitor New Sootblower Sequences - 1, 2 , 5; Verify effectiveness of 10/12 recommendations |  | 10/12/2012 (A) | Updated Recommendations provided 10/12 via R. Gratton e-mail.
| 62.6.2.2 | Update logic to implement 10/12 sootblowing recommendations |  | 12/4/2012 (A) 12/8 (A) | Add Alarms as to when to implement "enhanced mode"; Issued 12/4, revision 12/8
| 62.6.3 | Change graphics on water cannon screens |  |  | LGE action
| 62.6.3 | Advise Criteria for Aggressive mode cleaning |  | 10/12 (A) | Updated Sootblowing Recommendations provided 10/12
| 62.6.4 | Joint Doosan/LGE/Bechtel Sootblower meeting |  | Jan 4th (10:00 AM) Meeting with DP - LGE to advise by 1/16 on water lances | See Actions below. duplicate of 77.2 Supporting data to be issued by DPS 2/12/13. Meeting scheduled for 2/22/13. - Same as # 77.2.
| 62.7 | Stall Meeting to review calcs/operation |  | 2012-07-26 | After 7:30 mtg
| 62.7 | Hydrojet Drain line hangers |  | f/c = Run system during outage | Doosan reported hangers are funciotning properly.
| 62.7.1 | Piping |  | 12/5/2012 (A) | Issued Recommendation on 12/5 - Multiple pressure gauges added to determine location of excess DP.
| 62.7.2 | Valve Friction |  | 12/5/2012 (A) | Issued Recommendation on 12/5
| 62.7.3 | Analysis |  | 12/5/2012 (A) | Issued Recommendation on 12/5
| 62.7.5 | Recommendations on Hydrojet Supply Pump |  | f/c = 1 week after running system | Pending pressure drop analysis above - Doosan confirms issues are with the check valve, pump is acceptable.
WN-0346 | 62.7.6 | Hyrdrojet Mounting Bolt Heat Damage |  | f/c = ??? | See G. Davis response 6/18. Diamond considers center plate acceptable, offers to trial an upgrade to inconnel. Being addrssed by Warranty groups
| 62.7.6 | Diamond Power Site Visit Report |  | 3/26/13(A) | Diamond Rep made minor mod's to program, reset numerous heat flux setponits. Full report issued 3/26/2013 by S. Hammond
LGE Action | 62.9 | Review ID Fan C factor |  | 16-Aug-13 (A) | LGE/Bechtel in agreement per 8/21/13 AI mtg. Doosan recommends to maintain existing C factor per S. Hammond 8/16. Increased C factor to Howden design number 68,316 (10/26). Implemented C from 57,310 to 64,044 7/26; Need O2 measurements local to ID fan to check, G. Jones to obtain readings after restart
Bechtel | 64 | Baghouse outlet vs ID fan inlet pressure readings |  | Complete | Modify sensing line routing to add slope, meeting with SESS 10/12
LGE Action | 64.1 | Update Logic for ID fan suction pressure |  | f/c = ??? | Update ID fan setpoints. LGE elects not to change per 3/29 P. Rabe. Bechtel provided recommendation 2/20/2013
| 65 | Verify if 100% Riverview is to be tested prior to outage |  | 2012-07-31 | Identify test dates
| 66 | Establish Hold points prior to outage for flame/burner observations |  | 2012-09-14 | Post Outage Testing planned 9/14
| 66.1 | Issue to go Test Plan |  | 9/26/2012 Updated | Final Version issued by R. Gratton 9/26. Identify any load reductions for deslagging - Per R. Gratton 9/24, 3 mills/half load once per week.
| 67 | Banjo - RCA |  | 2012-12-01 | Banjo RCA Dave Anderson
| 67.1 | Doosan to trial ceramic rope in Gap Areas on Burners (qty = 15) |  | during outage | Sketch Provided, to be applied to 15 burners
| 67.2 | Document Burner As left Condition |  | 9/17/2012(A) | Photos and Defects on each burner provided to LGE
| 68 | RCA for coal in coal pipe |  | f/c = ??
| 69 | Pyrite Test on TC1 mill, burning Riverview |  | 10/5 (A) | To verify amount of pyrite/spillage on the TC1 mill setup.
| 67.1.1 | Review Prior B and A mill coal pipe testing |  | 2012-08-17 | D. Hough provided summary - Recommends no further testing is required
| 67.1.2 | Move Burner Register Settings |  | Prelim 8/28 Final - 10/1/2012 | Finalized after outage, All burners moved8/29 to S/A = 100% T/A = 60% Mill K factors changed 8/29
| 67.1.3 | Review Coal Samples |  | 2012-08-01 | Sample Analysis shows nothing abnormal
| 67.1.4 | Clear out B PA Flow Element |  | 2012-08-01 | Completed 8/1
| 67.1.5 | Review FE full scale DP = 0.6 inwc |  | 2012-08-20 | Duplicate, see 59.1.2TC1 = 3 inwc +/- in operation for venturies, others have similar DP
| 67.1.6 | Review Transmitter location - above/below tapping points |  | 2012-08-20 | Duplicate - See 59.1.2TC1 = Below
| 70 | Verify B/C mill tuning parameter changes |  | 2012-09-01 | All Mills returned to original tuning parameters. Mill B only tuning parameters returned to original settings. C to be returned after outage, Doosan to Bring Emerson back on site after outage to finalize tuning, logic changes., Detuned only HAD, not the cold
| 70.1 | Inspect B coal Mill |  | 2012-08-01 | 7/31 - Approx. 2 feet of coal in PA inlet 8/2 - No coal at inlet
| 71.3 | Questions being sent to Alstom |  | f/c = ?? | Post Steam Inert, then Dry PF discharge to pyrites followed by Water injection
Bechtel | 71.4 | Issue Test Results on Mill Swirl Water Test |  | 2012-11-28 | Test okay, no spillover of water back into inlet Duct. J. Babcock to issue.
| 71.4.1 | Review 40 kpph PA flow when OOS |  |  | A= Low, <10 kpph B= 40 kpph C = 7 to 20 kpph F = <1 kpph
| 71.4.2 | Perform "Aggressive" S/A purge |  | 2012-08-01 | Close T/A's - 60%, S/A = 100% 8/2 - Close T/A to 25% on problem burner
| 72 | Aggressive S/A Purge Procedure |  | 9/20/2012 (A) | Table Issued 8/3 - To be incorporated into Burner purge procedure
| 72.1 | Purge Any OOS mill every 3 days |  | 8/29?? | Update Procedure
| 72.1.1 | Increase Mill B load line to +15% |  | 2012-08-01 | Returned to +10%
| 72.1.2 | B-2 Oil Gun Inspection |  | 2012-08-01 | Rental unit doesn't have temp capability. Doosan cameras to arrive 8/10
| 72.1.3 | Single Pipe Purge - Measure ea coal pipe flow |  | 2012-07-31 | 114 - 117 kpph reported, no pluggage
| 72.1.4 | Determine Furnace Camera Status |  | on-going | Insufficient Cooling, won't work.
| 73 | Mill Logic - Proportional Control vs HAD controls flow, Cold Air Damper controls temp |  | Hold - Watch item | Evaluate on Restart - Suggestions sent to Doosan 8/8
| 74 | Mill - Contact Alstom to open up Pyrite Removal Opening |  | f/c = ??? | Per Doosan - This is the largest size opening offered by Alstom and consistent with another recent Alstom job. Mill B Tripped 9/19 - Under evaluation Clarification questions asked 8/17, replies sent 8/22 LGE review - 9 of last 11 had high alarms Final Mill trips (mill D and E 9/7) prior to mini outage - No high alarm
| 75 | Pyrite Rejects - Evaluate Spillage |  | 10/18 (A) | Alstom recommends after air flow/burner issues resolved. Quote Rec'd to trim wing tips, if needed. Riverview run on TC1, rejects were approx. half of other fuel, but still 6 times higher on TC1 vs TC2
| 75.1 | Wing Tip - Procedure for Adjusting |  | 14-Nov-12 (A) | See T. Smth (Alstom e-mail of 14-Nov-12)
| 75.11 | Steam Inerting Valve - Leakage |  | TBD | LGE rebuilt Valves for 2C and 2E coal mills (found with steam cuts) Steam traps on 2D and 2F inspected - found to be working properly
| 75.12 | Mill - Water Slugs - Investigate Cause |  | 7/19(A) | No slope or drainage issues found. S. H. issued Doosan summary 7/19/13. D. Brann issued summary of Bechtel pipe (5/22) and Doosan to writeup findings
| 75.12 | LGE Recommends adding low point drain |  | TBD | WN-0452 issued, need feed back from # 75.11 to understand whether there is a need or not.
| 75.13 | Investigate Upstream of Doosan Steam inerting Scope the Piping/Steam Supply |  |  | Walked down, no findings. Doosan reported 2/25 seeing water after initially dry steam while testing the semi dry logic
| 75.1.1 | Verify any leaks into Mill |  | 2012-08-03 | Operations - checked fire water, swirl water, steam inerting - No significant leaks found
| 75.2 | Revise control logic to dry clear-out of PF followed by water injection |  |  | Revised Philosophy provided 11/13. Comments sent 11/15
Bechtel | 75.3 | Increase pyrites removal system capacity |  | 4/5/13(A) | Clarifications sent to R. Donais 1/30. Alstom response sent 4/5
| 75.4 | Add air deflector at mill inlet |  |  | Adding Air Dam instead
| 75.5 | Add rod out connections at pyrites hopper outlet (Alstom to confirm) |  |  | Doosan Reply: Recommending no need for change to current system
| 75.6 | Change pyrites hopper overflow to loop seal |  | 4/5/3013(A) | Pending Doosan Reply; Alstom to quote. Alstom response sent 4/5
| 75.7 | Modify water lances in mill inlet duct (Design) |  | 1/11/13 (A) | Design Confirmed and Agreed Upon
| 75.7.1 | Modify water lances in mill inlet duct |  | f/c = TBC | Mod's completed to improve Operator Access sent 5/23 (D. Groom)
| 75.8 | Modify PA inlet duct drain |  | (A)
| 75.9 | Mill Clear Out Check Sheets |  |  | Move to Watch item. Doosan to complete check sheets
| 76 | Plant Trip during shutdown - evaluate logic | 2012-11-08 | 12/2/2012 (A) and 12/14(A) | Boiler Circ Pump - Review subcooling valve logic; Issued logic on 12/2; Philosophy agreed. Pump Motor protection revised logic issued 12/14 (based on cooling water temps)
| 77 | SCR Catalyst Sample Analysis | 2012-11-17 | 2013-03-28 | Pending results received from Hitachi. Deactivation curve updated and issued 08-Apr-13, catalyst report provided to LGE/Bechtel.
| 77 | Aggressive Mode Cleaning - Criteria for use |  | 12/15/2012(A) | Based on operations judjement to reduce FEGT balanced against thermal fatigue damage over a one month period.
| 77.1 | DPII to proivde analysis of thermal fatigue and cleaning success |  | 1/4/13 (A) | D. Groom to issue mtg notes from 1/4 mtg, send package to LGE for review of recommended water lances
| 77.2 | Send recommendation for Water lances to LGE |  | 2013-02-22 | See S. Hammond 1/29 - Minimal Benefit to FEGT/NOx. References Provided. LGE to review and advise. Meeting held 2/22/13.
| 77.2.1 | Water Lance - Follow Up Actions |  | f/c=??? | Evaluate impacts to SO3 conversions. Evaluate FEGT vs S/Ht and R/Ht spray flows. (See S. Hammond e-mail of 3/14). DPS response sent 04/08/13 - Item closed.
| 78 | BURNER THROATS
| 78 | Heat Flux Sensors Broken - Removal of the heat flux sensor from the boiler tubes on the furnace wall |  | 12/15/2012(A) | 1. Use pattern from similar zone (preferred) or 2. Use Manaul Sequence
| 78.1 | WN-0344 - Burner Tile / Quarl Inspections & any Repairs SMR0115 |  | Outage Inspection Item | comments provided 2/4 by Bechtel. Repairs being made by LGE.
| 80 | Max Burner Heat Input - Allow 10% above BMCR for 10 minutes |  | 12/10(A)/12/20(A) | See. S. Hammond e-mail of 12/10, Implemented 12/20 by C. Dukes
| 81 | PA/SA beck/damper linkage slipping |  | Outage Item | Re-set during Outage. All S/A drives/dampers retorqued and positions reverified
| 82 | PA Venturi - HP Tap not Responding |  | Venturi Testing completed | Revised PA K factors implemented approx. 6/20, Traverse Test Results distributed 6/18 via G. Jones
| 82.1 | Distibute Cold Air Venturi Test Results, Damper Characterization |  |  | Superseeded by Hot Air Flow Traverse Test
| 83.1 | PA-Venturi's (Storm) |  | f/c = ??? | A, E mills modelling completed. Turnign vanes modified at A and E mills. See item 82 above.
| 83.1 | PA - Traverse Tests | 2013-06-01 | Completed | Revised K factors implemented
| 83.3 | PA - Coal Pipe Distribution (Storm) |  | 2013-02-13 | Results distributed. Raw data issued 2/8/13. DPS issued report 2/13/13.
| 83.4 | PA - Issue Venturi Calibration Test Procedure |  | 2013-06-06 | DPS revised and reissued Mill PA test procedure
| 83.5 | PA - Schedule Addt'l coal pipe testing |  | f/c = TBC | Combustion Optimization Results issued 7/24
| 83.6 | SA - Existing Taps (FERCO) |  | 2/26/13(A) | Results to be analyzed/recommendations provided. Raw data issued 2/5/13. DPS issued FERCO report 2/26/13.
| 83.7 | SA - Update Test Procedure |  | 6/16/13 (A) | See G. Jones e-mail of 6/16
| 83.9 | PA - Response Testing of Venturis w/new HP Taps |  | 5/6 - 5-10 | Repeat of 82 - deleted
| 83.9 | SA - Alternate HP Tap |  | 2013-02-15 | Results to be analyzed/recommendations provided. DPS to issue comparative data and summary - same as # 8.32.4.1.
| 84 | WCAH Redesign (Armstrong) |  | 2013-02-21 | See Doosan reply 1/24 to freezing concerns. Meeting held 2/21/13.
| 84.1 | Test WCAH Flow |  | Outage Inspection of C.V. | 2nd WCAH flow control valve found to be plugged, similar to the B valve. Trim was replaced in spring 2013 outage
WN-441 | 84.2 | WCAH Data Sheet. |  | Design Agreed in Principle Issue of current DS 19-Nov-13 (A) | LGE requests final design data sheets. PO placed with Armstrong, f/c delivery 31-Jan-14. GA drawings issued 08-Oct-13 (A).
| 84.2.1 | WCAH P&ID markup |  | 14-Aug-13 (A) | P. Rabe comments sent 23-Aug-13. See Draft P&ID submitted via S. Hammond 14-Aug-13
| 84.2.1.1 | Doosan Response to LGE P&ID comments. |  | 26-Nov-13 (A) | See S. Hammond reply 12-Sep-13. Doosan responded 11/26 via S. Hammond to comments made 06-Nov-13 by P. Rabe re Position of temperature measurement and Isolating valves.
LGE Action | 84.2.2 | WCAH Racking Sketches |  | 19-Aug-13 (A) | See P. Rabe comments 8/26. Joint walkdown held W/O 29-Jul-13 (Bechtel, LGE, Doosan, Youngblood)
| 85 | Nox Outlet Probe Traverse |  | 2013-02-13 | Data to be Distributed. DPS issued test results 2/13. Further Nox distribution testing to be done post SCR modifications.
WN-0325 | 86 | COEN Ignitors - COEN to provide 35 new spark rod tips (Longer at 48 inches) |  | New spark rod tips, 5 Del'd, balance of 30 f/c = ??? | 5 on C Row. Watch on restart for approx. 2 weeks - Verify logic mods and new tips. Agreed 03-Jul-13 to move to watch item, continue with existing oil ignitors until burner mods
LGE Action | 87 | Building Vacuum |  | 2013-06-05 | Reponse Provided 6/5. Close off Inside building damper, see Doosan modified logic, monitor condensate pump performance. LGE to provide building vacuum readings taken during test. 4/16 P - Follow up clarifications requested 4/16
| 88 | OT Conversion - |  | on-going
LGE Action | 89 | RAT (13.8kV)to MAT Transfer - Unit Tripped |  | 2013-02-19 | Found issues in the transfer macro. Bechtel provided reply 2/19
| 90 | Updated Safety Valve Data Sheets |  | See AIL # 103 | Hard copy update completed - DPS to confirm status of CD's . Verify manual updates include new ID fan purge system. Final Manual update, prior to burner replacements to be issued.
LGE Action | 93 | ID Fan - Calibrate Stall Detection System (Stall Probes) |  |  | Doosan will calibrate the "new" stall warning system prior to restart - Completed, Laura to verify with Ricky stall probes have previously been calibrated.
| 94 | AIR HEATER RESTART ACTIONS |  |  | Monitor for dry steam, move Lime Injection Silo
| 94.1 | Monitor FD Fan Air Intake during Unit Operation/Rainfall |  | During Rain | - Modified Rain Hood intake superseeds this action - Close item. 6/13 Observation showed little water ingress. Similar observation 7/2 during heavy rainfall
| 94.2 | Change Air Heater Blow Pressures |  | At Restart | Cold End to 130 psig, Hot End to 160 psig, verify orifice plate size
| 94.3 | Monitor/Verify Dry Steam to Air Heater. |  | 17-Nov-13 (A) | Tell Tales in use thus far. Doosan response issued 17-Nov-13.
LGE Action | 94.4 | Relocate Temporary Lime Silo |  |  | Plan to move to the West end of building
| 94.5 | Verify ACET Logic BTSC changed to 80F |  | f/c = ??? | C. Dukes verified it has been changed to 80 F.
| 94.6 | Alstom Recommendations on Air Heater Air Cleaning |  |  | Alstom requires DRY, Isturment quality air, which is not available 245 psig Hot End- 4380 scfm 190 psig Cold End - 3460 scfm
| 94.6 | Verify min Air Inlet Temp - Alstom |  | f/c=??? | Alstom Response provided by Doosan, ACET is the governing criteria
| 95 | O2 Probes - Extend Wing O2 Probes |  | At Restart | Bring Emerson TA to site to support restart
| 96.2 | Stacks to measure SO3, Acid dew point. | 7/24 | 22-Aug-13 (A) STACs Test Report 08-Oct-13 (A) Updated Report | Stacs report and Doosan summary provided 22-Aug-13 (A) via S. Hammond. Bechtel comments sent 22-Aug-13.
| 96.3 | Hitachi Evaluation of Ash Pluggage and elevated SO3. |  | 17-Nov-13 (A) | Hitachi response provided via S. Hammond 11/17/13.
| 98 | Mill Seal Air Damper Leakage. |  | 09-Nov-13 (A) Comments 20-Nov-13 (A) Responses | Doosan to proceed with Effox damper. Address damper seal attachment - Seal will be both bonded and mechanically attached to the blade, details on drawing, issued 08-Jan-14 (A). Cut sheet issued 09-Jan-14 showing adhesive suitable for at least 450degF
| 99 | Alstom Mill Wing Tip Modification - Verfiy required or not. |  | f/c = 16-Dec-13 (A) | 3 mills tested for 20 mins, 7-8lb of reject, LGE do not see a need to progress wing tip tuning at this time.
| 100 | Burner Purge Procedures - Verify Current Requirements |  | 7/19/13(A) | Doosan recommends to maintain current procedures
| 102 | Catalyst Sample Results (from Spring '13 Outage) (catalyst end of life f/c March 1st, 2015) |  | 22-Aug-13 (A) | See Hitachi report submitted via S. Hammond 14-Aug-13, revised 22-Aug-13. Plan for Meeting on catalyst Selection for Spring 2014 Outage - LG&E to replace one layer with standard height catalyst in Spring 2014 outage. Corrected report issued via S. Hammond e-mail dated 08-Oct-13.
| 104 | ID fan Insulation - Discharge Ring |  | 8/9/2013 (A) | Complete Insulation
| 105 | WCAH Racking Sketches |  |  | Covered under item 84.2.2. J. Lee, Youngblood, LGE, Bechtel to walkdown
| 107 | Optimize Ht flux sensor settings vs Load |  | 19-Aug-13 DPII to visit site | Ref. S. H. e-mail of 7/27/2013. DPII to visit site 8/19 and 8/20. LGE to assign internal "champion"
| 108 | Mini-Outage Work List |  | f/c = 10-Oct-13 | ID fan Purge System Inspection, SCR Inspection, Air Heater Wash Verifcation, Pull F row oil ignitors, A3/D3 burners?, Add coal pipe manometers
AEROFOIL
| 9 | Verification of Aerofoil calibration checks Traverse Data Integrated into k factors Finalize k factors | 2012-05-20 | 2012-07-20 | - K factors and calcs issued 7/23. Implemented 7/24. Verified Acceptable 7/25
| 11 | Summation of all Aerofoil's = Combustion Calc (Verification Step) | 2012-05-20 | 2012-07-20 | Issued 7/23
| 11.1 | Review k Factor Calc | 2012-06-25 | 2012-06-25 | k factor calc reviewed in joint mtg 6/6/26
| 25.1 | Core Air Tips - Doosan to modify 5 of LGE spares (remove venturi, add section of HR-120) |  | 2012-08-08 | 7 total on site as of 8/9. Move to outage item
| 28.1 | Contact Effox for recommendations - Pin shafts (S/A dampers - A both sides, C South side | 2012-06-25 | 2012-09-01 | Set up dampers & Beck Drives during outage. Write Up meeting minutes
| 28.2 | Meeting with Beck |  | 2012-08-17 | Follow Up Reply rec'd 8/15. Partial response rec'd 8/14. Doosan requested additional clarifications from Effox. Doosan confirms torque is adequate and recommend to stay with current stroke times (approx. 20 seconds)
| 32 | NOx at SCR stack reading | 2012-07-02 | Watch | Watch after SCR/Ammonia tuning completed. 8.18 - Move to watch item
| 34 | Air Htr temp balance and Sootblower effectiveness | f/c | 2012-08-13 | Performance Review Rec'ed 8/14
November OUTAGE ITEMS
| 1 | Burners - Replace Thermal Rope |  |  | All 30 Burners
| 2 | Burners - Weld Repairs |  |  | See Doosan List
| 3 | PA FE - Correct Connection behind seal air pipe
| 4 | PA FE - Replace temporary pipe at Transmitters
| 5 | Amstar
| 7 | Inspect supherheat/rht biasing damper E |  |  | Linkage has broken twice
| 8 | Modify Impulse lines for ID fan inlet pressure measurement