## TC1 1- 2014
TC1 - 2014
[11 empty] | January | NDC | Period Hours | Available Hours | FOH | EFDH | EFOH | MOH | EMDH | EMOH | Act SH | Fcst SH | MW*Fcst SH | MW*EFOH | MW*Fcst SH | MW*EMOH | MW*Fcst SH | MW*F&MOH | FOR | EFOR | MOR | EUOR | RH | AH | EPDH | MW*PH | MW*(AH-DH) | EAF | MW*(EFOH+EMOH+EPDH) | MW*PH | UU
|  |  |  | 547 | MW's | [6 empty] | 383 | 744 | 673.4833 | 70.5167 | 7.2412 | 77.7578 | 0 |  | 0 | 673.4833 | 744 | 284952 | 29781.2491 | 0 | 257944.1167 | 29781.2491 | 284952 | 9.478% | 10.45% | 0% | 10.45% | 0 | 673.4833 | 0 | 284952 | 255170.7509 | 89.55% | 29781.2491 | 284952 | 10.45%
[13 empty] | POH | FOH |  | EFDH |  | EPDH
[12 empty] | PO | 0 | U1 | 70.5167 | D1 | 7.2412 | PD | 0
[14 empty] | U2 | 0 | D2 | 0 | DE | 0
[14 empty] | U3 | 0 | D3 | 0
[14 empty] | SF | 0
Event Data
Month | Event Number | Event Type | Event Description | MW Available | Start Date | Start Time | End Date | End Time | Actual Event Duration (hours) | Equivalent Outage Duration (hours)
January | 1 | NC |  | 0 | 01/02/2014 | 09:00 | 01/02/2014 | 15:00 | 6 | 0
| 2 | NC |  | 0 | 01/03/2014 | 05:00 | 01/03/2014 | 09:40 | 4.6667 | 0
| 3 | D1 |  | 505 | 01/03/2014 | 09:40 | 01/03/2014 | 11:31 | 1.85 | 0.14205
| 4 | D1 |  | 500 | 01/04/2014 | 02:47 | 01/04/2014 | 03:56 | 1.15 | 0.098812
| 5 | D1 |  | 489 | 01/04/2014 | 05:09 | 01/04/2014 | 08:18 | 3.15 | 0.334
| 6 | D1 |  | 490 | 01/07/2014 | 17:25 | 01/07/2014 | 21:08 | 3.7167 | 0.38729
| 7 | D1 |  | 500 | 01/08/2014 | 12:00 | 01/08/2014 | 17:26 | 5.4333 | 0.46685
| 8 | NC |  | 0 | 01/09/2014 | 07:00 | 01/09/2014 | 13:00 | 6 | 0
| 9 | NC |  | 0 | 01/10/2014 | 06:30 | 01/10/2014 | 15:00 | 8.5 | 0
| 10 | D1 |  | 450 | 01/11/2014 | 05:23 | 01/11/2014 | 19:09 | 13.7667 | 2.4413
| 11 | D1 |  | 275 | 01/11/2014 | 19:09 | 01/11/2014 | 21:03 | 1.9 | 0.94479
| 12 | U1 |  | 0 | 01/11/2014 | 21:03 | 01/12/2014 | 07:57 | 10.9 | 10.9
| 13 | D1 |  | 500 | 01/13/2014 | 06:39 | 01/13/2014 | 10:33 | 3.9 | 0.3351
| 14 | D1 |  | 500 | 01/14/2014 | 08:36 | 01/14/2014 | 10:39 | 2.05 | 0.17614
| 15 | U1 |  | 0 | 01/14/2014 | 10:39 | 01/16/2014 | 22:16 | 59.6167 | 59.6167
| 16 | D1 |  | 510 | 01/17/2014 | 15:20 | 01/17/2014 | 16:00 | 0.66667 | 0.045094
| 17 | D1 |  | 380 | 01/17/2014 | 16:00 | 01/17/2014 | 16:45 | 0.75 | 0.22898
| 18 | D1 |  | 250 | 01/17/2014 | 16:45 | 01/17/2014 | 19:40 | 2.9167 | 1.5836
| 19 | D1 |  | 480 | 01/17/2014 | 19:40 | 01/17/2014 | 20:08 | 0.46667 | 0.05716
| 20 | NC |  | 0 | 01/19/2014 | 01:00 | 01/19/2014 | 01:30 | 0.5 | 0
| 21 | NC |  | 0 | 01/21/2014 | 18:00 | 01/21/2014 | 23:59 | 5.9833 | 0
| 22 | NC |  | 0 | 01/29/2014 | 06:00 | 01/29/2014 | 08:00 | 2 | 0
| 23 | NC |  | 0 | 01/29/2014 | 08:00 | 01/29/2014 | 10:00 | 2 | 0
| 24 | NC |  | 0 | 01/29/2014 | 10:00 | 01/29/2014 | 14:37 | 4.6167 | 0
| 25 | NC |  | 0 | 01/31/2014 | 13:00 | 01/31/2014 | 20:00 | 7 | 0

## TC2 - 2011
TC2 - 2011
[13 empty] | 2011 | NDC | Period Hours | Available Hours | FOH | EFDH | EFOH | MOH | EMDH | EMOH | Act SH | Fcst SH | MW*Fcst SH | MW*EFOH | MW*Fcst SH | MW*EMOH | MW*Fcst SH | MW*F&MOH | FOR | EFOR | MOR | EUOR | RH | AH | EPDH | MW*PH | MW*(AH-DH) | EAF | MW*(EFOH+EMOH+EPDH) | MW*PH | UU
|  |  | 809 | Gross Winter |  |  | 760 | Net Winter | [5 empty] | 559.5 | 8760 | 8204.9 | 223.3833 | 141.5819 | 364.9652 | 331.7167 |  | 331.7167 | 8204.9 | 8428.2833 | 4715624.525 | 204198.0226 | 185595.475 | 4776237.025 | 389793.4976 | 4901220 | 2.65% | 4.33% | 3.886% | 7.953% | 0 | 8204.9 | 3.5048 | 4901220 | 4509465.5529 | 92.01% | 391754.4471 | 4901220 | 7.993%
|  |  | 781 | Gross Summer |  |  | 732 | Net Summer
[14 empty] | POH |  | FOH |  | EFDH |  | EPDH |  | MOH
[7 empty] | Winter - October through March | [6 empty] | PO | 0 | U1 | 170.4667 | D1 | 141.5819 | PD | 3.5048 | MO | 331.7167
[7 empty] | Summer - April through September | [6 empty] | PE |  | U2 | 0 | D2 | 0 | DE | 0 | ME | 0
[16 empty] | U3 | 0 | D3 | 0
[16 empty] | SF | 52.9167
Event Number | Event Type | Event Description | MW Available | Failure Mech Code | Cause Code | Amp Code | Start Date | Start Time | End Date | End Time | Actual Event Duration (hours) | Equivalent Outage Duration (hours)
5 | D1 | The "2D" Coal Mill tripped on a scanner fault. The scanners were cleaned; checked and the mill was placed back in service. The unit was returned to full load. | 667 | F460 | 0340 | 46 | 01/30/2011 | 13:03 | 01/30/2011 | 15:15 | 2.2 | 0.38616
24 | D1 | The "2B" Mill had fire fly's in the pyrite section of the mill. The mill was removed from service for inspection. No damage was noted from this issue, we did not place the spare mill in service due to the type of coal in the silo and the problems we were | 660 | FR00 | 0280 | R0 | 02/25/2011 | 09:35 | 02/25/2011 | 13:52 | 4.2833 | 0.7889
28 | D1 | The "F1" burner would not show flame to allow the Operator to change mills for the fuel box test. The unit load was reduced to allow for the mill change and I/E shop was working on the burner to correct the issue. | 780 | F460 | 0385 | 46 | 02/27/2011 | 21:25 | 02/28/2011 | 07:15 | 9.8333 | 0.35249
29 | MO | This outage was to inspect the burners after the first phase of the fuel test for Bechtel. We also allowed Bechtel to repair a number of the punch list items that required an outage. | 0 | F530 | 0390 | T2 | 03/03/2011 | 02:20 | 03/07/2011 | 16:30 | 110.1667 | 110.1667
31 | D1 | The "2C" Coal Mill tripped on a scanner fault. The scanners were cleaned; checked and the mill was placed back in service. The unit was returned to full load. | 660 | F460 | 0340 | 46 | 03/10/2011 | 07:54 | 03/10/2011 | 09:25 | 1.5167 | 0.27934
32 | PD | This was a planned derate to allow the unit to reduce load to a three mill operation so Bechtel could look at the burners on the "2E" Mill after the first attempt at the group 3 test fuel. | 457 | F530 | 0358 | 53 | 03/11/2011 | 00:00 | 03/11/2011 | 04:00 | 4 | 1.7404
40 | MO | This outage was to inspect the burners after the second phase of the fuel test for Bechtel. We also allowed Bechtel to repair some of the punch list items that required an outage. | 0 | F530 | 0390 | 53 | 03/17/2011 | 22:30 | 03/20/2011 | 13:42 | 63.2 | 63.2
47 | U1 | The sootblower control valve failed open and caused a steam leak in the system. The isolation valves were not operational so the unit was removed from service until repairs could be made to the piping; control valve; safety and isolation valves. | 0 | F540 | 0870 | T2 | 03/24/2011 | 08:08 | 03/29/2011 | 14:29 | 126.35 | 126.35
56 | SF | We had to remove the fires from the boiler on TC-2; we had three of the Aux. Air Dampers and two of the Overfire Air Dampers that would not move or position so that we had proper air flow for the boiler. The dampers were checked and adjusted in some cases | 0 | F690 | 1431 | 69 | 05/04/2011 | 03:00 | 05/06/2011 | 07:55 | 52.9167 | 52.9167
124 | D1 | Unit loading had to be reduced due to high NOX Emmisions. Boiler mill configuration was changed to allow for a coal feeder calibration causing the NOX readings to be to high. This could be caused by improper boiler tuning or by undersized equipment suppli | 580 | FE00 | 8820 | E0 | 06/16/2011 | 06:00 | 06/16/2011 | 11:20 | 5.3333 | 1.3726
135 | D1 | The "2B" F/D Fan started ringing in high vibration and flow started to drop off. Operators were looking into the issues with the fan when it tripped on high vibration. The unit started into a runback and was stabilized until the fan could be inspected and | 400 | F850 | 1400 | 85 | 06/30/2011 | 15:20 | 06/30/2011 | 16:00 | 0.66667 | 0.32522
136 | D1 | The "2B" F/D Fan started ringing in high vibration and flow started to drop off. Operators were looking into the issues with the fan when it tripped on high vibration. The unit started into a runback and was stabilized until the fan could be inspected and | 190 | F850 | 1400 | 85 | 06/30/2011 | 16:00 | 07/01/2011 | 00:00 | 8 | 6.0538
136 | D1 | The "2B" F/D Fan started ringing in high vibration and flow started to drop off. Operators were looking into the issues with the fan when it tripped on high vibration. The unit started into a runback and was stabilized until the fan could be inspected and | 190 | F850 | 1400 | 85 | 07/01/2011 | 00:00 | 07/01/2011 | 01:16 | 1.2667 | 0.95851
138 | D1 | The "2B" F/D Fan keeps going into a stall when the unit is at full load. We are looking into this issue, This load limit was after a run back on the fan due to a stall. | 335 | F850 | 1400 | 85 | 07/02/2011 | 00:30 | 07/02/2011 | 10:00 | 9.5 | 5.4251
139 | D1 | The "2B" F/D Fan keeps going into a stall when the unit is at full load. We are loking into this issue, This load limit was after the F/D Fan was returned to service but we are holding the load down to keep the fan from going into a stall and causing a un | 660 | F850 | 1400 | 85 | 07/02/2011 | 10:00 | 07/02/2011 | 11:00 | 1 | 0.15493
140 | D1 | The "2B" F/D Fan keeps going into a stall when the unit is at full load. We are looking into this issue, This load limit was after the F/D Fan was returned to service but we are holding the load down to keep the fan from going into a stall and causing a u | 650 | F850 | 1400 | 85 | 07/02/2011 | 11:00 | 07/08/2011 | 14:20 | 147.3333 | 24.7128
185 | PD | TC2 unit loading was reduced to allow for fuel testing at lower feed rates | 675 | F790 | 1990 | 79 | 07/31/2011 | 01:00 | 07/31/2011 | 07:00 | 6 | 0.81434
192 | PD | TC2 Load was reduced to allow for low feed rate testing on the coal mill with test coal in it. | 675 | F790 | 1990 | 79 | 08/03/2011 | 23:00 | 08/04/2011 | 06:00 | 7 | 0.95006
210 | U1 | 2B Forced Draft Fan tripped causing unit loading to run back. Duct work pressures did not balance causing a MFT | 0 | F820 | 1400 | T1 | 08/15/2011 | 06:29 | 08/16/2011 | 08:42 | 26.2167 | 26.2167
212 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 722 | F040 | 1400 | 83 | 08/17/2011 | 00:00 | 08/17/2011 | 08:16 | 8.2667 | 0.6245
213 | U1 | Unit came off line due to a trip on one of the Unit 2 Forced Draft Fans | 0 | F040 | 1400 | T1 | 08/17/2011 | 08:16 | 08/18/2011 | 02:10 | 17.9 | 17.9
214 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 500 | F040 | 1400 | 83 | 08/18/2011 | 08:29 | 08/18/2011 | 13:15 | 4.7667 | 1.715
215 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 430 | F040 | 1400 | 83 | 08/18/2011 | 13:15 | 08/18/2011 | 18:47 | 5.5333 | 2.4868
217 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 622 | F040 | 1400 | 83 | 08/18/2011 | 20:11 | 08/19/2011 | 04:00 | 7.8167 | 1.5914
219 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 682 | F040 | 1400 | 83 | 08/19/2011 | 13:00 | 08/19/2011 | 20:38 | 7.6333 | 0.96761
220 | D1 | Unit loading was reduced due to plugging issues with the 2D Coal Burners | 635 | F040 | 0410 | 83 | 08/19/2011 | 20:38 | 08/19/2011 | 22:00 | 1.3667 | 0.25548
221 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 682 | F040 | 1400 | 83 | 08/19/2011 | 22:00 | 08/20/2011 | 17:40 | 19.6667 | 2.493
222 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 660 | F040 | 1400 | 83 | 08/20/2011 | 17:40 | 08/20/2011 | 22:48 | 5.1333 | 0.79531
223 | D1 | Unit loading was reduced due to coal burner issues | 630 | F040 | 0410 | 83 | 08/20/2011 | 22:48 | 08/21/2011 | 00:30 | 1.7 | 0.32868
224 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 682 | F040 | 1400 | 83 | 08/21/2011 | 00:30 | 08/21/2011 | 11:51 | 11.35 | 1.4387
225 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 672 | F040 | 1400 | 83 | 08/21/2011 | 11:51 | 08/21/2011 | 13:19 | 1.4667 | 0.20469
226 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 662 | F040 | 1400 | 83 | 08/21/2011 | 13:19 | 08/21/2011 | 23:00 | 9.6833 | 1.4754
227 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 680 | F040 | 1400 | 83 | 08/21/2011 | 23:00 | 08/23/2011 | 13:00 | 38 | 4.9142
228 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 670 | F040 | 1400 | 83 | 08/23/2011 | 13:00 | 08/24/2011 | 00:00 | 11 | 1.5634
229 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 682 | F040 | 1400 | 83 | 08/24/2011 | 00:00 | 08/24/2011 | 10:52 | 10.8667 | 1.3775
230 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 670 | F040 | 1400 | 83 | 08/24/2011 | 10:52 | 08/24/2011 | 11:30 | 0.63333 | 0.090013
231 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 662 | F040 | 1400 | 83 | 08/24/2011 | 11:30 | 08/24/2011 | 14:32 | 3.0333 | 0.46219
232 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 652 | F040 | 1400 | 83 | 08/24/2011 | 14:32 | 08/25/2011 | 00:32 | 10 | 1.6517
233 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 667 | F040 | 1400 | 83 | 08/25/2011 | 00:32 | 08/25/2011 | 11:00 | 10.4667 | 1.5278
235 | D1 | Unit loading had to be reduced due to a burner temperature excursion. | 625 | F040 | 0400 | 83 | 08/25/2011 | 11:00 | 08/25/2011 | 11:56 | 0.93333 | 0.18643
236 | D1 | Unit loading was reduced due to issues Forced Draft Fans. There are problems keeping the fans from a stall condition. | 667 | F040 | 1400 | 83 | 08/25/2011 | 11:56 | 08/27/2011 | 01:37 | 37.6833 | 5.5005
237 | MO | Forced Draft fan blade replacement. | 0 | F590 | 1400 | T2 | 08/27/2011 | 01:37 | 08/29/2011 | 08:00 | 54.3833 | 54.3833
243 | D1 | Unit loading was reduced to stay in compliance with NOX emmision requirements | 645 | FE00 | 9610 | E0 | 09/16/2011 | 11:00 | 09/16/2011 | 13:04 | 2.0667 | 0.35988
244 | D1 | Unit loading was reduced to stay in compliance with NOX emmision requirements. | 655 | FE00 | 9610 | E0 | 09/16/2011 | 13:04 | 09/17/2011 | 00:00 | 10.9333 | 1.7639
0
246 | D1 | Unit loading was reduced due to problems keeping the FD Fans out of a Stall conditions | 767 | F040 | 1400 | 83 | 09/17/2011 | 15:22 | 09/19/2011 | 06:10 | 38.8 | 0.69552
247 | D1 | Unit loading was reduced due to problems keeping the FD Fans out of a Stall conditions | 747 | F040 | 1400 | 83 | 09/19/2011 | 06:10 | 09/26/2011 | 03:10 | 165 | 7.1831
248 | D1 | Unit 2 Loading was reduced due to the inability to maintain NOX emision limits in compliance at full load with Coal Mills currently available. | 712 | FE00 | 9610 | E0 | 09/26/2011 | 03:10 | 09/26/2011 | 16:11 | 13.0167 | 1.15
249 | D1 | TC2 loading was reduced due to the inability to maintain Nox Emmisions with in limits. The unit was also up against a FD fan Stall Curve. | 747 | FE00 | 9610 | E0 | 09/26/2011 | 16:11 | 09/27/2011 | 11:00 | 18.8167 | 0.81916
251 | D1 | Unit loading was reduced due to the inability to maintain Nox emmision within limits. There was also issues with the FD Fans up against a fan stall curve. | 747 | FE00 | 9610 | E0 | 09/27/2011 | 15:00 | 09/30/2011 | 01:18 | 58.3 | 2.538
253 | D1 | TC2 Unit loading was reduced due to problems 2B Coal Mill experencing low PA flow issues and the 2D3 Coal Mill Burner Banjo temperature running to high. | 410 | F830 | 0310 | 83 | 09/30/2011 | 13:15 | 09/30/2011 | 16:00 | 2.75 | 1.3063
254 | D1 | TC2 unit loading was reduced due to issues maintaining Nox Emmisions. The FD fans are also up against a stall curve. | 747 | FE00 | 9610 | E0 | 09/30/2011 | 16:00 | 10/01/2011 | 00:00 | 8 | 0.34827
254 | D1 | TC2 unit loading was reduced due to issues maintaining Nox Emmisions. The FD fans are also up against a stall curve. | 747 | FE00 | 9610 | E0 | 10/01/2011 | 00:00 | 10/05/2011 | 10:00 | 106 | 8.1236
296 | D1 | There were issues with the 2E Coal Mill Primary Air Supply instrumentation. As the I/E shop was troubleshooting the problem the PA flow reference to the control system was lost causing the 2E Coal Mill to shut down. | 670 | F090 | 0338 | 09 | 11/23/2011 | 10:00 | 11/23/2011 | 11:50 | 1.8333 | 0.315
306 | D1 | TC2 unit loading was reduced to allow for a coal mill swap. This was needed to allow for a more control of the boiler between the mills preventing a boiler upset. | 780 | F040 | 0340 | 04 | 12/08/2011 | 12:00 | 12/08/2011 | 16:00 | 4 | 0.14339
312 | D1 | TC2 Unit Loading was reduced due to issues with the 2B Air Heater Differential being to high. This is causing the Boiler Air Flow to swing. | 732 | F040 | 1493 | 04 | 12/09/2011 | 08:15 | 12/09/2011 | 08:30 | 0.25 | 0.023795
313 | D1 | TC2 Unit Loading was reduced due to issues with the 2B Air Heater Differential being to high. This is causing the Boiler Air Flow to swing. | 722 | F040 | 1493 | 04 | 12/09/2011 | 08:30 | 12/09/2011 | 13:45 | 5.25 | 0.56459
314 | D1 | TC2 Unit Loading was reduced due to issues with the 2B Air Heater Differential being to high. This is causing the Boiler Air Flow to swing. | 712 | F040 | 1493 | 04 | 12/09/2011 | 13:45 | 12/10/2011 | 06:00 | 16.25 | 1.9484
315 | D1 | TC2 Unit Loading was reduced due to issues with the 2B Air Heater Differential being to high. This is causing the Boiler Air Flow to swing. | 704 | F040 | 1493 | 04 | 12/10/2011 | 06:00 | 12/10/2011 | 09:15 | 3.25 | 0.42182
316 | D1 | TC2 Unit Loading was reduced due to issues with the 2B Air Heater Differential being to high. This is causing the Boiler Air Flow to swing. | 682 | F040 | 1493 | 04 | 12/10/2011 | 09:15 | 12/10/2011 | 13:00 | 3.75 | 0.58869
317 | D1 | TC2 Unit Loading was reduced due to issues with the 2B Air Heater Differential being to high. This is causing the Boiler Air Flow to swing. | 647 | F040 | 1493 | 04 | 12/10/2011 | 13:00 | 12/10/2011 | 14:00 | 1 | 0.20025
318 | D1 | TC2 Unit Loading was reduced due to issues with the 2B Air Heater Differential being to high. This is causing the Boiler Air Flow to swing. | 597 | F040 | 1493 | 04 | 12/10/2011 | 14:00 | 12/11/2011 | 00:00 | 10 | 2.6205
319 | D1 | TC2 Unit Loading was reduced due to issues with the 2B Air Heater Differential being to high. This is causing the Boiler Air Flow to swing. | 609 | F040 | 1493 | 04 | 12/11/2011 | 00:00 | 12/14/2011 | 07:20 | 79.3333 | 19.6127
320 | D1 | TC2 Unit loading had to be reduced due to plugging in the 2B Air Heater causing the boiler air flows to swing. | 587 | F040 | 1493 | 04 | 12/14/2011 | 07:20 | 12/15/2011 | 09:00 | 25.6667 | 7.0433
321 | D1 | TC2 loading had to be reduced due to plugging in the 2B Air Heater. This is causing the boiler air flow to swing. | 547 | F040 | 1493 | 04 | 12/15/2011 | 09:00 | 12/16/2011 | 04:53 | 19.8833 | 6.4393
322 | MO | TC2 was taken off line to allow for Air Heater Cleaning. This was needed due to plugging in the 2B Air Heater causing the boiler air flows to swing. | 0 | F120 | 1493 | T2 | 12/16/2011 | 04:53 | 12/20/2011 | 12:51 | 103.9667 | 103.9667
326 | D1 | TC2 unit loading had to be reduced due to high NOX readings on the unit. The unit loading was reduced to stay with in our emission limits. | 773 | FE00 | 9610 | E0 | 12/23/2011 | 07:00 | 12/24/2011 | 00:00 | 17 | 0.75649
328 | D1 | TC2 unit loading had to be reduced due to high NOX readings on the unit. The unit loading was reduced to stay with in our emmision limits. | 733 | FE00 | 9610 | E0 | 12/24/2011 | 19:00 | 12/24/2011 | 23:15 | 4.25 | 0.39926
329 | D1 | TC2 unit loading had to be reduced due to high NOX readings on the unit. The unit loading was reduced to stay with in our emmision limits. | 713 | FE00 | 9610 | E0 | 12/24/2011 | 23:15 | 12/25/2011 | 00:00 | 0.75 | 0.088999
331 | D1 | TC2 unit loading had to be reduced due to high NOX readings on the unit. The unit loading was reduced to stay with in our emission limits. | 773 | FE00 | 9610 | E0 | 12/25/2011 | 04:00 | 12/25/2011 | 05:30 | 1.5 | 0.066749
332 | D1 | TC2 unit loading had to be reduced due to high NOX readings on the unit. The unit loading was reduced to stay with in our emission limits. | 753 | FE00 | 9610 | E0 | 12/25/2011 | 05:30 | 12/25/2011 | 12:00 | 6.5 | 0.44994
333 | D1 | TC2 unit loading had to be reduced due to high NOX readings on the unit. The unit loading was reduced to stay with in our emission limits. | 743 | FE00 | 9610 | E0 | 12/25/2011 | 12:00 | 12/25/2011 | 13:30 | 1.5 | 0.12237
334 | D1 | TC2 unit loading had to be reduced due to high NOX readings on the unit. The unit loading was reduced to stay with in our emission limits. | 693 | FE00 | 9610 | E0 | 12/25/2011 | 13:30 | 12/26/2011 | 00:00 | 10.5 | 1.5056
336 | D1 | TC2 unit loading had to be reduced due to high NOX readings on the unit. The unit loading was reduced to stay with in our emission limits. | 753 | FE00 | 9610 | E0 | 12/26/2011 | 07:00 | 12/27/2011 | 05:00 | 22 | 1.5229
338 | D4 | TC2 loading was reduced due to slagging issues in the boiler that needed to be resolved. Unit loading was reduced to deslag the boiler to restore unit loading. | 437 | FS00 | 1100 | S0 | 12/27/2011 | 22:00 | 12/28/2011 | 04:00 | 6 | 2.759

## TC2 - 2012
TC2 - 2012
[13 empty] | 2012 | NDC | Period Hours | Available Hours | FOH | EFDH | EFOH | MOH | EMDH | EMOH | Act SH | Fcst SH | MW*Fcst SH | MW*EFOH | MW*Fcst SH | MW*EMOH | MW*Fcst SH | MW*F&MOH | FOR | EFOR | MOR | EUOR | RH | AH | EPDH | MW*PH | MW*(AH-DH) | EAF | MW*(EFOH+EMOH+EPDH) | MW*PH | UU
|  |  | 809 | Gross Winter |  |  | 760 | Net Winter | [5 empty] | 559.5 | 8784 | 7412.8 | 102.8667 | 229.0502 | 331.9169 | 211.85 |  | 211.85 | 7412.8 | 7515.6667 | 4205015.5 | 185707.5003 | 118530.075 | 4265991.675 | 304237.5753 | 4323545.575 | 1.369% | 4.416% | 2.778% | 7.037% | 0 | 7412.8 | 0 | 4914648 | 4019307.9997 | 81.78% | 304237.5753 | 4914648 | 6.19%
|  |  | 781 | Gross Summer |  |  | 732 | Net Summer
[14 empty] | POH |  | FOH |  | EFDH |  | EPDH |  | MOH
[7 empty] | Winter - October through March | [6 empty] | PO | 1056.4833 | U1 | 0 | D1 | 229.0502 | PD | 0 | MO | 211.85
[7 empty] | Summer - April through September | [6 empty] | PE | 605.7667 | U2 | 102.8667 | D2 | 0 | DE | 0 | ME | 0
[16 empty] | U3 | 0 | D3 | 0
[16 empty] | SF | 0
Event Number | Event Type | Event Description | MW Available | Failure Mech Code | Cause Code | Amp Code | Start Date | Start Time | End Date | End Time | Actual Event Duration (hours) | Equivalent Outage Duration (hours) |  |  | LEAP YEAR
2 | D1 | The NOX limits on the unit was running over the emissions limit so the load was reduced until the unit could be de-slaged later in the day off peak. | 735 | FE00 | 9610 | E0 | 01/06/2012 | 16:00 | 01/06/2012 | 22:00 | 6 | 0.54883
3 | NC | The NOX was running high on the unit so we reduced the load for de-slag. The unit load could have been returned to full load at any time the dispatcher requested. | 0 | FE00 | 9610 | E0 | 01/06/2012 | 22:00 | 01/07/2012 | 06:00 | 8 | 0
5 | U2 | TC-2 was removed from service @ 13:26 hrs. for a S/H tube leak. | 0 | F540 | 1040 | 54 | 01/07/2012 | 13:26 | 01/11/2012 | 20:18 | 102.8667 | 102.8667
10 | NC | The unit was held at different loads to test out NOX removal and SCR operation. The load could have been returned to normal if dispatch requested. | 0 | F790 | 9610 | 79 | 01/13/2012 | 15:00 | 01/14/2012 | 09:00 | 18 | 0
13 | D1 | The fan stall alarm was coming in on the F/D Fans; we changed the dampers on the intake of the fan and cleared the alarm. This allowed us to return to normal operation on the unit. | 775 | F780 | 1420 | 78 | 01/23/2012 | 10:00 | 01/23/2012 | 12:10 | 2.1667 | 0.091059
19 | D1 | The unit was running high on NOX from the high low on the unit early in the day from wide open valve test. The load was returned to normal when we were back with-in our environmental restrictions for the unit. | 758 | FE00 | 8817 | E0 | 02/03/2012 | 18:27 | 02/03/2012 | 19:30 | 1.05 | 0.066193
20 | D1 | The unit was running high on NOX from the high low on the unit early in the day from wide open valve test. The load was returned to normal when we were back with-in our environmental restrictions for the unit. | 733 | FE00 | 8817 | E0 | 02/03/2012 | 19:30 | 02/03/2012 | 23:00 | 3.5 | 0.3288
21 | D1 | The unit was running high on NOX from the high low on the unit early in the day from wide open valve test. The load was returned to normal when we were back with-in our environmental restrictions for the unit. | 708 | FE00 | 8817 | E0 | 02/03/2012 | 23:00 | 02/04/2012 | 00:00 | 1 | 0.12485
35 | D1 | The "2F" Mill needed the gasket on the pyrite hopper replaced from the last mill fire and the "2C" Mill had the "C4" burner getting hot. The unit was limited until the "2F" Mill was returned to service. | 752 | FR00 | 0280 | R0 | 02/16/2012 | 14:00 | 02/19/2012 | 06:31 | 64.5167 | 4.5457
37 | D1 | The F/D Fan had a stall issue and placed the unit into a run-back. This caused the load limit until the stall could be corrected on the fans. The fan dampers were placed in manual and adjusted to correct the issue. | 470 | F040 | 1400 | 04 | 02/20/2012 | 11:00 | 02/20/2012 | 12:29 | 1.4833 | 0.62157
39 | D1 | The NOX was running outside of our limit for the unit and load had to be reduced to stay with-in the environmental restrictions for the unit. | 667 | FE00 | 8823 | E0 | 02/20/2012 | 15:30 | 02/21/2012 | 00:01 | 8.5167 | 1.4949
41 | D1 | The NOX was running outside of our limit for the unit and load had to be reduced to stay with-in the environmental restrictions for the unit. | 702 | FE00 | 8823 | E0 | 02/21/2012 | 17:00 | 02/22/2012 | 00:00 | 7 | 0.92583
42 | NC | The unit load was reduced to de-slag the boiler. The NOX was running high on the unit and a boiler deslag was used to help reduce the NOX outlet of the boiler. | 0 | FS00 | 1305 | S0 | 02/22/2012 | 00:00 | 02/22/2012 | 06:08 | 6.1333 | 0
43 | D1 | The igniters would not light off to allow the "2C" Mill to be placed back in service after the boiler de-slag. | 735 | F460 | 0385 | 46 | 02/22/2012 | 06:08 | 02/22/2012 | 10:00 | 3.8667 | 0.35369
45 | D1 | The NOX was running outside of our limit for the unit and load had to be reduced to stay with-in the environmental restrictions for the unit. | 720 | FE00 | 8823 | E0 | 02/22/2012 | 12:30 | 02/22/2012 | 13:00 | 0.5 | 0.055006
46 | D1 | The NOX was running outside of our limit for the unit and load had to be reduced to stay with-in the environmental restrictions for the unit. | 657 | FE00 | 8823 | E0 | 02/22/2012 | 13:00 | 02/22/2012 | 14:50 | 1.8333 | 0.34446
49 | D1 | The NOX was running outside of our limit for the unit and load had to be reduced to stay with-in the environmental restrictions for the unit. | 747 | FE00 | 8823 | E0 | 02/25/2012 | 11:30 | 02/28/2012 | 12:30 | 73 | 5.5946
51 | D1 | The NOX was running outside of our limit for the unit and load had to be reduced to stay with-in the environmental restrictions for the unit. | 747 | FE00 | 8822 | E0 | 02/28/2012 | 14:00 | 02/29/2012 | 08:05 | 18.0833 | 1.3859
56 | D1 | The unit was running high NOX due to the mills set-up and combustion issues. The unit load was reduced to stay in environmental compliance. | 650 | FE00 | 8823 | E0 | 03/06/2012 | 16:00 | 03/06/2012 | 16:45 | 0.75 | 0.1474
57 | D1 | The unit was running high NOX due to the mills set-up and combustion issues. The unit load was reduced to stay in environmental compliance. | 600 | FE00 | 8823 | E0 | 03/06/2012 | 16:45 | 03/07/2012 | 01:00 | 8.25 | 2.1313
58 | D1 | The unit had combustion issues that required the above load reduction. The "2F" Mill was not available due to slag issues; The Forced Draft fans are nearing fan stall and the "2B" Airheater differential is at the upper limit. | 747 | F040 | 1999 | 04 | 03/07/2012 | 01:00 | 03/08/2012 | 00:01 | 23.0167 | 1.7639
59 | NC | The unit load was reduced to de-slag and clean the boiler. | 0 | FS00 | 1999 | S0 | 03/08/2012 | 00:01 | 03/08/2012 | 06:30 | 6.4833 | 0
60 | D1 | The unit had combustion issues that required the above load reduction. The "2F" Mill was not available due to slag issues; The Forced Draft fans are nearing fan stall and the "2B" Airheater differential is at the upper limit. | 744 | F040 | 1999 | 04 | 03/08/2012 | 06:30 | 03/12/2012 | 01:30 | 91 | 7.3115
61 | D1 | The unit had combustion issues that required the above load reduction. The "2F" Mill was not available due to slag issues; The Force Draft fans are nearing fan stall and the "2B" Airheater differential is at the upper limit. | 736 | F040 | 1999 | 04 | 03/12/2012 | 01:30 | 03/12/2012 | 05:20 | 3.8333 | 0.3459
62 | D1 | The unit had combustion issues that required the above load reduction. The "2F" Mill was not available due to slag issues; The Force Draft fans are nearing fan stall and the "2B" Airheater differential is at the upper limit. | 727 | F040 | 1999 | 04 | 03/12/2012 | 05:20 | 03/12/2012 | 19:30 | 14.1667 | 1.4359
63 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. Orignal Equipment Manufacturer requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 718 | F040 | 1999 | 04 | 03/12/2012 | 19:30 | 03/12/2012 | 21:30 | 2 | 0.22497
65 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. OEM requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 707 | F040 | 1999 | 04 | 03/12/2012 | 21:30 | 03/12/2012 | 23:00 | 1.5 | 0.18912
66 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. OEM requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 697 | F040 | 1999 | 04 | 03/12/2012 | 23:00 | 03/13/2012 | 03:00 | 4 | 0.55377
67 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. OEM requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 727 | F040 | 1999 | 04 | 03/13/2012 | 03:00 | 03/13/2012 | 17:18 | 14.3 | 1.4494
68 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. OEM requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 712 | F040 | 1999 | 04 | 03/13/2012 | 17:18 | 03/14/2012 | 00:00 | 6.7 | 0.80334
69 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. OEM requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 727 | F040 | 1999 | 04 | 03/14/2012 | 00:00 | 03/14/2012 | 22:42 | 22.7 | 2.3009
70 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. OEM requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 702 | F040 | 1999 | 04 | 03/14/2012 | 22:42 | 03/15/2012 | 03:00 | 4.3 | 0.56873
71 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. OEM requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 727 | F040 | 1999 | 04 | 03/15/2012 | 03:00 | 03/15/2012 | 16:14 | 13.2333 | 1.3413
72 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. OEM requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 687 | F040 | 1999 | 04 | 03/15/2012 | 16:14 | 03/16/2012 | 00:00 | 7.7667 | 1.1712
73 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. OEM requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 727 | F040 | 1999 | 04 | 03/16/2012 | 00:00 | 03/16/2012 | 10:12 | 10.2 | 1.0339
76 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. OEM requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 691 | F040 | 1999 | 04 | 03/16/2012 | 12:34 | 03/16/2012 | 13:00 | 0.43333 | 0.063206
77 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. OEM requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 727 | F040 | 1999 | 04 | 03/16/2012 | 13:00 | 03/16/2012 | 14:22 | 1.3667 | 0.13852
78 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. OEM requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 707 | F040 | 1999 | 04 | 03/16/2012 | 14:22 | 03/18/2012 | 17:30 | 51.1333 | 6.447
79 | D1 | The unit air flow was runnig up to the point of a stall on the fan curve. OEM requires us to keep the fans out of a stall condition. Unit loading was reduced to prevent this from happening. | 687 | F040 | 1999 | 04 | 03/18/2012 | 17:30 | 03/19/2012 | 21:20 | 27.8333 | 4.1974
80 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 667 | F040 | 1999 | 04 | 03/19/2012 | 21:20 | 03/19/2012 | 21:37 | 0.28333 | 0.049732
81 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 627 | F040 | 1999 | 04 | 03/19/2012 | 21:37 | 03/19/2012 | 22:45 | 1.1333 | 0.25496
82 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 607 | F040 | 1999 | 04 | 03/19/2012 | 22:45 | 03/20/2012 | 00:00 | 1.25 | 0.31211
83 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 687 | F040 | 1999 | 04 | 03/20/2012 | 00:00 | 03/20/2012 | 17:55 | 17.9167 | 2.7019
84 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 677 | F040 | 1999 | 04 | 03/20/2012 | 17:15 | 03/21/2012 | 00:00 | 6.75 | 1.1014
85 | D1 | The unit load was reduced for boiler de-slag and to help with boiler NOX issues. | 447 | F040 | 1999 | 04 | 03/21/2012 | 00:00 | 03/21/2012 | 05:00 | 5 | 2.2373
86 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 687 | F040 | 1999 | 04 | 03/21/2012 | 05:00 | 03/21/2012 | 07:35 | 2.5833 | 0.38958
87 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 677 | F040 | 1999 | 04 | 03/21/2012 | 07:35 | 03/21/2012 | 08:30 | 0.91667 | 0.14957
88 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 687 | F040 | 1999 | 04 | 03/21/2012 | 08:30 | 03/21/2012 | 19:30 | 11 | 1.6588
89 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 677 | F040 | 1999 | 04 | 03/21/2012 | 19:30 | 03/22/2012 | 09:00 | 13.5 | 2.2027
90 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 687 | F040 | 1999 | 04 | 03/22/2012 | 09:00 | 03/22/2012 | 12:30 | 3.5 | 0.52781
91 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 677 | F040 | 1999 | 04 | 03/22/2012 | 12:30 | 03/22/2012 | 13:40 | 1.1667 | 0.19036
92 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 667 | F040 | 1999 | 04 | 03/22/2012 | 13:40 | 03/23/2012 | 09:00 | 19.3333 | 3.3935
93 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 687 | F040 | 1999 | 04 | 03/23/2012 | 09:00 | 03/23/2012 | 11:00 | 2 | 0.30161
94 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 667 | F040 | 1999 | 04 | 03/23/2012 | 11:00 | 03/23/2012 | 11:05 | 0.083333 | 0.014627
95 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 657 | F040 | 1999 | 04 | 03/23/2012 | 11:05 | 03/23/2012 | 11:45 | 0.66667 | 0.12526
96 | D1 | The unit air flow was running up to the point of a stall on the fan curve. The Air Heater D/P was reaching the OEM limit and NOX on the unit was above the air permit limits. The unit loading was reduced to keep the above issues with-in limits. | 647 | F040 | 1999 | 04 | 03/23/2012 | 11:45 | 03/23/2012 | 23:31 | 11.7667 | 2.3562
97 | PO | This planned outage is to repair combustion issues on the boiler. The OEM is modifying the burners to improve NOX and correct other combustion issues. | 0 | F830 | 1999 | 59 | 03/23/2012 | 23:31 | 04/01/2012 | 00:00 | 192.4833 | 192.4833
97 | PO | This planned outage is to repair combustion issues on the boiler. The OEM is modifying the burners to improve NOX and correct other combustion issues. | 0 | F830 | 1999 | 59 | 04/01/2012 | 00:00 | 05/01/2012 | 00:00 | 720 | 720
97 | PO | This planned outage is to repair combustion issues on the boiler. The OEM is modifying the burners to improve NOX and correct other combustion issues. | 0 | F830 | 1999 | 59 | 05/01/2012 | 00:00 | 05/07/2012 | 00:00 | 144 | 144
98 | PE | This planned outage is to repair combustion issues on the boiler. The OEM is modifying the burners to improve NOX and correct other combustion issues. | 0 | F590 | 1999 | 59 | 05/07/2012 | 00:00 | 06/01/2012 | 00:00 | 600 | 600
98 | PE | This planned outage is to repair combustion issues on the boiler. The OEM is modifying the burners to improve NOX and correct other combustion issues. | 0 | F590 | 1999 | 59 | 06/01/2012 | 00:00 | 06/01/2012 | 05:46 | 5.7667 | 5.7667
100 | D1 | The combustion on the unit was an issues, the unit had low O2 readings and high Co readings that lead to emissions problems and required this load limit for safety and environmental reasons, | 687 | FE00 | 1450 | E0 | 06/02/2012 | 01:45 | 06/02/2012 | 14:51 | 13.1 | 1.5767
101 | D1 | The combustion on the unit was an issues, the unit had low O2 readings and high Co readings that lead to emissions problems and required this load limit for safety and environmental reasons, | 659 | FE00 | 1450 | E0 | 06/02/2012 | 14:51 | 06/03/2012 | 07:27 | 16.6 | 2.5931
103 | D1 | The unit was derated for combustion issues from tuning the new burners on the unit. | 599 | F090 | 0410 | 09 | 06/09/2012 | 13:00 | 06/11/2012 | 05:50 | 40.8333 | 9.5156
105 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 625 | F790 | 0410 | 79 | 06/11/2012 | 19:30 | 06/13/2012 | 13:30 | 42 | 8.3892
106 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 698 | F790 | 0410 | 79 | 06/13/2012 | 13:30 | 06/19/2012 | 09:07 | 139.6167 | 14.8376
108 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 696 | F790 | 0410 | 79 | 06/19/2012 | 11:00 | 06/20/2012 | 13:05 | 26.0833 | 2.8388
110 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 696 | F790 | 0410 | 79 | 06/20/2012 | 14:07 | 06/21/2012 | 06:00 | 15.8833 | 1.7287
111 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 726 | F790 | 0410 | 79 | 06/21/2012 | 06:00 | 06/21/2012 | 06:30 | 0.5 | 0.035211
112 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 0410 | 79 | 06/21/2012 | 06:30 | 06/21/2012 | 15:22 | 8.8667 | 0.35194
119 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 0410 | 79 | 06/22/2012 | 06:05 | 06/28/2012 | 14:40 | 152.5833 | 6.0564
120 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There was also issues with the FD Fans approaching a Stall condition. | 725 | F040 | 1400 | 04 | 06/28/2012 | 14:40 | 06/29/2012 | 02:00 | 11.3333 | 0.81263
121 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 0410 | 79 | 06/29/2012 | 02:00 | 06/29/2012 | 11:35 | 9.5833 | 0.38039
122 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There was also issues with the FD Fans approaching a Stall condition. | 720 | F040 | 1400 | 04 | 06/29/2012 | 11:35 | 06/29/2012 | 15:50 | 4.25 | 0.33195
123 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There was also issues with the FD Fans approaching a Stall condition. | 725 | F040 | 1400 | 04 | 06/29/2012 | 15:50 | 06/30/2012 | 08:50 | 17 | 1.219
124 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 0410 | 79 | 06/30/2012 | 08:50 | 07/01/2012 | 00:00 | 15.1667 | 0.60201
124 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 0410 | 79 | 07/01/2012 | 00:00 | 07/01/2012 | 04:05 | 4.0833 | 0.16208
125 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There were also issues with a Coal Feeder that caused a further reduction in unit loading. | 630 | F040 | 0250 | 04 | 07/01/2012 | 04:05 | 07/01/2012 | 04:40 | 0.58333 | 0.11278
126 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 0410 | 79 | 07/01/2012 | 04:40 | 07/01/2012 | 07:12 | 2.5333 | 0.10055
127 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There was an issure while trying to change Coal Mills on the unit requiring a reduction in unit load | 620 | F040 | 0310 | 04 | 07/01/2012 | 07:12 | 07/01/2012 | 07:45 | 0.55 | 0.11338
128 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 0410 | 79 | 07/01/2012 | 07:45 | 07/02/2012 | 21:45 | 38 | 1.5083
129 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There was also an issue with the ID fans approaching a stall condition. | 740 | F040 | 1455 | 79 | 07/02/2012 | 21:45 | 07/03/2012 | 00:00 | 2.25 | 0.11812
130 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 0410 | 79 | 07/03/2012 | 00:00 | 07/04/2012 | 19:45 | 43.75 | 1.7366
131 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There was also an issue with the ID fans aproaching a stall condition causing a further reduction in | 740 | F040 | 1455 | 79 | 07/04/2012 | 19:45 | 07/05/2012 | 00:00 | 4.25 | 0.22311
132 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 0410 | 79 | 07/05/2012 | 00:00 | 07/05/2012 | 08:50 | 8.8333 | 0.35062
133 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There was also issues with the water seal on the bottom ash drag chain that affected boiler air flow | 705 | F790 | 0410 | 79 | 07/06/2012 | 08:50 | 07/06/2012 | 09:05 | 0.25 | 0.024328
134 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There was also issues with the water seal on the bottom ash drag chain that also affected air flows. | 680 | F790 | 0410 | 79 | 07/06/2012 | 09:05 | 07/06/2012 | 13:00 | 3.9167 | 0.50651
135 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 0410 | 79 | 07/06/2012 | 13:00 | 07/09/2012 | 11:00 | 70 | 2.7785
136 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There was also a temperature excursion on a coal mill burner that caused a further reduction in load | 650 | F790 | 0410 | 79 | 07/09/2012 | 11:00 | 07/09/2012 | 12:45 | 1.75 | 0.29353
137 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 0410 | 79 | 07/09/2012 | 12:45 | 07/14/2012 | 03:30 | 110.75 | 4.396
138 | D1 | The "2B" Mill was removed from service to allow for clean out of the P/A flow tubes. The "2C" Mill was out of serice to allow Doosan to work on the S/A Dampers. This required a load limit for the above stated time and load. | 717 | F120 | 0340 | 40 | 07/14/2012 | 03:30 | 07/14/2012 | 03:45 | 0.25 | 0.020487
139 | D1 | The "2B" Mill was removed from service to allow for clean out of the P/A flow tubes. The "2C" Mill was out of serice to allow Doosan to work on the S/A Dampers. This required a load limit for the above stated time and load. | 677 | F120 | 0340 | 40 | 07/14/2012 | 03:45 | 07/14/2012 | 07:15 | 3.5 | 0.46607
140 | D1 | The "2B" Mill was removed from service to allow for clean out of the P/A flow tubes. The "2C" Mill was out of serice to allow Doosan to work on the S/A Dampers. This required a load limit for the above stated time and load. | 710 | F120 | 0340 | 40 | 07/14/2012 | 07:15 | 07/14/2012 | 10:00 | 2.75 | 0.25
141 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 0410 | 79 | 07/14/2012 | 10:00 | 07/14/2012 | 11:00 | 1 | 0.039693
142 | D1 | The "2B" Mill was removed from service to allow for clean out of the P/A flow tubes. When the mill was placed back in service the Mill tripped due to a loose connection on the P/A flow tube connection. The fitting was adjusted and the mill was returned to | 615 | F120 | 0340 | 40 | 07/14/2012 | 11:00 | 07/21/2012 | 13:00 | 170 | 36.1332
143 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 0410 | 79 | 07/14/2012 | 13:00 | 07/17/2012 | 12:00 | 71 | 2.8182
144 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 770 | F790 | 0410 | 79 | 07/17/2012 | 12:00 | 07/17/2012 | 17:48 | 5.8 | 0.08169
145 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There were also issues with fan stall alarms. | 760 | F790 | 0410 | 79 | 07/17/2012 | 17:48 | 07/18/2012 | 00:00 | 6.2 | 0.16671
146 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 770 | F790 | 0410 | 79 | 07/18/2012 | 00:00 | 07/18/2012 | 03:34 | 3.5667 | 0.050235
147 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There was also issues with ID Fans approaching a stall condition. | 760 | F790 | 0410 | 79 | 07/18/2012 | 03:34 | 07/18/2012 | 15:00 | 11.4333 | 0.30743
148 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There was also issues with ID Fans approaching a stall condition. | 732 | F790 | 0410 | 79 | 07/18/2012 | 15:00 | 07/19/2012 | 00:00 | 9 | 0.56466
149 | D4 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There was also a leak in the 2A ID Fan EHC System that had to be repaired. | 400 | F540 | 1455 | 54 | 07/19/2012 | 00:00 | 07/19/2012 | 02:11 | 2.1833 | 1.0651
150 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 760 | F790 | 0410 | 79 | 07/19/2012 | 02:11 | 07/19/2012 | 15:00 | 12.8167 | 0.34462
151 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There was also issues with ID Fans approaching a stall condition. | 745 | F790 | 0410 | 79 | 07/19/2012 | 15:00 | 07/19/2012 | 19:00 | 4 | 0.18438
152 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 760 | F790 | 0410 | 79 | 07/19/2012 | 19:00 | 07/19/2012 | 23:45 | 4.75 | 0.12772
153 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There were issues with the 2A Coal Mill Burner Temps during tuning that required the mill to be take | 625 | F790 | 0410 | 79 | 07/19/2012 | 23:45 | 07/20/2012 | 02:59 | 3.2333 | 0.64584
154 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 760 | F790 | 0410 | 79 | 07/20/2012 | 02:59 | 07/25/2012 | 12:30 | 129.5167 | 3.4825
155 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. The unit was also up against an ID Fan Stall Alarm. | 750 | F790 | 0410 | 79 | 07/25/2012 | 12:30 | 07/25/2012 | 17:00 | 4.5 | 0.17862
156 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. The unit was also up against an ID Fan Stall Alarm. | 740 | F790 | 0410 | 79 | 07/25/2012 | 17:00 | 07/26/2012 | 00:00 | 7 | 0.36748
157 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. The unit was also up against an ID Fan Stall Alarm. | 750 | F790 | 0410 | 79 | 07/26/2012 | 00:00 | 07/26/2012 | 12:30 | 12.5 | 0.49616
158 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 762 | F790 | 0410 | 79 | 07/26/2012 | 12:30 | 07/26/2012 | 13:15 | 0.75 | 0.018246
159 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 775 | F790 | 0410 | 79 | 07/26/2012 | 13:15 | 07/27/2012 | 00:00 | 10.75 | 0.082586
160 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 780 | F790 | 0410 | 79 | 07/27/2012 | 00:00 | 07/27/2012 | 08:00 | 8 | 0.010243
161 | NC | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. Unit setting @ 785 MW dring this period. | 0 | F790 | 0410 | 79 | 07/27/2012 | 08:00 | 07/27/2012 | 13:00 | 5 | 0
162 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 775 | F790 | 0410 | 79 | 07/27/2012 | 13:00 | 07/28/2012 | 03:37 | 14.6167 | 0.11229
163 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. Unit loading also had to be dropped due to a temperature excursion on the 2F Coal Mill Burners. | 657 | F790 | 0410 | 79 | 07/28/2012 | 03:37 | 07/28/2012 | 05:00 | 1.3833 | 0.21963
164 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 780 | F790 | 0410 | 79 | 07/28/2012 | 05:00 | 07/28/2012 | 09:00 | 4 | 0.0051216
165 | NC | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. Unit setting @ 785 MW during this period. | 0 | F790 | 0410 | 79 | 07/28/2012 | 09:00 | 07/30/2012 | 02:19 | 41.3167 | 0
166 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 762 | F790 | 0410 | 79 | 07/30/2012 | 02:19 | 07/30/2012 | 16:29 | 14.1667 | 0.34464
167 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. The load on the unit had to be lowered due to issues with the 2B Coal Mill Burners forcing the mill | 650 | F790 | 0410 | 79 | 07/30/2012 | 16:29 | 07/30/2012 | 20:05 | 3.6 | 0.60384
168 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. TC2 unit loading was reduced due to issues with the 2B Coal Mill Burners. | 640 | F790 | 0410 | 79 | 07/30/2012 | 20:05 | 07/30/2012 | 20:31 | 0.43333 | 0.078233
169 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. TC2 unit loading had to be reduced due to issues with both the 2A and 2B Coal Mill Burners. | 450 | F790 | 0410 | 79 | 07/30/2012 | 20:31 | 07/30/2012 | 22:10 | 1.65 | 0.6993
170 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. TC2 unit loading had to be reduced due to issues with both the 2A and 2B Coal Mill Burners. | 650 | F790 | 0410 | 79 | 07/30/2012 | 22:10 | 07/31/2012 | 00:00 | 1.8333 | 0.30751
171 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. TC2 unit loading had to be reduced due to issues with both the 2A and 2B Coal Mill Burners. | 680 | F790 | 0410 | 79 | 07/31/2012 | 00:00 | 07/31/2012 | 02:00 | 2 | 0.25864
172 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 765 | F790 | 0410 | 79 | 07/31/2012 | 02:00 | 07/31/2012 | 02:50 | 0.83333 | 0.017072
173 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. TC2 unit loading had to be reduced due to issues with both the 2B and 2C Coal Mill Burners. | 650 | F790 | 0410 | 79 | 07/31/2012 | 02:50 | 07/31/2012 | 05:00 | 2.1667 | 0.36342
174 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. TC2 unit loading had to be reduced due to issues with both the 2B and 2C Coal Mill Burners. | 760 | F790 | 0410 | 79 | 07/31/2012 | 05:00 | 07/31/2012 | 08:34 | 3.5667 | 0.095903
175 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. TC2 unit loading had to be reduced due to issues with both the 2B and 2C Coal Mill Burners. | 635 | F790 | 0410 | 79 | 07/31/2012 | 08:34 | 07/31/2012 | 10:20 | 1.7667 | 0.33026
177 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 760 | F790 | 0410 | 79 | 07/31/2012 | 10:20 | 08/01/2012 | 00:00 | 13.6667 | 0.36748
178 | D1 | We are holding load down on TC2 for Doosan to complete air fow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 765 | F790 | 0410 | 79 | 08/01/2012 | 00:00 | 08/01/2012 | 22:00 | 22 | 0.4507
177 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 760 | F790 | 0410 | 79 | 08/01/2012 | 00:00 | 08/01/2012 | 00:00 | 0 | 0
179 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There were issues with the 2B Coal Mill Burner Temps required the mill to be taken out of service. | 645 | F790 | 0410 | 79 | 08/01/2012 | 22:00 | 08/02/2012 | 00:00 | 2 | 0.34827
180 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 765 | F790 | 0410 | 79 | 08/02/2012 | 00:00 | 08/02/2012 | 10:16 | 10.2667 | 0.21033
181 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There were issues with the 2F Coal Mill Burner Temps that required the mill to be taken out of servi | 635 | F790 | 0410 | 79 | 08/02/2012 | 10:16 | 08/02/2012 | 21:00 | 10.7333 | 2.0065
182 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 765 | F790 | 0410 | 79 | 08/02/2012 | 21:00 | 08/02/2012 | 22:00 | 1 | 0.020487
183 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There were issues with the 2B & 2F Coal Mill Burner Temps that required the mills to be taken out of | 640 | F790 | 0410 | 79 | 08/02/2012 | 22:00 | 08/04/2012 | 06:09 | 32.15 | 5.8043
184 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There were issues with the 2A; 2B & 2F Coal Mill Burner Temps that required the mills to be taken ou | 480 | F790 | 0410 | 79 | 08/04/2012 | 06:09 | 08/04/2012 | 09:00 | 2.85 | 1.0984
185 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There were issues with the 2A & 2B Coal Mill Burner Temps that required the mills to be taken out o | 640 | F790 | 0410 | 79 | 08/04/2012 | 09:00 | 08/04/2012 | 13:15 | 4.25 | 0.76729
186 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There were issues with the 2B Coal Mill Burner Temps that required the mill to be taken out of servi | 765 | F790 | 0410 | 79 | 08/04/2012 | 13:15 | 08/06/2012 | 10:15 | 45 | 0.9219
187 | NC | We are holding load @ 785 mw's on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 0 | F790 | 0410 | 79 | 08/06/2012 | 10:15 | 08/06/2012 | 12:30 | 2.25 | 0
188 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There were issues with the 2B Coal Mill Burner Temps during tuning that required the mill to be take | 765 | F790 | 0410 | 79 | 08/06/2012 | 12:30 | 08/06/2012 | 15:30 | 3 | 0.06146
189 | NC | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 0 | F790 | 0410 | 79 | 08/06/2012 | 15:30 | 08/07/2012 | 08:52 | 17.3667 | 0
190 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 765 | F790 | 0410 | 79 | 08/07/2012 | 18:30 | 08/11/2012 | 01:12 | 78.7 | 1.6123
191 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. There were issues with the 2A Coal Mill Burner Temps during tuning that required the mill to be take | 640 | F790 | 0410 | 79 | 08/11/2012 | 01:12 | 08/11/2012 | 10:00 | 8.8 | 1.5887
192 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 760 | F790 | 0410 | 79 | 08/11/2012 | 10:00 | 08/17/2012 | 04:44 | 138.7333 | 3.7303
195 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 765 | F790 | 0410 | 79 | 08/17/2012 | 13:35 | 08/17/2012 | 18:30 | 4.9167 | 0.10073
196 | D1 | The "2F" Mill burner temperature was out of limits and the Operator had to trip the mill. The unit load was reduced until the burner could be purged out and the mill was returned to service. | 660 | F780 | 0410 | 78 | 08/17/2012 | 18:30 | 08/17/2012 | 21:00 | 2.5 | 0.38732
197 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 765 | F790 | 0410 | 79 | 08/17/2012 | 21:00 | 08/21/2012 | 09:00 | 84 | 1.7209
198 | NC | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 0 | F790 | 0410 | 79 | 08/21/2012 | 09:00 | 08/21/2012 | 18:00 | 9 | 0
199 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 760 | F790 | 0410 | 79 | 08/21/2012 | 18:00 | 08/22/2012 | 01:00 | 7 | 0.18822
200 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 780 | F790 | 0410 | 79 | 08/22/2012 | 01:00 | 08/22/2012 | 15:00 | 14 | 0.017926
201 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 760 | F790 | 0410 | 79 | 08/22/2012 | 15:00 | 08/25/2012 | 00:00 | 57 | 1.5327
202 | D4 | We are holding load down on TC-2 so Doosan can remove ammonia injection on each side of the SCR and still stay in compliance. This SCR testing is required by Doosan to set-up the proper injection balance and flow rates for this unit. | 447 | F790 | 8810 | 79 | 08/25/2012 | 00:00 | 08/25/2012 | 05:30 | 5.5 | 2.3521
203 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 760 | F790 | 0410 | 79 | 08/25/2012 | 05:30 | 08/28/2012 | 00:00 | 66.5 | 1.7881
204 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve. We were also having problems with the 2E Coal Feeder, the load was reduced to change out the feeder belt. | 645 | F790 | 0410 | 79 | 08/28/2012 | 00:00 | 08/28/2012 | 06:00 | 6 | 1.0448
205 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 760 | F790 | 0410 | 79 | 08/28/2012 | 06:00 | 09/01/2012 | 00:00 | 90 | 2.42
206 | D4 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve. We were also having problems with the 2F coal feeder at this time. Repairs were made to the feeder and the load limit was raised to 760 mw's. | 605 | F060 | 0250 | 06 | 08/29/2012 | 22:00 | 08/30/2012 | 03:45 | 5.75 | 1.2958
208 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 1455 | 79 | 08/31/2012 | 19:00 | 09/01/2012 | 00:00 | 5 | 0.19846
209 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 762 | F790 | 0410 | 79 | 09/01/2012 | 00:00 | 09/01/2012 | 01:00 | 1 | 0.024328
205 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 760 | F790 | 0410 | 79 | 09/01/2012 | 00:00 | 09/01/2012 | 00:00 | 0 | 0
208 | D1 | We are holding load down on TC-2 for Doosan to complete air flow testing and finish the air flow curve before we raise load to ensure air flow is correct. | 750 | F790 | 1455 | 79 | 09/01/2012 | 00:00 | 09/01/2012 | 00:00 | 0 | 0
210 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 750 | F040 | 0360 | 04 | 09/01/2012 | 01:00 | 09/02/2012 | 00:00 | 23 | 0.91293
211 | NC | TC2 Unit Loading was reduced to remove slag from the boiler. | 0 | FS00 | 1100 | S0 | 09/02/2012 | 00:00 | 09/02/2012 | 05:45 | 5.75 | 0
212 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 762 | F040 | 0360 | 04 | 09/02/2012 | 05:45 | 09/02/2012 | 15:41 | 9.9333 | 0.24166
213 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 750 | F040 | 0360 | 04 | 09/02/2012 | 15:41 | 09/03/2012 | 00:00 | 8.3167 | 0.33011
214 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 762 | F040 | 0360 | 04 | 09/03/2012 | 00:00 | 09/03/2012 | 09:07 | 9.1167 | 0.22179
215 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 752 | F040 | 0360 | 04 | 09/03/2012 | 09:07 | 09/03/2012 | 17:45 | 8.6333 | 0.32057
216 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 742 | F040 | 0360 | 04 | 09/03/2012 | 17:45 | 09/03/2012 | 18:00 | 0.25 | 0.012484
217 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 732 | F040 | 0360 | 04 | 09/03/2012 | 18:00 | 09/04/2012 | 00:00 | 6 | 0.37644
218 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 762 | F040 | 0360 | 04 | 09/04/2012 | 00:00 | 09/04/2012 | 10:15 | 10.25 | 0.24936
219 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 752 | F040 | 0360 | 04 | 09/04/2012 | 10:15 | 09/04/2012 | 12:53 | 2.6333 | 0.097781
220 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 742 | F040 | 0360 | 04 | 09/04/2012 | 12:53 | 09/05/2012 | 00:00 | 11.1167 | 0.55512
221 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 747 | F040 | 0360 | 04 | 09/05/2012 | 00:00 | 09/05/2012 | 11:08 | 11.1333 | 0.48468
222 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 737 | F040 | 0360 | 04 | 09/05/2012 | 11:08 | 09/05/2012 | 14:36 | 3.4667 | 0.19531
223 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 727 | F040 | 0360 | 04 | 09/05/2012 | 14:36 | 09/05/2012 | 19:00 | 4.4 | 0.30423
224 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 742 | F040 | 0360 | 04 | 09/05/2012 | 19:00 | 09/06/2012 | 13:46 | 18.7667 | 0.93713
225 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 737 | F040 | 0360 | 04 | 09/06/2012 | 13:46 | 09/07/2012 | 00:00 | 10.2333 | 0.57653
226 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 750 | F040 | 0360 | 04 | 09/07/2012 | 00:00 | 09/07/2012 | 18:42 | 18.7 | 0.74225
227 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 735 | F040 | 0360 | 04 | 09/07/2012 | 18:42 | 09/07/2012 | 22:00 | 3.3 | 0.19437
228 | D4 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. Reducing load to remove Unit from service for burner inspections. | 300 | F040 | 0360 | 04 | 09/07/2012 | 22:00 | 09/08/2012 | 02:47 | 4.7833 | 2.9459
229 | MO | TC2 was removed from service to allow for burner inpections on the unit. | 0 | F040 | 0360 | 04 | 09/08/2012 | 02:47 | 09/16/2012 | 22:38 | 211.85 | 211.85
231 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 775 | F040 | 0360 | 04 | 09/18/2012 | 00:30 | 09/18/2012 | 10:15 | 9.75 | 0.074904
238 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 775 | F040 | 0360 | 04 | 09/18/2012 | 16:00 | 09/19/2012 | 13:20 | 21.3333 | 0.16389
240 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 775 | F040 | 0360 | 04 | 09/19/2012 | 15:00 | 09/19/2012 | 22:03 | 7.05 | 0.054161
243 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 775 | F040 | 0360 | 04 | 09/20/2012 | 17:00 | 09/22/2012 | 16:30 | 47.5 | 0.36492
244 | D1 | Doosan was working on the purge air system for the "2C" Mill and tripped the mill off. The mill was cleaned out and returned to service. | 650 | F410 | 0340 | 41 | 09/22/2012 | 16:30 | 09/22/2012 | 20:30 | 4 | 0.67093
245 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 775 | F040 | 0360 | 04 | 09/22/2012 | 20:30 | 09/26/2012 | 00:00 | 75.5 | 0.58003
246 | NC | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 0 | F040 | 0360 | 04 | 09/26/2012 | 00:00 | 09/26/2012 | 08:40 | 8.6667 | 0
247 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. There was also issues with loss of the 2C Coal Mill. | 642 | F040 | 0360 | 04 | 09/26/2012 | 08:40 | 09/26/2012 | 10:00 | 1.3333 | 0.2373
248 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. Testing was also being done. | 705 | F040 | 0360 | 04 | 09/26/2012 | 10:00 | 09/26/2012 | 12:57 | 2.95 | 0.28707
250 | NC | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 0 | F040 | 0360 | 04 | 09/26/2012 | 15:00 | 09/26/2012 | 16:30 | 1.5 | 0
251 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 780 | F040 | 0360 | 04 | 09/26/2012 | 16:30 | 09/26/2012 | 18:15 | 1.75 | 0.0022407
252 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 770 | F040 | 0360 | 04 | 09/26/2012 | 18:15 | 09/27/2012 | 00:30 | 6.25 | 0.088028
253 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 780 | F040 | 0360 | 04 | 09/27/2012 | 00:30 | 09/27/2012 | 10:00 | 9.5 | 0.012164
254 | NC | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 0 | F040 | 0360 | 04 | 09/27/2012 | 10:00 | 09/27/2012 | 12:00 | 2 | 0
255 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 778 | F040 | 0360 | 04 | 09/27/2012 | 12:00 | 09/27/2012 | 14:30 | 2.5 | 0.0096031
256 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 763 | F040 | 0360 | 04 | 09/27/2012 | 14:30 | 09/27/2012 | 16:00 | 1.5 | 0.034571
257 | D1 | TC2 Unit Loading was reduced due to air flow issues with the unit. Holding load down to keep unit within OEM specs. | 780 | F040 | 0360 | 04 | 09/27/2012 | 16:00 | 09/28/2012 | 03:15 | 11.25 | 0.014405
259 | D1 | The load was limited due to air flow issues on the unit. The OEM is still working on getting air flow issues resolved on the unit. | 785 | F040 | 0360 | 04 | 10/01/2012 | 09:52 | 10/06/2012 | 00:00 | 110.1333 | 3.2672
260 | NC | This load reduction was scheduled to de-slag the boiler and burners on the unit. This was to help with burner problems on the unit at the OEM's request. | 0 | FS00 | 0360 | S0 | 10/06/2012 | 00:00 | 10/06/2012 | 04:45 | 4.75 | 0
261 | D1 | The load was limited due to air flow issues on the unit. The OEM is still working on getting air flow issues resolved on the unit. The available gross was 785 MW. | 785 | F040 | 0360 | 04 | 10/06/2012 | 04:45 | 10/10/2012 | 00:00 | 91.25 | 2.707
262 | D4 | This was a planned weekly de-slag as outlined by the OEM. | 435 | FS00 | 1190 | S0 | 10/13/2012 | 00:00 | 10/13/2012 | 05:30 | 5.5 | 2.5426
264 | D1 | This load limit was due to hitting the max feedrate limit on the coal feeders. Poor quality fuel or poor fuel blend (normal is 70/30 PRB blend) | 794 | FW00 | 9205 | FR | 10/14/2012 | 05:00 | 10/14/2012 | 18:15 | 13.25 | 0.24567
266 | D1 | This load limit was due to hitting the max feedrate limit on the coal feeders. Poor quality fuel or poor fuel blend (normal is 70/30 PRB blend) | 800 | FW00 | 9205 | FR | 10/14/2012 | 21:15 | 10/15/2012 | 07:00 | 9.75 | 0.10847
270 | D1 | The "2F" Mill was tripped due to high burner temps. on the "2F1" burner. This required the above listed de-rate on the unit. | 650 | F780 | 0360 | 82 | 10/20/2012 | 16:45 | 10/20/2012 | 21:00 | 4.25 | 0.83529
271 | D1 | The "2F" mill was tripped off due to high temp. on the "2F1" burner, this caused the above listed derate on the unit. | 690 | F780 | 0360 | 82 | 10/20/2012 | 22:30 | 10/20/2012 | 22:45 | 0.25 | 0.036774
272 | D1 | The "2F" Mill was removed from service due to high burner temp. we had trouble getting the spare mill back in service and this caused the above listed derate on the unit. | 650 | F780 | 0360 | 78 | 10/20/2012 | 22:45 | 10/21/2012 | 00:30 | 1.75 | 0.34394
276 | D1 | TC2 load was dropped to allow for a mill change on the unit. The load needed to be dropped to stay within OEM guidelines on the burners. | 795 | F040 | 0360 | 04 | 10/22/2012 | 14:15 | 10/22/2012 | 20:00 | 5.75 | 0.099506
282 | D1 | TC2 unit loading had to be reduced due to a temperature excursion on the 2B Coal Mill Burners requiring the mill to be removed from service. | 625 | F040 | 0360 | 83 | 10/26/2012 | 06:00 | 10/26/2012 | 09:00 | 3 | 0.68232
285 | D1 | TC2 Unit Loading had to be reduced due to a temperature excursion on the 2B Coal Mill Burners causing the mill to have to be removed from service. | 665 | F040 | 0360 | 83 | 10/26/2012 | 21:15 | 10/27/2012 | 02:29 | 5.2333 | 0.93152

## TC2 - 2013
TC2 - 2013
[13 empty] | 2013 | NDC | Period Hours | Available Hours | FOH | EFDH | EFOH | MOH | EMDH | EMOH | Act SH | Fcst SH | MW*Fcst SH | MW*EFOH | MW*Fcst SH | MW*EMOH | MW*Fcst SH | MW*F&MOH | FOR | EFOR | MOR | EUOR | RH | AH | EPDH | MW*PH | MW*(AH-DH) | EAF | MW*(EFOH+EMOH+EPDH) | MW*PH | UU
|  |  | 809 | Gross Winter |  |  | 760 | Net Winter | [5 empty] | 559.5 | 8760 | 7950.3833 | 287.4 | 84.0307 | 371.4307 | 0 |  | 0 | 7950.3833 | 8237.7833 | 4609039.775 | 207815.4788 | 0 | 4448239.475 | 207815.4788 | 4609039.775 | 3.489% | 4.509% | 0% | 4.509% | 0 | 7950.3833 | 15.915 | 4901220 | 4392319.8285 | 89.62% | 216719.9465 | 4901220 | 4.422%
|  |  | 781 | Gross Summer |  |  | 732 | Net Summer
[14 empty] | POH |  | FOH |  | EFDH |  | EPDH |  | MOH
[7 empty] | Winter - October through March | [6 empty] | PO | 522.2167 | U1 | 287.4 | D1 | 84.0307 | PD | 15.915 | MO | 0
[7 empty] | Summer - April through September | [6 empty] | PE | 0 | U2 | 0 | D2 | 0 | DE | 0 | ME | 0
[16 empty] | U3 | 0 | D3 | 0
[16 empty] | SF | 0
Event Number | Event Type | Event Description | MW Available | Failure Mech Code | Cause Code | Amp Code | Start Date | Start Time | End Date | End Time | Actual Event Duration (hours) | Equivalent Outage Duration (hours)
2 | NC | The unit is on line and ramping up. The mills are not with-in temp. limits so we are placing the mills on warm up and increasing load as the mills are available. | 0 | F780 | 0338 | 78 | 01/07/2013 | 18:06 | 01/08/2013 | 03:30 | 9.4 | 0
3 | D1 | The "2C" and "2F" Mills would not start due to temp. limits and limit switch issues. I/E and Doosan are working on the issues. | 660 | F780 | 0338 | 78 | 01/08/2013 | 03:30 | 01/08/2013 | 15:15 | 11.75 | 2.1641
8 | PD | This planned de-rate was to allow testing on the "2F" burners by Doosan and Bechtel. | 390 | F790 | 0360 | 79 | 01/09/2013 | 09:00 | 01/09/2013 | 14:30 | 5.5 | 2.8486
9 | PD | This planned de-rate was to allow testing on the "2F" burners by Doosan and Bechtel. | 445 | F790 | 0360 | 79 | 01/09/2013 | 14:30 | 01/09/2013 | 17:00 | 2.5 | 1.1248
10 | PD | This planned de-rate was to allow testing on the "2F" burners by Doosan and Bechtel. | 399 | F790 | 0360 | 79 | 01/09/2013 | 17:00 | 01/10/2013 | 04:00 | 11 | 5.5748
11 | D1 | The oil guns were causing a delay on increasing load, The oil guns would not light off as requested. | 499 | F460 | 0385 | FR | 01/10/2013 | 04:00 | 01/10/2013 | 05:00 | 1 | 0.38319
16 | D1 | The unit was limited due to issues related to wet coal the hot air dampers on the coal mills were running out and the cold air dampers were closed with the feeder about 70%. | 789 | FW00 | 9270 | W0 | 01/14/2013 | 08:45 | 01/14/2013 | 22:00 | 13.25 | 0.32756
20 | D4 | TC2 was derated in order to perform the weekly planned deslag of the boiler as recommended by the boiler OEM. | 435 | FS00 | 0920 | S0 | 01/19/2013 | 00:01 | 01/19/2013 | 06:00 | 5.9833 | 2.7661
21 | D4 | TC2 was ramped up in load to complete the weekly deslag of the boiler as recommended by the boiler OEM. | 680 | FS00 | 0920 | S0 | 01/19/2013 | 06:00 | 01/19/2013 | 06:30 | 0.5 | 0.079728
27 | D1 | The 2D coal mill tripped with support fuel in. C Mill was put back in service to return the unit to full load. | 650 | F820 | 0310 | 82 | 02/03/2013 | 18:00 | 02/03/2013 | 19:00 | 1 | 0.19654
38 | D1 | Complete details attributed to this derate are explained in Event No. 37. Further derate was necessary to attenuate and environmental impacts from having the ammonia system out of service. Following this derate, the system was brought back under control | 505 | F820 | 8825 | 82 | 02/21/2013 | 15:40 | 02/21/2013 | 16:13 | 0.55 | 0.20667
39 | D1 | Due to the ammonia system being out of service (event 37 and 38), NOx issues were being experienced by the unit, even after returning the ammonia system to service. Further derate to 360MW was necessary to ensure no NOx limits were reached. | 360 | FE00 | 8823 | E0 | 02/21/2013 | 16:13 | 02/21/2013 | 17:30 | 1.2833 | 0.71226
40 | D1 | Unit load was increased to 498MW as NOx limits began to come under control and risk of reaching limits was mitigated. This load increase was sustained as well for planned RATA testing. | 498 | FE00 | 8823 | E0 | 02/21/2013 | 17:30 | 02/21/2013 | 21:00 | 3.5 | 1.3455
44 | D1 | Differential pressure on the air heater began to rise and load was reduced while investigation and trouble shooting was undertaken. After the outage (taken on 2/25 at 1519) pluggage in the air heater was found and an air heater wash performed. | 650 | F660 | 1495 | 66 | 02/25/2013 | 06:30 | 02/25/2013 | 08:00 | 1.5 | 0.29481
45 | D1 | The C coal mill burner temperature alarm came in due to high temperature indication. Removal of the 2C mill from service required further unit derate. | 605 | F780 | 0360 | H0 | 02/25/2013 | 08:00 | 02/25/2013 | 09:15 | 1.25 | 0.3152
46 | D1 | The air heater differential remained high after 2C mill was removed from service. Load was maintained at the derated 605MW level while further investigation into the issue was completed. | 605 | F660 | 1495 | 66 | 02/25/2013 | 09:15 | 02/25/2013 | 11:00 | 1.75 | 0.44129
47 | D1 | The air heater differential remained high so further unit derate was required. Load was reduced to 542MW. | 542 | F660 | 1495 | 66 | 02/25/2013 | 11:00 | 02/25/2013 | 15:19 | 4.3167 | 1.4247
48 | U1 | With the air heater differential remaining an issue and increasing, the decision to take the unit offline and conduct an air heater wash was made. The fouling in the air heater was found and washed away. Root cause of pluggage not completely known and s | 0 | FF00 | 1495 | T2 | 02/25/2013 | 15:19 | 02/28/2013 | 14:48 | 71.4833 | 71.4833
54 | D1 | Continued wet coal required further de-rate. Still seeing issues with the Air Heater and Fans. | 704 | FW00 | 9270 | W0 | 03/12/2013 | 07:37 | 03/12/2013 | 10:00 | 2.3833 | 0.30933
55 | D1 | Unit 2 began experiences continued boiler swings after the wet coal issue was resolved. Air heater pluggage could be the basis for the swings as well as the Mill Limited by Air issue. However, the boiler swings were causing problems and required operati | 604 | F400 | 1999 | 40 | 03/12/2013 | 10:00 | 03/12/2013 | 19:00 | 9 | 2.2806
56 | D1 | Continued experiencing boiler swings and reduced load further to attempt to mitigate issues. | 545 | F400 | 1999 | 40 | 03/12/2013 | 19:00 | 03/13/2013 | 00:00 | 5 | 1.6316
57 | D1 | Continued experiencing boiler swings but increased load slightly to test out boiler operation/condition and whether issue had leveled. | 550 | F400 | 1999 | 40 | 03/13/2013 | 00:00 | 03/13/2013 | 11:00 | 11 | 3.5216
58 | D1 | Boiler swings still occurring and load had to be reduced further to regain boiler control. Operations was able to get control of unit at 470MW. | 470 | F400 | 1999 | 40 | 03/13/2013 | 11:00 | 03/13/2013 | 14:00 | 3 | 1.2571
59 | D1 | Load was able to be increased to 500 MW with boiler swings no longer being an issue. Decision was made to maintain unit at this load until the upcoming planned three week outage begins. At this point investigation into all of the issues will commence to | 500 | F400 | 1999 | 40 | 03/13/2013 | 14:00 | 03/17/2013 | 17:13 | 99.2167 | 37.8961
60 | U1 | The boiler swings were unable to be controlled further. Unit was taken offline and plant personnel moved directly into the planned 3 week outage. End of forced outage was after air heater was cleaned. | 0 | F400 | 1999 | T2 | 03/17/2013 | 17:13 | 03/24/2013 | 05:47 | 156.5667 | 156.5667
61 | PO | The Unit 2 outage was planned for complete modifications to the A, B, C, D, and E row of burners to match the modifications previously made to the F-row. This modification has been initiatied due to emission issues with the current burner design and issu | 0 | FE00 | 0360 | E0 | 03/24/2013 | 05:47 | 04/01/2013 | 00:00 | 186.2167 | 186.2167
61 | PO | The Unit 2 outage was planned for complete modifications to the A, B, C, D, and E row of burners to match the modifications previously made to the F-row. This modification has been initiatied due to emission issues with the current burner design and issu | 0 | FE00 | 0360 | E0 | 04/01/2013 | 00:00 | 04/15/2013 | 00:00 | 336 | 336
67 | U1 | Leak in tube weld near spiral balance header. | 0 | F540 | 1000 | 54 | 06/03/2013 | 08:32 | 06/05/2013 | 16:52 | 56.3333 | 56.3333
68 | D4 | Post outage tuning per Doosan request. Hold at 400 MW for testing and tuning of burners, mills, etc following the "F-Row" burner modification to all burners. | 438 | F790 | 0360 | 79 | 06/06/2013 | 02:00 | 06/06/2013 | 12:00 | 10 | 4.3918
69 | PD | Further tuning at a variable de-rate following 400 MW hold increasing to 550 MW over several hours of run-time. | 475 | F790 | 0360 | 79 | 06/06/2013 | 12:00 | 06/07/2013 | 04:15 | 16.25 | 6.3668
77 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 375 | F660 | 1455 | 66 | 06/07/2013 | 21:30 | 06/08/2013 | 00:00 | 2.5 | 1.2996
78 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 480 | F660 | 1455 | 66 | 06/08/2013 | 00:00 | 06/08/2013 | 05:00 | 5 | 1.927
79 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 700 | F660 | 1455 | 66 | 06/08/2013 | 05:00 | 06/08/2013 | 12:00 | 7 | 0.72599
80 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 760 | F660 | 1455 | 66 | 06/08/2013 | 12:00 | 06/08/2013 | 15:00 | 3 | 0.080666
81 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 680 | F660 | 1455 | 66 | 06/08/2013 | 15:00 | 06/08/2013 | 17:00 | 2 | 0.25864
82 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 660 | F660 | 1455 | 66 | 06/08/2013 | 17:00 | 06/08/2013 | 17:19 | 0.31667 | 0.049061
83 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 615 | F660 | 1455 | 66 | 06/08/2013 | 17:19 | 06/08/2013 | 18:00 | 0.68333 | 0.14524
84 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 575 | F660 | 1455 | 66 | 06/08/2013 | 18:00 | 06/09/2013 | 00:00 | 6 | 1.5826
85 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 670 | F660 | 1455 | 66 | 06/09/2013 | 00:00 | 06/09/2013 | 00:15 | 0.25 | 0.035531
86 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 620 | F660 | 1455 | 66 | 06/09/2013 | 00:15 | 06/10/2013 | 02:24 | 26.15 | 5.3907
87 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 600 | F660 | 1455 | 66 | 06/10/2013 | 02:24 | 06/10/2013 | 03:22 | 0.96667 | 0.22403
88 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 580 | F660 | 1455 | 66 | 06/10/2013 | 03:22 | 06/10/2013 | 12:30 | 9.1333 | 2.3506
89 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 750 | F660 | 1455 | 66 | 06/12/2013 | 14:40 | 06/12/2013 | 17:30 | 2.8333 | 0.11246
90 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 695 | F660 | 1455 | 66 | 06/13/2013 | 14:30 | 06/13/2013 | 18:30 | 4 | 0.44046
91 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 650 | F660 | 1455 | 66 | 06/14/2013 | 04:00 | 06/14/2013 | 04:50 | 0.83333 | 0.13978
92 | D1 | Fan stall issues using original fan stall ring, I/E regularly cleaned ports and checked transmitters. But stall issues continued. | 623 | F660 | 1455 | 66 | 06/14/2013 | 04:50 | 06/14/2013 | 05:20 | 0.5 | 0.10115
93 | D1 | Changed from original stall ring instrumentation to newly installed fan stall ring. | 270 | F660 | 1455 | 66 | 06/14/2013 | 05:20 | 06/14/2013 | 10:10 | 4.8333 | 3.1624
94 | D1 | During the fan stall ring change-out, load level required ammonia injection to be removed from service during the derate. This then required a hold at a lower load following the ammonia return to service to keep from reaching the 24-hr NOx limit. | 445 | FE00 | 9610 | E0 | 06/14/2013 | 10:10 | 06/14/2013 | 13:45 | 3.5833 | 1.5416
95 | D1 | During boiler tuning, spikes in CO brought the unit close to the exceedance limit for CO requiring a derate to avoid. | 690 | FE00 | 9616 | E0 | 06/19/2013 | 07:35 | 06/19/2013 | 09:53 | 2.3 | 0.26799
96 | D4 | TC2 was derated in order to perform the weekly planned deslag of the boiler as recommended by the boiler OEM. | 450 | FS00 | 0920 | S0 | 06/22/2013 | 23:00 | 06/23/2013 | 05:30 | 6.5 | 2.7548
101 | D4 | Weekly deslag for Unit 2 based on OEM recommendations for cleaning the boiler. | 450 | FS00 | 0920 | S0 | 06/30/2013 | 00:00 | 06/30/2013 | 09:00 | 9 | 3.8143
102 | NC | Weekly deslag planned for Unit 2 based on OEM recommendations | 0 | FS00 | 0920 | S0 | 07/07/2013 | 00:01 | 07/08/2013 | 03:45 | 27.7333 | 0
108 | NC | Tuning of the SCR by Doosan was scheduled and required a low removal rate in order to begin tuning efforts. Load was reduced to 649MW to allow for extra NOx emission room for the day to avoid any exceedance during the SCR tuning process. Event is Non-cu | 0 | F790 | 8810 | 79 | 07/16/2013 | 00:00 | 07/16/2013 | 03:00 | 3 | 0
109 | NC | This load reduction was for weekly boiler de-slag. The load could have been returned to full load if requested by the dispatcher. | 0 | FS00 | 1190 | S0 | 07/21/2013 | 00:00 | 07/21/2013 | 07:00 | 7 | 0
111 | NC | This load reduction was for weekly boiler de-slag. The load could have been returned to full load if requested by the dispatcher. | 0 | FS00 | 1190 | S0 | 07/28/2013 | 00:00 | 07/28/2013 | 09:00 | 9 | 0
112 | NC | Non-curtailing event to perform unit heat rate and capability test. | 782 | F790 | 1990 | 79 | 07/30/2013 | 08:00 | 07/30/2013 | 12:00 | 4 | 0
114 | NC | Non-curtailing derate to execute OEM recommended weekly boiler deslag on TC2. Full load available upon request if dispatch required. | 0 | FS00 | 1190 | S0 | 08/04/2013 | 00:00 | 08/04/2013 | 09:00 | 9 | 0
115 | D1 | High CO readings required a derate to avoid exceedances. | 681 | FE00 | 9616 | E0 | 08/07/2013 | 01:20 | 08/07/2013 | 02:55 | 1.5833 | 0.20273
117 | NC | Weekly OEM suggested derate for boiler deslag. Unit available for full load if required by dispatch. | 0 | FS00 | 1190 | S0 | 08/11/2013 | 00:00 | 08/11/2013 | 08:15 | 8.25 | 0
118 | NC | Weekly boiler deslag for cleaning of the furnace based on OEM recommendations. Able to return to full load if requested from dispatch. | 0 | FS00 | 1190 | S0 | 08/18/2013 | 00:00 | 08/18/2013 | 09:00 | 9 | 0
120 | NC | Weekly boiler deslag as recommended by boiler OEM. Deslag was performed at 450 MW. Unit was available to return to full load if requested by dispatch. | 0 | FS00 | 1190 | S0 | 08/24/2013 | 00:00 | 08/24/2013 | 08:00 | 8 | 0
121 | D1 | Derate due to CO spike. | 685 | FE00 | 9616 | E0 | 08/31/2013 | 19:53 | 08/31/2013 | 21:00 | 1.1167 | 0.13726
122 | D1 | CO emission issues continued with the unit and required derate. | 681 | FE00 | 9616 | E0 | 09/01/2013 | 16:48 | 09/01/2013 | 17:58 | 1.1667 | 0.14938
124 | D1 | Emissions issues involving CO levels following the low suction pressure on the ID Fans which created previous fan stall derate. | 750 | FE00 | 9616 | E0 | 09/01/2013 | 19:55 | 09/02/2013 | 00:00 | 4.0833 | 0.16208
125 | NC | Non-curtailing event to conduct boiler deslag as recommended by OEM at 450 MW. Unit available to return to full load if required by dispatch. | 0 | FS00 | 1190 | S0 | 09/02/2013 | 00:00 | 09/02/2013 | 07:00 | 7 | 0
126 | D1 | Continued CO issues along with FD Fan issues required derate to 680 MW. | 680 | FE00 | 9616 | E0 | 09/02/2013 | 12:00 | 09/02/2013 | 13:30 | 1.5 | 0.19398
129 | NC | Planned weekly boiler deslag as recommended by OEM. Unit available for full load if required by dispatch. | 0 | FS00 | 1190 | S0 | 09/06/2013 | 21:00 | 09/07/2013 | 06:00 | 9 | 0
130 | D1 | Derate required due to AH Differntial increase due to suspected pluggage. Air heater wash planned for weekend outage. | 764 | F660 | 0266 | 66 | 09/10/2013 | 10:57 | 09/10/2013 | 11:30 | 0.55 | 0.011972
131 | D1 | Derate required due to FD Fan stall. Air heater wash planned for weekend outage. | 771 | F660 | 1400 | 66 | 09/10/2013 | 15:17 | 09/11/2013 | 06:00 | 14.7167 | 0.18843
132 | D1 | Derate required due to FD Fan stall. Air heater wash planned for weekend outage. | 749 | F660 | 1400 | 66 | 09/11/2013 | 06:00 | 09/11/2013 | 19:04 | 13.0667 | 0.53538
133 | D1 | Derate required due to FD Fan stall. Air heater wash planned for weekend outage. | 729 | F660 | 1400 | 66 | 09/11/2013 | 19:04 | 09/12/2013 | 00:06 | 5.0333 | 0.33513
134 | D1 | Derate required due to FD Fan stall. Air heater wash planned for weekend outage. | 719 | F660 | 1400 | 66 | 09/12/2013 | 00:06 | 09/12/2013 | 09:32 | 9.4333 | 0.74887
135 | D1 | Derate required due to FD Fan stall. | 680 | F660 | 1400 | 66 | 09/12/2013 | 09:32 | 09/12/2013 | 15:02 | 5.5 | 0.71127
136 | D1 | Derate required due to FD Fan stall. | 275 | F660 | 1400 | 66 | 09/12/2013 | 15:02 | 09/12/2013 | 16:16 | 1.2333 | 0.79906
137 | U1 | FD Fan stall runback alarms started coming in and the F/D Fans went into a run back. We could not get the fans stable so the unit was removed from service. The I/E shop is working on cleaning out the stall probes so we can get control of the fans and keep | 0 | F660 | 1400 | T2 | 09/12/2013 | 16:16 | 09/12/2013 | 19:17 | 3.0167 | 3.0167
139 | D1 | Unit derate was due to air flow issues for the burners from the FD fans. Root cause was found to be the controls which had defaulted to increased stoichiometry on the unit restart. Operators put the controls in manual to mitigate the forced control sche | 650 | F400 | 1415 | 40 | 09/17/2013 | 02:00 | 09/17/2013 | 08:00 | 6 | 1.0064
140 | NC | Boiler deslag conducted at 450 MW based on OEM recommendations. Unit available to return to load if required by dispatch. Also conducted reactive capability testing for low load data. | 0 | FS00 | 1190 | S0 | 09/20/2013 | 17:00 | 09/20/2013 | 23:15 | 6.25 | 0
144 | NC | Boiler deslag conducted at 450 MW based on OEM recommendations. Unit available to return to load if required by dispatch. | 0 | FS00 | 1190 | S0 | 09/29/2013 | 00:01 | 09/29/2013 | 08:15 | 8.2333 | 0
146 | D1 | Excess CO emissions required a derate to keep the Unit from experiencing an excedance due to CO. | 704 | FE00 | 9616 | E0 | 10/01/2013 | 08:21 | 10/01/2013 | 10:30 | 2.15 | 0.27905
151 | NC | OEM recommended deslag of the boiler. Unit available to return to full load if dispatch required. | 0 | FS00 | 1190 | S0 | 10/06/2013 | 00:01 | 10/06/2013 | 09:00 | 8.9833 | 0
153 | NC | Non-curtailing derate for Boiler OEM recommended deslag. Unit available if required by dispatch. | 0 | FS00 | 1190 | S0 | 10/13/2013 | 00:00 | 10/13/2013 | 09:00 | 9 | 0
157 | NC | Non-curtailing derate for Boiler OEM recommended deslag. Unit available for full load if required by dispatch. | 0 | FS00 | 1190 | S0 | 10/20/2013 | 00:00 | 10/20/2013 | 07:00 | 7 | 0
159 | D1 | CO Emission issues due to O2 trim setting issues returning from deslag. | 699 | FE00 | 9616 | E0 | 10/20/2013 | 08:58 | 10/20/2013 | 11:00 | 2.0333 | 0.27647
161 | NC | Non-curtailing derate for OEM recommended weekly deslag. Unit available for full load if dispatch required. | 0 | FS00 | 1190 | S0 | 10/27/2013 | 00:00 | 10/27/2013 | 03:29 | 3.4833 | 0
173 | NC | Non-curtailing derate for Boiler OEM recommended weekly deslag. Unit available to return to load if required by dispatch. | 0 | FS00 | 1190 | S0 | 11/03/2013 | 00:00 | 11/03/2013 | 08:00 | 8 | 0
175 | NC | Non-curtailing derate for OEM recommended weekly deslag. Unit available for full load if dispatch required. | 0 | FS00 | 1190 | S0 | 11/10/2013 | 00:00 | 11/10/2013 | 08:00 | 8 | 0
180 | D1 | Derate necessary to ensure no NOx exceedance. See event 179 for additional details on high NOx causes. | 750 | FE00 | 9610 | E0 | 11/22/2013 | 01:00 | 11/22/2013 | 01:53 | 0.88333 | 0.064421
181 | D1 | Unit 2 combustion issues created high CO requiring derate to minimize exceedance. | 709 | FE00 | 9616 | E0 | 11/23/2013 | 13:32 | 11/23/2013 | 15:00 | 1.4667 | 0.18129
182 | D1 | Elevated CO required unit derate to avoid an exceedance. | 749 | FE00 | 9616 | E0 | 11/27/2013 | 08:25 | 11/27/2013 | 08:35 | 0.16667 | 0.012361
183 | D1 | Elevated CO required unit derate to avoid an exceedance. | 709 | FE00 | 9616 | E0 | 11/27/2013 | 08:35 | 11/27/2013 | 10:00 | 1.4167 | 0.17511
184 | D1 | Elevated CO required unit derate to avoid an exceedance. | 737 | FE00 | 9616 | E0 | 11/27/2013 | 10:00 | 11/27/2013 | 12:00 | 2 | 0.178
185 | D1 | Elevated CO required unit derate to avoid an exceedance. | 686 | FE00 | 9616 | E0 | 11/27/2013 | 12:00 | 11/27/2013 | 13:00 | 1 | 0.15204
186 | D1 | Elevated CO required unit derate to avoid an exceedance. | 754 | FE00 | 9616 | E0 | 11/27/2013 | 13:00 | 11/29/2013 | 00:01 | 35.0167 | 2.3806
187 | NC | Planned non curtailing derate to conduct OEM recommended boiler deslag. Unit available to return to load if required by dispatch. | 0 | FS00 | 1190 | S0 | 11/29/2013 | 00:01 | 11/29/2013 | 08:00 | 7.9833 | 0
188 | NC | Planned non curtailing derate to conduct OEM recommended boiler deslag. Unit available to return to load if required by dispatch. | 0 | FS00 | 1190 | S0 | 12/01/2013 | 00:00 | 12/01/2013 | 09:00 | 9 | 0
193 | D1 | High CO emissions required derate to avoid an exceedance on CO. | 709 | FE00 | 9616 | E0 | 12/23/2013 | 13:36 | 12/23/2013 | 14:00 | 0.4 | 0.049444
194 | D1 | High CO emissions required derate to avoid an exceedance on CO. | 659 | FE00 | 9616 | E0 | 12/23/2013 | 14:00 | 12/23/2013 | 17:00 | 3 | 0.55624

## TC2 - 2014
TC2 - 2014
[10 empty] | January | NDC | Period Hours | Available Hours | FOH | EFDH | EFOH | MOH | EMDH | EMOH | Act SH | Fcst SH | MW*Fcst SH | MW*EFOH | MW*Fcst SH | MW*EMOH | MW*Fcst SH | MW*F&MOH | FOR | EFOR | MOR | EUOR | RH | AH | EPDH | MW*PH | MW*(AH-DH) | EAF | MW*(EFOH+EMOH+EPDH) | MW*PH | UU
|  |  | 809 | MW's | [6 empty] | 570 | 8760 | 8760 | 0 | 0 | 0 | 0 |  | 0 | 8760 | 8760 | 4993200 | 0 | 0 | 4993200 | 0 | 4993200 | 0% | 0% | 0% | 0% | 0 | 8760 | 0 | 4993200 | 4993200 | 100% | 0 | 4993200 | 0%
[12 empty] | POH | FOH |  | EFDH |  | EPDH
[11 empty] | PO | 0 | U1 | 0 | D1 | 0 | PD | 0
[13 empty] | U2 | 0 | D2 | 0 | DE | 0
[13 empty] | U3 | 0 | D3 | 0
[13 empty] | SF | 0
Event Number | Event Type | Event Description | MW Available | Start Date | Start Time | End Date | End Time | Actual Event Duration (hours) | Equivalent Outage Duration (hours)

## Summary - TC1 & TC2
TC1 |  |  |  | TC2
| EFOR | EAF | UU |  | EFOR | EAF | UU
January | 10.45% | 89.55% | 10.45% | January
February |  |  |  | February
March |  |  |  | March
April |  |  |  | April
May |  |  |  | May
June |  |  |  | June
July |  |  |  | July
August |  |  |  | August
September |  |  |  | September
October |  |  |  | October
November |  |  |  | November
December |  |  |  | December
YTD | 10.45% | 89.55% | 10.45% | YTD | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | Year | EFOR | EAF | UU
|  |  |  | 2011 | 4.33% | 92.01% | 7.993%
|  |  |  | 2012 | 4.416% | 81.78% | 6.19%
|  |  |  | 2013 | 4.509% | 89.62% | 4.422%
[8 empty] | Year | Actual EFOR (%) | Combusion Related EFOR (%)
[8 empty] | 2011 | 10.32 | 4.3
[8 empty] | 2012 | 17.88 | 4.4
[8 empty] | 2013 | 15.77 | 4.51

## Definitions
AH = Available Hours = PH - ( FOH + MOH + POH )
EFDH = Equivalent Forced Derated Hours = D1 + D2 + D3
EPDH = Equivalent Planned Derated Hours = PD + DE
FOH = Forced Outage Hours = U1 + U2 + U3 + SF
MOH = Maintenance Outage Hours = MO
PH = Period Hours
POH = Planned (Outage Schedule) Hours = PO
NDC = Net Demonstrated Megawatt Capacity
RH = Reserve Hours