## Punch List
| Priority | 1 - Gas Path Cancellation - 7th May |  |  | SPRING OUTAGE CLOSE OUT PUNCH LIST
2 - All Plant Related / Prior to 1st Firing - 15th May
3 - All Outage Work - 30th May
Ref No | SMR No | Priority | Location | Description of Punch Item | Status / Action Outstanding | Owner | Drop Dead Completion Date | Verifying Company | Actual Completion | Verified By
1082 | SMR095 | 1 | WCAH | Fit drains pipework |  | Early | 2014-05-07 | LG&E 21-Apr | 2014-04-30 | M. Whitehouse
1165 | SMR095 | 1 | WCAH | Fit thermocouples electrics |  | Meiners | 2014-05-07 | LG&E 21-Apr | 2014-05-02 | M. Whitehouse
1083 | SMR095 | 1 | WCAH | Fit thermocouples |  | Early | 2014-05-07 | LG&E 21-Apr | 2014-04-25 | M. Whitehouse
1106 | SMR095 | 1 | WCAH | Drain Plugs Missing | A & B sides - 6 off Plugs missing - #3 per side | Early | 2014-05-07 | LG&E 21-Apr | 2014-04-25 | M. Whitehouse
1108 | SMR095 | 1 | WCAH | Remove Redundant Angles | A & B sides - #4 per side | Early | 2014-05-07 | Doosan | 2014-04-25 | M. Whitehouse
1109 | SMR095 | 1 | WCAH | 2A Rear - Reroute Conduit |  | Meiners | 2014-05-07 | Doosan | 2014-04-29 | M. Whitehouse
1107 | SMR095 | 2 | WCAH | External paint touch up | A & B sides - to include I-Beam Supports | Early | 2014-05-07 | LG&E 21-Apr | 2014-04-30 | M. Whitehouse
1188 | SMR095 | 2 | WCAH | Insulation to Finalise on Headers |  | Early | 2014-05-15 | Doosan
1084 | SMR095 | 2 | WCAH | Paint external surface of FD duct local to new flow straighteners |  | Early | 2014-05-15 | LG&E 21-Apr | 2014-04-29 | M. Whitehouse
1170 | SMR095 | 3 | WCAH | Permanent insulation retainers required |  | Early | 2014-05-15 | Doosan
1171 | SMR095 | 3 | WCAH | Temporary floor rigging attachments | Are these to be left or removed - Instructed to remove as per LG&E during walkdown of 1-May | Early | 2014-05-30 | LG&E | 2014-05-05 | M. Whitehouse
1076 | SMR107 | 1 | GAH - Level 16 | 2 Vent lines Re-route to solve lagging foul | Materials available Monday 28-Apr | Early | 2014-05-07 | Doosan | 2014-05-02 | V. Shrapnell
1149 | SMR107 | 1 | GAH- Level 16 | Clash with Air Receiver from CV050 | Air Receiver needs relocating to avoid insulation clash | LG&E | 2014-05-07 | Doosan | 2014-05-01 | V. Shrapnell
1077 | SMR107 | 1 | GAH- Level 16 | Safety valve access platform fouls to pipe insulation | Remedial work in progress (3 locations , 1 complete, 2 WIP) | Early | 2014-05-07 | Doosan | 2014-04-29 | V. Shrapnell
1079 | SMR107 | 1 | GAH Sootblower | Ensure silencer pipework cannot overheat the roof materials | Pipe confirmed as centrally located and additional lagging installed | Early | 2014-05-07 | LG&E | 2014-04-29 | J. Lee
1080 | SMR107 | 1 | GAH Sootblower | Determine the pressure range of the transmitter for the system | Confirmed as 0-1000 psi as per Ron Gratton | Doosan Babcock | 2014-05-07 | Doosan | 2014-04-29 | J. Lee
1081 | SMR107 | 1 | GAH- Level 14 | Insulation at the vertical support steelwork does not allow for movement | Reconfigured to allow for movement | Early | 2014-05-07 | Doosan | 2014-04-25 | V. Shrapnell
1090 | SMR107 | 1 | GAH Sootblower | Support 35711/SSV/2/1610 | Revise support to latest revision | Early | 2014-05-07 | Doosan | 2014-04-26 | V. Shrapnell
1091 | SMR107 | 1 | GAH Sootblower | Support 35710/SSS/1610 | Revise support to latest revision | Early | 2014-05-07 | Doosan | 2014-04-26 | V. Shrapnell
1094 | SMR107 | 1 | Roof | Silencer Flange | #3 Bolts missing | Early | 2014-05-07 | LG&E 21-Apr | 2014-04-26 | V. Shrapnell
1101 | SMR107 | 1 | GAH- Level 16 | 1" Warming Line SSV-1050 - Level 16 | Re-position Spring Support & Bolt Missing | Early | 2014-05-07 | LG&E 21-Apr | 2014-04-26 | V. Shrapnell
1102 | SMR107 | 1 | GAH- Level 16 | Drain Line - Level 16 | Cap Missing - Cannot be located, spurious item | Doosan Babcock | 2014-05-07 | Doosan | 2014-04-30 | V. Shrapnell
1103 | SMR107 | 1 | GAH- Level 17 | Hanger / Electrics Box Clash | Level 16 Column H9 | Early | 2014-05-07 | LG&E 21-Apr | 2014-04-28 | V. Shrapnell
1104 | SMR107 | 1 | GAH- Level 2 | Drain Line - Level 2 | Confirm what type of Valve is fitted - Valve No? This action was to confirm that the final in service purge would not cause a blockage due to any bore restriction in the valve (dependent upon type) but there are strainers upstream so this action can be closed - as per J. Lee email 28-Apr | Doosan Babcock | 2014-05-07 | LG&E | 2014-04-28 | J. Lee
1105 | SMR107 | 1 | GAH Sootblower | Valve Station - Level 2 | Check Drawing for Orifice Plate - Confirmed by SBR / J. Lee as fitted | DB | 2014-05-07 | Doosan | 2014-04-21 | J. Lee
1150 | SMR107 | 1 | GAH - Level 16 | Clash with conduit | Conduit needs relocating to avoid insulation clash | LG&E | 2014-05-07 | Doosan | 2014-04-29 | M. Whitehouse
1151 | SMR107 | 1 | GAH - Level 16 | Have we answered the question regarding the vent - Is it Required? | Required for Boiler Hydro as per S. Hammond | Doosan Babcock | 2014-05-07 | LG&E | 2014-04-26 | J. Lee
1153 | SMR107 | 1 | GAH - Level 16 | Is the bottom exiting pipe downstream of the Safety Valve a Drain? Where should it terminate? | Goes to Transmitter - see Ref 1080 | Doosan Babcock | 2014-05-07 | Doosan | 2014-04-25 | V. Shrapnell
1154 | SMR107 | 1 | GAH - Level 16 | DP small bore pipework from the exit of the Primary Isolator is not fitted |  | Early | 2014-05-07 | Doosan | 2014-04-29 | V. Shrapnell
1156 | SMR107 | 1 | GAH- Level 2 | Spring Hanger bottom thread does not protrude out of the bottom eye bolt |  | Early | 2014-05-07 | Doosan | 2014-04-26 | V. Shrapnell
1157 | SMR107 | 1 | GAH- Level 2 | Small bore DP Impulse Pipework not fitted |  | Early | 2014-05-07 | Doosan | 2014-04-26 | V. Shrapnell
1158 | SMR107 | 1 | GAH- Level 2 | Redundant Pipe Stools need to be removed |  | Early | 2014-05-07 | Doosan | 2014-04-26 | V. Shrapnell
1159 | SMR107 | 1 | GAH- Level 2 | Spring remains gagged under Sootblower Gallery |  | Early | 2014-05-07 | Doosan | 2014-04-26 | V. Shrapnell
1160 | SMR107 | 1 | GAH- Level 2 | Temporary Support is still underneath the existing section |  | Early | 2014-05-07 | Doosan | 2014-04-26 | V. Shrapnell
1162 | SMR107 | 1 | GAH- Level 2 | The design support arrangement local to the Sootblower Manifold requires closing out |  | Early | 2014-05-07 | Doosan | 2014-04-26 | V. Shrapnell
1163 | SMR107 | 1 | GAH- Level 2 | There are CL, VL, SR type supports, all in the same section of pipe. | Is this correct? - Confirmed as correct by Mark Stocker | Doosan Babcock | 2014-05-07 | Doosan | 2014-04-26 | J. Lee
1078 | SMR107 | 2 | Roof | Silencer support steelwork lightning strip to fit |  | Early | 2014-05-15 | LG&E 21-Apr | 2014-05-02 | V. Shrapnell
1095 | SMR107 | 2 | Roof | Silencer Support Legs | Depression in Roof local to Support Legs - Water Trap - American Roofing | Early | 2014-05-15 | Doosan | 2014-05-09 | V. Shrapnell
1096 | SMR107 | 2 | Roof | Silencer Support Legs | Legs have inadequate seal and incorrect seal in one position - American Roofing | Early | 2014-05-15 | LG&E 21-Apr | 2014-05-09 | V. Shrapnell
1161 | SMR107 | 2 | GAH- Level 2 | Damage to Insulation at the #2 Elbows |  | Early | 2014-05-15 | Doosan
1164 | SMR107 | 2 | GAH - Level 1 & 2 | Insulation to Finalise |  | Early | 2014-05-15 | Doosan
1196 | SMR107 | 2 | GAH - Level 16 | Impulse Pipework | Pipework from Rosemount Pressure Differential insufficiently supported | Early | 2014-05-15 | Doosan | 2014-05-02 | V. Shrapnell
1197 | SMR107 | 2 | GAH - Level 16 | Paint Drain Line |  | Early | 2014-05-15 | Doosan | 2014-05-06 | V. Shrapnell
1097 | SMR107 | 2 | Roof | Silencer Pipework | Pipework requires painting local to flange welds (both pipes) | Early | 2014-05-15 | LG&E 21-Apr | 2014-04-27 | V. Shrapnell
1152 | SMR107 | 2 | GAH - Level 16 | Safety Valve Drain requires painting |  | Early | 2014-05-15 | Doosan | 2014-04-25 | V. Shrapnell
1233 | SMR107 | 2 | GAH - Level 14 | PCV 1" Warming Line - Relief to Insulation at Supports | #9 Supports to rework insulation to create reliefs | PetroChem | 2014-05-15 | Doosan
1147 | SMR107 | 3 | Roof | Pipe Seals to Roof | One missing, other incomplete - American Roofing | Early | 2014-05-15 | LG&E 21-Apr
1155 | SMR107 | 3 | GAH - Level 16 | Insulation to Finalise |  | Early | 2014-05-15 | Doosan
1099 | SMR107 | 3 | GAH- Level 16 | Access Platform to Valves - Level 16 | To Fit | Early | 2014-05-30 | LG&E 21-Apr
1100 | SMR107 | 3 | GAH- Level 16 | Safety Valve Setting | LG&E to Co-Ordinate Safety Valve Settings There is NO ACTION for this item - as per J. Lee email 28-Apr |  | 2014-05-30 | LG&E 21-Apr
1198 | SMR107 | 3 | GAH - Level 16 | Bechtel Steelwork - Partly removed Angle | Remove Unsupported Angle - Full Angle reinstated | Early | 2014-05-30 | Doosan | 2014-05-05 | V. Shrapnell
1001 | SMR132 | 1 | Windboxes | Total shut of damper wheel clearance | Cannot be done until Gas path re-issued | Early | 2014-05-07 | Doosan | 2014-04-22 | J. Huntington
1002 | SMR132 | 1 | Burners FS and NFS | Alignment of atomiser swirlers | furnace access req'd | Early | 2014-05-07 | Doosan | 2014-04-25 | J. Huntington
1003 | SMR132 | 1 | All Burners | PA/coal barrel centralising feet require to be locked off | Not done - Furnace access req'd, pre scaffold strip | Early | 2014-05-07 | Doosan | 2014-04-24 | J. Huntington
1004 | SMR132 | 1 | All burners | Atomiser/igniter dimensional setting | Not done - Furnace access req'd, pre scaffold strip | DB assistance from Early | 2014-05-07 | Doosan | 2014-04-26 | J. Huntington
1005 | SMR132 | 1 | Windboxes | Burner support rod miss-alignment | Cannot be done until Gas path re-issued | Early | 2014-05-07 | Doosan | 2014-04-22 | J. Huntington
1007 | SMR132 | 1 | Burners | Purge air/PF pipe clashes | All clashes are being addressed | Early | 2014-05-07 | Doosan | 2014-04-22 | J. Huntington
1010 | SMR132 | 1 | Burners | Beck drives to install | Front Wall all fitted except C2, requires repair | Early | 2014-05-07 | Doosan | 2014-04-23 | J. Huntington
1014 | SMR132 | 1 | Burners | install 3/4 inch sample valves below knife gates | some valves and fittings are still connected to old pipes in yard should be reclaimed and fitted to new. 90% comp New Valves x 10 off ordered 21/4/14 | Early | 2014-05-07 | Doosan | 2014-04-24 | J. Huntington
1016 | SMR132 | 1 | Burner C1 | Runway beam potential to clash with PF to C2 | none | Early | 2014-05-07 | Doosan | 2014-04-17 | J. Huntington
1017 | SMR132 | 1 | Burners | CA bellows, some all thread gags to remove |  | Early | 2014-05-07 | Doosan | 2014-04-22 | J. Huntington
1019 | SMR132 | 1 | Burners | Fit Thermocouples x 4 per burner to install | Required for start up | Early and Meiners | 2014-05-07 | Doosan | 2014-04-27 | J. Huntington
1020 | SMR132 | 1 | Burners | Thermocouples 1 per burner, pad to weld to burner elbow at 6 o'clock position | Required for start up | Early and Meiners | 2014-05-07 | Doosan | 2014-04-27 | J. Huntington
1021 | SMR132 | 1 | Burners | Beck drive brass yoke to check off | JH to do | DB | 2014-05-07 | Doosan | 2014-04-19 | J. Huntington
1022 | SMR132 | 1 | Burners | Crowbar in D4 flame scanner tube | Early to confirm removal | Early | 2014-05-07 | Doosan | 2014-04-19 | J. Huntington
1025 | SMR132 | 1 | Burners | C5 Purge air pipe support rod missing | all thread rod required | Early | 2014-05-07 | Doosan | 2014-04-17 | J. Huntington
1026 | SMR132 | 1 | Burner C deck north end | PF pipe to C2 support rod clashes with gallery to CA damper | mod gallery or hanger rod | Early | 2014-05-07 | Doosan | 2014-04-17 | J. Huntington
1027 | SMR132 | 1 | Burner C deck south end | PF pipe to C4 clashes with gallery to CA damper | shorten gallery hand rail | Early | 2014-05-07 | Doosan | 2014-04-18 | J. Huntington
1028 | SMR132 | 1 | Burners Rear Wall F deck | PF pipe to F4 clashes with gallery to CA damper | shorten gallery hand rail | Early | 2014-05-07 | Doosan | 2014-04-24 | J. Huntington
1029 | SMR132 | 1 | Burner All | Gags in bellows: C1, C4, B5, B4, B3, B2 | Remove | Early | 2014-05-07 | Doosan | 2014-04-22 | J. Huntington
1030 | SMR132 | 1 | Burner All | CA T piece Tapping plugs missing: F2-5 | Fit | V Shrapnell | 2014-05-07 | Doosan | 2014-04-17 | J. Huntington
1031 | SMR132 | 1 | Burners | F1- 1 purge air V/V will clash with PF pipe to F2 | Early forman aware of solution required | Early | 2014-05-07 | Doosan | 2014-04-17 | J. Huntington
1033 | SMR132 | 1 | Burners | D5 PF support to RH side possible clash with purge air pipe | Adjust rods on PF support to give more clearance | Early | 2014-05-07 | Doosan | 2014-04-24 | J. Huntington
1034 | SMR132 | 1 | Burners | Above runway to D3 burner supports to existing pipelines x 2 are hung loose | Re-attach | Early | 2014-05-07 | Doosan | 2014-04-23 | J. Huntington
1041 | SMR132 | 1 | All PF pipes | Knife Gate Valve (KGV) operating wheels missing | Duplicated item - see 1088 | Early | 2014-05-07 | Doosan | 2014-04-29 | I. Fleming
1042 | SMR132 | 1 | C burner deck | PF pipe to C1 bnr, suport collar not sat correctly | Requires tightening | Early | 2014-05-07 | Doosan | 2014-04-27 | J. Huntington
1043 | SMR132 | 1 | C burner deck | C1, C2, C4, C5 burner sample valve missing from below KGV | Remove plugs and fit valves | Early | 2014-05-07 | Doosan | 2014-04-23 | J. Huntington
1044 | SMR132 | 1 | C burner deck | PF pipe to C4 burner, double Constant load supports (CLS) setting near hot, drop rods have insufficient threads to correct, will need to replace with longer rods Same applies to constant load supports to C2 burner north of C1 | reset CLS and replace rods oif required | Early | 2014-05-07 | Doosan | 2014-04-26 | J. Huntington
1045 | SMR132 | 1 | D burner deck | D1 bnr, PF pipe flange bolting incomplete | Complete bolting and tightening | Early | 2014-05-07 | Doosan | 2014-04-19 | J. Huntington
1046 | SMR132 | 1 | D burner deck | Sample valve below KGV missing | Part of valve still in pipe below flange, remove and place below KGV and fit plug in resulting hole | Early | 2014-05-07 | Doosan | 2014-04-23 | J. Huntington
1047 | SMR132 | 1 | D burner deck | PF hanger collar round PF to C1 not sat correctly, | Requires seating correctly and tightening | Early | 2014-05-07 | Doosan | 2014-04-23 | J. Huntington
1048 | SMR132 | 1 | D burner deck | D2, D3, D4, D5 sample valves below KGV broken or missing | Replace valves and parts thereof as required | Early | 2014-05-07 | Doosan | 2014-04-23 | J. Huntington
1049 | SMR132 | 1 | B burner deck | PF hanger collar round PF to D1 not sat correctly, | Requires seating correctly and tightening | Early | 2014-05-07 | Doosan | 2014-04-23 | J. Huntington
1050 | SMR132 | 1 | B burner deck | PF pipe to D1 flexi joint bolt loose | tighten bolts | Early | 2014-05-07 | Doosan | 2014-04-19 | J. Huntington
1051 | SMR132 | 1 | B burner deck | PF pipe to D2 support collar round pipe wrong | Replace incorrect collar. Early forman aware | Early | 2014-05-07 | Doosan | 2014-04-22 | J. Huntington
1052 | SMR132 | 1 | B burner deck | PF hanger collar round PF to D3 not sat correctly, | Requires seating correctly and tightening | Early | 2014-05-07 | Doosan | 2014-04-22 | J. Huntington
1053 | SMR132 | 1 | B burner deck | PF to D3 Flexi joint bolts missing and loose | Fit bolts and tighten all joint bolts | Early | 2014-05-07 | Doosan | 2014-04-19 | J. Huntington
1054 | SMR132 | 1 | B burner deck | PF hanger collar round PF to D4 not sat correctly, | Requires seating correctly and tightening | Early | 2014-05-07 | Doosan | 2014-04-27 | J. Huntington
1055 | SMR132 | 1 | E burner deck | PF hanger collar round PF to A1 not sat correctly, | Requires seating correctly and tightening | Early | 2014-05-07 | Doosan | 2014-04-27 | J. Huntington
1056 | SMR132 | 1 | E burner deck | E2 bnr sample valve below KGV missing barb nozzle | fit new barb | Early | 2014-05-07 | Doosan | 2014-04-23 | J. Huntington
1057 | SMR132 | 1 | E burner deck | PF hanger collar round PF to A4 not sat correctly, | Requires seating correctly and tightening | Early | 2014-05-07 | Doosan | 2014-04-27 | J. Huntington
1058 | SMR132 | 1 | E burner deck | PF hanger collar round PF to A5 not sat correctly, | Requires seating correctly and tightening | Early | 2014-05-07 | Doosan | 2014-04-27 | J. Huntington
1059 | SMR132 | 1 | A deck | A1, A2, A3, A5 sample valves below KGV broken or missing | Replace valves and parts thereof as required | Early | 2014-05-07 | Doosan | 2014-04-23 | J. Huntington
1060 | SMR132 | 1 | A Deck | PF pipe to F3 and F5 PF sample port valves x 3 missing | Replace sample port valves and required connectors | Early | 2014-05-07 | Doosan | 2014-04-23 | J. Huntington
1061 | SMR132 | 1 | A Deck | PF pipe to F5 PF sample port may clash with windbox | Check clearance for sample talking, rotate pF pipe if insufficient | Early | 2014-05-07 | Doosan | 2014-04-23 | J. Huntington
1062 | SMR132 | 1 | F deck | F1, F2, F4, F5 sample valves below KGV broken or missing | Replace valves and parts thereof as required | Early | 2014-05-07 | Doosan | 2014-04-23 | J. Huntington
1071 | SMR132 | 1 | Burners | Swirlers to centralise |  | Early | 2014-05-07 | Doosan | 2014-04-25 | J. Huntington
1072 | SMR132 | 1 | Burners | PF Pipework clashes (could use tracker) |  | Early | 2014-05-07 | Doosan | 2014-04-25 | J. Huntington
1008 | SMR132 | 1 | Burners | Hoses to fit, purge air sight glasses and flame scanners | Waiting for hose supplies delivery TBA. Required for start up | Early | 2014-05-07 | Doosan | 2014-05-01 | J. Huntington
1009 | SMR132 | 1 | Burners | TC connectors to fit, extension pieces to sight glasses, holes in beck drive actuator to fill, sight glasses replace glass | Holes in Beck Drive Rear Wall complete | Early | 2014-05-07 | Doosan | 2014-05-01 | J. Huntington
1175 | SMR132 | 1 | Burners | A Deck to RH side of burner A4, CLS, 2 x drop rods have lock nuts missing on top of spreader bar | Replace lock nuts and tighten | Early | 2014-05-07 | Doosan | 2014-05-02 | J. Huntington
1013 | SMR132 | 1 | Burners | Stroke check dampers and swirlers | Will start after completion of items 1 to 4 | DB - Early | 2014-05-07 | Doosan | 2014-05-01 | J. Huntington
1176 | SMR132 | 1 | Burners | A Deck to LH side of burner A1, CLS, 1 drop rods has lock nuts missing below spreader bar | Replace lock nut and tighten | Early | 2014-05-07 | Doosan | 2014-05-02 | J. Huntington
1086 | SMR132 | 1 | Burners | Rerouting of 13 of 30 coal flame scanner conduits |  | Meiners | 2014-05-07 | Doosan | 2014-04-29 | A. London
1023 | SMR132 | 1 | burners | Burner photographs from furnace as scaffold strip | JH to coordinate with PetroChem | PetroChem | 2014-05-07 | Doosan | 2014-04-30 | J. Huntington
1182 | SMR132 | 1 | Burners | D Deck CLS RH Burner D1: 2 x Lock Nuts Missing above Cross Bar | Fit Lock Nuts | Early | 2014-05-07 | Doosan | 2014-05-02 | R. Elliott
1089 | SMR132 | 1 | Burner C deck north end | PF pipe to C2 clashes with gallery | Cut Handrail | Early | 2014-05-07 | Doosan | 2014-04-24 | J. Huntington
1092 | SMR132 | 1 | PF pipe to D2 burner (B deck south) | PF Sample port clash with windbox, | rotate PF pipe section x 15 deg CCW | Early | 2014-05-07 | Doosan | 2014-04-24 | J. Huntington
1093 | SMR132 | 1 | PF pipe to F4 burner (A deck south) | PF Sample port clash with burner | rotate PF pipe section x 30 deg CCW | Early | 2014-05-07 | Doosan | 2014-04-24 | J. Huntington
1036 | SMR132 | 1 | Burners Rear Wall F deck | E3 and A3, impulse lines have been bent and disconnected | Make good and secure impulse lines | Early | 2014-05-07 | Doosan | 2014-05-01 | J. Huntington
1113 | SMR132 | 1 | Burners | Actuator Operating Airline | Union Couplings to prevent twisting airline - #30 Burners Coupling on cabinet end | Early | 2014-05-07 | Doosan | 2014-05-01 | V. Shrapnell
1192 | SMR132 | 1 | Burners | PF Support (F2) on Level 6 NW: Lock Nuts missing | Replace lock nut and tighten | Early | 2014-05-07 | Doosan | 2014-05-03 | R. Elliott
1193 | SMR132 | 1 | Burners | PF Support on Level 6 NE: Lock Nuts missing | Replace lock nut and tighten | Early | 2014-05-07 | Doosan | 2014-05-03 | R. Elliott
1194 | SMR132 | 1 | Burners | Pipe Support to LHS of D5 | Pipe Support / Hanger to re-attach | Early | 2014-05-07 | Doosan | 2014-05-03 | J. Huntington
1187 | SMR132 | 1 | Burners | Indicator Scales wrong on C5 & D3 Buners | Replace | Early | 2014-05-07 | Doosan | 2014-05-02 | J. Huntington
1200 | SMR132 | 1 | Burners | A-Deck - Instrument Air Line to be re-routed | Awaiting Tee Piece due 5-May | Early | 2014-05-07 | Doosan | 2014-05-05 | J. Huntington
1114 | SMR132 | 1 | Burners | Atomiser Closing Flange | Confirm Fully Bolted - #30 Burners | Early | 2014-05-07 | Doosan | 2014-04-25 | J. Huntington
1115 | SMR132 | 1 | Burner C2 | PF Inspection Nozzle - Ceramic Tile |  | Early | 2014-05-07 | Doosan | 2014-04-24 | J. Huntington
1117 | SMR132 | 1 | Burner D4 | Valve 4250 | Handle Missing | Early | 2014-05-07 | Doosan | 2014-04-25 | J. Huntington
1126 | SMR132 | 1 | Burners | Burner / KGC Bearbox B1 to rotate 90 deg | (LGE punch list) | Early | 2014-05-07 | Doosan | 2014-04-26 | J. Huntington
1074 | SMR132 | 2 | Burners | Modifications to walkways and handrails to allow cold to hot movement |  | Early | 2014-05-15 | Doosan | 2014-04-29 | J. Huntington
1195 | SMR132 | 2 | Burners | C-Row: Plywood Sheeting and Fire Blankets | Remove from above windbox | Early | 2014-05-15 | Doosan
1018 | SMR132 | 2 | Burners | Paint touch up windbox front + welded PF flanges |  | Early | 2014-05-15 | Doosan | 2014-05-06 | I. Fleming
1201 | SMR132 | 2 | Burners | Protection Boards placed over PA Duct EJ's | Remove Protections & Debris etc | Early | 2014-05-15 | Doosan
1032 | SMR132 | 2 | Burners | D5 CA duct repair lagging above burner | PetroChem via Early | Early | 2014-05-15 | Doosan | 2014-05-06 | J. Huntington
1035 | SMR132 | 2 | Burners | Lagging on CA duct will clash with purge air | Trim Lagging | Early | 2014-05-15 | Doosan | 2014-05-06 | J. Huntington
1189 | SMR132 | 2 | Burners | F2 - Scaffold Pole left above burner | Remove Scaffold Pole | PetroChem | 2014-05-15 | LG&E | 2014-05-06 | I. Fleming
1040 | SMR132 | 2 | All PF pipes | Gaggs, temporay steel restraints and lifting equipment in place | After PF pipes have been supported and CLS have been de gagged, remove all steel restraints | Early | 2014-05-15 | Doosan | 2014-05-02 | J. Huntington
1073 | SMR132 | 2 | Burners | Modifications to existing walkways to allow access to the burners | All Potential Clashes Rectirifed / Removed | Early | 2014-05-15 | Doosan | 2014-05-01 | J. Huntington
1207 | SMR132 | 2 | F-4 Burnner | Top of pipe insulation is damaged and weld reapair ove knife valve need touch up paint | Touch Up Paint complete, Insulation repaired | Early | 2014-05-15 | LG&E Gregory Wilson | 2014-05-10 | J. Huntington
1209 | SMR132 | 2 | Burner B Deck | overall on the B deck the lagging on the burner wall need repairing or straightening | Now only one area outstanding - B2 | Early | 2014-05-15 | LG&E Gregory Wilson
1204 | SMR132 | 2 | B-3 Burner | pipe insulation damaged/ beam clamp between 3 &4 need to be removed and safety wire on valve |  | Early | 2014-05-15 | LG&E Gregory Wilson | 2014-05-06 | J. Huntington
1205 | SMR132 | 2 | D-5 Burner | bottom of lagging of burner port & top of pipe insulation is damaged. | CA Pipe Insulation repaired, Lagging complete | Early | 2014-05-15 | LG&E Gregory Wilson | 2014-05-08 | J. Huntington
1206 | SMR132 | 2 | C-1 Burner | bottom of lagging of burner port & top of pipe insulation is damaged. | CA Pipe Insulation repaired, Lagging complete | Early | 2014-05-15 | LG&E Gregory Wilson | 2014-05-08 | J. Huntington
1211 | SMR132 | 2 | Burner C Deck | overall on the C deck the lagging on the burner wall and the coal pipes need touch up paint. | Lagging Complete | Early | 2014-05-15 | LG&E Gregory Wilson
1208 | SMR132 | 2 | F-1 Burner | Port lagging damaged and loose |  | Early | 2014-05-15 | LG&E Gregory Wilson | 2014-05-08 | J. Huntington
1212 | SMR132 | 2 | Burners | F Deck North - CA Damper Actuator Damaged | 1 - Source New Actuator cover plate and fit | Early | 2014-05-15 | Doosan
1210 | SMR132 | 2 | Burner D Deck | overall on the D deck the lagging on the burner wall need repairing and air exhaust pipe is missing | Lagging complete, Air Exhaust Duct - Is this Cooling Air Duct? - Complete | Early | 2014-05-15 | LG&E Gregory Wilson | 2014-05-08 | J. Huntington
1215 | SMR132 | 2 | Burners | Burner TC's, cables and hoses to tidy | clear of potential fouls, trip hazard, path cler to burner front | Early | 2014-05-15 | Doosan
1223 | SMR132 | 2 | Burner B-Deck | B1 - B2, Scaffolding below floor / behind burners to remove |  | PetroChem | 2014-05-15 | Doosan
1213 | SMR132 | 2 | Burners - A Deck | A Deck - #2 timber planks left overhead to LHS of A1 | Remove | Early | 2014-05-15 | Doosan | 2014-05-06 | I. Fleming
1228 | SMR132 | 2 | Burner A-Deck | A2 & A5 - Lagging on bottom section of burner fronts |  | PetroChem | 2014-05-15 | Doosan | 2014-05-10 | J. Huntington
1229 | SMR132 | 2 | Burner E-Deck | E4 - Lagging on burner front |  | PetroChem | 2014-05-15 | Doosan
1024 | SMR132 | 2 | Burners | Remove all debris, lifting equipment, temporary plates and steel | On-going | All | 2014-05-15 | Doosan
1232 | SMR132 | 2 | Burner A3 | PF Clash with Instrumentation Unistrut below deck |  | Early | 2014-05-15 | Doosan | 2014-05-11 | J. Huntington
1217 | SMR132 | 2 | Burners | Plugs Missing on Piping | All burners checked and plugs fitted where applicable | Doosan Babcock | 2014-05-15 | LG&E 22-Apr | 2014-05-29 | J. Huntington
1218 | SMR132 | 2 | B-5 Burner | Broken Valve Stem - Valve to be replaced | New Valve fitted | Early | 2014-05-15 | LG&E 22-Apr | 2014-05-24 | J. Huntington
1220 | SMR132 | 2 | Burner E-Deck | Purge Air - Bolts missing on Pipe Hangers |  | Early | 2014-05-15 | LG&E 22-Apr | 2014-05-28 | J. Huntington
1222 | SMR132 | 2 | E-5 Burner | PF Pipe Hangers digging into lagging | Cutaway relief section installed | PetroChem | 2014-05-15 | LG&E 22-Apr | 2014-05-25 | J. Huntington
1011 | SMR132 | 3 | Burners | Lagging windbox/burner front ring, CA ducts, bellows, and T pieces | some CA ducts started | PetoChem via Early | 2014-05-15 | Doosan
1038 | SMR132 | 3 | Burner Rear Wall E deck | Gallery to CA damper South end removed for PF mods | Return to pre-outage state | Early | 2014-05-30 | Doosan | 2014-04-28 | J. Huntington
1039 | SMR132 | 3 | Burners All | Handrails removed for lifting at north of galleries, temp gates installed | Return to pre-outage state | Early | 2014-05-30 | Doosan | 2014-04-29 | J. Huntington
1037 | SMR132 | 3 | Burner Rear Wall E deck | temp handrail and floor cover centre/rear of gallery roung PF pipe- | Return to pre-outage state | Early | 2014-05-30 | Doosan | 2014-05-02 | J. Huntington
1012 | SMR132 | 3 | Burner galleries | gallery mods and clashes | Duplicate - see 1075 | Early | 2014-05-30 | Doosan | 2014-05-02 | J. Huntington
1180 | SMR132 | 3 | Burners | D Deck North: 2 Temp Steel Lifting Gear Support Beams Welded to Floor | Remove & Repair Floor / Scrap to take down | Early | 2014-05-30 | Doosan | 2014-05-04 | J. Huntington
1181 | SMR132 | 3 | Burners | D Deck North: Handrail East of Gallery, Modified for Burner Instal | Return to pre-outage state | Early | 2014-05-30 | Doosan | 2014-05-06 | J. Huntington
1184 | SMR132 | 3 | Burners | D Deck North: Plate on Floor Next to Lift Well | Remove & Repair Floor | Early | 2014-05-30 | Doosan | 2014-05-06 | J. Huntington
1214 | SMR132 | 3 | Burners | F Deck North - PF Sample Valve Foul by Gallery | Modify Handrail, Splice Ladder to Gallery | Early | 2014-05-15 | Doosan | 2014-05-05 | JH
1203 | SMR132 | 3 | Burners | All Burners | Grease all Swirlers & Damper Drive Couplings - Completed | Early | 2014-05-30 | Doosan | 2014-05-08 | J. Huntington
1216 | SMR132 | 3 | Burners | A Deck North - PF Sample Valve Foul by Gallery | Modify Handrail, Splice Ladder to Gallery | Early | 2014-05-15 | Doosan | 2014-05-06 | J. Huntington
1219 | SMR132 | 3 | Burner A-Deck | PF Pipe Hanger - South End - Digging into lagging |  | PetroChem | 2014-05-15 | LG&E 22-Apr
1221 | SMR132 | 3 | E-3 Burner | PF Pipe Hangers digging into lagging |  | PetroChem | 2014-05-15 | LG&E 22-Apr
1015 | SMR132 | 3 | Burner and OFA galleries | Cooling air ducts and fans | Rear wall E,A & F deck done, Front Wall B & D deck done, C deck (hangers loose) and Level 6 to do | Early | 2014-05-30 | Doosan
1075 | SMR132 | 3 | Burners | Modifications to walkways and handrails which are not affected by boiler movement | On-going work other than thermal expansion clashes that are not outage critical | Early | 2014-05-30 | Doosan
1088 | SMR132 | 3 | Burners | Burner Shut Off Valves - Hand Wheels to install | Purchase and fit ratchets at each position where no handwheel is available and ensure Pins & Safety Wires are in place # 11 Handwheels, # 1 Ratchet Burner Ref's - A1, A3, A4, A5, E1, E2, E3, E4, E5, C1, C2, C5, D3, D4, B1, B2, B3, B5 - Complete F2, F3, F4, F5, | Early | 2014-05-30 | LG&E 22-Apr
1183 | SMR132 | 3 | Burners | C Deck North: Plate on Floor Next to Lift Well | Remove & Repair Floor - Kick Plate outstanding | Early | 2014-05-30 | Doosan
1224 | SMR132 | 3 | Burner B-Deck | Windbox Door - North End | Kick Plate Missing, to replace | Early | 2014-05-30 | Doosan
1225 | SMR132 | 3 | Burner C-Deck | Overhead Light - North End | Return to Original Position | Early | 2014-05-30 | Doosan
1226 | SMR132 | 3 | Burner F-Deck | Overhead Light - F2 | Return to Original Position | Early | 2014-05-30 | Doosan
1227 | SMR132 | 3 | Burner A-Deck | Timber protection on Cable Tray - adjacent to rear stair | Remove | Early | 2014-05-30 | Doosan
1230 | SMR132 | 3 | Burners | Hose Connections on Oil Gins | Replace with Braided Hose | Early | 2014-05-15 | LG&E 22-Apr
1236 | SMR132 | 3 | Burners | Thermocouple Cable Trays | Fit Covers | Meiners | 2014-05-30 | Doosan
1167 | SMR137 | 2 | SA Thermocouples | Insulation to Finalise |  | Early | 2014-05-15 | Doosan | 2014-05-05 | V. Shrapnell
1063 | SMR156 | 1 | OFA - Level 6 | 2 Damaged Expansion Joint cloths | See Ref No 1132 | Early | 2014-05-07 | Doosan | 2014-04-25 | M. Whitehouse
1066 | SMR156 | 1 | OFA - Level 6 | Moving electrics to clear for insulation (Beck drive electrics) |  | Meiners | 2014-05-07 | Doosan | 2014-04-29 | M. Whitehouse
1067 | SMR156 | 1 | OFA - Level 6 | Remove electrics to clear for insulation (Emergency lights, general lights and receptacle electrics) |  |  | 2014-05-07 | Doosan | 2014-04-27 | M. Whitehouse
1112 | SMR156 | 1 | OFA - Level 6 | NW Damper & Expansion Joint | Bolts Missing | Early | 2014-05-07 | LG&E 22-Apr | 2014-04-28 | M. Whitehouse
1128 | SMR156 | 1 | OFA - Level 6 | Windbox Link plates |  | Early | 2014-05-07 | Doosan | 2014-04-28 | M. Whitehouse
1129 | SMR156 | 1 | OFA - Level 6 | Lower Traverse Port to move |  | Early | 2014-05-07 | Doosan | 2014-04-29 | M. Whitehouse
1130 | SMR156 | 1 | OFA - Level 6 | Tube to fit on Aerofoil Division plate |  | Early | 2014-05-07 | Doosan | 2014-04-27 | M. Whitehouse
1131 | SMR156 | 1 | OFA - Level 6 | Remove temp. support / Lifting steelwork (Lower) | Duplicate - see Ref 1069 | Early | 2014-05-07 | Doosan | 2014-04-27 | M. Whitehouse
1133 | SMR156 | 1 | OFA - Level 6 | Fit Flow Element Pipework Connections to Duct |  | Early | 2014-05-07 | Doosan | 2014-04-29 | M. Whitehouse
1135 | SMR156 | 1 | OFA - Level 6 | Install Replacement Transmitter Pipework |  | Early | 2014-05-07 | Doosan | 2014-04-25 | M. Whitehouse
1137 | SMR156 | 1 | OFA - Level 6 | Aerofoil Division plate extension |  | Early | 2014-05-07 | Bechtel | 2014-04-27 | M. Whitehouse
1138 | SMR156 | 1 | OFA - Level 6 | Change "Toggle" Duct mandoors SE & NE corners |  | Early | 2014-05-07 | Doosan | 2014-04-29 | M. Whitehouse
1139 | SMR156 | 1 | OFA - Level 6 | Connections to fit O/T Post & Support Strap SW & NW Corners |  | Early | 2014-05-07 | Doosan | 2014-04-29 | M. Whitehouse
1140 | SMR156 | 1 | OFA - Level 6 | Lower internal bracings to install SW & NW corners | The horizontal stiffeners indicated on drg - B250/32199/0015 & 0017 – Section A-A need not be fitted as there are existing horizontal stiffeners in both A & B side sec air ducts. - as per email M. Stocker 28-Apr | Early | 2014-05-07 | Doosan | 2014-04-28 | M. Stocker
1145 | SMR156 | 1 | OFA - Level 6 | OFA Register Sling Rod to fit - SE Corner |  | Early | 2014-05-07 | Doosan | 2014-04-28 | M. Whitehouse
1146 | SMR156 | 1 | OFA - Level 6 | Mandoor Port Seal Welds |  | Early | 2014-05-07 | Doosan | 2014-04-29 | M. Whitehouse
1132 | SMR156 | 1 | OFA - Level 6 | Repairs to SE & NE Expansion Joints |  | Early | 2014-05-07 | Doosan | 2014-04-30 | M. Whitehouse
1177 | SMR156 | 1 | OFA - Level 6 | SE Damper & Expansion Joint | #2 Bolts Missing - Inboard side - Cannot be fitted due to local stiffeners | Early | 2014-05-07 | Doosan | 2014-04-30 | M. Whitehouse
1134 | SMR156 | 1 | OFA - Level 6 | Fab & Fit New Flow Element Pipework |  | Early | 2014-05-07 | Doosan | 2014-05-02 | M. Whitehouse
1142 | SMR156 | 1 | OFA - Level 6 | Cold set OFA SA Damper, Swirler and PA Damper |  | Early | 2014-05-07 | Doosan | 2014-05-02 | M. Whitehouse
1185 | SMR156 | 1 | OFA - Level 6 | OFA SW - Fit Stainless Steel Pins | As per M. Stocker email 30-Apr | Early | 2014-05-07 | Doosan | 2014-04-30 | M. Whitehouse
1186 | SMR156 | 1 | OFA - Level 6 | Toggle Access Doors | Remove Section of Chequer Plate in front of each Toggle Access Door | Early | 2014-05-07 | Doosan | 2014-05-02 | M. Whitehouse
1127 | SMR156 | 1 | OFA - Level 6 | Clear Bore Peizo tubes |  | Early | 2014-05-07 | Doosan | 2014-05-02 | M. Whitehouse
1136 | SMR156 | 1 | OFA - Level 6 | Ensure all Temp. Brackets & steelwork removed |  | Early | 2014-05-07 | Doosan | 2014-05-02 | M. Whitehouse
1172 | SMR156 | 1 | OFA - Level 6 | Repair damage to aerofoil instrument lines on each upper burner level (below OFA level) |  | Early | 2014-05-07 | Doosan | 2014-05-02 | M. Whitehouse
1173 | SMR156 | 1 | OFA - Level 6 | Inspect the bellows units on the burner decks below the OFA level for damage |  | Early | 2014-05-07 | Doosan | 2014-05-02 | M. Whitehouse
1199 | SMR156 | 1 | OFA - Level 6 | Close Flow Straightener Plate Doors |  | Early | 2014-05-07 | Doosan | 2014-05-02 | M. Whitehouse
1110 | SMR156 | 2 | OFA - Level 6 | 90 Deg Elbows - all 4 corners | Confirm Minimum Clearance between Cladding and Galleries for Thermal Expansion - Minimum clearance confirmed by Mark Stocker | Doosan Babcock | 2014-05-15 | Doosan | 2014-04-26 | J. Lee
1143 | SMR156 | 2 | OFA - Level 6 | Grab Handles above mandoors | Complete on SE & NE | Early | 2014-05-07 | Doosan | 2014-04-29 | M. Whitehouse
1166 | SMR156 | 2 | OFA - Level 6 | Remove temp. support / Lifting steelwork (Upper) | Duplicate - see Ref 1070 | Early | 2014-05-15 | Doosan | 2014-04-27 | M. Whitehouse
1178 | SMR156 | 2 | OFA - Level 6 | NE Elbow - Insulation Clash | Cladding tight to Gallery and Gussett plate | Early | 2014-05-15 | Doosan | 2014-05-01 | M. Stocker
1144 | SMR156 | 2 | OFA - Level 6 | Mandoor "Stops" SE & NE next to Dampers | Not Required - Installation of Handrails negates requirement | Early | 2014-05-07 | Doosan | 2014-05-02 | M. Whitehouse
1202 | SMR156 | 2 | OFA - Level 6 | SE Elbow - Insulation Clash | Recess Insulation as per M. Stocker email request of 2-May | PetroChem | 2014-05-07 | Doosan | 2014-05-05 | M. Whitehouse
1179 | SMR156 | 2 | OFA - Level 6 | NW Elbow - Insulation Clash | Cladding tight to Cable - check for movement Cable moved, now clear of duct | Doosan Babcock | 2014-05-15 | Doosan | 2014-05-02 | I. Fleming
1064 | SMR156 | 2 | OFA - Level 6 | Modifications to walkways and handrails to allow cold to hot movement |  | Early | 2014-05-15 | Doosan | 2014-05-08 | M. Whitehouse
1087 | SMR156 | 2 | OFA - Level 6 | OFA Dampers - Safety Mesh for Operating Arms |  | Early | 2014-05-15 | LG&E 22-Apr
1111 | SMR156 | 2 | OFA - Level 6 | Aerofoils / Instruments | Leak Check - Require Fans in Service | Early | 2014-05-15 | LG&E 22-Apr
1234 | SMR156 | 2 | OFA - Level 6 | Beck Drive / Handrail clash | Ensure Boiler Movement clearance around Beck Drives | Early | 2014-05-15 | Doosan
1174 | SMR156 | 3 | OFA - Level 6 | Paint Hydrojet pipework adjacent to NW OFA Duct |  | Early | 2014-05-30 | Doosan | 2014-05-07 | M. Whitehouse
1141 | SMR156 | 3 | OFA - Level 6 | Gallery mods to all four corners (door access etc) |  | Early | 2014-05-15 | Doosan
1065 | SMR156 | 3 | OFA - Level 6 | Modifications to walkways and handrails which are not affected by boiler movement |  | Early | 2014-05-30 | Doosan
1068 | SMR156 | 3 | OFA - Level 6 | Refit in new location, electrics to clear for insulation (Emergency lights, general lights and receptacle electrics) |  | Meiners | 2014-05-30 | Doosan | 2014-05-10 | M. Whitehouse
1231 | SMR156 | 3 | OFA - Level 6 | PF Slings | Plate in excessive floor guide holes / fit handrails | Early | 2014-05-30 | Doosan
1235 | SMR156 | 3 | OFA - Level 6 | Beck Drive Access Platform | Maintenance Platform required around and below Beck Drive, including Handrails | Early | 2014-05-30 | Doosan
1116 | SMR158 | 1 | Burners - Electrical | Igniter Power Cables | Grounding Cable to re-instate - #30 Burners | Meiners | 2014-05-07 | LG&E 22-Apr | 2014-04-27 | A. London
1191 | SMR158 | 1 | F deck | Electrical Box above F3 Burner | Close Box Door | Meiners | 2014-05-07 | Doosan | 2014-05-04 | I. Fleming
1069 | SMR167 | 2 | OFA - Level 6 | Remove temporary lifting steelwork below ducting |  | Early | 2014-05-15 | Doosan | 2014-05-02 | M. Whitehouse
1070 | SMR167 | 3 | OFA - Level 6 | Remove temporary lifting steelwork above ducting |  | Early | 2014-05-15 | Doosan | 2014-05-09 | M. Whitehouse
1168 | SMR169 | 2 | SCR Nox Probe | Insulation to Finalise |  | Early | 2014-05-15 | Doosan | 2014-05-05 | V. Shrapnell
1085 | SMR170 | 1 | Roof Fan | Reconnect Fan Electrics and ensure Fan runs |  | LG&E | 2014-05-07 | Doosan | 2014-05-03 | V. Shrapnell
1098 | SMR170 | 2 | Roof Fan | Fan Structure | Paint Areas where grinding scars are | Early | 2014-05-15 | Doosan | 2014-04-26 | V. Shrapnell
1148 | SMR170 | 2 | Roof Fan | Fit lightning strip |  | Early | 2014-05-15 | LG&E 21-Apr | 2014-05-02 | V. Shrapnell
1006 | SMR172 | 1 | Burners | Purge air orifice plates | 20% complete | Early | 2014-05-07 | Doosan | 2014-04-29 | V. Shrapnell
1118 | SMR172 | 1 | Burner B5 | Purge Air Valve | Spindle Broken New VV fitted | Early | 2014-05-07 | Doosan | 2014-04-23 | V. Shrapnell
1119 | SMR172 | 1 | Burner E2 | Purge Air Hanger | Bolts Missing | Early | 2014-05-07 | Doosan | 2014-04-27 | V. Shrapnell
1190 | SMR172 | 1 | F deck | Purge Air Support adjacent to F3 | Support to be re-aligned | Early | 2014-05-07 | Doosan | 2014-05-04 | I. Fleming
1124 | SMR174 | 1 | Mill Tell Tales | Various "U" bolts missing |  | Early | 2014-05-07 | Doosan | 2014-04-26 | V. Shrapnell
1125 | SMR174 | 1 | Mill Tell Tales | Pipe requires painting |  | Early | 2014-05-07 | Doosan | 2014-04-26 | V. Shrapnell
1169 | SMR174 | 2 | Mill Tell Tales | Insulation to Finalise |  | Early | 2014-05-15 | Doosan
1120 | SMR175 | 1 | Purge Air Fan | Loose threaded plugs |  | Early | 2014-05-07 | Doosan | 2014-04-26 | V. Shrapnell
1121 | SMR175 | 1 | Purge Air Fan | Valve Hand Wheels missing (substituted with wire) | Action closed as per J. Lee email 28-Apr | Early | 2014-05-07 | Doosan | 2014-04-28 | J. Lee
1123 | SMR175 | 1 | Purge Air Fan | Check for loose fasteners in flanges | Action closed as per J. Lee email 28-Apr | Early | 2014-05-07 | Doosan | 2014-04-28 | J. Lee
1122 | SMR175 | 3 | Purge Air Fan | Pipe requires painting |  | Early | 2014-05-30 | Doosan | 2014-04-30 | J. Lee
1237
1238
1239
1240
1241
1242
1243
1244
1245
1246
1247
1248
1249
1250
1251
1252
1253