## Summary
Trimble County Unit 2
Status with LG&E on Doosan Related Issues | [8 empty] | "GREEN" Line item (WN/PL) moved from previous category
"RED" Within Cells indicate LG&E Changes
| WN # | status w/ owner | description | LG&E $ invoiced and paid | LG&E $ invoiced not paid | LG&E $ intend to invoice | LG&E claim $ | Comments
|  |  |  | A | B | C | D = B + C
1 | WNs items closed with the Owner
| WN 007 | closed | APH basket material found in 2A flyash slurry pump | 2573 | 0 | 0 | 0
| WN 014 | closed | APH basket material found in 2B flyash slurry pump | 1488 | 0 | 0 | 0
| WN 015 | closed | The Sootblower Main Steam Supply valve is sticking while traveling open or closed at an indicated 25%. | 0 | 0 | 0 | 0
| WN 017 | closed | The 2F coal mill PA flow transmitter 2-CB-FT-345F found to be non-functional. | 496 | 0 | 0 | 0
| WN 030 | closed | Valves 2-BLS-V616 & V617 on the eight landing between the boiler and economizer are leaking at the valve body. | 0 | 0 | 0 | 0
| WN 043 | closed | The volume booster for sootblower pressure control valve 2-SB-CV-050 has blown a diaphragm | 1286.5 | 0 | 0 | 0
| WN 050 | closed | Hydrojet 4 (2D) water supply isolation valve 2-SB-307D leaks at the valve flange. | 496 | 0 | 0 | 0
| WN 051 | closed | The sootblower safety valve 2-SB-PSV-901 is leaking through | 16949 | 0 | 0 | 0 | Bechtel has paid this Invoice.
| WN 062 | closed | Oil leaking from where the 2nd stage blades meet the rotor hub. | 0 | 0 | 0 | 0
| WN 070 | closed | The 2-SB-PRV-901 Sootblower Header Safety Valve is leaking through. | 15624 | 0 | 0 | 0
| WN 072 | closed | SB-CV-050 periodically will not respond | 0 | 0 | 0 | 0
| WN 084 | closed | The cage drain blowdown isolation valve (2-BLS-MOV-516) is leaking at the body gasket | 14010 | 0 | 0 | 0
| WN 118 | closed | All the secondary air dampers need calibrating along with adjustments to the position of the damper blades. | 10540 | 0 | 0 | 0
| WN 085 | closed | The sootblower header on the 16th landing has been damaged due to the failure of the 2-SB-CV-050 valve to maintain system pressure below the safety valve set point of 610PSI. | 0 | 0 | 0 | 0
| WN 086 | closed | Sootblower header manual isolation valve 2-SB-V001 is binding. | 0 | 0 | 0 | 0
| WN 087 | closed | Volume boosters on the 2-SB-CV-050 SB header control valve are blowing air past the diaphragms. | 0 | 0 | 0 | 0
| WN 123 | closed | Secondary Air and Overfire Air damper bearings damaged | 0 | 0 | 0 | 0
| WN 133 | closed | hydraulic oil leak on the 2B FD fan | 2976 | 0 | 0 | 0
| WN 135 | closed | 2A & 2B ID fan discharge ducts at the transition piece from round to square duct leaking flue gas (leaks were from expansion joints) | 0 | 0 | 0 | 0
| WN 137 | closed | The 2-SB-PSV-901 SB Header safety valve is leaking through as low as 21% open on the 2-SB-CV-050. | 10421 | 0 | 0 | 0
| WN 143 | closed | 2-BLS-V260 leaking at the bonnet flange west of "F" burner deck. | 0 | 0 | 0 | 0
| WN 146 | closed | The 2-BLS-V677 valve is leaking at a body bolt. | 0 | 0 | 0 | 0
| WN 147 | closed | The hoses on the HJ2 and HJ4 Hydrojet Sootblowers are broken and leaking water on to electrical equipment. | 279 | 0 | 0 | 0
| WN 156 | closed | The 2-AT-V005 Manual Isolation valve to the 2-AT-CV-120B Valve leaking at the valve body pressure seal on landing 16 | 0 | 0 | 0 | 0
| WN 158 | closed | Excessive air leakage from each Negative Pressure Bellows on each Hydrojet | 0 | 0 | 0 | 0
| WN 182 | closed | Leaking water supply hose on hydrojet sootblower #3. | 217 | 0 | 0 | 0
| WN 194 | closed | The 2-BLS-MOV-597 valve or storage vessel sub-critical pressure warming drain valve is leaking at the body gasket | 0 | 0 | 0 | 0
| WN 199 | closed | 2A thru 2F PA Fan duct flow conditioners prior to the flow elements are plugged with ash and foreign material | 15596 | 0 | 0 | 0
| WN 200 | closed | Replace blades on the 2B FD Fan | 215049 | 0 | 0 | 0
| WN 208 | closed | 2A & 2B SCR Inlet Duct Bracing is bent and bowed. | 0 | 0 | 0 | 0
| WN 209 | closed | Boiler throat refractory is falling into the SSC. | 46276 | 0 | 0 | 0
| WN 222 | closed | Furmanite to eliminate the high pressure water leak of the 2-AT-V005 located on the 16th landing. | 2940 | 0 | 0 | 0
| WN 234 | closed | The Hydrojet Water Pumps common discharge pipe hangers not functioning as designed. | 0 | 0 | 0 | 0
| WN 262 | closed | The Expansion Joint on the Hot Primary Air ductwork on the vertical run from the APH down to the 505 elevation is torn at the joint. | 0 | 0 | 0 | 0
| WN 271 | closed | Check operation of sootblower drain valve to make sure the drain temp is set per OEM request to allow the blower to start. | 8491 | 0 | 0 | 0
| WN 281 | closed | Failed feed tube at Sootblower IK 80 weld | 6014 | 0 | 0 | 0
| WN 283 | closed | The cold end by-pass seals on both units 2A & 2B APHs have been mangled | 0 | 0 | 0 | 0
| WN 304 | closed | The Hydrojet Water Pumps common discharge pipe hangers are not functioning as designed | 0 | 0 | 0 | 0
| WN 312 | closed | 2-SB-MOV-514B sootblower drain valve will not operate | 0 | 0 | 0 | 0
| WN 329 | closed | Howden TA has recommended the following work to maintain warranty: A.) Replace all four bearing liners. PN-132425. B.) Replace thrust plates on the IB bearings of both PA fans. C.) Replace plunger screw assembly on all bearings of both PA Fans. D.) Replace bearing housing on the 2B OB PA Fan. E.) Replace all dust seals on all bearings (Auxilliary seal corks) F.) Stone Thrust collars with fine stone. G.) Polish shaft journals with 400 grit or fineremery cloth. H.) Blue check contact between new liners and housings and lap as necessary with fine lapping compound. I.) Check motor alignment and align as necessary. J.) Pressure check water cooling piping before installing housing cap. | 25242.72 | 0 | 0 | 0
| WN 330 | closed | The "A" side economizer outlet duct have damaged growth guides and structural beams. | 0 | 0 | 0 | 0
| WN 334 | closed | Install thermal Growth markers for SCR. | 0 | 0 | 0 | 0
| WN 335 | closed | Damage to several of the coal mill PA flow elements and three out of the six flow conditioners are corroding severely. | 0 | 0 | 0 | 0
| WN 347 | closed | Coal mill hot PA dampers difficult to operate | 0 | 0 | 0 | 0
| WN 348 | closed | Repair the seal on the lower header casing that split | 0 | 0 | 0 | 0
| WN 352 | closed | Econimizer vent line leaking inside duct | 0 | 0 | 0 | 0
| WN 360 | closed | 2-BLS-V716 Separator outlet manual vent valve is leaking through and has a leak in the weld on the downstream side of the valve | 0 | 0 | 0 | 0
| WN 361 | closed | Leaks in the expansion joints on the PA Duct just South of the SSC running West to East. | 0 | 0 | 0 | 0
| WN 372 | closed | Inspec SA & OFA dampers and drives for their correct position, correct any mis-alignments and ensure that the proper torque is applied to all Beck drive arms to prevent slippage. | 0 | 0 | 0 | 0
| WN 373 | closed | Hole in Unit 2 expansion joint on the hot PA duct west of the economizer hopper 234 | 0 | 0 | 0 | 0
2 | WNs items open w/owner - work complete - payment pending
| WN 250 | closed | The 2-AT-V002 manual isolation valve is leaking at the body gasket | 0 | 0 | 961.5 | 961.5 | Work performed by Owner
| WN 275 | closed | 2-BLS-V611 Econ. Inlet Flow transmitter 105A Downstream Blk Vlv. valve is leaking at bonnet gasket | 0 | 0 | 4471.5 | 4471.5 | Work performed by Owner
| WN 285 | closed | The 2A & 2B ID Fan Stall & D/P probes/sensing lines are plugging up | 0 | 0 | 98496.82 | 98496.82 | Work performed by Owner [Note: Permanent access to these probes remain an open issue under a separate PL.]
| WN 300 | closed | Install protective insulation blankets on all TC2 core air tubes to provide safety and personnel protection | 1320.52 | 0 | 2418.12 | 2418.12 | Work performed by Owner
| WN 343 | open | Boiler tubes in affected areas appeared to be corroded and pitted. | 0 | 34131.21 | 1805.91 | 35937.12 | Work complete
| WN 346 | closed | wallbox cardon joint assembly mounting bolts had eroded on the furnace side | 40336 | 0 | 13103.15 | 13103.15 | Work performed by Owner
| WN 351 | open | 2V-668A D/P Regulator leaking NH3 at top of regulator | 0 | 620 | 0 | 620 | Work complete
| WN 415 | open | 2-CB-CD-507A&B Hot Primary Air isolation dampers fail to close, damper seizes up. | 0 | 24195.12 | 0 | 24195.12 | Work complete
| WN 419 | open | All 30 burner tile sets in the "C" and "F rows have experienced severe tile loss and wear in the 10 o'clock and 4 o'clock positions. | 0 | 9100 | 0 | 9100 | Work complete
| WN 463 | open | Mill inerting steam MOVs are leaking through | 0 | 21701.64 | 0 | 21701.64 | Work complete
3 | WNs and PL items open w/owner - working
| WN 325 | open | High energy arc current detectors for ignitors are unrealiable and have to be jumped out. | 0 | 0 | 0 | 0 | Open - working w/ DNOx burner
| WN 406 | open | Flame Scanners on TC2 do not work correctly | 0 | 0 | 66131.75 | 66131.75 | Open - working w/ DNOx burner
| WN 421 | open | Both current hydro-jet pumps are not achieving desired GPM flow rates of 220 GPM | 0 | 0 | 0 | 0 | Open - working (hanger issues)
| WN 425 | open | Corrosion and cracking of the membrane along the line where the underneath side of the upper arch meets the rear wall of the furnace | 0 | 13088.95 | 0 | 13088.95 | Open - repair made; pending permanent correction
| WN 441 | open | Water Coil Air Heaters (WCAH) system needs to be corrected | 0 | 0 | 0 | 0 | Open - working
| WN 443 | open | Inspection of the 2A Ammonia pump removed from service indicated damage to all stages of the pump. | 0 | 15155.15 | 0 | 15155.15 | Open - working
| WN 452 | open | No capability to extract moisture from the steam inerting lines just prior to entering the PA duct at each mill. | 0 | 0 | 0 | 0 | Open - working
| WN 461 | open | Freezing of the Water Coil Air Heaters | 0 | 0 | 15370.55 | 15370.55 | Open - working
| WN 466E | open | 2A Mill Seal Air Fan Damper is not closing all the way, causing fan motor to rotate backwards. | 0 | 0 | 0 | 0 | Open - working
| WN 471E | open | Hydrojet Pumps piping hangers are severely bowed and not properly supporting the piping. | 0 | 0 | 0 | 0 | Open - working
| WN 475E | open | HJ1 Hydrojet Hose Failure | 0 | 0 | 1000 | 1000 | Open - working $1000 in Owner labor + cost of material if not supplied by Contractor, for this rewarranty item.
| PL 30556 | open | INSTALLATION OF FULLY FUNCTIONAL CLEAN OUT PORTS AT EACH BURNER THAT WILL ENABLE ON-LINE DESLAGGING OF BURNERS | 0 | 0 | 0 | 0 | Pending operation of DNOx burners
| PL 30382 | open | demonstratecombustion system's ability to burn fuel over design range | 0 | 0 | 417 | 417 | Open - working w/ DNOx burner
4 | WNs items open w/owner - pending LG&E verification
| WN 448 | open | Several PF lines with deposition in the horizontal legs adjacent to the vertical rises to the firing floors | 0 | 0 | 0 | 0 | Work not complete - Pending Final Resolution of Combustion System.
| WN 451 | open | The mill temperature controls do not automatically maintain the mill outlet temperature at or near the 150 degree set point. | 0 | 0 | 0 | 0 | Work not complete - Pending Final Resolution of Combustion System.
| WN 454 | open | Nine boiler roof tubes failed | 0 | 0 | 1200000 | 1200000 | Work not complete - to perform in Spring Outage
| WN 458 | open | Verify capacity of SCR for the amount of NOx produced by the boiler. | 0 | 0 | 0 | 0 | Work not complete - Pending Final Resolution of Combustion System.
| WN 462 | open | The Pyrite conveyance systems for the mills do not have sufficient capacity to convey the combined amounts of pyrite and coal entering the system when a mill trips. | 0 | 0 | 0 | 0 | Work not complete
5A | WNs and PL items (Completed) wholly or partially disputed w/owner
| WN 163 | disputed | Clean coils on WCAH | 0 | 0 | 5518 | 5518
| WN 294 | disputed | 2A hydrojet pump inlet check valve is bad and water is getting into the oil and leaking out | 0 | 7022 | 2146.74 | 9168.74
| WN 336 | disputed | waterwall material loss by what looks like corrosion in two areas on the left and right wall at the future locations of the water cannons opening in the middle of each wall at the middle burner elevation. | 0 | 19789.47 | 142322.54 | 162112.01 | Work complete - payment pending to LG&E; need invoice support documentation
| WN 341 | disputed | Water wall tube leaks in the elevation 637 field weld line | 0 | 371648.75 | 830359.93 | 1202008.68
| WN 344 | disputed | Missing tiles from burner fronts | 0 | 35565.63 | 0 | 35565.63
| WN 362 | disputed | One of the 2B Air Heater outer baskets is coming apart and needs to be replaced (damaged due to fire) | 0 | 91754.7 | 0 | 91754.7
| WN 426 | disputed | The #2 roller in the 2D Mill was unable to be turned and the Alstom TA recommended that the roll be removed from the mill to be inspected | 0 | 36237.14 | 0 | 36237.14
| WN 433 | disputed | Replace the 2B Hydrojet Pump mechanical seal. | 0 | 9513.48 | 0 | 9513.48
| PL 27481 | disputed | No access to core air dampers control valves 530 N and S ends of burner decks valves need way to bleed air off for carding | 0 | 0 | 0 | (part of PL 1700)
| PL 30351 | disputed | On the top 2 burners levels (F&A) along the rear wall, access doors need to be free of obstacles. | 0 | 0 | 0 | (part of PL 29386)
| PL 30385 | disputed | Provide additional ventilation air circulation in stagnant areas of boiler and SCR |  |  | 399434 | 399434
5B | WNs and PL items (Not Completed) wholly or partially disputed w/owner
| WN 105 | disputed | The overhead hoist installed for removal of the 2A ID fan regulating hub does not provide enough clearance over all ductwork | 0 | 0 | 0 | TBD
| WN 201 | disputed | Pull and inspect A2 and C3 burner tubes | 0 | 0 | 0 | TBD
| WN 437 | disputed | excessive wear of mills in the pulverized fuel handling system | 0 | 0 | 0 | TBD
| WN 442 | disputed | Lifting capacity problems with the supplied mill area crane hoist | 0 | 0 | 0 | TBD
| WN 444 | disputed | The originally supplied water cannon system does not reach the lower portion of the furnace. | 0 | 0 | 0 | TBD
| WN 459 | disputed | Make corrections as needed to provide ID fan margin consistent with specification | 0 | 0 | 0 | TBD
| PL 28041 | disputed | All of the following need to have access and have verified that all of the control end compartment cap can be taken off: 2-CB-CD-330A-MOD, 2-CB-CD-330B-MOD, 2-CB-CD-330C-MOD, 2-CB-CD-330D-MOD2-CB-CD-330E-MOD2-CB-CD-330F-MOD |  |  |  | TBD | Incl w/PL 1700
| PL 30228 | disputed | Make repairs to cranes and hoists per report issued from walkdown | 0 | 0 | 91583 | 91583 | (part of PL issue w/ Doosan)
| PL 30481 | disputed | convert Boiler access doors in the back pass to observation doors. Unable to do visual check for pluggage. Exhibit A supports requirement for visual inspection. | 0 | 0 | 0 | TBD
| PL 28486 | disputed | The SCR and SCR inlet duct lagging does not have a thermal break meeting the spec, Exhibit A, Section 12.10.4 | 0 | 0 | 0 | TBD
| PL 30473 | disputed | Address the differential pressure in the power block from inside to outside. The lower pressure inside creates large drafts inward, pulling cold air into the building which could create freezing problems | 0 | 0 | 0 | TBD
| PL 30552 | disputed | Sootblower System - all the control wire needs to be shielded instead of using relays to take care of the noise | 0 | 0 | 0 | TBD
| PL 24893 | disputed | 2-FC-PDT-037 A-7 BOWL DP NEED 3 WAY VALVES WITH AIR SUPPLY TO BLOW OUT PORTS | 0 | 0 | 0 | TBD | Owner willing to drop this item
| PL 27480 | disputed | FUEL OIL ATOMIZING AIR AND FUEL OIL GUN INSTRUMENT AIR SUPPLIES NEED AIR BLEED OFFS AFTER ISOLATION VALVES FOR CARDING PURPOSES. ALL BURNERS | 0 | 0 | 0 | TBD | Owner willing to drop this item
| PL 30374 |  | A' INDUCED DRAFT FAN MOTOR NEEDS TO BE CLEANED AS OIL HAS BEEN LEAKING ON MOTOR WINDINGS | 0 | 0 | 0 | TBD
| PL 30389 |  | PROVIDE WEATHER HOOD AND SIDING FOR ID FAN COOLING FANS AND OIL CABINETS. SAFETY CONCERN IN WET OR FREEZING CONDITIONS (LAST WINTER PLASTIC COVERS WERE IN PLACE) NEED A PERMANENT STRUCTURE | 0 | 0 | 0 | TBD