## Sheet1
Plant | Trimble | Unit | 2
Event Date | 2014-06-29 | Event Time | 0:45
EVENT
Prepared By | Phil Rabe | Date | 2014-07-08
TC2 was removed from service due to turbine EHC system issues. The 2A MSV had closed during a valve test the previous morning and failed to re-open.
OPERATIONS EVALUATION
Prepared By | Phil Rabe | Date | 2014-07-09
On 6/29/14 the unit was removed from service due to issues with the turbine EHC system. The 2A MSV had failed to re-open the previous morning following a valve test. After I/E performed trouble shooting and replacement of the MSV servo, it was discovered that a TCS 'master reset' had to be initiated to send a 4-20 mA control signal output to it. It was decided to wait and perform the master reset while the unit was down for scheduled deslag. The TCS was 'master reset' sucessfully and control current was re-established to the servo, but the valve still remained closed. The fast acting solenoid (FAS) located on the valve appeared to be dumping the actuator hydraulic supply based on the valve hydraulic drain line temperature. The decision was made to remove the unit from service to allow replacement of the FAS. While dropping load to remove the unit from service, it was noticed that the 2A CV was not traveling closed. Load dropped quickly from 230MW to 100MW and the turbine shutdown sequence initiated. At 80 MW the turbine tripped. The 2A CV remained open along with the 2B MSV. The generator line breaker remained closed and the unit stayed at 3600 rpm. After a few minutes, the generator reverse power 2 relay picked up and tripped the line breakers. Turbine speed began to decay on the machine with the turbine HP and LP bypass valves closed and dropped to 3150 rpm. The LP bypass valve opened up as normal following a turbine trip, but with the 2B MSV open along with the 2B CV open, a path for steam flow through the HP turbine to the condenser was established and the turbine began to pick up speed. The EHC pumps were tripped from service, the boiler MFT'd and the 2A PORV was opened. Turbine speed reached 3969 rpm before I/E personel manually actuated the 2B MSV FAS causing the valve to go closed. EHC trip pressure was slow to decay and was at 1300 psi when the valve closed. It began to re-open when the FAS was released, and the FAS had to be manually held open until EHC trip pressure was bled off. While reviewing data from the event, some question as to whether the HP and LP turbine bypass valves operated properly arose. Further evaluation of the logic for these controls needs to be done.
MAINTENANCE EVALUATION
Prepared By |  | Date
RECOMMENDATIONS
Prepared By |  | Date | 2014-06-18
WO #s |  | Date Written
Forward results to Operation for information to pass on to shifts and retraining if necessary.
Forward results to appropriate Maintenance shop for information to pass on to shifts and retraining if necessary.
Brown | 1
Cane Run | 2
Ghent | 3
Green River | 4
Mill Creek | 5
Trimble | 6
7
8
9
10
11
12
13

## Sheet2
Brown
Cane Run
Ghent
Green River
Mill Creek
Trimble