## Big Sandy Unit 2 Template
Plant Decommissioning | [8 empty] | Classification Key:
Engineering and Operational Requirements | [8 empty] | M = Mandatory by law, code or standard = In Scope R = Recommended to achieve program expectations = In Scope C = For Plant consideration; not required to achieve program expectations = Out of Scope INR = Investigated, but not required = Out of Scope
Big Sandy Unit 2 Site Evaluation Template - Rev.7/28/14
[10 empty] | Internal Labor | [5 empty] | Outside Services |  |  |  | Materials | [11 empty] | Duration (weeks) | Predecessor, if any | Milestone Finish Date
[10 empty] | Hours |  | Cost | [8 empty] | Total $ | [18 empty] | O&M |  |  |  | Removal |  |  |  | Asbestos |  |  |  | M Items Required in 2015
Line No. | Item No. | Category | S.M.E. | Classification | 'M' Items Required to be complete in 2015 | 'M' Items that can be delayed | Reference Standard | Electrical Loads Post-Decomm. | Notes | Plant | Service Corp. | Plant | Service Corp. | Other | Ongoing O&M | Hours | Hours *70 | Cost | Total $ | Cost | Total $ | O&M | 108 or 506 Rem | ARO Asbestos | ARO Pond | Other | O&M | Removal | Other | Asbestos | Pond Closure |  |  |  |  | M | R | C | INR | M | R | C | INR | M | R | C | INR | M | R | C | INR | O&M | Remvoal | Asbestos | Pond
1 | C1 | Circulating Water System | John Fall, Ron Balawajder | R |  |  |  |  | All intake and discharge tunnels on once-through units to be isolated from the river; sealed. Pull traveling screens from screen houses and dispose of on site. Sump pumps to be abandoned. Relocate active electrical loads out of basements. For the closed cycle units, pump the system empty, including the condenser, and then close the valves that will isolate the sections of the tunnels under the plant to keep such sections empty. There are sections of the intake canal outside and the cooling towers which will be exposed and subjected to catching rain water and hence will be prone to being wet depending on the weather. Prior to closing the system the plant needs to shock the system with bromine to kill the microbes before they dewater. Any plant sump discharges will be subject to technology-based limits for low-volume wastes (pH, TSS, and O&G). | 500 | [7 empty] | 350000 |  | 150000 | 535000 | X | X |  |  |  | 92500 | 92500 |  | 350000 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 92500 | 0 | 0 | 0 | 92500 | 0 | 0 | 0 | 350000 | 0 | 0 | 0 | 0 | 0 | 0
2 | C2 | Pond Closure - Ash Ponds - Ongoing Maintenance | M. Ajlouni | M | X |  | State Dam Safety and State EPA Permits | X | Closed ash ponds are inspected and maintained per the closure and post-closure QA/QC plan and Dam Safety Requirements. | n/a ??????? | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | C3 | Pond Management - Other Ponds | M. Ajlouni | M | X |  | NPDES Permits | X | Plant-Specific review of pond operations to determine which ponds to remain active. Anticipated flows that will require ongoing pond management include Storm Water and Seepage. It is anticipated that most Seepage will be eliminated with the CCR Pond Closure Program (Cerimele) and will therefore only contribute a short-term issue. Disposition of inactive ponds to be reviewed. Ponds to be reviewed: Coal Yard Runoff, Storm Water, Process Water, Bottom Ash, Other. Coal Yard Runoff Pond discussion to be integrated with Coal Pile Closure Strategy, including determination of final established condition of the coal pile and associated environmental impacts. | n/a ??????? | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | C4 | Stack Inspections - all units at site retired | Ron Balawajder | INR |  |  |  |  | Stack inspection not required if plant is closed and there are no personnel or equipment that can be harmed by any steel or concrete that may fall from the stack. | n/a | [15 empty] | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | C5 | Stack Inspections - some units at site retired | Ron Balawajder | R |  |  | Circular Letter # CI-M-CL-012A |  | Inactive stacks resulting from the closure of a unit at a plant with other units that will continue to operate will need to continue to be inspected as per the Circular Letter. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | C6 | Landfills | M. Ajlouni | M | X |  | State EPA Permits |  | TC and CR have active landfills. Landfill permits include closure plan and post-closure care. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | C7 | Landfill Leachate Collection Systems | M. Ajlouni | M | X |  | State EPA Permits |  | Landfill permits include closure plan and post-closure care. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | C8 | Stacks | Ron Balawajder | INR |  |  |  | X | Stack and stack elevator will be abandoned in place. | n/a | [15 empty] | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | C9 | Conveyors | Steve Torrell | R |  |  |  |  | Remove all belts, leave counterweights at grade or base platform. | 320 | [7 empty] | 65000 |  |  | 87400 | X |  |  |  |  | 87400 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 87400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | C10 | Coal Handling Equipment | Steve Torrell | C |  |  |  |  | a) Cover or fill with ash any hoppers that can be walked into to prevent accidents (e.g., coal yard reclaim and rail unloading); b) Remove or leave at a low energy level equipment supported by hoists/winches (rail car shakers, telescopic chutes, some magnetic separators). | 80 | [5 empty] | 500 |  |  |  | 15000 | 55600 | X |  |  |  |  | 55600 | 0 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 55600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | C11 | Coal Handling - Rail Facilities | Steve Torrell | C |  |  |  |  | Switch needs to be removed to block future train access. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | C12 | Railroad Bridges | Gene Sirca | INR |  |  | FRA Railroad Bridge Safety Standard |  | Continue to inspect if bridge/tracks are to be used by Class I or II railroad companies. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | C13 | Bridges and Conveyors over/under public roads | Gene Sirca | INR |  |  | State DOT |  | Continue to inspect in accordance with state regulations. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | C14 | Coal Reclaim Tunnels | Steve Torrell | C |  |  |  |  | Remove oil/grease from all equipment. Disconnect sump pump. Equipment will remain in place. Close/seal openings to prevent entry. Cover, fill or fence around coal reclaim hoppers. | 320 | [10 empty] | 22400 | X | X |  |  |  | 11200 | 11200 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 11200 | 0 | 0 | 0 | 11200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | C15 | Miscellaneous Bridges - Inspections | Gene Sirca | INR |  |  |  |  | Bridges to be maintained for access in and out of the plant property. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | E1 | Alarm/Control Systems Power | Pat Bawer | R |  |  |  |  | Evaluate need for back-up power feed. | 80 | [10 empty] | 5600 | X |  |  |  |  | 5600 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 5600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | E2 | Arc Flash | Mike Price | INR |  |  | AEP Arc Flash Protection Policy | X | Switchgear/MCCs will not be kept in service. Arc flash system will no longer be necessary. In order to switch/rack out switchgear the bus must be de-energized. | n/a | [15 empty] | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | E3 | Auxiliary Power (Reserve Aux Transformer) | Aaron Hinze | INR |  |  |  |  | Group auxiliary loads to allow more electrical equipment to be de-energized. Metered distribution feeds will power the remaining loads at the facility. This will enable the removal of the RAT and its protection, containment, inspections, etc. If there are major loads, then the RAT will have to be kept in-service. | n/a | [11 empty] | X |  |  |  | May be CAP for active units | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | E4 | Batteries/DC Power | Pat Bawer | INR |  |  |  |  | Batteries will not be needed and will either need to be disposed of or placed in-service elsewhere. A couple chargers/inverters may be kept as spare or placed in-service elsewhere. If RAT is left in service, batteries will need to maintained until such time the NERC protective relays can be switched to transmission. Will need to re-power breaker controls as needed. | n/a | [11 empty] | X | X |  |  | Transm | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | E5 | Cable - Above Ground | Jamin Hughes | INR |  |  |  |  | Abandon in place. | n/a | [15 empty] | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | E6.1 | Cable - Below Ground - Sodium Cable | Jamin Hughes/Marty Leedy | M |  | X | TSCA |  | Buried sodium cable can remain in place until plant demolition occurs. | n/a | [15 empty] | 0 | 0 | 0 | 0 | [6 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | E6.2 | Cable - Below Ground - PILC | Jamin Hughes/Marty Leedy | INR |  |  |  |  | Paper insulated lead sheathed cable could have PCB contaminated oil in it. We do not have to remove this cable, but since it is no longer in service, we need to characterize it’s PCB status by sampling the oil inside. If the oil is found to contain >50 ppm PCB, we will need to either remove the cable or obtain approval to leave the cable in place until a later date. If we find that oil reservoirs along the cable or the cable itself has leaked, we’ll need to conduct proper sampling and remediation. If the cable is found to contain 49 ppm PCB or less, we can leave it until plant demolition but we should pump all of the recoverable oil from the cable and reservoirs prior to abandonment. Also, when and if we cut the cable, we need to secure the ends to avoid allowing oil (PCB contaminated oil or otherwise) to escape and contaminate the adjacent soils. | n/a | [11 empty] | X | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | E7 | Emergency Lighting Systems | Ellis Loughner | INR |  |  |  | X | Emergency lighting will not be maintained in abandoned unit. | n/a | [15 empty] | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | E8 | Lighting Systems | Ellis Loughner | R |  |  |  | X | Any plant lighting, area, perimeter, etc. will be fed from distribution feeds. | 100 | [10 empty] | 7000 | X |  |  |  |  | 7000 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | E9 | Medium/Low-Voltage Switchgear | Mike Price | INR |  |  |  |  | Switchgear/MCCs will not be needed. | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | E10 | Oil-filled transformers | Aaron Hinze | R |  |  |  |  | GSUs, UATs, and RATs will either be transferred, sold or abandoned in place. Decision on transfer or sale and execution of that action to occur prior to end of Decommissioning period. Until transfer can take place, oil and nitrogen must remain in-service. Oil/water separator may need to be maintained and/or containment inspected periodically. Transformers to be transferred will require grounds. Drain or keep oil, depending on Asset Recovery decision to move or sell. Reference O15, Asset Recovery/Installed Components. | 120 | [5 empty] | 300 |  | 20000 |  |  | 49400 | X | X |  |  |  | 24700 | 24700 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 24700 | 0 | 0 | 0 | 24700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | E11 | Stack Lighting | Mark Shingleton | INR |  |  | FAA Advisory Circular AC No. 70/7460-1K | X | Legal to determine if stacks without lights will need to have lights added if the plants are closed. Need to maintain stack aviation obstruction lights for continued operation. Electric power to the lights need to be maintained. It is expected in the future that any light repairs and maintenance would be performed by a stack contractor. Contractor will inspect ladder system. It is expected that cost of maintaining lights is less expensive than partial (below height where lights are required) or complete stack demolition. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | E12 | Transmission Mitigation - Plant | Mark Shingleton | M |  | x | Generation Retirement High Level Assessment |  | Transmission is leading this effort. Will advise Generation of scope. Isolate unit from switchyard. Remove leads from disconnects; hang grounds from transformers. | n/a | [11 empty] | X | X |  |  | Transm | 0 | 0 | 0 | 0 | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | E13 | Barge Cell Lighting | Mark Shingleton | INR |  |  | USACE Permit and Coast Guard Requirements | X | Barge cell lights will remain in-service. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | E14 | Load List (Post-Decommissioning) | Aaron Hinze | C |  |  |  | X | Maintain post-decommissioning load list. | 500 | [10 empty] | 35000 | X |  |  |  |  | 35000 | 0 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 35000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | E15 | NERC Review | Katie Legates | M | x |  | NERC |  | The electrical configuration after shutdown (transition to decommissioned state) and after decommissioning (decommissioned state) of the plant will need to be finalized by AEP Electrical Engineering, Transmission and the plant. Once these configurations are finalized AEP Electrical Engineering will provide plant-specific guidance to minimize/eliminate the unit’s NERC PRC requirements. | 80 | [10 empty] | 5600 | X | X |  |  | Transm | 2800 | 2800 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0
32 | M1 | Boiler & Pressure Vessels | Ben Schaefer | M | X |  | Memorandum – Retirement of ASME Plated Pressure Retaining Vessels, 11/16/12 |  | AEP QCM (Schaefer) to manage the reporting for nameplate removal within 30 days of retirement. Plant QCC to manage the balance of activities listed in the Memorandum. | 160 | [7 empty] | 100000 |  |  | 111200 | X | X |  |  |  | 55600 | 55600 | [7 empty] | 1 | 0 | 0 | 0 | 55600 | 0 | 0 | 0 | 55600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55600 | 0 | 0 | 0
33 | M2 | Turbine | Ken Davis | C |  |  | Turbine Services Recommendations Tab |  | See Turbine Services Recommendations tab | 400 | [7 empty] | 25000 |  |  | 53000 | X | X |  |  |  | 26500 | 26500 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 26500 | 0 | 0 | 0 | 26500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | M3 | Ammonia Systems | Dennis Kovach | M | x |  |  |  | Ammonia storage and piping | 80 | [5 empty] | 150 |  | 10000 |  |  | 26100 |  | X |  |  |  | 0 | 26100 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | M4 | Cooling Towers | John Fall | INR |  |  |  |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Drain oil from motors and gear boxes on MD towers. Cooling towers to be abandoned in place. | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | M5 | Fans, FD, ID, GR, PA | J. J. Letcavits | C |  |  |  |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Drain oil from bearing housings and forced lube systems. Access doors welded, locked or barred shut. | 240 | [10 empty] | 16800 |  | X |  |  |  | 0 | 16800 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | M6 | Freeze Protection & Plant Heating (HVAC) | John Fall | R |  |  |  | X | Freeze protection will be req'd on any water lines that remain energized. If bldg is not heated, then the energized lines within the building will need to be heat traced and insulated. Evacuate freon from all air conditioning units. | 1500 |  |  |  |  | 20000 | 200 |  | 15000 |  |  | 134000 | X |  |  |  |  | 134000 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 134000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | M7 | Heaters & Deaerators | John Fall | C |  |  |  |  | Will need to be drained. | 80 | [10 empty] | 5600 |  | X |  |  |  | 0 | 5600 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | M8 | Piping - Above Ground | Bill Mauro | C |  |  |  |  | Abandoned piping shall be physically disconnected from any potentially energized sources. Valves shall not be considered a pressure boundary. Open ends shall be capped or otherwise closed. Energized piping may need to be insulated and heat traced. | 1000 | [5 empty] | 1000 |  |  |  | 25000 | 165000 |  | X |  |  |  | 0 | 165000 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | M9 | Piping - Below Ground | Bill Mauro | C |  |  |  |  | Abandoned piping shall be physically disconnected from any potentially energized sources. Valves shall not be considered a pressure boundary. Open ends shall be capped or otherwise closed. | 120 | [9 empty] | 25000 | 33400 |  | X |  |  |  | 0 | 33400 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | M10 | Potable Water System | John Fall | M | x |  | Review water contracts | X | If supplied by the city, the backflow preventer will need to be inspected on an annual basis. If not used, cap the line upstream of the back flow and notify city. For potable water permit, reference EV10. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | M11 | Pulverizers | J. J. Letcavits | C |  |  |  |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Drain oil from bearing housings and forced lube systems. Access doors welded, locked or barred shut. | 500 | [7 empty] | 10000 |  |  | 45000 |  | X |  |  |  | 0 | 45000 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | M12 | Storage Tanks - Above Ground | Bill Mauro | C |  |  |  |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Purge any flammable vapors. Physically remove any potential fluid input sources. Fuel oil tanks to be drained, all oil removed and cleaned of all sludge and residue from within the tank. Metal cleaning waste tanks to be cleaned. Water tanks to be drained. Fire water tank may be needed if fire system is to be left operable. Tanks are to be left open to disperse any residue fumes as approved by state or local fire marshal. | 320 | [5 empty] | 1000 |  | 50000 |  | 5000 | 147400 |  | X |  |  |  | 0 | 147400 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 147400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | M13 | Storage Tanks - Below Ground | Bill Mauro | C |  |  | Varies by State |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Purge any flammable vapors. Ensure tank has open vent to atmosphere. Physically remove any potential fluid input sources. State requirements may mandate removal. | 100 | [5 empty] | 300 |  | 50000 |  |  | 78000 |  | X |  |  |  | 0 | 78000 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | M14 | Pumps | John Fall | C |  |  |  | X | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Drain oil and water from pumps. | 640 | [10 empty] | 44800 | X | X |  |  |  | 22400 | 22400 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 22400 | 0 | 0 | 0 | 22400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | M15 | SCR, ESP and Ash Handling | Nick Fisher | C |  |  | AECE Recommendatons Tab |  | See AECE Recommendations tab. | 240 | [10 empty] | 16800 |  | X |  |  |  | 0 | 16800 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | M16 | Pond Closure - Ash Ponds - Relocation of inlet piping | Bill Mauro | C |  |  |  |  | Relocation of inlet piping (drains, sumps, etc.) not included in Pond Closure Program. Also need to review the operation of any inlet or outlet pumps, flow meters, or other equipment. Inlet pipes below water level need to be reviewed for antisiphon or vacuum breaker to ensure backflow protection. | 600 | [9 empty] | 25000 | 67000 |  |  |  | X |  | 0 | 0 | 0 | 0 | 67000 |  |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | M17 | River Water Intake | John Fall | INR |  |  |  |  | Remove any trash booms and traveling water screens. | n/a | [11 empty] | X | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | M18 | Oil-Water Separators | John Fall | INR |  |  |  |  | Completely drain and clean out sludge. Access doors welded, locked or barred shut. Abandon in place. | na/ | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | M19 | Air Compressors, Air Dryers and Air Receiver Tanks | John Fall | INR |  |  |  |  | Access doors welded, locked or barred shut. Abandon in place. | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | M20 | Air and Gas Ducts | J. J. Letcavits | C |  |  |  |  | Access doors welded, locked or barred shut. | 480 | [9 empty] | 1000 | 34600 |  | X |  |  |  | 0 | 34600 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | M21 | Plant Water Treatment System | J. Jacobsen | C |  |  |  |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Drain clarifiers, hose out, remove and dispose of any sludge in the bottom. Empty coagulant chemical feed tanks and polymer holding tanks, clean/neutralize as needed and delete chemical inventory. Drain and flush all chemical feed pumps and disconnect suction and discharge lines and flush. Drain the clearwell and remove and dispose of any debris in the bottom. Drain clearwell pumps. Drain and flush gravity and pressure filters and remove and dispose of media. Drain filtered water pumps. Drain and flush softener vessels and remove resin. Save resin and store if it can be reused elsewhere or dispose of resin. Drain softened water pumps. Remove all salt from Brine Saturator and Salt Storage Bin and flush and drain. Drain and flush brine holding tank and backwash pumps. Drain and flush filtered water storage head tank. Drain and flush various booster pumps. Drain and flush disinfection system and tank. Drain and flush dechlorinator. Drain and flush water treatment system piping. | 640 | [5 empty] | 1000 |  | 15000 |  |  | 129800 |  | X |  |  |  | 0 | 129800 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | M22 | Reverse Osmosis (RO) System | J. Jacobsen | C |  |  |  |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Drain the first pass and second pass RO train skids. Remove chemical feed totes and dispose. Drain and flush chemical feed pumps and piping. Drain and flush the clean in place (CIP) chemical holding tank. Drain the CIP skid. Drain and flush multimedia filter and dispose of filter media. Drain cartridge filters and dispose of filter elements. | 160 | [7 empty] | 5000 |  |  | 16200 |  | X |  |  |  | 0 | 16200 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | M23 | Boiler Water "Shot" Chemical Feed System | M. Beck | INR |  |  |  |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Remove and dispose the Charge Bottle. Drain and flush the chemical Charge Tank and remove any debris remaining in the bottom of the tank. Drain and flush chemical feed pumps and piping. | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | M24 | Feedwater / Boiler Water Continuous Chemical Feed System | M. Beck | C |  |  |  |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Drain and flush the chemical storage tanks (caustic soda, sodium phosphate, ammonia, hydrazine, other). Use a commercial tank cleaning contractor for chemical removal and cleaning of large chemical storage tanks. Drain and flush chemical feed pumps and piping. | 600 | [7 empty] | 150000 |  |  | 192000 |  | X |  |  |  | 0 | 192000 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | M25 | Condensate Clean-up System | J. Jacobsen | C |  |  |  |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Drain condensate clean-up pumps. Drain and flush clarite filters, coating tank and coating pumps. Drain demineralizer and remove resin. Dispose of resin. Flush and drain empty demineralizer vessels. Drain and flush the cation and anion regeneration tanks. Drain the sulfuric acid storage tank and flush. Use a commercial tank cleaning contractor for chemical removal and cleaning of large acid storage tanks. Drain and flush acid suction tank and acid feed pumps. Drain caustic storage tank and flush. Use a commercial tank cleaning contractor for chemical removal and cleaning of large caustic storage tanks. Drain and flush caustic suction tank and caustic feed pumps. Drain and flush chemical feed piping. Drain the clean condensate storage tank. Drain the contaminated condensate storage tank and remove and dispose of any debris in the bottom of the tank. | 600 | [7 empty] | 150000 |  |  | 192000 |  | X |  |  |  | 0 | 192000 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | M26 | Circulating Water Treatment System | J. Jacobsen | C |  |  |  |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Drain and flush the chlorination equipment. Drain and flush sulfuric acid storage tank. Use a commercial tank cleaning contractor for large chemical storage tanks. Drain and flush sulfuric acid feed pumps and piping. Drain and flush other chemical feed storage tanks, feed pumps and piping. | 500 | [7 empty] | 100000 |  |  | 135000 |  | X |  |  |  | 0 | 135000 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | M27 | Well Water System | M. Finneran | INR |  |  |  |  | Assume the well water system will be shutdown. Drain the well water pumps. Drain the well water and potable water storage tanks and remove and dispose of any debris in the bottom of the tank. Drain potable water piping to plant offices, restrooms and eyewash/safety showers. Drain the seal water storage tank and remove and dispose of any debris in the bottom of the tank. | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | M28 | Chemical Cleaning System | M. Beck | C |  |  |  |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Drain and flush the chemical cleaning solution storage tank and remove any remaining debris in the bottom of the tank. Drain and flush chemical cleaning pumps. Drain and flush the metal waste storage tank and remove any debris remaining in the bottom of the tank. Use a commercial tank cleaning contractor for assistance. Drain and flush chemical cleaning piping. Drain and flush the metal waste recirculation pump and the decanting pump. Drain and flush the metal cleaning waste storage tank area sump and remove and dispose of any debris in the bottom of the sump. Drain and flush the sump pump. | 150 | [7 empty] | 20000 |  |  | 30500 |  | X |  |  |  | 0 | 30500 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | M29 | Pond Chemical Treatment Systems | M. Beck | M | X |  |  | X | Each plant case will have to be reviewed to determine if chemical treatment of the pond is still required after decommissioning. Assuming chemical treatment of pond is no longer needed, drain and flush the sulfuric acid storage tank. Use a commercial tank cleaning contractor for large chemical storage tanks. Drain and flush acid feed pumps. Drain and flush acid feed piping. Close water supply isolation valve and drain eyewash station and safety shower. | n/a | [11 empty] | X | X |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | M30 | Plant Chemical Lab | M. Beck | C |  |  |  |  | Develop an inventory list of all chemicals on site. Dispose of all unwanted chemicals. May need to seek outside contractor assistance with the handling and disposal of certain chemicals. Flush out all lab sinks and piping. Drain the piping. Cleanup any spills on the counters, tables and flooring in the chemical lab. Wipe down lab counter and table surfaces to ensure there is no chemical residues left behind. Remove and dispose of lab equipment. | 80 | [7 empty] | 25000 |  |  | 30600 | X |  |  |  |  | 30600 | 0 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 30600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | M31 | Cycle Chemistry Instrumentation | M. Beck | C |  |  |  |  | Remove the pH probes and power down the electronics. Remove the conductivity probes and power down the electronics. Remove the dissolved oxygen probes and power down the electronics. Remove the sodium, silica and chloride analyzers. Drain sample coolers and chillers. Drain sample panel tubing, instruments, valves and sink. | 80 | [10 empty] | 5600 | X |  |  |  |  | 5600 | 0 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 5600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | M32 | Stator Cooling Water System | M. Beck | C |  |  |  |  | Drain and dry the stator ion exchange resin. Dispose of resin material. Drain and flush demineralizer vessel. Remove the conductivity probe and analyzer. Drain circulating pumps. Drain and flush filters and strainers. Drain and flush stator cooling water storage tank and remove any debris in the bottom of the tank. Drain and flush piping. See Turbine Services Recommendations tab. | 150 | [7 empty] | 25000 |  |  | 35500 |  | X |  |  |  | 0 | 35500 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | M33 | Electro-Hydraulic Control (EHC) Fluid System | M. Beck | C |  |  |  |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Drain and flush the control fluid tank and remove any debris in the bottom of the tank. Drain and flush the tank vapor extractor; remove and dispose of air filter and disconnect motor. Drain and flush the control fluid pumps. Drain and flush the control fluid coolers and filter. Drain and flush EHC fluid system piping. See Turbine Services Recommendations tab. | 600 | [7 empty] | 20000 |  |  | 62000 |  | X |  |  |  | 0 | 62000 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | M34 | Lube Oil (Main Turbine, Feed Pump) System | M. Beck | C |  |  |  |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Drain and flush the main oil tanks and remove any debris remaining in the bottom of the tank. Drain and flush the oil coolers and oil pumps. Drain and flush the tank vapor extractor and remove and dispose of any air filters. Drain and flush oil screens/strainers and dispose. Drain and flush lube oil piping. See Turbine Services Recommendations tab. | 420 | [7 empty] | 25000 |  |  | 54400 |  | X |  |  |  | 0 | 54400 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | M35 | Meet With Local First Responders | Dennis Kovach | M | X |  | Various |  | Meet with the local first responders before the plant is shut down. Review the plans for what state fire systems will be left in and receive buy-in. Review provisions for emergency site access. | 24 | [10 empty] | 1680 | X |  |  |  |  | 1680 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 1680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1680 | 0 | 0 | 0
67 | M36.1 | Fire Alarm Systems | Dennis Kovach | M | X |  | NFPA 72 | X | Route fire alarms that will remain in service to adjacent facility/unit which is continuously manned. In some cases, this may be the guard house. | 750 | [9 empty] | 10000 | 62500 | X |  |  |  |  | 62500 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 62500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 62500 | 0 | 0 | 0
68 | M36.2 | Battery Room Smoke Detection | Dennis Kovach | M | X |  | IFC 907.2.23 | X | Maintain existing smoke detection in service in the battery room(s) until the batteries are removed from service. | 150 | [9 empty] | 10000 | 20500 | X |  |  |  |  | 20500 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 20500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20500 | 0 | 0 | 0
69 | M36.3 | Electrical Room Smoke Detection | Dennis Kovach | M | X |  |  | X | Consider maintaining smoke detection systems in areas where electrical equipment (such as switchgear) will remain energized. | 150 | [9 empty] | 10000 | 20500 | X |  |  |  |  | 20500 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 20500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20500 | 0 | 0 | 0
70 | M36.4 | Smoke Detector Disposal | Dennis Kovach | M |  | x | State Universal Waste Disposal Requirements |  | Dispose of all ionization-type smoke detectors properly. As a general rule, most smoke detectors currently installed on site will be the ionization type. | 100 | [7 empty] | 25000 |  |  | 32000 |  | X |  |  |  | 0 | 32000 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | M36.5 | Fire Alarm System Abandonment | Dennis Kovach | M |  | x | IFC Chapter 311 / NFPA 1 Sec 10.13 |  | Once the protected equipment has been de-energized and the combustibles (i.e. coal, conveyor belts, oils, etc.) have been removed, the fire detection system may be removed from service with permission from the local fire official. Transformer fire protection systems may be removed from service once the transformers are permanently de-energized. | 100 | [7 empty] | 50000 |  |  | 57000 |  | X |  |  |  | 0 | 57000 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | M36.6 | Fire Alarm Panel Batteries | Dennis Kovach | C |  |  |  |  | Remove backup batteries from fire alarm panels which have been taken out of service and dispose of them properly. Note: most fire alarm panels will not be equipped with backup batteries. | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | M36.7 | Elevator Smoke/Heat Detection | Dennis Kovach | M | X |  | NFPA 72 / ANSI A17.1 | X | Elevator smoke/heat detection systems which are currently installed must be maintained as long as the protected elevator remains in service. | 100 | [9 empty] | 5000 | 12000 | X |  |  |  |  | 12000 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 0 | 0 | 0
74 | M37.1 | Fire Protection System Inspection, Testing, and Maintenance | Dennis Kovach | M | X |  | Various |  | All fire protection systems and equipment which remain in service must be inspected, tested, and maintained. | [8 empty] | 10000 |  |  | 10000 | X |  |  |  |  | 10000 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10000 | 0 | 0 | 0
75 | M37.2 | Fire Extinguisher Maintenance | Dennis Kovach | M | X |  | NFPA 10 |  | Establish a plan for monthly inspections and annual maintenance for fire extinguishers that will be maintained on site. | 80 | [7 empty] | 20000 |  |  | 25600 | X |  |  |  |  | 25600 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 25600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25600 | 0 | 0 | 0
76 | M37.3 | Fire Barrier Maintenance | Dennis Kovach | M | X |  | IFC 311.2.3 |  | Where only a portion of the plant will be vacated, fire barriers (including doors) between vacant spaces and operational units shall be maintained. A regular inspection program in accordance with NFPA 80 and NFPA 90A must be established. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | M37.4 | Fire Suppression System Maintenance | Dennis Kovach | M | X |  | NFPA 25 |  | Establish a plan for completing required periodic inspection, testing, and maintenance of fire suppression systems until they are permanently removed from service. | 80 | [9 empty] | 10000 | 15600 | X |  |  |  |  | 15600 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 15600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15600 | 0 | 0 | 0
78 | M37.5 | Fire Alarm System Maintenance | Dennis Kovach | M | X |  | NFPA 72 Chapter 14 / NFPA 1 Sec. 10.13 |  | Establish a plan for completing required periodic inspection, testing, and maintenance of fire alarm systems until they are permanently removed from service. | 80 | [7 empty] | 10000 |  |  | 15600 | X |  |  |  |  | 15600 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 15600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15600 | 0 | 0 | 0
79 | M37.6 | Fire Seal Maintenance | Dennis Kovach | M | X |  | IFC 311.2.3 |  | Develop a plan for periodic (recommended annual) inspection and maintenance of fire seals. This is primarily needed around trays containing energized cables or where energized transformers still create an exposure hazard. | 40 | [7 empty] | 10000 |  |  | 12800 | X |  |  |  |  | 12800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 12800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12800 | 0 | 0 | 0
80 | M37.7 | Transformer Oil Containment / Drainage Maintenance | Dennis Kovach | M | X |  | IFC 311.2.3 |  | Where oil-filled reserve aux. transformers will remain in service, a plan needs to be established for maintaining the containment and drainage around this equipment. | 40 | [7 empty] | 5000 |  |  | 7800 | X |  |  |  |  | 7800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 7800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7800 | 0 | 0 | 0
81 | M38.1 | Automatic Fire Suppression Systems | Dennis Kovach | M |  | x | IFC Chapter 311 / NFPA 1 Sec 10.13 |  | Once the protected equipment has been de-energized and the combustibles (i.e. coal, conveyor belts, oils, etc.) have been removed, the fire suppression system may be removed from service with permission from the local fire official. | 40 | [10 empty] | 2800 |  | X |  |  |  | 0 | 2800 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | M38.2 | Sprinkler Heads and Control Valves | Dennis Kovach | M |  | x | NFPA 13 Sec. 27.2 |  | Where all or part of an inactive sprinkler system is abandoned in place, components including sprinklers, hose valves and hoses, and alarm devices shall be removed. Control valves abandoned in place shall have the operating mechanisms removed. Alternate plans must be approved by the fire code official. | 500 | [10 empty] | 35000 |  | X |  |  |  | 0 | 35000 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | M38.3 | Freeze Protection of Fire Systems | Dennis Kovach | M | X |  | NFPA 13 | X | If water-based fire suppression systems will be maintained during cold weather periods, ensure plans are in place to provide temporary heat or otherwise protect the system from damage. | 200 | [7 empty] | 25000 |  |  | 39000 | X |  |  |  |  | 39000 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 39000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39000 | 0 | 0 | 0
84 | M38.4 | Draining Wet Pipe Sprinkler Systems | Dennis Kovach | C |  |  |  |  | Wet pipe sprinkler systems are only equipped with low point drains for sections of piping which are over 5 gallons water volume. Smaller sections will need to be drained by disassembling fittings or removing nozzles. A sprinkler contractor may be the best way to trace down the piping to make sure it has been completely drained. | 100 | [5 empty] | 250 |  | 10000 |  |  | 34500 |  | X |  |  |  | 0 | 34500 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | M38.5 | Draining Deluge Valve Headers | Dennis Kovach | R |  |  |  |  | Where deluge/sprinkler valve manifolds are drained, make sure all valve trim piping and deluge valve priming chambers are also drained. Leave the system isolation (hand shut-off) valve in a closed position. | 100 | [5 empty] | 150 |  |  |  | 10000 | 27500 |  | X |  |  |  | 0 | 27500 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | M38.6 | Mercury Removal from Fire System Components | Dennis Kovach | R |  |  | State Universal Waste Disposal Requirements |  | Remove all Mercoid-style switches installed on sprinkler and deluge valves or any gaseous fire systems. Environmental best practice. | 500 | [10 empty] | 35000 |  | X |  |  |  | 0 | 35000 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | M38.7 | Fire System CO2 and Nitrogen Cylinders | Dennis Kovach | R |  |  |  |  | Remove and properly dispose of any nitrogen cylinders associated with dry chemical systems or CO2 cylinders associated with high pressure CO2 fire systems. | 100 | [10 empty] | 7000 |  | X |  |  |  | 0 | 7000 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | M38.8 | Bulk CO2 Storage Tank | Dennis Kovach | R |  |  |  |  | Once areas protected with CO2 (pulverizers, silos, oil rooms) have been cleared of combustibles and generator has been purged, bulk CO2 tank can be taken out of service and drained. This can be done by opening the liquid fill valve (take precautions for personnel safety such as monitoring oxygen levels in the area). ONLY open the liquid fill valve to complete this process. | 250 | [9 empty] | 5000 | 22500 |  | X |  |  |  | 0 | 22500 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | M38.9 | Basement Foam System Tanks | Dennis Kovach | M |  | x | Breed Lessons Learned |  | Drain the foam tanks and dispose of the foam appropriately. | 100 | [7 empty] | 10000 |  |  | 17000 |  | X |  |  |  | 0 | 17000 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | M39.1 | Fire Protection Standpipes | Dennis Kovach | M |  | X | IFC 311.2.2 / IFC Chapter 14 |  | Drain all standpipe systems to prevent damage from freezing. Standpipe systems may have to be returned to service during demolition phase. | [6 empty] | 150 |  |  |  | 10000 | 20500 |  | X |  |  |  | 0 | 20500 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | M39.2 | Fire Hose Removal | Dennis Kovach | M |  | x | 29 CFR 1910.158 e 2 |  | Remove all fire hoses installed at standpipes. Hoses must be removed unless there is a plan in place to inspect, test, and maintain those hoses as required by the fire codes. | [6 empty] | 150 |  |  |  | 10000 | 20500 | X |  |  |  |  | 20500 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 20500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | M39.3 | Standpipe System Conversion | Dennis Kovach | INR |  |  |  |  | Consider modifying the standpipe system and equipping it with a fire department connection so that the standpipe can still be used by the fire department. Conversion will be required during demolition and may be required by the local fire code official at an earlier date. | n/a | [11 empty] | X |  |  |  | May be CAP for active units | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | M40.1 | Fire Extinguishers | Dennis Kovach | M |  | x | NFPA 10 / 29 CFR 1910.157 c 4 |  | Remove fire extinguishers from plant areas once they have been cleared of combustibles and hotwork activities associated with decommissioning are complete. Extinguishers which are not removed require monthly inspections. | 100 | [10 empty] | 7000 | X |  |  |  |  | 7000 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 7000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | M40.2 | Fire Extinguisher Cache | Dennis Kovach | C |  |  | Berger Plant Fire Lessons Learned |  | Consider maintaining a stockpile of extinguishers on site to be used for maintenance activities and for the fire department's use. Identify one or more locations where the extinguishers will be stored. | [6 empty] | 75 |  |  |  |  | 5250 | X |  |  |  | Stores | 5250 | 0 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 5250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | M40.3 | Fire Extinguisher Removal | Dennis Kovach | R |  |  |  |  | Remove excess extinguishers from site that will not be maintained. Extinguishers that are removed from service but are not maintained could be mistaken for "usable" during a fire emergency. Other plants will likely accept any extinguishers that are made available. Consider limiting the number of dry chemical extinguishers maintained versus CO2 (to prevent damage from vandals). | 100 | [5 empty] | 50 |  |  |  |  | 10500 | X |  |  |  |  | 10500 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 10500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | M40.4 | Wheeled Fire Extinguishers | Dennis Kovach | R |  |  |  |  | Arrange for proper removal and disposal of nitrogen cylinders connected to wheeled fire extinguishers which are not transferred to other plants. | [6 empty] | 50 |  |  |  |  | 3500 | X |  |  |  |  | 3500 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 3500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | M41 | Site Emergency Action Plan | Dennis Kovach (or Derek Carson) | M | x |  | 29 CFR 1910.38 |  | Revise the EAP to reflect new conditions and expectations for any personnel who will remain on site | 40 | [10 empty] | 2800 | X |  |  |  |  | 2800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0
98 | M42 | Diesel Fire Pump | Dennis Kovach | C |  |  | Breed Lessons Learned |  | For recommendations associated with draining and purging tanks and piping containing combusible materials, reference M50.1 thru M50.12. The balance of notes are Considerations or INR. Drain hazardous fluids from motor. Drain any remaining fuel from fuel tank. Notify state of removal of emission point source if required. | 24 | [7 empty] | 5000 |  |  | 6680 |  | X |  |  |  | 0 | 6680 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | M43 | Fire Hydrants | Dennis Kovach | R |  |  |  |  | Clearly mark any fire hydrants which are placed out-of-service (i.e., with tags or covers) if required by the local fire code official. | 80 | [9 empty] | 20000 | 25600 |  | X |  |  |  | 0 | 25600 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | M44.1 | Fire Water Source | Dennis Kovach | M | x |  | IFC Section 507 |  | The fire water source/fire water system shall be maintained until all required water-based fire suppression systems have been retired. | 50 | [9 empty] | 5000 | 8500 | X |  |  |  |  | 8500 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 8500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8500 | 0 | 0 | 0
101 | M44.2 | Fire Pump Maintenance | Dennis Kovach | M | X |  | IFC Section 507 |  | Where fire water must be maintained, maintain at least one set (one electric and one diesel) fire pump in service. Sites with multiple fire pump sets are only required to maintain a single set during the decommissioning period when the fire water system must remain in service. | 80 | [7 empty] | 30000 |  |  | 35600 | X |  |  |  |  | 35600 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 35600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35600 | 0 | 0 | 0
102 | M45 | Plant Fire Engine & Fire Brigade | Dennis Kovach | R |  |  |  |  | Plant fire engines are not required on site once the site fire brigade has been disbanded. Disbanding the site fire brigade prior to final unit shutdown shall be in accordance with the AEP Fire Protection Program. | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | M46 | Emergency Egress Maintenance | Dennis Kovach | M | X |  | 29 CFR 1910.37 |  | Develop a plan for maintaining required egress routes, signage, and lighting. | 40 | [9 empty] | 5000 | 7800 | X |  |  |  |  | 7800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 7800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7800 | 0 | 0 | 0
104 | M47 | Fixed Hazardous Gas Detection Systems | Dennis Kovach | INR |  |  |  |  | Hazardous gas (CO or methane) fixed detection systems can be abandoned in place once the potential source of gas (coal or fuel gas) has been removed. | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | M48.1 | First Responder Emergency Access | Dennis Kovach | M | x |  | IFC Chapter 5 |  | Decide whether or not access codes or keys will be provided to the first responders. Coordinate this effort with AEP Security and local fire officials. Note that in most jurisdictions the fire department has the right to request this access if they so desire. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | M48.2 | First Responder Emergency Access- Emergency Contacts | Dennis Kovach | R |  |  | Lessons Learned |  | Conspicuously post 24-hour emergency contact phone numbers at all site access points. Provide numbers to local first responders (including the local 9-1-1 center). Establish a plan for routinely updating these numbers and the emergency call-out list, if necessary. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | M48.3 | First Responder Notification of Vacancy | Dennis Kovach | INR |  |  |  |  | Notify the local first responders when decommissioning activities have been completed and the facility has in essence been vacated. Not required for sites where other units will remain in service. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | M48.4 | Fire Department Site Tour | Dennis Kovach | R |  |  |  |  | Give the fire department (and other local first responders) an opportunity to tour the site to review conditions once decommissioning is complete so they can pre-plan for an emergency. Consider limiting the number of participants (i.e. only allow chief officers to visit) for safety purposes. Do not permit access to any unsafe areas. | 16 | [10 empty] | 1120 | X |  |  |  |  | 1120 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | M49 | Vacant Premises Signage | Dennis Kovach | M |  | x | IFC 311.5 |  | Vacant premises signs in accordance with the IFC Section 311.5 shall be prominently posted if required by the local fire code official at locations selected by the local official. | 40 | [9 empty] | 5000 | 7800 | X |  |  |  |  | 7800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 7800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | M50.1 | Control of Combustibles | Dennis Kovach | M |  | x | IFC 311.3 / NFPA 1 Sec. 10.3 |  | Accumulations of combustible materials, flammable or combustible waste, or rubbish shall be removed and the premises shall be maintained clear of waste or hazardous materials. | 40 | [5 empty] | 80 |  |  |  |  | 8400 | X |  |  |  |  | 8400 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 8400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | M50.2 | Control of Combustibles- Coal | Dennis Kovach | M | x |  | Lessons Learned |  | Where adjacent units fed by a common reclaim/tripper system will remain in service, the bottom of all silos and hoppers should be opened to prevent coal from accumulating in the empty/abandoned vessels. | 40 | [5 empty] | 80 |  | 5000 |  |  | 13400 |  | X |  |  |  | 0 | 13400 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | M50.3 | Control of Combustibles- Coal | Dennis Kovach | M |  | x | IFC 311.3 / NFPA 1 Sec. 10.3 |  | Coal silos/bunkers, feeders, and pulverizers need to be emptied and cleaned. All coal handling areas needs to be cleaned (preferably with washdown, not vacuuming). Special care should be used to thoroughly clean areas where PRB coal was handled. | 320 | [5 empty] | 1000 |  | 25000 |  |  | 117400 |  | X |  |  |  | 0 | 117400 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | M50.4 | Control of Combustibles- Coal Dust Collectors | Dennis Kovach | INR |  |  | IFC 311.3 / NFPA 1 Sec. 10.4 |  | Coal dust collectors need to be emptied and cleaned. The equipment, including ductwork, should be washed. Bags should be disposed of. Where adjacent units will remain in service, steps such as disconnecting the ductwork and cutting off hopper bottoms may be needed to ensure coal dust will not be entrained or trapped in the equipment in the future. Special care should be used to thoroughly clean this equipment if PRB coal was handled. | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | M50.5 | Control of Combustibles- Natural Gas | Dennis Kovach | INR |  |  | NFPA 56 |  | Close the main natural gas supply to the unit as far upstream of the unit as possible (preferably at the supplier's delivery point). Purge the line out of service in accordance with NFPA 56 and AEP Safety guidelines. Disconnect and cap the line to prevent any potential gas leakage into the unit. | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | M50.6 | Control of Combustibles- Hydrogen (low pressure) | Dennis Kovach | R |  |  | NFPA 56 |  | Shut off the hydrogen supply to each generator at the bulk hydrogen storage tanks. Safely remove hydrogen from every generator. Purge all pipelines that contained hydrogen from the hydrogen storage system through the systems discharge vents. This will include the supply to each generator and to systems that may contain hydrogen such as the hydrogen seal oil system, purity monitoring systems, and generator liquid level indicators. | 20 | [5 empty] | 40 |  |  |  |  | 4200 |  | X |  |  |  | 0 | 4200 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | M50.7 | Control of Combustibles- Hydrogen (high pressure) | Dennis Kovach | R |  |  |  |  | Plan to use as much hydrogen as practical (without refilling the tanks) prior to unit shutdown. Steps should be taken to unload any hydrogen remaining in the storage tubes and transfer it off site. Simply releasing hydrogen to the air to empty the tanks is not recommended. Follow safety guidelines for purging and inerting the tanks to complete the decommissioning process for this equipment. | 20 | [5 empty] | 40 |  |  |  |  | 4200 |  | X |  |  |  | 0 | 4200 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | M50.8 | Control of Combustibles- Flammable Gases (other than hydrogen and natural gas) | Dennis Kovach | INR |  |  |  |  | Disconnect flammable gas cylinders at manifolds. Relocate portable flammable gas cylinders to outside storage areas until they can be permanently removed from the site. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | M50.9 | Control of Combustibles- Bulk Flammable/Combustible Liquid Storage | Dennis Kovach | R |  |  | IFC Chapters 27-44 / NFPA 400 |  | Develop an inventory list of all bulk chemicals (oils, solvents, cleaners, degreasers, lubricants, sealants, disinfectants, pesticides, etc.) on site. Dispose of all unwanted chemicals. May need to seek outside contractor assistance with the handling and disposal of certain chemicals. Drain and clean all tanks containing flammable or combustible liquids that are not portable or will not be removed from the site. Cleanup any spills in the bulk chemical storage area. | 40 | [5 empty] | 200 |  | 50000 |  |  | 66800 | X |  |  |  |  | 66800 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 66800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | M50.10 | Control of Combustibles- Flammable/Combustible Liquid Piping | Dennis Kovach | R |  |  |  |  | Drain and purge all lubricating oils lines and other systems carrying flammable or combustible liquids | 500 | [5 empty] | 200 |  | 50000 |  |  | 99000 | X |  |  |  |  | 99000 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 99000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | M50.11 | Control of Combustibles- Fuel Oil System | Dennis Kovach | R |  |  |  |  | Clean up all fuel oil spills in units that used fuel oil for igniters. Areas to address include at each igniter, at fuel oil igniter control package units, at fuel oil pumping areas, and in any day tank areas within the plant. | 160 | [7 empty] | 5000 |  |  | 16200 | X | X |  |  |  | 8100 | 8100 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 8100 | 0 | 0 | 0 | 8100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | M50.12 | Control of Combustibles- Aboveground Storage Tanks | Dennis Kovach | M |  | x | IFC Section 3404.2.14 |  | After contents of the tank have been removed, piping at tank openings that is not to be used further shall be disconnected unless otherwise approved by the fire code official. Tanks shall be thoroughly cleaned and purged of vapor and/or inerted. Tank openings shall be capped or plugged, leaving a 1/8-inch to 1/4 inch diameter opening for pressure equalization. | 240 | [5 empty] | 3500 |  | 100000 |  |  | 361800 |  | X |  |  |  | 0 | 361800 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | M51 | Lightning Protection on Cooling Towers | Dennis Kovach | INR |  |  | Circular Letter CY-M-CL-021A |  | Maintaining lightning protection systems is a critical step to preventing cooling tower fires. Visual inspections should be conducted annually and complete, in-depth inspections should be conducted every three to five years. Further information on maintaining lightning protection systems can be found in NFPA 780, Standard for the Installation of Lightning Protection Systems. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | M52 | Switchyard Fire Protection | Dennis Kovach | INR |  |  | Breed Lessons Learned |  | Where adjacent switchyards have fire protection (hydrants, detection or deluge systems) which are tied to plant systems, coordinate decommissioning of the fire protection with Transmission. | n/a | [11 empty] | X | X |  |  | Transm | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | M53.1 | Adjacent Units- Fire System Isolation | Dennis Kovach | R |  |  |  |  | Establish a plan to isolate fire water from the decommissioned units so that fire water can be maintained in adjacent units that will remain in service. Permanent modifications to the fire header should be documented on P&IDs/flow diagrams at a minimum. Consult with AE&BOPME fire protection engineers. | 80 |  |  |  | 25000 |  |  |  | 150000 |  |  | 180600 | X |  |  |  | May be CAP for active units | 180600 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 180600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | M53.2 | Adjacent Units- Maintaining Fire Water | Dennis Kovach | M | x |  |  |  | Where the plant fire header cannot be re-routed around an abandoned unit but serves adjacent units that will remain in service, plans must be established for maintaining the fire header through the abandoned unit in service. This may include the need for permanent heat trace/insulation or other freeze protection. | n/a | [11 empty] | X |  |  |  | May be CAP for active units | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | M54 | Reserve Aux. Transformer Fire Protection | Dennis Kovach | M | x |  | NFPA 850 / Berger Lessons Learned |  | Where oil-filled reserve aux. transformers will remain in service, conduct a fire hazards analysis review to confirm adequate safeguards are in place to minimize the potential for damage in the event of a transformer failure and fire. | 16 | [5 empty] | 40 |  | 10000 |  |  | 13920 | X |  |  |  |  | 13920 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 13920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13920 | 0 | 0 | 0
127 | M55 | Critical Ventilation Systems | Dennis Kovach | M | x |  | Various |  | Keep battery room ventilation systems in service until batteries are disconnected. Keep silo/bunker and reclaim tunnel ventilation systems in service until all coal has been removed. Keep ventilating fans in flammable liquids storage rooms in operation as long as the room contains flammable liquids. | 200 | [9 empty] | 8000 | 22000 | X |  |  |  |  | 22000 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 22000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22000 | 0 | 0 | 0
128 | M56 | Safeguarding of Premises | Dennis Kovach | M |  | x | IFC Section 311.2 |  | Protect all exterior windows vulnerable to items propelled from peripheral areas (depending on location of building relative to streets, alleys, vacant lots, etc.). Consider installing expanded metal over all windows at lower levels. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | I1 | Alarm Systems | R. Gupta | R |  |  |  | X | Route critical alarms to adjacent facility/unit like fire alarms, critical power fail, sump/tunnel, pond level and common system alarms. | 500 | [9 empty] | 2000 | 37000 | X |  |  |  |  | 37000 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 37000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | I2 | Control Systems (DCS, PLC, etc.) | R. Gupta | R |  |  |  | X | Evaluate if power to control system, PI server can be shutdown. Evaluate if we can scavenge controllers, IO cards, power supplies, servers, monitors etc. If only one unit is decommissioned then move plant common equipment controllers, servers, system etc. to other unit or keep operational. Also would need to modify flow diagrams, logic, graphics, network connections, IO connections between units for common equipment like FGD, Trona, NH3 injection, Compressed air, waste treatment, coal handling, fuel oil, etc. | 1500 | 1500 | [9 empty] | 210000 | X |  |  |  | May be CAP for active units | 210000 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 210000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | I3 | Control Room | R. Gupta | R |  |  |  |  | De-energize panels, cabinets, instruments etc. Evaluate if lighting, HVAC need to be maintained in control room. If only one unit is decommissioned then common equipment panels, cabinets, instruments, alarms would need to be kept operational or moved to other unit. | 4160 | [5 empty] | 200 |  |  |  | 8000 | 313200 | X |  |  |  | May be CAP for active units | 313200 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 313200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | I4.1 | CEMS | Rich Gill (AQS) | INR |  |  |  |  | AQS to inform proper Federal/State authorities about plant closure dates and get required approvals for shutting down CEMS equipment before removing power to CEMS equipment. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | I4.2 | CEMS | R. Gupta/Matt Morgan | INR |  |  |  | X | Five years of historical CEMS data must be available for 5 years after plant retirement to submit monitoring reports. For this purpose these servers will be moved to some common place and maintained for the next 5 years or if required a new big server will be purchased and individual plant servers will be created as virtual machines on this server. Funds will be needed for this work and for the maintenance contract for next 5 years. Activities to be managed by AEP I&C. Dispose of mercury from mercury monitoring equipment. Flush down chemicals, remove power, return gas cylinders to vendors. Evaluate if we can scavenge equipment like dilution probes, NOX/CO2 monitors, DAS equipment, pre-fabricated buildings, etc. | n/a | [11 empty] | X | X |  |  | May be CAP for active units | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | I4.3 | CEMS | R. Gupta/Matt Morgan | INR |  |  |  | X | Flush down chemicals, remove power, return gas cylinders to vendors. Evaluate if we can scavenge equipment like dilution probes, NOX/CO2 monitors, DAS equipment, pre-fabricated buildings, etc. | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | I5 | Local Panels/Cabinets | R. Gupta | C |  |  |  |  | De-energize local panels, cabinets, instruments, etc. | 200 | [10 empty] | 14000 | X |  |  |  |  | 14000 | 0 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 14000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | I6 | Field Instruments | R. Gupta | R |  |  |  |  | De-energize field instruments. Dispose of mercury from mercury switches and nuclear source from ash hopper level, etc. | 200 | [7 empty] | 5000 |  |  | 19000 | X |  |  |  |  | 19000 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 19000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | X1 | As-Builts/Drawing Updates for Remaining Equipment |  | R |  |  |  |  | Drawings for remaining or shared systems; updated/redlined (as-builts). | 960 | 1500 | [9 empty] | 172200 | X |  |  |  |  | 172200 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 172200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | P1 | Cranes & Hoists |  | INR |  |  |  | X | May be needed for abatement or demolition, but do not need to remain in-service until that time. Crane to be inspected and load-tested prior to reuse per OSHA requirements. Continue maintenance and inspection for set period, then tag out one year after last inspection. | n/a | [11 empty] | X | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | P2 | Deep wells/well water |  | INR |  |  |  |  | Maintain wells if needed for potable water. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | P3 | Elevator Maintenance |  | INR |  |  |  | X | Lock out the elevators when decommissioning complete. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | P4 | Exterior Buildings (e.g., Learning Centers, PDC's, warehouse) |  | INR |  |  |  |  | Exterior buildings should be abandoned. | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | P5 | Oils and Lubes |  | INR | [5 empty] | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | P6 | Road Maintenance |  | C |  |  |  |  | Maintenance not required except for main plant access road. | 80 | [9 empty] | 20000 | 25600 | X |  |  |  |  | 25600 | 0 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 25600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | P7 | Roof/Exterior Maintenance |  | INR |  |  |  |  | Not required on abandoned buildings. | n/a | [15 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | P8 | Site Maintenance |  | INR |  |  |  |  | Areas around cooling towers should be kept free of grass, weeds, brush, wood, or combustible waste materials. | [5 empty] | 40000 |  |  | 40000 |  |  | 40000 | X |  |  |  |  | 40000 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 40000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | P9 | Stack Lighting - Maintenance |  | M | x |  |  | X | To be managed by third party contractor. |  |  |  |  | 30000 |  | 640 |  | 40000 |  |  | 114800 | X |  |  |  |  | 114800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 114800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114800 | 0 | 0 | 0
147 | P10 | Sewage Systems/Sewage Plants |  | INR |  |  | Review sewage contracts | X | Will need to be thoroughly flushed. If tied into the city sewage, need to contact city to determine procedure for isolating. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | P11 | Telecommunications |  | R |  |  |  | X | Telecom group intends to maintain existing phone lines. Telephone lines can be used for alarms/communication. Alarm systems may need modification. | [11 empty] | 0 | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | P12 | Vehicle Expenses |  | INR | [5 empty] | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | P13 | Asbestos O&M |  | R |  |  | Asbestos Implementation Manual, Sec 10 |  | Decommissioning Plan to maintain or modify the existing Asbestos O&M program for the maintenance of asbestos that could become externally airborne and create an environmental hazard. NESHAP has a ‘no visible emissions’ rule for ACM. OSHA has exposure thresholds for worker protection, both 1-hr and 8-hr standards. Prompt cleanup of ACM is important to remain in compliance with both NESHAP (visible emissions) and OSHA (exposure thresholds). | [5 empty] | 53000 | 400 |  | 15000 |  | 10000 | 53000 | X |  |  |  |  | 53000 | 0 | 0 | 53000 | [5 empty] | 0 | 1 | 0 | 0 | 0 | 53000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 53000 | 0 | 0 | 0 | 0 | 0 | 0
151 | S1 | Job Safety Analysis | Ginocchi | R |  |  |  |  | AEP Safety to create JSA for decommissioned units. | 160 | [10 empty] | 11200 | X |  |  |  |  | 11200 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 11200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | S2 | Clearance Permit Command Center | Ginocchi | R |  |  |  |  | Establish clearance permit command center | [11 empty] | 0 | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 | O1 | Accounting & Finance | Belter | M | x |  |  |  | Comply with Accounting and Finance requirements. | 1380 | [9 empty] | 10000 | 106600 | X |  |  |  |  | 106600 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 106600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106600 | 0 | 0 | 0
154 | O2 | Audit Services | Festi/Martin | M | x |  |  |  | Comply with audit requirements. | [11 empty] | 0 | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | O3 | Coal Pile Inventory Reduction & Management ~($2.8M is considered a C Item) | Welsh | M | x |  | AEP Disposition Unit Coal Pile Management Strategy (2013-06-26) | X | Burn down inventory. Remove coal and other material (coal-soil-stone mix) in yard. Correct the book coal inventory to zero. At sites where other coal units remain in-service, the out-of-service bunkers/silos must be cleaned and the feed/path to them must be stopped/sealed. | [8 empty] | 2982295 |  |  | 2982295 | X |  |  |  | Fuel Handling if X-fer Coal to Keeper Units | 182295 | 2800000 | [7 empty] | 1 | 0 | 0 | 0 | 182295 | 0 | 0 | 0 | 0 | 0 | 2800000 | 0 | 0 | 0 | 0 | 0 | 182295 | 0 | 0 | 0
156 | O4 | Other consumables |  | R |  |  |  |  | Plant and FEL to determine plan to manage consumable chemical inventories. | 40 | [10 empty] | 2800 |  |  |  |  | Fuel | [9 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | O5 | Insurance - Liability | Bradley | R |  |  |  |  | Liability insurance carried on all units as long as we own the property (regardless of operating status) | [11 empty] | 0 |  |  |  |  | Insur | [9 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | O6 | Insurance - Property | Zuckerman | R |  |  |  |  | Property insurance NOT carried (CR3, GL56, KR12, SP15, CV3, PI5, BS2) and carried (TC14, MR15, BS1, KM13, NE4, WLSH2) and renewed in May 2013 | n/a | [15 empty] | Insur | [9 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | O7 | Land Leases/Real Estate | Ireland | R |  |  |  |  | Honor existing land contracts. GL Ash Pond (COE)? 115-acre of PI leased for agricultural (ref Ph1 ESA) | n/a | [15 empty] | Land Mgt | [9 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | O8 | Legal | Mazzei-Smith | M | x |  |  |  | Comply with legal requirements. | [11 empty] | 0 | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | O9 | NERC-CIP |  | M | x |  |  |  | Comply with NERC-CIP requirements. | 80 | [10 empty] | 5600 | X |  |  |  |  | 5600 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 5600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5600 | 0 | 0 | 0
162 | O10 | Property Taxes | Brandon Parmer | M | x |  |  |  | Comply with tax requirements. | [11 empty] | 0 |  |  |  |  | Tax | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | O11 | Purchase Order Closeout | Belter | R |  |  |  |  | Manage or close outside agreements/contracts. | 320 | [10 empty] | 22400 | X |  |  |  |  | 22400 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 22400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | O12 | Records Retention | Rhem/Felrath | M | x |  | AEP Records Retention Manual |  | Send original documents required by Legal to RIMS Long Term Storage. Plants will manage this process. |  |  |  |  | 15000 | [6 empty] | 15000 | X |  |  |  |  | 15000 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 15000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 0 | 0 | 0
165 | O13 | Security | Queeno/Partlow | R |  |  | Physical Security Plan for Decommissioned Sites, 3/8/2014 | X | Security Plan will include one guard during the day shift and two during the night shift for fully decommissioned plants, and no change to current security plan for partially decommissioned plants. No additional cameras will be installed. Determination of additional physical barricades to be made by AEP Security and Plant. | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | O14 | Storeroom/Inventory/Spare Parts Management | Hamilton | C |  |  |  |  | Generation Operations & Procurement will redeploy high dollar, high use items to other facilities. Remaining items will either be scrapped or bid. Plan to be developed by Q2 2014. | 320 | 160 | [9 empty] | 33600 |  | X |  |  | Stores | 0 | 33600 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | O15 | Asset Recovery/Installed Components | Hevener | R |  |  |  |  | AEP Asset Recovery to develop Asset Recovery Plan. Assets to include installed components (conveyor belts, reverse osmosis systems, etc.), spare components, and Mobile Material & Equipment (MME). Plan to be developed by Q2 2014. | 160 | [10 empty] | 11200 |  | X |  |  | Stores | 0 | 11200 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | O16 | Transmission Mitigation - Switchyard | Jay Zeek | INR |  |  | Generation Retirement High Level Assessment |  | Transmission is leading this effort. | n/a | [11 empty] | X | X |  |  | Transm | 0 | 0 |  | 0 | [5 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | O17 | Corporate Communications | Holliday | R |  |  | Communications Template, Power Plant Decommissioning, March 2014 |  | AEP Corporate Communications plan (which can be customized by the plants) outlines timing/messages to be used in communications with pertinent internal/external stakeholders in advance of -- and during -- decommissioning activities. | 40 | [10 empty] | 2800 | X |  |  |  |  | 2800 | 0 | [7 empty] | 0 | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | O18 | Final Coal Pile Surveys & Associated Schedule | Flynn | M | x |  |  |  |  | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | O19 | Coal Pile Accounting | Dooley | M | x |  |  |  |  | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 | N1 | City Water Permits (backflow preventer) | Lewis | M | x |  |  |  |  | 80 | [5 empty] | 160 |  |  |  | 3000 | 19800 | X |  |  |  |  | 19800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 19800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19800 | 0 | 0 | 0
173 | N2 | Railroad Permits | Lewis | INR | [5 empty] | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | N3 | Occupancy Permits | Lewis | INR | [5 empty] | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | N4 | Department of Highways Permits | Lewis | INR | [5 empty] | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | N5 | Fire Marshal Permits | Lewis | INR | [5 empty] | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | EV1 | Modify the Acid Rain and Title V air permit | AQS | M | x |  | CAA |  |  |  | 56 | [9 empty] | 3920 | X |  |  |  |  | 3920 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 3920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3920 | 0 | 0 | 0
178 | EV1.1 | Submit CAIR notification (if necessary) | AQS | M | x |  | CAA |  |  |  | 6 | [9 empty] | 420 | X |  |  |  |  | 420 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0
179 | EV2 | Revise Nox Averaging Plan | AQS | M | x |  | CAA |  |  |  | 32 | [9 empty] | 2240 | X |  |  |  |  | 2240 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2240 | 0 | 0 | 0
180 | EV3 | Remove the plant from the CAMD Allowance Management System | AQS | M | x |  | CAA |  |  |  | 12 | [9 empty] | 840 | X |  |  |  |  | 840 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 0 | 0 | 0
181 | EV3.1 | File Retirement Unit Exemption form with Clean Air Markets Division | AQS | M | x |  | CAA |  |  |  | 12 | [9 empty] | 840 | X |  |  |  |  | 840 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 0 | 0 | 0
182 | EV4 | Complete Greenhouse Gas Reporting for 3 years following decomission | AQS | M | x |  | CAA | X |  |  | 18 | [9 empty] | 1260 | X |  |  |  |  | 1260 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 1260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1260 | 0 | 0 | 0
183 | EV4.1 | After 3 years of reporting "0" emissions, submit Certificate of Representation | AQS | M | x |  | CAA |  |  |  | 8 | [9 empty] | 560 | X |  |  |  |  | 560 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0
184 | EV5 | Update the emissions certification & monitoring plan System | AQS | M | x |  | CAA |  |  |  | 8 | [9 empty] | 560 | X |  |  |  |  | 560 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0
185 | EV5.1 | Register tradable emission reductions with State | AQS | M | x |  | CAA |  |  |  | 12 | [9 empty] | 840 | X |  |  |  |  | 840 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 0 | 0 | 0
186 | EV6 | Continue the EPCRA Section 313 TRI reporting for remaining units | AQS | M | x |  | EPCRA |  |  |  | as needed | [10 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | EV7 | Update EPCRA/CERCLA continuous release report | AQS | M | x |  | EPCRA |  |  |  | 10 | [9 empty] | 700 | X |  |  |  |  | 700 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 0 | 0 | 0
188 | EV8 | Notify Consent Decree plaintiffs of removal of unit | AQS | M | x |  | Consent Decree |  |  |  | 12 | [9 empty] | 840 | X |  |  |  |  | 840 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 0 | 0 | 0
189 | EV9 | File retirement notice with US DOE (for the Energy Information Admin. Reports {EIA 860-M}) | AQS | M | x |  | EIA |  |  |  | 12 | [9 empty] | 840 | X |  |  |  |  | 840 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 0 | 0 | 0
190 | EV10 | Submit NESHAP notifications as needed for demolitions and asbestos abatement/renovations | Plant | M | x |  | NESHAP |  |  |  | as needed | [10 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | EV11 | Evaluate status of water withdrawal needs and modify registration / permit accordingly | WERS | M | x |  |  |  |  | 24 | [10 empty] | 1680 | X |  |  |  |  | 1680 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 1680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1680 | 0 | 0 | 0
192 | EV12 | Evaluate status of potable water supply and make necessary notifications | WERS | M | x |  |  |  |  | 24 | [10 empty] | 1680 | X |  |  |  |  | 1680 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 1680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1680 | 0 | 0 | 0
193 | EV13 | Evaluate what changes to the water balance result and modify NPDES permit | WERS | M | x |  | NPDES |  |  |  | 200 | [9 empty] | 14000 | X |  |  |  |  | 14000 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 14000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 0 | 0 | 0
194 | EV13.1 | Determine if any sources within unit(s) will continue to be discharged | Plant | M | x |  | NPDES |  |  | 40 | [10 empty] | 2800 | X |  |  |  |  | 2800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0
195 | EV13.2 | Determine how stormwater will continue to be handled | Plant | M | x |  | NPDES |  |  | 40 | [10 empty] | 2800 | X |  |  |  | May be CAP for active units | 2800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0
196 | EV13.3 | Determine how any pond or landfill leachate or seepage will be managed | Plant | M | x |  | NPDES |  |  | 40 | [10 empty] | 2800 | X |  |  |  | May be CAP for active units | 2800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0
197 | EV13.4 | Determine requirements to close plant's sewage treatment system or municipal connecton | Plant | M |  | x | NPDES |  |  | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | EV13.5 | Incorporate modifications into upcoming NPDES renewal | WERS | M | x |  | NPDES | [13 empty] | 0 | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | EV14 | Remediate stains and spills discovered upon removal of T/R sets and other electrical equip. | LERS | M | x |  | TSCA |  |  |  | 40 | [9 empty] | 2800 | X |  |  |  |  | 2800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0
200 | EV14.1 | Remove and dispose of fluid in the non-PCB T/R sets and other electical equipment | LERS | M |  | x | SPCC |  |  | 160 | 40 | [9 empty] | 14000 |  | X |  |  |  | 0 | 14000 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | EV14.2 | Inventory and determine PCB concentration in electrical equipment and operating equipment and determine disposition | LERS | M | x |  | TSCA/SPCC |  |  |  | 40 | [9 empty] | 2800 |  | X |  |  |  | 0 | 2800 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | EV15 | Inventory all chemicals and decide on disposition | LERS | M | x |  | RCRA |  |  |  | 40 | [9 empty] | 2800 | X |  |  |  |  | 2800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0
203 | EV15.1 | Identify, perform waste determination/classification, quantify, store properly and dispose of waste chemicals within 90 days of detemination (longer times may be available depending on volumes). | LERS | M | x |  | RCRA |  |  |  | 40 | [9 empty] | 2800 | X |  |  |  |  | 2800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0
204 | EV15.2 | Determine and implement applicable RCRA requirements if generator status changes | LERS | M | x |  | RCRA |  |  |  | 40 | [9 empty] | 2800 | X |  |  |  |  | 2800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0
205 | EV15.3 | Identify mercury / mercury containing equipment and determine disposition | LERS | M |  | x | RCRA |  |  | 100 | 40 | [6 empty] | 10000 |  |  | 19800 | X | X |  |  |  | 9900 | 9900 | [7 empty] | 1 | 0 | 0 | 0 | 9900 | 0 | 0 | 0 | 9900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | EV16 | Collect and recycle all volumes of oil | LERS | M |  | x | RCRA |  |  |  | 40 | [9 empty] | 2800 | X |  |  |  |  | 2800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | EV17 | Modify the oil SPCC plan (& Facility Response Plan if applicable) | WERS | M | x |  | SPCC |  |  |  | 40 | [9 empty] | 2800 | X |  |  |  |  | 2800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0
208 | EV17.1 | Permanently close or remove any bulk oil storage containers and operating equipment. | Plant | M |  | x | SPCC |  |  | 160 | [7 empty] | 10000 |  |  | 21200 | X | X |  |  |  | 10600 | 10600 | [7 empty] | 1 | 0 | 0 | 0 | 10600 | 0 | 0 | 0 | 10600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | EV17.2 | Notify US Coast Guard and/or USEPA if the Facility Response Plan is terminated | WERS | INR |  |  | SPCC |  |  | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | EV17.3 | Kentucky requires a closure registration notification per tank to KDEP 14 days prior to closure | WERS | M | x |  | KDEP |  |  | 24 | [10 empty] | 1680 | X |  |  |  |  | 1680 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 1680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1680 | 0 | 0 | 0
211 | EV18 | Modify SARA Emergency Planning / Chemical Inventory notification if chemicals are brought onto or removed from site | LERS | M | x |  | EPCRA |  |  |  | 40 | [9 empty] | 2800 | X |  |  |  |  | 2800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0
212 | EV19 | Develop and / or implement waste management unit closure plan (landfill and ponds) | LERS | M | x |  | RCRA |  |  |  | 40 | [9 empty] | 2800 | X |  |  |  |  | 2800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2800 | 0 | 0 | 0
213 | EV20 | Identify and remove all unnecessary radioactive sources | LERS | M |  | x | NRC |  |  | 120 | 40 | [6 empty] | 100000 |  |  | 111200 | X |  |  |  |  | 111200 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 111200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 | EV20.1 | Continue inspections of necessary radioactive sources | LERS | M | x |  | NRC |  |  | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | EV20.2 | Modify licenses to reflect the removal of unnecessary radioactive sources | LERS | M |  | x | NRC |  |  | 40 | [10 empty] | 2800 | X |  |  |  |  | 2800 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 2800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 | EV20.3 | Identify and determine disposition of generallly-licensed radioactive material remaining in place (e.g. Tritium exit signs, smoke detectors, luminous faceplates or pointers on instruments) | Plant | M |  | x | NRC |  |  | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | EV21 | Maintain the protective coatings on asbestos containing material | Plant | M | x |  | NESHAP |  |  | 160 | [5 empty] | 1000 |  |  |  | 4000 | 85200 | X |  |  |  |  | 85200 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 85200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85200 | 0 | 0 | 0
218 | EV22 | Appropriately monitor and manage Bilge water (if necessary) | Plant | M | x |  | NPDES | X |  | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219 | EV23 | Modify permits / notifications regarding the plant's sanitary waste facilities (if necessary) | WERS | M | x |  | NPDES |  |  | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220 | EV23.1 | Determine through Corps of Engineers whether waterway structures must be removed | WERS | INR |  |  | USACE |  |  | n/a | [12 empty] | X |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221 | EV24 | Remove waterway structures (if necessary) | Plant | INR |  |  | USACE |  |  |  | 80 | [9 empty] | 5600 |  | X |  |  |  | 0 | 5600 | [7 empty] | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222 | EV25 | Appropriately modify / update any wildlife habitat or DNR certifications / permits | WERS | M | x |  | DNR |  |  | 24 | [10 empty] | 1680 | X |  |  |  |  | 1680 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 1680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1680 | 0 | 0 | 0
223 | R1 | NERC/FERC Requirements |  | M | x |  |  |  |  | 80 | [10 empty] | 5600 | X |  |  |  |  | 5600 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 5600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5600 | 0 | 0 | 0
224 | R2 | Regulatory Requirements | Banks-Smith | M | x |  |  |  |  | n/a | [11 empty] | X |  |  |  |  | 0 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | R3 | PJM Interconnection and Interconnection Agreements | Tom Fecho | M | x |  | Plant IA's |  | PJM, Regulatory Services and Transmission Coordination/Notifications | 16 | [10 empty] | 1120 | X |  |  |  | Transm | 1120 | 0 | [7 empty] | 1 | 0 | 0 | 0 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0 | 0
[9 empty] | Totals | 29602 | 4118 | 0 | 0 | 70000 | 113000 | 12905 | 903350 | 5037295 | 5940645 | 426000 | 8797045 | [5 empty] | 3005565 | 5371680 | 0 | 403000 | 67000 | [20 empty] | 991195 | 0 | 0 | 0
[11 empty] | 33720 | [7 empty] | 6837595 | [7 empty] | 859450 | 37503
[11 empty] | 70 | [6 empty] | 6-30-14 Estimate | 6624622.4 | [7 empty] | 3865015 | 5409183 |  |  |  | Total | 9744198 | [18 empty] | M Items Total | 1950895
[11 empty] | 2360400 |  |  | 70000 |  |  | 426000 | 5940645 | -212972.6
[14 empty] | 8797045 | 350000 | 2716575 | 5730470 | 6627420
Misc. Items
|  | Misc Scaffold |  | C | [13 empty] | 75000 |  |  | 75000 | X | X |  |  |  | 37500 | 37500 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 37500 | 0 | 0 | 0 | 37500 | 0 | 0 | 0 | 0 | 0
|  | PLT/Labor for Battery Removal |  | C | [7 empty] | 7500 | [8 empty] | 0 | X |  |  |  |  | 0 | 0 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Remove Insulation on Turbine for RSO |  | C | [13 empty] | 75000 |  |  | 75000 |  | X |  |  |  | 75000 | 1 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 75000 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
|  | NAIS to clean Unit Internal and External |  | C | [13 empty] | 746950 |  |  | 746950 | X |  |  |  |  | 746950 | 2 | [7 empty] | 0 | 0 | 1 | 0 | 0 | 0 | 746950 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0
[9 empty] | Totals | 0 | 0 | 7500 | 0 | 0 | 0 | 0 |  | 896950 | [8 empty] | 859450 | 37503 | [11 empty] | 1172195 | 1561620 | 1091200 | 40000 | 778700 | 262500 | 4362383 | 5600 | 0 | 403000 | 0 | 0
[20 empty] | 2015 | [10 empty] | 2015 |  | 2016 | [5 empty] | 2016 |  |  | O&M Total | 3865015 |  |  | Removal Total | 5409183 |  |  | Asbestos Total | 403000
[17 empty] | Regulated Plants | Units | OPCo | O&M | 108 Removal | [5 empty] | Asbestos ARO | Pond ARO | Total $$$ | Total wo/ARO $$$ | Incremental O&M f/Forecast | Incremental Removal f/Forecast | O&M | 108 Removal | Asbestos ARO | Pond ARO | Total $$$ | Total wo/ARO $$$ | Incremental O&M f/Forecast | Incremental Removal f/Forecast |  |  |  |  | 9744198
[17 empty] | Big Sandy | 2 | KPCo | 773003 | 1081836.6 | [5 empty] | 80600 | 13400 |  |  |  |  | 3092012 | 4327346.4