## KPCo Outages
Kentucky Power Co.
05/01/2014 To 10/31/2014
Big Sandy Unit 1
HOURS OF DURATION
Month | From | To | Scheduled | Forced | Reserve Shutdown | Reason for Outage
May | 2014-04-18 01:16 | 2014-05-09 11:32 | 203.53 |  |  | Repair 1A1 and 1A3 SIRs
May | 2014-05-09 11:32 | 2014-05-10 08:22 |  |  | 20.83 | Reserve Shutdown
May | 2014-05-10 09:26 | 2014-05-10 09:37 |  | 0.18 |  | Governor Valve Issue
July | 2014-07-10 09:07 | 2014-07-11 |  | 14.88 |  | Had to trip unit due to loss of precip bus.
July | 2014-07-11 | 2014-07-12 |  |  | 24 | Reserve Shutdown
July | 2014-07-12 | 2014-07-21 02:55 | 218.92 |  |  | Precip Inspection
July | 2014-07-21 02:55 | 2014-07-21 21:16 |  |  | 18.35 | Reserve Shutdown
September | 2014-09-05 23:46 | 2014-09-06 |  | 0.23 |  | Out of Coal
September | 2014-09-06 | 2014-11-15 14:52 | 1344 |  |  | General maintenance.
Kentucky Power Co.
05/01/2014 To 10/31/2014
Big Sandy Unit 2
HOURS OF DURATION
Month | From | To | Scheduled | Forced | Reserve Shutdown | Reason for Outage
May | 2014-05-15 09:03 | 2014-05-18 13:47 |  | 76.73 |  | Tube leak
May | 2014-05-18 13:47 | 2014-05-25 16:00 | 170.22 |  |  | Replace HSO to GSLO Condenser, Casing Leaks, Reolocate HP filters on the EHC system.
May | 2014-05-25 16:00 | 2014-05-26 06:15 |  |  | 14.25 | Reserve Shutdown
July | 2014-07-04 05:11 | 2014-07-04 08:30 |  | 3.32 |  | Booster fan issue
July | 2014-07-04 08:30 | 2014-07-07 06:50 |  |  | 70.33 | Reserve Shutdown
August | 2014-08-08 01:45 | 2014-08-08 15:00 |  | 13.25 |  | Big Sandy 2 Tripped
August | 2014-08-08 15:00 | 2014-08-09 01:20 |  |  | 10.33 | Reserve Shutdown
September | 2014-09-12 23:19 | 2014-09-13 |  | 0.68 |  | Ran out of Coal
September | 2014-09-13 | 2014-12-08 03:54 | 1176 |  |  | General maintenance
Kentucky Power Co.
05/01/2014 To 10/31/2014
Mitchell Unit 1
HOURS OF DURATION
Month | From | To | Scheduled | Forced | Reserve Shutdown | Reason for Outage
May | 2014-05-21 23:59 | 2014-06-08 23:59 | 432 |  |  | General Boiler Inspection/Repair - GBIR
June | 2014-06-08 23:59 | 2014-06-09 |  |  | 0.02 | Reserve Shutdown
June | 2014-06-09 | 2014-06-09 16:41 | 16.68 |  |  | Continue planned outage tube repairs in the ash hopper area.
June | 2014-06-13 05:11 | 2014-06-14 16:47 | 35.6 |  |  | #12 ID Fan Hydraulic Leak Repairs
June | 2014-06-14 16:47 | 2014-06-15 11:52 |  |  | 19.08 | Reserve Shutdown
July | 2014-07-02 03:29 | 2014-07-03 10:05 |  | 30.6 |  | External steam leak on main turbine
July | 2014-07-03 10:05 | 2014-07-05 05:25 | 43.33 |  |  | Main steam line drain piping inspections
July | 2014-07-05 05:25 | 2014-07-06 09:59 |  |  | 28.57 | Reserve Shutdown
October | 2014-10-01 10:07 | 2014-10-06 |  | 109.88 |  | Tube Leak
October | 2014-10-06 | 2014-10-11 | 120 |  |  | Planned Outage preparation
October | 2014-10-11 | 2014-11-02 15:52 | 504 |  |  | General Maintenance
Kentucky Power Co.
05/01/2014 To 10/31/2014
Mitchell Unit 2
HOURS OF DURATION
Month | From | To | Scheduled | Forced | Reserve Shutdown | Reason for Outage
May | 2014-05-10 00:06 | 2014-05-18 12:28 | 204.37 |  |  | General Boiler Inspection/Repair - GBIR
June | 2014-06-28 13:20 | 2014-06-29 21:12 |  | 31.87 |  | Loss of 600V Kv buss. due to fault
June | 2014-06-29 21:12 | 2014-06-30 06:09 |  |  | 8.95 | Reserve Shutdown
August | 2014-08-11 08:03 | 2014-08-19 06:15 | 190.2 |  |  | Economizer tube leak repairs
August | 2014-08-19 06:15 | 2014-08-19 13:30 |  |  | 7.25 | Reserve Shutdown
August | 2014-08-19 13:30 | 2014-08-20 13:30 |  | 24 |  | Hydrolyzer condensate return line leak.
August | 2014-08-20 13:30 | 2014-08-21 18:00 |  | 28.5 |  | Hydrolyzer condensate return line leak then #21 ID Fan Bearing Lift Oil Low Flow
August | 2014-08-21 18:00 | 2014-08-22 08:06 |  |  | 14.1 | Reserve Shutdown
September | 2014-09-21 03:40 | 2014-09-24 10:30 |  | 78.83 |  | Exciter brush issues
September | 2014-09-24 10:30 | 2014-09-24 22:42 |  |  | 12.2 | Reserve Shutdown
September | 2014-09-24 23:04 | 2014-09-24 23:23 |  | 0.32 |  | Unit needs to come off line to reset valves
October | 2014-10-23 07:00 | 2014-10-23 13:49 |  | 6.82 |  | Control Valve Failed closed causing turbine vibration.
October | 2014-10-23 13:49 | 2014-10-23 17:42 |  |  | 3.88 | Reserve Shutdown