## KP
KP
Current Loss Factors
| Test Year Ending: | 2014-12-31
Loss Factors by System
| System | Total | Fixed
Demand
| Transmission | 0.04534 | 0.0031797
| Subtransmission-Reg | 0.023208 | 0.0010851
Subtransmission-Adj
| Primary Distribution | 0.02863 | 0.002097 | See Note 3
| Secondary Distribution | 0.032474 | 0.011309
Energy
| Transmission | 0.02972
| Subtransmission-Reg | 0.014101
Subtransmission-Adj
| Primary Distribution | 0.015245 |  | See Note 3
| Secondary Distribution | 0.026059
Cumulative Loss Factors
(Compounded)
System
Demand
| Transmission | 1.0453
| Subtransmission | 1.0696
| Primary Distribution | 1.0886
| Secondary Distribution | 1.1239
Energy
| Transmission | 1.0297
| Subtransmission | 1.0442
| Primary Distribution | 1.0584
| Secondary Distribution | 1.0859
Notes:
(1) | Updated with results from final MAC study dated March 2016.
(2) | Cumulative Loss Factors are applicable to load metered at respective system voltages to determine losses back to the generator.
(3) | MAC study value taken from Exhibit 8.

## Calculations (Exhibits 5 & 8)
From Exhibit 5 (Unadjusted, Connected Load) |  |  | From Exhibit 8 (Adjusted, Internal Load Only)
Primary Distribution Loss Factor |  |  | Primary Distribution Loss Factor
| Demand | Energy |  | Demand | Energy
DISTRIBUTION SUBST | 1.0051 | 1.0061 | DISTRIBUTION SUBST | 1.0057 | 1.006
PRIMARY LINES | 1.0204 | 1.0093 | PRIMARY LINES | 1.0228 | 1.0091
Cumulative (Calculated) | 1.0257 | 1.0154 | Cumulative (Calculated) | 1.0286 | 1.0152
Fixed and Variable Losses (Demand Only)
| Fixed | Variable
| (NO LOAD) | (LOAD)
| (MW) | (MW)
Transmission | 4.32 | 57.28
Subtransmission | 1.24 | 25.28
Primary Distribution
Substations | 2.22 | 3.99
Lines | 0 | 24.1
Subtotal | 2.22 | 28.09
Secondary Distribution
Line Transformers | 10.46 | 5.55
Secondary | 0 | 7.01
Services | 0.36 | 7.69
Subtotal | 10.82 | 20.25
Load Distribution
Input to Distr Transf: | MW LOAD
Connected to 161 kV | 14.8
Connected to 138 kV | 274.2
Connected to 69 kV | 743.7
Connected to 46 kV | 172.6
Connected to 34 kV | 6.2
Total | 1211.5
Distr Load on Trans | 23.85%
Distr Load on Subtrans | 76.15%
100%