## KU Summary
KENTUCKY UTILITIES COMPANY
ENVIRONMENTAL SURCHARGE REPORT
Pollution Control - Operations & Maintenance Expenses
| O&M Expense Account | 2017-03-01 | 2017-04-01 | % Change from Prior Period | Variance Explanation from Prior Period | 2017-05-01 | % Change from Prior Period | Variance Explanation from Prior Period | 2017-06-01 | % Change from Prior Period | Variance Explanation from Prior Period | 2017-07-01 | % Change from Prior Period | Variance Explanation from Prior Period | 2017-08-01 | % Change from Prior Period | Variance Explanation from Prior Period
2009 Plan
506154 | ECR NOx Operation -- Consumables | 9181.22 | 37371.49 | 307% | Ammonia purchase at EW Brown to fill tanks in preparation for summer load | 27834.94 | -25.52% | Additional purchase in May due to 45% increase in generation at EW Brown | 26597.69 | -4.44% |  | 41143.77 | 54.69% | 21% increase in generation at EW Brown over June | 22281.32 | -45.85% | 32% deccrease in generation at EW Brown over July and 7% decrease in price
506155 | ECR NOx Operation -- Labor and Other | 0 | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0%
512151 | ECR NOx Maintenance | -665.88 | 4312.64 | 747.7% | Returned a valve checked out of inventory in February but not used resulting in March credit | 41326.28 | 858.3% | SCR Sonic Air Horns repaired at EW Brown | 44977.17 | 8.83% |  | 22284.76 | -50.45% | Lower maintenance costs at EW Brown due to availability of unit (higher generation compared to June) | 45781.7 | 105.4% | Annual Catalyst testing and higher maintenance costs due to unit availability at EW Brown (lower generation compared to July)
506159 | ECR Sorbent Injection Operation | 0 | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0%
506152 | ECR Sorbent Reactant - Reagent Only | 0 | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0%
512152 | ECR Sorbent Injection Maintenance | 0 | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0%
502013 | ECR Landfill Operations | 388719 | 339545 | -12.65% | Lower costs for pipe conveyor repairs at Ghent | 322940 | -4.89% |  | 335017 | 3.74% |  | 331446 | -1.07% |  | 332322 | 0.26%
512107 | ECR Landfill Maintenance | 374213 | 167149 | -55.33% | Ash Transport line repairs in March at Ghent | 202427 | 21.11% | Gypsum building sump pump repairs at Ghent | 251767 | 24.37% | Vacuum Cloth Belt repairs; belt repairs; transport blower valve repairs at Ghent | 267062 | 6.08% |  | 305024 | 14.21% | Install new gypsum dewatering belt steam hood drying system including rental of boiler at Ghent
| Total 2009 Plan O&M Expenses | 771447.34 | 548378.13 | -28.92% |  | 594528.22 | 8.42% |  | 658358.86 | 10.74% |  | 661936.53 | 0.54% |  | 705409.02 | 6.57%
2011 Plan
506159 | ECR Sorbent Injection Operation | 49415.03 | 46168.47 | -6.57% |  | 47731.18 | 3.38% |  | 46015.94 | -3.59% |  | 43683.82 | -5.07% |  | 77441.77 | 77.28% | SO3 Operations Ghent -correction to January contract labor in amount of $34k incorrectly classified to wrong account. This was noted and communicated to the KPSC in the last 6-month/2-year ECR Case No. 2017-00266 (Response to Question 4 of the Commission Staff’s First Request for Information Dated July 27, 2017), as expenses "from January 2017 were incorrectly classified as non-ECR expenses and will be corrected in August 2017."
506152 | ECR Sorbent Reactant - Reagent Only | 751239.47 | 545050.81 | -27.45% | Lower hydrated lime usage - Ghent Unit 4 on outage; Lower generation at EW Brown | 725240.32 | 33.06% | Higher hydrated Lime usage - Ghent Unit 4 on outage in April; Higher generation at EW Brown | 817715.45 | 12.75% | Higher hydrated lime usage due to generation | 873733.48 | 6.85% |  | 841429.63 | -3.7%
512152 | ECR Sorbent Injection Maintenance | 34093.86 | 26809.81 | -21.36% | SO3 12" Blow thru rotary air lock repairs at Ghent; Servicing Sorbent Injection Air Compressors at EW Brown | 8169.4 | -69.53% | Minimal maintenance required at Ghent and EW Brown | 23909.21 | 192.7% | SO3 Air Compressor maintenance at Ghent | 22331.08 | -6.6% |  | 22013.13 | -1.42%
506156 | ECR Baghouse Operations | 0 | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0%
512156 | ECR Baghouse Maintenance | 24715.97 | 27506.12 | 11.29% | Additional maintenance performed during Ghent Unit 4 outage | 21274.49 | -22.66% | Decrease in routine maintenance due to Ghent units running all month | 53401.06 | 151% | Air Compressor maintenance and Air Dryer Switching Repair at Ghent; Ghent unit 1 sample testing; Purchased 2 filter kits at EW Brown | 43915.75 | -17.76% | Lower Air Compressor maintenance and Air Dryer Switching Repair at Ghent; no Ghent unit 1 sample testing | 42142.44 | -4.04%
506151 | ECR Activated Carbon | 460342.2 | 388403.4 | -15.63% | Lower activated carbon due to Ghent Unit 4 outage | 485547.94 | 25.01% | Higher activated carbon due to generation and Ghent Unit 4 outage in April | 485833.19 | 0.06% |  | 443874.2 | -8.64% |  | 413490 | -6.85%
502013 | ECR Landfill Operations | 61727 | 62869 | 1.85% |  | 64943 | 3.3% |  | 101097 | 55.67% | Groundwater monitoring and reporting at EW Brown | 64373 | -36.33% | Groundwater monitoring and reporting at EW Brown in June | 65724 | 2.1%
512107 | ECR Landfill Maintenance | 84490 | 74559 | -11.75% | Lower costs at EW Brown due to repairs to submerged flight conveyor in March | 82830 | 11.09% | Repairs to Gypsum Dewatering system belts and roller at EW Brown | 96496 | 16.5% | Repairs to Paddle Mixers at EW Brown | 126761 | 31.36% | Install disconnects on hoists in both ash silos at EW Brown | 101618 | -19.83% | Lower costs to install disconnects on hoists in both ash silos at EW Brown in July
| Total 2011 Plan O&M Expenses | 1466023.53 | 1171366.61 | -20.1% |  | 1435736.33 | 22.57% |  | 1624467.85 | 13.15% |  | 1618672.33 | -0.36% |  | 1563858.97 | -3.39%
The 2001 Plan was eliminated from ECR recovery in August 2010 per PSC Order No. 2009-00549.
2016 Plan
506153 | ECR Liquid Injection - Reagant Only | 0 | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0%
| Total 2016 Plan O&M Expenses | 0 | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0% |  | 0 | 0%