## Coal MOR Detail
[15 empty] | 10 yrs (2008-2017) |  | 7 yrs (2011-2017) |  | 5 yrs (2013-2017)
[5 empty] | MOR% | [10 empty] | 0.5 |  | 0.5 |  | 0.5
Unit/Station | Winter Capacity | Spring/Fall Capacity | Summer Capacity | Average Capacity | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | Avg | 50th %ile | Avg | 50th %ile | Avg | 50th %ile
BR 1 | 107 | 106.5 | 106 | 106.5 | 3.117% | 2.714% | 1.05% | 0% | 5.905% | 4.102% | 2.959% | 13.73% | 4.467% | 2.363% | 4.04% | 3.038% | 4.789% | 4.102% | 5.524% | 4.102%
BR 2 | 168 | 167 | 166 | 167 | 2.3% | 1.973% | 2.018% | 6.979% | 4.336% | 1.52% | 7.643% | 2.229% | 8.173% | 0.9648% | 3.814% | 2.265% | 4.549% | 4.336% | 4.106% | 2.229%
BR 3 | 413 | 411 | 409 | 411 | 0.9427% | 3.471% | 2.029% | 0% | 5.622% | 4.252% | 12.94% | 1.793% | 10.44% | 3.481% | 4.497% | 3.476% | 5.504% | 4.252% | 6.581% | 4.252%
BR Station | 688 | 684.5 | 681 | 684.5 | 1.585% | 3.097% | 1.889% | 1.488% | 5.3% | 3.544% | 10.06% | 3.465% | 9.107% | 2.906% | 4.244% | 3.281% | 5.124% | 3.544% | 5.816% | 3.544%
GH 1 | 476 | 475 | 474 | 475 | 1.65% | 1.345% | 0.446% | 0% | 3.477% | 0.7576% | 4.251% | 3.075% | 0.669% | 2.977% | 1.865% | 1.497% | 2.172% | 2.977% | 2.346% | 2.977%
GH 2 | 475 | 484 | 493 | 484 | 3.623% | 1.319% | 0.3615% | 0% | 0.8085% | 1.817% | 2.465% | 0.2366% | 1.204% | 1.463% | 1.33% | 1.261% | 1.142% | 1.204% | 1.437% | 1.463%
GH 3 | 478 | 481.5 | 485 | 481.5 | 6.644% | 1.476% | 0.898% | 0% | 1.803% | 5.073% | 6.373% | 4.17% | 5.426% | 0.2945% | 3.216% | 2.986% | 3.306% | 4.17% | 4.267% | 5.073%
GH 4 | 487 | 476 | 465 | 476 | 1.079% | 1.915% | 0.4642% | 13.9% | 4.174% | 6.501% | 7.756% | 3.334% | 1.607% | 0.0003846% | 4.073% | 2.624% | 5.325% | 4.174% | 3.84% | 3.334%
GH Station | 1916 | 1916.5 | 1917 | 1916.5 | 3.332% | 1.53% | 0.5478% | 3.498% | 2.606% | 3.532% | 5.101% | 2.777% | 2.208% | 1.181% | 2.631% | 2.691% | 2.986% | 2.777% | 2.96% | 2.777%
MC 1 | 300 | 300 | 300 | 300 | 0.85% | 1.165% | 3.257% | 0.3874% | 2.157% | 4.965% | 8.142% | 5.066% | 3.933% | 2.941% | 3.286% | 3.099% | 3.942% | 3.933% | 5.01% | 4.965%
MC 2 | 295 | 296 | 297 | 296 | 2.305% | 2.398% | 4.099% | 4.958% | 2.242% | 4.922% | 11.82% | 4.972% | 1.435% | 1.311% | 4.047% | 3.249% | 4.524% | 4.922% | 4.893% | 4.922%
MC 3 | 394 | 392.5 | 391 | 392.5 | 1.586% | 1.345% | 2.757% | 3.862% | 2.459% | 3.126% | 5.061% | 8.086% | 3.229% | 1.38% | 3.289% | 2.941% | 3.886% | 3.229% | 4.176% | 3.229%
MC 4 | 486 | 481.5 | 477 | 481.5 | 2.167% | 2.874% | 4.226% | 5.031% | 4.104% | 6.278% | 13.42% | 6.082% | 0.02738% | 1.655% | 4.586% | 4.165% | 5.228% | 5.031% | 5.492% | 6.082%
MC Station | 1475 | 1470 | 1465 | 1470 | 1.779% | 2.028% | 3.601% | 3.735% | 2.815% | 4.933% | 9.502% | 6.243% | 1.999% | 1.766% | 3.84% | 3.208% | 4.427% | 3.735% | 4.888% | 4.933%
TC 1@75% | 369.75 | 369.75 | 369.75 | 369.75 | 2.197% | 3.063% | 0.9129% | 0% | 4.776% | 3.951% | 6.759% | 2.775% | 0.2044% | 1.905% | 2.654% | 2.486% | 2.91% | 2.775% | 3.119% | 2.775%
TC 2@75% | 570 | 559.5 | 549 | 559.5 |  |  |  | 14.29% | 4.31% | 3.908% | 14.16% | 1.026% | 7.292% | 2.981% | 6.852% | 4.31% | 6.852% | 4.31% | 5.873% | 3.908%
TC Station @75% | 939.75 | 929.25 | 918.75 | 929.25 | 2.197% | 3.063% | 0.9129% | 8.847% | 4.558% | 3.928% | 10.51% | 1.69% | 3.962% | 2.561% | 4.223% | 3.495% | 5.151% | 3.962% | 4.531% | 3.928%
GH+MC+TC1 | 3760.75 | 3756.25 | 3751.75 | 3756.25 | 2.573% | 1.864% | 1.78% | 3.232% | 2.906% | 4.109% | 7.151% | 4.07% | 1.927% | 1.485% | 3.11% | 2.74% | 3.554% | 3.232% | 3.748% | 4.07%

## Coal EFOR Detail
[15 empty] | 10 yrs (2008-2017) |  | 7 yrs (2011-2017) |  | 5 yrs (2013-2017)
[5 empty] | EFOR% | [10 empty] | 0.5 |  | 0.5 |  | 0.5
Unit/Station | Winter Capacity | Spring/Fall Capacity | Summer Capacity | Average Capacity | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | Avg | 50th %ile | Avg | 50th %ile | Avg | 50th %ile
BR 1 | 107 | 106.5 | 106 | 106.5 | 16.4% | 13.52% | 2.635% | 4.453% | 3.682% | 2.834% | 1.79% | 1.04% | 0.9399% | 5.937% | 5.322% | 3.258% | 2.954% | 2.834% | 2.508% | 1.79%
BR 2 | 168 | 167 | 166 | 167 | 3.5% | 5.488% | 7.897% | 6.702% | 2.823% | 3.32% | 2.75% | 0.29% | 0.878% | 1.019% | 3.467% | 3.072% | 2.54% | 2.75% | 1.652% | 1.019%
BR 3 | 413 | 411 | 409 | 411 | 6.312% | 6.613% | 1.051% | 5.778% | 3.694% | 14.33% | 8.05% | 3.49% | 9.73% | 3.131% | 6.218% | 6.045% | 6.887% | 5.778% | 7.747% | 8.05%
BR Station | 688 | 684.5 | 681 | 684.5 | 7.085% | 7.009% | 3.07% | 5.799% | 3.44% | 9.836% | 5.71% | 2.28% | 6.609% | 2.804% | 5.364% | 5.755% | 5.211% | 5.71% | 5.448% | 5.71%
GH 1 | 476 | 475 | 474 | 475 | 6.336% | 12.03% | 2.626% | 4.257% | 9.539% | 5.117% | 2.37% | 5.91% | 3.951% | 3.089% | 5.523% | 4.687% | 4.891% | 4.257% | 4.087% | 3.951%
GH 2 | 475 | 484 | 493 | 484 | 12.39% | 3.883% | 1.227% | 2.335% | 2.863% | 1.7% | 0.72% | 2.4% | 1.09% | 1.014% | 2.963% | 2.017% | 1.732% | 1.7% | 1.385% | 1.09%
GH 3 | 478 | 481.5 | 485 | 481.5 | 8.296% | 4.32% | 7.368% | 3.104% | 2.36% | 3.566% | 1.9% | 3.63% | 4.186% | 2.65% | 4.138% | 3.598% | 3.057% | 3.104% | 3.186% | 3.566%
GH 4 | 487 | 476 | 465 | 476 | 4.037% | 3.757% | 3.171% | 3.579% | 1.977% | 6.021% | 2.93% | 2.07% | 4.075% | 3.49% | 3.511% | 3.535% | 3.449% | 3.49% | 3.717% | 3.49%
GH Station | 1916 | 1916.5 | 1917 | 1916.5 | 7.79% | 6.024% | 3.66% | 3.315% | 4.223% | 4.061% | 1.93% | 3.43% | 3.294% | 2.557% | 4.028% | 3.545% | 3.259% | 3.315% | 3.055% | 3.294%
MC 1 | 300 | 300 | 300 | 300 | 5.964% | 4.704% | 4.854% | 4.748% | 5.341% | 3.773% | 2.47% | 4.12% | 1.676% | 2.094% | 3.974% | 4.412% | 3.46% | 3.773% | 2.827% | 2.47%
MC 2 | 295 | 296 | 297 | 296 | 4.584% | 5.296% | 2.137% | 7.032% | 7.088% | 6.303% | 6.39% | 4.28% | 1.572% | 2.364% | 4.705% | 4.94% | 5.004% | 6.303% | 4.182% | 4.28%
MC 3 | 394 | 392.5 | 391 | 392.5 | 3.039% | 5.092% | 5.778% | 8.686% | 2.706% | 14.32% | 3.22% | 2.79% | 5.78% | 0.6706% | 5.209% | 4.156% | 5.454% | 3.22% | 5.357% | 3.22%
MC 4 | 486 | 481.5 | 477 | 481.5 | 6.191% | 2.978% | 5.001% | 10.55% | 21.24% | 10.49% | 10.01% | 1.33% | 2.686% | 2.481% | 7.296% | 5.596% | 8.399% | 10.01% | 5.4% | 2.686%
MC Station | 1475 | 1470 | 1465 | 1470 | 4.948% | 4.348% | 4.604% | 8.094% | 9.938% | 9.436% | 5.62% | 2.82% | 2.996% | 1.871% | 5.468% | 4.776% | 5.825% | 5.62% | 4.549% | 2.996%
TC 1@75% | 369.75 | 369.75 | 369.75 | 369.75 | 2.654% | 8.668% | 11.83% | 7.549% | 3.676% | 2.653% | 4.02% | 4.03% | 2.379% | 3.411% | 5.087% | 3.848% | 3.96% | 3.676% | 3.299% | 3.411%
TC 2@75% | 570 | 559.5 | 549 | 559.5 |  |  |  | 10.28% | 17.7% | 15.57% | 12.66% | 7.62% | 22.95% | 10.97% | 13.97% | 12.66% | 13.97% | 12.66% | 13.96% | 12.66%
TC Station @75% | 939.75 | 929.25 | 918.75 | 929.25 | 2.654% | 8.668% | 11.83% | 9.099% | 10.6% | 9.985% | 8.47% | 6.3% | 14.11% | 8.133% | 8.985% | 8.883% | 9.528% | 9.099% | 9.399% | 8.47%
GH+MC+TC1 | 3760.75 | 3756.25 | 3751.75 | 3756.25 | 6.183% | 5.612% | 4.801% | 5.627% | 6.481% | 5.987% | 3.723% | 3.309% | 3.133% | 2.381% | 4.724% | 5.207% | 4.377% | 3.723% | 3.707% | 3.309%

## PrimaryCT EFORd Detail
[15 empty] | 10 yrs (2008-2017) |  | 7 yrs (2011-2017) |  | 5 yrs (2013-2017)
[5 empty] | EFORd% | [10 empty] | 0.5 |  | 0.5 |  | 0.5
Unit/Station | Winter Capacity | Spring/Fall Capacity | Summer Capacity | Average Capacity | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | Avg | 50th %ile | Avg | 50th %ile | Avg | 50th %ile
BR5 | 130 | 120 | 130 | 125 | 7.44% | 17.95% | 28.18% | 17.46% | 23.7% | 12.65% | 6.67% | 3.57% | 8.86% | 20.04% | 14.65% | 15.06% | 13.28% | 12.65% | 10.36% | 8.86%
BR6 | 171 | 157 | 146 | 157.75 | 16.45% | 35.23% | 48.8% | 6.38% | 2.99% | 4.39% | 1.72% | 1.67% | 10.95% | 13.4% | 14.2% | 8.665% | 5.929% | 4.39% | 6.426% | 4.39%
BR7 | 171 | 157 | 146 | 157.75 | 8.69% | 21% | 6.87% | 8.45% | 2.54% | 11.53% | 3.56% | 1.53% | 14.29% | 15.35% | 9.381% | 8.57% | 8.179% | 8.45% | 9.252% | 11.53%
BR8 | 128 | 118 | 121 | 121.25 | 11.2% | 8.13% | 3.35% | 3.1% | 15.15% | 27.9% | 2.98% | 16.59% | 5.8% | 6.45% | 10.06% | 7.29% | 11.14% | 6.45% | 11.94% | 6.45%
BR9 | 138 | 118 | 121 | 123.75 | 18.04% | 22.26% | 5.03% | 8.85% | 4.1% | 3.29% | 2.64% | 7.12% | 8.08% | 8.3% | 8.771% | 7.6% | 6.054% | 7.12% | 5.886% | 7.12%
BR10 | 138 | 118 | 121 | 123.75 | 0.7% | 13.51% | 10.21% | 3.14% | 16.42% | 5.7% | 2.51% | 11.31% | 2.01% | 3.55% | 6.906% | 4.625% | 6.377% | 3.55% | 5.016% | 3.55%
BR11 | 128 | 118 | 121 | 121.25 | 31.22% | 12.42% | 14.01% | 7.65% | 8.42% | 37.72% | 3.81% | 8.65% | 4.01% | 15.49% | 14.34% | 10.54% | 12.25% | 8.42% | 13.94% | 8.65%
BR CTs (all) | 1004 | 906 | 906 | 930.5 | 13.28% | 19.38% | 17.51% | 7.855% | 9.922% | 14.14% | 3.361% | 6.762% | 8.089% | 12% | 11.23% | 10.96% | 8.876% | 8.089% | 8.872% | 8.089%
PR13 | 175 | 161 | 147 | 161 | 20.38% | 77.23% | 34.47% | 10.97% | 15.57% | 18.55% | 8.41% | 22.37% | 22.09% | 6.79% | 23.68% | 19.46% | 14.96% | 15.57% | 15.64% | 18.55%
TC5 | 179 | 169 | 159 | 169 | 1.67% | 0.15% | 11.13% | 7.19% | 2.78% | 2.75% | 1.63% | 7.7% | 5.85% | 3.44% | 4.429% | 3.11% | 4.477% | 3.44% | 4.274% | 3.44%
TC6 | 179 | 169 | 159 | 169 | 1.9% | 6.31% | 6.35% | 7.83% | 3.2% | 2.67% | 2.97% | 4.28% | 9.78% | 2.3% | 4.759% | 3.74% | 4.719% | 3.2% | 4.4% | 2.97%
TC7 | 179 | 169 | 159 | 169 | 8.04% | 3.62% | 2.67% | 2.48% | 6.96% | 2.38% | 2.77% | 8.55% | 3.9% | 6.68% | 4.805% | 3.76% | 4.817% | 3.9% | 4.856% | 3.9%
TC8 | 179 | 169 | 159 | 169 | 4.34% | 4.85% | 8.29% | 2.21% | 10.37% | 6.55% | 14.55% | 5.75% | 8.54% | 2.7% | 6.815% | 6.15% | 7.239% | 6.55% | 7.618% | 6.55%
TC9 | 179 | 169 | 159 | 169 | 2.21% | 0.24% | 3.75% | 3.42% | 3.86% | 4.91% | 8.27% | 5.04% | 0.36% | 1.47% | 3.353% | 3.585% | 3.904% | 3.86% | 4.01% | 4.91%
TC10 | 179 | 169 | 159 | 169 | 23.57% | 10.73% | 5.64% | 4.65% | 6.69% | 14.91% | 6.71% | 6.4% | 2.15% | 5.37% | 8.682% | 6.545% | 6.697% | 6.4% | 7.108% | 6.4%
TC CTs | 1074 | 1014 | 954 | 1014 | 6.955% | 4.317% | 6.305% | 4.63% | 5.643% | 5.695% | 6.15% | 6.287% | 5.097% | 3.66% | 5.474% | 5.669% | 5.309% | 5.643% | 5.378% | 5.695%

## Summary
Modeled EFOR%/EFORd%
|  | 2018 BP | 10-Year History | 7-Year History | 5-Year History | 2019 Business Plan | Comments
| BR Station | 5.7% | 5.755% | 5.71% | 5.71% | Keep at 5.7%
| GH+MC+TC1 | 5.5% | 5.207% | 3.723% | 3.309% | Drop to 5.2%
| TC2 | 7.6% | 12.66% | 12.66% | 12.66% | Raise to 9.3% | TC2 set to an average of 2015 and 2017; data post-2014 deemed more reflective of future operations, however 2016 is considered an anomaly due to rotor rewind
| BR CTs | 9.9% | 10.96% | 8.089% | 8.089% | Keep at 9.9%
| TC CTs | 5.7% | 5.669% | 5.643% | 5.695% | Keep at 5.7%
| PR13 | 9.9% | 19.46% | 15.57% | 18.55% | Keep at 9.9% | Historical EFORd was artificially high due to issues with gas supply (lack of availability in cold weather, coupled with failures of the gas compressor); gas pipeline project is eliminating these factors, so EFORd should improve, but the extent of the improvement is hard to quantify; consensus is to use the same value as the Brown CTs (9.9%) for PR13 until sufficient data is available to develop a history specific to PR13
Modeled MOR%
|  | 2018 BP | 10-Year History | 7-Year History | 5-Year History | 2019 Business Plan | Comments
| BR Station | 2.8% | 3.281% | 3.544% | 3.544% | Keep at 2.8% | Modeled MOR% reflects 0.5% reduction to account for ability to defer maintenance outages
| GH+MC+TC1 | 2.2% | 2.74% | 3.232% | 4.07% | Keep at 2.2%
| TC2 | 3.8% | 4.31% | 4.31% | 3.908% | Keep at 3.8%
CR7 Outage Rate Data
| 2018 BP | Jun-2015 to Dec-2015 | Jan-2016 to Dec-2016 | Jan-2017 to Dec-2017 | Jun-2015 to Dec-2017 | 2019 BP Recommendation | Comments
EFOR | 3% | 2.88% | 2.936% | 4.228% | 3.363% | Keep at 3.0% | 2015-2016 data suggests EFOR should remain unchanged, although EFOR is higher YTD in 2017; consensus is to keep EFOR as is until more data is available
MOR | 5.9% | 4.369% | 4.363% | 25.17% | 12.41% | Keep at 5.9% | 2015-2016 data suggests MOR should be lowered, but MOR is significantly higher YTD in 2017; consensus is to keep MOR as is until more data is available