## INPUT-GADS DATA
UnitName | EventType | EventNo | CauseCode | EventStart | EventEnd | GAC | GMC | NMC | Cause | eventDescription | Station Name | Event Category | Unit Type | Size | Year | Month | Duration_Hrs | Equiv. Hours | MWH Lost | Derate | Derate_RND
BR1 | D1 | 2 | 9270 | 2013-01-14 21:30 | 2013-01-14 22:10 | 90 | 114 | 107 | Wet coal | 1-3 mill feeder plugged | Brown | Derate | Coal | 1 | 2013 | 1 | 0.66667 | 0.14035 | 15.0175 | 22.5263 | 23
BR1 | D1 | 3 | 280 | 2013-01-15 02:40 | 2013-01-15 03:03 | 90 | 114 | 107 | Pulverizer fires | 1-2 mill pyrite fire | Brown | Derate | Coal | 1 | 2013 | 1 | 0.38333 | 0.080702 | 8.6351 | 22.5263 | 23
BR1 | PD | 4 | 260 | 2013-01-29 11:02 | 2013-01-29 18:25 | 90 | 114 | 107 | Primary air fan | 1-2 mill primary air fan out of balance 6417365 | Brown | Derate | Coal | 1 | 2013 | 1 | 7.3833 | 1.5544 | 166.3193 | 22.5263 | 23
BR1 | PD | 5 | 310 | 2013-01-30 07:46 | 2013-02-04 08:25 | 90 | 114 | 107 | Pulverizer mills | 1-2 mill race replacement 6414494 | Brown | Derate | Coal | 1 | 2013 | 1 | 120.65 | 25.4 | 2717.8 | 22.5263 | 23
BR1 | PD | 6 | 310 | 2013-02-04 08:25 | 2013-02-06 07:15 | 105 | 114 | 107 | Pulverizer mills | 1-2 mill race replacement | Brown | Derate | Coal | 1 | 2013 | 2 | 46.8333 | 3.6974 | 395.6184 | 8.4474 | 8
BR1 | D1 | 8 | 95 | 2013-02-06 07:15 | 2013-02-06 07:40 | 55 | 114 | 107 | Bunker flow problems | F1201-1 Mill Feeder plugged. | Brown | Derate | Coal | 1 | 2013 | 2 | 0.41667 | 0.21564 | 23.0738 | 55.3772 | 55
BR1 | PD | 9 | 310 | 2013-02-06 07:40 | 2013-02-07 | 105 | 114 | 107 | Pulverizer mills | 1-2 mill race replacement | Brown | Derate | Coal | 1 | 2013 | 2 | 16.3333 | 1.2895 | 137.9737 | 8.4474 | 8
BR1 | D4 | 7 | 344 | 2013-02-07 | 2013-02-07 03:44 | 60 | 114 | 107 | Pulverizer inspection | F5301-3 & 1-4 Mill Inspections | Brown | Derate | Coal | 1 | 2013 | 2 | 3.7333 | 1.7684 | 189.2211 | 50.6842 | 51
BR1 | PD | 10 | 310 | 2013-02-07 03:44 | 2013-02-08 | 105 | 114 | 107 | Pulverizer mills | 1-2 mill race replacement | Brown | Derate | Coal | 1 | 2013 | 2 | 20.2667 | 1.6 | 171.2 | 8.4474 | 8
BR1 | PD | 11 | 344 | 2013-02-08 | 2013-02-08 00:50 | 60 | 114 | 107 | Pulverizer inspection | Inspect 1-1 mill | Brown | Derate | Coal | 1 | 2013 | 2 | 0.83333 | 0.39474 | 42.2368 | 50.6842 | 51
BR1 | PD | 12 | 310 | 2013-02-08 00:50 | 2013-02-11 23:30 | 105 | 114 | 107 | Pulverizer mills | 1-2 mill race replacement | Brown | Derate | Coal | 1 | 2013 | 2 | 94.6667 | 7.4737 | 799.6842 | 8.4474 | 8
BR1 | D1 | 13 | 260 | 2013-02-11 23:30 | 2013-02-12 00:30 | 60 | 114 | 107 | Primary air fan | 1-3 mill PA fan OB bearing cooling water line leaking | Brown | Derate | Coal | 1 | 2013 | 2 | 1 | 0.47368 | 50.6842 | 50.6842 | 51
BR1 | PD | 14 | 310 | 2013-02-12 00:30 | 2013-02-12 04:49 | 105 | 114 | 107 | Pulverizer mills | 1-2 mill race replacement | Brown | Derate | Coal | 1 | 2013 | 2 | 4.3167 | 0.34079 | 36.4645 | 8.4474 | 8
BR1 | PD | 15 | 260 | 2013-02-22 12:10 | 2013-02-22 13:30 | 105 | 114 | 107 | Primary air fan | Repair 1-4 mill primary air fan oil leak | Brown | Derate | Coal | 1 | 2013 | 2 | 1.3333 | 0.10526 | 11.2632 | 8.4474 | 8
BR1 | NC | 16 | 8700 | 2013-02-28 01:00 | 2013-02-28 04:00 | 0 | 114 | 107 | CEMS Certification and Recertification | Low load RATA testing | Brown | Other | Coal | 1 | 2013 | 2 | 3 | 3 | 321 | 107 | 107
BR1 | NC | 17 | 4267 | 2013-03-06 | 2013-03-06 00:40 | 0 | 114 | 107 | Control valve testing | Valve test for #5 govenor valve | Brown | Other | Coal | 1 | 2013 | 3 | 0.66667 | 0.66667 | 71.3333 | 107 | 107
BR1 | D1 | 18 | 9270 | 2013-03-06 08:22 | 2013-03-06 08:37 | 90 | 114 | 107 | Wet coal | 1-1 mill feeder plugged | Brown | Derate | Coal | 1 | 2013 | 3 | 0.25 | 0.052632 | 5.6316 | 22.5263 | 23
BR1 | MO | 19 | 9656 | 2013-03-11 20:40 | 2013-03-16 00:11 | 0 | 114 | 107 | Other stack or exhaust emissions testing - fossil | Off line for mercury testing on Brown 3 | Brown | Maintenance | Coal | 1 | 2013 | 3 | 99.5167 | 99.5167 | 10648.2833 | 107 | 107
BR1 | MO | 20 | 8230 | 2013-03-16 00:11 | 2013-03-21 03:07 | 0 | 114 | 107 | Ducting A | Replace inlet and outlet FGD expansion joints | Brown | Maintenance | Coal | 1 | 2013 | 3 | 122.9333 | 122.9333 | 13153.8667 | 107 | 107
BR1 | U1 | 21 | 270 | 2013-03-21 10:15 | 2013-03-21 20:28 | 0 | 114 | 107 | Primary air duct and dampers | Hot air dampers to mills not operating properly preventing opening or closing of the d | Brown | Outage | Coal | 1 | 2013 | 3 | 10.2167 | 10.2167 | 1093.1833 | 107 | 107
BR1 | D1 | 22 | 9270 | 2013-03-26 05:50 | 2013-03-26 06:08 | 90 | 114 | 107 | Wet coal | Wet coal in 1-1 mill | Brown | Derate | Coal | 1 | 2013 | 3 | 0.3 | 0.063158 | 6.7579 | 22.5263 | 23
BR1 | NC | 23 | 1100 | 2013-03-28 12:15 | 2013-03-28 13:31 | 0 | 114 | 107 | Waterwall (Furnace wall) B | Deslag unit | Brown | Other | Coal | 1 | 2013 | 3 | 1.2667 | 1.2667 | 135.5333 | 107 | 107
BR1 | PD | 24 | 263 | 2013-04-18 | 2013-04-18 09:50 | 90 | 114 | 107 | Primary air fan drives | Investigate problem with 1-3 mill primary air fan IB bearing high temperature 6439585 | Brown | Derate | Coal | 1 | 2013 | 4 | 9.8333 | 2.0702 | 221.5088 | 22.5263 | 23
BR1 | PO | 25 | 1812 | 2013-04-20 02:18 | 2013-04-28 07:17 | 0 | 114 | 107 | Boiler Inspections - scheduled or routine | Planned outage for boiler inspection and general maintenance | Brown | Other | Coal | 1 | 2013 | 4 | 196.9833 | 196.9833 | 21077.2167 | 107 | 107
BR1 | D1 | 26 | 1410 | 2013-05-06 16:53 | 2013-05-06 19:37 | 60 | 114 | 107 | Forced draft fan motors | 1-1 FD Fan motor failure | Brown | Derate | Coal | 1 | 2013 | 5 | 2.7333 | 1.2947 | 138.5368 | 50.6842 | 51
BR1 | D1 | 27 | 1410 | 2013-05-06 19:37 | 2013-05-17 16:58 | 55 | 114 | 107 | Forced draft fan motors | 1-1 FD Fan motor failure 6445741 | Brown | Derate | Coal | 1 | 2013 | 5 | 261.35 | 135.2601 | 14472.8294 | 55.3772 | 55
BR1 | D1 | 28 | 267 | 2013-05-20 12:28 | 2013-05-20 13:05 | 90 | 114 | 107 | Primary air flow instrumentation | Replace 1-1 mill broken pitot tube 6448568 | Brown | Derate | Coal | 1 | 2013 | 5 | 0.61667 | 0.12982 | 13.8912 | 22.5263 | 23
BR1 | PD | 29 | 260 | 2013-05-25 04:45 | 2013-05-25 06:18 | 95 | 114 | 107 | Primary air fan | Repair 1-3 mill primary air fan IB bearing oil leak 6452730 | Brown | Derate | Coal | 1 | 2013 | 5 | 1.55 | 0.25833 | 27.6417 | 17.8333 | 18
BR1 | D1 | 30 | 4640 | 2013-06-01 10:08 | 2013-06-01 13:55 | 60 | 114 | 107 | Seal oil system and seals A | Seal oil system vacuum tank level control float valve not closing properly causing hig | Brown | Derate | Coal | 1 | 2013 | 6 | 3.7833 | 1.7921 | 191.7553 | 50.6842 | 51
BR1 | PD | 31 | 310 | 2013-06-05 22:40 | 2013-06-06 02:45 | 85 | 114 | 107 | Pulverizer mills | 1-1 and 1-2 mill inspections | Brown | Derate | Coal | 1 | 2013 | 6 | 4.0833 | 1.0387 | 111.1455 | 27.2193 | 27
BR1 | PD | 32 | 310 | 2013-06-06 22:00 | 2013-06-07 04:00 | 85 | 114 | 107 | Pulverizer mills | 1-3 mill inspection. Replaced broken spring bolt. | Brown | Derate | Coal | 1 | 2013 | 6 | 6 | 1.5263 | 163.3158 | 27.2193 | 27
BR1 | PD | 33 | 344 | 2013-06-08 06:00 | 2013-06-08 08:10 | 85 | 114 | 107 | Pulverizer inspection | 1-4 Mill Inspection | Brown | Derate | Coal | 1 | 2013 | 6 | 2.1667 | 0.55117 | 58.9751 | 27.2193 | 27
BR1 | PD | 34 | 310 | 2013-06-13 22:00 | 2013-06-14 01:03 | 85 | 114 | 107 | Pulverizer mills | Enlarge 1-2 mill oil flow orfice 6466979 | Brown | Derate | Coal | 1 | 2013 | 6 | 3.05 | 0.77588 | 83.0189 | 27.2193 | 27
BR1 | D1 | 35 | 9270 | 2013-06-27 19:50 | 2013-06-27 20:09 | 85 | 114 | 107 | Wet coal | Wet coal in 1-3 mill | Brown | Derate | Coal | 1 | 2013 | 6 | 0.31667 | 0.080556 | 8.6194 | 27.2193 | 27
BR1 | U1 | 36 | 4260 | 2013-06-30 22:04 | 2013-06-30 22:56 | 0 | 114 | 107 | Main stop valves | Left side throttle valve not giving closed limit on weekly valve test. Removed unit to | Brown | Outage | Coal | 1 | 2013 | 6 | 0.86667 | 0.86667 | 92.7333 | 107 | 107
BR1 | D1 | 37 | 9270 | 2013-07-08 11:25 | 2013-07-08 15:40 | 91 | 114 | 107 | Wet coal | Wet coal in 1-3 mill | Brown | Derate | Coal | 1 | 2013 | 7 | 4.25 | 0.85746 | 91.7478 | 21.5877 | 22
BR1 | MO | 38 | 4261 | 2013-07-24 08:39 | 2013-07-26 16:00 | 0 | 114 | 107 | Control valves | Turbine Gov. valve & burner line maintenance 6476754 6470986 | Brown | Maintenance | Coal | 1 | 2013 | 7 | 55.35 | 55.35 | 5922.45 | 107 | 107
BR1 | PD | 40 | 4261 | 2013-08-13 02:00 | 2013-08-13 04:00 | 80 | 114 | 107 | Control valves | Replace #6 governor valve control actuator 6484436 | Brown | Derate | Coal | 1 | 2013 | 8 | 2 | 0.59649 | 63.8246 | 31.9123 | 32
BR1 | D1 | 41 | 90 | 2013-08-22 13:00 | 2013-08-22 14:15 | 80 | 114 | 107 | Bunker fires | 1-2 Mill bunker fire | Brown | Derate | Coal | 1 | 2013 | 8 | 1.25 | 0.37281 | 39.8904 | 31.9123 | 32
BR1 | D1 | 42 | 90 | 2013-08-22 14:40 | 2013-08-22 20:24 | 80 | 114 | 107 | Bunker fires | 1-2 Mill bunker fire | Brown | Derate | Coal | 1 | 2013 | 8 | 5.7333 | 1.7099 | 182.9637 | 31.9123 | 32
BR1 | U1 | 43 | 1040 | 2013-08-23 01:29 | 2013-08-24 21:38 | 0 | 114 | 107 | First superheater B | SH tube leak W.O. #6487766 | Brown | Outage | Coal | 1 | 2013 | 8 | 44.15 | 44.15 | 4724.05 | 107 | 107
BR1 | D1 | 44 | 1710 | 2013-09-11 16:35 | 2013-09-11 19:04 | 110 | 114 | 107 | Combustion/steam condition controls (report local controls --- burners | Combustion air flow at maximum limit | Brown | Derate | Coal | 1 | 2013 | 9 | 2.4833 | 0.087135 | 9.3234 | 3.7544 | 4
BR1 | D1 | 45 | 3411 | 2013-09-13 10:05 | 2013-09-18 08:41 | 110 | 114 | 107 | Feedwater pump drive - motor | 1-1 BFP Motor failure 6494431 | Brown | Derate | Coal | 1 | 2013 | 9 | 118.6 | 4.1614 | 445.2702 | 3.7544 | 4
BR1 | D1 | 46 | 3411 | 2013-09-18 08:41 | 2013-09-18 10:10 | 105 | 114 | 107 | Feedwater pump drive - motor | 1-1 BFP Motor failure | Brown | Derate | Coal | 1 | 2013 | 9 | 1.4833 | 0.11711 | 12.5303 | 8.4474 | 8
BR1 | U1 | 48 | 4570 | 2013-10-09 10:21 | 2013-10-09 23:41 | 0 | 114 | 107 | Generator casing | Check Gen H2 Cooler for leak due to moist in sight glass. 6502387 | Brown | Outage | Coal | 1 | 2013 | 10 | 13.3333 | 13.3333 | 1426.6667 | 107 | 107
BR1 | MO | 49 | 8230 | 2013-10-16 20:19 | 2013-10-18 14:30 | 0 | 114 | 107 | Ducting A | Repair FGD inlet duct expansion joint | Brown | Maintenance | Coal | 1 | 2013 | 10 | 42.1833 | 42.1833 | 4513.6167 | 107 | 107
BR1 | D1 | 51 | 310 | 2013-10-22 17:42 | 2013-10-22 22:50 | 90 | 114 | 107 | Pulverizer mills | 1-1 Mill full of coal tripped on startup | Brown | Derate | Coal | 1 | 2013 | 10 | 5.1333 | 1.0807 | 115.6351 | 22.5263 | 23
BR1 | D1 | 52 | 310 | 2013-11-04 06:39 | 2013-11-04 09:45 | 90 | 114 | 107 | Pulverizer mills | 1-1 Mill full of coal tripped on startup | Brown | Derate | Coal | 1 | 2013 | 11 | 3.1 | 0.65263 | 69.8316 | 22.5263 | 23
BR1 | PD | 53 | 4261 | 2013-11-16 | 2013-11-16 00:39 | 65 | 114 | 107 | Control valves | Replace #4 governor valve servo 6510732 | Brown | Derate | Coal | 1 | 2013 | 11 | 0.65 | 0.27939 | 29.8943 | 45.9912 | 46
BR1 | D1 | 54 | 267 | 2013-11-19 09:48 | 2013-11-19 10:28 | 85 | 114 | 107 | Primary air flow instrumentation | Replace 1-3 mill pitot tube assembly 6513440 | Brown | Derate | Coal | 1 | 2013 | 11 | 0.66667 | 0.16959 | 18.1462 | 27.2193 | 27
BR1 | NC | 56 | 1100 | 2013-12-11 23:56 | 2013-12-12 01:10 | 0 | 114 | 107 | Waterwall (Furnace wall) B | Deslag boiler | Brown | Other | Coal | 1 | 2013 | 12 | 1.2333 | 1.2333 | 131.9667 | 107 | 107
BR1 | PD | 57 | 310 | 2013-12-18 21:30 | 2013-12-19 04:10 | 80 | 114 | 107 | Pulverizer mills | Inspect 1-1 & 1-3 mills | Brown | Derate | Coal | 1 | 2013 | 12 | 6.6667 | 1.9883 | 212.7485 | 31.9123 | 32
BR1 | PD | 58 | 310 | 2013-12-19 22:00 | 2013-12-20 03:30 | 80 | 114 | 107 | Pulverizer mills | Inspect 1-2 & 1-4 mills | Brown | Derate | Coal | 1 | 2013 | 12 | 5.5 | 1.6404 | 175.5175 | 31.9123 | 32
BR1 | PD | 1 | 260 | 2014-01-03 | 2014-01-03 02:00 | 80 | 114 | 107 | Primary air fan | 1-3 mil primary air fan housing leak repair - 6529878 | Brown | Derate | Coal | 1 | 2014 | 1 | 2 | 0.59649 | 63.8246 | 31.9123 | 32
BR1 | PD | 2 | 310 | 2014-02-19 22:00 | 2014-02-20 02:51 | 85 | 114 | 107 | Pulverizer mills | 1-1 & 1-4 mill inspection | Brown | Derate | Coal | 1 | 2014 | 2 | 4.85 | 1.2338 | 132.0136 | 27.2193 | 27
BR1 | PD | 3 | 310 | 2014-02-20 22:00 | 2014-02-21 03:39 | 85 | 114 | 107 | Pulverizer mills | 1-3 mill inspection | Brown | Derate | Coal | 1 | 2014 | 2 | 5.65 | 1.4373 | 153.789 | 27.2193 | 27
BR1 | PD | 4 | 1400 | 2014-02-26 23:00 | 2014-02-27 | 50 | 114 | 107 | Forced draft fans | Repair leaking cooler hose 1-1 FD Fan 6547051 | Brown | Derate | Coal | 1 | 2014 | 2 | 1 | 0.5614 | 60.0702 | 60.0702 | 60
BR1 | PD | 5 | 310 | 2014-02-27 | 2014-02-27 02:28 | 75 | 114 | 107 | Pulverizer mills | 1-2 mill inspection 6534494 | Brown | Derate | Coal | 1 | 2014 | 2 | 2.4667 | 0.84386 | 90.293 | 36.6053 | 37
BR1 | D1 | 6 | 280 | 2014-03-04 09:56 | 2014-03-04 13:25 | 80 | 114 | 107 | Pulverizer fires | 1-3 mill pyrite fire 6548834 | Brown | Derate | Coal | 1 | 2014 | 3 | 3.4833 | 1.0389 | 111.1611 | 31.9123 | 32
BR1 | NC | 7 | 9656 | 2014-03-11 11:42 | 2014-03-11 16:08 | 0 | 114 | 107 | Other stack or exhaust emissions testing - fossil | Low load RATA testing | Brown | Other | Coal | 1 | 2014 | 3 | 4.4333 | 4.4333 | 474.3667 | 107 | 107
BR1 | D1 | 8 | 310 | 2014-03-13 10:15 | 2014-03-13 13:45 | 80 | 114 | 107 | Pulverizer mills | 1-4 mill tripped due to air flow issues 6552310 | Brown | Derate | Coal | 1 | 2014 | 3 | 3.5 | 1.0439 | 111.693 | 31.9123 | 32
BR1 | D1 | 9 | 310 | 2014-03-17 06:32 | 2014-03-17 07:27 | 85 | 114 | 107 | Pulverizer mills | 1-4 mill air flow erratic 6552310 | Brown | Derate | Coal | 1 | 2014 | 3 | 0.91667 | 0.23319 | 24.951 | 27.2193 | 27
BR1 | D1 | 10 | 9205 | 2014-03-18 08:37 | 2014-03-18 10:37 | 107 | 114 | 107 | Poor quality natural gas fuel | Limited by coal quality | Brown | Derate | Coal | 1 | 2014 | 3 | 2 | 0.12281 | 13.1404 | 6.5702 | 7
BR1 | D1 | 11 | 9205 | 2014-03-18 10:37 | 2014-03-18 10:51 | 112 | 114 | 107 | Poor quality natural gas fuel | Limited by coal quality | Brown | Derate | Coal | 1 | 2014 | 3 | 0.23333 | 0.0040936 | 0.43801 | 1.8772 | 2
BR1 | D1 | 12 | 9270 | 2014-04-01 10:50 | 2014-04-01 11:48 | 74 | 114 | 107 | Wet coal | Wet coal in 1-3 mill causing pluggage | Brown | Derate | Coal | 1 | 2014 | 4 | 0.96667 | 0.33918 | 36.2924 | 37.5439 | 38
BR1 | D1 | 13 | 1140 | 2014-04-01 18:12 | 2014-04-01 18:16 | 86 | 114 | 107 | First superheater A | Boiler slagging causing air flow issues | Brown | Derate | Coal | 1 | 2014 | 4 | 0.066667 | 0.016374 | 1.752 | 26.2807 | 26
BR1 | D1 | 14 | 1140 | 2014-04-01 18:16 | 2014-04-01 18:22 | 79 | 114 | 107 | First superheater A | Boiler slagging causing air flow issues | Brown | Derate | Coal | 1 | 2014 | 4 | 0.1 | 0.030702 | 3.2851 | 32.8509 | 33
BR1 | D1 | 15 | 1140 | 2014-04-01 18:22 | 2014-04-01 21:07 | 59 | 114 | 107 | First superheater A | Boiler slagging causing air flow issues and pluggage | Brown | Derate | Coal | 1 | 2014 | 4 | 2.75 | 1.3268 | 141.9627 | 51.6228 | 52
BR1 | U1 | 16 | 1140 | 2014-04-01 21:07 | 2014-04-05 00:45 | 0 | 114 | 107 | First superheater A | Boiler slagging causing air flow issues and pluggage | Brown | Outage | Coal | 1 | 2014 | 4 | 75.6333 | 75.6333 | 8092.7667 | 107 | 107
BR1 | U1 | 17 | 4302 | 2014-04-05 04:22 | 2014-04-05 04:55 | 0 | 114 | 107 | Turbine trip devices (including instruments) | Turbine trip on loss of condenser vacuum | Brown | Outage | Coal | 1 | 2014 | 4 | 0.55 | 0.55 | 58.85 | 107 | 107
BR1 | D1 | 18 | 340 | 2014-04-05 13:42 | 2014-04-05 14:38 | 80 | 114 | 107 | Other pulverizer problems | Clean coal from 1-2 mill after unit MFT | Brown | Derate | Coal | 1 | 2014 | 4 | 0.93333 | 0.27836 | 29.7848 | 31.9123 | 32
BR1 | D1 | 19 | 9290 | 2014-04-05 14:38 | 2014-04-05 17:36 | 105 | 114 | 107 | Other fuel quality problems | Poor coal quality. Problems feeding and low BTU | Brown | Derate | Coal | 1 | 2014 | 4 | 2.9667 | 0.23421 | 25.0605 | 8.4474 | 8
BR1 | PD | 20 | 110 | 2014-04-05 17:36 | 2014-04-05 22:21 | 85 | 114 | 107 | Other coal fuel supply problems up through bunkers | Clean coal bunkers for outage 1-1 bunker empty 6497431 | Brown | Derate | Coal | 1 | 2014 | 4 | 4.75 | 1.2083 | 129.2917 | 27.2193 | 27
BR1 | PD | 21 | 110 | 2014-04-05 22:21 | 2014-04-06 01:23 | 55 | 114 | 107 | Other coal fuel supply problems up through bunkers | Clean coal bunkers for outage 1-1 & 1-2 bunkers empty 6497394 | Brown | Derate | Coal | 1 | 2014 | 4 | 3.0333 | 1.5699 | 167.9775 | 55.3772 | 55
BR1 | PO | 22 | 1812 | 2014-04-06 01:23 | 2014-04-27 23:38 | 0 | 114 | 107 | Boiler Inspections - scheduled or routine | Planned outage. Various inspections, Performed annual boiler assessment, Performed loc | Brown | Other | Coal | 1 | 2014 | 4 | 526.25 | 526.25 | 56308.75 | 107 | 107
BR1 | D1 | 25 | 310 | 2014-04-28 03:30 | 2014-04-28 08:45 | 80 | 114 | 107 | Pulverizer mills | 1-2 mill pyrite door failed to open 6565658 | Brown | Derate | Coal | 1 | 2014 | 4 | 5.25 | 1.5658 | 167.5395 | 31.9123 | 32
BR1 | D1 | 26 | 310 | 2014-04-28 08:45 | 2014-04-28 11:32 | 85 | 114 | 107 | Pulverizer mills | 1-3 mill pyrite door failed to close 6565658 | Brown | Derate | Coal | 1 | 2014 | 4 | 2.7833 | 0.70804 | 75.7604 | 27.2193 | 27
BR1 | D1 | 27 | 1700 | 2014-04-28 11:32 | 2014-04-28 11:47 | 13 | 114 | 107 | Feedwater controls (report local controls --- feedwater pump | Boiler trip due to low drum level which occured after losing 2 mills. | Brown | Derate | Coal | 1 | 2014 | 4 | 0.25 | 0.22149 | 23.6996 | 94.7982 | 95
BR1 | U1 | 28 | 4300 | 2014-04-28 11:47 | 2014-04-28 12:14 | 0 | 114 | 107 | Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | Turbine trip due to low condenser vacuum | Brown | Outage | Coal | 1 | 2014 | 4 | 0.45 | 0.45 | 48.15 | 107 | 107
BR1 | D1 | 29 | 280 | 2014-04-29 14:17 | 2014-04-29 15:20 | 85 | 114 | 107 | Pulverizer fires | 1-2 mill pyrite fire | Brown | Derate | Coal | 1 | 2014 | 4 | 1.05 | 0.26711 | 28.5803 | 27.2193 | 27
BR1 | D1 | 30 | 280 | 2014-04-29 15:20 | 2014-04-29 15:43 | 90 | 114 | 107 | Pulverizer fires | 1-2 mill pyrite fire | Brown | Derate | Coal | 1 | 2014 | 4 | 0.38333 | 0.080702 | 8.6351 | 22.5263 | 23
BR1 | D1 | 31 | 9270 | 2014-05-02 10:21 | 2014-05-02 11:38 | 100 | 114 | 107 | Wet coal | Wet coal plugging from bunker to feeder. | Brown | Derate | Coal | 1 | 2014 | 5 | 1.2833 | 0.1576 | 16.8635 | 13.1404 | 13
BR1 | NC | 32 | 1100 | 2014-05-02 21:40 | 2014-05-02 22:41 | 0 | 114 | 107 | Waterwall (Furnace wall) B | Deslag boiler. | Brown | Other | Coal | 1 | 2014 | 5 | 1.0167 | 1.0167 | 108.7833 | 107 | 107
BR1 | D1 | 33 | 358 | 2014-05-04 17:35 | 2014-05-04 19:28 | 93 | 114 | 107 | Oil burner piping and valves | 1-3C burner shutoff gate not opening. 6566429 | Brown | Derate | Coal | 1 | 2014 | 5 | 1.8833 | 0.34693 | 37.1215 | 19.7105 | 20
BR1 | PD | 34 | 3410 | 2014-05-06 23:00 | 2014-05-07 01:30 | 50 | 114 | 107 | Feedwater pump | 1-3 BFP mechanical seal leak 6567750 | Brown | Derate | Coal | 1 | 2014 | 5 | 2.5 | 1.4035 | 150.1754 | 60.0702 | 60
BR1 | U1 | 35 | 1455 | 2014-05-08 10:16 | 2014-05-08 18:45 | 0 | 114 | 107 | Induced draft fans | ID Fan trip due to high vibration 6568246 | Brown | Outage | Coal | 1 | 2014 | 5 | 8.4833 | 8.4833 | 907.7167 | 107 | 107
BR1 | SF | 36 | 1455 | 2014-05-08 18:45 | 2014-05-08 22:03 | 0 | 114 | 107 | Induced draft fans | ID Fan trip due to high vibration 6568246 | Brown | Outage | Coal | 1 | 2014 | 5 | 3.3 | 3.3 | 353.1 | 107 | 107
BR1 | D1 | 37 | 310 | 2014-05-08 23:40 | 2014-05-10 12:00 | 95 | 114 | 107 | Pulverizer mills | 1-2 mill broken race 6568288 | Brown | Derate | Coal | 1 | 2014 | 5 | 36.3333 | 6.0556 | 647.9444 | 17.8333 | 18
BR1 | PD | 38 | 510 | 2014-05-14 20:16 | 2014-05-15 00:05 | 63 | 114 | 107 | Main steam relief/safety valves off superheater | Set boiler saftey valves | Brown | Derate | Coal | 1 | 2014 | 5 | 3.8167 | 1.7075 | 182.6978 | 47.8684 | 48
BR1 | PD | 39 | 260 | 2014-05-19 11:41 | 2014-05-19 13:11 | 75 | 114 | 107 | Primary air fan | Repair 1-2 mill primary air fan bearing water leak. 6570276 | Brown | Derate | Coal | 1 | 2014 | 5 | 1.5 | 0.51316 | 54.9079 | 36.6053 | 37
BR1 | D1 | 40 | 95 | 2014-05-20 13:06 | 2014-05-20 14:23 | 80 | 114 | 107 | Bunker flow problems | 1-2 mill coal bunker pluggage. | Brown | Derate | Coal | 1 | 2014 | 5 | 1.2833 | 0.38275 | 40.9541 | 31.9123 | 32
BR1 | PD | 41 | 310 | 2014-05-30 22:00 | 2014-06-01 08:25 | 90 | 114 | 107 | Pulverizer mills | 1-3 mill race replacement | Brown | Derate | Coal | 1 | 2014 | 5 | 34.4167 | 7.2456 | 775.2807 | 22.5263 | 23
BR1 | PD | 42 | 3210 | 2014-06-26 22:00 | 2014-06-27 03:21 | 80 | 114 | 107 | Circulating water pumps | Inspect 1-2 CWP coupling | Brown | Derate | Coal | 1 | 2014 | 6 | 5.35 | 1.5956 | 170.7307 | 31.9123 | 32
BR1 | D1 | 43 | 250 | 2014-06-30 21:14 | 2014-07-01 02:05 | 90 | 114 | 107 | Pulverizer feeders | 1-4 mill feeder controls failed | Brown | Derate | Coal | 1 | 2014 | 6 | 4.85 | 1.0211 | 109.2526 | 22.5263 | 23
BR1 | D1 | 44 | 410 | 2014-07-01 09:45 | 2014-07-01 09:59 | 66 | 114 | 107 | Other burner problems | Lost 1-2 mill due to burner gate issues | Brown | Derate | Coal | 1 | 2014 | 7 | 0.23333 | 0.098246 | 10.5123 | 45.0526 | 45
BR1 | D1 | 45 | 250 | 2014-07-01 10:28 | 2014-07-01 11:29 | 101 | 114 | 107 | Pulverizer feeders | 1-4 mill feeder VFD problem 6585589 | Brown | Derate | Coal | 1 | 2014 | 7 | 1.0167 | 0.11594 | 12.4051 | 12.2018 | 12
BR1 | D1 | 46 | 250 | 2014-07-02 19:12 | 2014-07-02 19:25 | 95 | 114 | 107 | Pulverizer feeders | 1-3 Feeder | Brown | Derate | Coal | 1 | 2014 | 7 | 0.21667 | 0.036111 | 3.8639 | 17.8333 | 18
BR1 | U1 | 48 | 4261 | 2014-07-07 23:40 | 2014-07-08 18:19 | 0 | 114 | 107 | Control valves | F060Broken spring bolts on #3 and #5 turbine governor valves. 6587251 | Brown | Outage | Coal | 1 | 2014 | 7 | 18.65 | 18.65 | 1995.55 | 107 | 107
BR1 | D1 | 49 | 250 | 2014-07-14 15:10 | 2014-07-14 18:10 | 85 | 114 | 107 | Pulverizer feeders | 1-2 mill feeder inlet gate restricting coal feed. 6589203 | Brown | Derate | Coal | 1 | 2014 | 7 | 3 | 0.76316 | 81.6579 | 27.2193 | 27
BR1 | PD | 50 | 344 | 2014-07-24 22:00 | 2014-07-25 03:48 | 85 | 114 | 107 | Pulverizer inspection | 1-1 & 1-2 mill inspections | Brown | Derate | Coal | 1 | 2014 | 7 | 5.8 | 1.4754 | 157.8719 | 27.2193 | 27
BR1 | MO | 51 | 3420 | 2014-07-29 20:02 | 2014-07-31 03:14 | 0 | 114 | 107 | Feedwater piping and supports | Repair leaking SH spray stop valve 6589205 | Brown | Maintenance | Coal | 1 | 2014 | 7 | 31.2 | 31.2 | 3338.4 | 107 | 107
BR1 | D1 | 52 | 385 | 2014-08-07 16:02 | 2014-08-07 18:18 | 55 | 114 | 107 | Igniters | Problems with 1-1 & 1-4 mill igniters. 6596529 | Brown | Derate | Coal | 1 | 2014 | 8 | 2.2667 | 1.1731 | 125.5216 | 55.3772 | 55
BR1 | D1 | 53 | 380 | 2014-08-07 18:18 | 2014-08-07 18:35 | 80 | 114 | 107 | Light-off (igniter) systems (including fuel supply) | F320Loss of flame scanners on 1-1 mill igniters. | Brown | Derate | Coal | 1 | 2014 | 8 | 0.28333 | 0.084503 | 9.0418 | 31.9123 | 32
BR1 | U1 | 54 | 4700 | 2014-08-14 11:04 | 2014-08-14 12:03 | 0 | 114 | 107 | Generator voltage control | Generator over excitation trip 6596671 | Brown | Outage | Coal | 1 | 2014 | 8 | 0.98333 | 0.98333 | 105.2167 | 107 | 107
BR1 | PD | 55 | 310 | 2014-08-27 21:15 | 2014-08-28 07:55 | 85 | 114 | 107 | Pulverizer mills | Inspection of 1-1 and 1-3 mills | Brown | Derate | Coal | 1 | 2014 | 8 | 10.6667 | 2.7135 | 290.3392 | 27.2193 | 27
BR1 | PD | 56 | 310 | 2014-08-28 21:20 | 2014-08-29 03:25 | 85 | 114 | 107 | Pulverizer mills | Inspection of 1-2 and 1-4 mills | Brown | Derate | Coal | 1 | 2014 | 8 | 6.0833 | 1.5475 | 165.5841 | 27.2193 | 27
BR1 | MO | 57 | 840 | 2014-08-29 21:40 | 2014-08-31 06:57 | 0 | 114 | 107 | Refractory and insulation | F310Missing refractory is boiler back pass causing air in leakage. | Brown | Maintenance | Coal | 1 | 2014 | 8 | 33.2833 | 33.2833 | 3561.3167 | 107 | 107
BR1 | D1 | 59 | 8551 | 2014-09-01 09:17 | 2014-09-01 09:27 | 40 | 114 | 107 | Electrostatic precipitator field out of service | FE00ESP Brakers all left open without operator notification | Brown | Derate | Coal | 1 | 2014 | 9 | 0.16667 | 0.10819 | 11.576 | 69.4561 | 69
BR1 | MO | 61 | 1000 | 2014-09-16 12:55 | 2014-09-17 15:25 | 0 | 114 | 107 | Waterwall (Furnace wall) A | Waterwall tube leak 6607681 | Brown | Maintenance | Coal | 1 | 2014 | 9 | 26.5 | 26.5 | 2835.5 | 107 | 107
BR1 | D1 | 63 | 4261 | 2014-10-19 02:33 | 2014-10-19 12:15 | 40 | 114 | 107 | Control valves | #1 governor valve erratic operation | Brown | Derate | Coal | 1 | 2014 | 10 | 9.7 | 6.2965 | 673.7246 | 69.4561 | 69
BR1 | D1 | 65 | 1710 | 2014-11-11 21:23 | 2014-11-11 22:10 | 8 | 114 | 107 | Combustion/steam condition controls (report local controls --- burners | Boiler trip due to low combustion air | Brown | Derate | Coal | 1 | 2014 | 11 | 0.78333 | 0.72836 | 77.9348 | 99.4912 | 99
BR1 | PD | 66 | 1190 | 2014-11-20 23:48 | 2014-11-21 00:43 | 80 | 114 | 107 | Other tube slagging or fouling | Hydrowash deslag of boiler | Brown | Derate | Coal | 1 | 2014 | 11 | 0.91667 | 0.27339 | 29.2529 | 31.9123 | 32
BR1 | PD | 67 | 1190 | 2014-11-21 00:43 | 2014-11-21 01:13 | 55 | 114 | 107 | Other tube slagging or fouling | Hydrowash deslag of boiler | Brown | Derate | Coal | 1 | 2014 | 11 | 0.5 | 0.25877 | 27.6886 | 55.3772 | 55
BR1 | PD | 68 | 1190 | 2014-11-21 01:13 | 2014-11-21 01:52 | 40 | 114 | 107 | Other tube slagging or fouling | Hydrowash deslag of boiler | Brown | Derate | Coal | 1 | 2014 | 11 | 0.65 | 0.42193 | 45.1465 | 69.4561 | 69
BR1 | D1 | 69 | 310 | 2014-12-05 10:27 | 2014-12-05 11:43 | 75 | 114 | 107 | Pulverizer mills | 1-4 mill broken spring bolt | Brown | Derate | Coal | 1 | 2014 | 12 | 1.2667 | 0.43333 | 46.3667 | 36.6053 | 37
BR1 | D1 | 70 | 9270 | 2014-12-06 18:53 | 2014-12-06 19:22 | 80 | 114 | 107 | Wet coal | Wet coal | Brown | Derate | Coal | 1 | 2014 | 12 | 0.48333 | 0.14415 | 15.4243 | 31.9123 | 32
BR1 | D1 | 71 | 310 | 2014-12-06 22:35 | 2014-12-07 02:47 | 80 | 114 | 107 | Pulverizer mills | 1-4 mill broken spring bolt | Brown | Derate | Coal | 1 | 2014 | 12 | 4.2 | 1.2526 | 134.0316 | 31.9123 | 32
BR1 | D1 | 72 | 300 | 2014-12-08 06:20 | 2014-12-08 06:35 | 90 | 114 | 107 | Pulverizer motors and drives | 1-3 mill failed to start | Brown | Derate | Coal | 1 | 2014 | 12 | 0.25 | 0.052632 | 5.6316 | 22.5263 | 23
BR1 | NC | 1 | 8700 | 2015-01-13 21:30 | 2015-01-14 01:47 | 0 | 114 | 107 | CEMS Certification and Recertification | Low load RATA testing | Brown | Other | Coal | 1 | 2015 | 1 | 4.2833 | 4.2833 | 458.3167 | 107 | 107
BR1 | PD | 2 | 310 | 2015-01-14 23:00 | 2015-01-15 04:00 | 80 | 114 | 107 | Pulverizer mills | Inspect 1-1 & 1-4 mills | Brown | Derate | Coal | 1 | 2015 | 1 | 5 | 1.4912 | 159.5614 | 31.9123 | 32
BR1 | PD | 3 | 310 | 2015-01-15 23:00 | 2015-01-16 03:00 | 80 | 114 | 107 | Pulverizer mills | Inspect 1-2 & 1-3 mills | Brown | Derate | Coal | 1 | 2015 | 1 | 4 | 1.193 | 127.6491 | 31.9123 | 32
BR1 | MO | 4 | 1512 | 2015-01-16 23:10 | 2015-01-17 16:44 | 0 | 114 | 107 | Flue gas expansion joints | Repair expansion joint on combined duct to the FGD | Brown | Maintenance | Coal | 1 | 2015 | 1 | 17.5667 | 17.5667 | 1879.6333 | 107 | 107
BR1 | D1 | 6 | 1599 | 2015-01-23 06:30 | 2015-01-23 06:45 | 75 | 114 | 107 | Other miscellaneous boiler air and gas system problems | Boiler air flow erratic, having deviation alarms | Brown | Derate | Coal | 1 | 2015 | 1 | 0.25 | 0.085526 | 9.1513 | 36.6053 | 37
BR1 | PO | 7 | 4400 | 2015-02-28 09:38 | 2015-05-07 17:08 | 0 | 114 | 107 | Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | Planned outage for turbine overhaul | Brown | Other | Coal | 1 | 2015 | 2 | 1639.5 | 1639.5 | 175426.5 | 107 | 107
BR1 | D1 | 8 | 300 | 2015-05-08 04:39 | 2015-05-08 05:20 | 66 | 114 | 107 | Pulverizer motors and drives | 1-2 mill failed to start | Brown | Derate | Coal | 1 | 2015 | 5 | 0.68333 | 0.28772 | 30.786 | 45.0526 | 45
BR1 | MO | 9 | 4499 | 2015-05-08 08:54 | 2015-05-08 14:06 | 0 | 114 | 107 | Other miscellaneous steam turbine problems | Balance shot for vibration after returning from major outage | Brown | Maintenance | Coal | 1 | 2015 | 5 | 5.2 | 5.2 | 556.4 | 107 | 107
BR1 | MO | 10 | 4499 | 2015-05-08 18:01 | 2015-05-09 16:29 | 0 | 114 | 107 | Other miscellaneous steam turbine problems | Balance shot for vibration after returning from major outage | Brown | Maintenance | Coal | 1 | 2015 | 5 | 22.4667 | 22.4667 | 2403.9333 | 107 | 107
BR1 | MO | 11 | 4490 | 2015-05-11 08:17 | 2015-05-11 11:01 | 0 | 114 | 107 | Turbine performance testing (use code 9999 for total unit performance testing) | Balance shot for vibration after returning from major outage | Brown | Maintenance | Coal | 1 | 2015 | 5 | 2.7333 | 2.7333 | 292.4667 | 107 | 107
BR1 | U1 | 12 | 4302 | 2015-05-11 11:03 | 2015-05-11 18:15 | 0 | 114 | 107 | Turbine trip devices (including instruments) | Turbine trip due to high vibration | Brown | Outage | Coal | 1 | 2015 | 5 | 7.2 | 7.2 | 770.4 | 107 | 107
BR1 | MO | 13 | 4619 | 2015-05-12 22:43 | 2015-05-14 04:46 | 0 | 114 | 107 | Other hydrogen system problems | Investigate and repair generator H2 leak | Brown | Maintenance | Coal | 1 | 2015 | 5 | 30.05 | 30.05 | 3215.35 | 107 | 107
BR1 | U1 | 14 | 1035 | 2015-05-14 23:12 | 2015-05-16 02:25 | 0 | 114 | 107 | Platen superheater | SH tube leak | Brown | Outage | Coal | 1 | 2015 | 5 | 27.2167 | 27.2167 | 2912.1833 | 107 | 107
BR1 | MO | 15 | 1512 | 2015-05-21 20:05 | 2015-05-24 13:55 | 0 | 114 | 107 | Flue gas expansion joints | Replace Unit 1 & 2 combined duct expansion joint | Brown | Maintenance | Coal | 1 | 2015 | 5 | 65.8333 | 65.8333 | 7044.1667 | 107 | 107
BR1 | D1 | 17 | 9910 | 2015-06-09 14:21 | 2015-06-09 15:06 | 65 | 114 | 107 | Maintenance personnel error | Electrical feed for fuel oil pumps cut during building demolition | Brown | Derate | Coal | 1 | 2015 | 6 | 0.75 | 0.32237 | 34.4934 | 45.9912 | 46
BR1 | MO | 19 | 4613 | 2015-07-10 09:09 | 2015-07-17 23:07 | 0 | 114 | 107 | Hydrogen seals | Replace generator H2 seals | Brown | Maintenance | Coal | 1 | 2015 | 7 | 181.9667 | 181.9667 | 19470.4333 | 107 | 107
BR1 | D1 | 20 | 250 | 2015-07-23 11:40 | 2015-07-23 14:38 | 80 | 114 | 107 | Pulverizer feeders | 1-2 mill feeder controller failed | Brown | Derate | Coal | 1 | 2015 | 7 | 2.9667 | 0.8848 | 94.6731 | 31.9123 | 32
BR1 | MO | 21 | 4613 | 2015-08-18 22:03 | 2015-09-01 09:00 | 0 | 114 | 107 | Hydrogen seals | Repair generator H2 leak | Brown | Maintenance | Coal | 1 | 2015 | 8 | 322.95 | 322.95 | 34555.65 | 107 | 107
BR1 | D1 | 22 | 320 | 2015-09-02 13:15 | 2015-09-02 14:38 | 80 | 114 | 107 | Foreign object in Pulverizers mill | Noise in 1-4 Mill | Brown | Derate | Coal | 1 | 2015 | 9 | 1.3833 | 0.41257 | 44.1453 | 31.9123 | 32
BR1 | MO | 24 | 4289 | 2015-09-15 06:00 | 2015-09-15 06:11 | 0 | 114 | 107 | Other lube oil system problems | Lube oil vapor extractor replacement | Brown | Maintenance | Coal | 1 | 2015 | 9 | 0.18333 | 0.18333 | 19.6167 | 107 | 107
BR1 | MO | 26 | 8720 | 2015-09-30 15:02 | 2015-09-30 16:31 | 0 | 114 | 107 | NOx analyzer problems | Install mercury monitoring probe in duct | Brown | Maintenance | Coal | 1 | 2015 | 9 | 1.4833 | 1.4833 | 158.7167 | 107 | 107
BR1 | MO | 28 | 8720 | 2015-10-01 06:00 | 2015-10-02 15:24 | 0 | 114 | 107 | NOx analyzer problems | Install mercury monitoring probe in duct | Brown | Maintenance | Coal | 1 | 2015 | 10 | 33.4 | 33.4 | 3573.8 | 107 | 107
BR1 | MO | 30 | 8250 | 2015-10-03 10:26 | 2015-10-03 12:47 | 0 | 114 | 107 | Dampers other than bypass | Inspect unit 1 & 2 isolation damper at FGD inlet | Brown | Maintenance | Coal | 1 | 2015 | 10 | 2.35 | 2.35 | 251.45 | 107 | 107
BR1 | D1 | 33 | 4261 | 2015-11-04 18:35 | 2015-11-06 04:01 | 101 | 114 | 107 | Control valves | EH fluid leaks on #1, #3 & #5 govenor valves. #3 & #5 isolated. | Brown | Derate | Coal | 1 | 2015 | 11 | 33.4333 | 3.8126 | 407.9453 | 12.2018 | 12
BR1 | D1 | 34 | 110 | 2015-11-06 04:01 | 2015-11-06 06:10 | 79 | 114 | 107 | Other coal fuel supply problems up through bunkers | 1-4 mill coal bunker empty | Brown | Derate | Coal | 1 | 2015 | 11 | 2.15 | 0.66009 | 70.6294 | 32.8509 | 33
BR1 | D1 | 35 | 4261 | 2015-11-06 06:10 | 2015-11-06 14:11 | 101 | 114 | 107 | Control valves | EH fluid leaks on #1, #3 & #5 govenor valves. #3 & #5 isolated. | Brown | Derate | Coal | 1 | 2015 | 11 | 8.0167 | 0.91418 | 97.8174 | 12.2018 | 12
BR1 | MO | 36 | 4261 | 2015-11-06 14:11 | 2015-11-07 19:53 | 0 | 114 | 107 | Control valves | Repair EH fluid leaks on #1, #3 & #5 govenor valves. #3 & #5 isolated. | Brown | Maintenance | Coal | 1 | 2015 | 11 | 29.7 | 29.7 | 3177.9 | 107 | 107
BR1 | D1 | 37 | 4261 | 2015-11-07 22:52 | 2015-11-09 08:23 | 100 | 114 | 107 | Control valves | EH Fluid leak on #3 turbine govenor valve | Brown | Derate | Coal | 1 | 2015 | 11 | 33.5167 | 4.1161 | 440.4208 | 13.1404 | 13
BR1 | D1 | 38 | 310 | 2015-11-23 05:48 | 2015-11-23 11:22 | 85 | 114 | 107 | Pulverizer mills | Vacuum out 1-1 mill due to coal gate leaking thru. | Brown | Derate | Coal | 1 | 2015 | 11 | 5.5667 | 1.4161 | 151.5208 | 27.2193 | 27
BR1 | MO | 2 | 1512 | 2016-01-13 23:42 | 2016-01-17 01:21 | 0 | 114 | 107 | Flue gas expansion joints | Replace Unit 2 ID Fan discharge expansion joint to the FGD | Brown | Maintenance | Coal | 1 | 2016 | 1 | 73.65 | 73.65 | 7880.55 | 107 | 107
BR1 | PO | 4 | 4261 | 2016-03-14 12:18 | 2016-04-11 22:06 | 0 | 114 | 107 | Control valves | Turbine valve and minor boiler spring outage | Brown | Other | Coal | 1 | 2016 | 3 | 681.8 | 681.8 | 72952.6 | 107 | 107
BR1 | D1 | 5 | 253 | 2016-04-12 09:30 | 2016-04-12 16:50 | 85 | 114 | 107 | Pulverizer feeder motor | 1-4 mill feeder will not start | Brown | Derate | Coal | 1 | 2016 | 4 | 7.3333 | 1.8655 | 199.6082 | 27.2193 | 27
BR1 | U1 | 6 | 4261 | 2016-04-14 04:25 | 2016-04-14 21:27 | 0 | 114 | 107 | Control valves | EHC leak on #5 gov. valve causing fire around turbine casing | Brown | Outage | Coal | 1 | 2016 | 4 | 17.0333 | 17.0333 | 1822.5667 | 107 | 107
BR1 | NC | 7 | 8700 | 2016-04-22 22:00 | 2016-04-23 02:00 | 0 | 114 | 107 | CEMS Certification and Recertification | Low Load RATA testing | Brown | Other | Coal | 1 | 2016 | 4 | 4 | 4 | 428 | 107 | 107
BR1 | NC | 8 | 8700 | 2016-04-25 23:00 | 2016-04-26 01:45 | 0 | 114 | 107 | CEMS Certification and Recertification | RATA Testing | Brown | Other | Coal | 1 | 2016 | 4 | 2.75 | 2.75 | 294.25 | 107 | 107
BR1 | NC | 9 | 8700 | 2016-04-26 21:00 | 2016-04-27 02:19 | 0 | 114 | 107 | CEMS Certification and Recertification | RATA Testing | Brown | Other | Coal | 1 | 2016 | 4 | 5.3167 | 5.3167 | 568.8833 | 107 | 107
BR1 | NC | 10 | 8700 | 2016-04-27 21:00 | 2016-04-28 04:03 | 0 | 114 | 107 | CEMS Certification and Recertification | RATA Testing | Brown | Other | Coal | 1 | 2016 | 4 | 7.05 | 7.05 | 754.35 | 107 | 107
BR1 | D1 | 11 | 300 | 2016-04-28 10:51 | 2016-04-28 11:29 | 85 | 114 | 107 | Pulverizer motors and drives | 1-4 pulverizer will not start | Brown | Derate | Coal | 1 | 2016 | 4 | 0.63333 | 0.16111 | 17.2389 | 27.2193 | 27
BR1 | NC | 13 | 8700 | 2016-05-23 23:00 | 2016-05-24 05:20 | 0 | 114 | 107 | CEMS Certification and Recertification | Mercury testing | Brown | Other | Coal | 1 | 2016 | 5 | 6.3333 | 6.3333 | 677.6667 | 107 | 107
BR1 | PD | 14 | 344 | 2016-06-26 23:00 | 2016-06-27 09:19 | 80 | 114 | 107 | Pulverizer inspection | 1-1 Mill Inspection | Brown | Derate | Coal | 1 | 2016 | 6 | 10.3167 | 3.0769 | 329.2284 | 31.9123 | 32
BR1 | PD | 15 | 344 | 2016-06-27 23:00 | 2016-06-28 03:08 | 80 | 114 | 107 | Pulverizer inspection | Mill Inspections | Brown | Derate | Coal | 1 | 2016 | 6 | 4.1333 | 1.2327 | 131.9041 | 31.9123 | 32
BR1 | PD | 16 | 344 | 2016-06-28 23:00 | 2016-06-29 00:21 | 80 | 114 | 107 | Pulverizer inspection | 1-4 Mill Inspection | Brown | Derate | Coal | 1 | 2016 | 6 | 1.35 | 0.40263 | 43.0816 | 31.9123 | 32
BR1 | PD | 17 | 310 | 2016-07-20 04:16 | 2016-07-20 04:48 | 95 | 114 | 107 | Pulverizer mills | Replace 1-1 mill heat slinger | Brown | Derate | Coal | 1 | 2016 | 7 | 0.53333 | 0.088889 | 9.5111 | 17.8333 | 18
BR1 | U1 | 18 | 4260 | 2016-07-27 13:50 | 2016-07-28 09:23 | 0 | 114 | 107 | Main stop valves | EHC oil leak on Throttle Valve | Brown | Outage | Coal | 1 | 2016 | 7 | 19.55 | 19.55 | 2091.85 | 107 | 107
BR1 | MO | 19 | 3410 | 2016-07-28 09:23 | 2016-07-28 18:04 | 0 | 114 | 107 | Feedwater pump | Repair 1-3 BFP recirculating valve regulator | Brown | Maintenance | Coal | 1 | 2016 | 7 | 8.6833 | 8.6833 | 929.1167 | 107 | 107
BR1 | PD | 20 | 310 | 2016-08-07 22:45 | 2016-08-08 05:15 | 90 | 114 | 107 | Pulverizer mills | 1-1 mill inspection | Brown | Derate | Coal | 1 | 2016 | 8 | 6.5 | 1.3684 | 146.4211 | 22.5263 | 23
BR1 | PD | 21 | 310 | 2016-08-08 23:00 | 2016-08-09 04:46 | 90 | 114 | 107 | Pulverizer mills | 1-2 mill inspection | Brown | Derate | Coal | 1 | 2016 | 8 | 5.7667 | 1.214 | 129.9018 | 22.5263 | 23
BR1 | PD | 22 | 310 | 2016-08-09 23:00 | 2016-08-10 04:47 | 80 | 114 | 107 | Pulverizer mills | 1-3 mill inspection | Brown | Derate | Coal | 1 | 2016 | 8 | 5.7833 | 1.7249 | 184.5594 | 31.9123 | 32
BR1 | PD | 23 | 310 | 2016-08-10 23:17 | 2016-08-11 04:53 | 90 | 114 | 107 | Pulverizer mills | 1-4 mill inspection | Brown | Derate | Coal | 1 | 2016 | 8 | 5.6 | 1.1789 | 126.1474 | 22.5263 | 23
BR1 | MO | 25 | 8250 | 2016-08-22 02:15 | 2016-08-22 15:38 | 0 | 114 | 107 | Dampers other than bypass | Inspect Brown 3 FGD shutoff damper | Brown | Maintenance | Coal | 1 | 2016 | 8 | 13.3833 | 13.3833 | 1432.0167 | 107 | 107
BR1 | U1 | 27 | 4302 | 2016-09-02 01:49 | 2016-09-02 02:15 | 0 | 114 | 107 | Turbine trip devices (including instruments) | Turbine trip on low vacuum due to loss of gland water | Brown | Outage | Coal | 1 | 2016 | 9 | 0.43333 | 0.43333 | 46.3667 | 107 | 107
BR1 | MO | 30 | 847 | 2016-10-08 00:50 | 2016-10-11 12:57 | 0 | 114 | 107 | Other expansion joints | Repair FGD expansion joint | Brown | Maintenance | Coal | 1 | 2016 | 10 | 84.1167 | 84.1167 | 9000.4833 | 107 | 107
BR1 | MO | 33 | 8560 | 2016-10-26 06:00 | 2016-10-26 17:11 | 0 | 114 | 107 | Electrostatic precipitator problems | Check for precipitator ground | Brown | Maintenance | Coal | 1 | 2016 | 10 | 11.1833 | 11.1833 | 1196.6167 | 107 | 107
BR1 | U1 | 35 | 4899 | 2016-11-03 17:16 | 2016-11-04 00:56 | 0 | 114 | 107 | Other miscellaneous generator problems | GCB control cabinet CT circuit loose connection | Brown | Outage | Coal | 1 | 2016 | 11 | 7.6667 | 7.6667 | 820.3333 | 107 | 107
BR1 | MO | 37 | 8560 | 2016-11-30 07:00 | 2016-12-01 14:02 | 0 | 114 | 107 | Electrostatic precipitator problems | F490Inspect 1-4 electrostatic precipitator | Brown | Maintenance | Coal | 1 | 2016 | 11 | 31.0333 | 31.0333 | 3320.5667 | 107 | 107
BR1 | MO | 39 | 1510 | 2016-12-30 05:00 | 2016-12-30 13:14 | 0 | 114 | 107 | Flue gas ducts (except recirculation) | FGD Duct inspection | Brown | Maintenance | Coal | 1 | 2016 | 12 | 8.2333 | 8.2333 | 880.9667 | 107 | 107
BR1 | PO | 3 | 1812 | 2017-03-03 07:00 | 2017-03-13 | 0 | 114 | 107 | Boiler Inspections - scheduled or routine | Annual outage for boiler inspection and misc repairs | Brown | Other | Coal | 1 | 2017 | 3 | 233 | 233 | 24931 | 107 | 107
BR1 | PE | 5 | 1812 | 2017-03-13 | 2017-03-18 13:42 | 0 | 114 | 107 | Boiler Inspections - scheduled or routine | Continue with testing/repairs of GSU | Brown | Other | Coal | 1 | 2017 | 3 | 133.7 | 133.7 | 14305.9 | 107 | 107
BR1 | D1 | 6 | 310 | 2017-04-18 10:15 | 2017-04-18 11:13 | 90 | 114 | 107 | Pulverizer mills | 1-2 mill pyrite door stuck closed | Brown | Derate | Coal | 1 | 2017 | 4 | 0.96667 | 0.20351 | 21.7754 | 22.5263 | 23
BR1 | NC | 8 | 4842 | 2017-06-19 05:58 | 2017-06-19 06:52 | 0 | 114 | 107 | Reactive and capability testing | Conducting MOD-025 testing | Brown | Other | Coal | 1 | 2017 | 6 | 0.9 | 0.9 | 96.3 | 107 | 107
BR1 | U1 | 11 | 1456 | 2017-06-28 10:27 | 2017-06-28 13:35 | 0 | 114 | 107 | Induced draft fan dampers | ID Fan outlet damper will not open | Brown | Outage | Coal | 1 | 2017 | 6 | 3.1333 | 3.1333 | 335.2667 | 107 | 107
BR1 | U1 | 15 | 4810 | 2017-07-20 06:43 | 2017-07-20 12:07 | 0 | 114 | 107 | Generator output breaker | Faulty cable on trip circuit between generator control and OCB | Brown | Outage | Coal | 1 | 2017 | 7 | 5.4 | 5.4 | 577.8 | 107 | 107
BR1 | U1 | 16 | 4810 | 2017-07-20 14:51 | 2017-07-20 20:02 | 0 | 114 | 107 | Generator output breaker | Faulty cable on trip circuit between genetator control and OCB | Brown | Outage | Coal | 1 | 2017 | 7 | 5.1833 | 5.1833 | 554.6167 | 107 | 107
BR1 | MO | 18 | 3112 | 2017-09-05 06:00 | 2017-09-06 10:37 | 0 | 114 | 107 | Condenser tube fouling tube side | Inspect condenser water boxes | Brown | Maintenance | Coal | 1 | 2017 | 9 | 28.6167 | 28.6167 | 3061.9833 | 107 | 107
BR1 | U1 | 20 | 3612 | 2017-09-08 08:36 | 2017-09-08 13:57 | 0 | 114 | 107 | Switchyard system protection devices - external | FX00Loss of Brown North transmission lines protective ralaying. | Brown | Outage | Coal | 1 | 2017 | 9 | 5.35 | 5.35 | 572.45 | 107 | 107
BR1 | U1 | 22 | 4499 | 2017-09-14 07:38 | 2017-09-14 12:55 | 0 | 114 | 107 | Other miscellaneous steam turbine problems | Main turbine turning gear motor failure | Brown | Outage | Coal | 1 | 2017 | 9 | 5.2833 | 5.2833 | 565.3167 | 107 | 107
BR1 | D1 | 24 | 264 | 2017-10-29 20:39 | 2017-10-30 06:47 | 95 | 114 | 107 | Other primary air fan problems | 1-1 mill primary air fan IB bearing failed | Brown | Derate | Coal | 1 | 2017 | 10 | 10.1333 | 1.6889 | 180.7111 | 17.8333 | 18
BR1 | U1 | 25 | 4299 | 2017-11-06 15:30 | 2017-11-07 09:14 | 0 | 114 | 107 | Other hydraulic system problems | EHC fluid leak on left side throttle valve | Brown | Outage | Coal | 1 | 2017 | 11 | 17.7333 | 17.7333 | 1897.4667 | 107 | 107
BR1 | U1 | 27 | 3641 | 2017-12-30 17:27 | 2018-01-01 |  | 114 | 107 | AC Circuit breakers | 1-2 BFP 2300V breaker failure | Brown | Outage | Coal | 1 | 2017 | 12 | 30.55 | 30.55 | 3268.85 | 107 | 107
BR1 | U1 | 1 | 3641 | 2018-01-01 | 2018-01-01 13:20 | 0 | 114 | 107 | AC Circuit breakers | 1-2 BFP 2300V breaker failure | Brown | Outage | Coal | 1 | 2018 | 1 | 13.3333 | 13.3333 | 1426.6667 | 107 | 107
BR1 | NC | 2 | 920 | 2018-01-04 | 2018-01-04 05:19 | 0 | 114 | 107 | Other slag and ash removal problems A | De-slag boiler | Brown | Other | Coal | 1 | 2018 | 1 | 5.3167 | 5.3167 | 568.8833 | 107 | 107
BR1 | D1 | 3 | 920 | 2018-01-04 05:19 | 2018-01-04 08:50 | 50 | 114 | 107 | Other slag and ash removal problems A | De-slag boiler | Brown | Derate | Coal | 1 | 2018 | 1 | 3.5167 | 1.9743 | 211.2468 | 60.0702 | 60
BR1 | NC | 4 | 9200 | 2018-01-05 10:54 | 2018-01-08 19:51 | 0 | 114 | 107 | High ash content | Combustion & slagging issues. Unit available for full load if needed. | Brown | Other | Coal | 1 | 2018 | 1 | 80.95 | 80.95 | 8661.65 | 107 | 107
BR1 | MO | 5 | 8560 | 2018-01-08 19:51 | 2018-01-09 13:22 | 0 | 114 | 107 | Electrostatic precipitator problems | Inspect precipitator | Brown | Maintenance | Coal | 1 | 2018 | 1 | 17.5167 | 17.5167 | 1874.2833 | 107 | 107
BR1 | MO | 7 | 1000 | 2018-01-23 21:07 | 2018-01-24 21:55 | 0 | 114 | 107 | Waterwall (Furnace wall) A | Waterwall tube leak east side | Brown | Maintenance | Coal | 1 | 2018 | 1 | 24.8 | 24.8 | 2653.6 | 107 | 107
BR1 | U1 | 9 | 4284 | 2018-01-31 15:19 | 2018-02-01 19:39 | 0 | 114 | 107 | Lube oil pump drive | Turbine auxiliary oil pump motor locked up | Brown | Outage | Coal | 1 | 2018 | 1 | 28.3333 | 28.3333 | 3031.6667 | 107 | 107
BR1 | SF | 11 | 4290 | 2018-03-02 07:00 | 2018-03-02 12:02 | 0 | 114 | 107 | Hydraulic system pumps | F340EH accumulator issue prevented turbine latching | Brown | Outage | Coal | 1 | 2018 | 3 | 5.0333 | 5.0333 | 538.5667 | 107 | 107
BR1 | U1 | 12 | 780 | 2018-03-09 06:52 | 2018-03-14 10:24 | 0 | 114 | 107 | Headers between tube bundles | F540Boiler leak at mud drum header. Loss of drum level (Dry). | Brown | Outage | Coal | 1 | 2018 | 3 | 123.5333 | 123.5333 | 13218.0667 | 107 | 107
BR2 | PD | 1 | 310 | 2013-01-04 13:00 | 2013-01-04 15:30 | 123 | 179 | 167 | Pulverizer mills | Investigate noise in 2-2 mill pyrite section 6408932 | Brown | Derate | Coal | 2 | 2013 | 1 | 2.5 | 0.78212 | 130.6145 | 52.2458 | 52
BR2 | U1 | 2 | 4601 | 2013-01-09 10:57 | 2013-01-09 23:20 | 0 | 179 | 167 | Exciter field rheostat | Rheostat contacts arching 6410703 | Brown | Outage | Coal | 2 | 2013 | 1 | 12.3833 | 12.3833 | 2068.0167 | 167 | 167
BR2 | PD | 3 | 255 | 2013-01-11 10:00 | 2013-01-11 13:40 | 135 | 179 | 167 | Pulverizer feeder coal scales | 2-1 mill feeder calibration 6410999 | Brown | Derate | Coal | 2 | 2013 | 1 | 3.6667 | 0.9013 | 150.5177 | 41.0503 | 41
BR2 | D1 | 4 | 9270 | 2013-01-14 21:06 | 2013-01-15 00:10 | 130 | 179 | 167 | Wet coal | 2-4 mill feeder plugged-wet coal | Brown | Derate | Coal | 2 | 2013 | 1 | 3.0667 | 0.83948 | 140.1929 | 45.7151 | 46
BR2 | D1 | 5 | 1700 | 2013-01-16 05:50 | 2013-01-16 06:48 | 135 | 179 | 167 | Feedwater controls (report local controls --- feedwater pump | Feedwater system upset causing the HP heater extractions to close. | Brown | Derate | Coal | 2 | 2013 | 1 | 0.96667 | 0.23762 | 39.6819 | 41.0503 | 41
BR2 | D1 | 6 | 1700 | 2013-01-16 20:30 | 2013-01-16 21:28 | 100 | 179 | 167 | Feedwater controls (report local controls --- feedwater pump | Feedwater system upset causing the HP heater extractions to close. | Brown | Derate | Coal | 2 | 2013 | 1 | 0.96667 | 0.42663 | 71.2471 | 73.7039 | 74
BR2 | PD | 7 | 300 | 2013-01-18 12:30 | 2013-01-18 16:51 | 130 | 179 | 167 | Pulverizer motors and drives | Align 2-4 mill motor 6412985 | Brown | Derate | Coal | 2 | 2013 | 1 | 4.35 | 1.1908 | 198.8606 | 45.7151 | 46
BR2 | PD | 8 | 3410 | 2013-01-24 23:25 | 2013-01-25 05:00 | 105 | 179 | 167 | Feedwater pump | Inspect 2-2 BFP OB bearing noise 6415235 | Brown | Derate | Coal | 2 | 2013 | 1 | 5.5833 | 2.3082 | 385.4683 | 69.0391 | 69
BR2 | D2 | 9 | 3410 | 2013-01-25 05:00 | 2013-01-25 23:08 | 105 | 179 | 167 | Feedwater pump | 2-2 BFP thrust shoes damaged 6415235 | Brown | Derate | Coal | 2 | 2013 | 1 | 18.1333 | 7.4965 | 1251.9091 | 69.0391 | 69
BR2 | D1 | 10 | 310 | 2013-01-26 08:45 | 2013-01-26 09:35 | 120 | 179 | 167 | Pulverizer mills | 2-2 mill south roll not deflecting | Brown | Derate | Coal | 2 | 2013 | 1 | 0.83333 | 0.27467 | 45.8706 | 55.0447 | 55
BR2 | PD | 11 | 310 | 2013-01-26 23:00 | 2013-01-27 00:34 | 120 | 179 | 167 | Pulverizer mills | Replace 2-2 mill south roll 6415610 | Brown | Derate | Coal | 2 | 2013 | 1 | 1.5667 | 0.51639 | 86.2367 | 55.0447 | 55
BR2 | D1 | 12 | 310 | 2013-01-27 18:32 | 2013-01-27 22:45 | 130 | 179 | 167 | Pulverizer mills | 2-2 mill south roll not deflecting 6415809 | Brown | Derate | Coal | 2 | 2013 | 1 | 4.2167 | 1.1543 | 192.7653 | 45.7151 | 46
BR2 | NC | 13 | 310 | 2013-01-29 23:00 | 2013-01-30 05:28 | 0 | 179 | 167 | Pulverizer mills | Set rolls on U2 mills 6365821 | Brown | Other | Coal | 2 | 2013 | 1 | 6.4667 | 6.4667 | 1079.9333 | 167 | 167
BR2 | D1 | 14 | 3410 | 2013-02-04 21:30 | 2013-02-06 14:50 | 110 | 179 | 167 | Feedwater pump | F9202-1 BFP thrust bearing wiped | Brown | Derate | Coal | 2 | 2013 | 2 | 41.3333 | 15.933 | 2660.8045 | 64.3743 | 64
BR2 | D1 | 15 | 30 | 2013-02-07 07:10 | 2013-02-07 07:20 | 80 | 179 | 167 | Coal conveyors and feeders | Coal transport conveyor tripper failed to start with coal bunker levels low 6420328 | Brown | Derate | Coal | 2 | 2013 | 2 | 0.16667 | 0.092179 | 15.3939 | 92.3631 | 92
BR2 | PD | 16 | 250 | 2013-02-21 23:52 | 2013-02-22 03:53 | 130 | 179 | 167 | Pulverizer feeders | 2-1 feeder belt replacement | Brown | Derate | Coal | 2 | 2013 | 2 | 4.0167 | 1.0995 | 183.6223 | 45.7151 | 46
BR2 | NC | 17 | 255 | 2013-02-22 10:35 | 2013-02-22 12:10 | 0 | 179 | 167 | Pulverizer feeder coal scales | 2-1 mill feeder calibration | Brown | Other | Coal | 2 | 2013 | 2 | 1.5833 | 1.5833 | 264.4167 | 167 | 167
BR2 | NC | 18 | 8700 | 2013-02-28 01:00 | 2013-02-28 04:00 | 0 | 179 | 167 | CEMS Certification and Recertification | Low load RATA testing | Brown | Other | Coal | 2 | 2013 | 2 | 3 | 3 | 501 | 167 | 167
BR2 | MO | 19 | 4263 | 2013-02-28 22:59 | 2013-02-28 23:44 | 0 | 179 | 167 | Reheat stop valves | Testing RH stop valves | Brown | Maintenance | Coal | 2 | 2013 | 2 | 0.75 | 0.75 | 125.25 | 167 | 167
BR2 | U1 | 20 | 3411 | 2013-03-01 21:44 | 2013-03-02 00:02 | 0 | 179 | 167 | Feedwater pump drive - motor | F490Ground in 2-2 BFP motor caused Aux Trans Trip relay to activate. | Brown | Outage | Coal | 2 | 2013 | 3 | 2.3 | 2.3 | 384.1 | 167 | 167
BR2 | D1 | 21 | 3411 | 2013-03-02 02:00 | 2013-03-05 22:12 | 110 | 179 | 167 | Feedwater pump drive - motor | F4902-2 BFP motor grounded out and can not be run. | Brown | Derate | Coal | 2 | 2013 | 3 | 92.2 | 35.5408 | 5935.3106 | 64.3743 | 64
BR2 | MO | 22 | 4609 | 2013-03-06 00:34 | 2013-03-06 04:47 | 0 | 179 | 167 | Other exciter problems | Roll A & C phase CT circuits on overall diff relays. | Brown | Maintenance | Coal | 2 | 2013 | 3 | 4.2167 | 4.2167 | 704.1833 | 167 | 167
BR2 | PD | 23 | 1980 | 2013-03-08 19:49 | 2013-03-08 22:10 | 150 | 179 | 167 | Boiler safety valve test | Set boiler main steam safeties | Brown | Derate | Coal | 2 | 2013 | 3 | 2.35 | 0.38073 | 63.5813 | 27.0559 | 27
BR2 | PD | 24 | 300 | 2013-03-10 03:00 | 2013-03-10 17:21 | 140 | 179 | 167 | Pulverizer motors and drives | Replace 2-1 mill motor bearing | Brown | Derate | Coal | 2 | 2013 | 3 | 14.35 | 3.1265 | 522.1316 | 36.3855 | 36
BR2 | MO | 25 | 9656 | 2013-03-11 22:31 | 2013-03-13 21:38 | 0 | 179 | 167 | Other stack or exhaust emissions testing - fossil | Off line for mercury testing on Brown 3 | Brown | Maintenance | Coal | 2 | 2013 | 3 | 47.1167 | 47.1167 | 7868.4833 | 167 | 167
BR2 | D1 | 26 | 9270 | 2013-03-18 18:09 | 2013-03-18 18:37 | 130 | 179 | 167 | Wet coal | 2-4 mill feeder plugged | Brown | Derate | Coal | 2 | 2013 | 3 | 0.46667 | 0.12775 | 21.3337 | 45.7151 | 46
BR2 | D1 | 27 | 9270 | 2013-03-18 18:37 | 2013-03-18 23:17 | 125 | 179 | 167 | Wet coal | 2-4 mill feeder plugged | Brown | Derate | Coal | 2 | 2013 | 3 | 4.6667 | 1.4078 | 235.1061 | 50.3799 | 50
BR2 | D1 | 28 | 9270 | 2013-03-19 06:02 | 2013-03-19 16:40 | 130 | 179 | 167 | Wet coal | 2-4 mill feeder plugged | Brown | Derate | Coal | 2 | 2013 | 3 | 10.6333 | 2.9108 | 486.1037 | 45.7151 | 46
BR2 | D1 | 29 | 9270 | 2013-03-19 17:33 | 2013-03-20 11:00 | 125 | 179 | 167 | Wet coal | 2-4 mill feeder plugged | Brown | Derate | Coal | 2 | 2013 | 3 | 17.45 | 5.2642 | 879.1291 | 50.3799 | 50
BR2 | D1 | 30 | 9270 | 2013-03-20 11:00 | 2013-03-20 11:29 | 145 | 179 | 167 | Wet coal | 2-4 mill feeder plugged | Brown | Derate | Coal | 2 | 2013 | 3 | 0.48333 | 0.091806 | 15.3317 | 31.7207 | 32
BR2 | D1 | 31 | 9270 | 2013-03-20 11:29 | 2013-03-20 17:18 | 135 | 179 | 167 | Wet coal | 2-4 mill feeder plugged | Brown | Derate | Coal | 2 | 2013 | 3 | 5.8167 | 1.4298 | 238.7758 | 41.0503 | 41
BR2 | D1 | 32 | 9270 | 2013-03-20 17:18 | 2013-03-20 19:59 | 135 | 179 | 167 | Wet coal | 2-4 mill feeder plugged | Brown | Derate | Coal | 2 | 2013 | 3 | 2.6833 | 0.65959 | 110.1516 | 41.0503 | 41
BR2 | D1 | 33 | 9270 | 2013-03-21 00:38 | 2013-03-21 14:10 | 130 | 179 | 167 | Wet coal | 2-4 mill coal feed problems | Brown | Derate | Coal | 2 | 2013 | 3 | 13.5333 | 3.7047 | 618.6775 | 45.7151 | 46
BR2 | D1 | 34 | 9270 | 2013-03-21 14:10 | 2013-03-21 18:48 | 160 | 179 | 167 | Wet coal | 2-4 mill coal feed problems | Brown | Derate | Coal | 2 | 2013 | 3 | 4.6333 | 0.49181 | 82.1317 | 17.7263 | 18
BR2 | D1 | 35 | 9270 | 2013-03-21 18:48 | 2013-03-21 19:43 | 165 | 179 | 167 | Wet coal | 2-4 mill coal feed problems | Brown | Derate | Coal | 2 | 2013 | 3 | 0.91667 | 0.071695 | 11.973 | 13.0615 | 13
BR2 | D1 | 37 | 9270 | 2013-03-21 19:43 | 2013-03-21 20:09 | 170 | 179 | 167 | Wet coal | 2-4 mill coal feed problems | Brown | Derate | Coal | 2 | 2013 | 3 | 0.43333 | 0.021788 | 3.6385 | 8.3966 | 8
BR2 | NC | 36 | 1100 | 2013-03-24 21:50 | 2013-03-24 22:05 | 0 | 179 | 167 | Waterwall (Furnace wall) B | Deslag boiler | Brown | Other | Coal | 2 | 2013 | 3 | 0.25 | 0.25 | 41.75 | 167 | 167
BR2 | NC | 38 | 1100 | 2013-03-28 11:15 | 2013-03-28 12:15 | 0 | 179 | 167 | Waterwall (Furnace wall) B | Deslag unit | Brown | Other | Coal | 2 | 2013 | 3 | 1 | 1 | 167 | 167 | 167
BR2 | D1 | 39 | 310 | 2013-04-01 09:09 | 2013-04-01 09:35 | 140 | 179 | 167 | Pulverizer mills | 2-3 mill vibration | Brown | Derate | Coal | 2 | 2013 | 4 | 0.43333 | 0.094413 | 15.767 | 36.3855 | 36
BR2 | D1 | 40 | 310 | 2013-04-01 09:35 | 2013-04-01 14:23 | 135 | 179 | 167 | Pulverizer mills | 2-3 mill vibration 6436028 | Brown | Derate | Coal | 2 | 2013 | 4 | 4.8 | 1.1799 | 197.0413 | 41.0503 | 41
BR2 | D1 | 41 | 310 | 2013-04-11 11:55 | 2013-04-11 12:54 | 135 | 179 | 167 | Pulverizer mills | Elevated vibration in 2-3 mill grinding section 6438408 | Brown | Derate | Coal | 2 | 2013 | 4 | 0.98333 | 0.24171 | 40.3661 | 41.0503 | 41
BR2 | D1 | 42 | 310 | 2013-04-19 17:34 | 2013-04-20 03:28 | 150 | 179 | 167 | Pulverizer mills | 2-3 mill south roll replacement due to broken spring bolt 6440220 | Brown | Derate | Coal | 2 | 2013 | 4 | 9.9 | 1.6039 | 267.8531 | 27.0559 | 27
BR2 | D1 | 43 | 9620 | 2013-04-22 14:10 | 2013-04-22 14:25 | 170 | 179 | 167 | Particulate stack emissions (fossil) | Exccedance of Particulate Matter target limit | Brown | Derate | Coal | 2 | 2013 | 4 | 0.25 | 0.01257 | 2.0992 | 8.3966 | 8
BR2 | D1 | 44 | 9620 | 2013-04-22 14:25 | 2013-04-23 05:34 | 165 | 179 | 167 | Particulate stack emissions (fossil) | Exccedance of Particulate Matter target limit | Brown | Derate | Coal | 2 | 2013 | 4 | 15.15 | 1.1849 | 197.881 | 13.0615 | 13
BR2 | D1 | 45 | 9620 | 2013-04-23 05:34 | 2013-04-23 08:58 | 170 | 179 | 167 | Particulate stack emissions (fossil) | Exccedance of Particulate Matter target limit | Brown | Derate | Coal | 2 | 2013 | 4 | 3.4 | 0.17095 | 28.5486 | 8.3966 | 8
BR2 | D1 | 46 | 310 | 2013-04-25 22:35 | 2013-04-26 00:20 | 135 | 179 | 167 | Pulverizer mills | Replace 2-3 mill west roll 6441769 | Brown | Derate | Coal | 2 | 2013 | 4 | 1.75 | 0.43017 | 71.838 | 41.0503 | 41
BR2 | D1 | 47 | 310 | 2013-04-27 09:27 | 2013-04-27 10:03 | 150 | 179 | 167 | Pulverizer mills | 2-1 mill loading up, need rolls set | Brown | Derate | Coal | 2 | 2013 | 4 | 0.6 | 0.097207 | 16.2335 | 27.0559 | 27
BR2 | D1 | 48 | 310 | 2013-04-27 10:03 | 2013-04-27 10:31 | 140 | 179 | 167 | Pulverizer mills | 2-1 mill loading up need rolls set 6442054 | Brown | Derate | Coal | 2 | 2013 | 4 | 0.46667 | 0.10168 | 16.9799 | 36.3855 | 36
BR2 | D1 | 49 | 310 | 2013-05-01 13:44 | 2013-05-01 17:28 | 135 | 179 | 167 | Pulverizer mills | Replace broken roll in 2-1 mill 6444295 | Brown | Derate | Coal | 2 | 2013 | 5 | 3.7333 | 0.91769 | 153.2544 | 41.0503 | 41
BR2 | D1 | 50 | 310 | 2013-05-01 17:28 | 2013-05-01 20:17 | 80 | 179 | 167 | Pulverizer mills | Replace broken roll in 2-1 mill and replace pyrite scrapper in 2-2 mill | Brown | Derate | Coal | 2 | 2013 | 5 | 2.8167 | 1.5578 | 260.1561 | 92.3631 | 92
BR2 | D1 | 51 | 310 | 2013-05-01 20:17 | 2013-05-01 21:36 | 135 | 179 | 167 | Pulverizer mills | Replace pyrite scrapper in 2-2 mill 6444295 | Brown | Derate | Coal | 2 | 2013 | 5 | 1.3167 | 0.32365 | 54.0495 | 41.0503 | 41
BR2 | D1 | 52 | 310 | 2013-05-21 14:48 | 2013-05-21 17:10 | 135 | 179 | 167 | Pulverizer mills | 2-4 mill vibration in grinding section | Brown | Derate | Coal | 2 | 2013 | 5 | 2.3667 | 0.58175 | 97.1523 | 41.0503 | 41
BR2 | D1 | 53 | 310 | 2013-05-21 17:10 | 2013-05-21 17:14 | 145 | 179 | 167 | Pulverizer mills | 2-4 mill vibration in grinding section 6452128 | Brown | Derate | Coal | 2 | 2013 | 5 | 0.066667 | 0.012663 | 2.1147 | 31.7207 | 32
BR2 | PD | 54 | 250 | 2013-05-23 21:00 | 2013-05-24 05:05 | 120 | 179 | 167 | Pulverizer feeders | Replace 2-4 mill feeder belt 6447918 | Brown | Derate | Coal | 2 | 2013 | 5 | 8.0833 | 2.6643 | 444.9446 | 55.0447 | 55
BR2 | D1 | 55 | 250 | 2013-05-27 11:15 | 2013-05-27 13:57 | 120 | 179 | 167 | Pulverizer feeders | 2-2 mill feeder speed very erratic 6458266 | Brown | Derate | Coal | 2 | 2013 | 5 | 2.7 | 0.88994 | 148.6207 | 55.0447 | 55
BR2 | NC | 56 | 4268 | 2013-05-29 04:08 | 2013-05-29 05:14 | 0 | 179 | 167 | Reheat/intercept valve testing | Turbine reheat/intercept valve test to troubleshoot problems with limits not reaching | Brown | Other | Coal | 2 | 2013 | 5 | 1.1 | 1.1 | 183.7 | 167 | 167
BR2 | U1 | 57 | 4268 | 2013-05-29 05:14 | 2013-05-29 06:23 | 0 | 179 | 167 | Reheat/intercept valve testing | Turbine trip while conducting reheat/intercept valve testing 6423407 | Brown | Outage | Coal | 2 | 2013 | 5 | 1.15 | 1.15 | 192.05 | 167 | 167
BR2 | U1 | 58 | 1000 | 2013-06-16 10:59 | 2013-06-17 01:59 | 0 | 179 | 167 | Waterwall (Furnace wall) A | Waterwall tube leak 6467216 | Brown | Outage | Coal | 2 | 2013 | 6 | 15 | 15 | 2505 | 167 | 167
BR2 | SF | 59 | 400 | 2013-06-17 01:59 | 2013-06-17 06:07 | 0 | 179 | 167 | Burner wind box fires | Investigate possible fire in burner windbox. | Brown | Outage | Coal | 2 | 2013 | 6 | 4.1333 | 4.1333 | 690.2667 | 167 | 167
BR2 | PD | 60 | 310 | 2013-06-20 23:00 | 2013-06-21 02:00 | 140 | 179 | 167 | Pulverizer mills | Inspect 2-4 mill motor coupling 6468780 | Brown | Derate | Coal | 2 | 2013 | 6 | 3 | 0.65363 | 109.1564 | 36.3855 | 36
BR2 | PD | 61 | 300 | 2013-06-23 22:00 | 2013-06-24 07:40 | 140 | 179 | 167 | Pulverizer motors and drives | Replace 2-4 mill motor bearings 6417202 | Brown | Derate | Coal | 2 | 2013 | 6 | 9.6667 | 2.1061 | 351.7263 | 36.3855 | 36
BR2 | U1 | 62 | 3420 | 2013-06-25 08:00 | 2013-06-26 05:16 | 0 | 179 | 167 | Feedwater piping and supports | 2-2 BFP warming line leaking at the connection to the discharge line. 6470031 | Brown | Outage | Coal | 2 | 2013 | 6 | 21.2667 | 21.2667 | 3551.5333 | 167 | 167
BR2 | PD | 63 | 310 | 2013-06-27 | 2013-06-28 03:22 | 140 | 179 | 167 | Pulverizer mills | Balance 2-4 mill exhauster | Brown | Derate | Coal | 2 | 2013 | 6 | 27.3667 | 5.9626 | 995.7492 | 36.3855 | 36
BR2 | U1 | 64 | 4750 | 2013-07-20 10:51 | 2013-07-20 12:26 | 0 | 179 | 167 | Other generator controls and metering problems | Generator tripped while investigating stator temp issue 6477753 | Brown | Outage | Coal | 2 | 2013 | 7 | 1.5833 | 1.5833 | 264.4167 | 167 | 167
BR2 | MO | 65 | 8560 | 2013-07-28 08:49 | 2013-07-28 20:20 | 0 | 179 | 167 | Electrostatic precipitator problems | Inspect precipitators for ground 6481210 | Brown | Maintenance | Coal | 2 | 2013 | 7 | 11.5167 | 11.5167 | 1923.2833 | 167 | 167
BR2 | PD | 67 | 3410 | 2013-08-11 06:00 | 2013-08-12 02:32 | 99 | 179 | 167 | Feedwater pump | Replace 2-1 BFP mechanical seals. Insp. 2-4 mill gearbox 6481606 6473659 | Brown | Derate | Coal | 2 | 2013 | 8 | 20.5333 | 9.1769 | 1532.5438 | 74.6369 | 75
BR2 | D1 | 68 | 3210 | 2013-08-24 09:47 | 2013-08-24 10:33 | 130 | 179 | 167 | Circulating water pumps | Change oil in 2-1 CWP OB bearing | Brown | Derate | Coal | 2 | 2013 | 8 | 0.76667 | 0.20987 | 35.0482 | 45.7151 | 46
BR2 | PD | 69 | 310 | 2013-08-25 22:00 | 2013-08-26 03:20 | 140 | 179 | 167 | Pulverizer mills | 2-1 Mill pre outage inspection | Brown | Derate | Coal | 2 | 2013 | 8 | 5.3333 | 1.162 | 194.0559 | 36.3855 | 36
BR2 | PD | 70 | 344 | 2013-08-26 22:00 | 2013-08-27 03:25 | 140 | 179 | 167 | Pulverizer inspection | 2-2 Mill pre outage inspection | Brown | Derate | Coal | 2 | 2013 | 8 | 5.4167 | 1.1802 | 197.088 | 36.3855 | 36
BR2 | PD | 71 | 344 | 2013-08-27 22:00 | 2013-08-28 02:30 | 140 | 179 | 167 | Pulverizer inspection | 2-3 Mill pre outage inspection | Brown | Derate | Coal | 2 | 2013 | 8 | 4.5 | 0.98045 | 163.7346 | 36.3855 | 36
BR2 | PD | 72 | 344 | 2013-08-28 22:00 | 2013-08-29 03:00 | 140 | 179 | 167 | Pulverizer inspection | 2-4 Mill pre outage inspection | Brown | Derate | Coal | 2 | 2013 | 8 | 5 | 1.0894 | 181.9274 | 36.3855 | 36
BR2 | MO | 73 | 8551 | 2013-09-03 09:31 | 2013-09-04 18:15 | 0 | 179 | 167 | Electrostatic precipitator field out of service | 2-1C & 2-1D precipitators out of service 6488094 | Brown | Maintenance | Coal | 2 | 2013 | 9 | 32.7333 | 32.7333 | 5466.4667 | 167 | 167
BR2 | SF | 75 | 8700 | 2013-09-05 07:40 | 2013-09-05 22:31 | 0 | 179 | 167 | CEMS Certification and Recertification | PM testing for BR3. Unable to startup unit during testing due to common stack. | Brown | Outage | Coal | 2 | 2013 | 9 | 14.85 | 14.85 | 2479.95 | 167 | 167
BR2 | U1 | 76 | 3431 | 2013-09-06 11:48 | 2013-09-07 02:51 | 0 | 179 | 167 | Other feedwater valves | HP heater inlet valve packing failure 6492643 | Brown | Outage | Coal | 2 | 2013 | 9 | 15.05 | 15.05 | 2513.35 | 167 | 167
BR2 | PD | 79 | 310 | 2013-10-10 02:00 | 2013-10-10 04:00 | 140 | 179 | 167 | Pulverizer mills | Inspect 2-3 mill exhauster coupling 6502142 | Brown | Derate | Coal | 2 | 2013 | 10 | 2 | 0.43575 | 72.7709 | 36.3855 | 36
BR2 | PD | 80 | 310 | 2013-10-17 20:20 | 2013-10-17 23:33 | 140 | 179 | 167 | Pulverizer mills | Replace 2-1 mill west roll cover 6504209 | Brown | Derate | Coal | 2 | 2013 | 10 | 3.2167 | 0.70084 | 117.0399 | 36.3855 | 36
BR2 | U2 | 82 | 270 | 2013-10-28 09:34 | 2013-10-30 23:06 | 0 | 179 | 167 | Primary air duct and dampers | 2-4 mill duct work explosion clean up & repair 6506580 6506586 | Brown | Outage | Coal | 2 | 2013 | 10 | 61.5333 | 61.5333 | 10276.0667 | 167 | 167
BR2 | D1 | 83 | 270 | 2013-10-30 23:06 | 2013-10-31 07:36 | 135 | 179 | 167 | Primary air duct and dampers | 2-4 mill duct work explosion damage | Brown | Derate | Coal | 2 | 2013 | 10 | 8.5 | 2.0894 | 348.9274 | 41.0503 | 41
BR2 | D1 | 84 | 270 | 2013-10-31 07:36 | 2013-11-01 12:48 | 140 | 179 | 167 | Primary air duct and dampers | 2-4 mill duct work explosion damage 6506586 | Brown | Derate | Coal | 2 | 2013 | 10 | 29.2 | 6.362 | 1062.4559 | 36.3855 | 36
BR2 | PO | 85 | 1801 | 2013-11-01 12:48 | 2013-11-25 02:58 | 0 | 179 | 167 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Planned outage | Brown | Other | Coal | 2 | 2013 | 11 | 566.1667 | 566.1667 | 94549.8333 | 167 | 167
BR2 | PD | 86 | 3410 | 2013-11-25 03:07 | 2013-11-25 09:15 | 115 | 179 | 167 | Feedwater pump | 2-2 BFP rebuild 6510580 | Brown | Derate | Coal | 2 | 2013 | 11 | 6.1333 | 2.1929 | 366.2182 | 59.7095 | 60
BR2 | PD | 87 | 855 | 2013-12-05 23:00 | 2013-12-06 01:00 | 100 | 179 | 167 | Drum relief/safety valves (Single drum only) | Set boiler safeties | Brown | Derate | Coal | 2 | 2013 | 12 | 2 | 0.88268 | 147.4078 | 73.7039 | 74
BR2 | D1 | 88 | 3410 | 2013-12-15 07:33 | 2013-12-16 16:39 | 115 | 179 | 167 | Feedwater pump | 2-2 BFP OB bearing temperature high 6521569 | Brown | Derate | Coal | 2 | 2013 | 12 | 33.1 | 11.8346 | 1976.3844 | 59.7095 | 60
BR2 | MO | 89 | 3410 | 2013-12-16 16:39 | 2013-12-17 14:44 | 0 | 179 | 167 | Feedwater pump | Replace 2-2 BFP balance line stop valve 6521569 | Brown | Maintenance | Coal | 2 | 2013 | 12 | 22.0833 | 22.0833 | 3687.9167 | 167 | 167
BR2 | D1 | 90 | 310 | 2013-12-17 21:30 | 2013-12-18 00:10 | 125 | 179 | 167 | Pulverizer mills | 2-4 mill broken spring bolt 6522662 | Brown | Derate | Coal | 2 | 2013 | 12 | 2.6667 | 0.80447 | 134.3464 | 50.3799 | 50
BR2 | NC | 91 | 8700 | 2013-12-18 08:30 | 2013-12-18 18:10 | 0 | 179 | 167 | CEMS Certification and Recertification | RATA testing to the bypass stack | Brown | Other | Coal | 2 | 2013 | 12 | 9.6667 | 9.6667 | 1614.3333 | 167 | 167
BR2 | D1 | 92 | 310 | 2013-12-18 18:10 | 2013-12-18 21:34 | 130 | 179 | 167 | Pulverizer mills | Replace 2-3 mill broken spring bolt 6522613 | Brown | Derate | Coal | 2 | 2013 | 12 | 3.4 | 0.93073 | 155.4313 | 45.7151 | 46
BR2 | NC | 93 | 8700 | 2013-12-19 09:10 | 2013-12-19 13:43 | 0 | 179 | 167 | CEMS Certification and Recertification | RATA testing to the bypass stack | Brown | Other | Coal | 2 | 2013 | 12 | 4.55 | 4.55 | 759.85 | 167 | 167
BR2 | PD | 1 | 310 | 2014-01-02 22:00 | 2014-01-03 02:00 | 125 | 179 | 167 | Pulverizer mills | Inspect 2-3 mill gearbox - 6529384 | Brown | Derate | Coal | 2 | 2014 | 1 | 4 | 1.2067 | 201.5196 | 50.3799 | 50
BR2 | D1 | 2 | 310 | 2014-01-11 18:55 | 2014-01-11 21:25 | 135 | 179 | 167 | Pulverizer mills | Repair 2-2 mill broken spring bolt - 6532683 | Brown | Derate | Coal | 2 | 2014 | 1 | 2.5 | 0.61453 | 102.6257 | 41.0503 | 41
BR2 | PD | 3 | 344 | 2014-01-13 09:44 | 2014-01-13 12:15 | 115 | 179 | 167 | Pulverizer inspection | Inspect 2-3 mill concerning thrust bearing issue | Brown | Derate | Coal | 2 | 2014 | 1 | 2.5167 | 0.89981 | 150.2689 | 59.7095 | 60
BR2 | D1 | 4 | 310 | 2014-02-11 20:04 | 2014-02-12 02:17 | 130 | 179 | 167 | Pulverizer mills | 2-4 mill west door broken spring bolt | Brown | Derate | Coal | 2 | 2014 | 2 | 6.2167 | 1.7018 | 284.1954 | 45.7151 | 46
BR2 | D1 | 5 | 310 | 2014-02-14 18:23 | 2014-02-14 19:11 | 135 | 179 | 167 | Pulverizer mills | 2-4 hot air damper not making limit 6543271 | Brown | Derate | Coal | 2 | 2014 | 2 | 0.8 | 0.19665 | 32.8402 | 41.0503 | 41
BR2 | D1 | 6 | 310 | 2014-02-16 06:34 | 2014-02-16 17:57 | 125 | 179 | 167 | Pulverizer mills | 2-2 mill shaft broken | Brown | Derate | Coal | 2 | 2014 | 2 | 11.3833 | 3.4341 | 573.4911 | 50.3799 | 50
BR2 | D1 | 7 | 310 | 2014-02-16 17:57 | 2014-02-19 12:47 | 130 | 179 | 167 | Pulverizer mills | Broken coal mill shaft 2-2 mill 6543464 | Brown | Derate | Coal | 2 | 2014 | 2 | 66.8333 | 18.2952 | 3055.2914 | 45.7151 | 46
BR2 | D1 | 8 | 310 | 2014-02-19 12:47 | 2014-02-20 22:00 | 135 | 179 | 167 | Pulverizer mills | Broken shaft 2-2 mill 6543464 | Brown | Derate | Coal | 2 | 2014 | 2 | 33.2167 | 8.165 | 1363.5534 | 41.0503 | 41
BR2 | PD | 9 | 3410 | 2014-02-20 22:00 | 2014-02-21 09:00 | 110 | 179 | 167 | Feedwater pump | Repair 2-2 BFP drain valve 6532228 | Brown | Derate | Coal | 2 | 2014 | 2 | 11 | 4.2402 | 708.1173 | 64.3743 | 64
BR2 | D1 | 10 | 310 | 2014-02-21 09:00 | 2014-02-21 22:13 | 130 | 179 | 167 | Pulverizer mills | Broken shaft 2-2 mill 6543464 | Brown | Derate | Coal | 2 | 2014 | 2 | 13.2167 | 3.618 | 604.201 | 45.7151 | 46
BR2 | MO | 11 | 3110 | 2014-02-21 22:13 | 2014-02-23 02:07 | 0 | 179 | 167 | Condenser tube leaks | Repair condenser tube leak and other misc. issues 6522386 | Brown | Maintenance | Coal | 2 | 2014 | 2 | 27.9 | 27.9 | 4659.3 | 167 | 167
BR2 | D1 | 12 | 310 | 2014-02-23 08:51 | 2014-02-24 08:24 | 130 | 179 | 167 | Pulverizer mills | Broken shaft 2-2 mill 6543464 | Brown | Derate | Coal | 2 | 2014 | 2 | 23.55 | 6.4466 | 1076.5902 | 45.7151 | 46
BR2 | D1 | 13 | 3410 | 2014-02-24 08:24 | 2014-02-26 20:00 | 105 | 179 | 167 | Feedwater pump | 2-2 BFP OB bearing hot 6546733 | Brown | Derate | Coal | 2 | 2014 | 2 | 59.6 | 24.6391 | 4114.7307 | 69.0391 | 69
BR2 | D1 | 14 | 310 | 2014-02-26 20:00 | 2014-02-28 12:26 | 130 | 179 | 167 | Pulverizer mills | Broken shaft 2-2 mill 6543464 | Brown | Derate | Coal | 2 | 2014 | 2 | 40.4333 | 11.0683 | 1848.4132 | 45.7151 | 46
BR2 | MO | 15 | 8560 | 2014-02-28 12:26 | 2014-03-02 18:19 | 0 | 179 | 167 | Electrostatic precipitator problems | Precipitator fields out of service and tube leak repair 6546848 | Brown | Maintenance | Coal | 2 | 2014 | 2 | 53.8833 | 53.8833 | 8998.5167 | 167 | 167
BR2 | D1 | 16 | 310 | 2014-03-02 20:15 | 2014-03-03 07:22 | 130 | 179 | 167 | Pulverizer mills | Broken shaft 2-2 mill 6543464 | Brown | Derate | Coal | 2 | 2014 | 3 | 11.1167 | 3.0431 | 508.1993 | 45.7151 | 46
BR2 | D1 | 17 | 3410 | 2014-03-03 07:22 | 2014-03-06 16:50 | 105 | 179 | 167 | Feedwater pump | 2-2 BFP oil leak 6546733 | Brown | Derate | Coal | 2 | 2014 | 3 | 81.4667 | 33.679 | 5624.3858 | 69.0391 | 69
BR2 | D1 | 18 | 310 | 2014-03-06 16:50 | 2014-03-06 19:00 | 130 | 179 | 167 | Pulverizer mills | Broken shaft 2-2 mill 6543464 | Brown | Derate | Coal | 2 | 2014 | 3 | 2.1667 | 0.59311 | 99.0493 | 45.7151 | 46
BR2 | PD | 19 | 310 | 2014-03-06 19:00 | 2014-03-08 07:40 | 130 | 179 | 167 | Pulverizer mills | 2-3 mill thrust bearing replacement 6529384 | Brown | Derate | Coal | 2 | 2014 | 3 | 36.6667 | 10.0372 | 1676.2197 | 45.7151 | 46
BR2 | U1 | 20 | 1040 | 2014-03-10 14:50 | 2014-03-11 21:09 | 0 | 179 | 167 | First superheater B | Tube leak in boiler penthouse area. 6550561 | Brown | Outage | Coal | 2 | 2014 | 3 | 30.3167 | 30.3167 | 5062.8833 | 167 | 167
BR2 | D1 | 21 | 350 | 2014-03-27 09:06 | 2014-03-27 10:05 | 145 | 179 | 167 | Pulverized fuel and air piping (from pulverizer to wind box) | 2-2 mill burner line temperature high | Brown | Derate | Coal | 2 | 2014 | 3 | 0.98333 | 0.18678 | 31.192 | 31.7207 | 32
BR2 | D1 | 22 | 350 | 2014-03-27 10:31 | 2014-03-27 13:13 | 145 | 179 | 167 | Pulverized fuel and air piping (from pulverizer to wind box) | 2-2 mill burner line temperature high | Brown | Derate | Coal | 2 | 2014 | 3 | 2.7 | 0.51285 | 85.6458 | 31.7207 | 32
BR2 | D1 | 23 | 350 | 2014-03-27 14:25 | 2014-03-27 14:47 | 145 | 179 | 167 | Pulverized fuel and air piping (from pulverizer to wind box) | Inspect 2-1A burner line for pluggage | Brown | Derate | Coal | 2 | 2014 | 3 | 0.36667 | 0.069646 | 11.6309 | 31.7207 | 32
BR2 | U1 | 24 | 1035 | 2014-04-24 10:11 | 2014-04-26 01:28 | 0 | 179 | 167 | Platen superheater | Tube leak in boiler SH section - 6563627 | Brown | Outage | Coal | 2 | 2014 | 4 | 39.2833 | 39.2833 | 6560.3167 | 167 | 167
BR2 | D1 | 25 | 3415 | 2014-04-27 15:00 | 2014-04-27 15:05 | 110 | 179 | 167 | Feedwater pump/drive lube oil system | 2-2 BFP auxiliary oil pump start failure -6564035 | Brown | Derate | Coal | 2 | 2014 | 4 | 0.083333 | 0.032123 | 5.3645 | 64.3743 | 64
BR2 | D1 | 26 | 270 | 2014-05-01 06:20 | 2014-05-01 13:27 | 130 | 179 | 167 | Primary air duct and dampers | 2-4 mill hot damper not opening 6564036 | Brown | Derate | Coal | 2 | 2014 | 5 | 7.1167 | 1.9481 | 325.339 | 45.7151 | 46
BR2 | D1 | 27 | 310 | 2014-05-03 07:58 | 2014-05-03 13:15 | 130 | 179 | 167 | Pulverizer mills | 2-4 mill vibrating and running rough 6566773 | Brown | Derate | Coal | 2 | 2014 | 5 | 5.2833 | 1.4463 | 241.528 | 45.7151 | 46
BR2 | D1 | 28 | 310 | 2014-05-08 20:00 | 2014-05-09 01:30 | 130 | 179 | 167 | Pulverizer mills | 2-2 mill roll vibrating | Brown | Derate | Coal | 2 | 2014 | 5 | 5.5 | 1.5056 | 251.433 | 45.7151 | 46
BR2 | D1 | 29 | 310 | 2014-05-15 07:22 | 2014-05-15 11:45 | 130 | 179 | 167 | Pulverizer mills | 2-2 mill vibration and air flow problems 6569852 | Brown | Derate | Coal | 2 | 2014 | 5 | 4.3833 | 1.1999 | 200.3845 | 45.7151 | 46
BR2 | D1 | 30 | 3620 | 2014-05-22 07:07 | 2014-05-22 07:30 | 80 | 179 | 167 | Main transformer | GSU cooling fans blown fuse. 6571527 | Brown | Derate | Coal | 2 | 2014 | 5 | 0.38333 | 0.21201 | 35.4059 | 92.3631 | 92
BR2 | D1 | 31 | 253 | 2014-05-28 23:52 | 2014-05-29 02:15 | 145 | 179 | 167 | Pulverizer feeder motor | 2-4 mill feeder tripped and would not restart 6575091 | Brown | Derate | Coal | 2 | 2014 | 5 | 2.3833 | 0.4527 | 75.6009 | 31.7207 | 32
BR2 | D1 | 32 | 310 | 2014-05-30 01:24 | 2014-05-30 02:13 | 145 | 179 | 167 | Pulverizer mills | Inspection for possible metal in 2-3 mill | Brown | Derate | Coal | 2 | 2014 | 5 | 0.81667 | 0.15512 | 25.9052 | 31.7207 | 32
BR2 | D1 | 33 | 300 | 2014-05-30 04:08 | 2014-05-30 05:43 | 135 | 179 | 167 | Pulverizer motors and drives | 2-3 mill failed to start 6575372 | Brown | Derate | Coal | 2 | 2014 | 5 | 1.5833 | 0.3892 | 64.9963 | 41.0503 | 41
BR2 | MO | 34 | 891 | 2014-06-04 22:35 | 2014-06-06 23:50 | 0 | 179 | 167 | Bottom ash hoppers (including gates) | Repair bottom ash hopper inside doors 6536640 & 6536645 | Brown | Maintenance | Coal | 2 | 2014 | 6 | 49.25 | 49.25 | 8224.75 | 167 | 167
BR2 | D1 | 35 | 1455 | 2014-06-07 09:50 | 2014-06-07 10:27 | 80 | 179 | 167 | Induced draft fans | 2-1 ID Fan tachometer problems 6577705 | Brown | Derate | Coal | 2 | 2014 | 6 | 0.61667 | 0.34106 | 56.9573 | 92.3631 | 92
BR2 | D1 | 36 | 310 | 2014-06-19 09:00 | 2014-06-19 09:32 | 130 | 179 | 167 | Pulverizer mills | 2-2 mill cold air damper won't operate 6581093 | Brown | Derate | Coal | 2 | 2014 | 6 | 0.53333 | 0.146 | 24.3814 | 45.7151 | 46
BR2 | D1 | 37 | 310 | 2014-06-20 07:12 | 2014-06-20 08:24 | 110 | 179 | 167 | Pulverizer mills | 2-4 mill broken spring bolt 6581258 | Brown | Derate | Coal | 2 | 2014 | 6 | 1.2 | 0.46257 | 77.2492 | 64.3743 | 64
BR2 | D1 | 38 | 310 | 2014-06-20 08:24 | 2014-06-20 09:56 | 130 | 179 | 167 | Pulverizer mills | 2-4 mill broken spring bolt 6581258 - | Brown | Derate | Coal | 2 | 2014 | 6 | 1.5333 | 0.41974 | 70.0965 | 45.7151 | 46
BR2 | PD | 39 | 310 | 2014-06-26 22:00 | 2014-06-27 03:21 | 130 | 179 | 167 | Pulverizer mills | Repair 2-4 mill CO probe leak | Brown | Derate | Coal | 2 | 2014 | 6 | 5.35 | 1.4645 | 244.5757 | 45.7151 | 46
BR2 | PD | 40 | 335 | 2014-07-02 22:00 | 2014-07-03 02:34 | 130 | 179 | 167 | Pulverizer lube oil system | Changed oil in 2-2 pulverizer 6585722 | Brown | Derate | Coal | 2 | 2014 | 7 | 4.5667 | 1.2501 | 208.7655 | 45.7151 | 46
BR2 | PD | 41 | 3631 | 2014-07-21 23:35 | 2014-07-22 00:08 | 80 | 179 | 167 | 480-volt circuit breakers | Isolate 2A 480 volt switchgear for breaker replacement 6590315 | Brown | Derate | Coal | 2 | 2014 | 7 | 0.55 | 0.30419 | 50.7997 | 92.3631 | 92
BR2 | U1 | 42 | 1700 | 2014-08-15 09:22 | 2014-08-15 11:02 | 0 | 179 | 167 | Feedwater controls (report local controls --- feedwater pump | Loss of drum level initiated boiler MFT 6598460 | Brown | Outage | Coal | 2 | 2014 | 8 | 1.6667 | 1.6667 | 278.3333 | 167 | 167
BR2 | U1 | 43 | 4293 | 2014-08-15 11:02 | 2014-08-15 13:13 | 0 | 179 | 167 | Hydraulic system pipes and valves | Turbine trip during roll up while starting up unit | Brown | Outage | Coal | 2 | 2014 | 8 | 2.1833 | 2.1833 | 364.6167 | 167 | 167
BR2 | U1 | 44 | 1700 | 2014-08-15 14:48 | 2014-08-15 15:38 | 0 | 179 | 167 | Feedwater controls (report local controls --- feedwater pump | Loss of drum level initiated boiler MFT SEE EVENT 42 | Brown | Outage | Coal | 2 | 2014 | 8 | 0.83333 | 0.83333 | 139.1667 | 167 | 167
BR2 | U1 | 45 | 4293 | 2014-08-15 15:38 | 2014-08-15 18:52 | 0 | 179 | 167 | Hydraulic system pipes and valves | Turbine tripped while synchronizing unit to grid with Main Field Bkr. closed | Brown | Outage | Coal | 2 | 2014 | 8 | 3.2333 | 3.2333 | 539.9667 | 167 | 167
BR2 | SF | 46 | 4810 | 2014-08-15 18:52 | 2014-08-15 21:30 | 0 | 179 | 167 | Generator output breaker | OCB not closing when synchronizing unit to grid. 6598633 | Brown | Outage | Coal | 2 | 2014 | 8 | 2.6333 | 2.6333 | 439.7667 | 167 | 167
BR2 | SF | 47 | 4810 | 2014-08-15 21:30 | 2014-08-15 23:43 | 0 | 179 | 167 | Generator output breaker | OCB not closing when synchronizing unit to grid. SEE EVENT 46 | Brown | Outage | Coal | 2 | 2014 | 8 | 2.2167 | 2.2167 | 370.1833 | 167 | 167
BR2 | PD | 48 | 1476 | 2014-08-20 05:00 | 2014-08-20 05:32 | 80 | 179 | 167 | Induced draft fan speed changer | Repair 2-2 ID Fan speed changer linkage 6599725 | Brown | Derate | Coal | 2 | 2014 | 8 | 0.53333 | 0.29497 | 49.2603 | 92.3631 | 92
BR2 | D1 | 49 | 350 | 2014-08-26 01:54 | 2014-08-26 05:16 | 135 | 179 | 167 | Pulverized fuel and air piping (from pulverizer to wind box) | 2-4A burner line fire at boiler | Brown | Derate | Coal | 2 | 2014 | 8 | 3.3667 | 0.82756 | 138.2026 | 41.0503 | 41
BR2 | PD | 50 | 310 | 2014-09-30 02:00 | 2014-09-30 08:41 | 135 | 179 | 167 | Pulverizer mills | 2-2 mill inspection | Brown | Derate | Coal | 2 | 2014 | 9 | 6.6833 | 1.6428 | 274.3527 | 41.0503 | 41
BR2 | PD | 51 | 310 | 2014-10-10 | 2014-10-10 01:26 | 135 | 179 | 167 | Pulverizer mills | Check 2-2 mill roll eccentrics 6612069 | Brown | Derate | Coal | 2 | 2014 | 10 | 1.4333 | 0.35233 | 58.8387 | 41.0503 | 41
BR2 | PO | 52 | 4402 | 2014-10-17 19:07 | 2014-11-17 14:10 | 0 | 179 | 167 | Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | Planned outage for turbine valve maint. | Brown | Other | Coal | 2 | 2014 | 10 | 739.05 | 739.05 | 123421.35 | 167 | 167
BR2 | PD | 53 | 1480 | 2014-11-23 07:00 | 2014-11-23 12:20 | 120 | 179 | 167 | Other induced draft fan problems | 2-1 ID Fan Vibration Inspection | Brown | Derate | Coal | 2 | 2014 | 11 | 5.3333 | 1.7579 | 293.5717 | 55.0447 | 55
BR2 | MO | 54 | 4619 | 2014-11-29 18:04 | 2014-12-11 02:52 | 0 | 179 | 167 | Other hydrogen system problems | Investigate and repair hydrogen leak and eccentricity issues | Brown | Maintenance | Coal | 2 | 2014 | 11 | 272.8 | 272.8 | 45557.6 | 167 | 167
BR2 | PD | 55 | 310 | 2014-12-11 23:00 | 2014-12-12 04:15 | 135 | 179 | 167 | Pulverizer mills | 2-4 mill south roll replacement | Brown | Derate | Coal | 2 | 2014 | 12 | 5.25 | 1.2905 | 215.514 | 41.0503 | 41
BR2 | NC | 1 | 8700 | 2015-01-13 21:30 | 2015-01-14 01:47 | 0 | 179 | 167 | CEMS Certification and Recertification | Low load RATA testing | Brown | Other | Coal | 2 | 2015 | 1 | 4.2833 | 4.2833 | 715.3167 | 167 | 167
BR2 | D1 | 2 | 310 | 2015-02-24 15:54 | 2015-02-25 09:16 | 140 | 179 | 167 | Pulverizer mills | 2-2 mill coal feeder pipe disconnected | Brown | Derate | Coal | 2 | 2015 | 2 | 17.3667 | 3.7838 | 631.8944 | 36.3855 | 36
BR2 | D1 | 3 | 320 | 2015-03-05 08:15 | 2015-03-05 10:57 | 140 | 179 | 167 | Foreign object in Pulverizers mill | Inspect ofr possible metal in mill | Brown | Derate | Coal | 2 | 2015 | 3 | 2.7 | 0.58827 | 98.2408 | 36.3855 | 36
BR2 | D1 | 4 | 3370 | 2015-03-05 21:25 | 2015-03-05 23:23 | 15 | 179 | 167 | Condensate system controls and instrumentation (not hotwell level | Condensate Throttling regulator erratic operation causing boiler trip | Brown | Derate | Coal | 2 | 2015 | 3 | 1.9667 | 1.8019 | 300.911 | 153.0056 | 153
BR2 | D1 | 5 | 310 | 2015-03-29 04:05 | 2015-03-29 09:15 | 140 | 179 | 167 | Pulverizer mills | 2-3 Mill south roll not deflecting | Brown | Derate | Coal | 2 | 2015 | 3 | 5.1667 | 1.1257 | 187.9916 | 36.3855 | 36
BR2 | D1 | 6 | 310 | 2015-03-30 05:32 | 2015-03-30 05:52 | 130 | 179 | 167 | Pulverizer mills | 2-4 mill hot air gate not opening | Brown | Derate | Coal | 2 | 2015 | 3 | 0.33333 | 0.091248 | 15.2384 | 45.7151 | 46
BR2 | D1 | 7 | 9270 | 2015-04-04 01:46 | 2015-04-04 02:27 | 140 | 179 | 167 | Wet coal | 2-3 mill feeder plugged due to wet coal | Brown | Derate | Coal | 2 | 2015 | 4 | 0.68333 | 0.14888 | 24.8634 | 36.3855 | 36
BR2 | U1 | 8 | 250 | 2015-04-17 02:07 | 2015-04-17 02:16 | 0 | 179 | 167 | Pulverizer feeders | 2-3 mill feeder plugged causing boiler MFT | Brown | Outage | Coal | 2 | 2015 | 4 | 0.15 | 0.15 | 25.05 | 167 | 167
BR2 | SF | 9 | 4740 | 2015-04-17 02:16 | 2015-04-17 09:15 | 0 | 179 | 167 | Emergency generator trip devices | Investigating generator protective realy trip | Brown | Outage | Coal | 2 | 2015 | 4 | 6.9833 | 6.9833 | 1166.2167 | 167 | 167
BR2 | MO | 11 | 3619 | 2015-04-18 05:56 | 2015-04-18 12:13 | 0 | 179 | 167 | Other switchyard equipment - external | Transmission maintenance in south substation | Brown | Maintenance | Coal | 2 | 2015 | 4 | 6.2833 | 6.2833 | 1049.3167 | 167 | 167
BR2 | D1 | 13 | 250 | 2015-05-18 06:42 | 2015-05-18 07:29 | 130 | 179 | 167 | Pulverizer feeders | 2-4 mill coal feeder inlet gate blockage | Brown | Derate | Coal | 2 | 2015 | 5 | 0.78333 | 0.21443 | 35.8101 | 45.7151 | 46
BR2 | MO | 14 | 1512 | 2015-05-21 18:32 | 2015-05-24 13:55 | 0 | 179 | 167 | Flue gas expansion joints | Replace Unit 1 & 2 combined duct expansion joint | Brown | Maintenance | Coal | 2 | 2015 | 5 | 67.3833 | 67.3833 | 11253.0167 | 167 | 167
BR2 | PD | 17 | 8700 | 2015-07-01 23:00 | 2015-07-02 05:14 | 110 | 179 | 167 | CEMS Certification and Recertification | Conducting load vs flow test for new monitoring probe | Brown | Derate | Coal | 2 | 2015 | 7 | 6.2333 | 2.4028 | 401.2665 | 64.3743 | 64
BR2 | D1 | 18 | 310 | 2015-07-23 10:10 | 2015-07-23 10:47 | 125 | 179 | 167 | Pulverizer mills | 2-4 mill hot gate failed to open | Brown | Derate | Coal | 2 | 2015 | 7 | 0.61667 | 0.18603 | 31.0676 | 50.3799 | 50
BR2 | D1 | 19 | 3414 | 2015-08-04 09:45 | 2015-08-04 10:18 | 160 | 179 | 167 | Feedwater pump local controls | 2-2 BFP recirc. valve not closing | Brown | Derate | Coal | 2 | 2015 | 8 | 0.55 | 0.05838 | 9.7494 | 17.7263 | 18
BR2 | D1 | 20 | 310 | 2015-08-14 19:18 | 2015-08-14 20:51 | 130 | 179 | 167 | Pulverizer mills | Excessive noise and vibration in 2-4 mill | Brown | Derate | Coal | 2 | 2015 | 8 | 1.55 | 0.4243 | 70.8584 | 45.7151 | 46
BR2 | MO | 21 | 1512 | 2015-08-21 21:28 | 2015-08-23 20:00 | 0 | 179 | 167 | Flue gas expansion joints | Repalce Unit 1/2 combined duct expansion join | Brown | Maintenance | Coal | 2 | 2015 | 8 | 46.5333 | 46.5333 | 7771.0667 | 167 | 167
BR2 | D1 | 23 | 3410 | 2015-08-31 21:30 | 2015-09-01 07:19 | 110 | 179 | 167 | Feedwater pump | Repair 2-1 BFP balance line leak | Brown | Derate | Coal | 2 | 2015 | 8 | 9.8167 | 3.7841 | 631.9411 | 64.3743 | 64
BR2 | U1 | 24 | 1710 | 2015-09-09 22:50 | 2015-09-10 00:34 | 0 | 179 | 167 | Combustion/steam condition controls (report local controls --- burners | At 2 mill, had a high bowl DP which initiated a boiler rundown | Brown | Outage | Coal | 2 | 2015 | 9 | 1.7333 | 1.7333 | 289.4667 | 167 | 167
BR2 | MO | 26 | 8720 | 2015-09-30 15:02 | 2015-09-30 16:31 | 0 | 179 | 167 | NOx analyzer problems | Install mercury monitoring probe in duct | Brown | Maintenance | Coal | 2 | 2015 | 9 | 1.4833 | 1.4833 | 247.7167 | 167 | 167
BR2 | MO | 28 | 8720 | 2015-10-01 06:00 | 2015-10-02 15:24 | 0 | 179 | 167 | NOx analyzer problems | Install mercury monitoring probe in duct | Brown | Maintenance | Coal | 2 | 2015 | 10 | 33.4 | 33.4 | 5577.8 | 167 | 167
BR2 | MO | 30 | 8250 | 2015-10-03 10:26 | 2015-10-03 12:47 | 0 | 179 | 167 | Dampers other than bypass | Inspect unit 1 & 2 isolation damper at FGD inlet | Brown | Maintenance | Coal | 2 | 2015 | 10 | 2.35 | 2.35 | 392.45 | 167 | 167
BR2 | PO | 33 | 1801 | 2015-10-16 10:33 | 2015-10-25 09:33 | 0 | 179 | 167 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Misc. boiler repairs along with CCRT system tie in. | Brown | Other | Coal | 2 | 2015 | 10 | 215 | 215 | 35905 | 167 | 167
BR2 | D1 | 34 | 129 | 2015-11-06 07:55 | 2015-11-06 08:33 | 135 | 179 | 167 | Other coal processing system problems | Flop gate limit for crushers malfunction causing crusher to be inoperable | Brown | Derate | Coal | 2 | 2015 | 11 | 0.63333 | 0.15568 | 25.9985 | 41.0503 | 41
BR2 | D1 | 35 | 250 | 2015-11-06 20:33 | 2015-11-06 21:14 | 130 | 179 | 167 | Pulverizer feeders | 2-4 mill feeder temperature start permissive not met | Brown | Derate | Coal | 2 | 2015 | 11 | 0.68333 | 0.18706 | 31.2386 | 45.7151 | 46
BR2 | MO | 37 | 1599 | 2015-12-14 07:00 | 2015-12-14 15:22 | 0 | 179 | 167 | Other miscellaneous boiler air and gas system problems | Repair leaks on 2-2 side of air preheating coils | Brown | Maintenance | Coal | 2 | 2015 | 12 | 8.3667 | 8.3667 | 1397.2333 | 167 | 167
BR2 | MO | 1 | 1512 | 2016-01-13 23:56 | 2016-01-17 04:57 | 0 | 179 | 167 | Flue gas expansion joints | Replace Unit 2 ID Fan discharge expansion joint to the FGD | Brown | Maintenance | Coal | 2 | 2016 | 1 | 77.0167 | 77.0167 | 12861.7833 | 167 | 167
BR2 | MO | 2 | 8560 | 2016-01-30 09:42 | 2016-02-01 14:48 | 0 | 179 | 167 | Electrostatic precipitator problems | Inspect 2-1 precipitators for grounds | Brown | Maintenance | Coal | 2 | 2016 | 1 | 53.1 | 53.1 | 8867.7 | 167 | 167
BR2 | MO | 3 | 8560 | 2016-02-01 15:17 | 2016-02-01 21:02 | 0 | 179 | 167 | Electrostatic precipitator problems | Inspect for precip. ground and repair small waterwall tube above bottom ash hopper #67 | Brown | Maintenance | Coal | 2 | 2016 | 2 | 5.75 | 5.75 | 960.25 | 167 | 167
BR2 | MO | 7 | 8560 | 2016-02-17 07:00 | 2016-02-18 14:20 | 0 | 179 | 167 | Electrostatic precipitator problems | Inspect precipitator | Brown | Maintenance | Coal | 2 | 2016 | 2 | 31.3333 | 31.3333 | 5232.6667 | 167 | 167
BR2 | MO | 9 | 1599 | 2016-02-19 08:10 | 2016-02-19 14:00 | 0 | 179 | 167 | Other miscellaneous boiler air and gas system problems | Repair air preheating coil leaks | Brown | Maintenance | Coal | 2 | 2016 | 2 | 5.8333 | 5.8333 | 974.1667 | 167 | 167
BR2 | PO | 11 | 1801 | 2016-03-14 12:18 | 2016-04-10 17:45 | 0 | 179 | 167 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Annual spring outage for boiler and misc. repairs | Brown | Other | Coal | 2 | 2016 | 3 | 653.45 | 653.45 | 109126.15 | 167 | 167
BR2 | D1 | 12 | 3431 | 2016-04-11 00:03 | 2016-04-11 03:02 | 110 | 179 | 167 | Other feedwater valves | 2-1 BFP recirc. valve will not close | Brown | Derate | Coal | 2 | 2016 | 4 | 2.9833 | 1.15 | 192.05 | 64.3743 | 64
BR2 | PD | 13 | 1455 | 2016-04-12 22:01 | 2016-04-13 02:52 | 80 | 179 | 167 | Induced draft fans | Investigate 2-1 ID Fan vibration | Brown | Derate | Coal | 2 | 2016 | 4 | 4.85 | 2.6824 | 447.9612 | 92.3631 | 92
BR2 | D1 | 14 | 310 | 2016-04-13 05:00 | 2016-04-13 08:20 | 130 | 179 | 167 | Pulverizer mills | Investigate liquid in 2-1 mill exhauster section | Brown | Derate | Coal | 2 | 2016 | 4 | 3.3333 | 0.91248 | 152.3836 | 45.7151 | 46
BR2 | D1 | 15 | 1455 | 2016-04-16 13:53 | 2016-04-16 14:22 | 125 | 179 | 167 | Induced draft fans | 2-1 ID Fan vibration | Brown | Derate | Coal | 2 | 2016 | 4 | 0.48333 | 0.14581 | 24.3503 | 50.3799 | 50
BR2 | D1 | 16 | 1455 | 2016-04-16 14:22 | 2016-04-18 12:35 | 160 | 179 | 167 | Induced draft fans | 2-1 ID Fan vibration | Brown | Derate | Coal | 2 | 2016 | 4 | 46.2167 | 4.9057 | 819.2485 | 17.7263 | 18
BR2 | D1 | 17 | 1455 | 2016-04-18 12:35 | 2016-04-23 16:45 | 150 | 179 | 167 | Induced draft fans | 2-1 ID Fan Vibration | Brown | Derate | Coal | 2 | 2016 | 4 | 124.1667 | 20.1164 | 3359.4367 | 27.0559 | 27
BR2 | MO | 18 | 1455 | 2016-04-22 21:00 | 2016-04-23 16:45 | 0 | 179 | 167 | Induced draft fans | 2-1 ID Fan vibration | Brown | Maintenance | Coal | 2 | 2016 | 4 | 19.75 | 19.75 | 3298.25 | 167 | 167
BR2 | NC | 20 | 8700 | 2016-04-25 23:00 | 2016-04-26 01:45 | 0 | 179 | 167 | CEMS Certification and Recertification | RATA testing | Brown | Other | Coal | 2 | 2016 | 4 | 2.75 | 2.75 | 459.25 | 167 | 167
BR2 | NC | 21 | 8700 | 2016-04-26 21:00 | 2016-04-27 02:19 | 0 | 179 | 167 | CEMS Certification and Recertification | RATA testing | Brown | Other | Coal | 2 | 2016 | 4 | 5.3167 | 5.3167 | 887.8833 | 167 | 167
BR2 | NC | 22 | 8700 | 2016-04-27 21:00 | 2016-04-28 04:03 | 0 | 179 | 167 | CEMS Certification and Recertification | RATA testing | Brown | Other | Coal | 2 | 2016 | 4 | 7.05 | 7.05 | 1177.35 | 167 | 167
BR2 | MO | 24 | 1360 | 2016-05-04 06:00 | 2016-05-04 16:42 | 0 | 179 | 167 | Boiler drains system | Replace main steam drains & repair boiler WW tube leak | Brown | Maintenance | Coal | 2 | 2016 | 5 | 10.7 | 10.7 | 1786.9 | 167 | 167
BR2 | MO | 25 | 1000 | 2016-05-05 14:40 | 2016-05-05 18:14 | 0 | 179 | 167 | Waterwall (Furnace wall) A | Inspect suspect tube for possible leak | Brown | Maintenance | Coal | 2 | 2016 | 5 | 3.5667 | 3.5667 | 595.6333 | 167 | 167
BR2 | U1 | 28 | 3399 | 2016-05-20 07:39 | 2016-05-20 09:18 | 0 | 179 | 167 | Other miscellaneous condensate system problems | APC system drain valve malfunction causing colis to purge. Lost DA tank level which le | Brown | Outage | Coal | 2 | 2016 | 5 | 1.65 | 1.65 | 275.55 | 167 | 167
BR2 | NC | 29 | 8700 | 2016-05-23 23:00 | 2016-05-24 05:20 | 0 | 179 | 167 | CEMS Certification and Recertification | Mercury testing | Brown | Other | Coal | 2 | 2016 | 5 | 6.3333 | 6.3333 | 1057.6667 | 167 | 167
BR2 | D1 | 30 | 310 | 2016-08-01 19:27 | 2016-08-02 00:37 | 130 | 179 | 167 | Pulverizer mills | Repair 2-3 mill north roll (not deflecting) | Brown | Derate | Coal | 2 | 2016 | 8 | 5.1667 | 1.4143 | 236.1946 | 45.7151 | 46
BR2 | D1 | 31 | 310 | 2016-08-04 07:09 | 2016-08-04 11:39 | 135 | 179 | 167 | Pulverizer mills | Repair 2-2 mill broken spring bolt | Brown | Derate | Coal | 2 | 2016 | 8 | 4.5 | 1.1061 | 184.7263 | 41.0503 | 41
BR2 | MO | 33 | 8250 | 2016-08-22 02:15 | 2016-08-22 15:38 | 0 | 179 | 167 | Dampers other than bypass | Inspect Brown 3 FGD shutoff damper | Brown | Maintenance | Coal | 2 | 2016 | 8 | 13.3833 | 13.3833 | 2235.0167 | 167 | 167
BR2 | MO | 36 | 1000 | 2016-09-17 12:08 | 2016-09-17 20:28 | 0 | 179 | 167 | Waterwall (Furnace wall) A | Frontwall steam drum terminal tube leak. | Brown | Maintenance | Coal | 2 | 2016 | 9 | 8.3333 | 8.3333 | 1391.6667 | 167 | 167
BR2 | MO | 39 | 1999 | 2016-09-27 05:28 | 2016-09-29 11:41 | 0 | 179 | 167 | Boiler | Repair A boiler corner buckstay along with misc. repairs. | Brown | Maintenance | Coal | 2 | 2016 | 9 | 54.2167 | 54.2167 | 9054.1833 | 167 | 167
BR2 | MO | 41 | 847 | 2016-10-07 22:38 | 2016-10-11 12:57 | 0 | 179 | 167 | Other expansion joints | REPAIR FGD EXPANSION JOINT | Brown | Maintenance | Coal | 2 | 2016 | 10 | 86.3167 | 86.3167 | 14414.8833 | 167 | 167
BR2 | D1 | 43 | 350 | 2016-10-21 04:23 | 2016-10-21 06:21 | 130 | 179 | 167 | Pulverized fuel and air piping (from pulverizer to wind box) | 2-3 mill exhauster distributor box coal leak | Brown | Derate | Coal | 2 | 2016 | 10 | 1.9667 | 0.53836 | 89.9063 | 45.7151 | 46
BR2 | MO | 45 | 8560 | 2016-10-26 06:00 | 2016-10-27 17:35 | 0 | 179 | 167 | Electrostatic precipitator problems | Check for precipitator ground & repair RH stop valve springs | Brown | Maintenance | Coal | 2 | 2016 | 10 | 35.5833 | 35.5833 | 5942.4167 | 167 | 167
BR2 | D1 | 47 | 250 | 2016-10-31 04:20 | 2016-10-31 07:19 | 135 | 179 | 167 | Pulverizer feeders | 2-2 mill feeder controls failed | Brown | Derate | Coal | 2 | 2016 | 10 | 2.9833 | 0.73333 | 122.4667 | 41.0503 | 41
BR2 | U1 | 48 | 3420 | 2016-11-15 12:21 | 2016-11-16 02:55 | 0 | 179 | 167 | Feedwater piping and supports | 2-2 BFP warming line leak | Brown | Outage | Coal | 2 | 2016 | 11 | 14.5667 | 14.5667 | 2432.6333 | 167 | 167
BR2 | MO | 50 | 580 | 2016-12-12 07:00 | 2016-12-13 14:04 | 0 | 179 | 167 | Desuperheater/attemperator piping | Repair SH attemperator piping identified during inspection | Brown | Maintenance | Coal | 2 | 2016 | 12 | 31.0667 | 31.0667 | 5188.1333 | 167 | 167
BR2 | MO | 52 | 1510 | 2016-12-30 05:00 | 2016-12-30 13:14 | 0 | 179 | 167 | Flue gas ducts (except recirculation) | FGD Duct inspection | Brown | Maintenance | Coal | 2 | 2016 | 12 | 8.2333 | 8.2333 | 1374.9667 | 167 | 167
BR2 | D1 | 2 | 270 | 2017-01-05 11:08 | 2017-01-05 12:01 | 130 | 179 | 167 | Primary air duct and dampers | 2-2 mill primary air damper drive failure | Brown | Derate | Coal | 2 | 2017 | 1 | 0.88333 | 0.24181 | 40.3817 | 45.7151 | 46
BR2 | D1 | 3 | 270 | 2017-01-05 12:01 | 2017-01-05 15:01 | 140 | 179 | 167 | Primary air duct and dampers | 2-2 mill primary air damper drive failure | Brown | Derate | Coal | 2 | 2017 | 1 | 3 | 0.65363 | 109.1564 | 36.3855 | 36
BR2 | D4 | 4 | 310 | 2017-01-23 09:30 | 2017-01-23 11:30 | 145 | 179 | 167 | Pulverizer mills | 2-3 Mill west door broken spring bolt | Brown | Derate | Coal | 2 | 2017 | 1 | 2 | 0.37989 | 63.4413 | 31.7207 | 32
BR2 | MO | 6 | 4263 | 2017-02-20 07:00 | 2017-02-21 09:54 | 0 | 179 | 167 | Reheat stop valves | Replace right side reheat stop valve actuator | Brown | Maintenance | Coal | 2 | 2017 | 2 | 26.9 | 26.9 | 4492.3 | 167 | 167
BR2 | NC | 8 | 8700 | 2017-03-13 22:00 | 2017-03-14 03:00 | 0 | 179 | 167 | CEMS Certification and Recertification | RATA testing | Brown | Other | Coal | 2 | 2017 | 3 | 5 | 5 | 835 | 167 | 167
BR2 | NC | 9 | 8700 | 2017-03-14 03:00 | 2017-03-14 09:15 | 0 | 179 | 167 | CEMS Certification and Recertification | RATA testing | Brown | Other | Coal | 2 | 2017 | 3 | 6.25 | 6.25 | 1043.75 | 167 | 167
BR2 | PO | 10 | 1801 | 2017-03-23 23:55 | 2017-04-09 01:20 | 0 | 179 | 167 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Planned Outage with boiler inspection and duct expansion joint replacement | Brown | Other | Coal | 2 | 2017 | 3 | 385.4167 | 385.4167 | 64364.5833 | 167 | 167
BR2 | D1 | 12 | 3410 | 2017-04-09 04:00 | 2017-04-10 03:30 | 110 | 179 | 167 | Feedwater pump | 2-1 BFP awaiting run form outage rebuild. | Brown | Derate | Coal | 2 | 2017 | 4 | 23.5 | 9.0587 | 1512.7961 | 64.3743 | 64
BR2 | D1 | 13 | 3410 | 2017-04-09 19:38 | 2017-04-10 03:30 | 90 | 179 | 167 | Feedwater pump | 2-2 BFP fluid coupling maximum output needs adjustment | Brown | Derate | Coal | 2 | 2017 | 4 | 7.8667 | 3.9114 | 653.197 | 83.0335 | 83
BR2 | PD | 14 | 1980 | 2017-04-11 21:10 | 2017-04-11 22:20 | 120 | 179 | 167 | Boiler safety valve test | Setting boiler safties post outage | Brown | Derate | Coal | 2 | 2017 | 4 | 1.1667 | 0.38454 | 64.2188 | 55.0447 | 55
BR2 | PD | 15 | 1980 | 2017-04-11 22:20 | 2017-04-12 01:06 | 80 | 179 | 167 | Boiler safety valve test | Setting boiler safties post outage | Brown | Derate | Coal | 2 | 2017 | 4 | 2.7667 | 1.5302 | 255.538 | 92.3631 | 92
BR2 | U1 | 17 | 1090 | 2017-06-02 10:25 | 2017-06-03 10:42 | 0 | 179 | 167 | Other boiler tube leaks | Tube leak in penthouse area | Brown | Outage | Coal | 2 | 2017 | 6 | 24.2833 | 24.2833 | 4055.3167 | 167 | 167
BR2 | NC | 19 | 9999 | 2017-06-14 23:50 | 2017-06-15 01:01 | 0 | 179 | 167 | Total unit performance testing (use appropriate codes for individual component testing) | VAR testing | Brown | Other | Coal | 2 | 2017 | 6 | 1.1833 | 1.1833 | 197.6167 | 167 | 167
BR2 | D1 | 20 | 250 | 2017-06-22 14:43 | 2017-06-22 15:41 | 140 | 179 | 167 | Pulverizer feeders | 2-1 mill feeder tachometer failure | Brown | Derate | Coal | 2 | 2017 | 6 | 0.96667 | 0.21061 | 35.1726 | 36.3855 | 36
BR2 | MO | 23 | 3110 | 2017-08-09 06:00 | 2017-08-09 17:32 | 0 | 179 | 167 | Condenser tube leaks | Check main condenser for possible tube leak | Brown | Maintenance | Coal | 2 | 2017 | 8 | 11.5333 | 11.5333 | 1926.0667 | 167 | 167
BR2 | U1 | 26 | 3612 | 2017-09-08 08:36 | 2017-09-08 13:57 | 0 | 179 | 167 | Switchyard system protection devices - external | FX00Loss of protective relaying for Brown North transmission lines. | Brown | Outage | Coal | 2 | 2017 | 9 | 5.35 | 5.35 | 893.45 | 167 | 167
BR2 | D1 | 28 | 3210 | 2017-10-23 18:13 | 2017-10-23 18:32 | 80 | 179 | 167 | Circulating water pumps | 2-2 circulating water pump bearing problem | Brown | Derate | Coal | 2 | 2017 | 10 | 0.31667 | 0.17514 | 29.2483 | 92.3631 | 92
BR2 | D1 | 30 | 3411 | 2017-12-29 08:33 | 2017-12-29 08:41 | 110 | 179 | 167 | Feedwater pump drive - motor | 2-1 BFP failed to start | Brown | Derate | Coal | 2 | 2017 | 12 | 0.13333 | 0.051397 | 8.5832 | 64.3743 | 64
BR2 | D1 | 1 | 1710 | 2018-01-02 02:00 | 2018-01-02 03:10 | 10 | 179 | 167 | Combustion/steam condition controls (report local controls --- burners | Boiler trip due to upset when losing air preheating coils | Brown | Derate | Coal | 2 | 2018 | 1 | 1.1667 | 1.1015 | 183.9488 | 157.6704 | 158
BR2 | D1 | 2 | 1710 | 2018-01-02 03:43 | 2018-01-02 08:12 | 10 | 179 | 167 | Combustion/steam condition controls (report local controls --- burners | Boiler trip due to upset when losing air preheating coils | Brown | Derate | Coal | 2 | 2018 | 1 | 4.4833 | 4.2329 | 706.8889 | 157.6704 | 158
BR2 | D1 | 3 | 1710 | 2018-01-02 09:30 | 2018-01-02 12:15 | 10 | 179 | 167 | Combustion/steam condition controls (report local controls --- burners | Boiler trip due to upset when losing air preheating coils | Brown | Derate | Coal | 2 | 2018 | 1 | 2.75 | 2.5964 | 433.5936 | 157.6704 | 158
BR2 | NC | 4 | 920 | 2018-01-04 | 2018-01-04 03:00 | 0 | 179 | 167 | Other slag and ash removal problems A | De-slag boiler | Brown | Other | Coal | 2 | 2018 | 1 | 3 | 3 | 501 | 167 | 167
BR2 | MO | 5 | 3621 | 2018-01-21 00:44 | 2018-01-21 00:58 | 0 | 179 | 167 | Unit auxiliaries transformer | 2B main feed brekaer inspection | Brown | Maintenance | Coal | 2 | 2018 | 1 | 0.23333 | 0.23333 | 38.9667 | 167 | 167
BR2 | PD | 7 | 310 | 2018-03-06 02:00 | 2018-03-06 05:00 | 135 | 179 | 167 | Pulverizer mills | F0602-4 Mill had a broken roll. | Brown | Derate | Coal | 2 | 2018 | 3 | 3 | 0.73743 | 123.1508 | 41.0503 | 41
BR2 | U1 | 8 | 9650 | 2018-03-12 07:59 | 2018-03-12 19:28 | 0 | 179 | 167 | Other stack or exhaust emissions (fossil) | F830Lost power to scrubber facility | Brown | Outage | Coal | 2 | 2018 | 3 | 11.4833 | 11.4833 | 1917.7167 | 167 | 167
BR2 | PD | 9 | 250 | 2018-03-19 21:59 | 2018-03-19 23:46 | 59 | 179 | 167 | Pulverizer feeders | F0602-3 mill feeder belt broken and needed repair. | Brown | Derate | Coal | 2 | 2018 | 3 | 1.7833 | 1.1955 | 199.6536 | 111.9553 | 112
BR3 | NC | 1 | 1710 | 2013-01-05 19:00 | 2013-01-05 21:15 | 0 | 456 | 411 | Combustion/steam condition controls (report local controls --- burners | Tuning boiler controls | Brown | Other | Coal | 3 | 2013 | 1 | 2.25 | 2.25 | 924.75 | 411 | 411
BR3 | U1 | 2 | 1060 | 2013-01-07 12:52 | 2013-01-09 14:44 | 0 | 456 | 411 | First reheater A | Suspected leak in RH section 6410136 | Brown | Outage | Coal | 3 | 2013 | 1 | 49.8667 | 49.8667 | 20495.2 | 411 | 411
BR3 | D1 | 3 | 3410 | 2013-01-10 11:44 | 2013-01-10 15:20 | 325 | 456 | 411 | Feedwater pump | 3-2 BFP IB pmp bearing temp hi 6410884 | Brown | Derate | Coal | 3 | 2013 | 1 | 3.6 | 1.0342 | 425.0605 | 118.0724 | 118
BR3 | NC | 4 | 8817 | 2013-01-11 09:00 | 2013-01-11 18:00 | 0 | 456 | 411 | SCR NOx Control system | Mid load SCR testing | Brown | Other | Coal | 3 | 2013 | 1 | 9 | 9 | 3699 | 411 | 411
BR3 | PD | 5 | 250 | 2013-01-17 | 2013-01-17 04:15 | 350 | 456 | 411 | Pulverizer feeders | Replace 3-5 mill feeder belt & roller 6412801 | Brown | Derate | Coal | 3 | 2013 | 1 | 4.25 | 0.98794 | 406.0428 | 95.5395 | 96
BR3 | D1 | 6 | 310 | 2013-01-17 06:48 | 2013-01-17 09:25 | 355 | 456 | 411 | Pulverizer mills | 3-3 mill thrust bearing failure | Brown | Derate | Coal | 3 | 2013 | 1 | 2.6167 | 0.57957 | 238.2027 | 91.0329 | 91
BR3 | PD | 7 | 8817 | 2013-01-17 09:25 | 2013-01-17 17:50 | 340 | 456 | 411 | SCR NOx Control system | SCR mid load testing | Brown | Derate | Coal | 3 | 2013 | 1 | 8.4167 | 2.1411 | 879.9846 | 104.5526 | 105
BR3 | D1 | 8 | 310 | 2013-01-17 17:50 | 2013-01-19 12:00 | 355 | 456 | 411 | Pulverizer mills | 3-3 mill thrust bearing failure | Brown | Derate | Coal | 3 | 2013 | 1 | 42.1667 | 9.3395 | 3838.5537 | 91.0329 | 91
BR3 | PD | 9 | 8817 | 2013-01-19 12:00 | 2013-01-19 17:40 | 180 | 456 | 411 | SCR NOx Control system | SCR low load testing | Brown | Derate | Coal | 3 | 2013 | 1 | 5.6667 | 3.4298 | 1409.6579 | 248.7632 | 249
BR3 | D1 | 10 | 310 | 2013-01-19 17:40 | 2013-01-19 22:41 | 355 | 456 | 411 | Pulverizer mills | 3-3 mill thrust bearing failure 6412940 | Brown | Derate | Coal | 3 | 2013 | 1 | 5.0167 | 1.1111 | 456.6817 | 91.0329 | 91
BR3 | D1 | 11 | 3414 | 2013-01-22 06:20 | 2013-01-22 06:54 | 295 | 456 | 411 | Feedwater pump local controls | 3-1 BFPT LP stm stp vlv not opening 6414641 | Brown | Derate | Coal | 3 | 2013 | 1 | 0.56667 | 0.20007 | 82.23 | 145.1118 | 145
BR3 | PD | 12 | 310 | 2013-01-27 22:00 | 2013-01-28 04:57 | 330 | 456 | 411 | Pulverizer mills | 3-1 mill pre outage inspection 6415483 | Brown | Derate | Coal | 3 | 2013 | 1 | 6.95 | 1.9204 | 789.2822 | 113.5658 | 114
BR3 | NC | 13 | 740 | 2013-01-28 21:00 | 2013-01-28 22:00 | 0 | 456 | 411 | Boiler recirculation pumps | Testing Hot Water Recirc. system @ minimum loading | Brown | Other | Coal | 3 | 2013 | 1 | 1 | 1 | 411 | 411 | 411
BR3 | PD | 14 | 310 | 2013-01-28 22:00 | 2013-01-29 04:26 | 350 | 456 | 411 | Pulverizer mills | 3-4 mill pre-out insp in conj with HWRS testing. 6415487 The Hot Water Recirc. testing | Brown | Derate | Coal | 3 | 2013 | 1 | 6.4333 | 1.4955 | 614.6373 | 95.5395 | 96
BR3 | NC | 15 | 740 | 2013-01-29 14:00 | 2013-01-29 22:00 | 0 | 456 | 411 | Boiler recirculation pumps | Hot Water Recirc. testing at mid load | Brown | Other | Coal | 3 | 2013 | 1 | 8 | 8 | 3288 | 411 | 411
BR3 | PD | 16 | 310 | 2013-01-29 22:00 | 2013-01-30 03:10 | 350 | 456 | 411 | Pulverizer mills | 3-5 mill preoutage inspection 6415488 | Brown | Derate | Coal | 3 | 2013 | 1 | 5.1667 | 1.201 | 493.6206 | 95.5395 | 96
BR3 | NC | 17 | 310 | 2013-02-08 00:35 | 2013-02-08 01:30 | 0 | 456 | 411 | Pulverizer mills | Set rolls 3-2 & 3-3 mills | Brown | Other | Coal | 3 | 2013 | 2 | 0.91667 | 0.91667 | 376.75 | 411 | 411
BR3 | MO | 18 | 1500 | 2013-02-10 00:48 | 2013-02-12 23:07 | 0 | 456 | 411 | Air heater soot blowers | Inspect Air Heater sootblowers 6408251 | Brown | Maintenance | Coal | 3 | 2013 | 2 | 70.3167 | 70.3167 | 28900.15 | 411 | 411
BR3 | D1 | 19 | 310 | 2013-02-13 02:36 | 2013-02-14 14:10 | 350 | 456 | 411 | Pulverizer mills | 3-3 mill radial seal damage | Brown | Derate | Coal | 3 | 2013 | 2 | 35.5667 | 8.2677 | 3398.0206 | 95.5395 | 96
BR3 | D1 | 20 | 310 | 2013-02-14 14:10 | 2013-02-15 11:32 | 360 | 456 | 411 | Pulverizer mills | 3-3 mill radial seal damage 6421955 | Brown | Derate | Coal | 3 | 2013 | 2 | 21.3667 | 4.4982 | 1848.7789 | 86.5263 | 87
BR3 | MO | 22 | 1360 | 2013-02-16 08:30 | 2013-02-17 15:53 | 0 | 456 | 411 | Boiler drains system | Modify boiler blowdown tank discharge piping | Brown | Maintenance | Coal | 3 | 2013 | 2 | 31.3833 | 31.3833 | 12898.55 | 411 | 411
BR3 | D1 | 24 | 310 | 2013-02-19 06:08 | 2013-02-19 17:00 | 360 | 456 | 411 | Pulverizer mills | 3-3 mill radial seal replacement 6421955 | Brown | Derate | Coal | 3 | 2013 | 2 | 10.8667 | 2.2877 | 940.2526 | 86.5263 | 87
BR3 | D1 | 25 | 300 | 2013-02-20 06:02 | 2013-02-20 06:32 | 350 | 456 | 411 | Pulverizer motors and drives | 3-3 mill motor ground | Brown | Derate | Coal | 3 | 2013 | 2 | 0.5 | 0.11623 | 47.7697 | 95.5395 | 96
BR3 | D1 | 26 | 300 | 2013-02-20 06:32 | 2013-02-20 17:35 | 365 | 456 | 411 | Pulverizer motors and drives | 3-3 mill motor ground | Brown | Derate | Coal | 3 | 2013 | 2 | 11.05 | 2.2052 | 906.3181 | 82.0197 | 82
BR3 | D1 | 27 | 8825 | 2013-02-20 17:35 | 2013-02-20 18:15 | 365 | 456 | 411 | Other SCR NOx problems | Request loading to 330 mw after boiler trip to establish temperatures for SCR ammonia | Brown | Derate | Coal | 3 | 2013 | 2 | 0.66667 | 0.13304 | 54.6798 | 82.0197 | 82
BR3 | D1 | 28 | 300 | 2013-02-20 18:15 | 2013-02-20 20:55 | 365 | 456 | 411 | Pulverizer motors and drives | 3-3 mill motor ground 6423841 | Brown | Derate | Coal | 3 | 2013 | 2 | 2.6667 | 0.53216 | 218.7193 | 82.0197 | 82
BR3 | NC | 29 | 770 | 2013-02-22 09:00 | 2013-02-22 11:35 | 0 | 456 | 411 | Other boiler recirculation problems | Hot Water Recirculating System testing | Brown | Other | Coal | 3 | 2013 | 2 | 2.5833 | 2.5833 | 1061.75 | 411 | 411
BR3 | PD | 30 | 300 | 2013-02-23 06:30 | 2013-02-23 11:10 | 350 | 456 | 411 | Pulverizer motors and drives | 3-3 mill motor alignment check | Brown | Derate | Coal | 3 | 2013 | 2 | 4.6667 | 1.0848 | 445.8509 | 95.5395 | 96
BR3 | NC | 31 | 8700 | 2013-02-28 01:00 | 2013-02-28 04:00 | 0 | 456 | 411 | CEMS Certification and Recertification | Low load RATA testing | Brown | Other | Coal | 3 | 2013 | 2 | 3 | 3 | 1233 | 411 | 411
BR3 | PD | 32 | 3412 | 2013-03-14 22:00 | 2013-03-14 22:45 | 315 | 456 | 411 | Feedwater pump drive - steam turbine | Check 3-1 BFPT vibration | Brown | Derate | Coal | 3 | 2013 | 3 | 0.75 | 0.23191 | 95.3141 | 127.0855 | 127
BR3 | PO | 33 | 1812 | 2013-03-16 00:11 | 2013-03-24 05:45 | 0 | 456 | 411 | Boiler Inspections - scheduled or routine | Planned spring outage for boiler inspection & repairs and Replacing inlet and outlet F | Brown | Other | Coal | 3 | 2013 | 3 | 197.5667 | 197.5667 | 81199.9 | 411 | 411
BR3 | SF | 34 | 860 | 2013-03-24 05:45 | 2013-03-25 02:33 | 0 | 456 | 411 | Soot blowers - air (see code 3844 for air delivery system) | Air Heater sootblowing air compressors safeties failure | Brown | Outage | Coal | 3 | 2013 | 3 | 20.8 | 20.8 | 8548.8 | 411 | 411
BR3 | U1 | 35 | 1750 | 2013-03-25 03:39 | 2013-03-25 04:14 | 0 | 456 | 411 | Burner management system | Oil guns tripped resulting in boiler MFT | Brown | Outage | Coal | 3 | 2013 | 3 | 0.58333 | 0.58333 | 239.75 | 411 | 411
BR3 | U1 | 36 | 810 | 2013-03-25 08:18 | 2013-03-30 04:30 | 0 | 456 | 411 | Boiler supports and structures (use code 1320 for tube supports) | PF pipe structural steel damaged | Brown | Outage | Coal | 3 | 2013 | 3 | 116.2 | 116.2 | 47758.2 | 411 | 411
BR3 | D1 | 37 | 3410 | 2013-03-30 12:25 | 2013-04-02 01:30 | 312 | 456 | 411 | Feedwater pump | 3-1 BFP rebuild 6430239 | Brown | Derate | Coal | 3 | 2013 | 3 | 61.0833 | 19.2895 | 7927.9737 | 129.7895 | 130
BR3 | D1 | 38 | 3410 | 2013-04-02 11:50 | 2013-04-08 15:28 | 310 | 456 | 411 | Feedwater pump | Removed 3-1 BFP to inspect due to high IB & OB bearing temperatures. Pump seized after | Brown | Derate | Coal | 3 | 2013 | 4 | 147.6333 | 47.2686 | 19427.3811 | 131.5921 | 132
BR3 | D1 | 39 | 3410 | 2013-04-09 15:10 | 2013-04-10 09:28 | 310 | 456 | 411 | Feedwater pump | 3-1 BFP extremely high temperature on OB bearing 6430239 | Brown | Derate | Coal | 3 | 2013 | 4 | 18.3 | 5.8592 | 2408.1355 | 131.5921 | 132
BR3 | D1 | 40 | 3410 | 2013-04-10 09:28 | 2013-04-15 10:40 | 320 | 456 | 411 | Feedwater pump | 3-1 BFP extremely high temperature on OB bearing | Brown | Derate | Coal | 3 | 2013 | 4 | 121.2 | 36.1474 | 14856.5684 | 122.5789 | 123
BR3 | D1 | 41 | 3410 | 2013-04-15 10:40 | 2013-04-15 13:30 | 310 | 456 | 411 | Feedwater pump | 3-1 BFP extremely high temperature on OB bearing | Brown | Derate | Coal | 3 | 2013 | 4 | 2.8333 | 0.90716 | 372.8443 | 131.5921 | 132
BR3 | D1 | 42 | 3410 | 2013-04-15 13:30 | 2013-04-18 20:50 | 320 | 456 | 411 | Feedwater pump | 3-1 BFP extremely high temperature on OB bearing | Brown | Derate | Coal | 3 | 2013 | 4 | 79.3333 | 23.6608 | 9724.5965 | 122.5789 | 123
BR3 | D1 | 43 | 3412 | 2013-04-19 21:45 | 2013-04-20 01:10 | 310 | 456 | 411 | Feedwater pump drive - steam turbine | Investigate and repair oil leak on 3-1 BFPT OB turbine bearing 6438098 | Brown | Derate | Coal | 3 | 2013 | 4 | 3.4167 | 1.0939 | 449.6064 | 131.5921 | 132
BR3 | D1 | 44 | 3412 | 2013-04-20 02:15 | 2013-04-20 22:14 | 320 | 456 | 411 | Feedwater pump drive - steam turbine | Investigate and repair oil leak on 3-1 BFPT OB turbine bearing 6438098 | Brown | Derate | Coal | 3 | 2013 | 4 | 19.9833 | 5.9599 | 2449.536 | 122.5789 | 123
BR3 | D1 | 45 | 3410 | 2013-04-23 10:20 | 2013-05-03 08:52 | 320 | 456 | 411 | Feedwater pump | Investigate elevated injection water temperature on 3-2 BFP OB pump gland 6441283 | Brown | Derate | Coal | 3 | 2013 | 4 | 238.5333 | 71.1415 | 29239.1649 | 122.5789 | 123
BR3 | MO | 46 | 360 | 2013-05-03 08:52 | 2013-05-05 11:19 | 0 | 456 | 411 | Burners | Replace 3-3C and 3-4C burner nozzles 6444537 | Brown | Maintenance | Coal | 3 | 2013 | 5 | 50.45 | 50.45 | 20734.95 | 411 | 411
BR3 | D1 | 47 | 3410 | 2013-05-05 14:58 | 2013-05-13 10:30 | 320 | 456 | 411 | Feedwater pump | Rebuild 3-2 BFP due to failed pump bearings 6441283 | Brown | Derate | Coal | 3 | 2013 | 5 | 187.5333 | 55.931 | 22987.6386 | 122.5789 | 123
BR3 | D1 | 48 | 253 | 2013-05-19 12:40 | 2013-05-19 15:55 | 325 | 456 | 411 | Pulverizer feeder motor | 3-3 Feeder tripped, unknown reason 6448510 | Brown | Derate | Coal | 3 | 2013 | 5 | 3.25 | 0.93366 | 383.7352 | 118.0724 | 118
BR3 | D1 | 49 | 253 | 2013-05-19 16:05 | 2013-05-19 19:07 | 350 | 456 | 411 | Pulverizer feeder motor | 3-3 Feeder tripped, unknown reason 6448510 | Brown | Derate | Coal | 3 | 2013 | 5 | 3.0333 | 0.70512 | 289.8031 | 95.5395 | 96
BR3 | D1 | 50 | 310 | 2013-05-20 12:46 | 2013-05-20 13:23 | 370 | 456 | 411 | Pulverizer mills | Found 3-3 mill pyrite section door open 6451908 | Brown | Derate | Coal | 3 | 2013 | 5 | 0.61667 | 0.1163 | 47.7998 | 77.5132 | 78
BR3 | PD | 51 | 250 | 2013-05-20 23:00 | 2013-05-21 04:46 | 350 | 456 | 411 | Pulverizer feeders | Replace 3-2 mill feeder tail roller 6448484 | Brown | Derate | Coal | 3 | 2013 | 5 | 5.7667 | 1.3405 | 550.9443 | 95.5395 | 96
BR3 | D1 | 52 | 310 | 2013-05-25 13:01 | 2013-05-25 18:40 | 350 | 456 | 411 | Pulverizer mills | 3-4 mill tripped, unknown reason. 6452825 | Brown | Derate | Coal | 3 | 2013 | 5 | 5.65 | 1.3134 | 539.798 | 95.5395 | 96
BR3 | D1 | 53 | 3410 | 2013-05-30 18:35 | 2013-05-30 19:11 | 310 | 456 | 411 | Feedwater pump | Oil leak on 3-2 BFP IB bearing 6458871 | Brown | Derate | Coal | 3 | 2013 | 5 | 0.6 | 0.19211 | 78.9553 | 131.5921 | 132
BR3 | D1 | 54 | 3410 | 2013-05-30 19:11 | 2013-05-31 03:18 | 320 | 456 | 411 | Feedwater pump | Oil leak on 3-2 BFP IB bearing and replace 3-1D burner line elbow 6458871 | Brown | Derate | Coal | 3 | 2013 | 5 | 8.1167 | 2.4208 | 994.9325 | 122.5789 | 123
BR3 | PD | 55 | 350 | 2013-05-31 03:18 | 2013-05-31 03:28 | 350 | 456 | 411 | Pulverized fuel and air piping (from pulverizer to wind box) | Replace 3-1D burner line elbow 6452707 | Brown | Derate | Coal | 3 | 2013 | 5 | 0.16667 | 0.038743 | 15.9232 | 95.5395 | 96
BR3 | D1 | 56 | 310 | 2013-06-01 15:04 | 2013-06-01 15:32 | 360 | 456 | 411 | Pulverizer mills | 3-2 mill exhauster bearing vibration high | Brown | Derate | Coal | 3 | 2013 | 6 | 0.46667 | 0.098246 | 40.3789 | 86.5263 | 87
BR3 | NC | 57 | 750 | 2013-06-06 22:00 | 2013-06-07 03:50 | 0 | 456 | 411 | Boiler recirculation piping including downcomers | Hot Water Recirculating System testing | Brown | Other | Coal | 3 | 2013 | 6 | 5.8333 | 5.8333 | 2397.5 | 411 | 411
BR3 | D1 | 59 | 3440 | 2013-06-19 03:30 | 2013-06-19 14:49 | 400 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP Heater tube leak | Brown | Derate | Coal | 3 | 2013 | 6 | 11.3167 | 1.3898 | 571.1939 | 50.4737 | 50
BR3 | D1 | 60 | 3440 | 2013-06-19 14:49 | 2013-06-19 23:25 | 435 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP Heater tube leak | Brown | Derate | Coal | 3 | 2013 | 6 | 8.6 | 0.39605 | 162.7776 | 18.9276 | 19
BR3 | PD | 61 | 3410 | 2013-06-19 23:25 | 2013-06-20 02:09 | 310 | 456 | 411 | Feedwater pump | Inspect 3-1 BFP balance line orfice sizing 6468481 | Brown | Derate | Coal | 3 | 2013 | 6 | 2.7333 | 0.87515 | 359.6851 | 131.5921 | 132
BR3 | D1 | 62 | 3440 | 2013-06-20 02:09 | 2013-06-20 09:59 | 435 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP Heater tube leak | Brown | Derate | Coal | 3 | 2013 | 6 | 7.8333 | 0.36075 | 148.2664 | 18.9276 | 19
BR3 | D1 | 63 | 3414 | 2013-06-20 09:59 | 2013-06-20 11:35 | 320 | 456 | 411 | Feedwater pump local controls | 3-1 BFP LP & HP stop valves would not open 6468667 | Brown | Derate | Coal | 3 | 2013 | 6 | 1.6 | 0.47719 | 196.1263 | 122.5789 | 123
BR3 | D1 | 64 | 3440 | 2013-06-20 11:35 | 2013-06-20 22:00 | 435 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP Heater tube leak | Brown | Derate | Coal | 3 | 2013 | 6 | 10.4167 | 0.47971 | 197.1628 | 18.9276 | 19
BR3 | PD | 65 | 3410 | 2013-06-20 22:00 | 2013-06-21 04:20 | 310 | 456 | 411 | Feedwater pump | Modify 3-2 BFP balance line orfice 6468481 | Brown | Derate | Coal | 3 | 2013 | 6 | 6.3333 | 2.0278 | 833.4167 | 131.5921 | 132
BR3 | D1 | 66 | 3440 | 2013-06-21 04:20 | 2013-06-21 05:27 | 435 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP Heater tube leak | Brown | Derate | Coal | 3 | 2013 | 6 | 1.1167 | 0.051425 | 21.1359 | 18.9276 | 19
BR3 | D1 | 67 | 3410 | 2013-06-21 05:27 | 2013-06-21 09:49 | 310 | 456 | 411 | Feedwater pump | Inspect 3-2 BFP OB pump bearing and oil piping 6468481 | Brown | Derate | Coal | 3 | 2013 | 6 | 4.3667 | 1.3981 | 574.6189 | 131.5921 | 132
BR3 | D1 | 68 | 3440 | 2013-06-21 09:49 | 2013-06-23 12:30 | 435 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP heater tube leak | Brown | Derate | Coal | 3 | 2013 | 6 | 50.6833 | 2.3341 | 959.3155 | 18.9276 | 19
BR3 | D1 | 69 | 1750 | 2013-06-23 12:30 | 2013-06-23 13:00 | 60 | 456 | 411 | Burner management system | Boiler trip from loss of 3-2 mill feeder | Brown | Derate | Coal | 3 | 2013 | 6 | 0.5 | 0.43421 | 178.4605 | 356.9211 | 357
BR3 | D1 | 70 | 1750 | 2013-06-23 13:00 | 2013-06-23 13:40 | 145 | 456 | 411 | Burner management system | Boiler trip from loss of 3-2 mill feeder | Brown | Derate | Coal | 3 | 2013 | 6 | 0.66667 | 0.45468 | 186.8728 | 280.3092 | 280
BR3 | D1 | 71 | 3440 | 2013-06-23 13:40 | 2013-06-25 12:25 | 435 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP heater tube leak | Brown | Derate | Coal | 3 | 2013 | 6 | 46.75 | 2.153 | 884.8668 | 18.9276 | 19
BR3 | D1 | 72 | 3440 | 2013-06-25 12:25 | 2013-06-28 21:24 | 430 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP heater tube leak | Brown | Derate | Coal | 3 | 2013 | 6 | 80.9833 | 4.6175 | 1897.7805 | 23.4342 | 23
BR3 | MO | 73 | 3440 | 2013-06-28 21:24 | 2013-07-02 10:28 | 0 | 456 | 411 | High pressure heater tube leaks | Repair 3F-2 HP heater tube leak and replace 3-3 BCWP | Brown | Maintenance | Coal | 3 | 2013 | 6 | 85.0667 | 85.0667 | 34962.4 | 411 | 411
BR3 | D1 | 75 | 1470 | 2013-07-08 09:40 | 2013-07-08 10:33 | 55 | 456 | 411 | Induced draft fan motors and drives | MFT due furn overpress from 3-2 ID Fan trip. 6474832 6474835 | Brown | Derate | Coal | 3 | 2013 | 7 | 0.88333 | 0.77679 | 319.2611 | 361.4276 | 361
BR3 | U1 | 76 | 1470 | 2013-07-08 10:33 | 2013-07-08 12:25 | 0 | 456 | 411 | Induced draft fan motors and drives | 3-2 ID Fan motor trip caused a boiler MFT. Further investigation found 3-1 ID Fan inle | Brown | Outage | Coal | 3 | 2013 | 7 | 1.8667 | 1.8667 | 767.2 | 411 | 411
BR3 | D1 | 77 | 300 | 2013-07-10 16:17 | 2013-07-11 03:37 | 350 | 456 | 411 | Pulverizer motors and drives | 3-1 mill motor failed due to ground 6475403 | Brown | Derate | Coal | 3 | 2013 | 7 | 11.3333 | 2.6345 | 1082.7807 | 95.5395 | 96
BR3 | D1 | 78 | 3439 | 2013-07-11 03:37 | 2013-07-11 16:57 | 435 | 456 | 411 | HP heater head leaks | 3F-2 HP Heater head leaking | Brown | Derate | Coal | 3 | 2013 | 7 | 13.3333 | 0.61404 | 252.3684 | 18.9276 | 19
BR3 | D1 | 79 | 3439 | 2013-07-12 06:10 | 2013-07-13 | 435 | 456 | 411 | HP heater head leaks | 3F-2 HP Heater head leaking | Brown | Derate | Coal | 3 | 2013 | 7 | 17.8333 | 0.82127 | 337.5428 | 18.9276 | 19
BR3 | PD | 80 | 350 | 2013-07-13 | 2013-07-13 04:25 | 370 | 456 | 411 | Pulverized fuel and air piping (from pulverizer to wind box) | Install blank 3-3C burner line 6475717 | Brown | Derate | Coal | 3 | 2013 | 7 | 4.4167 | 0.83297 | 342.3498 | 77.5132 | 78
BR3 | D1 | 81 | 3439 | 2013-07-13 04:25 | 2013-07-15 07:45 | 435 | 456 | 411 | HP heater head leaks | 3F-2 HP Heater head leaking | Brown | Derate | Coal | 3 | 2013 | 7 | 51.3333 | 2.364 | 971.6184 | 18.9276 | 19
BR3 | D1 | 82 | 310 | 2013-07-15 07:45 | 2013-07-15 08:32 | 360 | 456 | 411 | Pulverizer mills | 3-3 mill west roll vibration 6476725 | Brown | Derate | Coal | 3 | 2013 | 7 | 0.78333 | 0.16491 | 67.7789 | 86.5263 | 87
BR3 | D1 | 83 | 3439 | 2013-07-15 08:32 | 2013-07-16 | 435 | 456 | 411 | HP heater head leaks | 3F-2 HP Heater head leaking | Brown | Derate | Coal | 3 | 2013 | 7 | 15.4667 | 0.71228 | 292.7474 | 18.9276 | 19
BR3 | PD | 84 | 310 | 2013-07-16 | 2013-07-16 05:18 | 370 | 456 | 411 | Pulverizer mills | Check 3-3 mill rolls for vibration 6476725 | Brown | Derate | Coal | 3 | 2013 | 7 | 5.3 | 0.99956 | 410.8197 | 77.5132 | 78
BR3 | D1 | 85 | 3439 | 2013-07-16 05:18 | 2013-07-16 22:45 | 435 | 456 | 411 | HP heater head leaks | 3F-2 HP heater head leaking | Brown | Derate | Coal | 3 | 2013 | 7 | 17.45 | 0.80362 | 330.2872 | 18.9276 | 19
BR3 | D1 | 86 | 3415 | 2013-07-16 22:45 | 2013-07-16 23:35 | 275 | 456 | 411 | Feedwater pump/drive lube oil system | Swap 3-2 BFP TO cooler, suspected leak | Brown | Derate | Coal | 3 | 2013 | 7 | 0.83333 | 0.33077 | 135.9485 | 163.1382 | 163
BR3 | D1 | 87 | 3439 | 2013-07-16 23:35 | 2013-07-17 07:37 | 435 | 456 | 411 | HP heater head leaks | 3F-2 HP heater head leaking 6475012 | Brown | Derate | Coal | 3 | 2013 | 7 | 8.0333 | 0.36996 | 152.052 | 18.9276 | 19
BR3 | D1 | 88 | 1470 | 2013-07-17 15:29 | 2013-07-17 20:02 | 435 | 456 | 411 | Induced draft fan motors and drives | 3-2 ID Fan Hi amps and in alarm | Brown | Derate | Coal | 3 | 2013 | 7 | 4.55 | 0.20954 | 86.1207 | 18.9276 | 19
BR3 | U1 | 89 | 1060 | 2013-07-17 20:02 | 2013-07-21 22:59 | 0 | 456 | 411 | First reheater A | Radiant RH tube leak 6477271 | Brown | Outage | Coal | 3 | 2013 | 7 | 98.95 | 98.95 | 40668.45 | 411 | 411
BR3 | D1 | 90 | 300 | 2013-07-23 07:52 | 2013-07-23 08:55 | 350 | 456 | 411 | Pulverizer motors and drives | 3-2 mill motor high IB bearing temperature 6478807 | Brown | Derate | Coal | 3 | 2013 | 7 | 1.05 | 0.24408 | 100.3164 | 95.5395 | 96
BR3 | NC | 91 | 4842 | 2013-08-01 12:05 | 2013-08-01 13:19 | 0 | 456 | 411 | Reactive and capability testing | Annual generator reactive testing | Brown | Other | Coal | 3 | 2013 | 8 | 1.2333 | 1.2333 | 506.9 | 411 | 411
BR3 | U1 | 92 | 1060 | 2013-08-10 00:19 | 2013-08-15 06:00 | 0 | 456 | 411 | First reheater A | Radiant RH Tube leak W.O. #6484253 | Brown | Outage | Coal | 3 | 2013 | 8 | 125.6833 | 125.6833 | 51655.85 | 411 | 411
BR3 | D1 | 94 | 253 | 2013-08-19 09:45 | 2013-08-19 15:45 | 340 | 456 | 411 | Pulverizer feeder motor | 3-2 Mill feeder repeated tripping 6486882 | Brown | Derate | Coal | 3 | 2013 | 8 | 6 | 1.5263 | 627.3158 | 104.5526 | 105
BR3 | D1 | 95 | 3415 | 2013-08-20 11:51 | 2013-08-20 20:06 | 300 | 456 | 411 | Feedwater pump/drive lube oil system | 3-2 BFP OB bearing oil leak 6487203 | Brown | Derate | Coal | 3 | 2013 | 8 | 8.25 | 2.8224 | 1159.9934 | 140.6053 | 141
BR3 | PD | 96 | 344 | 2013-08-20 23:00 | 2013-08-21 01:24 | 340 | 456 | 411 | Pulverizer inspection | 3-1 Mill riffle inspection | Brown | Derate | Coal | 3 | 2013 | 8 | 2.4 | 0.61053 | 250.9263 | 104.5526 | 105
BR3 | PD | 97 | 344 | 2013-08-21 23:07 | 2013-08-22 00:54 | 360 | 456 | 411 | Pulverizer inspection | 3-1 mill riffle inspection | Brown | Derate | Coal | 3 | 2013 | 8 | 1.7833 | 0.37544 | 154.3053 | 86.5263 | 87
BR3 | PD | 98 | 344 | 2013-08-22 23:30 | 2013-08-23 00:26 | 360 | 456 | 411 | Pulverizer inspection | 3-1 MIl riffle inspection | Brown | Derate | Coal | 3 | 2013 | 8 | 0.93333 | 0.19649 | 80.7579 | 86.5263 | 87
BR3 | PD | 99 | 344 | 2013-08-25 22:00 | 2013-08-26 00:43 | 360 | 456 | 411 | Pulverizer inspection | 3-1 MIl riffle inspection | Brown | Derate | Coal | 3 | 2013 | 8 | 2.7167 | 0.57193 | 235.0632 | 86.5263 | 87
BR3 | PD | 100 | 310 | 2013-08-26 22:00 | 2013-08-26 23:50 | 360 | 456 | 411 | Pulverizer mills | 3-1 Mill riffle inspection 6485947 | Brown | Derate | Coal | 3 | 2013 | 8 | 1.8333 | 0.38596 | 158.6316 | 86.5263 | 87
BR3 | D1 | 101 | 740 | 2013-08-27 17:43 | 2013-08-28 | 430 | 456 | 411 | Boiler recirculation pumps | Load limitation with 3-1 BCWP outage | Brown | Derate | Coal | 3 | 2013 | 8 | 6.2833 | 0.35826 | 147.245 | 23.4342 | 23
BR3 | D1 | 102 | 740 | 2013-08-28 20:03 | 2013-08-28 22:00 | 430 | 456 | 411 | Boiler recirculation pumps | Load limitation with 3-1 BCWP outage | Brown | Derate | Coal | 3 | 2013 | 8 | 1.95 | 0.11118 | 45.6967 | 23.4342 | 23
BR3 | PD | 103 | 310 | 2013-08-28 22:00 | 2013-08-29 03:50 | 360 | 456 | 411 | Pulverizer mills | 3-2 Mill riffle inspection 6485947 | Brown | Derate | Coal | 3 | 2013 | 8 | 5.8333 | 1.2281 | 504.7368 | 86.5263 | 87
BR3 | D1 | 104 | 1470 | 2013-08-29 13:53 | 2013-08-30 22:20 | 180 | 456 | 411 | Induced draft fan motors and drives | 3-2 ID Fan trip. Expansion joint failure | Brown | Derate | Coal | 3 | 2013 | 8 | 32.45 | 19.6408 | 8072.3645 | 248.7632 | 249
BR3 | U2 | 105 | 1512 | 2013-08-30 22:20 | 2013-09-01 22:23 | 0 | 456 | 411 | Flue gas expansion joints | Replace 3-2 ID Fan Expansion joint & 3-1 BCWP | Brown | Outage | Coal | 3 | 2013 | 8 | 48.05 | 48.05 | 19748.55 | 411 | 411
BR3 | PD | 106 | 310 | 2013-09-02 22:05 | 2013-09-02 22:50 | 350 | 456 | 411 | Pulverizer mills | 3-2 mill riffle inspection | Brown | Derate | Coal | 3 | 2013 | 9 | 0.75 | 0.17434 | 71.6546 | 95.5395 | 96
BR3 | D1 | 107 | 300 | 2013-09-02 22:50 | 2013-09-02 23:55 | 250 | 456 | 411 | Pulverizer motors and drives | 3-5 mill failed to start 6491823 | Brown | Derate | Coal | 3 | 2013 | 9 | 1.0833 | 0.4894 | 201.1436 | 185.6711 | 186
BR3 | PD | 108 | 310 | 2013-09-02 23:55 | 2013-09-03 01:00 | 350 | 456 | 411 | Pulverizer mills | 3-2 mill riffle inspection 6485947 | Brown | Derate | Coal | 3 | 2013 | 9 | 1.0833 | 0.25183 | 103.5011 | 95.5395 | 96
BR3 | PD | 109 | 310 | 2013-09-03 22:00 | 2013-09-04 01:41 | 350 | 456 | 411 | Pulverizer mills | 3-2 mill riffle inspection 6485947 | Brown | Derate | Coal | 3 | 2013 | 9 | 3.6833 | 0.85621 | 351.9037 | 95.5395 | 96
BR3 | D1 | 110 | 3408 | 2013-09-04 15:27 | 2013-09-04 15:34 | 310 | 456 | 411 | Feedwater pump drive - local controls | 3-2 BFP failed to start | Brown | Derate | Coal | 3 | 2013 | 9 | 0.11667 | 0.037354 | 15.3524 | 131.5921 | 132
BR3 | PD | 111 | 310 | 2013-09-04 22:00 | 2013-09-05 00:59 | 350 | 456 | 411 | Pulverizer mills | 3-2 mill riffle inspection 6485947 | Brown | Derate | Coal | 3 | 2013 | 9 | 2.9833 | 0.69349 | 285.0261 | 95.5395 | 96
BR3 | NC | 112 | 8700 | 2013-09-05 10:15 | 2013-09-05 19:15 | 0 | 456 | 411 | CEMS Certification and Recertification | Full load PM testing | Brown | Other | Coal | 3 | 2013 | 9 | 9 | 9 | 3699 | 411 | 411
BR3 | PD | 113 | 310 | 2013-09-05 22:00 | 2013-09-06 00:03 | 350 | 456 | 411 | Pulverizer mills | 3-2 mill riffle inspection 6485947 | Brown | Derate | Coal | 3 | 2013 | 9 | 2.05 | 0.47654 | 195.8559 | 95.5395 | 96
BR3 | PD | 114 | 310 | 2013-09-06 00:03 | 2013-09-06 01:36 | 350 | 456 | 411 | Pulverizer mills | 3-3 mill roll replacement 6491820 | Brown | Derate | Coal | 3 | 2013 | 9 | 1.55 | 0.36031 | 148.0862 | 95.5395 | 96
BR3 | PD | 115 | 3410 | 2013-09-06 01:36 | 2013-09-07 03:00 | 310 | 456 | 411 | Feedwater pump | 3-2 BFP bearings inspections 6492556 | Brown | Derate | Coal | 3 | 2013 | 9 | 25.4 | 8.1325 | 3342.4395 | 131.5921 | 132
BR3 | D1 | 116 | 3410 | 2013-09-09 15:30 | 2013-09-24 08:44 | 440 | 456 | 411 | Feedwater pump | 3-2 BFP excessive vibration | Brown | Derate | Coal | 3 | 2013 | 9 | 353.2333 | 12.3942 | 5093.9965 | 14.4211 | 14
BR3 | D1 | 117 | 250 | 2013-09-24 08:44 | 2013-09-24 09:27 | 350 | 456 | 411 | Pulverizer feeders | 3-4 feeder controls erratic 6497316 | Brown | Derate | Coal | 3 | 2013 | 9 | 0.71667 | 0.16659 | 68.47 | 95.5395 | 96
BR3 | D1 | 118 | 3410 | 2013-09-24 09:27 | 2013-09-24 18:54 | 440 | 456 | 411 | Feedwater pump | 3-2 BFP excessive vibration | Brown | Derate | Coal | 3 | 2013 | 9 | 9.45 | 0.33158 | 136.2789 | 14.4211 | 14
BR3 | D1 | 119 | 3410 | 2013-09-24 18:54 | 2013-09-24 21:46 | 370 | 456 | 411 | Feedwater pump | 3-2 BFP excessive vibration | Brown | Derate | Coal | 3 | 2013 | 9 | 2.8667 | 0.54064 | 222.2044 | 77.5132 | 78
BR3 | D1 | 120 | 3410 | 2013-09-24 21:46 | 2013-10-01 | 310 | 456 | 411 | Feedwater pump | 3-2 BFP out of service due to excessive vibration | Brown | Derate | Coal | 3 | 2013 | 9 | 146.2333 | 46.8203 | 19243.1522 | 131.5921 | 132
BR3 | D1 | 121 | 3410 | 2013-10-01 | 2013-10-12 11:14 | 310 | 456 | 411 | Feedwater pump | 3-2 BFP out of service due to excessive vibration | Brown | Derate | Coal | 3 | 2013 | 10 | 275.2333 | 88.123 | 36218.5338 | 131.5921 | 132
BR3 | PO | 122 | 360 | 2013-10-12 11:14 | 2013-10-21 21:41 | 0 | 456 | 411 | Burners | Replace coal burners 6493752 | Brown | Other | Coal | 3 | 2013 | 10 | 226.45 | 226.45 | 93070.95 | 411 | 411
BR3 | D1 | 123 | 3410 | 2013-10-21 21:41 | 2013-10-22 17:42 | 310 | 456 | 411 | Feedwater pump | 3-2 BFP out of service due to excessive vibration 6493703 | Brown | Derate | Coal | 3 | 2013 | 10 | 20.0167 | 6.4088 | 2634.0353 | 131.5921 | 132
BR3 | U1 | 124 | 3620 | 2013-10-22 17:42 | 2013-10-22 20:43 | 0 | 456 | 411 | Main transformer | GSU high temperature indication 6505727 | Brown | Outage | Coal | 3 | 2013 | 10 | 3.0167 | 3.0167 | 1239.85 | 411 | 411
BR3 | D1 | 125 | 3410 | 2013-10-22 20:43 | 2013-10-29 | 310 | 456 | 411 | Feedwater pump | 3-2 BFP out of service due to excessive vibration | Brown | Derate | Coal | 3 | 2013 | 10 | 147.2833 | 47.1565 | 19381.3239 | 131.5921 | 132
BR3 | NC | 126 | 8700 | 2013-10-29 | 2013-10-30 03:45 | 0 | 456 | 411 | CEMS Certification and Recertification | Low load RATA testing | Brown | Other | Coal | 3 | 2013 | 10 | 27.75 | 27.75 | 11405.25 | 411 | 411
BR3 | D1 | 127 | 3410 | 2013-10-30 03:45 | 2013-11-01 08:45 | 310 | 456 | 411 | Feedwater pump | 3-2 BFP out of service due to excessive vibration | Brown | Derate | Coal | 3 | 2013 | 10 | 53 | 16.9693 | 6974.3816 | 131.5921 | 132
BR3 | PD | 128 | 8700 | 2013-11-01 08:45 | 2013-11-01 21:02 | 430 | 456 | 411 | CEMS Certification and Recertification | High load RATA testing 6508515 | Brown | Derate | Coal | 3 | 2013 | 11 | 12.2833 | 0.70037 | 287.8502 | 23.4342 | 23
BR3 | D1 | 129 | 3502 | 2013-11-06 16:23 | 2013-11-06 17:10 | 435 | 456 | 411 | Heater level control | 3G-1 HP heater level controller erratic 6510138 | Brown | Derate | Coal | 3 | 2013 | 11 | 0.78333 | 0.036075 | 14.8266 | 18.9276 | 19
BR3 | PD | 130 | 310 | 2013-11-11 10:50 | 2013-11-11 14:20 | 355 | 456 | 411 | Pulverizer mills | 3-1 mill exhauster bearing vibration 6511418 | Brown | Derate | Coal | 3 | 2013 | 11 | 3.5 | 0.77522 | 318.6151 | 91.0329 | 91
BR3 | PD | 131 | 310 | 2013-11-11 14:48 | 2013-11-11 16:45 | 355 | 456 | 411 | Pulverizer mills | 3-1 mill exhauster bearing vibration 6511418 | Brown | Derate | Coal | 3 | 2013 | 11 | 1.95 | 0.43191 | 177.5141 | 91.0329 | 91
BR3 | U1 | 132 | 9910 | 2013-11-12 16:50 | 2013-11-12 17:18 | 0 | 456 | 411 | Maintenance personnel error | Unit tripped while investigating problem with vibration probes | Brown | Outage | Coal | 3 | 2013 | 11 | 0.46667 | 0.46667 | 191.8 | 411 | 411
BR3 | MO | 134 | 740 | 2013-12-01 13:29 | 2013-12-04 20:30 | 0 | 456 | 411 | Boiler recirculation pumps | Replace 3-3 BCWP 6516186 | Brown | Maintenance | Coal | 3 | 2013 | 12 | 79.0167 | 79.0167 | 32475.85 | 411 | 411
BR3 | U1 | 135 | 1000 | 2013-12-04 20:30 | 2013-12-06 01:33 | 0 | 456 | 411 | Waterwall (Furnace wall) A | Waterwall tube leak 6518081 | Brown | Outage | Coal | 3 | 2013 | 12 | 29.05 | 29.05 | 11939.55 | 411 | 411
BR3 | PD | 136 | 310 | 2013-12-09 22:30 | 2013-12-10 03:24 | 360 | 456 | 411 | Pulverizer mills | Adjust 3-3 mill riffle elements, change oil in 3-2 mill motor brg. 6485947 | Brown | Derate | Coal | 3 | 2013 | 12 | 4.9 | 1.0316 | 423.9789 | 86.5263 | 87
BR3 | PD | 137 | 310 | 2013-12-10 22:55 | 2013-12-11 02:33 | 360 | 456 | 411 | Pulverizer mills | Adjust 3-3 mill riffle elements 6485947 | Brown | Derate | Coal | 3 | 2013 | 12 | 3.6333 | 0.76491 | 314.3789 | 86.5263 | 87
BR3 | PD | 138 | 310 | 2013-12-11 22:05 | 2013-12-12 02:07 | 360 | 456 | 411 | Pulverizer mills | Adjust 3-3 mill riffle elements 6485947 | Brown | Derate | Coal | 3 | 2013 | 12 | 4.0333 | 0.84912 | 348.9895 | 86.5263 | 87
BR3 | PD | 139 | 310 | 2013-12-12 22:00 | 2013-12-13 01:30 | 360 | 456 | 411 | Pulverizer mills | Adjust 3-3 mill riffle elements 6485947 | Brown | Derate | Coal | 3 | 2013 | 12 | 3.5 | 0.73684 | 302.8421 | 86.5263 | 87
BR3 | PD | 140 | 300 | 2013-12-13 22:00 | 2013-12-14 05:22 | 360 | 456 | 411 | Pulverizer motors and drives | Replace 3-2 mill motor 6520265 | Brown | Derate | Coal | 3 | 2013 | 12 | 7.3667 | 1.5509 | 637.4105 | 86.5263 | 87
BR3 | PD | 141 | 310 | 2013-12-16 21:54 | 2013-12-17 00:43 | 350 | 456 | 411 | Pulverizer mills | Adjust 3-3 mill riffle elements 6485947 | Brown | Derate | Coal | 3 | 2013 | 12 | 2.8167 | 0.65475 | 269.1029 | 95.5395 | 96
BR3 | PD | 142 | 310 | 2013-12-17 22:00 | 2013-12-18 03:00 | 350 | 456 | 411 | Pulverizer mills | Adjust 3-5 mill riffle elements 6485947 | Brown | Derate | Coal | 3 | 2013 | 12 | 5 | 1.1623 | 477.6974 | 95.5395 | 96
BR3 | PD | 143 | 310 | 2013-12-18 21:45 | 2013-12-19 01:53 | 350 | 456 | 411 | Pulverizer mills | Adjust 3-5 mill riffle elements 6485947 | Brown | Derate | Coal | 3 | 2013 | 12 | 4.1333 | 0.96082 | 394.8965 | 95.5395 | 96
BR3 | PD | 144 | 310 | 2013-12-19 21:35 | 2013-12-20 00:36 | 350 | 456 | 411 | Pulverizer mills | Adjust 3-5 mill riffle elements 6485947 | Brown | Derate | Coal | 3 | 2013 | 12 | 3.0167 | 0.70124 | 288.2107 | 95.5395 | 96
BR3 | U1 | 146 | 1000 | 2013-12-22 11:46 | 2013-12-23 19:35 | 0 | 456 | 411 | Waterwall (Furnace wall) A | Waterwall tube leaks on C and D corners 6524142 | Brown | Outage | Coal | 3 | 2013 | 12 | 31.8167 | 31.8167 | 13076.65 | 411 | 411
BR3 | PD | 1 | 310 | 2014-01-08 22:33 | 2014-01-09 01:15 | 350 | 456 | 411 | Pulverizer mills | Adjust 3-4 mill riffle elements - 6485947 | Brown | Derate | Coal | 3 | 2014 | 1 | 2.7 | 0.62763 | 257.9566 | 95.5395 | 96
BR3 | PD | 2 | 310 | 2014-01-09 21:20 | 2014-01-10 00:33 | 350 | 456 | 411 | Pulverizer mills | Adjust 3-4 mill riffle elements 6485947 | Brown | Derate | Coal | 3 | 2014 | 1 | 3.2167 | 0.74773 | 307.3186 | 95.5395 | 96
BR3 | MO | 4 | 740 | 2014-01-11 10:37 | 2014-01-12 04:08 | 0 | 456 | 411 | Boiler recirculation pumps | Replace 3-1 BCWP - 6524483 | Brown | Maintenance | Coal | 3 | 2014 | 1 | 17.5167 | 17.5167 | 7199.35 | 411 | 411
BR3 | PD | 5 | 310 | 2014-01-13 22:00 | 2014-01-14 00:29 | 350 | 456 | 411 | Pulverizer mills | Adjust 3-4 mill riffle elements 6485947 | Brown | Derate | Coal | 3 | 2014 | 1 | 2.4833 | 0.57727 | 237.2564 | 95.5395 | 96
BR3 | PD | 6 | 310 | 2014-01-14 21:35 | 2014-01-15 00:37 | 350 | 456 | 411 | Pulverizer mills | Adjust 3-4 mill riffle elements 6485947 | Brown | Derate | Coal | 3 | 2014 | 1 | 3.0333 | 0.70512 | 289.8031 | 95.5395 | 96
BR3 | PD | 7 | 310 | 2014-01-15 21:57 | 2014-01-16 00:40 | 350 | 456 | 411 | Pulverizer mills | Adjust 3-4 mill riffle elements 6485947 | Brown | Derate | Coal | 3 | 2014 | 1 | 2.7167 | 0.63151 | 259.5489 | 95.5395 | 96
BR3 | U1 | 8 | 339 | 2014-01-30 03:57 | 2014-02-01 16:05 | 0 | 456 | 411 | Pulverizer System Puff | 3-5 Mill puff causing D corner burner damage and associated boiler tube leak. | Brown | Outage | Coal | 3 | 2014 | 1 | 60.1333 | 60.1333 | 24714.8 | 411 | 411
BR3 | PD | 9 | 3412 | 2014-02-04 22:00 | 2014-02-05 01:52 | 310 | 456 | 411 | Feedwater pump drive - steam turbine | Collecting 3-2 BFP vibration data | Brown | Derate | Coal | 3 | 2014 | 2 | 3.8667 | 1.238 | 508.8228 | 131.5921 | 132
BR3 | D1 | 10 | 3414 | 2014-02-21 22:08 | 2014-02-22 23:58 | 305 | 456 | 411 | Feedwater pump local controls | 3-2 BFPT LP governor valve indication 6545010 | Brown | Derate | Coal | 3 | 2014 | 2 | 25.8333 | 8.5545 | 3515.8827 | 136.0987 | 136
BR3 | NC | 11 | 1710 | 2014-02-24 22:00 | 2014-02-25 02:05 | 0 | 456 | 411 | Combustion/steam condition controls (report local controls --- burners | Combustion tuning 6544234 | Brown | Other | Coal | 3 | 2014 | 2 | 4.0833 | 4.0833 | 1678.25 | 411 | 411
BR3 | D1 | 12 | 3414 | 2014-02-25 05:51 | 2014-02-25 07:39 | 300 | 456 | 411 | Feedwater pump local controls | 3-2 BFP LP gov. servo problems 6546920 | Brown | Derate | Coal | 3 | 2014 | 2 | 1.8 | 0.61579 | 253.0895 | 140.6053 | 141
BR3 | NC | 13 | 9656 | 2014-03-11 11:42 | 2014-03-11 13:51 | 0 | 456 | 411 | Other stack or exhaust emissions testing - fossil | Low load RATA testing | Brown | Other | Coal | 3 | 2014 | 3 | 2.15 | 2.15 | 883.65 | 411 | 411
BR3 | D1 | 14 | 310 | 2014-03-11 13:51 | 2014-03-11 15:36 | 350 | 456 | 411 | Pulverizer mills | 3-1 mill broken spring bolt 6550819 | Brown | Derate | Coal | 3 | 2014 | 3 | 1.75 | 0.4068 | 167.1941 | 95.5395 | 96
BR3 | NC | 15 | 9656 | 2014-03-11 15:36 | 2014-03-11 16:08 | 0 | 456 | 411 | Other stack or exhaust emissions testing - fossil | Low load RATA testing | Brown | Other | Coal | 3 | 2014 | 3 | 0.53333 | 0.53333 | 219.2 | 411 | 411
BR3 | NC | 16 | 9656 | 2014-03-12 08:45 | 2014-03-12 20:38 | 0 | 456 | 411 | Other stack or exhaust emissions testing - fossil | RATA testing at 425 mw. | Brown | Other | Coal | 3 | 2014 | 3 | 11.8833 | 11.8833 | 4884.05 | 411 | 411
BR3 | NC | 17 | 9656 | 2014-03-13 12:30 | 2014-03-13 17:00 | 0 | 456 | 411 | Other stack or exhaust emissions testing - fossil | RATA testing at 425 mw. | Brown | Other | Coal | 3 | 2014 | 3 | 4.5 | 4.5 | 1849.5 | 411 | 411
BR3 | D1 | 18 | 740 | 2014-03-17 14:15 | 2014-03-18 | 430 | 456 | 411 | Boiler recirculation pumps | 3-1 BCWP out of service | Brown | Derate | Coal | 3 | 2014 | 3 | 9.75 | 0.55592 | 228.4836 | 23.4342 | 23
BR3 | D1 | 19 | 740 | 2014-03-19 10:13 | 2014-03-19 10:32 | 57 | 456 | 411 | Boiler recirculation pumps | Boiler trip due to BCWP differential pressure | Brown | Derate | Coal | 3 | 2014 | 3 | 0.31667 | 0.27708 | 113.8812 | 359.625 | 360
BR3 | U1 | 20 | 740 | 2014-03-19 10:32 | 2014-03-19 12:29 | 0 | 456 | 411 | Boiler recirculation pumps | Boiler trip due to BCWP differential pressure | Brown | Outage | Coal | 3 | 2014 | 3 | 1.95 | 1.95 | 801.45 | 411 | 411
BR3 | D1 | 21 | 310 | 2014-03-19 21:47 | 2014-03-19 23:04 | 350 | 456 | 411 | Pulverizer mills | 3-5 mill explosion | Brown | Derate | Coal | 3 | 2014 | 3 | 1.2833 | 0.29832 | 122.609 | 95.5395 | 96
BR3 | U1 | 22 | 310 | 2014-03-19 23:04 | 2014-03-21 06:05 | 0 | 456 | 411 | Pulverizer mills | 3-5 mill explosion, damage inspection and repair | Brown | Outage | Coal | 3 | 2014 | 3 | 31.0167 | 31.0167 | 12747.85 | 411 | 411
BR3 | D1 | 23 | 310 | 2014-03-21 11:20 | 2014-03-21 16:28 | 340 | 456 | 411 | Pulverizer mills | 3-5 mill post explosion calibrations and inspections | Brown | Derate | Coal | 3 | 2014 | 3 | 5.1333 | 1.3058 | 536.7035 | 104.5526 | 105
BR3 | D1 | 24 | 310 | 2014-03-21 16:28 | 2014-03-24 10:30 | 420 | 456 | 411 | Pulverizer mills | High exhauster to furnance pressure due to 3-5D burner out of service. | Brown | Derate | Coal | 3 | 2014 | 3 | 66.0333 | 5.2132 | 2142.6079 | 32.4474 | 32
BR3 | D1 | 25 | 310 | 2014-03-24 10:30 | 2014-03-24 10:43 | 335 | 456 | 411 | Pulverizer mills | 3-3 mill exhauster bearing high vibration | Brown | Derate | Coal | 3 | 2014 | 3 | 0.21667 | 0.057493 | 23.6295 | 109.0592 | 109
BR3 | D1 | 26 | 310 | 2014-03-24 10:43 | 2014-03-25 07:04 | 420 | 456 | 411 | Pulverizer mills | High exhauster to furnance pressure due to 3-5D burner out of service. | Brown | Derate | Coal | 3 | 2014 | 3 | 20.35 | 1.6066 | 660.3039 | 32.4474 | 32
BR3 | D1 | 27 | 350 | 2014-03-25 07:04 | 2014-03-25 11:00 | 335 | 456 | 411 | Pulverized fuel and air piping (from pulverizer to wind box) | 3-5A burner line coal leak | Brown | Derate | Coal | 3 | 2014 | 3 | 3.9333 | 1.0437 | 428.9662 | 109.0592 | 109
BR3 | D1 | 28 | 350 | 2014-03-25 11:00 | 2014-03-25 12:06 | 345 | 456 | 411 | Pulverized fuel and air piping (from pulverizer to wind box) | 3-5A burner line coal leak | Brown | Derate | Coal | 3 | 2014 | 3 | 1.1 | 0.26776 | 110.0507 | 100.0461 | 100
BR3 | D1 | 29 | 310 | 2014-03-25 12:06 | 2014-03-28 23:33 | 420 | 456 | 411 | Pulverizer mills | High exhauster to furnance pressure due to 3-5D burner out of service. | Brown | Derate | Coal | 3 | 2014 | 3 | 83.45 | 6.5882 | 2707.7329 | 32.4474 | 32
BR3 | PO | 30 | 1801 | 2014-03-28 23:33 | 2014-04-28 18:30 | 0 | 456 | 411 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Planned spring outage Installed new terminal tubes & assemblies in radiant reheat | Brown | Other | Coal | 3 | 2014 | 3 | 738.95 | 738.95 | 303708.45 | 411 | 411
BR3 | SF | 31 | 1000 | 2014-04-28 18:30 | 2014-04-30 05:45 | 0 | 456 | 411 | Waterwall (Furnace wall) A | Lower waterwall tube leak found during startup | Brown | Outage | Coal | 3 | 2014 | 4 | 35.25 | 35.25 | 14487.75 | 411 | 411
BR3 | SF | 32 | 1090 | 2014-04-30 05:45 | 2014-05-01 01:28 | 0 | 456 | 411 | Other boiler tube leaks | Sample line from steam drum leaking 6566287 | Brown | Outage | Coal | 3 | 2014 | 4 | 19.7167 | 19.7167 | 8103.55 | 411 | 411
BR3 | D1 | 33 | 3352 | 2014-05-01 09:56 | 2014-05-01 11:10 | 250 | 456 | 411 | Feedwater chemistry (not specific to condenser | High silica from startup | Brown | Derate | Coal | 3 | 2014 | 5 | 1.2333 | 0.55716 | 228.9943 | 185.6711 | 186
BR3 | D1 | 34 | 3352 | 2014-05-01 11:10 | 2014-05-01 13:55 | 330 | 456 | 411 | Feedwater chemistry (not specific to condenser | High silica from startup | Brown | Derate | Coal | 3 | 2014 | 5 | 2.75 | 0.75987 | 312.3059 | 113.5658 | 114
BR3 | D1 | 35 | 310 | 2014-05-01 13:55 | 2014-05-01 15:30 | 365 | 456 | 411 | Pulverizer mills | Setting mill rolls | Brown | Derate | Coal | 3 | 2014 | 5 | 1.5833 | 0.31597 | 129.8646 | 82.0197 | 82
BR3 | D1 | 36 | 3352 | 2014-05-01 15:30 | 2014-05-01 18:11 | 430 | 456 | 411 | Feedwater chemistry (not specific to condenser | High silica from startup | Brown | Derate | Coal | 3 | 2014 | 5 | 2.6833 | 0.153 | 62.8818 | 23.4342 | 23
BR3 | D1 | 37 | 800 | 2014-05-02 04:00 | 2014-05-02 04:15 | 180 | 456 | 411 | Drums and drum internals (single drum only) | Possible leak on SW mud drum door 6566407 | Brown | Derate | Coal | 3 | 2014 | 5 | 0.25 | 0.15132 | 62.1908 | 248.7632 | 249
BR3 | PD | 38 | 510 | 2014-05-13 19:11 | 2014-05-13 23:00 | 389 | 456 | 411 | Main steam relief/safety valves off superheater | Set boiler safety valves | Brown | Derate | Coal | 3 | 2014 | 5 | 3.8167 | 0.56078 | 230.4815 | 60.3882 | 60
BR3 | MO | 39 | 740 | 2014-05-16 23:43 | 2014-05-18 02:29 | 0 | 456 | 411 | Boiler recirculation pumps | Clean HWRC pump strainers 6567942 | Brown | Maintenance | Coal | 3 | 2014 | 5 | 26.7667 | 26.7667 | 11001.1 | 411 | 411
BR3 | D1 | 40 | 3414 | 2014-05-22 15:30 | 2014-05-22 17:00 | 310 | 456 | 411 | Feedwater pump local controls | 3-1 BFP EHC low pressure governor oil leak 6571636 | Brown | Derate | Coal | 3 | 2014 | 5 | 1.5 | 0.48026 | 197.3882 | 131.5921 | 132
BR3 | D1 | 41 | 3414 | 2014-05-22 17:00 | 2014-05-22 21:31 | 285 | 456 | 411 | Feedwater pump local controls | 3-1 BFP EHC low pressure governor oil leak 6571636 | Brown | Derate | Coal | 3 | 2014 | 5 | 4.5167 | 1.6937 | 696.1312 | 154.125 | 154
BR3 | PD | 42 | 3410 | 2014-05-28 22:00 | 2014-05-29 01:17 | 310 | 456 | 411 | Feedwater pump | Inspect 3-2 BFP coupling 6568444 | Brown | Derate | Coal | 3 | 2014 | 5 | 3.2833 | 1.0512 | 432.0607 | 131.5921 | 132
BR3 | PD | 43 | 3410 | 2014-05-29 22:00 | 2014-05-30 06:12 | 310 | 456 | 411 | Feedwater pump | Inspect 3-2 BFP coupling 6568444 | Brown | Derate | Coal | 3 | 2014 | 5 | 8.2 | 2.6254 | 1079.0553 | 131.5921 | 132
BR3 | PD | 44 | 1400 | 2014-06-02 23:00 | 2014-06-03 02:35 | 300 | 456 | 411 | Forced draft fans | Inspect 3-1 FD Fan coupling 6576497 | Brown | Derate | Coal | 3 | 2014 | 6 | 3.5833 | 1.2259 | 503.8355 | 140.6053 | 141
BR3 | D1 | 45 | 3440 | 2014-06-04 13:15 | 2014-06-07 01:56 | 425 | 456 | 411 | High pressure heater tube leaks | 3-F2 HP heater leak | Brown | Derate | Coal | 3 | 2014 | 6 | 60.6833 | 4.1254 | 1695.5402 | 27.9408 | 28
BR3 | MO | 46 | 3440 | 2014-06-07 01:56 | 2014-06-10 01:55 | 0 | 456 | 411 | High pressure heater tube leaks | Repair 3-F2 HP heater tube leak 6576933 | Brown | Maintenance | Coal | 3 | 2014 | 6 | 71.9833 | 71.9833 | 29585.15 | 411 | 411
BR3 | U1 | 47 | 4860 | 2014-06-10 16:09 | 2014-06-11 04:21 | 0 | 456 | 411 | Generator Neutral Grounding Equipment | Loose wire on ground neutral transformer 6579166 | Brown | Outage | Coal | 3 | 2014 | 6 | 12.2 | 12.2 | 5014.2 | 411 | 411
BR3 | U1 | 48 | 3621 | 2014-06-11 08:52 | 2014-06-11 23:07 | 0 | 456 | 411 | Unit auxiliaries transformer | "A" Auxiliary Transformer A phase bushing failure 6579361 | Brown | Outage | Coal | 3 | 2014 | 6 | 14.25 | 14.25 | 5856.75 | 411 | 411
BR3 | D1 | 49 | 3352 | 2014-06-12 05:50 | 2014-06-12 07:16 | 425 | 456 | 411 | Feedwater chemistry (not specific to condenser | High silica after unit startup | Brown | Derate | Coal | 3 | 2014 | 6 | 1.4333 | 0.097442 | 40.0485 | 27.9408 | 28
BR3 | U1 | 50 | 1000 | 2014-06-14 22:56 | 2014-06-16 08:10 | 0 | 456 | 411 | Waterwall (Furnace wall) A | Waterwall tube leak at C corner upper burner level 6579764 | Brown | Outage | Coal | 3 | 2014 | 6 | 33.2333 | 33.2333 | 13658.9 | 411 | 411
BR3 | D1 | 51 | 9910 | 2014-07-01 11:25 | 2014-07-01 12:10 | 55 | 456 | 411 | Maintenance personnel error | Transmission employee tripped West Cliff substation feed to unit 3 6585768 | Brown | Derate | Coal | 3 | 2014 | 7 | 0.75 | 0.65954 | 271.0707 | 361.4276 | 361
BR3 | U1 | 52 | 9910 | 2014-07-01 12:10 | 2014-07-01 13:20 | 0 | 456 | 411 | Maintenance personnel error | Transmission employee tripped West Cliff substation feed to unit 3 6585768 | Brown | Outage | Coal | 3 | 2014 | 7 | 1.1667 | 1.1667 | 479.5 | 411 | 411
BR3 | U1 | 53 | 3245 | 2014-07-17 13:11 | 2014-07-22 15:50 | 0 | 456 | 411 | Other cooling tower problems | 3-2 Cooloing tower cell damage 6589856 | Brown | Outage | Coal | 3 | 2014 | 7 | 122.65 | 122.65 | 50409.15 | 411 | 411
BR3 | SF | 54 | 3210 | 2014-07-22 15:50 | 2014-07-22 20:41 | 0 | 456 | 411 | Circulating water pumps | 3-2 CWP discharge valve not fully open. 3-1 CWP unavailable 6591462 | Brown | Outage | Coal | 3 | 2014 | 7 | 4.85 | 4.85 | 1993.35 | 411 | 411
BR3 | D1 | 55 | 3412 | 2014-07-23 00:07 | 2014-07-23 03:35 | 300 | 456 | 411 | Feedwater pump drive - steam turbine | 3-1 BFP turbine bearing replacement 6590040 | Brown | Derate | Coal | 3 | 2014 | 7 | 3.4667 | 1.186 | 487.4316 | 140.6053 | 141
BR3 | D1 | 56 | 3412 | 2014-07-23 03:35 | 2014-07-24 10:30 | 280 | 456 | 411 | Feedwater pump drive - steam turbine | 3-1 BFP turbine bearing replacement 6590040 | Brown | Derate | Coal | 3 | 2014 | 7 | 30.9167 | 11.9327 | 4904.3596 | 158.6316 | 159
BR3 | D1 | 57 | 3410 | 2014-07-26 16:55 | 2014-07-27 14:25 | 300 | 456 | 411 | Feedwater pump | 3-1 BFP IB pump bearing high temperature | Brown | Derate | Coal | 3 | 2014 | 7 | 21.5 | 7.3553 | 3023.0132 | 140.6053 | 141
BR3 | PD | 58 | 3415 | 2014-08-05 02:20 | 2014-08-05 06:40 | 300 | 456 | 411 | Feedwater pump/drive lube oil system | Clean 3-1 BFP lube oil cuno filters 6595168 | Brown | Derate | Coal | 3 | 2014 | 8 | 4.3333 | 1.4825 | 609.2895 | 140.6053 | 141
BR3 | PD | 59 | 3412 | 2014-09-02 22:00 | 2014-09-03 04:38 | 300 | 456 | 411 | Feedwater pump drive - steam turbine | 3-2 BFP vibration check | Brown | Derate | Coal | 3 | 2014 | 9 | 6.6333 | 2.2693 | 932.6816 | 140.6053 | 141
BR3 | NC | 60 | 3412 | 2014-09-11 11:50 | 2014-09-11 13:45 | 0 | 456 | 411 | Feedwater pump drive - steam turbine | Collecting vibration data for 3-2 BFP | Brown | Other | Coal | 3 | 2014 | 9 | 1.9167 | 1.9167 | 787.75 | 411 | 411
BR3 | MO | 62 | 1500 | 2014-09-15 06:40 | 2014-09-15 16:18 | 0 | 456 | 411 | Air heater soot blowers | Inspect AH sootblowers | Brown | Maintenance | Coal | 3 | 2014 | 9 | 9.6333 | 9.6333 | 3959.3 | 411 | 411
BR3 | U1 | 64 | 4281 | 2014-09-17 13:05 | 2014-09-20 13:36 | 0 | 456 | 411 | Lube oil coolers A | 3-1 Turbine Oil cooler leak. 6606790 | Brown | Outage | Coal | 3 | 2014 | 9 | 72.5167 | 72.5167 | 29804.35 | 411 | 411
BR3 | MO | 66 | 3621 | 2014-10-09 21:59 | 2014-10-11 17:30 | 0 | 456 | 411 | Unit auxiliaries transformer | Replace 3A Aux. transformer buss 6598348 | Brown | Maintenance | Coal | 3 | 2014 | 10 | 43.5167 | 43.5167 | 17885.35 | 411 | 411
BR3 | D1 | 69 | 3440 | 2014-10-21 19:00 | 2014-10-22 07:05 | 400 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP heater leak | Brown | Derate | Coal | 3 | 2014 | 10 | 12.0833 | 1.4839 | 609.8904 | 50.4737 | 50
BR3 | D1 | 70 | 3440 | 2014-10-22 07:05 | 2014-10-22 08:29 | 405 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP heater leak 6617285 | Brown | Derate | Coal | 3 | 2014 | 10 | 1.4 | 0.15658 | 64.3539 | 45.9671 | 46
BR3 | D1 | 71 | 3440 | 2014-10-22 08:29 | 2014-10-23 12:30 | 430 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP heater leak and full load RATA testing 6617059 | Brown | Derate | Coal | 3 | 2014 | 10 | 28.0167 | 1.5974 | 656.5485 | 23.4342 | 23
BR3 | PD | 72 | 8700 | 2014-10-23 12:30 | 2014-10-23 16:10 | 225 | 456 | 411 | CEMS Certification and Recertification | Low load RATA testing 6617059 | Brown | Derate | Coal | 3 | 2014 | 10 | 3.6667 | 1.8575 | 763.4145 | 208.2039 | 208
BR3 | D1 | 73 | 3440 | 2014-10-23 16:10 | 2014-10-24 22:05 | 430 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP heater leak 6617285 | Brown | Derate | Coal | 3 | 2014 | 10 | 29.9167 | 1.7058 | 701.0735 | 23.4342 | 23
BR3 | MO | 74 | 3440 | 2014-10-24 22:05 | 2014-10-27 13:45 | 0 | 456 | 411 | High pressure heater tube leaks | Repair 3F-2 HP heater leak 6617285 | Brown | Maintenance | Coal | 3 | 2014 | 10 | 63.6667 | 63.6667 | 26167 | 411 | 411
BR3 | D1 | 76 | 3502 | 2014-10-31 06:53 | 2014-10-31 08:00 | 400 | 456 | 411 | Heater level control | 3F-2 heater level controller replacement 6620029 | Brown | Derate | Coal | 3 | 2014 | 10 | 1.1167 | 0.13713 | 56.3623 | 50.4737 | 50
BR3 | U1 | 77 | 1070 | 2014-11-12 17:24 | 2014-11-17 04:41 | 0 | 456 | 411 | Second reheater B | Reheat tube leak 6622981 | Brown | Outage | Coal | 3 | 2014 | 11 | 107.2833 | 107.2833 | 44093.45 | 411 | 411
BR3 | MO | 78 | 8816 | 2014-12-13 02:10 | 2014-12-20 04:31 | 0 | 456 | 411 | SCR NOx Plugging | Clean and inspect SCR | Brown | Maintenance | Coal | 3 | 2014 | 12 | 170.35 | 170.35 | 70013.85 | 411 | 411
BR3 | D1 | 1 | 1710 | 2015-01-02 10:55 | 2015-01-02 12:22 | 57 | 456 | 411 | Combustion/steam condition controls (report local controls --- burners | Boiler trip while swapping out mills to empty coal bunkers | Brown | Derate | Coal | 3 | 2015 | 1 | 1.45 | 1.2688 | 521.4563 | 359.625 | 360
BR3 | PD | 2 | 335 | 2015-01-05 23:00 | 2015-01-06 01:45 | 350 | 456 | 411 | Pulverizer lube oil system | Repair 3-4 mill oil filtration valve 6640989 | Brown | Derate | Coal | 3 | 2015 | 1 | 2.75 | 0.63925 | 262.7336 | 95.5395 | 96
BR3 | NC | 3 | 8700 | 2015-01-13 21:45 | 2015-01-14 01:47 | 0 | 456 | 411 | CEMS Certification and Recertification | Low load RATA testing | Brown | Other | Coal | 3 | 2015 | 1 | 4.0333 | 4.0333 | 1657.7 | 411 | 411
BR3 | U1 | 5 | 4609 | 2015-01-22 19:00 | 2015-01-22 22:02 | 0 | 456 | 411 | Other exciter problems | Exciter cooler piping leak | Brown | Outage | Coal | 3 | 2015 | 1 | 3.0333 | 3.0333 | 1246.7 | 411 | 411
BR3 | SF | 7 | 500 | 2015-01-25 21:08 | 2015-01-26 18:20 | 0 | 456 | 411 | Main steam piping up to turbine stop valves | Pin hole leak in main steam drain line prior to isolation valve. | Brown | Outage | Coal | 3 | 2015 | 1 | 21.2 | 21.2 | 8713.2 | 411 | 411
BR3 | D1 | 8 | 310 | 2015-02-05 07:48 | 2015-02-05 09:16 | 350 | 456 | 411 | Pulverizer mills | Water from 3-1 mil pyrite tank leaking back into mill | Brown | Derate | Coal | 3 | 2015 | 2 | 1.4667 | 0.34094 | 140.1246 | 95.5395 | 96
BR3 | D1 | 9 | 4560 | 2015-02-06 06:48 | 2015-02-06 07:45 | 325 | 456 | 411 | Generator vibration (excluding vibration due to failed bearing and other components) | #7 generator/exciter bearing vibration | Brown | Derate | Coal | 3 | 2015 | 2 | 0.95 | 0.27292 | 112.1687 | 118.0724 | 118
BR3 | D1 | 10 | 4560 | 2015-02-06 07:45 | 2015-02-06 09:08 | 380 | 456 | 411 | Generator vibration (excluding vibration due to failed bearing and other components) | #7 generator/exciter bearing vibration | Brown | Derate | Coal | 3 | 2015 | 2 | 1.3833 | 0.23056 | 94.7583 | 68.5 | 69
BR3 | U1 | 11 | 4560 | 2015-02-06 09:08 | 2015-02-06 19:03 | 0 | 456 | 411 | Generator vibration (excluding vibration due to failed bearing and other components) | #7 generator/exciter bearing vibration | Brown | Outage | Coal | 3 | 2015 | 2 | 9.9167 | 9.9167 | 4075.75 | 411 | 411
BR3 | U1 | 12 | 90 | 2015-02-20 13:34 | 2015-02-20 15:55 | 0 | 456 | 411 | Bunker fires | FR00Unit 3 coal bunker fires in 3-4 and partially in 3-5 bunker | Brown | Outage | Coal | 3 | 2015 | 2 | 2.35 | 2.35 | 965.85 | 411 | 411
BR3 | D1 | 13 | 9270 | 2015-02-20 22:16 | 2015-02-21 03:20 | 350 | 456 | 411 | Wet coal | FW00Wet Coal | Brown | Derate | Coal | 3 | 2015 | 2 | 5.0667 | 1.1778 | 484.0667 | 95.5395 | 96
BR3 | D1 | 14 | 340 | 2015-02-22 23:35 | 2015-02-23 00:54 | 360 | 456 | 411 | Other pulverizer problems | 3-5 Mill CO issues | Brown | Derate | Coal | 3 | 2015 | 2 | 1.3167 | 0.27719 | 113.9263 | 86.5263 | 87
BR3 | PD | 15 | 344 | 2015-02-24 22:00 | 2015-02-25 01:05 | 350 | 456 | 411 | Pulverizer inspection | Inspect 3-5 mill for cause of high CO readings | Brown | Derate | Coal | 3 | 2015 | 2 | 3.0833 | 0.71674 | 294.58 | 95.5395 | 96
BR3 | U1 | 16 | 500 | 2015-03-06 01:49 | 2015-03-07 03:19 | 0 | 456 | 411 | Main steam piping up to turbine stop valves | Leak in main steam drain line 6660146 | Brown | Outage | Coal | 3 | 2015 | 3 | 25.5 | 25.5 | 10480.5 | 411 | 411
BR3 | PO | 17 | 8812 | 2015-03-29 12:46 | 2015-04-20 07:19 | 0 | 456 | 411 | SCR NOxCatalyst | Replace SCR catalyst | Brown | Other | Coal | 3 | 2015 | 3 | 522.55 | 522.55 | 214768.05 | 411 | 411
BR3 | D1 | 18 | 3352 | 2015-04-20 15:19 | 2015-04-21 05:40 | 420 | 456 | 411 | Feedwater chemistry (not specific to condenser | High silica | Brown | Derate | Coal | 3 | 2015 | 4 | 14.35 | 1.1329 | 465.6197 | 32.4474 | 32
BR3 | PD | 19 | 3410 | 2015-04-24 23:00 | 2015-04-25 00:40 | 310 | 456 | 411 | Feedwater pump | F590Steam leak on low pressure steam chest to the 3-1BFP | Brown | Derate | Coal | 3 | 2015 | 4 | 1.6667 | 0.53363 | 219.3202 | 131.5921 | 132
BR3 | NC | 20 | 8812 | 2015-05-07 21:00 | 2015-05-07 23:24 | 0 | 456 | 411 | SCR NOxCatalyst | SCR ammonia injection tuning at 350 mw | Brown | Other | Coal | 3 | 2015 | 5 | 2.4 | 2.4 | 986.4 | 411 | 411
BR3 | NC | 21 | 8812 | 2015-05-07 23:24 | 2015-05-08 | 0 | 456 | 411 | SCR NOxCatalyst | SCR ammonia injection tuning at180 mw | Brown | Other | Coal | 3 | 2015 | 5 | 0.6 | 0.6 | 246.6 | 411 | 411
BR3 | U1 | 22 | 3211 | 2015-05-11 12:20 | 2015-05-11 13:06 | 0 | 456 | 411 | Circulating water pump motors | 3-2 CWP trip leading to turbine trip | Brown | Outage | Coal | 3 | 2015 | 5 | 0.76667 | 0.76667 | 315.1 | 411 | 411
BR3 | MO | 24 | 1090 | 2015-06-02 07:14 | 2015-06-02 14:30 | 0 | 456 | 411 | Other boiler tube leaks | Lower water wall tube leak above ash hopper | Brown | Maintenance | Coal | 3 | 2015 | 6 | 7.2667 | 7.2667 | 2986.6 | 411 | 411
BR3 | PD | 26 | 3415 | 2015-06-28 22:00 | 2015-06-29 02:15 | 300 | 456 | 411 | Feedwater pump/drive lube oil system | Repair oil leak on 3-1 BFP piping | Brown | Derate | Coal | 3 | 2015 | 6 | 4.25 | 1.4539 | 597.5724 | 140.6053 | 141
BR3 | D1 | 27 | 310 | 2015-06-29 02:15 | 2015-06-29 06:26 | 350 | 456 | 411 | Pulverizer mills | Repair oil leak on 3-3 mill | Brown | Derate | Coal | 3 | 2015 | 6 | 4.1833 | 0.97244 | 399.6735 | 95.5395 | 96
BR3 | PD | 28 | 3412 | 2015-06-29 22:00 | 2015-06-30 02:12 | 300 | 456 | 411 | Feedwater pump drive - steam turbine | Inspect 3-2 BFP circulating water lines | Brown | Derate | Coal | 3 | 2015 | 6 | 4.2 | 1.4368 | 590.5421 | 140.6053 | 141
BR3 | D1 | 29 | 3440 | 2015-06-30 09:41 | 2015-07-01 23:00 | 425 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP heater leak | Brown | Derate | Coal | 3 | 2015 | 6 | 37.3167 | 2.5369 | 1042.6571 | 27.9408 | 28
BR3 | PD | 30 | 8700 | 2015-07-01 23:00 | 2015-07-02 05:14 | 180 | 456 | 411 | CEMS Certification and Recertification | Conducting load vs flow test for new monitoring probe | Brown | Derate | Coal | 3 | 2015 | 7 | 6.2333 | 3.7728 | 1550.6237 | 248.7632 | 249
BR3 | D1 | 31 | 3440 | 2015-07-02 05:14 | 2015-07-02 22:00 | 425 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP heater leak | Brown | Derate | Coal | 3 | 2015 | 7 | 16.7667 | 1.1398 | 468.4739 | 27.9408 | 28
BR3 | MO | 32 | 3440 | 2015-07-02 22:00 | 2015-07-04 18:05 | 0 | 456 | 411 | High pressure heater tube leaks | 3F-2 HP heater leak repair | Brown | Maintenance | Coal | 3 | 2015 | 7 | 44.0833 | 44.0833 | 18118.25 | 411 | 411
BR3 | D1 | 34 | 1710 | 2015-07-07 08:30 | 2015-07-07 08:58 | 95 | 456 | 411 | Combustion/steam condition controls (report local controls --- burners | Boiler MFT after loosing 3-3 mill feeder multiple times | Brown | Derate | Coal | 3 | 2015 | 7 | 0.46667 | 0.36944 | 151.8417 | 325.375 | 325
BR3 | MO | 35 | 740 | 2015-07-08 07:16 | 2015-07-09 16:19 | 0 | 456 | 411 | Boiler recirculation pumps | Replace 3-3 BCWP | Brown | Maintenance | Coal | 3 | 2015 | 7 | 33.05 | 33.05 | 13583.55 | 411 | 411
BR3 | D1 | 37 | 9270 | 2015-07-14 16:14 | 2015-07-14 17:40 | 340 | 456 | 411 | Wet coal | 3-4 feeder plugged due to wet coal | Brown | Derate | Coal | 3 | 2015 | 7 | 1.4333 | 0.36462 | 149.8588 | 104.5526 | 105
BR3 | D1 | 38 | 9270 | 2015-07-14 17:40 | 2015-07-15 00:43 | 240 | 456 | 411 | Wet coal | 3-3 & 3-4 feeders plugged due to wet coal | Brown | Derate | Coal | 3 | 2015 | 7 | 7.05 | 3.3395 | 1372.5237 | 194.6842 | 195
BR3 | D1 | 39 | 9270 | 2015-07-15 00:43 | 2015-07-15 01:35 | 240 | 456 | 411 | Wet coal | 3-2 & 3-3 fedders plugged due to wet coal | Brown | Derate | Coal | 3 | 2015 | 7 | 0.86667 | 0.41053 | 168.7263 | 194.6842 | 195
BR3 | PD | 40 | 300 | 2015-07-15 01:35 | 2015-07-15 02:35 | 350 | 456 | 411 | Pulverizer motors and drives | Replace 3-2 mill motor | Brown | Derate | Coal | 3 | 2015 | 7 | 1 | 0.23246 | 95.5395 | 95.5395 | 96
BR3 | D1 | 41 | 9270 | 2015-07-15 02:35 | 2015-07-15 03:49 | 55 | 456 | 411 | Wet coal | Boiler trip due to wet coal | Brown | Derate | Coal | 3 | 2015 | 7 | 1.2333 | 1.0846 | 445.7607 | 361.4276 | 361
BR3 | U1 | 42 | 9270 | 2015-07-15 03:49 | 2015-07-15 06:52 | 0 | 456 | 411 | Wet coal | Unit trip due to wet coal | Brown | Outage | Coal | 3 | 2015 | 7 | 3.05 | 3.05 | 1253.55 | 411 | 411
BR3 | SF | 43 | 9270 | 2015-07-15 06:52 | 2015-07-15 12:21 | 0 | 456 | 411 | Wet coal | Startup failure due to wet coal conditions | Brown | Outage | Coal | 3 | 2015 | 7 | 5.4833 | 5.4833 | 2253.65 | 411 | 411
BR3 | D1 | 44 | 9270 | 2015-07-15 18:24 | 2015-07-15 22:22 | 305 | 456 | 411 | Wet coal | Wet coal causing mill feeder issues | Brown | Derate | Coal | 3 | 2015 | 7 | 3.9667 | 1.3135 | 539.8581 | 136.0987 | 136
BR3 | D1 | 45 | 9270 | 2015-07-15 22:22 | 2015-07-16 00:30 | 160 | 456 | 411 | Wet coal | Wet coal causing mill feeder issues | Brown | Derate | Coal | 3 | 2015 | 7 | 2.1333 | 1.3848 | 569.1509 | 266.7895 | 267
BR3 | D1 | 46 | 9930 | 2015-07-25 09:12 | 2015-07-25 09:20 | 240 | 456 | 411 | Operating procedure error | Suction valve at fuel oil tank left in closed position | Brown | Derate | Coal | 3 | 2015 | 7 | 0.13333 | 0.063158 | 25.9579 | 194.6842 | 195
BR3 | D1 | 47 | 250 | 2015-07-25 09:26 | 2015-07-25 13:30 | 350 | 456 | 411 | Pulverizer feeders | 3-2 feeder belt replaced due to damage from foregin metal in feeder. | Brown | Derate | Coal | 3 | 2015 | 7 | 4.0667 | 0.94532 | 388.5272 | 95.5395 | 96
BR3 | D1 | 48 | 3414 | 2015-07-28 18:01 | 2015-07-28 20:17 | 275 | 456 | 411 | Feedwater pump local controls | 3-1 BFP LP stop valve control problems | Brown | Derate | Coal | 3 | 2015 | 7 | 2.2667 | 0.89971 | 369.7798 | 163.1382 | 163
BR3 | D1 | 49 | 3414 | 2015-07-28 20:17 | 2015-07-28 21:45 | 315 | 456 | 411 | Feedwater pump local controls | 3-1 BFP LP stop valve control problems | Brown | Derate | Coal | 3 | 2015 | 7 | 1.4667 | 0.45351 | 186.3921 | 127.0855 | 127
BR3 | D1 | 50 | 3414 | 2015-08-02 16:07 | 2015-08-02 16:25 | 315 | 456 | 411 | Feedwater pump local controls | 3-1 BFP governor valve control problems | Brown | Derate | Coal | 3 | 2015 | 8 | 0.3 | 0.092763 | 38.1257 | 127.0855 | 127
BR3 | D1 | 51 | 3414 | 2015-08-04 13:50 | 2015-08-05 11:51 | 300 | 456 | 411 | Feedwater pump local controls | 3-1 BFP LP/HP governor controls not responding | Brown | Derate | Coal | 3 | 2015 | 8 | 22.0167 | 7.532 | 3095.6592 | 140.6053 | 141
BR3 | D1 | 52 | 3412 | 2015-08-17 13:59 | 2015-08-18 04:43 | 300 | 456 | 411 | Feedwater pump drive - steam turbine | 3-1 BFP steam leak at LP steam line connection | Brown | Derate | Coal | 3 | 2015 | 8 | 14.7333 | 5.0404 | 2071.5842 | 140.6053 | 141
BR3 | NC | 53 | 8700 | 2015-08-18 21:23 | 2015-08-19 10:44 | 0 | 456 | 411 | CEMS Certification and Recertification | Duct Gas RATA testing | Brown | Other | Coal | 3 | 2015 | 8 | 13.35 | 13.35 | 5486.85 | 411 | 411
BR3 | NC | 54 | 8700 | 2015-08-19 21:00 | 2015-08-20 00:48 | 0 | 456 | 411 | CEMS Certification and Recertification | Duct low flow RATA testing | Brown | Other | Coal | 3 | 2015 | 8 | 3.8 | 3.8 | 1561.8 | 411 | 411
BR3 | D1 | 55 | 350 | 2015-09-01 13:21 | 2015-09-01 14:52 | 325 | 456 | 411 | Pulverized fuel and air piping (from pulverizer to wind box) | 3-4 mill burner line fire | Brown | Derate | Coal | 3 | 2015 | 9 | 1.5167 | 0.43571 | 179.0764 | 118.0724 | 118
BR3 | D1 | 56 | 310 | 2015-09-01 14:52 | 2015-09-01 15:30 | 325 | 456 | 411 | Pulverizer mills | Inspect 3-2 mill motor coupling | Brown | Derate | Coal | 3 | 2015 | 9 | 0.63333 | 0.18194 | 74.7792 | 118.0724 | 118
BR3 | D1 | 57 | 310 | 2015-09-01 15:30 | 2015-09-02 05:04 | 350 | 456 | 411 | Pulverizer mills | Replace 3-2 mill motor to mill coupling | Brown | Derate | Coal | 3 | 2015 | 9 | 13.5667 | 3.1537 | 1296.1522 | 95.5395 | 96
BR3 | D1 | 58 | 350 | 2015-09-02 08:07 | 2015-09-02 10:53 | 350 | 456 | 411 | Pulverized fuel and air piping (from pulverizer to wind box) | Suspect fire in 3-4D burner line | Brown | Derate | Coal | 3 | 2015 | 9 | 2.7667 | 0.64313 | 264.3259 | 95.5395 | 96
BR3 | MO | 60 | 891 | 2015-09-14 06:00 | 2015-09-14 22:08 | 0 | 456 | 411 | Bottom ash hoppers (including gates) | Pre-outage inspection of bottom ash hopper by Skanska | Brown | Maintenance | Coal | 3 | 2015 | 9 | 16.1333 | 16.1333 | 6630.8 | 411 | 411
BR3 | MO | 62 | 350 | 2015-09-16 08:02 | 2015-09-16 11:07 | 0 | 456 | 411 | Pulverized fuel and air piping (from pulverizer to wind box) | Inspect 3-1C burner nozzle | Brown | Maintenance | Coal | 3 | 2015 | 9 | 3.0833 | 3.0833 | 1267.25 | 411 | 411
BR3 | D1 | 65 | 110 | 2015-09-23 17:04 | 2015-09-23 17:48 | 105 | 456 | 411 | Other coal fuel supply problems up through bunkers | 3-5 mill coal bunker empty | Brown | Derate | Coal | 3 | 2015 | 9 | 0.73333 | 0.56447 | 231.9987 | 316.3618 | 316
BR3 | D1 | 66 | 310 | 2015-09-28 06:40 | 2015-09-29 01:43 | 350 | 456 | 411 | Pulverizer mills | Repair 3-2 mill exhauster coupling | Brown | Derate | Coal | 3 | 2015 | 9 | 19.05 | 4.4283 | 1820.027 | 95.5395 | 96
BR3 | PO | 67 | 1800 | 2015-10-02 13:12 | 2015-11-22 18:01 | 0 | 456 | 411 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Replace boiler corners and connect to PJFF | Brown | Other | Coal | 3 | 2015 | 10 | 1228.8167 | 1228.8167 | 505043.65 | 411 | 411
BR3 | D1 | 68 | 3410 | 2015-11-23 03:30 | 2015-11-23 04:50 | 340 | 456 | 411 | Feedwater pump | Inspect 3-2 BFP for damage due to excessive balance line pressure | Brown | Derate | Coal | 3 | 2015 | 11 | 1.3333 | 0.33918 | 139.4035 | 104.5526 | 105
BR3 | D1 | 69 | 3410 | 2015-11-23 04:50 | 2015-11-23 12:09 | 310 | 456 | 411 | Feedwater pump | Inspect 3-2 BFP for damage due to excessive balance line pressure | Brown | Derate | Coal | 3 | 2015 | 11 | 7.3167 | 2.3426 | 962.8156 | 131.5921 | 132
BR3 | U1 | 70 | 3399 | 2015-11-23 12:09 | 2015-11-23 23:00 | 0 | 456 | 411 | Other miscellaneous condensate system problems | Repair DA level transmitter | Brown | Outage | Coal | 3 | 2015 | 11 | 10.85 | 10.85 | 4459.35 | 411 | 411
BR3 | SF | 71 | 9930 | 2015-11-23 23:00 | 2015-11-24 03:16 | 0 | 456 | 411 | Operating procedure error | Trouble with rolling off 3-1 BFP | Brown | Outage | Coal | 3 | 2015 | 11 | 4.2667 | 4.2667 | 1753.6 | 411 | 411
BR3 | D1 | 72 | 3410 | 2015-11-24 03:16 | 2015-11-24 10:30 | 310 | 456 | 411 | Feedwater pump | Inspect 3-2 BFP for damage due to excessive balance line pressure | Brown | Derate | Coal | 3 | 2015 | 11 | 7.2333 | 2.3159 | 951.8496 | 131.5921 | 132
BR3 | D1 | 73 | 3410 | 2015-11-24 10:30 | 2015-11-25 16:00 | 325 | 456 | 411 | Feedwater pump | Inspect 3-2 BFP for damage due to excessive balance line pressure | Brown | Derate | Coal | 3 | 2015 | 11 | 29.5 | 8.4748 | 3483.1349 | 118.0724 | 118
BR3 | D1 | 74 | 1761 | 2015-11-25 16:00 | 2015-11-25 20:32 | 67 | 456 | 411 | Combustion /Steam condition instrumentation (not local controls) | Boiler MFT due to loss of 3-3 mill feeder | Brown | Derate | Coal | 3 | 2015 | 11 | 4.5333 | 3.8673 | 1589.4404 | 350.6118 | 351
BR3 | D1 | 75 | 3410 | 2015-11-25 20:32 | 2015-12-02 16:21 | 325 | 456 | 411 | Feedwater pump | Inspect 3-2 BFP for damage due to excessive balance line pressure | Brown | Derate | Coal | 3 | 2015 | 11 | 163.8167 | 47.0614 | 19342.2218 | 118.0724 | 118
BR3 | D1 | 76 | 250 | 2015-12-02 17:20 | 2015-12-02 17:37 | 350 | 456 | 411 | Pulverizer feeders | 3-5 mill feeder motor failed | Brown | Derate | Coal | 3 | 2015 | 12 | 0.28333 | 0.065863 | 27.0695 | 95.5395 | 96
BR3 | D1 | 77 | 250 | 2015-12-02 17:37 | 2015-12-03 21:57 | 360 | 456 | 411 | Pulverizer feeders | 3-5 mill feeder motor failed | Brown | Derate | Coal | 3 | 2015 | 12 | 28.3333 | 5.9649 | 2451.5789 | 86.5263 | 87
BR3 | D1 | 78 | 250 | 2015-12-03 21:57 | 2015-12-03 23:28 | 57 | 456 | 411 | Pulverizer feeders | Boiler trip due to loss of mill feeder | Brown | Derate | Coal | 3 | 2015 | 12 | 1.5167 | 1.3271 | 545.4313 | 359.625 | 360
BR3 | D1 | 79 | 250 | 2015-12-03 23:28 | 2015-12-04 04:15 | 360 | 456 | 411 | Pulverizer feeders | 3-5 mill feeder motor failed | Brown | Derate | Coal | 3 | 2015 | 12 | 4.7833 | 1.007 | 413.8842 | 86.5263 | 87
BR3 | D1 | 80 | 250 | 2015-12-04 04:15 | 2015-12-04 17:55 | 250 | 456 | 411 | Pulverizer feeders | 3-1 & 3-5 mill feeder motors failed | Brown | Derate | Coal | 3 | 2015 | 12 | 13.6667 | 6.174 | 2537.5044 | 185.6711 | 186
BR3 | D1 | 81 | 250 | 2015-12-04 17:55 | 2015-12-05 00:52 | 360 | 456 | 411 | Pulverizer feeders | 3-1 mill feeder failed | Brown | Derate | Coal | 3 | 2015 | 12 | 6.95 | 1.4632 | 601.3579 | 86.5263 | 87
BR3 | NC | 82 | 8100 | 2015-12-10 07:20 | 2015-12-10 15:37 | 0 | 456 | 411 | Scrubber/absorber tower or module | Low load FGD water flow test | Brown | Other | Coal | 3 | 2015 | 12 | 8.2833 | 8.2833 | 3404.45 | 411 | 411
BR3 | NC | 83 | 8100 | 2015-12-11 09:00 | 2015-12-11 15:31 | 0 | 456 | 411 | Scrubber/absorber tower or module | Mid load FGD water flow test | Brown | Other | Coal | 3 | 2015 | 12 | 6.5167 | 6.5167 | 2678.35 | 411 | 411
BR3 | NC | 84 | 4261 | 2015-12-11 15:31 | 2015-12-11 17:15 | 0 | 456 | 411 | Control valves | Calibrating main turbine governor valves | Brown | Other | Coal | 3 | 2015 | 12 | 1.7333 | 1.7333 | 712.4 | 411 | 411
BR3 | D1 | 85 | 310 | 2015-12-17 07:50 | 2015-12-17 12:26 | 360 | 456 | 411 | Pulverizer mills | Repair 3-5 mill pyrite scrapper | Brown | Derate | Coal | 3 | 2015 | 12 | 4.6 | 0.96842 | 398.0211 | 86.5263 | 87
BR3 | NC | 86 | 8650 | 2015-12-17 20:00 | 2015-12-18 05:01 | 0 | 456 | 411 | Baghouse systems | PJFF low load testing | Brown | Other | Coal | 3 | 2015 | 12 | 9.0167 | 9.0167 | 3705.85 | 411 | 411
BR3 | NC | 87 | 8650 | 2015-12-19 00:05 | 2015-12-19 04:53 | 0 | 456 | 411 | Baghouse systems | PJFF low load testing | Brown | Other | Coal | 3 | 2015 | 12 | 4.8 | 4.8 | 1972.8 | 411 | 411
BR3 | MO | 89 | 880 | 2015-12-28 12:00 | 2015-12-28 16:45 | 0 | 456 | 411 | Fly ash Removal System (not precipitators | Ash Hopper Maint | Brown | Maintenance | Coal | 3 | 2015 | 12 | 4.75 | 4.75 | 1952.25 | 411 | 411
BR3 | D1 | 2 | 1455 | 2016-01-06 07:20 | 2016-01-10 23:28 | 290 | 456 | 411 | Induced draft fans | 3-1 ID Fan trip due to vibration | Brown | Derate | Coal | 3 | 2016 | 1 | 112.1333 | 40.8205 | 16777.2123 | 149.6184 | 150
BR3 | MO | 3 | 4260 | 2016-01-07 12:00 | 2016-01-10 18:22 | 0 | 456 | 411 | Main stop valves | Repair leak on turbine left side throttle valve | Brown | Maintenance | Coal | 3 | 2016 | 1 | 78.3667 | 78.3667 | 32208.7 | 411 | 411
BR3 | D1 | 4 | 1455 | 2016-01-10 23:28 | 2016-01-12 10:15 | 425 | 456 | 411 | Induced draft fans | 3-1 ID Fan high vibration | Brown | Derate | Coal | 3 | 2016 | 1 | 34.7833 | 2.3647 | 971.8738 | 27.9408 | 28
BR3 | PD | 5 | 250 | 2016-01-12 10:15 | 2016-01-12 13:06 | 360 | 456 | 411 | Pulverizer feeders | Replace 3-4 feeder belt | Brown | Derate | Coal | 3 | 2016 | 1 | 2.85 | 0.6 | 246.6 | 86.5263 | 87
BR3 | D1 | 6 | 1455 | 2016-01-12 13:06 | 2016-01-26 12:34 | 425 | 456 | 411 | Induced draft fans | 3-1 ID Fan vibration | Brown | Derate | Coal | 3 | 2016 | 1 | 335.4667 | 22.8058 | 9373.2035 | 27.9408 | 28
BR3 | MO | 7 | 1455 | 2016-01-26 12:34 | 2016-01-30 19:36 | 0 | 456 | 411 | Induced draft fans | Inspect 3-1 ID Fan due for vibration issues | Brown | Maintenance | Coal | 3 | 2016 | 1 | 103.0333 | 103.0333 | 42346.7 | 411 | 411
BR3 | D1 | 9 | 3410 | 2016-02-16 08:43 | 2016-02-16 21:00 | 440 | 456 | 411 | Feedwater pump | 3-2 BFP vibration | Brown | Derate | Coal | 3 | 2016 | 2 | 12.2833 | 0.43099 | 177.1386 | 14.4211 | 14
BR3 | PD | 10 | 310 | 2016-02-16 21:00 | 2016-02-16 23:17 | 350 | 456 | 411 | Pulverizer mills | Repair 3-5 mill pyrite scrapper | Brown | Derate | Coal | 3 | 2016 | 2 | 2.2833 | 0.53077 | 218.1485 | 95.5395 | 96
BR3 | D1 | 11 | 3410 | 2016-02-16 23:17 | 2016-02-17 07:00 | 440 | 456 | 411 | Feedwater pump | 3-2 BFP vibration | Brown | Derate | Coal | 3 | 2016 | 2 | 7.7167 | 0.27076 | 111.2825 | 14.4211 | 14
BR3 | MO | 13 | 1510 | 2016-02-23 07:00 | 2016-02-23 15:22 | 0 | 456 | 411 | Flue gas ducts (except recirculation) | PJFF inlet duct inspection | Brown | Maintenance | Coal | 3 | 2016 | 2 | 8.3667 | 8.3667 | 3438.7 | 411 | 411
BR3 | D1 | 15 | 9900 | 2016-03-17 12:00 | 2016-03-17 12:39 | 56 | 456 | 411 | Operator error | Error in managing feedwater system during unit startup | Brown | Derate | Coal | 3 | 2016 | 3 | 0.65 | 0.57018 | 234.3421 | 360.5263 | 361
BR3 | U1 | 16 | 9900 | 2016-03-17 12:39 | 2016-03-17 15:05 | 0 | 456 | 411 | Operator error | Error in managing feedwater system during unit startup | Brown | Outage | Coal | 3 | 2016 | 3 | 2.4333 | 2.4333 | 1000.1 | 411 | 411
BR3 | PO | 17 | 8812 | 2016-03-21 10:04 | 2016-04-16 17:15 | 0 | 456 | 411 | SCR NOxCatalyst | Add additional layer of SCR catalyst and perform minor boiler repairs | Brown | Other | Coal | 3 | 2016 | 3 | 631.1833 | 631.1833 | 259416.35 | 411 | 411
BR3 | SF | 18 | 1591 | 2016-04-16 17:15 | 2016-04-18 05:59 | 0 | 456 | 411 | Stack damper and linkage | U3 FGD shutoff damper motor failed | Brown | Outage | Coal | 3 | 2016 | 4 | 36.7333 | 36.7333 | 15097.4 | 411 | 411
BR3 | U1 | 19 | 1999 | 2016-04-18 09:14 | 2016-04-19 08:41 | 0 | 456 | 411 | Boiler | Lower mud drum header gasket blown | Brown | Outage | Coal | 3 | 2016 | 4 | 23.45 | 23.45 | 9637.95 | 411 | 411
BR3 | D1 | 20 | 3412 | 2016-04-19 20:41 | 2016-04-20 18:17 | 320 | 456 | 411 | Feedwater pump drive - steam turbine | 3-2 BFP vibration | Brown | Derate | Coal | 3 | 2016 | 4 | 21.6 | 6.4421 | 2647.7053 | 122.5789 | 123
BR3 | NC | 21 | 8700 | 2016-04-22 22:00 | 2016-04-23 02:00 | 0 | 456 | 411 | CEMS Certification and Recertification | Low Load RATA testing | Brown | Other | Coal | 3 | 2016 | 4 | 4 | 4 | 1644 | 411 | 411
BR3 | NC | 22 | 8700 | 2016-04-25 23:00 | 2016-04-26 01:45 | 0 | 456 | 411 | CEMS Certification and Recertification | RATA testing | Brown | Other | Coal | 3 | 2016 | 4 | 2.75 | 2.75 | 1130.25 | 411 | 411
BR3 | NC | 23 | 8700 | 2016-04-26 21:00 | 2016-04-27 02:19 | 0 | 456 | 411 | CEMS Certification and Recertification | RATA testing | Brown | Other | Coal | 3 | 2016 | 4 | 5.3167 | 5.3167 | 2185.15 | 411 | 411
BR3 | NC | 24 | 8812 | 2016-04-27 13:18 | 2016-04-27 16:34 | 0 | 456 | 411 | SCR NOxCatalyst | SCR ammonia mid load tuning | Brown | Other | Coal | 3 | 2016 | 4 | 3.2667 | 3.2667 | 1342.6 | 411 | 411
BR3 | NC | 25 | 8700 | 2016-04-27 21:00 | 2016-04-28 04:03 | 0 | 456 | 411 | CEMS Certification and Recertification | RATA testing | Brown | Other | Coal | 3 | 2016 | 4 | 7.05 | 7.05 | 2897.55 | 411 | 411
BR3 | NC | 26 | 8812 | 2016-04-28 22:00 | 2016-04-29 02:15 | 0 | 456 | 411 | SCR NOxCatalyst | SCR ammonia min load tuning | Brown | Other | Coal | 3 | 2016 | 4 | 4.25 | 4.25 | 1746.75 | 411 | 411
BR3 | D1 | 27 | 3410 | 2016-05-09 06:10 | 2016-05-09 11:14 | 320 | 456 | 411 | Feedwater pump | Repair 3-2 BFP drain line leak | Brown | Derate | Coal | 3 | 2016 | 5 | 5.0667 | 1.5111 | 621.0667 | 122.5789 | 123
BR3 | MO | 29 | 1000 | 2016-05-16 15:57 | 2016-05-18 12:00 | 0 | 456 | 411 | Waterwall (Furnace wall) A | Lower WW leak in dead air space above bottom ash hopper | Brown | Maintenance | Coal | 3 | 2016 | 5 | 44.05 | 44.05 | 18104.55 | 411 | 411
BR3 | NC | 31 | 8700 | 2016-05-23 23:00 | 2016-05-24 05:20 | 0 | 456 | 411 | CEMS Certification and Recertification | Mercury testing | Brown | Other | Coal | 3 | 2016 | 5 | 6.3333 | 6.3333 | 2603 | 411 | 411
BR3 | D1 | 32 | 95 | 2016-05-30 17:17 | 2016-05-30 17:57 | 360 | 456 | 411 | Bunker flow problems | No coal 3-5 bunker | Brown | Derate | Coal | 3 | 2016 | 5 | 0.66667 | 0.14035 | 57.6842 | 86.5263 | 87
BR3 | PD | 33 | 344 | 2016-06-23 22:00 | 2016-06-24 02:40 | 360 | 456 | 411 | Pulverizer inspection | 3-2 Pulverizer Inspection | Brown | Derate | Coal | 3 | 2016 | 6 | 4.6667 | 0.98246 | 403.7895 | 86.5263 | 87
BR3 | D1 | 34 | 1750 | 2016-06-24 03:21 | 2016-06-24 08:00 | 47 | 456 | 411 | Burner management system | F820Boiler MFT while switching out mills | Brown | Derate | Coal | 3 | 2016 | 6 | 4.65 | 4.1707 | 1714.1674 | 368.6382 | 369
BR3 | D1 | 35 | 1750 | 2016-06-24 08:00 | 2016-06-24 11:16 | 140 | 456 | 411 | Burner management system | Continued. MFT while switching out mills | Brown | Derate | Coal | 3 | 2016 | 6 | 3.2667 | 2.2637 | 930.3982 | 284.8158 | 285
BR3 | D1 | 36 | 310 | 2016-06-24 11:16 | 2016-06-24 12:00 | 200 | 456 | 411 | Pulverizer mills | Vacuum coal out of mills after MFT | Brown | Derate | Coal | 3 | 2016 | 6 | 0.73333 | 0.4117 | 169.207 | 230.7368 | 231
BR3 | D1 | 37 | 300 | 2016-06-24 12:00 | 2016-06-24 19:49 | 360 | 456 | 411 | Pulverizer motors and drives | Replaced 2-2 mill motor due to bearing failure. | Brown | Derate | Coal | 3 | 2016 | 6 | 7.8167 | 1.6456 | 676.3474 | 86.5263 | 87
BR3 | PD | 38 | 344 | 2016-06-30 23:00 | 2016-07-01 00:15 | 360 | 456 | 411 | Pulverizer inspection | Inspect 3-2 Mill Pyreite Scraper | Brown | Derate | Coal | 3 | 2016 | 6 | 1.25 | 0.26316 | 108.1579 | 86.5263 | 87
BR3 | D1 | 39 | 1750 | 2016-07-01 04:30 | 2016-07-01 06:23 | 25 | 456 | 411 | Burner management system | Boiler MFT due to loss of coal flow to mill | Brown | Derate | Coal | 3 | 2016 | 7 | 1.8833 | 1.7801 | 731.613 | 388.4671 | 388
BR3 | D1 | 40 | 1710 | 2016-07-01 04:30 | 2016-07-01 06:23 | 55 | 456 | 411 | Combustion/steam condition controls (report local controls --- burners | 3-2 mill out for maintenance and 3-1 mill ran out of coal resulting in boiler MFT | Brown | Derate | Coal | 3 | 2016 | 7 | 1.8833 | 1.6562 | 680.6887 | 361.4276 | 361
BR3 | U1 | 41 | 1160 | 2016-07-01 12:21 | 2016-07-05 15:36 | 0 | 456 | 411 | First reheater B | Reheat tube leak | Brown | Outage | Coal | 3 | 2016 | 7 | 99.25 | 99.25 | 40791.75 | 411 | 411
BR3 | D1 | 42 | 1512 | 2016-07-05 17:26 | 2016-07-05 21:43 | 250 | 456 | 411 | Flue gas expansion joints | 3-1 ID Fan expansion joint leak | Brown | Derate | Coal | 3 | 2016 | 7 | 4.2833 | 1.935 | 795.291 | 185.6711 | 186
BR3 | U1 | 43 | 1512 | 2016-07-05 21:43 | 2016-07-07 10:41 | 0 | 456 | 411 | Flue gas expansion joints | 3-1 ID Fan expansion joint leak | Brown | Outage | Coal | 3 | 2016 | 7 | 36.9667 | 36.9667 | 15193.3 | 411 | 411
BR3 | D1 | 44 | 4263 | 2016-07-09 17:06 | 2016-07-09 19:46 | 300 | 456 | 411 | Reheat stop valves | Both right and left side turbine RH Stop valves stuck closed during weekly testing | Brown | Derate | Coal | 3 | 2016 | 7 | 2.6667 | 0.91228 | 374.9474 | 140.6053 | 141
BR3 | D1 | 45 | 310 | 2016-07-15 07:50 | 2016-07-15 12:15 | 360 | 456 | 411 | Pulverizer mills | Repair 3-1 mill pyrite scraper | Brown | Derate | Coal | 3 | 2016 | 7 | 4.4167 | 0.92982 | 382.1579 | 86.5263 | 87
BR3 | D1 | 46 | 3620 | 2016-07-19 21:46 | 2016-07-19 22:03 | 428 | 456 | 411 | Main transformer | Main tranformer winding and oil temperatures in alarm | Brown | Derate | Coal | 3 | 2016 | 7 | 0.28333 | 0.017398 | 7.1504 | 25.2368 | 25
BR3 | D1 | 47 | 3620 | 2016-07-19 22:03 | 2016-07-19 22:14 | 418 | 456 | 411 | Main transformer | Main Transformer winding and oil temperatires in alarm | Brown | Derate | Coal | 3 | 2016 | 7 | 0.18333 | 0.015278 | 6.2792 | 34.25 | 34
BR3 | D1 | 48 | 3620 | 2016-07-19 22:14 | 2016-07-19 22:40 | 408 | 456 | 411 | Main transformer | Main Transformer winding and oil temperatires in alarm | Brown | Derate | Coal | 3 | 2016 | 7 | 0.43333 | 0.045614 | 18.7474 | 43.2632 | 43
BR3 | D1 | 49 | 3620 | 2016-07-19 22:40 | 2016-07-20 00:15 | 390 | 456 | 411 | Main transformer | Main Transformer winding and oil temperatires in alarm | Brown | Derate | Coal | 3 | 2016 | 7 | 1.5833 | 0.22917 | 94.1875 | 59.4868 | 59
BR3 | NC | 50 | 9999 | 2016-07-27 23:00 | 2016-07-28 09:44 | 0 | 456 | 411 | Total unit performance testing (use appropriate codes for individual component testing) | Heat Rate testing at various loads | Brown | Other | Coal | 3 | 2016 | 7 | 10.7333 | 10.7333 | 4411.4 | 411 | 411
BR3 | NC | 51 | 4263 | 2016-08-08 22:04 | 2016-08-08 23:19 | 0 | 456 | 411 | Reheat stop valves | Testing operation of RH stop valves | Brown | Other | Coal | 3 | 2016 | 8 | 1.25 | 1.25 | 513.75 | 411 | 411
BR3 | PD | 52 | 3412 | 2016-08-11 22:54 | 2016-08-12 05:44 | 320 | 456 | 411 | Feedwater pump drive - steam turbine | Replace 3-2 BFPT turning gear | Brown | Derate | Coal | 3 | 2016 | 8 | 6.8333 | 2.038 | 837.6228 | 122.5789 | 123
BR3 | MO | 53 | 740 | 2016-08-13 20:13 | 2016-08-17 05:56 | 0 | 456 | 411 | Boiler recirculation pumps | Replace 3-3 BCWP and 3-1 ID Fan oulet expansion joint | Brown | Maintenance | Coal | 3 | 2016 | 8 | 81.7167 | 81.7167 | 33585.55 | 411 | 411
BR3 | U1 | 54 | 740 | 2016-08-17 22:43 | 2016-08-18 21:43 | 0 | 456 | 411 | Boiler recirculation pumps | 3-2 BCWP discharge valve bypass line leak | Brown | Outage | Coal | 3 | 2016 | 8 | 23 | 23 | 9453 | 411 | 411
BR3 | MO | 56 | 8250 | 2016-08-22 02:15 | 2016-08-22 15:35 | 0 | 456 | 411 | Dampers other than bypass | Inspect Brown 3 FGD shutoff damper | Brown | Maintenance | Coal | 3 | 2016 | 8 | 13.3333 | 13.3333 | 5480 | 411 | 411
BR3 | D1 | 58 | 4263 | 2016-08-28 18:08 | 2016-08-28 18:18 | 280 | 456 | 411 | Reheat stop valves | Left side RH Stop valve stuck closed on weekly test | Brown | Derate | Coal | 3 | 2016 | 8 | 0.16667 | 0.064327 | 26.4386 | 158.6316 | 159
BR3 | U1 | 59 | 1090 | 2016-08-29 13:20 | 2016-08-31 17:30 | 0 | 456 | 411 | Other boiler tube leaks | Waterwall leak from tube rupture | Brown | Outage | Coal | 3 | 2016 | 8 | 52.1667 | 52.1667 | 21440.5 | 411 | 411
BR3 | NC | 60 | 8700 | 2016-09-22 03:00 | 2016-09-22 06:10 | 0 | 456 | 411 | CEMS Certification and Recertification | Mid load RATA testing | Brown | Other | Coal | 3 | 2016 | 9 | 3.1667 | 3.1667 | 1301.5 | 411 | 411
BR3 | NC | 61 | 8700 | 2016-09-22 23:00 | 2016-09-23 09:04 | 0 | 456 | 411 | CEMS Certification and Recertification | Low load RATA testing | Brown | Other | Coal | 3 | 2016 | 9 | 10.0667 | 10.0667 | 4137.4 | 411 | 411
BR3 | D1 | 62 | 310 | 2016-09-23 22:29 | 2016-09-24 06:53 | 350 | 456 | 411 | Pulverizer mills | 3-4 mill exhauster coupling broken | Brown | Derate | Coal | 3 | 2016 | 9 | 8.4 | 1.9526 | 802.5316 | 95.5395 | 96
BR3 | MO | 64 | 1000 | 2016-10-03 06:00 | 2016-10-16 00:07 | 0 | 456 | 411 | Waterwall (Furnace wall) A | Inspect and repair waterwall tubes related to tube failure in August. Event #59 | Brown | Maintenance | Coal | 3 | 2016 | 10 | 306.1167 | 306.1167 | 125813.95 | 411 | 411
BR3 | U1 | 65 | 4609 | 2016-11-01 06:56 | 2016-11-10 14:05 | 0 | 456 | 411 | Other exciter problems | Exciter insulation damaged | Brown | Outage | Coal | 3 | 2016 | 11 | 223.15 | 223.15 | 91714.65 | 411 | 411
BR3 | U1 | 66 | 4710 | 2016-11-10 14:34 | 2016-11-11 04:55 | 0 | 456 | 411 | Generator metering devices | Blown fuses on metering and GCB circuits | Brown | Outage | Coal | 3 | 2016 | 11 | 14.35 | 14.35 | 5897.85 | 411 | 411
BR3 | U1 | 67 | 4609 | 2016-11-11 13:22 | 2016-11-11 15:12 | 0 | 456 | 411 | Other exciter problems | Balance adjustment to temporary static exciter | Brown | Outage | Coal | 3 | 2016 | 11 | 1.8333 | 1.8333 | 753.5 | 411 | 411
BR3 | U1 | 68 | 4609 | 2016-11-11 19:06 | 2016-11-12 01:01 | 0 | 456 | 411 | Other exciter problems | Balance adjustment to temporary static exciter | Brown | Outage | Coal | 3 | 2016 | 11 | 5.9167 | 5.9167 | 2431.75 | 411 | 411
BR3 | SF | 69 | 4609 | 2016-11-12 01:01 | 2016-11-12 04:08 | 0 | 456 | 411 | Other exciter problems | Generator lockout due to lockout in temporary exciter circuits | Brown | Outage | Coal | 3 | 2016 | 11 | 3.1167 | 3.1167 | 1280.95 | 411 | 411
BR3 | D1 | 71 | 250 | 2016-12-04 19:20 | 2016-12-05 02:02 | 360 | 456 | 411 | Pulverizer feeders | 3-2 feeder will not start | Brown | Derate | Coal | 3 | 2016 | 12 | 6.7 | 1.4105 | 579.7263 | 86.5263 | 87
BR3 | MO | 73 | 1510 | 2016-12-30 05:00 | 2016-12-30 13:14 | 0 | 456 | 411 | Flue gas ducts (except recirculation) | FGD Duct inspection | Brown | Maintenance | Coal | 3 | 2016 | 12 | 8.2333 | 8.2333 | 3383.9 | 411 | 411
BR3 | D1 | 2 | 1455 | 2017-01-05 10:16 | 2017-01-05 11:49 | 260 | 456 | 411 | Induced draft fans | 3-1 ID Fan trip on high vibration | Brown | Derate | Coal | 3 | 2017 | 1 | 1.55 | 0.66623 | 273.8197 | 176.6579 | 177
BR3 | MO | 3 | 1100 | 2017-01-10 00:14 | 2017-01-12 13:25 | 0 | 456 | 411 | Waterwall (Furnace wall) B | Rear water wall tube leak above ash hopper | Brown | Maintenance | Coal | 3 | 2017 | 1 | 61.1833 | 61.1833 | 25146.35 | 411 | 411
BR3 | MO | 5 | 1455 | 2017-01-19 07:00 | 2017-01-20 11:49 | 0 | 456 | 411 | Induced draft fans | Balance 3-1 ID Fan due to vibration | Brown | Maintenance | Coal | 3 | 2017 | 1 | 28.8167 | 28.8167 | 11843.65 | 411 | 411
BR3 | SF | 7 | 440 | 2017-02-28 03:41 | 2017-02-28 12:06 | 0 | 456 | 411 | Fuel oil pumps (general) | Boiler trip on loss of fuel oil pump | Brown | Outage | Coal | 3 | 2017 | 2 | 8.4167 | 8.4167 | 3459.25 | 411 | 411
BR3 | U1 | 8 | 1000 | 2017-03-08 08:58 | 2017-03-09 06:19 | 0 | 456 | 411 | Waterwall (Furnace wall) A | Waterwall tube leak, "A" corner below conveyor level. | Brown | Outage | Coal | 3 | 2017 | 3 | 21.35 | 21.35 | 8774.85 | 411 | 411
BR3 | NC | 10 | 8700 | 2017-03-13 22:00 | 2017-03-14 03:00 | 0 | 456 | 411 | CEMS Certification and Recertification | RATA testing | Brown | Other | Coal | 3 | 2017 | 3 | 5 | 5 | 2055 | 411 | 411
BR3 | NC | 11 | 8700 | 2017-03-14 03:00 | 2017-03-14 09:15 | 0 | 456 | 411 | CEMS Certification and Recertification | RATA testing | Brown | Other | Coal | 3 | 2017 | 3 | 6.25 | 6.25 | 2568.75 | 411 | 411
BR3 | D1 | 9 | 4263 | 2017-03-18 21:05 | 2017-03-18 21:11 | 292 | 456 | 411 | Reheat stop valves | Right RH stop valve stuck closed during valve check | Brown | Derate | Coal | 3 | 2017 | 3 | 0.1 | 0.035965 | 14.7816 | 147.8158 | 148
BR3 | U1 | 12 | 9900 | 2017-03-24 11:33 | 2017-03-24 12:02 | 0 | 456 | 411 | Operator error | GCB opened by mistake when performing non related switching | Brown | Outage | Coal | 3 | 2017 | 3 | 0.48333 | 0.48333 | 198.65 | 411 | 411
BR3 | PO | 13 | 1801 | 2017-04-14 23:01 | 2017-05-06 17:39 | 0 | 456 | 411 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Planned outage with misc. tasks | Brown | Other | Coal | 3 | 2017 | 4 | 522.6333 | 522.6333 | 214802.3 | 411 | 411
BR3 | MO | 15 | 4609 | 2017-05-09 21:41 | 2017-05-10 03:01 | 0 | 456 | 411 | Other exciter problems | Perform balance move on #7 Exciter bearing | Brown | Maintenance | Coal | 3 | 2017 | 5 | 5.3333 | 5.3333 | 2192 | 411 | 411
BR3 | PD | 16 | 3410 | 2017-05-10 03:01 | 2017-05-10 06:15 | 300 | 456 | 411 | Feedwater pump | Perform alignment on 3-2 BFP | Brown | Derate | Coal | 3 | 2017 | 5 | 3.2333 | 1.1061 | 454.6237 | 140.6053 | 141
BR3 | MO | 17 | 4609 | 2017-05-10 06:15 | 2017-05-10 09:36 | 0 | 456 | 411 | Other exciter problems | Perform balance move on #7 Exciter bearing | Brown | Maintenance | Coal | 3 | 2017 | 5 | 3.35 | 3.35 | 1376.85 | 411 | 411
BR3 | D1 | 18 | 1850 | 2017-05-11 06:37 | 2017-05-11 07:02 | 420 | 456 | 411 | Boiler water condition (not feedwater water quality) | High silica | Brown | Derate | Coal | 3 | 2017 | 5 | 0.41667 | 0.032895 | 13.5197 | 32.4474 | 32
BR3 | MO | 19 | 4609 | 2017-05-11 07:58 | 2017-05-11 12:06 | 0 | 456 | 411 | Other exciter problems | Perform balance move on #7 Exciter bearing | Brown | Maintenance | Coal | 3 | 2017 | 5 | 4.1333 | 4.1333 | 1698.8 | 411 | 411
BR3 | D1 | 20 | 1850 | 2017-05-11 14:06 | 2017-05-11 15:40 | 400 | 456 | 411 | Boiler water condition (not feedwater water quality) | High boiler feedwater silica | Brown | Derate | Coal | 3 | 2017 | 5 | 1.5667 | 0.1924 | 79.0754 | 50.4737 | 50
BR3 | U1 | 21 | 4609 | 2017-05-12 10:56 | 2017-05-12 12:30 | 0 | 456 | 411 | Other exciter problems | Water leak inside exciter housing | Brown | Outage | Coal | 3 | 2017 | 5 | 1.5667 | 1.5667 | 643.9 | 411 | 411
BR3 | MO | 22 | 4609 | 2017-05-12 12:30 | 2017-05-13 20:01 | 0 | 456 | 411 | Other exciter problems | Perform balance move due to #7 exciter beraing vibration | Brown | Maintenance | Coal | 3 | 2017 | 5 | 31.5167 | 31.5167 | 12953.35 | 411 | 411
BR3 | D1 | 23 | 310 | 2017-05-14 01:20 | 2017-05-14 06:08 | 370 | 456 | 411 | Pulverizer mills | Noise in 3-3 mill pyrite section | Brown | Derate | Coal | 3 | 2017 | 5 | 4.8 | 0.90526 | 372.0632 | 77.5132 | 78
BR3 | PD | 24 | 1980 | 2017-05-15 19:00 | 2017-05-15 22:18 | 365 | 456 | 411 | Boiler safety valve test | Set boiler safties post outage | Brown | Derate | Coal | 3 | 2017 | 5 | 3.3 | 0.65855 | 270.6651 | 82.0197 | 82
BR3 | D1 | 25 | 250 | 2017-05-19 15:30 | 2017-05-20 00:05 | 350 | 456 | 411 | Pulverizer feeders | 3-3 mill feeder tripped and would not restart | Brown | Derate | Coal | 3 | 2017 | 5 | 8.5833 | 1.9952 | 820.0471 | 95.5395 | 96
BR3 | D1 | 26 | 3620 | 2017-05-20 17:22 | 2017-05-20 21:15 | 390 | 456 | 411 | Main transformer | Main transformer oil temperature high | Brown | Derate | Coal | 3 | 2017 | 5 | 3.8833 | 0.56206 | 231.0072 | 59.4868 | 59
BR3 | D1 | 27 | 310 | 2017-06-05 15:45 | 2017-06-05 18:02 | 370 | 456 | 411 | Pulverizer mills | Noise in 3-2 mill pyrite area | Brown | Derate | Coal | 3 | 2017 | 6 | 2.2833 | 0.43063 | 176.9884 | 77.5132 | 78
BR3 | D1 | 28 | 310 | 2017-06-09 10:04 | 2017-06-09 13:02 | 370 | 456 | 411 | Pulverizer mills | Repair 3-4 mill pyrtie scrapper | Brown | Derate | Coal | 3 | 2017 | 6 | 2.9667 | 0.5595 | 229.9557 | 77.5132 | 78
BR3 | D1 | 30 | 310 | 2017-07-03 06:38 | 2017-07-03 09:38 | 360 | 456 | 411 | Pulverizer mills | Broken pyrite scrapper 3-4 mill | Brown | Derate | Coal | 3 | 2017 | 7 | 3 | 0.63158 | 259.5789 | 86.5263 | 87
BR3 | D1 | 31 | 310 | 2017-07-04 16:30 | 2017-07-04 19:37 | 360 | 456 | 411 | Pulverizer mills | Broken pyrite scrapper 3-4 mill | Brown | Derate | Coal | 3 | 2017 | 7 | 3.1167 | 0.65614 | 269.6737 | 86.5263 | 87
BR3 | D1 | 32 | 310 | 2017-07-08 16:05 | 2017-07-08 21:16 | 350 | 456 | 411 | Pulverizer mills | Broken pyrite scrapper 3-2 mill | Brown | Derate | Coal | 3 | 2017 | 7 | 5.1833 | 1.2049 | 495.2129 | 95.5395 | 96
BR3 | PD | 33 | 1407 | 2017-07-14 23:00 | 2017-07-15 00:57 | 300 | 456 | 411 | Forced draft fan lubrication system | F7803-1 FD FAN MOTOR IB BEARING TEMP HIGH | Brown | Derate | Coal | 3 | 2017 | 7 | 1.95 | 0.66711 | 274.1803 | 140.6053 | 141
BR3 | MO | 34 | 1060 | 2017-08-04 20:32 | 2017-08-07 16:17 | 0 | 456 | 411 | First reheater A | Repair potential RH leak | Brown | Maintenance | Coal | 3 | 2017 | 8 | 67.75 | 67.75 | 27845.25 | 411 | 411
BR3 | U1 | 36 | 4430 | 2017-08-14 16:13 | 2017-08-14 23:04 | 0 | 456 | 411 | Gland seal system | BFPT gland steam desuperheater plugged. cannot control temperature | Brown | Outage | Coal | 3 | 2017 | 8 | 6.85 | 6.85 | 2815.35 | 411 | 411
BR3 | D1 | 37 | 300 | 2017-08-17 10:46 | 2017-08-17 11:24 | 350 | 456 | 411 | Pulverizer motors and drives | F8203-1 Mill breaker would not close in fully/tripping back out. | Brown | Derate | Coal | 3 | 2017 | 8 | 0.63333 | 0.14722 | 60.5083 | 95.5395 | 96
BR3 | PD | 38 | 310 | 2017-08-24 22:00 | 2017-08-25 00:45 | 350 | 456 | 411 | Pulverizer mills | Replace 3-2 mill north door | Brown | Derate | Coal | 3 | 2017 | 8 | 2.75 | 0.63925 | 262.7336 | 95.5395 | 96
BR3 | U1 | 40 | 1180 | 2017-09-05 11:46 | 2017-09-07 15:47 | 0 | 456 | 411 | Economizer A | Economizer tube leak | Brown | Outage | Coal | 3 | 2017 | 9 | 52.0167 | 52.0167 | 21378.85 | 411 | 411
BR3 | U1 | 41 | 3612 | 2017-09-08 08:36 | 2017-09-08 13:57 | 0 | 456 | 411 | Switchyard system protection devices - external | FX00loss of Brown North transmission lines protective relaying. | Brown | Outage | Coal | 3 | 2017 | 9 | 5.35 | 5.35 | 2198.85 | 411 | 411
BR3 | D1 | 44 | 3414 | 2017-09-24 14:15 | 2017-09-24 14:51 | 245 | 456 | 411 | Feedwater pump local controls | 3-2 BFP trip causing boiler upset | Brown | Derate | Coal | 3 | 2017 | 9 | 0.6 | 0.27763 | 114.1066 | 190.1776 | 190
BR3 | NC | 45 | 8700 | 2017-10-16 16:42 | 2017-10-16 21:00 | 0 | 456 | 411 | CEMS Certification and Recertification | Low load RATA testing | Brown | Other | Coal | 3 | 2017 | 10 | 4.3 | 4.3 | 1767.3 | 411 | 411
BR3 | PD | 46 | 3412 | 2017-10-16 21:00 | 2017-10-17 05:26 | 300 | 456 | 411 | Feedwater pump drive - steam turbine | Repair steam leak on 3-2 BFP | Brown | Derate | Coal | 3 | 2017 | 10 | 8.4333 | 2.8851 | 1185.7711 | 140.6053 | 141
BR3 | D1 | 47 | 3412 | 2017-11-01 15:18 | 2017-11-01 15:53 | 310 | 456 | 411 | Feedwater pump drive - steam turbine | F5403-2 BFP steam leak causing pump to trip | Brown | Derate | Coal | 3 | 2017 | 11 | 0.58333 | 0.18677 | 76.7621 | 131.5921 | 132
BR3 | D1 | 48 | 3412 | 2017-11-01 15:53 | 2017-11-01 20:43 | 325 | 456 | 411 | Feedwater pump drive - steam turbine | F5403-2 BFP steam leak causing pump to trip | Brown | Derate | Coal | 3 | 2017 | 11 | 4.8333 | 1.3885 | 570.6831 | 118.0724 | 118
BR3 | PO | 50 | 891 | 2017-11-25 | 2017-12-08 12:52 | 0 | 456 | 411 | Bottom ash hoppers (including gates) | Replace spray ring header in ash hopper | Brown | Other | Coal | 3 | 2017 | 11 | 324.8667 | 324.8667 | 133520.2 | 411 | 411
BR3 | PD | 51 | 3412 | 2017-12-09 07:00 | 2017-12-09 13:50 | 315 | 456 | 411 | Feedwater pump drive - steam turbine | Repair leaking joints on 3-1 BFP LP steam supply line | Brown | Derate | Coal | 3 | 2017 | 12 | 6.8333 | 2.1129 | 868.4178 | 127.0855 | 127
BR3 | U1 | 53 | 385 | 2017-12-25 06:20 | 2017-12-25 06:37 | 0 | 456 | 411 | Igniters | Lost oil guns on unit startup | Brown | Outage | Coal | 3 | 2017 | 12 | 0.28333 | 0.28333 | 116.45 | 411 | 411
BR3 | U1 | 54 | 1180 | 2017-12-27 01:41 | 2017-12-29 21:50 | 0 | 456 | 411 | Economizer A | Economizer tube leak | Brown | Outage | Coal | 3 | 2017 | 12 | 68.15 | 68.15 | 28009.65 | 411 | 411
BR3 | D1 | 55 | 310 | 2017-12-30 15:17 | 2017-12-31 09:59 | 375 | 456 | 411 | Pulverizer mills | 3-3 mill broken vertical shaft | Brown | Derate | Coal | 3 | 2017 | 12 | 18.7 | 3.3217 | 1365.223 | 73.0066 | 73
BR3 | D1 | 56 | 30 | 2017-12-31 09:59 | 2017-12-31 10:53 | 250 | 456 | 411 | Coal conveyors and feeders | H conveyor failure to start | Brown | Derate | Coal | 3 | 2017 | 12 | 0.9 | 0.40658 | 167.1039 | 185.6711 | 186
BR3 | D1 | 57 | 310 | 2017-12-31 10:53 | 2017-12-31 18:24 | 375 | 456 | 411 | Pulverizer mills | 3-3 Pulv broken vertical shaft | Brown | Derate | Coal | 3 | 2017 | 12 | 7.5167 | 1.3352 | 548.7661 | 73.0066 | 73
BR3 | D1 | 58 | 310 | 2017-12-31 18:24 | 2018-01-01 | 360 | 456 | 411 | Pulverizer mills | 3-3 Pulv broken vertical shaft | Brown | Derate | Coal | 3 | 2017 | 12 | 5.6 | 1.1789 | 484.5474 | 86.5263 | 87
BR3 | D1 | 1 | 310 | 2018-01-01 | 2018-01-04 17:21 | 360 | 456 | 411 | Pulverizer mills | 3-3 Pulv broken vertical shaft | Brown | Derate | Coal | 3 | 2018 | 1 | 89.35 | 18.8105 | 7731.1263 | 86.5263 | 87
BR3 | U1 | 2 | 1090 | 2018-01-04 17:21 | 2018-01-05 19:29 | 0 | 456 | 411 | Other boiler tube leaks | Boiler leak in lower waterwall above ash hopper | Brown | Outage | Coal | 3 | 2018 | 1 | 26.1333 | 26.1333 | 10740.8 | 411 | 411
BR3 | D1 | 3 | 310 | 2018-01-05 19:30 | 2018-01-11 16:30 | 360 | 456 | 411 | Pulverizer mills | 3-3 Pulv broken vertical shaft | Brown | Derate | Coal | 3 | 2018 | 1 | 141 | 29.6842 | 12200.2105 | 86.5263 | 87
BR3 | U1 | 4 | 1090 | 2018-01-11 16:30 | 2018-01-15 14:57 | 0 | 456 | 411 | Other boiler tube leaks | Various leak repairs in reheat section of boiler | Brown | Outage | Coal | 3 | 2018 | 1 | 94.45 | 94.45 | 38818.95 | 411 | 411
BR3 | D1 | 5 | 310 | 2018-01-15 14:58 | 2018-01-15 16:48 | 360 | 456 | 411 | Pulverizer mills | 3-3 mill broken vertical shaft | Brown | Derate | Coal | 3 | 2018 | 1 | 1.8333 | 0.38596 | 158.6316 | 86.5263 | 87
BR3 | U1 | 6 | 1710 | 2018-01-15 16:48 | 2018-01-15 21:06 | 0 | 456 | 411 | Combustion/steam condition controls (report local controls --- burners | Boiler trip while removing oil guns. Natural draft purge required | Brown | Outage | Coal | 3 | 2018 | 1 | 4.3 | 4.3 | 1767.3 | 411 | 411
BR3 | D1 | 7 | 310 | 2018-01-15 21:07 | 2018-01-16 12:12 | 360 | 456 | 411 | Pulverizer mills | 3-3 mill broken vertical shaft | Brown | Derate | Coal | 3 | 2018 | 1 | 15.0833 | 3.1754 | 1305.1053 | 86.5263 | 87
BR3 | D1 | 8 | 1488 | 2018-01-16 12:12 | 2018-01-16 13:01 | 270 | 456 | 411 | Air heater (regenerative) | 3-2 air heater stopped rotating | Brown | Derate | Coal | 3 | 2018 | 1 | 0.81667 | 0.33311 | 136.9099 | 167.6447 | 168
BR3 | D1 | 9 | 310 | 2018-01-16 13:01 | 2018-01-16 21:58 | 360 | 456 | 411 | Pulverizer mills | 3-3 mill broken vertical shaft | Brown | Derate | Coal | 3 | 2018 | 1 | 8.95 | 1.8842 | 774.4105 | 86.5263 | 87
BR3 | PD | 10 | 3221 | 2018-01-20 21:00 | 2018-01-20 23:00 | 310 | 456 | 411 | Circulating water piping fouling | Clean 3-2 BFP CW lines | Brown | Derate | Coal | 3 | 2018 | 1 | 2 | 0.64035 | 263.1842 | 131.5921 | 132
BR3 | MO | 11 | 3340 | 2018-01-31 11:06 | 2018-02-02 02:25 | 0 | 456 | 411 | LP heater tube leaks | Repair 3A cond heater tube leak | Brown | Maintenance | Coal | 3 | 2018 | 1 | 39.3167 | 39.3167 | 16159.15 | 411 | 411
BR3 | PD | 12 | 310 | 2018-02-06 22:00 | 2018-02-07 04:00 | 360 | 456 | 411 | Pulverizer mills | Inspect 3-3 mill due to excessive vibration | Brown | Derate | Coal | 3 | 2018 | 2 | 6 | 1.2632 | 519.1579 | 86.5263 | 87
BR3 | U1 | 15 | 3621 | 2018-03-12 01:42 | 2018-03-13 05:45 | 0 | 456 | 411 | Unit auxiliaries transformer | F820Generator lockout due to 60 fl vt fuse loss grnd neut. overcurrent 86u 3-1 86u 3-2 | Brown | Outage | Coal | 3 | 2018 | 3 | 28.05 | 28.05 | 11528.55 | 411 | 411
BR3 | SF | 16 | 3621 | 2018-03-13 05:45 | 2018-03-13 07:09 | 0 | 456 | 411 | Unit auxiliaries transformer | Bad Potential transformer preventing sync | Brown | Outage | Coal | 3 | 2018 | 3 | 1.4 | 1.4 | 575.4 | 411 | 411
BR3 | D1 | 17 | 1470 | 2018-03-13 07:10 | 2018-04-14 01:17 | 375 | 456 | 411 | Induced draft fan motors and drives | F820Ground fault on 3-1 ID fan | Brown | Derate | Coal | 3 | 2018 | 3 | 762.1167 | 135.376 | 55639.5306 | 73.0066 | 73
BR3 | NC | 18 | 9656 | 2018-03-13 20:00 | 2018-03-14 02:07 | 0 | 456 | 411 | Other stack or exhaust emissions testing - fossil | RATA Testing | Brown | Other | Coal | 3 | 2018 | 3 | 6.1167 | 6.1167 | 2513.95 | 411 | 411
BR3 | NC | 19 | 9656 | 2018-03-14 20:00 | 2018-03-15 00:27 | 0 | 456 | 411 | Other stack or exhaust emissions testing - fossil | F790RATA testing | Brown | Other | Coal | 3 | 2018 | 3 | 4.45 | 4.45 | 1828.95 | 411 | 411
BR3 | D1 | 20 | 344 | 2018-03-16 13:54 | 2018-03-16 17:22 | 350 | 456 | 411 | Pulverizer inspection | F5903-2 Mill gear inspection | Brown | Derate | Coal | 3 | 2018 | 3 | 3.4667 | 0.80585 | 331.2035 | 95.5395 | 96
BR3 | D1 | 21 | 8544 | 2018-03-25 22:58 | 2018-03-25 23:13 | 295 | 456 | 411 | Mechanical failures | F130Turbine left side throttle valve closed on valve test and would not re open. | Brown | Derate | Coal | 3 | 2018 | 3 | 0.25 | 0.088268 | 36.278 | 145.1118 | 145
BR3 | NC | 22 | 9590 | 2018-03-27 | 2018-03-27 01:37 | 0 | 456 | 411 | Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | F790BR3 MATS test (300 MW) | Brown | Other | Coal | 3 | 2018 | 3 | 1.6167 | 1.6167 | 664.45 | 411 | 411
BR3 | D1 | 23 | 9270 | 2018-03-28 13:29 | 2018-03-28 18:51 | 83 | 456 | 411 | Wet coal | FW00Wet coal causes feeder trip due to serve pluggage on 3-4 mill and resulted in a MF | Brown | Derate | Coal | 3 | 2018 | 3 | 5.3667 | 4.3898 | 1804.2239 | 336.1908 | 336
GH1 | D1 | 1 | 740 | 2013-01-01 | 2013-01-10 22:14 | 460 | 520 | 477 | Boiler recirculation pumps | Load Reduction #11-3 BCWP off due to blown seal. Unit limited to 90% capacity. | Ghent | Derate | Coal | 3 | 2013 | 1 | 238.2333 | 27.4885 | 13111.9962 | 55.0385 | 55
GH1 | MO | 3 | 740 | 2013-01-10 22:14 | 2013-01-12 01:51 | 0 | 520 | 477 | Boiler recirculation pumps | F540Outage #11-3 BCWP had blown seals. Tried to remove the pump, but valves were | Ghent | Maintenance | Coal | 3 | 2013 | 1 | 27.6167 | 27.6167 | 13173.15 | 477 | 477
GH1 | SF | 4 | 9900 | 2013-01-12 01:51 | 2013-01-12 09:44 | 0 | 520 | 477 | Operator error | Outage #2The unit had been firing for start up for just under 2 hours and it was n | Ghent | Outage | Coal | 3 | 2013 | 1 | 7.8833 | 7.8833 | 3760.35 | 477 | 477
GH1 | D1 | 5 | 4499 | 2013-01-12 09:44 | 2013-01-12 10:15 | 200 | 520 | 477 | Other miscellaneous steam turbine problems | Load Reduction #21-2 ID fan VFD tripped and would not start. | Ghent | Derate | Coal | 3 | 2013 | 1 | 0.51667 | 0.31795 | 151.6615 | 293.5385 | 294
GH1 | D1 | 6 | 4499 | 2013-01-12 17:04 | 2013-02-27 22:35 | 450 | 520 | 477 | Other miscellaneous steam turbine problems | Load Reduction #3Turbine performance due to copper deposits. | Ghent | Derate | Coal | 3 | 2013 | 1 | 1109.5167 | 149.358 | 71243.7721 | 64.2115 | 64
GH1 | D1 | 7 | 9270 | 2013-01-13 17:04 | 2013-01-13 18:00 | 450 | 520 | 477 | Wet coal | Load Reduction #41-2 Feeder tripped due to wet coal. | Ghent | Derate | Coal | 3 | 2013 | 1 | 0.93333 | 0.12564 | 59.9308 | 64.2115 | 64
GH1 | PD | 8 | 4611 | 2013-01-25 22:00 | 2013-01-26 01:06 | 400 | 520 | 477 | Hydrogen coolers | F540Load Reduction #5Load was reduced to repair a LPSW leak on H2 cooler. | Ghent | Derate | Coal | 3 | 2013 | 1 | 3.1 | 0.71538 | 341.2385 | 110.0769 | 110
GH1 | D1 | 9 | 3415 | 2013-02-01 11:46 | 2013-02-01 12:40 | 325 | 520 | 477 | Feedwater pump/drive lube oil system | Load Reduction #61-1 BFP tripped due to control oil issues. | Ghent | Derate | Coal | 3 | 2013 | 2 | 0.9 | 0.3375 | 160.9875 | 178.875 | 179
GH1 | D1 | 10 | 9270 | 2013-02-07 19:26 | 2013-02-07 20:48 | 485 | 520 | 477 | Wet coal | Load Reduction #71-2 Feeder tripped due to wet coal plugging the chute. | Ghent | Derate | Coal | 3 | 2013 | 2 | 1.3667 | 0.091987 | 43.8779 | 32.1058 | 32
GH1 | PD | 11 | 344 | 2013-02-14 08:40 | 2013-02-14 14:20 | 470 | 520 | 477 | Pulverizer inspection | Load Reduction #81-5 Mill had a noise in the grinding section. Took the mill off | Ghent | Derate | Coal | 3 | 2013 | 2 | 5.6667 | 0.54487 | 259.9038 | 45.8654 | 46
GH1 | U1 | 12 | 1000 | 2013-02-27 22:35 | 2013-02-28 22:23 | 0 | 520 | 477 | Waterwall (Furnace wall) A | F380Outage #3A water wall tube leak developed on 9 1/3 floor, northeast corner of | Ghent | Outage | Coal | 3 | 2013 | 2 | 23.8 | 23.8 | 11352.6 | 477 | 477
GH1 | D1 | 13 | 4499 | 2013-03-01 05:10 | 2013-04-08 06:00 | 510 | 520 | 477 | Other miscellaneous steam turbine problems | Load Reduction #9Load reduced due to turbine degradation. | Ghent | Derate | Coal | 3 | 2013 | 3 | 912.8333 | 17.5545 | 8373.4904 | 9.1731 | 9
GH1 | D1 | 14 | 1000 | 2013-04-08 06:00 | 2013-04-10 00:57 | 390 | 520 | 477 | Waterwall (Furnace wall) A | F540Load Reduction #10U1 tube leak suspected water cooled spacer tube. | Ghent | Derate | Coal | 3 | 2013 | 4 | 42.95 | 10.7375 | 5121.7875 | 119.25 | 119
GH1 | U2 | 15 | 1075 | 2013-04-10 00:57 | 2013-04-11 21:57 | 0 | 520 | 477 | External reheater link tubing | F380Outage #4Unit had been running with tube leak in boiler that could be heard bu | Ghent | Outage | Coal | 3 | 2013 | 4 | 45 | 45 | 21465 | 477 | 477
GH1 | PO | 16 | 1060 | 2013-04-11 21:57 | 2013-04-27 13:47 | 0 | 520 | 477 | First reheater A | F590Outage #5Unit had been off line due to a reheat pendant tube leak. Afterlea | Ghent | Other | Coal | 3 | 2013 | 4 | 375.8333 | 375.8333 | 179272.5 | 477 | 477
GH1 | U1 | 17 | 4700 | 2013-04-27 14:02 | 2013-04-27 14:38 | 0 | 520 | 477 | Generator voltage control | Outage #6The unit had come on line from the Spring Planned Outage at 13:47 with a | Ghent | Outage | Coal | 3 | 2013 | 4 | 0.6 | 0.6 | 286.2 | 477 | 477
GH1 | D1 | 18 | 1850 | 2013-04-28 03:30 | 2013-04-28 09:30 | 450 | 520 | 477 | Boiler water condition (not feedwater water quality) | Load Reduction #11U1 Boiler silica was high after the Spring Outage. This caused | Ghent | Derate | Coal | 3 | 2013 | 4 | 6 | 0.80769 | 385.2692 | 64.2115 | 64
GH1 | D1 | 19 | 340 | 2013-04-30 17:40 | 2013-05-01 01:37 | 500 | 520 | 477 | Other pulverizer problems | Load Reduction #121-6 Mill was removed from service to inspect due to noise. | Ghent | Derate | Coal | 3 | 2013 | 4 | 7.95 | 0.30577 | 145.8519 | 18.3462 | 18
GH1 | D1 | 20 | 340 | 2013-05-03 03:23 | 2013-05-03 10:58 | 500 | 520 | 477 | Other pulverizer problems | Load Reduction #131-5 Mill was out of service due to noise in the grinding section | Ghent | Derate | Coal | 3 | 2013 | 5 | 7.5833 | 0.29167 | 139.125 | 18.3462 | 18
GH1 | D1 | 21 | 340 | 2013-05-07 07:39 | 2013-05-07 11:32 | 500 | 520 | 477 | Other pulverizer problems | Load Reduction #141-6 Mill pyrite scraper broke. | Ghent | Derate | Coal | 3 | 2013 | 5 | 3.8833 | 0.14936 | 71.2442 | 18.3462 | 18
GH1 | D1 | 22 | 1470 | 2013-05-09 17:34 | 2013-05-09 19:00 | 180 | 520 | 477 | Induced draft fan motors and drives | Load Reduction #151-1 ID fan trippped due to VFD control problems. | Ghent | Derate | Coal | 3 | 2013 | 5 | 1.4333 | 0.93718 | 447.0346 | 311.8846 | 312
GH1 | D1 | 23 | 1470 | 2013-05-09 19:00 | 2013-05-09 23:20 | 225 | 520 | 477 | Induced draft fan motors and drives | Load Reduction #161-1 ID fan trippped due to VFD control problems. | Ghent | Derate | Coal | 3 | 2013 | 5 | 4.3333 | 2.4583 | 1172.625 | 270.6058 | 271
GH1 | D1 | 24 | 1470 | 2013-05-10 06:15 | 2013-05-10 20:41 | 220 | 520 | 477 | Induced draft fan motors and drives | Load Reduction #171-1 ID fan VFD C phase input CT failed. | Ghent | Derate | Coal | 3 | 2013 | 5 | 14.4333 | 8.3269 | 3971.9423 | 275.1923 | 275
GH1 | D1 | 25 | 340 | 2013-05-13 22:00 | 2013-05-14 02:45 | 470 | 520 | 477 | Other pulverizer problems | Load Reduction #181-6 mill pyrite scraper broke off. | Ghent | Derate | Coal | 3 | 2013 | 5 | 4.75 | 0.45673 | 217.8606 | 45.8654 | 46
GH1 | PD | 26 | 340 | 2013-06-04 23:00 | 2013-06-05 01:00 | 470 | 520 | 477 | Other pulverizer problems | F060Load Reduction #191-1 Mill pyrite scraper broke. | Ghent | Derate | Coal | 3 | 2013 | 6 | 2 | 0.19231 | 91.7308 | 45.8654 | 46
GH1 | D1 | 27 | 1470 | 2013-06-12 14:22 | 2013-06-12 14:58 | 500 | 520 | 477 | Induced draft fan motors and drives | Load Reduction #201-1 ID fan VFD high temperature alarm. Dropped load to help red | Ghent | Derate | Coal | 3 | 2013 | 6 | 0.6 | 0.023077 | 11.0077 | 18.3462 | 18
GH1 | PD | 28 | 340 | 2013-06-20 03:00 | 2013-06-20 05:20 | 460 | 520 | 477 | Other pulverizer problems | F590Load Reduction #211-5 Mill was removed from service for west journal replaceme | Ghent | Derate | Coal | 3 | 2013 | 6 | 2.3333 | 0.26923 | 128.4231 | 55.0385 | 55
GH1 | D1 | 29 | 340 | 2013-07-20 10:23 | 2013-07-20 21:30 | 510 | 520 | 477 | Other pulverizer problems | Load Reduction #22U1 Mill bowl differentials were running high causing the mills t | Ghent | Derate | Coal | 3 | 2013 | 7 | 11.1167 | 0.21378 | 101.974 | 9.1731 | 9
GH1 | PD | 30 | 340 | 2013-07-20 22:39 | 2013-07-21 00:02 | 420 | 520 | 477 | Other pulverizer problems | Load Reduction #231-3 Mill pyrite scraper broke off. | Ghent | Derate | Coal | 3 | 2013 | 7 | 1.3833 | 0.26603 | 126.8942 | 91.7308 | 92
GH1 | D1 | 31 | 340 | 2013-07-26 04:20 | 2013-07-26 11:49 | 475 | 520 | 477 | Other pulverizer problems | Load Reduction #241-3 Mill vane wheel came loose and broke off pyrite scrapers. | Ghent | Derate | Coal | 3 | 2013 | 7 | 7.4833 | 0.6476 | 308.9034 | 41.2788 | 41
GH1 | PD | 32 | 340 | 2013-08-15 22:00 | 2013-08-16 00:50 | 475 | 520 | 477 | Other pulverizer problems | Load Reduction #251-3 Mill off for inspection due to noise in grinding section. | Ghent | Derate | Coal | 3 | 2013 | 8 | 2.8333 | 0.24519 | 116.9567 | 41.2788 | 41
GH1 | D1 | 33 | 250 | 2013-08-28 01:10 | 2013-08-28 02:00 | 470 | 520 | 477 | Pulverizer feeders | Load Reduction #261-2 Feeder plugged in throat section causing 1-2 mill to trip. | Ghent | Derate | Coal | 3 | 2013 | 8 | 0.83333 | 0.080128 | 38.2212 | 45.8654 | 46
GH1 | D1 | 34 | 1000 | 2013-09-09 06:02 | 2013-09-13 07:53 | 450 | 520 | 477 | Waterwall (Furnace wall) A | Load Reductions #27U1 Water wall tube leak. Reduced pressure to reduce loss of wa | Ghent | Derate | Coal | 3 | 2013 | 9 | 97.85 | 13.1721 | 6283.099 | 64.2115 | 64
GH1 | MO | 35 | 1000 | 2013-09-13 07:53 | 2013-09-14 18:30 | 0 | 520 | 477 | Waterwall (Furnace wall) A | F540Outage #7Unit 1 came off line at 0753 to repair a water wall tube leak. | Ghent | Maintenance | Coal | 3 | 2013 | 9 | 34.6167 | 34.6167 | 16512.15 | 477 | 477
GH1 | D1 | 37 | 340 | 2013-09-16 23:48 | 2013-09-17 08:03 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #281-2 Mill vane wheel came loose and broke pyrite scrapers off. | Ghent | Derate | Coal | 3 | 2013 | 9 | 8.25 | 0.95192 | 454.0673 | 55.0385 | 55
GH1 | D1 | 38 | 344 | 2013-09-17 12:33 | 2013-09-17 14:23 | 460 | 520 | 477 | Pulverizer inspection | Load Reduction #291-2 Mill developed noise in the grinding section. Removed the m | Ghent | Derate | Coal | 3 | 2013 | 9 | 1.8333 | 0.21154 | 100.9038 | 55.0385 | 55
GH1 | D1 | 39 | 250 | 2013-09-18 07:42 | 2013-09-18 10:54 | 460 | 520 | 477 | Pulverizer feeders | Load Reduction #301-6 Feeder head roll bearing went out causing belt to misalign. | Ghent | Derate | Coal | 3 | 2013 | 9 | 3.2 | 0.36923 | 176.1231 | 55.0385 | 55
GH1 | D1 | 40 | 340 | 2013-09-24 20:40 | 2013-09-24 23:30 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #311-2 Mill pyrite scraper broke. | Ghent | Derate | Coal | 3 | 2013 | 9 | 2.8333 | 0.32692 | 155.9423 | 55.0385 | 55
GH1 | D1 | 41 | 3815 | 2013-10-06 17:30 | 2013-10-06 18:20 | 300 | 520 | 477 | Service water strainer | Load Reduction #32U1 LPSW strainers plugged due to debris. Dropped load due to tu | Ghent | Derate | Coal | 3 | 2013 | 10 | 0.83333 | 0.35256 | 168.1731 | 201.8077 | 202
GH1 | D1 | 42 | 340 | 2013-10-14 18:32 | 2013-10-14 22:12 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #331-1 Mill north journal locked up. Removed the mill from service f | Ghent | Derate | Coal | 3 | 2013 | 10 | 3.6667 | 0.42308 | 201.8077 | 55.0385 | 55
GH1 | D1 | 43 | 340 | 2013-10-19 15:10 | 2013-10-19 17:26 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #341-6 Mill pyrite scraper broken off. | Ghent | Derate | Coal | 3 | 2013 | 10 | 2.2667 | 0.26154 | 124.7538 | 55.0385 | 55
GH1 | PD | 44 | 340 | 2013-10-22 23:25 | 2013-10-23 03:23 | 460 | 520 | 477 | Other pulverizer problems | F060Load Reduction #351-6 Mill off to repair a pyrite scraper. | Ghent | Derate | Coal | 3 | 2013 | 10 | 3.9667 | 0.45769 | 218.3192 | 55.0385 | 55
GH1 | PD | 45 | 344 | 2013-10-23 22:00 | 2013-10-24 00:48 | 460 | 520 | 477 | Pulverizer inspection | F850Load Reduction #361-2 Mill off for inspection. High exhauster vibration. | Ghent | Derate | Coal | 3 | 2013 | 10 | 2.8 | 0.32308 | 154.1077 | 55.0385 | 55
GH1 | PD | 46 | 344 | 2013-10-24 01:23 | 2013-10-24 05:13 | 460 | 520 | 477 | Pulverizer inspection | F850Load Reduction #371-3 Mill off for inspection. Journal vibration. | Ghent | Derate | Coal | 3 | 2013 | 10 | 3.8333 | 0.44231 | 210.9808 | 55.0385 | 55
GH1 | D1 | 47 | 340 | 2013-10-31 11:41 | 2013-10-31 15:17 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #381-6 Mill pyrite scraper broke off. | Ghent | Derate | Coal | 3 | 2013 | 10 | 3.6 | 0.41538 | 198.1385 | 55.0385 | 55
GH1 | D1 | 48 | 1100 | 2013-11-08 12:23 | 2013-11-10 05:36 | 200 | 520 | 477 | Waterwall (Furnace wall) B | Load Reduction #39Unit was limited to 200 MWs due to wet ash hopper slag pluggage. | Ghent | Derate | Coal | 3 | 2013 | 11 | 41.2167 | 25.3641 | 12098.6769 | 293.5385 | 294
GH1 | U1 | 49 | 1100 | 2013-11-10 05:36 | 2013-11-10 07:08 | 0 | 520 | 477 | Waterwall (Furnace wall) B | FS00Outage #9The unit had been reduced on load due to slag buildup on the east wal | Ghent | Outage | Coal | 3 | 2013 | 11 | 1.5333 | 1.5333 | 731.4 | 477 | 477
GH1 | D1 | 50 | 1100 | 2013-11-10 07:08 | 2013-11-11 03:05 | 240 | 520 | 477 | Waterwall (Furnace wall) B | Load Reduction #40Unit was limited to 240 MWs due to wet ash hopper slag pluggage. | Ghent | Derate | Coal | 3 | 2013 | 11 | 19.95 | 10.7423 | 5124.0808 | 256.8462 | 257
GH1 | U1 | 51 | 1000 | 2013-11-14 08:17 | 2013-11-16 00:31 | 0 | 520 | 477 | Waterwall (Furnace wall) A | Outage #10Unit 1 developed a very large tube leak in the upper furnace arch that w | Ghent | Outage | Coal | 3 | 2013 | 11 | 40.2333 | 40.2333 | 19191.3 | 477 | 477
GH1 | D1 | 52 | 340 | 2013-11-25 23:37 | 2013-11-26 04:46 | 440 | 520 | 477 | Other pulverizer problems | Load Reduction #411-3 Mill vanewheel and pyrite scraper broke off. | Ghent | Derate | Coal | 3 | 2013 | 11 | 5.15 | 0.79231 | 377.9308 | 73.3846 | 73
GH1 | D1 | 53 | 1470 | 2013-11-27 23:34 | 2013-11-28 06:30 | 215 | 520 | 477 | Induced draft fan motors and drives | Load Reduction #421-2 ID fan tripped due to loss of VFD drive. | Ghent | Derate | Coal | 3 | 2013 | 11 | 6.9333 | 4.0667 | 1939.8 | 279.7788 | 280
GH1 | D1 | 54 | 1470 | 2013-11-28 22:22 | 2013-11-29 02:37 | 215 | 520 | 477 | Induced draft fan motors and drives | Load Reduction #431-2 ID fan tripped due to loss of coolant level on VFD drive. 1 | Ghent | Derate | Coal | 3 | 2013 | 11 | 4.25 | 2.4928 | 1189.0601 | 279.7788 | 280
GH1 | PD | 55 | 250 | 2013-12-04 10:00 | 2013-12-04 14:13 | 460 | 520 | 477 | Pulverizer feeders | Load Reduction #441-4 Feeder belt needs replaced. | Ghent | Derate | Coal | 3 | 2013 | 12 | 4.2167 | 0.48654 | 232.0788 | 55.0385 | 55
GH1 | D1 | 56 | 340 | 2013-12-08 07:35 | 2013-12-08 12:54 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #451-6 Mill pyrite scrapers broke off. | Ghent | Derate | Coal | 3 | 2013 | 12 | 5.3167 | 0.61346 | 292.6212 | 55.0385 | 55
GH1 | D1 | 57 | 30 | 2013-12-15 05:52 | 2013-12-15 12:00 | 400 | 520 | 477 | Coal conveyors and feeders | Load Reduction #461J Conveyor motor went out, couldn't keep silos full. Dropped l | Ghent | Derate | Coal | 3 | 2013 | 12 | 6.1333 | 1.4154 | 675.1385 | 110.0769 | 110
GH1 | D1 | 58 | 9650 | 2013-12-16 18:33 | 2013-12-16 22:23 | 400 | 520 | 477 | Other stack or exhaust emissions (fossil) | Load Reduction #47H2SO4 came in alarm. Had to drop load to clear. | Ghent | Derate | Coal | 3 | 2013 | 12 | 3.8333 | 0.88462 | 421.9615 | 110.0769 | 110
GH1 | U1 | 59 | 4430 | 2013-12-28 21:17 | 2013-12-30 08:05 | 0 | 520 | 477 | Gland seal system | Outage #11Gland Steam Exhauster developed a tube leak which requires a unit outage | Ghent | Outage | Coal | 3 | 2013 | 12 | 34.8 | 34.8 | 16599.6 | 477 | 477
GH1 | D1 | 1 | 9270 | 2014-01-08 07:48 | 2014-01-08 09:10 | 460 | 520 | 477 | Wet coal | Load Reduction #11-6 Feeder plugged due to wet coal and this tripped the mill. | Ghent | Derate | Coal | 3 | 2014 | 1 | 1.3667 | 0.15769 | 75.2192 | 55.0385 | 55
GH1 | PD | 2 | 344 | 2014-01-14 23:37 | 2014-01-15 02:30 | 460 | 520 | 477 | Pulverizer inspection | Load Reduction #21-6 Mill off to inspect and clean air flow transmitters. | Ghent | Derate | Coal | 3 | 2014 | 1 | 2.8833 | 0.33269 | 158.6942 | 55.0385 | 55
GH1 | PD | 3 | 340 | 2014-01-16 21:57 | 2014-01-17 00:49 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #31-1 Mill journal replacement. | Ghent | Derate | Coal | 3 | 2014 | 1 | 2.8667 | 0.33077 | 157.7769 | 55.0385 | 55
GH1 | D1 | 4 | 344 | 2014-01-27 06:00 | 2014-01-27 11:33 | 460 | 520 | 477 | Pulverizer inspection | Load Reduction #41-6 Mill off to inspect grinding section. | Ghent | Derate | Coal | 3 | 2014 | 1 | 5.55 | 0.64038 | 305.4635 | 55.0385 | 55
GH1 | D1 | 5 | 250 | 2014-01-28 21:25 | 2014-01-29 04:05 | 460 | 520 | 477 | Pulverizer feeders | Load Reduction #51-4 Feeder belt was torn when cleanout conveyor failed. | Ghent | Derate | Coal | 3 | 2014 | 1 | 6.6667 | 0.76923 | 366.9231 | 55.0385 | 55
GH1 | MO | 6 | 1060 | 2014-02-01 15:04 | 2014-02-03 01:27 | 0 | 520 | 477 | First reheater A | F540Outage #1Unit 1 had been running with a tube leak, located around IK #6, for s | Ghent | Maintenance | Coal | 3 | 2014 | 2 | 34.3833 | 34.3833 | 16400.85 | 477 | 477
GH1 | D1 | 7 | 250 | 2014-02-07 12:35 | 2014-02-07 13:45 | 460 | 520 | 477 | Pulverizer feeders | Load Reduction #6Metal hung in 1-4 mill feeder. | Ghent | Derate | Coal | 3 | 2014 | 2 | 1.1667 | 0.13462 | 64.2115 | 55.0385 | 55
GH1 | D1 | 8 | 250 | 2014-02-09 16:20 | 2014-02-09 19:43 | 450 | 520 | 477 | Pulverizer feeders | Load Reduction #71-4 Feeder belt bound up. | Ghent | Derate | Coal | 3 | 2014 | 2 | 3.3833 | 0.45545 | 217.249 | 64.2115 | 64
GH1 | PD | 9 | 250 | 2014-02-10 09:00 | 2014-02-10 15:33 | 450 | 520 | 477 | Pulverizer feeders | Load Reduction #81-4 Mill off to replace feeder discharge pipe pluggage detector. | Ghent | Derate | Coal | 3 | 2014 | 2 | 6.55 | 0.88173 | 420.5856 | 64.2115 | 64
GH1 | D1 | 10 | 9650 | 2014-02-13 07:23 | 2014-02-13 09:08 | 490 | 520 | 477 | Other stack or exhaust emissions (fossil) | Load Reduction #9U1 H2SO4 was high. Dropped load to keep it in compliance. | Ghent | Derate | Coal | 3 | 2014 | 2 | 1.75 | 0.10096 | 48.1587 | 27.5192 | 28
GH1 | D1 | 11 | 344 | 2014-02-21 08:30 | 2014-02-21 12:30 | 450 | 520 | 477 | Pulverizer inspection | Load Reduction #101-6 Mill off to inspect grinding section. | Ghent | Derate | Coal | 3 | 2014 | 2 | 4 | 0.53846 | 256.8462 | 64.2115 | 64
GH1 | D1 | 13 | 344 | 2014-02-21 22:00 | 2014-02-22 01:04 | 460 | 520 | 477 | Pulverizer inspection | Load Reduction #111-2 Mill off to inspect grinding section. | Ghent | Derate | Coal | 3 | 2014 | 2 | 3.0667 | 0.35385 | 168.7846 | 55.0385 | 55
GH1 | MO | 12 | 1060 | 2014-02-22 14:49 | 2014-02-23 11:03 | 0 | 520 | 477 | First reheater A | F370Outage #2A leak was detected in Reheater pendant section of the boiler. Dispa | Ghent | Maintenance | Coal | 3 | 2014 | 2 | 20.2333 | 20.2333 | 9651.3 | 477 | 477
GH1 | PD | 14 | 340 | 2014-02-24 13:42 | 2014-02-24 16:59 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #121-1 Mill off to inspect grinding section. | Ghent | Derate | Coal | 3 | 2014 | 2 | 3.2833 | 0.37885 | 180.7096 | 55.0385 | 55
GH1 | D1 | 15 | 320 | 2014-02-25 11:17 | 2014-02-25 12:57 | 460 | 520 | 477 | Foreign object in Pulverizers mill | Load Reduction #131-3 Mill had noise in the pyrite section. Removed the mill to i | Ghent | Derate | Coal | 3 | 2014 | 2 | 1.6667 | 0.19231 | 91.7308 | 55.0385 | 55
GH1 | D1 | 16 | 250 | 2014-03-03 16:05 | 2014-03-03 22:16 | 460 | 520 | 477 | Pulverizer feeders | Load Reduction #141-3 Feeder belt failed. Removed from service to replace belt. | Ghent | Derate | Coal | 3 | 2014 | 3 | 6.1833 | 0.71346 | 340.3212 | 55.0385 | 55
GH1 | U1 | 17 | 1000 | 2014-03-05 00:42 | 2014-03-05 23:00 | 0 | 520 | 477 | Waterwall (Furnace wall) A | Outage #3Water water tube leak blew out on the upper slope of the boiler about 15 | Ghent | Outage | Coal | 3 | 2014 | 3 | 22.3 | 22.3 | 10637.1 | 477 | 477
GH1 | D1 | 18 | 346 | 2014-03-17 07:42 | 2014-03-17 12:14 | 460 | 520 | 477 | Pulverizer pyrite removal system | Load Reduction #151-3 Mill out of service to inspect pyrite section. | Ghent | Derate | Coal | 3 | 2014 | 3 | 4.5333 | 0.52308 | 249.5077 | 55.0385 | 55
GH1 | PO | 19 | 1812 | 2014-03-21 21:30 | 2014-04-13 17:56 | 0 | 520 | 477 | Boiler Inspections - scheduled or routine | F590Outage #4Unit 1 scheduled for a Planned Spring Outage. Removed the unit from | Ghent | Other | Coal | 3 | 2014 | 3 | 548.4333 | 548.4333 | 261602.7 | 477 | 477
GH1 | D1 | 20 | 1850 | 2014-04-14 05:56 | 2014-04-15 05:49 | 430 | 520 | 477 | Boiler water condition (not feedwater water quality) | Load Reduction #16U1 Silica derate due to start up. | Ghent | Derate | Coal | 3 | 2014 | 4 | 23.8833 | 4.1337 | 1971.7529 | 82.5577 | 83
GH1 | D1 | 21 | 1850 | 2014-04-15 21:34 | 2014-04-16 00:58 | 506 | 520 | 477 | Boiler water condition (not feedwater water quality) | Load Reduction #17U1 Silica derate due to start up. | Ghent | Derate | Coal | 3 | 2014 | 4 | 3.4 | 0.091538 | 43.6638 | 12.8423 | 13
GH1 | PD | 22 | 250 | 2014-04-21 03:11 | 2014-04-21 04:06 | 480 | 520 | 477 | Pulverizer feeders | Load Reduction #181-4 Mill feeder gate inspection to check for obstruction. | Ghent | Derate | Coal | 3 | 2014 | 4 | 0.91667 | 0.070513 | 33.6346 | 36.6923 | 37
GH1 | D1 | 23 | 250 | 2014-04-21 17:26 | 2014-04-21 22:48 | 490 | 520 | 477 | Pulverizer feeders | Load Reduction #191-4 Feeder breaker keeps tripping out. | Ghent | Derate | Coal | 3 | 2014 | 4 | 5.3667 | 0.30962 | 147.6865 | 27.5192 | 28
GH1 | PD | 24 | 8590 | 2014-04-28 22:30 | 2014-04-29 05:51 | 400 | 520 | 477 | Other precipitator problems | Load Reduction #20Precipitator electrical work due to TR sets shorting out during | Ghent | Derate | Coal | 3 | 2014 | 4 | 7.35 | 1.6962 | 809.0654 | 110.0769 | 110
GH1 | D1 | 25 | 9650 | 2014-05-06 14:20 | 2014-05-06 20:25 | 490 | 520 | 477 | Other stack or exhaust emissions (fossil) | Load Reduction #21Multiple injection probes plugged. Reduced load to keep H2SO4 w | Ghent | Derate | Coal | 3 | 2014 | 5 | 6.0833 | 0.35096 | 167.4087 | 27.5192 | 28
GH1 | D1 | 26 | 9650 | 2014-05-07 06:58 | 2014-05-07 08:01 | 490 | 520 | 477 | Other stack or exhaust emissions (fossil) | Load Reduction #22Multiple injection probes plugged. Reduced load to keep H2SO4 w | Ghent | Derate | Coal | 3 | 2014 | 5 | 1.05 | 0.060577 | 28.8952 | 27.5192 | 28
GH1 | D1 | 27 | 340 | 2014-05-07 20:00 | 2014-05-08 06:39 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #231-1 Mill gear box vertical shaft broke. Removed the mill from s | Ghent | Derate | Coal | 3 | 2014 | 5 | 10.65 | 1.2288 | 586.1596 | 55.0385 | 55
GH1 | D1 | 28 | 340 | 2014-05-08 06:39 | 2014-05-16 06:39 | 500 | 520 | 477 | Other pulverizer problems | Load Reduction #241-1 Mill gear box vertical shaft broke. Removed the mill from s | Ghent | Derate | Coal | 3 | 2014 | 5 | 192 | 7.3846 | 3522.4615 | 18.3462 | 18
GH1 | MO | 29 | 1000 | 2014-05-16 23:03 | 2014-05-17 22:01 | 0 | 520 | 477 | Waterwall (Furnace wall) A | F910Outage #5Unit 1 was running with a small water wall boiler tube leak. Loading | Ghent | Maintenance | Coal | 3 | 2014 | 5 | 22.9667 | 22.9667 | 10955.1 | 477 | 477
GH1 | D1 | 30 | 1850 | 2014-05-18 11:35 | 2014-05-18 12:24 | 475 | 520 | 477 | Boiler water condition (not feedwater water quality) | Load Reduction #25Boiler drum pressure was reduced due to silica. | Ghent | Derate | Coal | 3 | 2014 | 5 | 0.81667 | 0.070673 | 33.7111 | 41.2788 | 41
GH1 | D1 | 31 | 9650 | 2014-06-21 12:59 | 2014-06-21 14:02 | 490 | 520 | 477 | Other stack or exhaust emissions (fossil) | Load Reduction #26GH1 H2SO4 was high. Dropped load to keep within the set limits. | Ghent | Derate | Coal | 3 | 2014 | 6 | 1.05 | 0.060577 | 28.8952 | 27.5192 | 28
GH1 | D1 | 32 | 3631 | 2014-07-11 15:05 | 2014-07-11 16:31 | 455 | 520 | 477 | 480-volt circuit breakers | Load Reduction #271-1 Mill was tripped due to loss of electrical feed 1E causing a | Ghent | Derate | Coal | 3 | 2014 | 7 | 1.4333 | 0.17917 | 85.4625 | 59.625 | 60
GH1 | D1 | 33 | 250 | 2014-07-20 13:53 | 2014-07-20 14:20 | 500 | 520 | 477 | Pulverizer feeders | Load Reduction #281-1 Feeder tripped the overloads on the breaker. | Ghent | Derate | Coal | 3 | 2014 | 7 | 0.45 | 0.017308 | 8.2558 | 18.3462 | 18
GH1 | D1 | 34 | 250 | 2014-07-20 15:01 | 2014-07-20 16:14 | 500 | 520 | 477 | Pulverizer feeders | Load Reduction #291-1 Feeder tripped the overloads on the breaker. | Ghent | Derate | Coal | 3 | 2014 | 7 | 1.2167 | 0.046795 | 22.3212 | 18.3462 | 18
GH1 | D1 | 35 | 346 | 2014-07-31 13:52 | 2014-07-31 15:22 | 500 | 520 | 477 | Pulverizer pyrite removal system | Load Reduction #301-4 Mill was off to inspect pyrite section. | Ghent | Derate | Coal | 3 | 2014 | 7 | 1.5 | 0.057692 | 27.5192 | 18.3462 | 18
GH1 | D1 | 36 | 320 | 2014-08-02 21:15 | 2014-08-03 07:44 | 460 | 520 | 477 | Foreign object in Pulverizers mill | Load Reduction #311-4 Mill had a grinding issue. Took the mill off to inspect. | Ghent | Derate | Coal | 3 | 2014 | 8 | 10.4833 | 1.2096 | 576.9865 | 55.0385 | 55
GH1 | D1 | 37 | 346 | 2014-08-13 22:30 | 2014-08-14 00:30 | 450 | 520 | 477 | Pulverizer pyrite removal system | Load Reduction #321-2 Mill had a noise in the pyrite section. Took the mill off t | Ghent | Derate | Coal | 3 | 2014 | 8 | 2 | 0.26923 | 128.4231 | 64.2115 | 64
GH1 | D1 | 38 | 340 | 2014-08-15 12:22 | 2014-08-15 15:54 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #331-3 Mill was off for inspection due to noise in the grinding sec | Ghent | Derate | Coal | 3 | 2014 | 8 | 3.5333 | 0.40769 | 194.4692 | 55.0385 | 55
GH1 | PD | 39 | 344 | 2014-08-20 22:00 | 2014-08-20 23:32 | 500 | 520 | 477 | Pulverizer inspection | Load Reduction #341-2 Mill off to inspect pyrite section. | Ghent | Derate | Coal | 3 | 2014 | 8 | 1.5333 | 0.058974 | 28.1308 | 18.3462 | 18
GH1 | D1 | 40 | 340 | 2014-08-23 18:16 | 2014-08-23 22:45 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #351-3 Mill off for noise in the pyrite section of the mill. | Ghent | Derate | Coal | 3 | 2014 | 8 | 4.4833 | 0.51731 | 246.7558 | 55.0385 | 55
GH1 | D1 | 41 | 9650 | 2014-08-24 19:42 | 2014-08-24 20:06 | 500 | 520 | 477 | Other stack or exhaust emissions (fossil) | Load Reduction #36Unit 1 was derated due to H2SO4 injection system not working pro | Ghent | Derate | Coal | 3 | 2014 | 8 | 0.4 | 0.015385 | 7.3385 | 18.3462 | 18
GH1 | D1 | 42 | 1480 | 2014-08-26 10:28 | 2014-08-26 13:30 | 500 | 520 | 477 | Other induced draft fan problems | Load Reduction #371-2 ID fan inlet vanes stuck at 75% and wouldn't move. | Ghent | Derate | Coal | 3 | 2014 | 8 | 3.0333 | 0.11667 | 55.65 | 18.3462 | 18
GH1 | D1 | 43 | 1190 | 2014-08-26 13:30 | 2014-08-26 21:00 | 450 | 520 | 477 | Other tube slagging or fouling | Load Reduction #38Boiler slag was very heavy causing air flow issues. | Ghent | Derate | Coal | 3 | 2014 | 8 | 7.5 | 1.0096 | 481.5865 | 64.2115 | 64
GH1 | D1 | 44 | 1190 | 2014-08-26 21:00 | 2014-08-27 01:30 | 200 | 520 | 477 | Other tube slagging or fouling | Load Reduction #39Boiler slag was very heavy causing air flow issues. | Ghent | Derate | Coal | 3 | 2014 | 8 | 4.5 | 2.7692 | 1320.9231 | 293.5385 | 294
GH1 | D1 | 45 | 320 | 2014-09-01 15:48 | 2014-09-01 17:15 | 460 | 520 | 477 | Foreign object in Pulverizers mill | Load Reduction #401-3 Mill off to inspect for noise in grinding section. | Ghent | Derate | Coal | 3 | 2014 | 9 | 1.45 | 0.16731 | 79.8058 | 55.0385 | 55
GH1 | D1 | 46 | 9650 | 2014-09-04 17:15 | 2014-09-04 20:04 | 200 | 520 | 477 | Other stack or exhaust emissions (fossil) | Load Reduction #41Dropped load to keep H2S04 within limit. Ethernet switch failed | Ghent | Derate | Coal | 3 | 2014 | 9 | 2.8167 | 1.7333 | 826.8 | 293.5385 | 294
GH1 | PD | 47 | 250 | 2014-09-12 12:12 | 2014-09-12 14:03 | 500 | 520 | 477 | Pulverizer feeders | Load Reduction #421-4 Feeder head roll lagging was coming loose. | Ghent | Derate | Coal | 3 | 2014 | 9 | 1.85 | 0.071154 | 33.9404 | 18.3462 | 18
GH1 | D1 | 48 | 344 | 2014-09-17 12:35 | 2014-09-17 15:30 | 420 | 520 | 477 | Pulverizer inspection | Load Reduction #431-6 Mill off to inspect pyrite section of mill. | Ghent | Derate | Coal | 3 | 2014 | 9 | 2.9167 | 0.5609 | 267.5481 | 91.7308 | 92
GH1 | D1 | 49 | 9210 | 2014-09-17 15:30 | 2014-09-17 23:03 | 450 | 520 | 477 | Low grindability | Load Reduction #44The unit was derated due to mill grinding and air flow issues du | Ghent | Derate | Coal | 3 | 2014 | 9 | 7.55 | 1.0163 | 484.7971 | 64.2115 | 64
GH1 | D1 | 50 | 250 | 2014-09-21 19:27 | 2014-09-21 20:41 | 480 | 520 | 477 | Pulverizer feeders | Load Reduction #451-5 Feeder was tripping out. Found a ceramic tile wedged under | Ghent | Derate | Coal | 3 | 2014 | 9 | 1.2333 | 0.094872 | 45.2538 | 36.6923 | 37
GH1 | D1 | 51 | 253 | 2014-09-30 05:06 | 2014-09-30 07:30 | 460 | 520 | 477 | Pulverizer feeder motor | Load Reduction #461-1 Feeder tripped with the VFD module failed. | Ghent | Derate | Coal | 3 | 2014 | 9 | 2.4 | 0.27692 | 132.0923 | 55.0385 | 55
GH1 | D1 | 52 | 250 | 2014-10-04 11:28 | 2014-10-04 13:28 | 485 | 520 | 477 | Pulverizer feeders | Load Reduction #471-1 Feeder tripped and wouldn't restart. | Ghent | Derate | Coal | 3 | 2014 | 10 | 2 | 0.13462 | 64.2115 | 32.1058 | 32
GH1 | D1 | 53 | 340 | 2014-10-05 16:18 | 2014-10-05 18:33 | 480 | 520 | 477 | Other pulverizer problems | Load Reduction #481-2 Mill pyrite scraper broke off. | Ghent | Derate | Coal | 3 | 2014 | 10 | 2.25 | 0.17308 | 82.5577 | 36.6923 | 37
GH1 | PD | 54 | 250 | 2014-10-11 22:00 | 2014-10-11 23:26 | 460 | 520 | 477 | Pulverizer feeders | Load Reduction #49Unit 1 was derated to 460 MWs to replace 1-2 feeder belt. Belt | Ghent | Derate | Coal | 3 | 2014 | 10 | 1.4333 | 0.16538 | 78.8885 | 55.0385 | 55
GH1 | PD | 55 | 344 | 2014-10-11 23:26 | 2014-10-12 01:25 | 460 | 520 | 477 | Pulverizer inspection | Load Reduction #50Unit 1 was derated to 460 MWs to inspect 1-4 mill grinding secti | Ghent | Derate | Coal | 3 | 2014 | 10 | 1.9833 | 0.22885 | 109.1596 | 55.0385 | 55
GH1 | D1 | 56 | 340 | 2014-10-14 05:15 | 2014-10-14 06:11 | 450 | 520 | 477 | Other pulverizer problems | Load Reduction #511-4 Mill out of service to hot set rolls on the mill due to high | Ghent | Derate | Coal | 3 | 2014 | 10 | 0.93333 | 0.12564 | 59.9308 | 64.2115 | 64
GH1 | PD | 57 | 340 | 2014-10-14 22:00 | 2014-10-14 23:48 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #521-4 Mill out of service to trim the vane wheel due to high bowl | Ghent | Derate | Coal | 3 | 2014 | 10 | 1.8 | 0.20769 | 99.0692 | 55.0385 | 55
GH1 | PD | 58 | 340 | 2014-10-23 00:53 | 2014-10-23 01:47 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #531-6 Mill off to install a new type of scraper (spring loaded). | Ghent | Derate | Coal | 3 | 2014 | 10 | 0.9 | 0.10385 | 49.5346 | 55.0385 | 55
GH1 | D1 | 59 | 9650 | 2014-10-29 19:46 | 2014-10-29 20:25 | 450 | 520 | 477 | Other stack or exhaust emissions (fossil) | Load Reduction #54Unit 1 was limited due to H2SO4 running high. Load was reduced | Ghent | Derate | Coal | 3 | 2014 | 10 | 0.65 | 0.0875 | 41.7375 | 64.2115 | 64
GH1 | D1 | 60 | 1160 | 2014-10-31 03:44 | 2014-11-02 04:00 | 338 | 520 | 477 | First reheater B | Load Reduction #55U1 Boiler was plugged up with slag. Cycled load to thermal shoc | Ghent | Derate | Coal | 3 | 2014 | 10 | 48.2667 | 16.8933 | 8058.12 | 166.95 | 167
GH1 | D1 | 61 | 340 | 2014-11-06 03:19 | 2014-11-06 11:35 | 450 | 520 | 477 | Other pulverizer problems | Load Reduction #561-3 Mill was off to inspect pyrite section. Found the vane whee | Ghent | Derate | Coal | 3 | 2014 | 11 | 8.2667 | 1.1128 | 530.8154 | 64.2115 | 64
GH1 | D1 | 62 | 344 | 2014-11-13 23:00 | 2014-11-14 | 460 | 520 | 477 | Pulverizer inspection | Load Reduction #571-4 Mill off to inspect the pyrite section. | Ghent | Derate | Coal | 3 | 2014 | 11 | 1 | 0.11538 | 55.0385 | 55.0385 | 55
GH1 | PD | 63 | 1100 | 2014-11-14 | 2014-11-14 03:24 | 200 | 520 | 477 | Waterwall (Furnace wall) B | Load Reduction #58U1 Boiler slag was heavy. Dropped load to deslag. | Ghent | Derate | Coal | 3 | 2014 | 11 | 3.4 | 2.0923 | 998.0308 | 293.5385 | 294
GH1 | PD | 64 | 1100 | 2014-11-15 01:00 | 2014-11-15 04:06 | 200 | 520 | 477 | Waterwall (Furnace wall) B | Load Reduction #59Unit 1 was brought down to clean up slag on the RH pendants. | Ghent | Derate | Coal | 3 | 2014 | 11 | 3.1 | 1.9077 | 909.9692 | 293.5385 | 294
GH1 | D1 | 65 | 1100 | 2014-11-15 06:45 | 2014-11-20 06:25 | 317 | 520 | 477 | Waterwall (Furnace wall) B | Load Reduction #60Unit 1 is being cycled up and down to clean up slag on the RH pe | Ghent | Derate | Coal | 3 | 2014 | 11 | 119.6667 | 46.716 | 22283.5442 | 186.2135 | 186
GH1 | D1 | 66 | 300 | 2014-11-20 06:25 | 2014-11-29 18:29 | 460 | 520 | 477 | Pulverizer motors and drives | Load Reduction #611-6 Mill motor making noise. Shipping motor out for inspection. | Ghent | Derate | Coal | 3 | 2014 | 11 | 228.0667 | 26.3154 | 12552.4385 | 55.0385 | 55
GH1 | D1 | 67 | 1100 | 2014-11-20 09:30 | 2014-11-23 05:00 | 317 | 520 | 477 | Waterwall (Furnace wall) B | Load Reduction #62The unit is being cycled up and down to clean up slag on the RH | Ghent | Derate | Coal | 3 | 2014 | 11 | 67.5 | 26.351 | 12569.4087 | 186.2135 | 186
GH1 | D1 | 68 | 250 | 2014-11-25 00:50 | 2014-11-25 02:10 | 100 | 520 | 477 | Pulverizer feeders | Load Reduction #631-1 and 1-3 Feeders tripped during deslag of boiler. This cause | Ghent | Derate | Coal | 3 | 2014 | 11 | 1.3333 | 1.0769 | 513.6923 | 385.2692 | 385
GH1 | PD | 69 | 1100 | 2014-11-26 | 2014-11-26 04:00 | 190 | 520 | 477 | Waterwall (Furnace wall) B | FS00Load Reduction #64Boiler slag was heavy. The unit was scheduled for a deslag. | Ghent | Derate | Coal | 3 | 2014 | 11 | 4 | 2.5385 | 1210.8462 | 302.7115 | 303
GH1 | D1 | 70 | 1100 | 2014-11-29 10:25 | 2014-11-29 11:00 | 400 | 520 | 477 | Waterwall (Furnace wall) B | Load Reduction #65Slag was building up on nose arch. Dropped load to get a better | Ghent | Derate | Coal | 3 | 2014 | 11 | 0.58333 | 0.13462 | 64.2115 | 110.0769 | 110
GH1 | D1 | 71 | 340 | 2014-11-29 11:40 | 2014-11-29 17:39 | 350 | 520 | 477 | Other pulverizer problems | Load Reduction #661-4 Mill off to inspect grinding section. | Ghent | Derate | Coal | 3 | 2014 | 11 | 5.9833 | 1.9561 | 933.0548 | 155.9423 | 156
GH1 | D1 | 72 | 3631 | 2014-12-01 13:16 | 2014-12-01 14:40 | 477 | 520 | 477 | 480-volt circuit breakers | Load Reduction #671-4 Feeder tripped. Investigated and found cooling fan bad in b | Ghent | Derate | Coal | 3 | 2014 | 12 | 1.4 | 0.11577 | 55.2219 | 39.4442 | 39
GH1 | PD | 73 | 1100 | 2014-12-02 23:00 | 2014-12-03 04:00 | 190 | 520 | 477 | Waterwall (Furnace wall) B | Load Reduction #68Unit 1 dropped load for a planned deslag due to slag build up on | Ghent | Derate | Coal | 3 | 2014 | 12 | 5 | 3.1731 | 1513.5577 | 302.7115 | 303
GH1 | D1 | 74 | 250 | 2014-12-03 10:23 | 2014-12-03 11:22 | 480 | 520 | 477 | Pulverizer feeders | Load Reduction #691-4 Feeder tripped when the power supply got hot. | Ghent | Derate | Coal | 3 | 2014 | 12 | 0.98333 | 0.075641 | 36.0808 | 36.6923 | 37
GH1 | MO | 75 | 1000 | 2014-12-05 23:29 | 2014-12-09 08:02 | 0 | 520 | 477 | Waterwall (Furnace wall) A | F540Outage #6Unit 1 had been running with two water wall tube leaks. Removed the | Ghent | Maintenance | Coal | 3 | 2014 | 12 | 80.55 | 80.55 | 38422.35 | 477 | 477
GH1 | D1 | 76 | 1850 | 2014-12-09 20:20 | 2014-12-09 23:46 | 390 | 520 | 477 | Boiler water condition (not feedwater water quality) | Load Reduction #70Unit 1 was derated due to boiler chemistry; silica was high. | Ghent | Derate | Coal | 3 | 2014 | 12 | 3.4333 | 0.85833 | 409.425 | 119.25 | 119
GH1 | U1 | 77 | 1060 | 2014-12-09 23:46 | 2014-12-11 03:07 | 0 | 520 | 477 | First reheater A | Outage #7Reheat pendant tube ruptured a few feet out from the east side of the boi | Ghent | Outage | Coal | 3 | 2014 | 12 | 27.35 | 27.35 | 13045.95 | 477 | 477
GH1 | D1 | 78 | 1850 | 2014-12-11 15:07 | 2014-12-12 02:23 | 447 | 520 | 477 | Boiler water condition (not feedwater water quality) | Load Reduction #71High boiler drum silica after start up. | Ghent | Derate | Coal | 3 | 2014 | 12 | 11.2667 | 1.5817 | 754.455 | 66.9635 | 67
GH1 | D1 | 1 | 340 | 2015-01-01 23:56 | 2015-01-02 04:25 | 440 | 520 | 477 | Other pulverizer problems | Load Reduction #1Removed 1-3 Mill from service to secure a vane wheel segment. | Ghent | Derate | Coal | 3 | 2015 | 1 | 4.4833 | 0.68974 | 329.0077 | 73.3846 | 73
GH1 | D1 | 2 | 340 | 2015-01-02 04:25 | 2015-01-02 05:07 | 440 | 520 | 477 | Other pulverizer problems | Load Reduction #2Removed 1-2 Mill from service to inspect exhauster for vibration | Ghent | Derate | Coal | 3 | 2015 | 1 | 0.7 | 0.10769 | 51.3692 | 73.3846 | 73
GH1 | D1 | 3 | 340 | 2015-01-05 02:40 | 2015-01-05 06:45 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #31-3 Mill was off to inspect the pyrite section for noise. Found | Ghent | Derate | Coal | 3 | 2015 | 1 | 4.0833 | 0.47115 | 224.7404 | 55.0385 | 55
GH1 | D1 | 4 | 340 | 2015-01-08 20:09 | 2015-01-08 23:00 | 450 | 520 | 477 | Other pulverizer problems | Load Reduction #41-4 Mill off to inspect noise in pyrite section. Found vane whee | Ghent | Derate | Coal | 3 | 2015 | 1 | 2.85 | 0.38365 | 183.0029 | 64.2115 | 64
GH1 | D3 | 5 | 9650 | 2015-01-14 00:01 | 2015-01-14 01:15 | 200 | 520 | 477 | Other stack or exhaust emissions (fossil) | Load reduction #5GH1 load reduced to 200 MWs to switch the DSI outlet injection from | Ghent | Derate | Coal | 3 | 2015 | 1 | 1.2333 | 0.75897 | 362.0308 | 293.5385 | 294
GH1 | D1 | 6 | 340 | 2015-01-16 00:05 | 2015-01-16 04:15 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #61-3 mill has noise in pyrite section, removed mill to inspect. | Ghent | Derate | Coal | 3 | 2015 | 1 | 4.1667 | 0.48077 | 229.3269 | 55.0385 | 55
GH1 | D1 | 7 | 320 | 2015-01-16 14:29 | 2015-01-16 18:00 | 430 | 520 | 477 | Foreign object in Pulverizers mill | Load Reduction #71-3 Mill off to inspect noise in the grinding section. The vanew | Ghent | Derate | Coal | 3 | 2015 | 1 | 3.5167 | 0.60865 | 290.3279 | 82.5577 | 83
GH1 | D1 | 8 | 340 | 2015-01-18 16:12 | 2015-01-18 20:36 | 440 | 520 | 477 | Other pulverizer problems | Load Reduction #81-3 Mill off to inspect noise in the grinding section. Found van | Ghent | Derate | Coal | 3 | 2015 | 1 | 4.4 | 0.67692 | 322.8923 | 73.3846 | 73
GH1 | D1 | 9 | 250 | 2015-01-20 12:00 | 2015-01-20 12:51 | 365 | 520 | 477 | Pulverizer feeders | Load Reduction #91-2 and 1-4 Feeders tripped due to 005 error code (high voltage) | Ghent | Derate | Coal | 3 | 2015 | 1 | 0.85 | 0.25337 | 120.8553 | 142.1827 | 142
GH1 | D1 | 10 | 250 | 2015-01-22 03:32 | 2015-01-22 11:57 | 440 | 520 | 477 | Pulverizer feeders | Load Reduction #101-1 Feeder belt came apart at the splice. | Ghent | Derate | Coal | 3 | 2015 | 1 | 8.4167 | 1.2949 | 617.6538 | 73.3846 | 73
GH1 | PD | 11 | 340 | 2015-01-22 22:00 | 2015-01-23 03:04 | 440 | 520 | 477 | Other pulverizer problems | Load Reduction #111-3 Mill was off to replace hardware in the vanewheel sections. | Ghent | Derate | Coal | 3 | 2015 | 1 | 5.0667 | 0.77949 | 371.8154 | 73.3846 | 73
GH1 | U1 | 12 | 1040 | 2015-02-10 09:28 | 2015-02-11 10:07 | 0 | 520 | 477 | First superheater B | Outage #1Boiler had been running several weeks with tube leak in upper furnace and | Ghent | Outage | Coal | 3 | 2015 | 2 | 24.65 | 24.65 | 11758.05 | 477 | 477
GH1 | D1 | 13 | 1850 | 2015-02-11 18:24 | 2015-02-11 20:50 | 470 | 520 | 477 | Boiler water condition (not feedwater water quality) | Load Reduction #12GH! was derated due to boiler chemistry after start-up (silica); | Ghent | Derate | Coal | 3 | 2015 | 2 | 2.4333 | 0.23397 | 111.6058 | 45.8654 | 46
GH1 | PO | 14 | 4400 | 2015-02-28 15:25 | 2015-05-06 09:33 | 0 | 520 | 477 | Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | F590Outage #2Removed the unit form service for the Planned Spring Outage. Major w | Ghent | Other | Coal | 3 | 2015 | 2 | 1602.1333 | 1602.1333 | 764217.6 | 477 | 477
GH1 | D1 | 15 | 1850 | 2015-05-08 09:33 | 2015-05-08 18:30 | 490 | 520 | 477 | Boiler water condition (not feedwater water quality) | Load Reduction #13Unit 1 was derated due to boiler chemistry (high silica) after s | Ghent | Derate | Coal | 3 | 2015 | 5 | 8.95 | 0.51635 | 246.2971 | 27.5192 | 28
GH1 | D1 | 16 | 550 | 2015-05-08 12:09 | 2015-05-08 17:05 | 479 | 520 | 477 | Reheat steam relief/safety valves | Load Reduction #14Unit 1 was already derated for high silica. Had to reduce the l | Ghent | Derate | Coal | 3 | 2015 | 5 | 4.9333 | 0.38897 | 185.5408 | 37.6096 | 38
GH1 | D1 | 17 | 1455 | 2015-05-15 13:47 | 2015-05-15 14:02 | 510 | 520 | 477 | Induced draft fans | Load Reduction #15Operations suspected ID Fan Inlet pressure was near trip point. | Ghent | Derate | Coal | 3 | 2015 | 5 | 0.25 | 0.0048077 | 2.2933 | 9.1731 | 9
GH1 | U1 | 18 | 4293 | 2015-05-18 15:28 | 2015-05-18 22:07 | 0 | 520 | 477 | Hydraulic system pipes and valves | Outage #3The unit developed a leak on the Main Turbine Governor Valve #1 EH fittin | Ghent | Outage | Coal | 3 | 2015 | 5 | 6.65 | 6.65 | 3172.05 | 477 | 477
GH1 | D1 | 19 | 1850 | 2015-05-19 10:10 | 2015-05-19 12:54 | 494 | 520 | 477 | Boiler water condition (not feedwater water quality) | Load Reduction #16High boiler drum silica after taking the unit off to repair an E | Ghent | Derate | Coal | 3 | 2015 | 5 | 2.7333 | 0.13667 | 65.19 | 23.85 | 24
GH1 | MO | 20 | 4262 | 2015-05-20 19:34 | 2015-05-23 02:24 | 0 | 520 | 477 | Intercept valves | F590Outage #4The unit was running with fine mesh screens in the Turbine after the | Ghent | Maintenance | Coal | 3 | 2015 | 5 | 54.8333 | 54.8333 | 26155.5 | 477 | 477
GH1 | PD | 21 | 1480 | 2015-05-29 23:01 | 2015-05-30 01:44 | 450 | 520 | 477 | Other induced draft fan problems | Load Reduction #171-1A ID Fan was off for hardware change out. | Ghent | Derate | Coal | 3 | 2015 | 5 | 2.7167 | 0.36571 | 174.4413 | 64.2115 | 64
GH1 | MO | 22 | 4420 | 2015-06-06 20:54 | 2015-06-07 20:00 | 0 | 520 | 477 | Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | F040Outage #5Unit 1 was removed from service to place a balance weight in the HP s | Ghent | Maintenance | Coal | 3 | 2015 | 6 | 23.1 | 23.1 | 11018.7 | 477 | 477
GH1 | PD | 23 | 8601 | 2015-06-09 21:40 | 2015-06-10 01:45 | 450 | 520 | 477 | SO3 mitigation | Load Reduction #18Mid load SAMs testing, unit off control. | Ghent | Derate | Coal | 3 | 2015 | 6 | 4.0833 | 0.54968 | 262.1971 | 64.2115 | 64
GH1 | PD | 24 | 8601 | 2015-06-10 22:00 | 2015-06-11 01:48 | 375 | 520 | 477 | SO3 mitigation | Load Reduction #19Low load SAMs testing, unit off control. | Ghent | Derate | Coal | 3 | 2015 | 6 | 3.8 | 1.0596 | 505.4365 | 133.0096 | 133
GH1 | PD | 25 | 1455 | 2015-06-17 23:00 | 2015-06-18 03:00 | 460 | 520 | 477 | Induced draft fans | Load Reduction #201-1B ID fan was off to change out a cell and to troubleshoot har | Ghent | Derate | Coal | 3 | 2015 | 6 | 4 | 0.46154 | 220.1538 | 55.0385 | 55
GH1 | D1 | 26 | 250 | 2015-06-19 11:34 | 2015-06-19 13:27 | 480 | 520 | 477 | Pulverizer feeders | Load Reduction #211-5 Mill off to repair damaged feeder belt. | Ghent | Derate | Coal | 3 | 2015 | 6 | 1.8833 | 0.14487 | 69.1038 | 36.6923 | 37
GH1 | D1 | 27 | 344 | 2015-06-28 06:36 | 2015-06-28 09:13 | 470 | 520 | 477 | Pulverizer inspection | Load Reduction #221-2 Mill off to inspect. Mill could not make temperature. | Ghent | Derate | Coal | 3 | 2015 | 6 | 2.6167 | 0.2516 | 120.0144 | 45.8654 | 46
GH1 | PD | 28 | 1980 | 2015-06-30 23:00 | 2015-07-01 00:25 | 460 | 520 | 477 | Boiler safety valve test | Load Reduction #23Boiler drum pressure was reduced to set drum and main steam line | Ghent | Derate | Coal | 3 | 2015 | 6 | 1.4167 | 0.16346 | 77.9712 | 55.0385 | 55
GH1 | D1 | 29 | 9270 | 2015-07-03 12:12 | 2015-07-03 15:13 | 450 | 520 | 477 | Wet coal | Load Reduction #241-1 Feeder plugged with wet coal. | Ghent | Derate | Coal | 3 | 2015 | 7 | 3.0167 | 0.40609 | 193.7048 | 64.2115 | 64
GH1 | PD | 30 | 1470 | 2015-07-07 22:48 | 2015-07-08 00:35 | 460 | 520 | 477 | Induced draft fan motors and drives | Load Reduction #251-2A ID fan off to replace motor outboard "X" vibration probe. | Ghent | Derate | Coal | 3 | 2015 | 7 | 1.7833 | 0.20577 | 98.1519 | 55.0385 | 55
GH1 | PD | 31 | 339 | 2015-07-13 21:52 | 2015-07-14 01:40 | 440 | 520 | 477 | Pulverizer System Puff | Load Reduction #261-5 Feeder off to change out the weigh span roll. | Ghent | Derate | Coal | 3 | 2015 | 7 | 3.8 | 0.58462 | 278.8615 | 73.3846 | 73
GH1 | D1 | 32 | 250 | 2015-07-14 04:47 | 2015-07-14 05:33 | 450 | 520 | 477 | Pulverizer feeders | Load Reduction #271-5 Feeder PLC control board went out. | Ghent | Derate | Coal | 3 | 2015 | 7 | 0.76667 | 0.10321 | 49.2288 | 64.2115 | 64
GH1 | D1 | 33 | 320 | 2015-07-15 21:32 | 2015-07-16 01:37 | 440 | 520 | 477 | Foreign object in Pulverizers mill | Load Reduction #281-1 Mill off for inspection. Mill had high bowl DP and ran back | Ghent | Derate | Coal | 3 | 2015 | 7 | 4.0833 | 0.62821 | 299.6538 | 73.3846 | 73
GH1 | D1 | 34 | 320 | 2015-07-16 02:00 | 2015-07-16 03:12 | 440 | 520 | 477 | Foreign object in Pulverizers mill | Load Reduction #291-2 Mill off for inspection. Mill had noise in pyrite section. | Ghent | Derate | Coal | 3 | 2015 | 7 | 1.2 | 0.18462 | 88.0615 | 73.3846 | 73
GH1 | U1 | 35 | 8650 | 2015-07-19 09:31 | 2015-07-19 10:28 | 0 | 520 | 477 | Baghouse systems | Outage #6PJFF inlet pressure reached tripping point and tripped one set of ID fans | Ghent | Outage | Coal | 3 | 2015 | 7 | 0.95 | 0.95 | 453.15 | 477 | 477
GH1 | D1 | 36 | 340 | 2015-07-19 12:02 | 2015-07-19 22:32 | 480 | 520 | 477 | Other pulverizer problems | Load Reduction #301-6 Mill off due to mill explosion after restart of mill. | Ghent | Derate | Coal | 3 | 2015 | 7 | 10.5 | 0.80769 | 385.2692 | 36.6923 | 37
GH1 | D1 | 37 | 1470 | 2015-07-19 22:32 | 2015-07-20 06:00 | 460 | 520 | 477 | Induced draft fan motors and drives | Load Reduction #311-1B ID fan tripped due to VFD coolant conductivity transmitter | Ghent | Derate | Coal | 3 | 2015 | 7 | 7.4667 | 0.86154 | 410.9538 | 55.0385 | 55
GH1 | D1 | 38 | 340 | 2015-07-20 06:00 | 2015-07-23 20:39 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #321-6 Mill explosion derate continued after 1-1B ID fan was return | Ghent | Derate | Coal | 3 | 2015 | 7 | 86.65 | 9.9981 | 4769.0827 | 55.0385 | 55
GH1 | D1 | 39 | 350 | 2015-07-22 05:46 | 2015-07-22 07:07 | 350 | 520 | 477 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #331-2 Mill 'D' burner line became hot. Removed mill from service. | Ghent | Derate | Coal | 3 | 2015 | 7 | 1.35 | 0.44135 | 210.5221 | 155.9423 | 156
GH1 | D1 | 40 | 1040 | 2015-08-04 04:40 | 2015-08-04 06:24 | 300 | 520 | 477 | First superheater B | Load Reduction #34Dropping drum pressure due to tube leak in the Primary Superheat | Ghent | Derate | Coal | 3 | 2015 | 8 | 1.7333 | 0.73333 | 349.8 | 201.8077 | 202
GH1 | U2 | 41 | 1040 | 2015-08-04 06:24 | 2015-08-05 05:12 | 0 | 520 | 477 | First superheater B | Outage #7Tube leak was heard in backpass of boiler around the Primary Superheat in | Ghent | Outage | Coal | 3 | 2015 | 8 | 22.8 | 22.8 | 10875.6 | 477 | 477
GH1 | D1 | 42 | 339 | 2015-08-05 07:41 | 2015-08-05 22:36 | 460 | 520 | 477 | Pulverizer System Puff | Load Reduction #351-4 Mill was off to inspect after mill puff. | Ghent | Derate | Coal | 3 | 2015 | 8 | 14.9167 | 1.7212 | 820.9904 | 55.0385 | 55
GH1 | D1 | 43 | 340 | 2015-08-07 23:31 | 2015-08-08 02:24 | 480 | 520 | 477 | Other pulverizer problems | Load Reduction #361-3 Mill off for inspection due to noise in mill. | Ghent | Derate | Coal | 3 | 2015 | 8 | 2.8833 | 0.22179 | 105.7962 | 36.6923 | 37
GH1 | U2 | 44 | 520 | 2015-08-12 21:49 | 2015-08-16 00:39 | 0 | 520 | 477 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Outage #8A leak developed in the Main Steam line drain S9. Removed the unit from | Ghent | Outage | Coal | 3 | 2015 | 8 | 74.8333 | 74.8333 | 35695.5 | 477 | 477
GH1 | D1 | 45 | 310 | 2015-08-21 10:19 | 2015-08-21 12:24 | 450 | 520 | 477 | Pulverizer mills | Load Reduction #371-2 Mill tripped due to air flow issues. Cleaned the mill and r | Ghent | Derate | Coal | 3 | 2015 | 8 | 2.0833 | 0.28045 | 133.774 | 64.2115 | 64
GH1 | PD | 46 | 344 | 2015-08-23 23:00 | 2015-08-24 01:25 | 460 | 520 | 477 | Pulverizer inspection | Load Reduction #381-2 Mill off to inspect hot and cold air dampers, as well as air | Ghent | Derate | Coal | 3 | 2015 | 8 | 2.4167 | 0.27885 | 133.0096 | 55.0385 | 55
GH1 | U2 | 47 | 1040 | 2015-08-26 22:15 | 2015-09-01 21:46 | 0 | 520 | 477 | First superheater B | F380Outage #9Unit 1 developed what appeared to be a leak in the Primary Superheate | Ghent | Outage | Coal | 3 | 2015 | 8 | 143.5167 | 143.5167 | 68457.45 | 477 | 477
GH1 | U2 | 48 | 1080 | 2015-09-08 09:56 | 2015-09-10 15:29 | 0 | 520 | 477 | Economizer B | F910Outage #10Unit 1 developed a tube leak in the Economizer section of the boiler | Ghent | Outage | Coal | 3 | 2015 | 9 | 53.55 | 53.55 | 25543.35 | 477 | 477
GH1 | D1 | 49 | 340 | 2015-10-02 03:24 | 2015-10-02 07:26 | 450 | 520 | 477 | Other pulverizer problems | Load Reduction #391-3 Mill north journal locked up. | Ghent | Derate | Coal | 3 | 2015 | 10 | 4.0333 | 0.54295 | 258.9865 | 64.2115 | 64
GH1 | MO | 50 | 1000 | 2015-10-27 12:50 | 2015-10-29 23:16 | 0 | 520 | 477 | Waterwall (Furnace wall) A | F540Outage #11Unit 1 was running with a water wall tube leak. Removed the unit fo | Ghent | Maintenance | Coal | 3 | 2015 | 10 | 58.4333 | 58.4333 | 27872.7 | 477 | 477
GH1 | PD | 51 | 8460 | 2015-11-04 22:00 | 2015-11-05 01:58 | 375 | 520 | 477 | Testing A | F790Load Reduction #40Ghent 1 had a planned derate for SAMs emission testing. | Ghent | Derate | Coal | 3 | 2015 | 11 | 3.9667 | 1.1061 | 527.6048 | 133.0096 | 133
GH1 | MO | 52 | 1060 | 2015-11-10 22:27 | 2015-11-13 16:35 | 0 | 520 | 477 | First reheater A | F540Outage #12Unit 1 was running with a Radiant Reheat tube leak. The unit remove | Ghent | Maintenance | Coal | 3 | 2015 | 11 | 66.1333 | 66.1333 | 31545.6 | 477 | 477
GH1 | U1 | 53 | 4810 | 2015-11-13 22:23 | 2015-11-16 08:28 | 0 | 520 | 477 | Generator output breaker | Outage #13GH1 generator breaker 165-716 manual disconnect failed, which caused the | Ghent | Outage | Coal | 3 | 2015 | 11 | 58.0833 | 58.0833 | 27705.75 | 477 | 477
GH1 | U1 | 54 | 4610 | 2015-11-16 09:23 | 2015-11-16 10:39 | 0 | 520 | 477 | Hydrogen cooling system piping and valves | Outage #14GH1 tripped off line due to high generator hydrogen gas temperature. | Ghent | Outage | Coal | 3 | 2015 | 11 | 1.2667 | 1.2667 | 604.2 | 477 | 477
GH1 | D1 | 55 | 340 | 2015-11-17 10:50 | 2015-11-17 12:31 | 450 | 520 | 477 | Other pulverizer problems | Load Reduction #41Removed 1-2 mill from service to adjust a pyrite scraper. | Ghent | Derate | Coal | 3 | 2015 | 11 | 1.6833 | 0.2266 | 108.0894 | 64.2115 | 64
GH1 | MO | 56 | 3611 | 2015-11-18 21:24 | 2015-11-19 03:08 | 0 | 520 | 477 | Switchyard circuit breakers - external | Outage #15Unit 1 was removed from service to repair a failed bus bar on the 165-70 | Ghent | Maintenance | Coal | 3 | 2015 | 11 | 5.7333 | 5.7333 | 2734.8 | 477 | 477
GH1 | D1 | 57 | 250 | 2015-12-01 12:43 | 2015-12-01 16:39 | 425 | 520 | 477 | Pulverizer feeders | Load Reduction #421-6 Feeder belt broke. | Ghent | Derate | Coal | 3 | 2015 | 12 | 3.9333 | 0.71859 | 342.7673 | 87.1442 | 87
GH1 | PD | 58 | 3415 | 2015-12-11 13:26 | 2015-12-11 14:03 | 315 | 520 | 477 | Feedwater pump/drive lube oil system | Load Reduction #43Operations removed 1-1 BFPT from service long enough for Instrum | Ghent | Derate | Coal | 3 | 2015 | 12 | 0.61667 | 0.24311 | 115.963 | 188.0481 | 188
GH1 | PD | 59 | 3415 | 2015-12-12 08:20 | 2015-12-12 08:32 | 320 | 520 | 477 | Feedwater pump/drive lube oil system | Load Reduction #44Operations removed 1-1 BFPT from service long enough for Instrum | Ghent | Derate | Coal | 3 | 2015 | 12 | 0.2 | 0.076923 | 36.6923 | 183.4615 | 183
GH1 | PD | 60 | 4611 | 2015-12-19 01:00 | 2015-12-19 01:45 | 410 | 520 | 477 | Hydrogen coolers | F540Load Reduction #45Unit 1 hydrogen cooler gauge line leak. | Ghent | Derate | Coal | 3 | 2015 | 12 | 0.75 | 0.15865 | 75.6779 | 100.9038 | 101
GH1 | PD | 61 | 340 | 2015-12-27 06:07 | 2015-12-27 08:31 | 470 | 520 | 477 | Other pulverizer problems | F060Load Reduction #461-4 Mill was removed from service to replace a journal. | Ghent | Derate | Coal | 3 | 2015 | 12 | 2.4 | 0.23077 | 110.0769 | 45.8654 | 46
GH1 | PD | 1 | 1470 | 2016-01-06 09:40 | 2016-01-06 22:30 | 430 | 520 | 477 | Induced draft fan motors and drives | F590Load Reduction #11-2B ID fan VFD had a bad PLC and flow meter. | Ghent | Derate | Coal | 3 | 2016 | 1 | 12.8333 | 2.2212 | 1059.4904 | 82.5577 | 83
GH1 | PD | 2 | 340 | 2016-01-15 14:27 | 2016-01-15 15:17 | 440 | 520 | 477 | Other pulverizer problems | Load Reduction #21-6 Mill feeder clean out conveyor coupling key came out. | Ghent | Derate | Coal | 3 | 2016 | 1 | 0.83333 | 0.12821 | 61.1538 | 73.3846 | 73
GH1 | U1 | 3 | 1480 | 2016-01-20 09:17 | 2016-01-20 10:18 | 0 | 520 | 477 | Other induced draft fan problems | Outage #1GH1 was removed from service due to loss of ID fans causing MFT. ID fans | Ghent | Outage | Coal | 3 | 2016 | 1 | 1.0167 | 1.0167 | 484.95 | 477 | 477
GH1 | D1 | 4 | 350 | 2016-01-20 13:31 | 2016-01-20 16:15 | 460 | 520 | 477 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #31-6 Mill "B" burner line caught fire. | Ghent | Derate | Coal | 3 | 2016 | 1 | 2.7333 | 0.31538 | 150.4385 | 55.0385 | 55
GH1 | D1 | 5 | 350 | 2016-01-22 06:51 | 2016-01-22 07:15 | 415 | 520 | 477 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #41-4 Mill "C" burner fire. | Ghent | Derate | Coal | 3 | 2016 | 1 | 0.4 | 0.080769 | 38.5269 | 96.3173 | 96
GH1 | D1 | 6 | 350 | 2016-01-22 10:11 | 2016-01-22 11:43 | 415 | 520 | 477 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #51-4 Mill "C" burner fire. | Ghent | Derate | Coal | 3 | 2016 | 1 | 1.5333 | 0.30962 | 147.6865 | 96.3173 | 96
GH1 | U1 | 7 | 1060 | 2016-01-27 15:12 | 2016-01-28 17:49 | 0 | 520 | 477 | First reheater A | F830Outage #2Unit 1 was removed from service due to a reheat tube leak at the IK # | Ghent | Outage | Coal | 3 | 2016 | 1 | 26.6167 | 26.6167 | 12696.15 | 477 | 477
GH1 | U1 | 8 | 1060 | 2016-02-04 10:48 | 2016-02-06 19:50 | 0 | 520 | 477 | First reheater A | F830Outage #3Unit 1 was removed from service due to reheat tube leak at the IK #6 | Ghent | Outage | Coal | 3 | 2016 | 2 | 57.0333 | 57.0333 | 27204.9 | 477 | 477
GH1 | U1 | 9 | 3220 | 2016-02-06 19:50 | 2016-02-07 11:00 |  | 520 | 477 | Circulating water piping | Outage #4GH1 Forced Outage was changed from a Reheat tube leak, once repairs were | Ghent | Outage | Coal | 3 | 2016 | 2 | 15.1667 | 15.1667 | 7234.5 | 477 | 477
GH1 | PD | 10 | 340 | 2016-02-17 23:00 | 2016-02-18 02:00 | 425 | 520 | 477 | Other pulverizer problems | Load Reduction #61-1 Mill was removed from service for noise in pyrite section. | Ghent | Derate | Coal | 3 | 2016 | 2 | 3 | 0.54808 | 261.4327 | 87.1442 | 87
GH1 | U1 | 11 | 1040 | 2016-02-18 02:00 | 2016-02-18 23:47 | 0 | 520 | 477 | First superheater B | Outage #5Unit 1 was removed from service due to a Reheat tube leak at the IK #6 ar | Ghent | Outage | Coal | 3 | 2016 | 2 | 21.7833 | 21.7833 | 10390.65 | 477 | 477
GH1 | PO | 13 | 1060 | 2016-02-24 08:07 | 2016-03-19 23:16 | 0 | 520 | 477 | First reheater A | F590Outage #7Unit 1 was changed from a Reserve to a Planned Outage for Reheat tube | Ghent | Other | Coal | 3 | 2016 | 2 | 591.15 | 591.15 | 281978.55 | 477 | 477
GH1 | U1 | 14 | 1710 | 2016-03-20 03:31 | 2016-03-20 04:55 | 0 | 520 | 477 | Combustion/steam condition controls (report local controls --- burners | Outage #8Unit 1 tripped due to loss of boiler fire. | Ghent | Outage | Coal | 3 | 2016 | 3 | 1.4 | 1.4 | 667.8 | 477 | 477
GH1 | PD | 15 | 250 | 2016-03-28 21:30 | 2016-03-29 00:05 | 435 | 520 | 477 | Pulverizer feeders | Load Reduction #71-3 Mill feeder card was bad, couldn't calibrate feeder. | Ghent | Derate | Coal | 3 | 2016 | 3 | 2.5833 | 0.42228 | 201.4255 | 77.9712 | 78
GH1 | PD | 16 | 340 | 2016-04-04 23:09 | 2016-04-05 00:47 | 460 | 520 | 477 | Other pulverizer problems | F620Load Reduction #81-2 Mill was making noise. | Ghent | Derate | Coal | 3 | 2016 | 4 | 1.6333 | 0.18846 | 89.8962 | 55.0385 | 55
GH1 | PD | 17 | 340 | 2016-04-05 23:00 | 2016-04-06 00:46 | 460 | 520 | 477 | Other pulverizer problems | F620Load Reduction #91-2 Mill was making noise. | Ghent | Derate | Coal | 3 | 2016 | 4 | 1.7667 | 0.20385 | 97.2346 | 55.0385 | 55
GH1 | D1 | 18 | 340 | 2016-04-15 18:00 | 2016-04-16 05:04 | 470 | 520 | 477 | Other pulverizer problems | Load Reduction #101-2 Mill exhauster bearing change out. | Ghent | Derate | Coal | 3 | 2016 | 4 | 11.0667 | 1.0641 | 507.5769 | 45.8654 | 46
GH1 | D1 | 19 | 340 | 2016-04-16 05:04 | 2016-04-16 14:25 | 450 | 520 | 477 | Other pulverizer problems | Load Reduction #111-2 Mill exhauster bearing change out. | Ghent | Derate | Coal | 3 | 2016 | 4 | 9.35 | 1.2587 | 600.3779 | 64.2115 | 64
GH1 | D1 | 20 | 250 | 2016-04-20 02:40 | 2016-04-20 08:10 | 450 | 520 | 477 | Pulverizer feeders | Load Reduction #121-4 Mill coal feeder belt broke. | Ghent | Derate | Coal | 3 | 2016 | 4 | 5.5 | 0.74038 | 353.1635 | 64.2115 | 64
GH1 | PD | 21 | 340 | 2016-04-28 23:00 | 2016-04-29 01:56 | 460 | 520 | 477 | Other pulverizer problems | F590Load Reduction #131-6 Mill planned derate to trim vane wheel, torque race, and | Ghent | Derate | Coal | 3 | 2016 | 4 | 2.9333 | 0.33846 | 161.4462 | 55.0385 | 55
GH1 | PD | 22 | 340 | 2016-05-11 00:01 | 2016-05-11 00:56 | 460 | 520 | 477 | Other pulverizer problems | F320Load Reduction #14Cleaned 1-4 mill air flow probes. | Ghent | Derate | Coal | 3 | 2016 | 5 | 0.91667 | 0.10577 | 50.4519 | 55.0385 | 55
GH1 | D1 | 23 | 250 | 2016-05-12 08:45 | 2016-05-12 11:24 | 480 | 520 | 477 | Pulverizer feeders | F830Load Reduction #151-3 Mill feeder belt broke. | Ghent | Derate | Coal | 3 | 2016 | 5 | 2.65 | 0.20385 | 97.2346 | 36.6923 | 37
GH1 | MO | 24 | 510 | 2016-05-14 16:22 | 2016-05-14 21:28 | 0 | 520 | 477 | Main steam relief/safety valves off superheater | F590Outage #9U1 was removed from service to repair a leaking SH spray valve. Also | Ghent | Maintenance | Coal | 3 | 2016 | 5 | 5.1 | 5.1 | 2432.7 | 477 | 477
GH1 | U1 | 26 | 3133 | 2016-05-15 13:30 | 2016-05-15 14:14 | 0 | 520 | 477 | Vacuum pumps | Outage #11Unit 1 tripped due to loss of 1-1 main condenser vacuum pump seal water | Ghent | Outage | Coal | 3 | 2016 | 5 | 0.73333 | 0.73333 | 349.8 | 477 | 477
GH1 | U1 | 27 | 3210 | 2016-05-15 14:39 | 2016-05-15 15:30 | 0 | 520 | 477 | Circulating water pumps | Outage #12Unit 1 tripped off line due to boiler swing causing a low differential p | Ghent | Outage | Coal | 3 | 2016 | 5 | 0.85 | 0.85 | 405.45 | 477 | 477
GH1 | D1 | 28 | 250 | 2016-06-06 14:27 | 2016-06-06 15:37 | 465 | 520 | 477 | Pulverizer feeders | F830Load Reduction #161-2 Mill feeder plugged causing feeder to trip. | Ghent | Derate | Coal | 3 | 2016 | 6 | 1.1667 | 0.1234 | 58.8606 | 50.4519 | 50
GH1 | PD | 29 | 4267 | 2016-06-08 04:32 | 2016-06-08 04:43 | 440 | 520 | 477 | Control valve testing | F590Load Reduction #17U1 Main turbine valve curve adjustment. | Ghent | Derate | Coal | 3 | 2016 | 6 | 0.18333 | 0.028205 | 13.4538 | 73.3846 | 73
GH1 | D1 | 30 | 8020 | 2016-06-11 18:00 | 2016-06-11 18:08 | 340 | 520 | 477 | Mill slurry tanks supply problems | F830Load Reduction #18"B" Limestone slurry loop went out of service when LSP lost | Ghent | Derate | Coal | 3 | 2016 | 6 | 0.13333 | 0.046154 | 22.0154 | 165.1154 | 165
GH1 | PD | 31 | 9656 | 2016-06-14 23:00 | 2016-06-15 02:57 | 450 | 520 | 477 | Other stack or exhaust emissions testing - fossil | F790Load Reduction #19U1 Stack RATA testing. | Ghent | Derate | Coal | 3 | 2016 | 6 | 3.95 | 0.53173 | 253.6356 | 64.2115 | 64
GH1 | PD | 32 | 9656 | 2016-06-15 22:50 | 2016-06-16 02:26 | 375 | 520 | 477 | Other stack or exhaust emissions testing - fossil | F790Load Reduction #20Low load RATA test. | Ghent | Derate | Coal | 3 | 2016 | 6 | 3.6 | 1.0038 | 478.8346 | 133.0096 | 133
GH1 | D1 | 33 | 250 | 2016-06-21 22:14 | 2016-06-21 23:10 | 440 | 520 | 477 | Pulverizer feeders | F830Load Reduction #211-2 Mill feeder pipe plugged. | Ghent | Derate | Coal | 3 | 2016 | 6 | 0.93333 | 0.14359 | 68.4923 | 73.3846 | 73
GH1 | D1 | 34 | 250 | 2016-06-22 03:25 | 2016-06-22 03:51 | 340 | 520 | 477 | Pulverizer feeders | F820Load Reduction #221-2 Mill feeder pipe plugged. 1-1 Mill was off an could not | Ghent | Derate | Coal | 3 | 2016 | 6 | 0.43333 | 0.15 | 71.55 | 165.1154 | 165
GH1 | D1 | 35 | 250 | 2016-06-22 03:51 | 2016-06-22 05:30 | 440 | 520 | 477 | Pulverizer feeders | F830Load Reduction #231-2 Mill feeder pipe plugged tripping the feeder. | Ghent | Derate | Coal | 3 | 2016 | 6 | 1.65 | 0.25385 | 121.0846 | 73.3846 | 73
GH1 | D1 | 36 | 250 | 2016-06-23 23:16 | 2016-06-23 23:55 | 440 | 520 | 477 | Pulverizer feeders | F830Load Reduction #241-2 Mill feeder pipe plugged tripping the feeder. | Ghent | Derate | Coal | 3 | 2016 | 6 | 0.65 | 0.1 | 47.7 | 73.3846 | 73
GH1 | PD | 37 | 250 | 2016-06-24 23:00 | 2016-06-25 01:34 | 440 | 520 | 477 | Pulverizer feeders | F930Load Reduction #25Planned derate on U1 for 1-2 coal feeder pipe repair. | Ghent | Derate | Coal | 3 | 2016 | 6 | 2.5667 | 0.39487 | 188.3538 | 73.3846 | 73
GH1 | D1 | 38 | 3311 | 2016-06-27 16:12 | 2016-07-01 00:09 | 298 | 520 | 477 | Condensate/hotwell pump motor | F830Load Reduction #261-2 Condensate pump tripped. Motor was tested and found it | Ghent | Derate | Coal | 3 | 2016 | 6 | 79.95 | 34.1325 | 16281.2025 | 203.6423 | 204
GH1 | MO | 39 | 1480 | 2016-06-28 22:39 | 2016-06-29 21:29 | 0 | 520 | 477 | Other induced draft fan problems | F930Outage #13Unit 1 was removed from service for expansion joint repair. | Ghent | Maintenance | Coal | 3 | 2016 | 6 | 22.8333 | 22.8333 | 10891.5 | 477 | 477
GH1 | PD | 41 | 340 | 2016-07-01 23:50 | 2016-07-02 02:23 | 460 | 520 | 477 | Other pulverizer problems | F060Load Reduction #271-1 Mill was removed from service to replace a journal. | Ghent | Derate | Coal | 3 | 2016 | 7 | 2.55 | 0.29423 | 140.3481 | 55.0385 | 55
GH1 | PD | 42 | 340 | 2016-07-08 02:06 | 2016-07-08 03:14 | 450 | 520 | 477 | Other pulverizer problems | F060Load Reduction #281-5 Mill was removed from service to replace a journal. | Ghent | Derate | Coal | 3 | 2016 | 7 | 1.1333 | 0.15256 | 72.7731 | 64.2115 | 64
GH1 | D1 | 43 | 250 | 2016-07-08 12:09 | 2016-07-08 15:23 | 440 | 520 | 477 | Pulverizer feeders | F060Load Reduction #291-5 Mill was removed from service to replace the feeder belt | Ghent | Derate | Coal | 3 | 2016 | 7 | 3.2333 | 0.49744 | 237.2769 | 73.3846 | 73
GH1 | PD | 44 | 340 | 2016-07-12 23:24 | 2016-07-13 02:54 | 450 | 520 | 477 | Other pulverizer problems | F120Load Reduction #30Planned derate to clean 1-3 and 1-5 Mill airflow pitot tubes | Ghent | Derate | Coal | 3 | 2016 | 7 | 3.5 | 0.47115 | 224.7404 | 64.2115 | 64
GH1 | PD | 45 | 340 | 2016-07-13 23:45 | 2016-07-14 02:57 | 450 | 520 | 477 | Other pulverizer problems | F120Load Reduction #31Removed 1-2 and 1-4 mills from service to clean the air flow | Ghent | Derate | Coal | 3 | 2016 | 7 | 3.2 | 0.43077 | 205.4769 | 64.2115 | 64
GH1 | D1 | 46 | 3408 | 2016-07-17 03:50 | 2016-07-17 10:30 | 330 | 520 | 477 | Feedwater pump drive - local controls | F700Load Reduction #321-1 BFPT would not re-latch. | Ghent | Derate | Coal | 3 | 2016 | 7 | 6.6667 | 2.4359 | 1161.9231 | 174.2885 | 174
GH1 | D1 | 47 | 340 | 2016-07-27 19:26 | 2016-07-27 21:48 | 460 | 520 | 477 | Other pulverizer problems | Load Reduction #33Removed 1-3 Mill from service due to noise in the pyrite system. | Ghent | Derate | Coal | 3 | 2016 | 7 | 2.3667 | 0.27308 | 130.2577 | 55.0385 | 55
GH1 | D1 | 48 | 340 | 2016-07-29 06:30 | 2016-07-29 09:10 | 450 | 520 | 477 | Other pulverizer problems | Load Reduction #341-6 Mill journal spring can broke off. | Ghent | Derate | Coal | 3 | 2016 | 7 | 2.6667 | 0.35897 | 171.2308 | 64.2115 | 64
GH1 | MO | 49 | 740 | 2016-08-05 23:42 | 2016-08-06 19:28 | 0 | 520 | 477 | Boiler recirculation pumps | F540Outage #141-4 Boiler circulating water pump mechanical seal failed. The unit | Ghent | Maintenance | Coal | 3 | 2016 | 8 | 19.7667 | 19.7667 | 9428.7 | 477 | 477
GH1 | D1 | 50 | 770 | 2016-08-24 23:02 | 2016-08-25 01:48 | 405 | 520 | 477 | Other boiler recirculation problems | Load Reduction #351-1 Circulating water pump was removed from service due to water | Ghent | Derate | Coal | 3 | 2016 | 8 | 2.7667 | 0.61186 | 291.8567 | 105.4904 | 105
GH1 | PD | 51 | 4261 | 2016-09-08 23:00 | 2016-09-09 00:15 | 415 | 520 | 477 | Control valves | F540Load Reduction #36U1 Main turbine #6 governor valve hydraulic actuator had a l | Ghent | Derate | Coal | 3 | 2016 | 9 | 1.25 | 0.2524 | 120.3966 | 96.3173 | 96
GH1 | D1 | 52 | 1040 | 2016-09-16 16:28 | 2016-09-16 18:36 | 500 | 520 | 477 | First superheater B | F820Load Reduction #37Unit 1 was derated due to AH duct pressure maxing out, which | Ghent | Derate | Coal | 3 | 2016 | 9 | 2.1333 | 0.082051 | 39.1385 | 18.3462 | 18
GH1 | U1 | 53 | 1040 | 2016-09-16 18:36 | 2016-09-23 01:56 | 0 | 520 | 477 | First superheater B | F820Outage #15Unit 1 came off line due to a Primary Superheat tube leak. | Ghent | Outage | Coal | 3 | 2016 | 9 | 151.3333 | 151.3333 | 72186 | 477 | 477
GH1 | PD | 54 | 4261 | 2016-09-24 22:45 | 2016-09-24 23:25 | 450 | 520 | 477 | Control valves | F540Load Reduction #38U1 was derated due to an EH leak on the Main Turbine #1 gove | Ghent | Derate | Coal | 3 | 2016 | 9 | 0.66667 | 0.089744 | 42.8077 | 64.2115 | 64
GH1 | PD | 55 | 4261 | 2016-09-24 23:25 | 2016-09-25 00:41 | 200 | 520 | 477 | Control valves | F540Load Reduction #39Unit 1 was derated due to an EH leak on the Main Turbine #1 | Ghent | Derate | Coal | 3 | 2016 | 9 | 1.2667 | 0.77949 | 371.8154 | 293.5385 | 294
GH1 | U1 | 56 | 4261 | 2016-09-25 00:41 | 2016-09-25 01:41 | 0 | 520 | 477 | Control valves | F540Outage #16Unit 1 was removed from service due to an EH leak on the Main Turbin | Ghent | Outage | Coal | 3 | 2016 | 9 | 1 | 1 | 477 | 477 | 477
GH1 | MO | 57 | 4261 | 2016-10-03 22:45 | 2016-10-04 03:03 | 0 | 520 | 477 | Control valves | F930Outage #17Unit 1 was removed from service to replace O-rings on main turbine g | Ghent | Maintenance | Coal | 3 | 2016 | 10 | 4.3 | 4.3 | 2051.1 | 477 | 477
GH1 | D1 | 58 | 250 | 2016-10-23 08:53 | 2016-10-23 14:00 | 470 | 520 | 477 | Pulverizer feeders | Load Reduction #40Unit 1 was derated due to 1-3 mill feeder belt failure. Belt wa | Ghent | Derate | Coal | 3 | 2016 | 10 | 5.1167 | 0.49199 | 234.6779 | 45.8654 | 46
GH1 | D1 | 59 | 250 | 2016-10-23 23:15 | 2016-10-24 04:03 | 430 | 520 | 477 | Pulverizer feeders | Load Reduction #41Unit 1 was derated due to 1-1 mill feeder belt failure. The bel | Ghent | Derate | Coal | 3 | 2016 | 10 | 4.8 | 0.83077 | 396.2769 | 82.5577 | 83
GH1 | D1 | 60 | 250 | 2016-10-24 07:24 | 2016-10-24 13:25 | 430 | 520 | 477 | Pulverizer feeders | Load Reduction #421-6 Mill feeder belt developed a rip. | Ghent | Derate | Coal | 3 | 2016 | 10 | 6.0167 | 1.0413 | 496.7221 | 82.5577 | 83
GH1 | D1 | 61 | 9270 | 2016-10-25 15:15 | 2016-10-25 16:22 | 430 | 520 | 477 | Wet coal | Load Reduction #431-3 Mill feeder plugged due to wet coal. | Ghent | Derate | Coal | 3 | 2016 | 10 | 1.1167 | 0.19327 | 92.1894 | 82.5577 | 83
GH1 | D1 | 62 | 9270 | 2016-10-25 23:16 | 2016-10-26 04:00 | 460 | 520 | 477 | Wet coal | Load Reduction #441-4 Mill feeder plugged due to wet coal. Feeder belt ripped and | Ghent | Derate | Coal | 3 | 2016 | 10 | 4.7333 | 0.54615 | 260.5154 | 55.0385 | 55
GH1 | D1 | 63 | 9270 | 2016-10-26 04:03 | 2016-10-26 05:05 | 460 | 520 | 477 | Wet coal | Load Reduction #451-3 Mill feeder plugged due to wet coal. | Ghent | Derate | Coal | 3 | 2016 | 10 | 1.0333 | 0.11923 | 56.8731 | 55.0385 | 55
GH1 | D1 | 64 | 9270 | 2016-10-26 05:05 | 2016-10-26 05:37 | 370 | 520 | 477 | Wet coal | Load Reduction #461-3 Mill feeder plugged due to wet coal and not enough steam to | Ghent | Derate | Coal | 3 | 2016 | 10 | 0.53333 | 0.15385 | 73.3846 | 137.5962 | 138
GH1 | D1 | 65 | 340 | 2016-10-26 11:28 | 2016-10-26 19:17 | 450 | 520 | 477 | Other pulverizer problems | Load Reduction #471-1 Mill feeder developed a hole in piping. | Ghent | Derate | Coal | 3 | 2016 | 10 | 7.8167 | 1.0522 | 501.9202 | 64.2115 | 64
GH1 | D1 | 66 | 250 | 2016-11-09 16:27 | 2016-11-09 22:13 | 450 | 520 | 477 | Pulverizer feeders | Load Reduction #481-6 Feeder tail roll bearing failed and belt tracked off to one | Ghent | Derate | Coal | 3 | 2016 | 11 | 5.7667 | 0.77628 | 370.2865 | 64.2115 | 64
GH1 | PD | 67 | 4610 | 2016-11-15 23:47 | 2016-11-16 03:56 | 400 | 520 | 477 | Hydrogen cooling system piping and valves | F540Load Reduction #491-3 Hydrogen cooler inlet leak. | Ghent | Derate | Coal | 3 | 2016 | 11 | 4.15 | 0.95769 | 456.8192 | 110.0769 | 110
GH1 | PD | 68 | 250 | 2016-11-26 22:02 | 2016-11-27 | 450 | 520 | 477 | Pulverizer feeders | F810Load Reduction #501-1 Mill feeder had a tear in the feeder belt. | Ghent | Derate | Coal | 3 | 2016 | 11 | 1.9667 | 0.26474 | 126.2827 | 64.2115 | 64
GH1 | D1 | 69 | 250 | 2016-12-13 07:51 | 2016-12-13 08:16 | 475 | 520 | 477 | Pulverizer feeders | Load Reduction #511-2 Feeder belt tore and needed to be replaced. | Ghent | Derate | Coal | 3 | 2016 | 12 | 0.41667 | 0.036058 | 17.1995 | 41.2788 | 41
GH1 | D1 | 70 | 4610 | 2016-12-16 21:03 | 2016-12-17 00:14 | 411 | 520 | 477 | Hydrogen cooling system piping and valves | Load Reduction #52#3 Hydrogen cooler LPSW return line developed a leak. | Ghent | Derate | Coal | 3 | 2016 | 12 | 3.1833 | 0.66728 | 318.2905 | 99.9865 | 100
GH1 | D1 | 71 | 250 | 2016-12-27 18:33 | 2016-12-27 18:57 | 450 | 520 | 477 | Pulverizer feeders | Load Reduction #531-6 Mill feeder tripped causing the mill to trip. Mill had to b | Ghent | Derate | Coal | 3 | 2016 | 12 | 0.4 | 0.053846 | 25.6846 | 64.2115 | 64
GH1 | PD | 1 | 250 | 2017-01-09 23:44 | 2017-01-10 04:41 | 460 | 520 | 477 | Pulverizer feeders | Load Reduction #11-5 Mill feeder calibration and inspection. | Ghent | Derate | Coal | 3 | 2017 | 1 | 4.95 | 0.57115 | 272.4404 | 55.0385 | 55
GH1 | MO | 2 | 1000 | 2017-01-10 12:48 | 2017-01-11 01:38 | 0 | 520 | 477 | Waterwall (Furnace wall) A | Outage #1The unit was removed from service to repair a water wall tube leak on "A" | Ghent | Maintenance | Coal | 3 | 2017 | 1 | 12.8333 | 12.8333 | 6121.5 | 477 | 477
GH1 | D1 | 3 | 3408 | 2017-01-11 05:50 | 2017-01-11 16:57 | 330 | 520 | 477 | Feedwater pump drive - local controls | Load Reduction #21-1 BFPT control valve arm broke. Unis is only good for 330 MWs | Ghent | Derate | Coal | 3 | 2017 | 1 | 11.1167 | 4.0619 | 1937.5067 | 174.2885 | 174
GH1 | MO | 4 | 1000 | 2017-01-15 22:19 | 2017-01-17 23:57 | 0 | 520 | 477 | Waterwall (Furnace wall) A | F540Outage #2Unit 1 was removed from service to repair a water wall tube leak. | Ghent | Maintenance | Coal | 3 | 2017 | 1 | 49.6333 | 49.6333 | 23675.1 | 477 | 477
GH1 | U1 | 5 | 1040 | 2017-01-18 16:51 | 2017-01-22 00:04 | 0 | 520 | 477 | First superheater B | Outage #3Unit 1 off line for a tube leak in the Low Temp SH section of the boiler. | Ghent | Outage | Coal | 3 | 2017 | 1 | 79.2167 | 79.2167 | 37786.35 | 477 | 477
GH1 | MO | 6 | 1060 | 2017-01-27 13:13 | 2017-01-29 11:19 | 0 | 520 | 477 | First reheater A | F540Outage #4Unit 1 removed from service to repair a leak in a radiant RH tube. | Ghent | Maintenance | Coal | 3 | 2017 | 1 | 46.1 | 46.1 | 21989.7 | 477 | 477
GH1 | D1 | 7 | 250 | 2017-01-31 03:19 | 2017-01-31 05:24 | 460 | 520 | 477 | Pulverizer feeders | F830Load Reduction #31-2 Mill feeder belt broke causing mill to trip. | Ghent | Derate | Coal | 3 | 2017 | 1 | 2.0833 | 0.24038 | 114.6635 | 55.0385 | 55
GH1 | MO | 8 | 1000 | 2017-02-01 22:46 | 2017-02-02 10:33 | 0 | 520 | 477 | Waterwall (Furnace wall) A | F540Outage #5Water wall tube leak on 'D' corner. | Ghent | Maintenance | Coal | 3 | 2017 | 2 | 11.7833 | 11.7833 | 5620.65 | 477 | 477
GH1 | D1 | 9 | 891 | 2017-02-07 15:00 | 2017-02-07 22:49 | 240 | 520 | 477 | Bottom ash hoppers (including gates) | Load Reduction #4Unit 1 Wet ash hopper slag bridged over. High pressure washed th | Ghent | Derate | Coal | 3 | 2017 | 2 | 7.8167 | 4.209 | 2007.6808 | 256.8462 | 257
GH1 | U1 | 10 | 891 | 2017-02-07 22:49 | 2017-02-08 15:47 | 0 | 520 | 477 | Bottom ash hoppers (including gates) | FS00Outage #6B-Side Wet Ash Hopper bridged over with slag. Removed the unit from | Ghent | Outage | Coal | 3 | 2017 | 2 | 16.9667 | 16.9667 | 8093.1 | 477 | 477
GH1 | PD | 11 | 855 | 2017-02-17 23:00 | 2017-02-18 02:33 | 475 | 520 | 477 | Drum relief/safety valves (Single drum only) | F590Load Reduction #5Unit 1 was derated for Precision to set safeties. | Ghent | Derate | Coal | 3 | 2017 | 2 | 3.55 | 0.30721 | 146.5399 | 41.2788 | 41
GH1 | PO | 12 | 1801 | 2017-03-11 00:41 | 2017-04-03 00:27 | 0 | 520 | 477 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Outage #7Unit 1 was removed from service for a Planned Outage. | Ghent | Other | Coal | 3 | 2017 | 3 | 551.7667 | 551.7667 | 263192.7 | 477 | 477
GH1 | PD | 13 | 344 | 2017-04-10 23:00 | 2017-04-11 02:25 | 470 | 520 | 477 | Pulverizer inspection | F530Load Reduction #6Removed 1-6 Mill from service to inspect and check exhauster | Ghent | Derate | Coal | 3 | 2017 | 4 | 3.4167 | 0.32853 | 156.7067 | 45.8654 | 46
GH1 | PD | 14 | 3410 | 2017-04-12 01:00 | 2017-04-12 01:52 | 325 | 520 | 477 | Feedwater pump | F790Load Reduction #71-1 Boiler feed pump emergency bearing oil pump testing. | Ghent | Derate | Coal | 3 | 2017 | 4 | 0.86667 | 0.325 | 155.025 | 178.875 | 179
GH1 | PD | 15 | 250 | 2017-04-28 23:00 | 2017-04-29 01:14 | 480 | 520 | 477 | Pulverizer feeders | F590Load Reduction #81-6 Feeder was removed from service to replace the control bo | Ghent | Derate | Coal | 3 | 2017 | 4 | 2.2333 | 0.17179 | 81.9462 | 36.6923 | 37
GH1 | PD | 16 | 4261 | 2017-04-29 02:11 | 2017-04-29 02:38 | 300 | 520 | 477 | Control valves | F090Load Reduction #9Load was reduced to stroke and calibrate the 1-5 governor val | Ghent | Derate | Coal | 3 | 2017 | 4 | 0.45 | 0.19038 | 90.8135 | 201.8077 | 202
GH1 | D1 | 17 | 9270 | 2017-04-29 17:16 | 2017-04-29 21:26 | 470 | 520 | 477 | Wet coal | F830Load Reduction #101-1 Feeder plugged with wet coal. | Ghent | Derate | Coal | 3 | 2017 | 4 | 4.1667 | 0.40064 | 191.1058 | 45.8654 | 46
GH1 | D1 | 18 | 250 | 2017-04-30 07:35 | 2017-04-30 10:08 | 450 | 520 | 477 | Pulverizer feeders | F830Load Reduction #111-6 Feeder clean out conveyor failed. | Ghent | Derate | Coal | 3 | 2017 | 4 | 2.55 | 0.34327 | 163.7394 | 64.2115 | 64
GH1 | MO | 19 | 3246 | 2017-05-20 22:15 | 2017-05-21 17:24 | 0 | 520 | 477 | Cooling tower fouling | F590Outage #8Unit 1 was removed from service to clean the cooling tower screens. | Ghent | Maintenance | Coal | 3 | 2017 | 5 | 19.15 | 19.15 | 9134.55 | 477 | 477
GH1 | PD | 21 | 250 | 2017-06-07 03:24 | 2017-06-07 04:47 | 460 | 520 | 477 | Pulverizer feeders | Load Reduction #121-6 Mill feeder belt wiper was in need of repair. | Ghent | Derate | Coal | 3 | 2017 | 6 | 1.3833 | 0.15962 | 76.1365 | 55.0385 | 55
GH1 | MO | 20 | 3110 | 2017-06-10 09:16 | 2017-06-11 06:16 | 0 | 520 | 477 | Condenser tube leaks | F540Outage #9Unit was removed from service due to a Main Condenser tube leak. | Ghent | Maintenance | Coal | 3 | 2017 | 6 | 21 | 21 | 10017 | 477 | 477
GH1 | U1 | 22 | 1080 | 2017-06-14 22:06 | 2017-06-18 04:29 | 0 | 520 | 477 | Economizer B | F540Outage #10GH1 was forced off line due to an economizer tube leak. | Ghent | Outage | Coal | 3 | 2017 | 6 | 78.3833 | 78.3833 | 37388.85 | 477 | 477
GH1 | MO | 23 | 1060 | 2017-07-07 22:31 | 2017-07-10 | 0 | 520 | 477 | First reheater A | F540Outage #11Unit 1 was removed from service due to a reheat tube leak in the boi | Ghent | Maintenance | Coal | 3 | 2017 | 7 | 49.4833 | 49.4833 | 23603.55 | 477 | 477
GH1 | ME | 25 | 1060 | 2017-07-10 | 2017-07-10 08:40 | 0 | 520 | 477 | First reheater A | F540Outage #12Reheat boiler tube leak repairs extended beyond 7/10/17 @ 0000. | Ghent | Maintenance | Coal | 3 | 2017 | 7 | 8.6667 | 8.6667 | 4134 | 477 | 477
GH1 | D1 | 24 | 3341 | 2017-07-10 15:51 | 2017-07-13 07:48 | 460 | 520 | 477 | Other LP heater - general | Load Reduction #13Load was reduced due to having both LP heaters out of service. | Ghent | Derate | Coal | 3 | 2017 | 7 | 63.95 | 7.3788 | 3519.7096 | 55.0385 | 55
GH1 | PD | 26 | 340 | 2017-08-04 05:00 | 2017-08-04 09:00 | 450 | 520 | 477 | Other pulverizer problems | F040Load Reduction #141-2 Mill exhauster bearing replacement. | Ghent | Derate | Coal | 3 | 2017 | 8 | 4 | 0.53846 | 256.8462 | 64.2115 | 64
GH1 | PD | 27 | 250 | 2017-08-07 21:47 | 2017-08-08 03:26 | 460 | 520 | 477 | Pulverizer feeders | F090Load Reduction #15Calibration of U1 feeders: 1-1, 1-2, -13 and 1-5. | Ghent | Derate | Coal | 3 | 2017 | 8 | 5.65 | 0.65192 | 310.9673 | 55.0385 | 55
GH1 | PD | 28 | 340 | 2017-08-10 22:18 | 2017-08-10 23:57 | 450 | 520 | 477 | Other pulverizer problems | F590Load Reduction #161-6 Mill was out of service to install the zero speed cover. | Ghent | Derate | Coal | 3 | 2017 | 8 | 1.65 | 0.22212 | 105.949 | 64.2115 | 64
GH1 | PD | 29 | 344 | 2017-08-14 22:00 | 2017-08-15 04:01 | 460 | 520 | 477 | Pulverizer inspection | F530Load Reduction #171-2 Mill was removed from service for an inspection due to k | Ghent | Derate | Coal | 3 | 2017 | 8 | 6.0167 | 0.69423 | 331.1481 | 55.0385 | 55
GH1 | D1 | 31 | 250 | 2017-08-15 12:00 | 2017-08-15 16:34 | 410 | 520 | 477 | Pulverizer feeders | Load Reduction #191-6 Mill feeder belt shifted to one side and tripped the feeder. | Ghent | Derate | Coal | 3 | 2017 | 8 | 4.5667 | 0.96603 | 460.7942 | 100.9038 | 101
GH1 | D1 | 32 | 340 | 2017-08-16 14:14 | 2017-08-16 14:43 | 480 | 520 | 477 | Other pulverizer problems | Load Reduction #201-5 Mill temperatures became high and 1-2 Mill was already out o | Ghent | Derate | Coal | 3 | 2017 | 8 | 0.48333 | 0.037179 | 17.7346 | 36.6923 | 37
GH1 | D1 | 33 | 340 | 2017-08-16 14:43 | 2017-08-21 09:46 | 500 | 520 | 477 | Other pulverizer problems | Load Reduction #211-2 Mill is out of service due to a broken veritical shaft. | Ghent | Derate | Coal | 3 | 2017 | 8 | 115.05 | 4.425 | 2110.725 | 18.3462 | 18
GH1 | MO | 35 | 3110 | 2017-09-09 06:25 | 2017-09-09 14:49 | 0 | 520 | 477 | Condenser tube leaks | F540Outage #14The Reserve Outage was changed to a Maintenance Outage to repair con | Ghent | Maintenance | Coal | 3 | 2017 | 9 | 8.4 | 8.4 | 4006.8 | 477 | 477
GH1 | D4 | 37 | 3412 | 2017-09-12 12:00 | 2017-09-13 12:00 | 350 | 520 | 477 | Feedwater pump drive - steam turbine | F090Load Reduction #221-1 BFP HP control valve out of calibration. | Ghent | Derate | Coal | 3 | 2017 | 9 | 24 | 7.8462 | 3742.6154 | 155.9423 | 156
GH1 | D1 | 38 | 250 | 2017-09-15 18:00 | 2017-09-15 20:31 | 465 | 520 | 477 | Pulverizer feeders | Load Reduction #231-2 Feeder tach input alarm came in. Electricians found a large | Ghent | Derate | Coal | 3 | 2017 | 9 | 2.5167 | 0.26619 | 126.9707 | 50.4519 | 50
GH1 | PD | 39 | 344 | 2017-09-26 23:32 | 2017-09-27 00:23 | 480 | 520 | 477 | Pulverizer inspection | F530Load Reduction #241-1 Mill was removed from service due to noise in pyrite sec | Ghent | Derate | Coal | 3 | 2017 | 9 | 0.85 | 0.065385 | 31.1885 | 36.6923 | 37
GH1 | PD | 40 | 250 | 2017-10-11 23:00 | 2017-10-12 04:00 | 480 | 520 | 477 | Pulverizer feeders | F090Load Reduction #25Calibration of 1-6 feeder. | Ghent | Derate | Coal | 3 | 2017 | 10 | 5 | 0.38462 | 183.4615 | 36.6923 | 37
GH1 | D1 | 42 | 250 | 2017-10-12 05:22 | 2017-10-12 06:40 | 480 | 520 | 477 | Pulverizer feeders | F830Load Reduction #271-6 Feeder circut board Issues. | Ghent | Derate | Coal | 3 | 2017 | 10 | 1.3 | 0.1 | 47.7 | 36.6923 | 37
GH1 | D1 | 43 | 1401 | 2017-10-14 10:48 | 2017-10-14 12:36 | 400 | 520 | 477 | Forced draft fan dampers | F930Load Reduction #281-2 FD Fan inlet vane drive had a striped gear. | Ghent | Derate | Coal | 3 | 2017 | 10 | 1.8 | 0.41538 | 198.1385 | 110.0769 | 110
GH1 | U1 | 44 | 1100 | 2017-10-18 22:54 | 2017-10-19 21:54 | 0 | 520 | 477 | Waterwall (Furnace wall) B | F540Outage #16 GH1 was forced offline due to water wall tube leak on 4th elevation | Ghent | Outage | Coal | 3 | 2017 | 10 | 23 | 23 | 10971 | 477 | 477
GH1 | D1 | 45 | 920 | 2017-10-29 22:05 | 2017-10-30 02:18 | 240 | 520 | 477 | Other slag and ash removal problems A | FS00Load Reduction #28Unit 1 had heavy slag build up around IK 6, | Ghent | Derate | Coal | 3 | 2017 | 10 | 4.2167 | 2.2705 | 1083.0346 | 256.8462 | 257
GH1 | D1 | 46 | 920 | 2017-11-14 22:45 | 2017-11-15 17:24 | 200 | 520 | 477 | Other slag and ash removal problems A | FS00Load Reduction #29Unit 1 was derated due to boiler de-slag. | Ghent | Derate | Coal | 3 | 2017 | 11 | 18.65 | 11.4769 | 5474.4923 | 293.5385 | 294
GH1 | D1 | 47 | 3410 | 2017-11-15 19:19 | 2017-11-15 19:29 | 350 | 520 | 477 | Feedwater pump | F830Load Reduction #301-2 BFP vibration derated Unit 1. | Ghent | Derate | Coal | 3 | 2017 | 11 | 0.16667 | 0.054487 | 25.9904 | 155.9423 | 156
GH1 | D1 | 48 | 250 | 2017-11-20 03:18 | 2017-11-20 07:23 | 460 | 520 | 477 | Pulverizer feeders | F830Load Reduction #311-3 Coal feeder plugged. | Ghent | Derate | Coal | 3 | 2017 | 11 | 4.0833 | 0.47115 | 224.7404 | 55.0385 | 55
GH1 | D1 | 52 | 250 | 2017-11-20 21:06 | 2017-11-20 23:04 | 460 | 520 | 477 | Pulverizer feeders | F830Load Reduction #351-3 coal feeder plugged causing derate. | Ghent | Derate | Coal | 3 | 2017 | 11 | 1.9667 | 0.22692 | 108.2423 | 55.0385 | 55
GH1 | D1 | 49 | 920 | 2017-11-22 08:00 | 2017-11-22 10:53 | 180 | 520 | 477 | Other slag and ash removal problems A | FS00Load Reduction #32GH1 was derated due to boiler slagging. | Ghent | Derate | Coal | 3 | 2017 | 11 | 2.8833 | 1.8853 | 899.2673 | 311.8846 | 312
GH1 | D1 | 50 | 250 | 2017-11-22 11:39 | 2017-11-22 13:01 | 425 | 520 | 477 | Pulverizer feeders | F830Load Reduction #331-3 coal mill feeder plugged. | Ghent | Derate | Coal | 3 | 2017 | 11 | 1.3667 | 0.24968 | 119.0971 | 87.1442 | 87
GH1 | D1 | 51 | 320 | 2017-11-26 10:51 | 2017-11-26 13:39 | 460 | 520 | 477 | Foreign object in Pulverizers mill | Load Reduction #341-1 and 1-4 mills were removed from service to remove metal from | Ghent | Derate | Coal | 3 | 2017 | 11 | 2.8 | 0.32308 | 154.1077 | 55.0385 | 55
GH1 | D1 | 53 | 250 | 2017-12-05 07:30 | 2017-12-05 14:03 | 460 | 520 | 477 | Pulverizer feeders | F830Load Reduction #361-4 mill feeder would not calibrate last night. Found belt t | Ghent | Derate | Coal | 3 | 2017 | 12 | 6.55 | 0.75577 | 360.5019 | 55.0385 | 55
GH1 | PD | 1 | 920 | 2018-01-05 00:02 | 2018-01-05 04:00 | 200 | 520 | 477 | Other slag and ash removal problems A | F830Load Reduction #1U-1 boiler deslag. | Ghent | Derate | Coal | 3 | 2018 | 1 | 3.9667 | 2.441 | 1164.3692 | 293.5385 | 294
GH1 | PD | 2 | 920 | 2018-01-07 20:11 | 2018-01-08 00:40 | 240 | 520 | 477 | Other slag and ash removal problems A | F830Load Reduction #2U-1 planned deslag. | Ghent | Derate | Coal | 3 | 2018 | 1 | 4.4833 | 2.4141 | 1151.5269 | 256.8462 | 257
GH1 | PD | 3 | 340 | 2018-01-11 07:00 | 2018-01-11 14:20 | 460 | 520 | 477 | Other pulverizer problems | F590Load Reduction #3Planned derate for 1-6 feeder repairs. | Ghent | Derate | Coal | 3 | 2018 | 1 | 7.3333 | 0.84615 | 403.6154 | 55.0385 | 55
GH1 | D1 | 4 | 920 | 2018-01-18 18:24 | 2018-01-20 00:17 | 200 | 520 | 477 | Other slag and ash removal problems A | F830Load Reduction #4Slagging of the boiler in the wet ash pit. | Ghent | Derate | Coal | 3 | 2018 | 1 | 29.8833 | 18.3897 | 8771.9077 | 293.5385 | 294
GH1 | PD | 5 | 344 | 2018-01-22 22:00 | 2018-01-23 03:49 | 460 | 520 | 477 | Pulverizer inspection | F530Load Reduction #5Planned Derate for pre-outage mill inspection of 1-1 & 1-6 mi | Ghent | Derate | Coal | 3 | 2018 | 1 | 5.8167 | 0.67115 | 320.1404 | 55.0385 | 55
GH1 | PD | 6 | 344 | 2018-01-23 22:00 | 2018-01-24 04:32 | 460 | 520 | 477 | Pulverizer inspection | F530Load Reduction #6Pre-outage mill inspections 1-2 & 1-3. | Ghent | Derate | Coal | 3 | 2018 | 1 | 6.5333 | 0.75385 | 359.5846 | 55.0385 | 55
GH1 | PD | 7 | 344 | 2018-01-24 22:00 | 2018-01-25 03:51 | 460 | 520 | 477 | Pulverizer inspection | F530Load Reduction #7Pre-outage mill inspections 1-4 & 1-5. | Ghent | Derate | Coal | 3 | 2018 | 1 | 5.85 | 0.675 | 321.975 | 55.0385 | 55
GH1 | PD | 8 | 310 | 2018-01-25 22:00 | 2018-01-26 01:51 | 460 | 520 | 477 | Pulverizer mills | F590Load Reduction #8Cleaned mill Peto tubes.. | Ghent | Derate | Coal | 3 | 2018 | 1 | 3.85 | 0.44423 | 211.8981 | 55.0385 | 55
GH1 | D1 | 9 | 320 | 2018-01-30 16:29 | 2018-01-30 20:04 | 460 | 520 | 477 | Foreign object in Pulverizers mill | F590Load Reduction #91-5 millhad a piece of concrete in the grinding section. | Ghent | Derate | Coal | 3 | 2018 | 1 | 3.5833 | 0.41346 | 197.2212 | 55.0385 | 55
GH1 | D1 | 10 | 1480 | 2018-02-07 18:00 | 2018-02-07 18:31 | 36 | 520 | 477 | Other induced draft fan problems | F820Load Reduction #101-6 pulverizer loaded up when being placed in service. Furn | Ghent | Derate | Coal | 3 | 2018 | 2 | 0.51667 | 0.4809 | 229.3881 | 443.9769 | 444
GH1 | U1 | 11 | 1450 | 2018-02-07 18:31 | 2018-02-07 21:21 | 0 | 520 | 477 | Other air supply problems | Outage #1Loss of ID fans due to furance pressure caused a flame out of the boiler. | Ghent | Outage | Coal | 3 | 2018 | 2 | 2.8333 | 2.8333 | 1351.5 | 477 | 477
GH1 | D1 | 12 | 1470 | 2018-02-21 10:21 | 2018-02-21 11:54 | 200 | 520 | 477 | Induced draft fan motors and drives | F820Load Reduction #11Loss of 3 ID fans. | Ghent | Derate | Coal | 3 | 2018 | 2 | 1.55 | 0.95385 | 454.9846 | 293.5385 | 294
GH1 | D1 | 13 | 1471 | 2018-02-21 11:54 | 2018-02-22 11:59 | 450 | 520 | 477 | Induced draft fan motors - variable speed | F820Load Reduction #121-1A ID fan out of service. | Ghent | Derate | Coal | 3 | 2018 | 2 | 24.0833 | 3.242 | 1546.4279 | 64.2115 | 64
GH1 | U1 | 14 | 1000 | 2018-02-24 17:00 | 2018-02-27 03:43 | 0 | 520 | 477 | Waterwall (Furnace wall) A | Outage #2Unit was removed from service due to a water wall leak on 7th floor. | Ghent | Outage | Coal | 3 | 2018 | 2 | 58.7167 | 58.7167 | 28007.85 | 477 | 477
GH1 | U1 | 16 | 3520 | 2018-02-28 15:45 | 2018-02-28 17:45 | 0 | 520 | 477 | HP Extraction steam piping | Outage #4Unit was placed on a forced outage due to a drain line broken off the ext | Ghent | Outage | Coal | 3 | 2018 | 2 | 2 | 2 | 954 | 477 | 477
GH1 | PO | 18 | 1801 | 2018-03-02 06:00 | 2018-04-02 | 0 | 520 | 477 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Outage #6Unit 1 was moved from Reserve Shutdown and placed on Planned Outage. | Ghent | Other | Coal | 3 | 2018 | 3 | 738 | 738 | 352026 | 477 | 477
GH1 | PE | 19 | 1801 | 2018-04-02 | 2018-04-03 18:55 | 0 | 520 | 477 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Outage #7 Unit 1 was placed on a Planned Outage extension. | Ghent | Other | Coal | 3 | 2018 | 4 | 42.9167 | 42.9167 | 20471.25 | 477 | 477
GH1 | D1 | 20 | 1432 | 2018-04-05 22:20 | 2018-04-05 23:17 | 300 | 520 | 477 | Air supply duct expansion joints | F540Load Reduction #13Reduced load to repair wind box leak on 6 1/2 floor D corner | Ghent | Derate | Coal | 3 | 2018 | 4 | 0.95 | 0.40192 | 191.7173 | 201.8077 | 202
GH1 | PD | 21 | 344 | 2018-04-19 23:00 | 2018-04-20 01:14 | 460 | 520 | 477 | Pulverizer inspection | F530Load Reduction #141-1 coal mill maintenance inspection due to poor coal finene | Ghent | Derate | Coal | 3 | 2018 | 4 | 2.2333 | 0.25769 | 122.9192 | 55.0385 | 55
GH1 | PD | 22 | 3415 | 2018-04-26 23:39 | 2018-04-27 01:46 | 320 | 520 | 477 | Feedwater pump/drive lube oil system | F590Load Reduction #151-1 BFPT EOP low pressure switch repair. | Ghent | Derate | Coal | 3 | 2018 | 4 | 2.1167 | 0.8141 | 388.3269 | 183.4615 | 183
GH2 | PD | 1 | 310 | 2013-01-03 22:30 | 2013-01-04 02:00 | 475 | 520 | 486 | Pulverizer mills | Load Reduction #12-6 Mill out of service to retorque race. | Ghent | Derate | Coal | 3 | 2013 | 1 | 3.5 | 0.30288 | 147.2019 | 42.0577 | 42
GH2 | D1 | 3 | 340 | 2013-01-09 06:46 | 2013-01-09 07:01 | 475 | 520 | 486 | Other pulverizer problems | Load Reduction #32-4 Mill tripped for no apparent reason. | Ghent | Derate | Coal | 3 | 2013 | 1 | 0.25 | 0.021635 | 10.5144 | 42.0577 | 42
GH2 | D1 | 4 | 3415 | 2013-01-28 07:23 | 2013-01-28 08:08 | 330 | 520 | 486 | Feedwater pump/drive lube oil system | Load Reduction #42-2 BFP oil seal leaking oil had to take pump off to reseat seal. | Ghent | Derate | Coal | 3 | 2013 | 1 | 0.75 | 0.27404 | 133.1827 | 177.5769 | 178
GH2 | D1 | 5 | 9280 | 2013-02-03 22:30 | 2013-02-03 23:27 | 470 | 520 | 486 | Frozen coal | Load Reduction #52-1 Feeder tripped due to frozen coal. | Ghent | Derate | Coal | 3 | 2013 | 2 | 0.95 | 0.091346 | 44.3942 | 46.7308 | 47
GH2 | U3 | 6 | 4611 | 2013-02-04 11:09 | 2013-02-05 07:34 | 0 | 520 | 486 | Hydrogen coolers | F540Outage #1The unit was running with a hydrogen leak in the generator. The leak | Ghent | Outage | Coal | 3 | 2013 | 2 | 20.4167 | 20.4167 | 9922.5 | 486 | 486
GH2 | D1 | 7 | 1850 | 2013-02-05 15:30 | 2013-02-05 18:27 | 440 | 520 | 486 | Boiler water condition (not feedwater water quality) | Load Reduction #6Unit 2 was derated after start up due to reduced pressure caused | Ghent | Derate | Coal | 3 | 2013 | 2 | 2.95 | 0.45385 | 220.5692 | 74.7692 | 75
GH2 | D1 | 8 | 1850 | 2013-02-05 18:27 | 2013-02-05 19:11 | 480 | 520 | 486 | Boiler water condition (not feedwater water quality) | Load Reduction #7Unit 2 was derated after start up due to reduced pressure caused | Ghent | Derate | Coal | 3 | 2013 | 2 | 0.73333 | 0.05641 | 27.4154 | 37.3846 | 37
GH2 | D1 | 9 | 3441 | 2013-02-05 19:11 | 2013-02-05 20:34 | 480 | 520 | 486 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | Load Reduction #8Unit 2 was derated due to HP heater level control issues. | Ghent | Derate | Coal | 3 | 2013 | 2 | 1.3833 | 0.10641 | 51.7154 | 37.3846 | 37
GH2 | D1 | 10 | 3531 | 2013-02-05 20:34 | 2013-02-05 22:24 | 408 | 520 | 486 | IP Extraction steam valves | Load Reduction #9Unit 2 was derated due to 3 feedwater heaters being out of servic | Ghent | Derate | Coal | 3 | 2013 | 2 | 1.8333 | 0.39487 | 191.9077 | 104.6769 | 105
GH2 | D1 | 11 | 3441 | 2013-02-05 22:24 | 2013-02-06 09:15 | 480 | 520 | 486 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | Load Reduction #10Unit 2 was derated due to HP heater level controls. | Ghent | Derate | Coal | 3 | 2013 | 2 | 10.85 | 0.83462 | 405.6231 | 37.3846 | 37
GH2 | U1 | 12 | 1000 | 2013-02-10 16:10 | 2013-02-12 04:22 | 0 | 520 | 486 | Waterwall (Furnace wall) A | F540Outage #2A water wall tube leak developed on 8th floor SE corner of the boiler | Ghent | Outage | Coal | 3 | 2013 | 2 | 36.2 | 36.2 | 17593.2 | 486 | 486
GH2 | D1 | 13 | 760 | 2013-02-15 19:25 | 2013-02-15 19:50 | 480 | 520 | 486 | Boiler recirculation valves | Load Reduction #112-1 BCWP safety leaking. Dropped load to get safety to reseat. | Ghent | Derate | Coal | 3 | 2013 | 2 | 0.41667 | 0.032051 | 15.5769 | 37.3846 | 37
GH2 | D1 | 14 | 760 | 2013-02-15 19:50 | 2013-02-15 21:15 | 400 | 520 | 486 | Boiler recirculation valves | Load Reduction #122-1 BCWP safety leaking. Dropped load to 400 MWs to get safety | Ghent | Derate | Coal | 3 | 2013 | 2 | 1.4167 | 0.32692 | 158.8846 | 112.1538 | 112
GH2 | D1 | 15 | 3415 | 2013-02-17 06:55 | 2013-02-17 08:10 | 320 | 520 | 486 | Feedwater pump/drive lube oil system | Load Reductiom #132-2 BFP started slinging oil from IB seal. Had to drop load and | Ghent | Derate | Coal | 3 | 2013 | 2 | 1.25 | 0.48077 | 233.6538 | 186.9231 | 187
GH2 | D1 | 16 | 3415 | 2013-02-19 06:56 | 2013-02-19 07:52 | 320 | 520 | 486 | Feedwater pump/drive lube oil system | Load Reduction #142-2 BFP IB bearing started leaking oil. Had to remove the pump | Ghent | Derate | Coal | 3 | 2013 | 2 | 0.93333 | 0.35897 | 174.4615 | 186.9231 | 187
GH2 | D1 | 17 | 346 | 2013-03-05 13:10 | 2013-03-05 16:06 | 475 | 520 | 486 | Pulverizer pyrite removal system | Load Reduction #152-2 Mill pyrite scraper broke off. | Ghent | Derate | Coal | 3 | 2013 | 3 | 2.9333 | 0.25385 | 123.3692 | 42.0577 | 42
GH2 | D1 | 18 | 1475 | 2013-03-06 11:24 | 2013-03-06 13:42 | 200 | 520 | 486 | Induced draft fan controls | Load Reduction #162-2 ID fan tripped on false vibration indication | Ghent | Derate | Coal | 3 | 2013 | 3 | 2.3 | 1.4154 | 687.8769 | 299.0769 | 299
GH2 | MO | 19 | 1000 | 2013-03-15 13:01 | 2013-03-17 11:31 | 0 | 520 | 486 | Waterwall (Furnace wall) A | F380Outage #3Unit 2 has been running with a water wall tube leak for over a week. | Ghent | Maintenance | Coal | 3 | 2013 | 3 | 46.5 | 46.5 | 22599 | 486 | 486
GH2 | D1 | 20 | 3440 | 2013-03-21 23:14 | 2013-03-22 01:53 | 465 | 520 | 486 | High pressure heater tube leaks | Load Reduction #17Took High Pressure heaters out of service to check for leaks. | Ghent | Derate | Coal | 3 | 2013 | 3 | 2.65 | 0.28029 | 136.2202 | 51.4038 | 51
GH2 | D1 | 21 | 346 | 2013-03-22 14:15 | 2013-03-22 18:28 | 460 | 520 | 486 | Pulverizer pyrite removal system | Load Reduction #182-2 Mill pyrite scraper broke off. | Ghent | Derate | Coal | 3 | 2013 | 3 | 4.2167 | 0.48654 | 236.4577 | 56.0769 | 56
GH2 | D1 | 22 | 346 | 2013-03-25 21:10 | 2013-03-26 17:00 | 490 | 520 | 486 | Pulverizer pyrite removal system | Load Reduction #192-4 Mill vane wheel and pyrite scraper broke. | Ghent | Derate | Coal | 3 | 2013 | 3 | 19.8333 | 1.1442 | 556.0962 | 28.0385 | 28
GH2 | D1 | 23 | 3661 | 2013-03-26 19:41 | 2013-03-26 23:59 | 490 | 520 | 486 | 4160-volt circuit breakers | Load Reduction #20Relay in 2-2 Mill 4KV breaker failed causing the mill to trip. | Ghent | Derate | Coal | 3 | 2013 | 3 | 4.3 | 0.24808 | 120.5654 | 28.0385 | 28
GH2 | D1 | 24 | 344 | 2013-03-27 13:42 | 2013-03-27 16:22 | 480 | 520 | 486 | Pulverizer inspection | Load Reduction #212-4 Mill was removed for inspection. | Ghent | Derate | Coal | 3 | 2013 | 3 | 2.6667 | 0.20513 | 99.6923 | 37.3846 | 37
GH2 | D1 | 25 | 346 | 2013-03-31 21:05 | 2013-04-01 13:20 | 485 | 520 | 486 | Pulverizer pyrite removal system | Load Reduction #222-4 mill out of service. Pyrite scrapers broken off. | Ghent | Derate | Coal | 3 | 2013 | 3 | 16.25 | 1.0938 | 531.5625 | 32.7115 | 33
GH2 | D1 | 26 | 253 | 2013-04-19 18:59 | 2013-04-20 00:57 | 470 | 520 | 486 | Pulverizer feeder motor | Load Reduction #232-1 Mill feeder motor failed. | Ghent | Derate | Coal | 3 | 2013 | 4 | 5.9667 | 0.57372 | 278.8269 | 46.7308 | 47
GH2 | D1 | 27 | 340 | 2013-04-21 10:20 | 2013-04-21 14:14 | 470 | 520 | 486 | Other pulverizer problems | Load Reduction #242-5 Mill air flow went to minimum causing mill to load up. | Ghent | Derate | Coal | 3 | 2013 | 4 | 3.9 | 0.375 | 182.25 | 46.7308 | 47
GH2 | D1 | 28 | 340 | 2013-04-25 13:11 | 2013-04-25 20:35 | 440 | 520 | 486 | Other pulverizer problems | Load Reduction #252-2 Mill journal locked up. | Ghent | Derate | Coal | 3 | 2013 | 4 | 7.4 | 1.1385 | 553.2923 | 74.7692 | 75
GH2 | PO | 29 | 1812 | 2013-04-26 22:30 | 2013-05-01 05:01 | 0 | 520 | 486 | Boiler Inspections - scheduled or routine | F590Outage #4Removed the unit from service to perform the annual Planned Outage. | Ghent | Other | Coal | 3 | 2013 | 4 | 102.5167 | 102.5167 | 49823.1 | 486 | 486
GH2 | D1 | 30 | 1850 | 2013-05-01 14:00 | 2013-05-01 16:00 | 456 | 520 | 486 | Boiler water condition (not feedwater water quality) | Load Reduction #26Silica levels were high in the boiler after the unit returned to | Ghent | Derate | Coal | 3 | 2013 | 5 | 2 | 0.24615 | 119.6308 | 59.8154 | 60
GH2 | PD | 31 | 340 | 2013-05-01 16:00 | 2013-05-01 16:40 | 480 | 520 | 486 | Other pulverizer problems | F590Load Reduction #272-4 Mill is out of service to rebuild the gear box. | Ghent | Derate | Coal | 3 | 2013 | 5 | 0.66667 | 0.051282 | 24.9231 | 37.3846 | 37
GH2 | PD | 32 | 340 | 2013-05-01 16:40 | 2013-05-04 22:38 | 510 | 520 | 486 | Other pulverizer problems | F590Load Reduction #282-4 Mill is out of service to rebuild the gear box. | Ghent | Derate | Coal | 3 | 2013 | 5 | 77.9667 | 1.4994 | 728.6885 | 9.3462 | 9
GH2 | MO | 33 | 4302 | 2013-05-04 22:38 | 2013-05-04 23:07 | 0 | 520 | 486 | Turbine trip devices (including instruments) | F790Outage #5A new Main Turbine Mechanical Overspeed trip mechanism was installed | Ghent | Maintenance | Coal | 3 | 2013 | 5 | 0.48333 | 0.48333 | 234.9 | 486 | 486
GH2 | D1 | 34 | 340 | 2013-05-04 23:07 | 2013-05-05 00:23 | 507 | 520 | 486 | Other pulverizer problems | Load Reduction #292-4 Mill gear box rebuild derate continued following the Unit 2 | Ghent | Derate | Coal | 3 | 2013 | 5 | 1.2667 | 0.031667 | 15.39 | 12.15 | 12
GH2 | D1 | 35 | 340 | 2013-05-13 05:30 | 2013-05-13 07:30 | 495 | 520 | 486 | Other pulverizer problems | Load Reduction #302-2 mill seal air hose leaking. | Ghent | Derate | Coal | 3 | 2013 | 5 | 2 | 0.096154 | 46.7308 | 23.3654 | 23
GH2 | D1 | 36 | 340 | 2013-05-14 02:45 | 2013-05-14 05:15 | 495 | 520 | 486 | Other pulverizer problems | Load Reduction #312-4 mill out of service to re-torque mill race after outage repa | Ghent | Derate | Coal | 3 | 2013 | 5 | 2.5 | 0.12019 | 58.4135 | 23.3654 | 23
GH2 | D1 | 37 | 8601 | 2013-05-28 20:13 | 2013-05-28 21:54 | 375 | 520 | 486 | SO3 mitigation | Load Reduction #32Sorbent injection blower system tripped causing high emissions a | Ghent | Derate | Coal | 3 | 2013 | 5 | 1.6833 | 0.46939 | 228.124 | 135.5192 | 136
GH2 | D1 | 38 | 340 | 2013-06-06 19:50 | 2013-06-07 13:14 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #332-2 Mill journal locked up. Parts of the journal broke the pyri | Ghent | Derate | Coal | 3 | 2013 | 6 | 17.4 | 2.0077 | 975.7385 | 56.0769 | 56
GH2 | D1 | 39 | 1455 | 2013-06-13 18:00 | 2013-06-13 20:10 | 190 | 520 | 486 | Induced draft fans | Load Reduction #342-1 ID fan tripped when the coolant water pumps swapped. | Ghent | Derate | Coal | 3 | 2013 | 6 | 2.1667 | 1.375 | 668.25 | 308.4231 | 308
GH2 | PD | 40 | 340 | 2013-06-13 23:00 | 2013-06-14 03:12 | 68 | 520 | 486 | Other pulverizer problems | F590Load Reduction #352-2 Mill was out of service to replace a ceramic roll. | Ghent | Derate | Coal | 3 | 2013 | 6 | 4.2 | 3.6508 | 1774.2738 | 422.4462 | 422
GH2 | D1 | 41 | 1470 | 2013-06-17 03:10 | 2013-06-17 08:36 | 250 | 520 | 486 | Induced draft fan motors and drives | Load Reduction #362-1 ID fan tripped for unknown reasons. | Ghent | Derate | Coal | 3 | 2013 | 6 | 5.4333 | 2.8212 | 1371.0808 | 252.3462 | 252
GH2 | D1 | 42 | 1455 | 2013-06-20 04:05 | 2013-06-20 10:14 | 200 | 520 | 486 | Induced draft fans | Load Reduction #372-1 ID fan tripped when the coolant water pumps showed not avail | Ghent | Derate | Coal | 3 | 2013 | 6 | 6.15 | 3.7846 | 1839.3231 | 299.0769 | 299
GH2 | D1 | 43 | 360 | 2013-07-08 10:30 | 2013-07-08 13:15 | 450 | 520 | 486 | Burners | Load Reduction #382-6 Mill 'C' burner fire. The mill was removed from service to | Ghent | Derate | Coal | 3 | 2013 | 7 | 2.75 | 0.37019 | 179.9135 | 65.4231 | 65
GH2 | D1 | 44 | 1050 | 2013-07-09 15:15 | 2013-07-10 22:57 | 438 | 520 | 486 | Second superheater B | Load Reduction #39U2 Boiler tube leak in the front superheat pendant area. Reduce | Ghent | Derate | Coal | 3 | 2013 | 7 | 31.7 | 4.9988 | 2429.4392 | 76.6385 | 77
GH2 | MO | 45 | 1050 | 2013-07-10 22:57 | 2013-07-14 10:30 | 0 | 520 | 486 | Second superheater B | F540Outage #6Unit was running with tube leak in upper furnace area above upper slo | Ghent | Maintenance | Coal | 3 | 2013 | 7 | 83.55 | 83.55 | 40605.3 | 486 | 486
GH2 | D1 | 46 | 1850 | 2013-07-14 09:10 | 2013-07-14 10:30 | 480 | 520 | 486 | Boiler water condition (not feedwater water quality) | Load Reduction #40Unit 2 was derated due to boiler drum silica being high. Drum p | Ghent | Derate | Coal | 3 | 2013 | 7 | 1.3333 | 0.10256 | 49.8462 | 37.3846 | 37
GH2 | D1 | 48 | 360 | 2013-07-22 07:50 | 2013-07-22 12:55 | 450 | 520 | 486 | Burners | Load Reduction #422-6 C burner fire. Removed the mill from service. | Ghent | Derate | Coal | 3 | 2013 | 7 | 5.0833 | 0.68429 | 332.5673 | 65.4231 | 65
GH2 | PD | 49 | 340 | 2013-08-01 22:29 | 2013-08-02 05:20 | 480 | 520 | 486 | Other pulverizer problems | F530Load Reduction #432-3 Mill was off for inspection of pyrite scrapers. | Ghent | Derate | Coal | 3 | 2013 | 8 | 6.85 | 0.52692 | 256.0846 | 37.3846 | 37
GH2 | D1 | 50 | 344 | 2013-08-08 01:00 | 2013-08-08 03:20 | 480 | 520 | 486 | Pulverizer inspection | Load Reduction #442-5 Mill was off for inspection due to a noise in the pyrite sec | Ghent | Derate | Coal | 3 | 2013 | 8 | 2.3333 | 0.17949 | 87.2308 | 37.3846 | 37
GH2 | PD | 51 | 3410 | 2013-08-13 21:00 | 2013-08-14 03:42 | 320 | 520 | 486 | Feedwater pump | Load Reduction #452-2 BFP off to replace suction safety. | Ghent | Derate | Coal | 3 | 2013 | 8 | 6.7 | 2.5769 | 1252.3846 | 186.9231 | 187
GH2 | D1 | 52 | 1000 | 2013-08-26 15:55 | 2013-08-26 22:28 | 440 | 520 | 486 | Waterwall (Furnace wall) A | Load Reduction #46Boiler water wall leak on 7 2/3 at IR 75. Reduced pressure unti | Ghent | Derate | Coal | 3 | 2013 | 8 | 6.55 | 1.0077 | 489.7385 | 74.7692 | 75
GH2 | MO | 53 | 1000 | 2013-08-26 22:28 | 2013-08-27 23:20 | 0 | 520 | 486 | Waterwall (Furnace wall) A | F540Outage #7A leak developed in rear water wall tube on 7 1/2 level at IR #75. D | Ghent | Maintenance | Coal | 3 | 2013 | 8 | 24.8667 | 24.8667 | 12085.2 | 486 | 486
GH2 | SF | 54 | 380 | 2013-08-27 23:20 | 2013-08-28 02:46 | 0 | 520 | 486 | Light-off (igniter) systems (including fuel supply) | F540Outage #8While starting back up after the previous event with a water wall lea | Ghent | Outage | Coal | 3 | 2013 | 8 | 3.4333 | 3.4333 | 1668.6 | 486 | 486
GH2 | D1 | 55 | 3410 | 2013-09-06 10:45 | 2013-09-06 13:07 | 320 | 520 | 486 | Feedwater pump | Load Reduction #472-2 BFP low pressure stop valve controls failed. | Ghent | Derate | Coal | 3 | 2013 | 9 | 2.3667 | 0.91026 | 442.3846 | 186.9231 | 187
GH2 | D1 | 56 | 344 | 2013-09-09 15:36 | 2013-09-09 21:31 | 465 | 520 | 486 | Pulverizer inspection | Load Reduction #482-4 Mill off to inspect grinding section. | Ghent | Derate | Coal | 3 | 2013 | 9 | 5.9167 | 0.6258 | 304.1394 | 51.4038 | 51
GH2 | PD | 57 | 345 | 2013-09-14 03:00 | 2013-09-22 15:24 | 460 | 520 | 486 | Pulverizer overhaul | Load Reduction #492-5 Mill is out of service for a planned overhaul of the mill ge | Ghent | Derate | Coal | 3 | 2013 | 9 | 204.4 | 23.5846 | 11462.1231 | 56.0769 | 56
GH2 | D1 | 58 | 340 | 2013-09-19 23:00 | 2013-09-19 23:57 | 350 | 520 | 486 | Other pulverizer problems | Load Reduction #502-2 Mill off for inspection. Found south roll down on race. | Ghent | Derate | Coal | 3 | 2013 | 9 | 0.95 | 0.31058 | 150.9404 | 158.8846 | 159
GH2 | D1 | 59 | 3620 | 2013-09-21 16:35 | 2013-09-21 16:52 | 400 | 520 | 486 | Main transformer | Load Reduction #51U2 GSU developed an oil leak caused by excessive nitrogen blanke | Ghent | Derate | Coal | 3 | 2013 | 9 | 0.28333 | 0.065385 | 31.7769 | 112.1538 | 112
GH2 | D1 | 60 | 340 | 2013-09-22 11:45 | 2013-09-22 13:47 | 350 | 520 | 486 | Other pulverizer problems | F060Load Reduction #522-4 Mill race clamping ring broke. | Ghent | Derate | Coal | 3 | 2013 | 9 | 2.0333 | 0.66474 | 323.0654 | 158.8846 | 159
GH2 | U2 | 61 | 799 | 2013-09-22 15:24 | 2013-09-24 08:16 | 0 | 520 | 486 | Other miscellaneous piping system problems | F540Outage #9Steam was coming out of the penthouse on top of the boiler. The pent | Ghent | Outage | Coal | 3 | 2013 | 9 | 40.8667 | 40.8667 | 19861.2 | 486 | 486
GH2 | PD | 63 | 345 | 2013-09-24 08:16 | 2013-10-10 09:32 | 460 | 520 | 486 | Pulverizer overhaul | F590Load Reduction #532-5 Pulverizer is out of service for an overhaul. | Ghent | Derate | Coal | 3 | 2013 | 9 | 385.2667 | 44.4538 | 21604.5692 | 56.0769 | 56
GH2 | D1 | 64 | 280 | 2013-10-06 20:31 | 2013-10-07 02:58 | 360 | 520 | 486 | Pulverizer fires | Load Reduction #542-3 Mill had a fire in the pyrite section. Removed the mill fro | Ghent | Derate | Coal | 3 | 2013 | 10 | 6.45 | 1.9846 | 964.5231 | 149.5385 | 150
GH2 | PD | 65 | 340 | 2013-10-21 22:00 | 2013-10-22 15:17 | 460 | 520 | 486 | Other pulverizer problems | F590Load Reduction #552-3 Mill out of service to replace the dust plate in the pyr | Ghent | Derate | Coal | 3 | 2013 | 10 | 17.2833 | 1.9942 | 969.1962 | 56.0769 | 56
GH2 | D1 | 66 | 340 | 2013-10-22 07:53 | 2013-10-22 14:05 | 360 | 520 | 486 | Other pulverizer problems | Load Reduction #562-4 Mill off for inspection due to loud noise in grinding sectio | Ghent | Derate | Coal | 3 | 2013 | 10 | 6.2 | 1.9077 | 927.1385 | 149.5385 | 150
GH2 | PD | 67 | 344 | 2013-10-22 22:00 | 2013-10-23 00:54 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #572-2 Mill was out of service to inspect the grinding section. | Ghent | Derate | Coal | 3 | 2013 | 10 | 2.9 | 0.33462 | 162.6231 | 56.0769 | 56
GH2 | D1 | 68 | 350 | 2013-10-23 01:34 | 2013-10-23 05:24 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #582-4 Mill off for inspection due to fire on D burner line. | Ghent | Derate | Coal | 3 | 2013 | 10 | 3.8333 | 0.44231 | 214.9615 | 56.0769 | 56
GH2 | PD | 69 | 340 | 2013-10-24 22:00 | 2013-10-25 05:40 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #592-2 Mill out of service to inspect. Found bad journal. | Ghent | Derate | Coal | 3 | 2013 | 10 | 7.6667 | 0.88462 | 429.9231 | 56.0769 | 56
GH2 | D1 | 70 | 920 | 2013-11-05 23:15 | 2013-11-06 04:00 | 200 | 520 | 486 | Other slag and ash removal problems A | Load Reduction #60Dropped load to deslag the boiler and to catch up on ash. | Ghent | Derate | Coal | 3 | 2013 | 11 | 4.75 | 2.9231 | 1420.6154 | 299.0769 | 299
GH2 | PD | 71 | 3642 | 2013-11-09 09:00 | 2013-11-09 18:25 | 420 | 520 | 486 | AC Conductors and buses | F610Load Reduction #61Unit limited to 420 MWs due to FGD "A" electrical feed isola | Ghent | Derate | Coal | 3 | 2013 | 11 | 9.4167 | 1.8109 | 880.0962 | 93.4615 | 93
GH2 | PD | 72 | 3642 | 2013-11-10 07:36 | 2013-11-10 15:07 | 420 | 520 | 486 | AC Conductors and buses | F610Load Reduction #62Unit limited to 420 MWs due to FGD "B" electrical feed isola | Ghent | Derate | Coal | 3 | 2013 | 11 | 7.5167 | 1.4455 | 702.5192 | 93.4615 | 93
GH2 | D1 | 73 | 340 | 2013-11-11 03:10 | 2013-11-11 13:07 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #632-2 Mill is out of service due to south journal locking up. | Ghent | Derate | Coal | 3 | 2013 | 11 | 9.95 | 1.1481 | 557.9654 | 56.0769 | 56
GH2 | D1 | 74 | 30 | 2013-12-15 05:52 | 2013-12-15 12:00 | 400 | 520 | 486 | Coal conveyors and feeders | Load Reduction #641J Conveyor motor went out, couldn't keep silos full. Dropped l | Ghent | Derate | Coal | 3 | 2013 | 12 | 6.1333 | 1.4154 | 687.8769 | 112.1538 | 112
GH2 | U1 | 75 | 9020 | 2013-12-21 22:14 | 2013-12-22 01:54 | 0 | 520 | 486 | Lightning | Outage #11GH2 tripped off line due to loss of power feed to the U2 FGD. | Ghent | Outage | Coal | 3 | 2013 | 12 | 3.6667 | 3.6667 | 1782 | 486 | 486
GH2 | D1 | 76 | 250 | 2013-12-29 02:06 | 2013-12-29 06:50 | 460 | 520 | 486 | Pulverizer feeders | Load Reduction #652-4 Feeder belt developed a rip. | Ghent | Derate | Coal | 3 | 2013 | 12 | 4.7333 | 0.54615 | 265.4308 | 56.0769 | 56
GH2 | D1 | 1 | 9650 | 2014-01-06 11:20 | 2014-01-06 12:00 | 347 | 520 | 486 | Other stack or exhaust emissions (fossil) | Load Reduction #1Lost SO3 mitigation system. Air pressure / injection causing H2S | Ghent | Derate | Coal | 3 | 2014 | 1 | 0.66667 | 0.22179 | 107.7923 | 161.6885 | 162
GH2 | PD | 2 | 344 | 2014-01-14 23:43 | 2014-01-15 04:11 | 450 | 520 | 486 | Pulverizer inspection | Load Reduction #22-6 Mill off to inspect and repair spring can shaft. | Ghent | Derate | Coal | 3 | 2014 | 1 | 4.4667 | 0.60128 | 292.2231 | 65.4231 | 65
GH2 | D1 | 3 | 9650 | 2014-01-15 19:20 | 2014-01-15 21:03 | 420 | 520 | 486 | Other stack or exhaust emissions (fossil) | Load Reduction #3H2SO4 in high alarm. Dropped load to investigate. Blower for ou | Ghent | Derate | Coal | 3 | 2014 | 1 | 1.7167 | 0.33013 | 160.4423 | 93.4615 | 93
GH2 | PD | 4 | 344 | 2014-01-17 23:30 | 2014-01-18 11:44 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #42-6 Mill off for gear box inspection. | Ghent | Derate | Coal | 3 | 2014 | 1 | 12.2333 | 1.4115 | 686.0077 | 56.0769 | 56
GH2 | D1 | 5 | 280 | 2014-01-18 13:37 | 2014-01-18 14:14 | 460 | 520 | 486 | Pulverizer fires | Load Reduction #52-6 Mill off due to fire in the pyrite line. | Ghent | Derate | Coal | 3 | 2014 | 1 | 0.61667 | 0.071154 | 34.5808 | 56.0769 | 56
GH2 | D1 | 6 | 312 | 2014-02-01 14:40 | 2014-02-01 18:00 | 480 | 520 | 486 | Pulverizer mill classifiers | Load Reduction #62-1 Mill not grinding, took off for inspection. | Ghent | Derate | Coal | 3 | 2014 | 2 | 3.3333 | 0.25641 | 124.6154 | 37.3846 | 37
GH2 | PD | 7 | 344 | 2014-02-06 23:00 | 2014-02-07 01:24 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #72-2 Mill was removed from service to inspect due to high differen | Ghent | Derate | Coal | 3 | 2014 | 2 | 2.4 | 0.27692 | 134.5846 | 56.0769 | 56
GH2 | PD | 8 | 340 | 2014-02-13 23:00 | 2014-02-14 02:11 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #82-5 Mill off to replace pyrite scraper. | Ghent | Derate | Coal | 3 | 2014 | 2 | 3.1833 | 0.36731 | 178.5115 | 56.0769 | 56
GH2 | PD | 9 | 340 | 2014-02-14 02:11 | 2014-02-14 03:39 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #92-6 Mill off to inspect grinding section and classifiers. | Ghent | Derate | Coal | 3 | 2014 | 2 | 1.4667 | 0.16923 | 82.2462 | 56.0769 | 56
GH2 | D1 | 10 | 250 | 2014-02-15 03:20 | 2014-02-15 10:00 | 460 | 520 | 486 | Pulverizer feeders | Load Reduction #102-1 Feeder control issue. | Ghent | Derate | Coal | 3 | 2014 | 2 | 6.6667 | 0.76923 | 373.8462 | 56.0769 | 56
GH2 | D1 | 11 | 340 | 2014-02-17 06:24 | 2014-02-17 14:00 | 455 | 520 | 486 | Other pulverizer problems | Load Reduction #11Removed 2-4 Mill from service for journal issue. | Ghent | Derate | Coal | 3 | 2014 | 2 | 7.6 | 0.95 | 461.7 | 60.75 | 61
GH2 | D1 | 12 | 250 | 2014-02-19 05:20 | 2014-02-19 11:30 | 450 | 520 | 486 | Pulverizer feeders | Load Reduction #122-6 Feeder off to replace the belt. | Ghent | Derate | Coal | 3 | 2014 | 2 | 6.1667 | 0.83013 | 403.4423 | 65.4231 | 65
GH2 | D1 | 13 | 344 | 2014-02-24 23:55 | 2014-02-25 06:30 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #132-6 Mill off to inspect the grinding section. | Ghent | Derate | Coal | 3 | 2014 | 2 | 6.5833 | 0.75962 | 369.1731 | 56.0769 | 56
GH2 | D1 | 14 | 280 | 2014-02-27 07:34 | 2014-02-27 12:11 | 460 | 520 | 486 | Pulverizer fires | Load Reduction #14Load was reduced due to a fire in 2-1 Mill. | Ghent | Derate | Coal | 3 | 2014 | 2 | 4.6167 | 0.53269 | 258.8885 | 56.0769 | 56
GH2 | PD | 15 | 345 | 2014-03-06 12:00 | 2014-03-07 22:07 | 460 | 520 | 486 | Pulverizer overhaul | Load Reduction #152-4 Mill out of service for scheduled overhaul. | Ghent | Derate | Coal | 3 | 2014 | 3 | 34.1167 | 3.9365 | 1913.1577 | 56.0769 | 56
GH2 | PO | 16 | 1812 | 2014-03-07 22:07 | 2014-03-21 11:04 | 0 | 520 | 486 | Boiler Inspections - scheduled or routine | F590Outage #1Unit 2 scheduled for Planned Spring Outage. Removed the unit from se | Ghent | Other | Coal | 3 | 2014 | 3 | 324.95 | 324.95 | 157925.7 | 486 | 486
GH2 | PD | 17 | 345 | 2014-03-21 11:05 | 2014-03-27 12:02 | 460 | 520 | 486 | Pulverizer overhaul | Load Reduction #162-4 Mill out of service for overhaul. | Ghent | Derate | Coal | 3 | 2014 | 3 | 144.95 | 16.725 | 8128.35 | 56.0769 | 56
GH2 | D1 | 18 | 1850 | 2014-03-21 19:34 | 2014-03-22 06:10 | 350 | 520 | 486 | Boiler water condition (not feedwater water quality) | Load Reduction #17Boiler water chemistry - high silica during start up. | Ghent | Derate | Coal | 3 | 2014 | 3 | 10.6 | 3.4654 | 1684.1769 | 158.8846 | 159
GH2 | D1 | 19 | 890 | 2014-03-29 11:16 | 2014-03-29 15:40 | 420 | 520 | 486 | Bottom ash systems (wet or dry) | Load Reduction #18Unit 2 was derated due to wet ash system pluggage. | Ghent | Derate | Coal | 3 | 2014 | 3 | 4.4 | 0.84615 | 411.2308 | 93.4615 | 93
GH2 | D1 | 20 | 890 | 2014-04-01 17:32 | 2014-04-01 23:33 | 300 | 520 | 486 | Bottom ash systems (wet or dry) | Load Reduction #19U2 Wet ash crusher failed and ash was building up. | Ghent | Derate | Coal | 3 | 2014 | 4 | 6.0167 | 2.5455 | 1237.1192 | 205.6154 | 206
GH2 | D1 | 21 | 890 | 2014-04-01 23:33 | 2014-04-02 01:03 | 200 | 520 | 486 | Bottom ash systems (wet or dry) | Load Reduction #20U2 Wet ash crusher failed and ash was building up. The overload | Ghent | Derate | Coal | 3 | 2014 | 4 | 1.5 | 0.92308 | 448.6154 | 299.0769 | 299
GH2 | D1 | 22 | 3820 | 2014-04-03 17:14 | 2014-04-03 22:07 | 320 | 520 | 486 | Closed cooling water pumps | Load Reduction #21U2 Bearing water pump motors went to ground. Lost cooling mediu | Ghent | Derate | Coal | 3 | 2014 | 4 | 4.8833 | 1.8782 | 912.8077 | 186.9231 | 187
GH2 | D1 | 23 | 280 | 2014-04-08 19:29 | 2014-04-08 22:04 | 500 | 520 | 486 | Pulverizer fires | Load Reduction #222-3 Mill burner fire. Tripped the mill. | Ghent | Derate | Coal | 3 | 2014 | 4 | 2.5833 | 0.099359 | 48.2885 | 18.6923 | 19
GH2 | D1 | 24 | 9270 | 2014-04-09 16:57 | 2014-04-09 18:29 | 480 | 520 | 486 | Wet coal | Load Reduction #232-4 Feeder tripped due to wet coal plugging feeder discharge thr | Ghent | Derate | Coal | 3 | 2014 | 4 | 1.5333 | 0.11795 | 57.3231 | 37.3846 | 37
GH2 | D1 | 25 | 346 | 2014-04-10 11:47 | 2014-04-10 13:30 | 490 | 520 | 486 | Pulverizer pyrite removal system | Load Reduction #242-4 Mill off to inspect the pyrite section. | Ghent | Derate | Coal | 3 | 2014 | 4 | 1.7167 | 0.099038 | 48.1327 | 28.0385 | 28
GH2 | PD | 26 | 1100 | 2014-04-11 23:00 | 2014-04-12 04:00 | 210 | 520 | 486 | Waterwall (Furnace wall) B | Load Reduction #25Unit 2 deslag of boiler. | Ghent | Derate | Coal | 3 | 2014 | 4 | 5 | 2.9808 | 1448.6538 | 289.7308 | 290
GH2 | D1 | 27 | 330 | 2014-04-16 23:43 | 2014-04-17 00:18 | 450 | 520 | 486 | Pulverizer coal leak (pulverizers only) | Load Reduction #262-6 Mill sensing line broke causing coal to leak out. | Ghent | Derate | Coal | 3 | 2014 | 4 | 0.58333 | 0.078526 | 38.1635 | 65.4231 | 65
GH2 | MO | 28 | 1520 | 2014-04-18 23:39 | 2014-04-20 02:52 | 0 | 520 | 486 | Flue gas dampers (except recirculation) | F720Outage #2Unit 3 flue gas outlet damper at combined stack with Unit 2 was stick | Ghent | Maintenance | Coal | 3 | 2014 | 4 | 27.2167 | 27.2167 | 13227.3 | 486 | 486
GH2 | D1 | 29 | 320 | 2014-04-25 18:40 | 2014-04-25 20:50 | 460 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #272-1 Mill was removed from service to remove metal from pyrite se | Ghent | Derate | Coal | 3 | 2014 | 4 | 2.1667 | 0.25 | 121.5 | 56.0769 | 56
GH2 | U1 | 30 | 9020 | 2014-04-28 06:35 | 2014-04-28 09:19 | 0 | 520 | 486 | Lightning | Outage #3Lightning strike triped U2 FGD electric feed, ID fans tripped. Transform | Ghent | Outage | Coal | 3 | 2014 | 4 | 2.7333 | 2.7333 | 1328.4 | 486 | 486
GH2 | D1 | 31 | 3410 | 2014-04-30 08:05 | 2014-04-30 08:50 | 460 | 520 | 486 | Feedwater pump | Load Reduction #282-4 BCWP seal blew. The pump was removed from service. | Ghent | Derate | Coal | 3 | 2014 | 4 | 0.75 | 0.086538 | 42.0577 | 56.0769 | 56
GH2 | D1 | 32 | 3410 | 2014-04-30 08:50 | 2014-05-13 06:10 | 505 | 520 | 486 | Feedwater pump | Load Reduction #292-4 BCWP is out of service due to a blown seal.Note: This i | Ghent | Derate | Coal | 3 | 2014 | 4 | 309.3333 | 8.9231 | 4336.6154 | 14.0192 | 14
GH2 | D1 | 33 | 1455 | 2014-05-15 12:10 | 2014-05-15 13:10 | 250 | 520 | 486 | Induced draft fans | Load Reduction #302-2 ID Fan tripped on high vibration. | Ghent | Derate | Coal | 3 | 2014 | 5 | 1 | 0.51923 | 252.3462 | 252.3462 | 252
GH2 | PD | 34 | 3812 | 2014-05-17 05:01 | 2014-05-17 08:09 | 200 | 520 | 486 | Service water valves | Load Reduction #31Unit load was reduced to remove LPSW from service in order to re | Ghent | Derate | Coal | 3 | 2014 | 5 | 3.1333 | 1.9282 | 937.1077 | 299.0769 | 299
GH2 | D1 | 35 | 344 | 2014-05-31 13:57 | 2014-05-31 15:22 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #322-6 Mill off for inspection. Not grinding and making noise. | Ghent | Derate | Coal | 3 | 2014 | 5 | 1.4167 | 0.16346 | 79.4423 | 56.0769 | 56
GH2 | PD | 36 | 1471 | 2014-06-02 23:00 | 2014-06-03 04:46 | 200 | 520 | 486 | Induced draft fan motors - variable speed | Load Reduction #332-1 ID Fan off for VFD coolant leak repair. | Ghent | Derate | Coal | 3 | 2014 | 6 | 5.7667 | 3.5487 | 1724.6769 | 299.0769 | 299
GH2 | D1 | 37 | 280 | 2014-06-05 14:55 | 2014-06-05 17:46 | 490 | 520 | 486 | Pulverizer fires | Load Reduction #342-5 Mill had a fire in the grinding section. Took off mill to i | Ghent | Derate | Coal | 3 | 2014 | 6 | 2.85 | 0.16442 | 79.9096 | 28.0385 | 28
GH2 | D1 | 38 | 360 | 2014-06-14 12:55 | 2014-06-14 15:05 | 440 | 520 | 486 | Burners | Load Reduction #352-6 Mill off due to "A" burner temp high. | Ghent | Derate | Coal | 3 | 2014 | 6 | 2.1667 | 0.33333 | 162 | 74.7692 | 75
GH2 | PD | 39 | 1470 | 2014-06-20 21:30 | 2014-06-21 03:27 | 240 | 520 | 486 | Induced draft fan motors and drives | Load Reduction #362-1 ID fan off to repair coolant leak on the VFD. | Ghent | Derate | Coal | 3 | 2014 | 6 | 5.95 | 3.2038 | 1557.0692 | 261.6923 | 262
GH2 | D1 | 40 | 3414 | 2014-06-23 20:25 | 2014-06-23 21:34 | 340 | 520 | 486 | Feedwater pump local controls | Load Reduction #372-1 BFP tripped due to loss of vacuum on auxiliary condenser. | Ghent | Derate | Coal | 3 | 2014 | 6 | 1.15 | 0.39808 | 193.4654 | 168.2308 | 168
GH2 | PD | 41 | 344 | 2014-06-30 23:00 | 2014-07-01 03:11 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #382-5 Mill off to inspect a noise in the pyrite section. | Ghent | Derate | Coal | 3 | 2014 | 6 | 4.1833 | 0.48269 | 234.5885 | 56.0769 | 56
GH2 | PD | 42 | 344 | 2014-07-02 23:00 | 2014-07-03 01:36 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #392-3 Mill off to inspect the grinding section and calibrate the f | Ghent | Derate | Coal | 3 | 2014 | 7 | 2.6 | 0.3 | 145.8 | 56.0769 | 56
GH2 | D1 | 43 | 346 | 2014-07-18 00:10 | 2014-07-18 02:10 | 470 | 520 | 486 | Pulverizer pyrite removal system | Load Reduction #402-5 Mill pyrite scraper broke. | Ghent | Derate | Coal | 3 | 2014 | 7 | 2 | 0.19231 | 93.4615 | 46.7308 | 47
GH2 | D1 | 44 | 346 | 2014-07-22 03:04 | 2014-07-22 05:11 | 460 | 520 | 486 | Pulverizer pyrite removal system | Load Reduction #412-5 Mill off to replace a pyrite scraper that had broken off. | Ghent | Derate | Coal | 3 | 2014 | 7 | 2.1167 | 0.24423 | 118.6962 | 56.0769 | 56
GH2 | U1 | 45 | 3416 | 2014-07-23 09:00 | 2014-07-23 14:33 | 0 | 520 | 486 | Other feedwater pump problems | Outage #4While pulling the breaker for 2-1 BFPT High Pressure Oil Control Fluid Pu | Ghent | Outage | Coal | 3 | 2014 | 7 | 5.55 | 5.55 | 2697.3 | 486 | 486
GH2 | D1 | 46 | 1850 | 2014-07-23 20:35 | 2014-07-23 22:20 | 450 | 520 | 486 | Boiler water condition (not feedwater water quality) | Load Reduction #42The unit was limited on drum pressure due to boiler chemistry af | Ghent | Derate | Coal | 3 | 2014 | 7 | 1.75 | 0.23558 | 114.4904 | 65.4231 | 65
GH2 | D1 | 47 | 320 | 2014-07-27 08:22 | 2014-07-27 09:20 | 460 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #432-1 Mill out of service to inspect grinding section. Mill had p | Ghent | Derate | Coal | 3 | 2014 | 7 | 0.96667 | 0.11154 | 54.2077 | 56.0769 | 56
GH2 | D1 | 48 | 250 | 2014-07-27 10:05 | 2014-07-27 12:50 | 460 | 520 | 486 | Pulverizer feeders | Load Reduction #442-1 Feeder would not start. Electrical and Instrument shops che | Ghent | Derate | Coal | 3 | 2014 | 7 | 2.75 | 0.31731 | 154.2115 | 56.0769 | 56
GH2 | PD | 49 | 3682 | 2014-07-29 05:00 | 2014-07-29 16:44 | 250 | 520 | 486 | Other voltage system conductors and buses | Load Reduction #45Unit 2 was limited due to North Bus outage to tie in for the new | Ghent | Derate | Coal | 3 | 2014 | 7 | 11.7333 | 6.0923 | 2960.8615 | 252.3462 | 252
GH2 | D1 | 50 | 344 | 2014-07-31 14:10 | 2014-07-31 15:48 | 480 | 520 | 486 | Pulverizer inspection | Load Reduction #462-3 Mill was off to inspect grinding section after high temperat | Ghent | Derate | Coal | 3 | 2014 | 7 | 1.6333 | 0.12564 | 61.0615 | 37.3846 | 37
GH2 | D1 | 51 | 340 | 2014-08-02 19:38 | 2014-08-03 06:35 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #472-5 Mill had grinding issues. Took mill off to inspect. | Ghent | Derate | Coal | 3 | 2014 | 8 | 10.95 | 1.2635 | 614.0423 | 56.0769 | 56
GH2 | D1 | 52 | 340 | 2014-08-09 23:28 | 2014-08-10 01:44 | 480 | 520 | 486 | Other pulverizer problems | Load Reduction #482-Mill off to inspect grinding section for vibration. | Ghent | Derate | Coal | 3 | 2014 | 8 | 2.2667 | 0.17436 | 84.7385 | 37.3846 | 37
GH2 | D1 | 53 | 340 | 2014-08-10 21:00 | 2014-08-11 01:56 | 480 | 520 | 486 | Other pulverizer problems | Load Reduction #492-5 Mill off to inspect grinding section for vibration. | Ghent | Derate | Coal | 3 | 2014 | 8 | 4.9333 | 0.37949 | 184.4308 | 37.3846 | 37
GH2 | D1 | 54 | 344 | 2014-08-13 11:00 | 2014-08-13 13:18 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #502-3 Mill off for inspection due to noise in pyrite section. | Ghent | Derate | Coal | 3 | 2014 | 8 | 2.3 | 0.26538 | 128.9769 | 56.0769 | 56
GH2 | PD | 55 | 250 | 2014-08-14 22:00 | 2014-08-14 23:45 | 460 | 520 | 486 | Pulverizer feeders | Load Reduction #512-3 Feeder was out of service to replace the belt and inspect th | Ghent | Derate | Coal | 3 | 2014 | 8 | 1.75 | 0.20192 | 98.1346 | 56.0769 | 56
GH2 | PD | 56 | 340 | 2014-08-23 22:00 | 2014-08-24 01:00 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #522-5 Mill off to repair coal leak. | Ghent | Derate | Coal | 3 | 2014 | 8 | 3 | 0.34615 | 168.2308 | 56.0769 | 56
GH2 | D1 | 57 | 320 | 2014-08-28 15:27 | 2014-08-28 19:38 | 460 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #532-5 Mill off to inspect for noise in the pyrite section. | Ghent | Derate | Coal | 3 | 2014 | 8 | 4.1833 | 0.48269 | 234.5885 | 56.0769 | 56
GH2 | D1 | 58 | 350 | 2014-09-02 18:02 | 2014-09-02 19:43 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #542-2 Mill had a coal leak. Took mill off to repair. | Ghent | Derate | Coal | 3 | 2014 | 9 | 1.6833 | 0.19423 | 94.3962 | 56.0769 | 56
GH2 | D1 | 60 | 350 | 2014-09-02 19:43 | 2014-09-03 10:46 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #55Removed 2-3 mill from service to repair coal leak. | Ghent | Derate | Coal | 3 | 2014 | 9 | 15.05 | 1.7365 | 843.9577 | 56.0769 | 56
GH2 | D1 | 61 | 9650 | 2014-09-03 20:48 | 2014-09-03 22:04 | 450 | 520 | 486 | Other stack or exhaust emissions (fossil) | Load Reduction #56GH2 H2S04 was running high. Dropped load to keep in compliance. | Ghent | Derate | Coal | 3 | 2014 | 9 | 1.2667 | 0.17051 | 82.8692 | 65.4231 | 65
GH2 | D1 | 62 | 9650 | 2014-09-04 17:19 | 2014-09-04 19:02 | 460 | 520 | 486 | Other stack or exhaust emissions (fossil) | Load Reduction #57Dropped load to keep H2S04 within limit. | Ghent | Derate | Coal | 3 | 2014 | 9 | 1.7167 | 0.19808 | 96.2654 | 56.0769 | 56
GH2 | D1 | 63 | 9650 | 2014-09-05 19:22 | 2014-09-06 00:05 | 417 | 520 | 486 | Other stack or exhaust emissions (fossil) | Load Reduction #58Dropped load to keep H2S04 within limit. Four of 6 inlet inject | Ghent | Derate | Coal | 3 | 2014 | 9 | 4.7167 | 0.93426 | 454.0517 | 96.2654 | 96
GH2 | D1 | 64 | 320 | 2014-09-09 21:35 | 2014-09-09 23:00 | 460 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #59Removed 2-2 Mill from service due to metal in the grinding secti | Ghent | Derate | Coal | 3 | 2014 | 9 | 1.4167 | 0.16346 | 79.4423 | 56.0769 | 56
GH2 | D1 | 65 | 340 | 2014-09-10 09:46 | 2014-09-10 14:31 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #60Removed 2-2 Mill from service to replace the east journal. This | Ghent | Derate | Coal | 3 | 2014 | 9 | 4.75 | 0.54808 | 266.3654 | 56.0769 | 56
GH2 | D1 | 66 | 267 | 2014-09-18 22:58 | 2014-09-18 23:46 | 427 | 520 | 486 | Primary air flow instrumentation | Load Reduction #61Unit 2 was derated due to changing out primary air control trans | Ghent | Derate | Coal | 3 | 2014 | 9 | 0.8 | 0.14308 | 69.5354 | 86.9192 | 87
GH2 | D1 | 67 | 9650 | 2014-09-22 05:20 | 2014-09-22 09:58 | 200 | 520 | 486 | Other stack or exhaust emissions (fossil) | Load Reduction #62Unit is limited due to H2SO4 emission being high. Outlet inject | Ghent | Derate | Coal | 3 | 2014 | 9 | 4.6333 | 2.8513 | 1385.7231 | 299.0769 | 299
GH2 | PD | 68 | 345 | 2014-09-24 05:32 | 2014-09-30 23:59 | 460 | 520 | 486 | Pulverizer overhaul | Load Reduction #63Planned overhaul on 2-6 mill. | Ghent | Derate | Coal | 3 | 2014 | 9 | 162.45 | 18.7442 | 9109.6962 | 56.0769 | 56
GH2 | MO | 69 | 1999 | 2014-09-24 11:03 | 2014-09-28 02:53 | 0 | 520 | 486 | Boiler | Outage #5Unit 2 came off line to tie in the new auxiliary sump lines for KBR. | Ghent | Maintenance | Coal | 3 | 2014 | 9 | 87.8333 | 87.8333 | 42687 | 486 | 486
GH2 | D1 | 70 | 1850 | 2014-09-28 10:53 | 2014-09-28 11:21 | 400 | 520 | 486 | Boiler water condition (not feedwater water quality) | Load Reduction #64Boiler drum pressure was limited due to high silica. | Ghent | Derate | Coal | 3 | 2014 | 9 | 0.46667 | 0.10769 | 52.3385 | 112.1538 | 112
GH2 | D1 | 71 | 346 | 2014-09-28 18:54 | 2014-09-28 20:48 | 370 | 520 | 486 | Pulverizer pyrite removal system | Load Reduction #652-4 Mill pyrite chute plugged. Took mill off to inspect the pyr | Ghent | Derate | Coal | 3 | 2014 | 9 | 1.9 | 0.54808 | 266.3654 | 140.1923 | 140
GH2 | PD | 72 | 345 | 2014-10-01 00:01 | 2014-10-13 08:35 | 460 | 520 | 486 | Pulverizer overhaul | Load Reduction #66Planned overhaul on 2-6 Mill. | Ghent | Derate | Coal | 3 | 2014 | 10 | 296.5667 | 34.2192 | 16630.5462 | 56.0769 | 56
GH2 | D1 | 73 | 344 | 2014-10-06 18:18 | 2014-10-06 23:11 | 370 | 520 | 486 | Pulverizer inspection | Load Reduction #672-4 Mill off to inspect grinding section due to mill dumping coa | Ghent | Derate | Coal | 3 | 2014 | 10 | 4.8833 | 1.4087 | 684.6058 | 140.1923 | 140
GH2 | D1 | 74 | 350 | 2014-10-13 16:20 | 2014-10-13 18:20 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #682-6 A Burner line was leaking at flange next to the boiler. Too | Ghent | Derate | Coal | 3 | 2014 | 10 | 2 | 0.23077 | 112.1538 | 56.0769 | 56
GH2 | U1 | 75 | 4619 | 2014-10-16 07:55 | 2014-10-16 08:59 | 0 | 520 | 486 | Other hydrogen system problems | Outage #6Unit 2 tripped off line when a fuse blew in the Generator Hydrogen cabine | Ghent | Outage | Coal | 3 | 2014 | 10 | 1.0667 | 1.0667 | 518.4 | 486 | 486
GH2 | D1 | 76 | 350 | 2014-10-18 22:33 | 2014-10-19 23:02 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #692-4 Mill off due to high burner temperature on 'C' burner. | Ghent | Derate | Coal | 3 | 2014 | 10 | 24.4833 | 2.825 | 1372.95 | 56.0769 | 56
GH2 | D1 | 77 | 350 | 2014-10-19 09:10 | 2014-10-19 12:05 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #702-4 Mill off due to coal leak on 'C' burner next to windbox. | Ghent | Derate | Coal | 3 | 2014 | 10 | 2.9167 | 0.33654 | 163.5577 | 56.0769 | 56
GH2 | D1 | 78 | 350 | 2014-10-19 18:20 | 2014-10-19 19:04 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #712-4 Mill coal leak at 'C' burner flange, same leak as previously | Ghent | Derate | Coal | 3 | 2014 | 10 | 0.73333 | 0.084615 | 41.1231 | 56.0769 | 56
GH2 | PD | 79 | 250 | 2014-10-20 22:45 | 2014-10-21 03:05 | 460 | 520 | 486 | Pulverizer feeders | Load Reduction #722-6 Feeder off to replace and calibrate the belt. | Ghent | Derate | Coal | 3 | 2014 | 10 | 4.3333 | 0.5 | 243 | 56.0769 | 56
GH2 | D1 | 80 | 340 | 2014-10-21 16:08 | 2014-10-21 19:05 | 480 | 520 | 486 | Other pulverizer problems | Load Reduction #732-5 Mill off to replace a pyrite scraper. | Ghent | Derate | Coal | 3 | 2014 | 10 | 2.95 | 0.22692 | 110.2846 | 37.3846 | 37
GH2 | PD | 81 | 340 | 2014-10-22 22:00 | 2014-10-22 23:14 | 475 | 520 | 486 | Other pulverizer problems | Load Reduction #742-5 Mill off to adjust the pyrite scraper. | Ghent | Derate | Coal | 3 | 2014 | 10 | 1.2333 | 0.10673 | 51.8712 | 42.0577 | 42
GH2 | PD | 82 | 340 | 2014-10-22 23:35 | 2014-10-23 00:53 | 475 | 520 | 486 | Other pulverizer problems | Load Reduction #752-6 Mill off to retorque race after overhaul. | Ghent | Derate | Coal | 3 | 2014 | 10 | 1.3 | 0.1125 | 54.675 | 42.0577 | 42
GH2 | D1 | 83 | 340 | 2014-10-23 08:10 | 2014-10-23 10:00 | 480 | 520 | 486 | Other pulverizer problems | Load Reduction #762-5 Mill off to replace broken pyrite scraper. | Ghent | Derate | Coal | 3 | 2014 | 10 | 1.8333 | 0.14103 | 68.5385 | 37.3846 | 37
GH2 | D1 | 84 | 340 | 2014-10-23 23:00 | 2014-10-24 01:22 | 480 | 520 | 486 | Other pulverizer problems | Load Reduction #772-5 Mill off to replace broken pryite scraper. | Ghent | Derate | Coal | 3 | 2014 | 10 | 2.3667 | 0.18205 | 88.4769 | 37.3846 | 37
GH2 | D1 | 85 | 340 | 2014-10-24 22:02 | 2014-10-25 03:05 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #782-5 Mill off to inspect grinding section. Found east journal ba | Ghent | Derate | Coal | 3 | 2014 | 10 | 5.05 | 0.58269 | 283.1885 | 56.0769 | 56
GH2 | PD | 86 | 9300 | 2014-10-29 06:00 | 2014-10-29 20:15 | 375 | 520 | 486 | Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | Load Reduction #79Unit 2 was limited due to substation work. South 345 KV bus out | Ghent | Derate | Coal | 3 | 2014 | 10 | 14.25 | 3.9736 | 1931.149 | 135.5192 | 136
GH2 | PD | 87 | 340 | 2014-11-01 23:09 | 2014-11-02 01:37 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #802-4 Mill was off to replace the pyrite scraper. | Ghent | Derate | Coal | 3 | 2014 | 11 | 2.4667 | 0.28462 | 138.3231 | 56.0769 | 56
GH2 | D1 | 88 | 350 | 2014-11-02 01:55 | 2014-11-02 02:35 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #812-4 Mill off due to high burner temperature on "A" burner line. | Ghent | Derate | Coal | 3 | 2014 | 11 | 0.66667 | 0.076923 | 37.3846 | 56.0769 | 56
GH2 | D1 | 89 | 340 | 2014-11-06 05:52 | 2014-11-06 08:38 | 450 | 520 | 486 | Other pulverizer problems | Load Reduction #822-5 Mill was off to replace the pyrite scraper. | Ghent | Derate | Coal | 3 | 2014 | 11 | 2.7667 | 0.37244 | 181.0038 | 65.4231 | 65
GH2 | MO | 90 | 1040 | 2014-11-07 23:57 | 2014-11-09 09:32 | 0 | 520 | 486 | First superheater B | F540Outage #7Unit 2 had been running with a leak in the East Side Superheat spray | Ghent | Maintenance | Coal | 3 | 2014 | 11 | 33.5833 | 33.5833 | 16321.5 | 486 | 486
GH2 | PD | 91 | 340 | 2014-11-10 23:00 | 2014-11-11 06:27 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #832-5 Mill off to replace pyrite scraper and inspect mill. | Ghent | Derate | Coal | 3 | 2014 | 11 | 7.45 | 0.85962 | 417.7731 | 56.0769 | 56
GH2 | PD | 92 | 344 | 2014-11-11 23:00 | 2014-11-12 02:50 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #842-4 Mill off for inspection. | Ghent | Derate | Coal | 3 | 2014 | 11 | 3.8333 | 0.44231 | 214.9615 | 56.0769 | 56
GH2 | D1 | 93 | 344 | 2014-11-12 02:50 | 2014-11-12 04:29 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #852-5 Mill off for inspection. | Ghent | Derate | Coal | 3 | 2014 | 11 | 1.65 | 0.19038 | 92.5269 | 56.0769 | 56
GH2 | D1 | 94 | 340 | 2014-11-12 11:20 | 2014-11-12 16:10 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #862-5 Mill journal failed. | Ghent | Derate | Coal | 3 | 2014 | 11 | 4.8333 | 0.55769 | 271.0385 | 56.0769 | 56
GH2 | D1 | 95 | 344 | 2014-11-19 23:00 | 2014-11-20 01:50 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #872-6 Mill off to inspect noise in pyrite section. | Ghent | Derate | Coal | 3 | 2014 | 11 | 2.8333 | 0.32692 | 158.8846 | 56.0769 | 56
GH2 | PD | 96 | 350 | 2014-11-22 06:24 | 2014-11-22 09:04 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #882-5 Mill off to repair coal leaks. Burner line gaskets leaking. | Ghent | Derate | Coal | 3 | 2014 | 11 | 2.6667 | 0.30769 | 149.5385 | 56.0769 | 56
GH2 | D1 | 97 | 1470 | 2014-11-25 00:50 | 2014-11-25 04:42 | 200 | 520 | 486 | Induced draft fan motors and drives | Load Reduction #892-2 ID fan VFD tripped due to loss of power supply. | Ghent | Derate | Coal | 3 | 2014 | 11 | 3.8667 | 2.3795 | 1156.4308 | 299.0769 | 299
GH2 | D1 | 98 | 340 | 2014-11-25 18:51 | 2014-11-25 21:34 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #902-6 Mill off to inspect the pyrite section. | Ghent | Derate | Coal | 3 | 2014 | 11 | 2.7167 | 0.31346 | 152.3423 | 56.0769 | 56
GH2 | D1 | 99 | 350 | 2014-11-30 08:36 | 2014-11-30 11:15 | 450 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #912-6 Mill off to inspect 'A' burner line due to getting hot. | Ghent | Derate | Coal | 3 | 2014 | 11 | 2.65 | 0.35673 | 173.3712 | 65.4231 | 65
GH2 | PD | 100 | 1100 | 2014-12-03 23:00 | 2014-12-04 04:00 | 200 | 520 | 486 | Waterwall (Furnace wall) B | FS00Load Reduction #92Unit 2 was derated for a planned boiler deslag. | Ghent | Derate | Coal | 3 | 2014 | 12 | 5 | 3.0769 | 1495.3846 | 299.0769 | 299
GH2 | D1 | 101 | 340 | 2014-12-12 01:40 | 2014-12-12 03:20 | 440 | 520 | 486 | Other pulverizer problems | Load Reduction #93Removed 2-5 Mill from service to repair a coal leak. | Ghent | Derate | Coal | 3 | 2014 | 12 | 1.6667 | 0.25641 | 124.6154 | 74.7692 | 75
GH2 | D1 | 102 | 340 | 2014-12-12 11:00 | 2014-12-12 13:30 | 440 | 520 | 486 | Other pulverizer problems | Load Reduction #94Removed 2-5 Mill from service to repair a coal leak. | Ghent | Derate | Coal | 3 | 2014 | 12 | 2.5 | 0.38462 | 186.9231 | 74.7692 | 75
GH2 | D1 | 103 | 320 | 2014-12-26 00:52 | 2014-12-26 01:56 | 430 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #952-3 Feeder tripped. | Ghent | Derate | Coal | 3 | 2014 | 12 | 1.0667 | 0.18462 | 89.7231 | 84.1154 | 84
GH2 | D1 | 104 | 346 | 2014-12-26 13:30 | 2014-12-26 15:09 | 460 | 520 | 486 | Pulverizer pyrite removal system | Load Reduction #962-6 Mill was off to inspect the pyrite and grinding sections due | Ghent | Derate | Coal | 3 | 2014 | 12 | 1.65 | 0.19038 | 92.5269 | 56.0769 | 56
GH2 | D1 | 1 | 340 | 2015-01-08 13:12 | 2015-01-08 17:35 | 440 | 520 | 486 | Other pulverizer problems | Load Reduction #12-3 Mill discharge temperature was high. Took mill off to inspec | Ghent | Derate | Coal | 3 | 2015 | 1 | 4.3833 | 0.67436 | 327.7385 | 74.7692 | 75
GH2 | D1 | 2 | 340 | 2015-01-08 17:35 | 2015-01-08 20:14 | 440 | 520 | 486 | Other pulverizer problems | Load Reduction #22-4 Mill had a loud noise in the grinding section. Found a bad j | Ghent | Derate | Coal | 3 | 2015 | 1 | 2.65 | 0.40769 | 198.1385 | 74.7692 | 75
GH2 | D1 | 3 | 280 | 2015-01-09 03:53 | 2015-01-09 10:35 | 440 | 520 | 486 | Pulverizer fires | Load Reduction #32-3 Mill had a fire in the grinding section. Mill off to inspect | Ghent | Derate | Coal | 3 | 2015 | 1 | 6.7 | 1.0308 | 500.9538 | 74.7692 | 75
GH2 | D1 | 4 | 340 | 2015-01-16 13:58 | 2015-01-16 18:00 | 430 | 520 | 486 | Other pulverizer problems | Load Reduction #42-4 Mill was off to inspect noise coming from the grinding sectio | Ghent | Derate | Coal | 3 | 2015 | 1 | 4.0333 | 0.69808 | 339.2654 | 84.1154 | 84
GH2 | U1 | 5 | 3621 | 2015-01-25 15:00 | 2015-01-25 20:38 | 0 | 520 | 486 | Unit auxiliaries transformer | Outage #1Unit Auxiliary Transformer 2A tripped on differential on 'B' and 'C' phas | Ghent | Outage | Coal | 3 | 2015 | 1 | 5.6333 | 5.6333 | 2737.8 | 486 | 486
GH2 | SF | 6 | 4309 | 2015-01-25 20:38 | 2015-01-26 19:52 | 0 | 520 | 486 | Other turbine instrument and control problems | Outage #2During the previous event of the UAT-2 differential, the Main Turbine wen | Ghent | Outage | Coal | 3 | 2015 | 1 | 23.2333 | 23.2333 | 11291.4 | 486 | 486
GH2 | D1 | 7 | 344 | 2015-01-29 14:20 | 2015-01-29 16:26 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #52-6 Mill off to inspect noise in the pyrite section. Pyrite scra | Ghent | Derate | Coal | 3 | 2015 | 1 | 2.1 | 0.24231 | 117.7615 | 56.0769 | 56
GH2 | D1 | 8 | 344 | 2015-01-29 18:26 | 2015-01-29 20:30 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #62-6 Mill off to inspect for mill vibration. | Ghent | Derate | Coal | 3 | 2015 | 1 | 2.0667 | 0.23846 | 115.8923 | 56.0769 | 56
GH2 | D1 | 9 | 344 | 2015-02-06 01:54 | 2015-02-06 07:00 | 480 | 520 | 486 | Pulverizer inspection | Load Reduction #72-6 Mill off to inspect for the cause of noise in the grinding se | Ghent | Derate | Coal | 3 | 2015 | 2 | 5.1 | 0.39231 | 190.6615 | 37.3846 | 37
GH2 | D1 | 10 | 350 | 2015-02-06 07:23 | 2015-02-06 10:37 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #82-6 Mill off due to C burner line fire next to boiler. | Ghent | Derate | Coal | 3 | 2015 | 2 | 3.2333 | 0.37308 | 181.3154 | 56.0769 | 56
GH2 | D1 | 11 | 3621 | 2015-02-10 08:58 | 2015-02-10 11:42 | 390 | 520 | 486 | Unit auxiliaries transformer | Unit was limited to Reserve Aux. transformer loading being too high. GH2 is on reserve | Ghent | Derate | Coal | 3 | 2015 | 2 | 2.7333 | 0.68333 | 332.1 | 121.5 | 122
GH2 | MO | 12 | 3621 | 2015-02-10 21:58 | 2015-02-11 01:29 | 0 | 520 | 486 | Unit auxiliaries transformer | F580Outage #3Unit had been running on Reserve power since a fault took the unit of | Ghent | Maintenance | Coal | 3 | 2015 | 2 | 3.5167 | 3.5167 | 1709.1 | 486 | 486
GH2 | U1 | 13 | 690 | 2015-02-11 02:06 | 2015-02-11 03:05 | 0 | 520 | 486 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Outage #4While unit was raising load from just coming back on line from previous e | Ghent | Outage | Coal | 3 | 2015 | 2 | 0.98333 | 0.98333 | 477.9 | 486 | 486
GH2 | D1 | 14 | 340 | 2015-02-17 21:49 | 2015-02-17 22:24 | 440 | 520 | 486 | Other pulverizer problems | Load Reduction #102-2 Mill burner shut off air supply solenoid failed causing BSO | Ghent | Derate | Coal | 3 | 2015 | 2 | 0.58333 | 0.089744 | 43.6154 | 74.7692 | 75
GH2 | D1 | 15 | 3410 | 2015-02-18 09:45 | 2015-02-18 10:04 | 300 | 520 | 486 | Feedwater pump | Load Reduction #112-2 BFP IB oil seal started slinging oil. Found oil temperature | Ghent | Derate | Coal | 3 | 2015 | 2 | 0.31667 | 0.13397 | 65.1115 | 205.6154 | 206
GH2 | D1 | 16 | 3410 | 2015-02-23 06:00 | 2015-02-23 06:50 | 300 | 520 | 486 | Feedwater pump | Load Reduction #122-2 BFP inboard oil seal started slinging oil. Found oil pressu | Ghent | Derate | Coal | 3 | 2015 | 2 | 0.83333 | 0.35256 | 171.3462 | 205.6154 | 206
GH2 | D1 | 17 | 350 | 2015-02-28 15:49 | 2015-02-28 18:32 | 390 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #132-5 Mill off to unplug the pyrite chute. | Ghent | Derate | Coal | 3 | 2015 | 2 | 2.7167 | 0.67917 | 330.075 | 121.5 | 122
GH2 | D1 | 18 | 320 | 2015-03-07 07:30 | 2015-03-07 09:00 | 440 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #142-2 Mill off to inspect due to noise in the grinding section. | Ghent | Derate | Coal | 3 | 2015 | 3 | 1.5 | 0.23077 | 112.1538 | 74.7692 | 75
GH2 | D1 | 19 | 340 | 2015-03-08 04:40 | 2015-03-08 11:05 | 440 | 520 | 486 | Other pulverizer problems | Load Reduction #152-3 Feeder off to inspect for noise in tail roll area. | Ghent | Derate | Coal | 3 | 2015 | 3 | 6.4167 | 0.98718 | 479.7692 | 74.7692 | 75
GH2 | D1 | 20 | 344 | 2015-03-09 04:11 | 2015-03-09 07:33 | 430 | 520 | 486 | Pulverizer inspection | Load Reduction #162-1 Mill off to inspect due to not grinding when placing in serv | Ghent | Derate | Coal | 3 | 2015 | 3 | 3.3667 | 0.58269 | 283.1885 | 84.1154 | 84
GH2 | D1 | 21 | 250 | 2015-03-09 08:50 | 2015-03-09 09:22 | 430 | 520 | 486 | Pulverizer feeders | Load Reduction #172-1 Feeder was off to inspect for pluggage. | Ghent | Derate | Coal | 3 | 2015 | 3 | 0.53333 | 0.092308 | 44.8615 | 84.1154 | 84
GH2 | PO | 22 | 4402 | 2015-03-13 23:59 | 2015-03-22 11:00 | 0 | 520 | 486 | Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | Outage #5Removed the unit from service for the Planned Spring Outage. | Ghent | Other | Coal | 3 | 2015 | 3 | 203.0167 | 203.0167 | 98666.1 | 486 | 486
GH2 | D1 | 23 | 1850 | 2015-03-22 19:00 | 2015-03-23 06:20 | 406 | 520 | 486 | Boiler water condition (not feedwater water quality) | Load Reduction #18Boiler chemistry was out of range after unit start up. Silica w | Ghent | Derate | Coal | 3 | 2015 | 3 | 11.3333 | 2.4846 | 1207.5231 | 106.5462 | 107
GH2 | D1 | 24 | 3410 | 2015-03-26 07:17 | 2015-03-26 08:13 | 350 | 520 | 486 | Feedwater pump | Load Reduction #192-2 Boiler feed pump started leaking oil from the seal. Removed | Ghent | Derate | Coal | 3 | 2015 | 3 | 0.93333 | 0.30513 | 148.2923 | 158.8846 | 159
GH2 | D1 | 25 | 320 | 2015-04-11 07:20 | 2015-04-11 10:00 | 430 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #202-4 Mill off to inspect due to a noise in the grinding section. | Ghent | Derate | Coal | 3 | 2015 | 4 | 2.6667 | 0.46154 | 224.3077 | 84.1154 | 84
GH2 | D1 | 26 | 340 | 2015-04-13 05:44 | 2015-04-13 08:43 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #212-4 Mill off to inspect north journal due to low mill amps. | Ghent | Derate | Coal | 3 | 2015 | 4 | 2.9833 | 0.34423 | 167.2962 | 56.0769 | 56
GH2 | D1 | 27 | 3662 | 2015-04-13 18:14 | 2015-04-14 00:25 | 117 | 520 | 486 | 4160-volt conductors and buses | Load Reduction #22Unit load was dropped due to loss of power to the 4KV Coal Handl | Ghent | Derate | Coal | 3 | 2015 | 4 | 6.1833 | 4.7921 | 2328.9525 | 376.65 | 377
GH2 | D1 | 28 | 345 | 2015-04-19 19:04 | 2015-05-02 12:43 | 483 | 520 | 486 | Pulverizer overhaul | Load Reduction #232-3 Mill is out of service for inspection. | Ghent | Derate | Coal | 3 | 2015 | 4 | 305.65 | 21.7482 | 10569.6121 | 34.5808 | 35
GH2 | D1 | 29 | 340 | 2015-05-02 13:41 | 2015-05-02 15:00 | 485 | 520 | 486 | Other pulverizer problems | Load Reduction #242-3 Mill off for limit on burner shut off gate. | Ghent | Derate | Coal | 3 | 2015 | 5 | 1.3167 | 0.088622 | 43.0702 | 32.7115 | 33
GH2 | D1 | 30 | 3416 | 2015-05-03 01:35 | 2015-05-03 03:28 | 350 | 520 | 486 | Other feedwater pump problems | Load Reduction #252-1 BFP would not reset after testing. HP stop valve limit issu | Ghent | Derate | Coal | 3 | 2015 | 5 | 1.8833 | 0.61571 | 299.2327 | 158.8846 | 159
GH2 | PD | 31 | 3662 | 2015-05-04 22:30 | 2015-05-04 23:17 | 300 | 520 | 486 | 4160-volt conductors and buses | Load Reduction #26Checking cables on 4KV feed to CHB. Load was reduced to remove | Ghent | Derate | Coal | 3 | 2015 | 5 | 0.78333 | 0.33141 | 161.0654 | 205.6154 | 206
GH2 | D1 | 32 | 340 | 2015-05-07 19:00 | 2015-05-07 20:16 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #272-4 Mill was off to inspect for noise in the pyrite section. | Ghent | Derate | Coal | 3 | 2015 | 5 | 1.2667 | 0.14615 | 71.0308 | 56.0769 | 56
GH2 | D1 | 33 | 350 | 2015-05-19 07:54 | 2015-05-19 10:05 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #282-6C Burner line high temperature increased at a fast rate. Ope | Ghent | Derate | Coal | 3 | 2015 | 5 | 2.1833 | 0.25192 | 122.4346 | 56.0769 | 56
GH2 | D1 | 34 | 350 | 2015-05-21 11:00 | 2015-05-21 17:00 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #29Operations took 2-6 Mill out of service after attempts to stop t | Ghent | Derate | Coal | 3 | 2015 | 5 | 6 | 0.69231 | 336.4615 | 56.0769 | 56
GH2 | MO | 35 | 740 | 2015-05-30 20:50 | 2015-05-31 09:36 | 0 | 520 | 486 | Boiler recirculation pumps | F540Outage #6Unit 2 was removed from service to replace the 2-3 BCWP. The mechani | Ghent | Maintenance | Coal | 3 | 2015 | 5 | 12.7667 | 12.7667 | 6204.6 | 486 | 486
GH2 | PD | 37 | 312 | 2015-06-11 23:00 | 2015-06-12 01:54 | 460 | 520 | 486 | Pulverizer mill classifiers | Load Reduction #302-3 Mill off to inspect and repair classifier section. | Ghent | Derate | Coal | 3 | 2015 | 6 | 2.9 | 0.33462 | 162.6231 | 56.0769 | 56
GH2 | D1 | 38 | 350 | 2015-06-13 15:55 | 2015-06-13 16:20 | 450 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #312-6 Mill "D" BSO came off the open limit and tripped the mill. | Ghent | Derate | Coal | 3 | 2015 | 6 | 0.41667 | 0.05609 | 27.2596 | 65.4231 | 65
GH2 | PD | 39 | 344 | 2015-07-13 22:26 | 2015-07-14 01:17 | 440 | 520 | 486 | Pulverizer inspection | Load Reduction #322-4 Mill off to inspect due to mill fineness being poor. | Ghent | Derate | Coal | 3 | 2015 | 7 | 2.85 | 0.43846 | 213.0923 | 74.7692 | 75
GH2 | D1 | 40 | 250 | 2015-07-14 04:47 | 2015-07-14 11:57 | 450 | 520 | 486 | Pulverizer feeders | Load Reduction #332-3 Feeder head roll bearing failed. | Ghent | Derate | Coal | 3 | 2015 | 7 | 7.1667 | 0.96474 | 468.8654 | 65.4231 | 65
GH2 | D1 | 41 | 320 | 2015-07-16 | 2015-07-16 00:27 | 460 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #342-6 Mill off for inspection due to noise in grinding section. | Ghent | Derate | Coal | 3 | 2015 | 7 | 0.45 | 0.051923 | 25.2346 | 56.0769 | 56
GH2 | D1 | 42 | 350 | 2015-07-21 06:10 | 2015-07-21 08:09 | 450 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #35Removed 2-6 Mill from service after receiving indications of a b | Ghent | Derate | Coal | 3 | 2015 | 7 | 1.9833 | 0.26699 | 129.7558 | 65.4231 | 65
GH2 | D1 | 43 | 350 | 2015-07-24 15:15 | 2015-07-25 03:53 | 440 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #362-4 Mill off due to low amps. Inspected and found the feeder pi | Ghent | Derate | Coal | 3 | 2015 | 7 | 12.6333 | 1.9436 | 944.5846 | 74.7692 | 75
GH2 | D1 | 44 | 350 | 2015-07-25 08:30 | 2015-07-25 10:43 | 410 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #372-4C Burner line was plugged with coal that had settled out when | Ghent | Derate | Coal | 3 | 2015 | 7 | 2.2167 | 0.46891 | 227.8904 | 102.8077 | 103
GH2 | PD | 45 | 350 | 2015-07-29 22:00 | 2015-07-29 23:02 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #382-6 Mill off to remove the blank from 2-6 'C' burner line. | Ghent | Derate | Coal | 3 | 2015 | 7 | 1.0333 | 0.11923 | 57.9462 | 56.0769 | 56
GH2 | PD | 46 | 250 | 2015-07-29 23:02 | 2015-07-30 02:45 | 460 | 520 | 486 | Pulverizer feeders | Load Reduction #392-3 Feeder was off to repair the belt splice and calibrate the f | Ghent | Derate | Coal | 3 | 2015 | 7 | 3.7167 | 0.42885 | 208.4192 | 56.0769 | 56
GH2 | D1 | 47 | 340 | 2015-08-02 18:53 | 2015-08-02 21:04 | 450 | 520 | 486 | Other pulverizer problems | Load Reduction #402-4 Mill was off due to noise in the pyrite section. | Ghent | Derate | Coal | 3 | 2015 | 8 | 2.1833 | 0.29391 | 142.8404 | 65.4231 | 65
GH2 | D1 | 48 | 3410 | 2015-08-03 11:03 | 2015-08-03 11:45 | 386 | 520 | 486 | Feedwater pump | Load Reduction #412-2 BFP inboard pump bearing was leaking oil. Dropped load to g | Ghent | Derate | Coal | 3 | 2015 | 8 | 0.7 | 0.18038 | 87.6669 | 125.2385 | 125
GH2 | D1 | 49 | 3631 | 2015-08-08 16:12 | 2015-08-08 17:30 | 228 | 520 | 486 | 480-volt circuit breakers | Load Reduction #422-1 ID fan tripped due to loss of 480V feed to fan. | Ghent | Derate | Coal | 3 | 2015 | 8 | 1.3 | 0.73 | 354.78 | 272.9077 | 273
GH2 | D1 | 50 | 3632 | 2015-08-11 03:35 | 2015-08-11 05:46 | 280 | 520 | 486 | 480-volt conductors and buses | Load Reduction #432E MCC fire limited the ability to get coal to U2 due to CHB iso | Ghent | Derate | Coal | 3 | 2015 | 8 | 2.1833 | 1.0077 | 489.7385 | 224.3077 | 224
GH2 | D1 | 51 | 340 | 2015-08-16 15:25 | 2015-08-16 17:34 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #442-4 Mill off to repair a coal leak on the spring can. | Ghent | Derate | Coal | 3 | 2015 | 8 | 2.15 | 0.24808 | 120.5654 | 56.0769 | 56
GH2 | PD | 52 | 320 | 2015-08-23 08:19 | 2015-08-23 10:19 | 420 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #452-3 Feeder off due to metal in feeder. | Ghent | Derate | Coal | 3 | 2015 | 8 | 2 | 0.38462 | 186.9231 | 93.4615 | 93
GH2 | U2 | 53 | 1000 | 2015-08-23 20:03 | 2015-08-24 20:02 | 0 | 520 | 486 | Waterwall (Furnace wall) A | Outage #8Unit 2 developed a water wall tube leak. Removed the unit from service f | Ghent | Outage | Coal | 3 | 2015 | 8 | 23.9833 | 23.9833 | 11655.9 | 486 | 486
GH2 | PD | 54 | 340 | 2015-08-31 22:10 | 2015-09-01 04:10 | 480 | 520 | 486 | Other pulverizer problems | Load Reduction #462-2 Mill off to replace bolts in the top of the mill that holds | Ghent | Derate | Coal | 3 | 2015 | 8 | 6 | 0.46154 | 224.3077 | 37.3846 | 37
GH2 | D1 | 55 | 340 | 2015-09-14 06:15 | 2015-09-16 07:13 | 450 | 520 | 486 | Other pulverizer problems | Load Reduction #472-5 Mill stopped grinding coal. Removed from service and found | Ghent | Derate | Coal | 3 | 2015 | 9 | 48.9667 | 6.5917 | 3203.55 | 65.4231 | 65
GH2 | PD | 56 | 346 | 2015-09-14 22:00 | 2015-09-15 00:56 | 350 | 520 | 486 | Pulverizer pyrite removal system | Load Reduction #482-6 Mill had a knocking noise in the pyrite section. Removed fr | Ghent | Derate | Coal | 3 | 2015 | 9 | 2.9333 | 0.95897 | 466.0615 | 158.8846 | 159
GH2 | D1 | 57 | 340 | 2015-09-15 13:00 | 2015-09-15 17:18 | 299 | 520 | 486 | Other pulverizer problems | Load Reduction #492-4 Mill feeder belt tore and 2-6 mill journal locked up. Both | Ghent | Derate | Coal | 3 | 2015 | 9 | 4.3 | 1.8275 | 888.165 | 206.55 | 207
GH2 | D1 | 58 | 340 | 2015-09-15 17:18 | 2015-09-15 17:52 | 320 | 520 | 486 | Other pulverizer problems | Load Reduction #502-4 Mill feeder belt was broken and out of service for replaceme | Ghent | Derate | Coal | 3 | 2015 | 9 | 0.56667 | 0.21795 | 105.9231 | 186.9231 | 187
GH2 | U2 | 59 | 1000 | 2015-09-16 07:13 | 2015-09-17 07:33 | 0 | 520 | 486 | Waterwall (Furnace wall) A | F370Outage #9Unit 2 developed a water wall tube leak on 7 1/2 floor, south side of | Ghent | Outage | Coal | 3 | 2015 | 9 | 24.3333 | 24.3333 | 11826 | 486 | 486
GH2 | D1 | 60 | 340 | 2015-09-17 07:33 | 2015-09-25 09:50 | 450 | 520 | 486 | Other pulverizer problems | Load Reduction #512-5 Mill vertical shaft broke. | Ghent | Derate | Coal | 3 | 2015 | 9 | 194.2833 | 26.1535 | 12710.6135 | 65.4231 | 65
GH2 | PO | 61 | 8650 | 2015-09-25 09:50 | 2015-11-27 00:39 | 0 | 520 | 486 | Baghouse systems | F610Outage #10Unit 2 was scheduled for a Planned Fall Outage to do general mainten | Ghent | Other | Coal | 3 | 2015 | 9 | 1502.8167 | 1502.8167 | 730368.9 | 486 | 486
GH2 | D1 | 62 | 340 | 2015-11-28 22:22 | 2015-11-29 01:13 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #522-6 Mill was removed from service to repair pyrite scrapers. | Ghent | Derate | Coal | 3 | 2015 | 11 | 2.85 | 0.32885 | 159.8192 | 56.0769 | 56
GH2 | D1 | 63 | 3661 | 2015-11-30 23:27 | 2015-12-01 02:14 | 300 | 520 | 486 | 4160-volt circuit breakers | Load Reduction #53U2 FGDA 4KV reserve breaker failed. Dropped load until FGD 4KV | Ghent | Derate | Coal | 3 | 2015 | 11 | 2.7833 | 1.1776 | 572.2962 | 205.6154 | 206
GH2 | PD | 64 | 3407 | 2015-12-03 23:38 | 2015-12-04 03:05 | 320 | 520 | 486 | Feedwater pump suction screens | Load Reduction #542-2 BFP was removed from service long enough to backflush the su | Ghent | Derate | Coal | 3 | 2015 | 12 | 3.45 | 1.3269 | 644.8846 | 186.9231 | 187
GH2 | D1 | 65 | 340 | 2015-12-18 02:30 | 2015-12-18 02:41 | 440 | 520 | 486 | Other pulverizer problems | Load Reduction #552-2 Mill burner shut off valve came off the open limit and tripp | Ghent | Derate | Coal | 3 | 2015 | 12 | 0.18333 | 0.028205 | 13.7077 | 74.7692 | 75
GH2 | D1 | 1 | 320 | 2016-01-02 09:00 | 2016-01-02 10:15 | 460 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #12-1 Mill was making loud noise. | Ghent | Derate | Coal | 3 | 2016 | 1 | 1.25 | 0.14423 | 70.0962 | 56.0769 | 56
GH2 | D1 | 2 | 350 | 2016-01-12 23:18 | 2016-01-13 02:15 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #22-2 Mill "D" burner caught fire. Blanked burner line off. | Ghent | Derate | Coal | 3 | 2016 | 1 | 2.95 | 0.34038 | 165.4269 | 56.0769 | 56
GH2 | U1 | 3 | 260 | 2016-01-13 09:17 | 2016-01-13 14:43 | 0 | 520 | 486 | Primary air fan | Outage #1Unit 2 Primary air fan catastrophic failure of fan and motor. | Ghent | Outage | Coal | 3 | 2016 | 1 | 5.4333 | 5.4333 | 2640.6 | 486 | 486
GH2 | D1 | 4 | 320 | 2016-01-19 14:22 | 2016-01-19 15:33 | 460 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #32-1 Mill was removed from service because of a knocking noise com | Ghent | Derate | Coal | 3 | 2016 | 1 | 1.1833 | 0.13654 | 66.3577 | 56.0769 | 56
GH2 | D1 | 5 | 340 | 2016-01-21 13:29 | 2016-01-21 14:08 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #42-5 Mill burner shut off actuator arm came off causing it to come | Ghent | Derate | Coal | 3 | 2016 | 1 | 0.65 | 0.075 | 36.45 | 56.0769 | 56
GH2 | D1 | 6 | 360 | 2016-02-04 06:14 | 2016-02-04 06:38 | 425 | 520 | 486 | Burners | Load Reduction #5High burner temperature on 2-5B mill burner. | Ghent | Derate | Coal | 3 | 2016 | 2 | 0.4 | 0.073077 | 35.5154 | 88.7885 | 89
GH2 | D1 | 7 | 1470 | 2016-02-20 05:18 | 2016-02-20 08:50 | 255 | 520 | 486 | Induced draft fan motors and drives | Load Reduction #62-2 ID fan tripped due to the VFD HVAC compressor going to ground | Ghent | Derate | Coal | 3 | 2016 | 2 | 3.5333 | 1.8006 | 875.1115 | 247.6731 | 248
GH2 | D1 | 8 | 1475 | 2016-02-20 08:50 | 2016-02-20 09:10 | 180 | 520 | 486 | Induced draft fan controls | Load Reduction #7ID and FD fan cross trips were not disabled during the starting o | Ghent | Derate | Coal | 3 | 2016 | 2 | 0.33333 | 0.21795 | 105.9231 | 317.7692 | 318
GH2 | PD | 9 | 340 | 2016-02-25 23:00 | 2016-02-26 09:12 | 420 | 520 | 486 | Other pulverizer problems | Load Reduction #82-5 Mill was off for south journal replacement. | Ghent | Derate | Coal | 3 | 2016 | 2 | 10.2 | 1.9615 | 953.3077 | 93.4615 | 93
GH2 | PD | 10 | 1470 | 2016-02-28 12:35 | 2016-02-28 15:21 | 200 | 520 | 486 | Induced draft fan motors and drives | Load Reduction #92-1 ID fan VFD had a coolant leak. | Ghent | Derate | Coal | 3 | 2016 | 2 | 2.7667 | 1.7026 | 827.4462 | 299.0769 | 299
GH2 | D1 | 11 | 350 | 2016-03-06 18:13 | 2016-03-06 21:01 | 400 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #102-6C Burner fire. | Ghent | Derate | Coal | 3 | 2016 | 3 | 2.8 | 0.64615 | 314.0308 | 112.1538 | 112
GH2 | D1 | 12 | 350 | 2016-03-07 06:09 | 2016-03-07 06:55 | 480 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #11Mill performance problems. 2-2 and 2-6 had burners out. | Ghent | Derate | Coal | 3 | 2016 | 3 | 0.76667 | 0.058974 | 28.6615 | 37.3846 | 37
GH2 | D1 | 13 | 320 | 2016-03-22 05:00 | 2016-03-22 06:02 | 440 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #122-2 Mill feeder plugged. | Ghent | Derate | Coal | 3 | 2016 | 3 | 1.0333 | 0.15897 | 77.2615 | 74.7692 | 75
GH2 | D1 | 14 | 320 | 2016-03-22 06:08 | 2016-03-22 10:53 | 440 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #132-2 Mill feeder plugged. | Ghent | Derate | Coal | 3 | 2016 | 3 | 4.75 | 0.73077 | 355.1538 | 74.7692 | 75
GH2 | PD | 15 | 260 | 2016-03-29 22:00 | 2016-03-30 02:22 | 25 | 520 | 486 | Primary air fan | Load Reduction #14Load reduced to remove blank from 2-3 PA Fan. | Ghent | Derate | Coal | 3 | 2016 | 3 | 4.3667 | 4.1567 | 2020.1712 | 462.6346 | 463
GH2 | PD | 16 | 250 | 2016-04-10 11:46 | 2016-04-10 14:41 | 79 | 520 | 486 | Pulverizer feeders | F590Load Reduction #15Load was reduced to replace 2-3 feeder belt. | Ghent | Derate | Coal | 3 | 2016 | 4 | 2.9167 | 2.4736 | 1202.149 | 412.1654 | 412
GH2 | D1 | 17 | 1850 | 2016-04-23 08:24 | 2016-04-23 20:20 | 360 | 520 | 486 | Boiler water condition (not feedwater water quality) | F830Load Reduction #16Boiler chemistry. | Ghent | Derate | Coal | 3 | 2016 | 4 | 11.9333 | 3.6718 | 1784.4923 | 149.5385 | 150
GH2 | PD | 18 | 340 | 2016-04-27 22:00 | 2016-04-28 00:15 | 420 | 520 | 486 | Other pulverizer problems | F060Load Reduction #172-6 Mill north journal replacement. | Ghent | Derate | Coal | 3 | 2016 | 4 | 2.25 | 0.43269 | 210.2885 | 93.4615 | 93
GH2 | MO | 19 | 3110 | 2016-05-02 22:15 | 2016-05-04 20:32 | 0 | 520 | 486 | Condenser tube leaks | F540Outage #2Unit 2 was removed from service to repair a 2-1 Main Condenser tube l | Ghent | Maintenance | Coal | 3 | 2016 | 5 | 46.2833 | 46.2833 | 22493.7 | 486 | 486
GH2 | PD | 20 | 3410 | 2016-06-07 20:02 | 2016-06-08 08:26 | 345 | 520 | 486 | Feedwater pump | F590Load Reduction #182-2 BFP out of service to rebuild the recirculation valve. | Ghent | Derate | Coal | 3 | 2016 | 6 | 12.4 | 4.1731 | 2028.1154 | 163.5577 | 164
GH2 | D1 | 21 | 1400 | 2016-06-16 12:51 | 2016-06-16 20:33 | 514 | 520 | 486 | Forced draft fans | Load Reduction #19Boiler FD fans maxed out. Not enough air flow. Air flow issue. | Ghent | Derate | Coal | 3 | 2016 | 6 | 7.7 | 0.088846 | 43.1792 | 5.6077 | 6
GH2 | D1 | 22 | 1400 | 2016-06-16 20:33 | 2016-06-17 11:20 | 522 | 520 | 486 | Forced draft fans | Load Reduction #20Boiler FD fans maxed out. Not enough air flow. Air flow issue. | Ghent | Derate | Coal | 3 | 2016 | 6 | 14.7833 | -0.056859 | -27.6335 | 0 | 0
GH2 | D1 | 23 | 4499 | 2016-06-17 11:20 | 2016-07-08 14:27 | 523 | 520 | 486 | Other miscellaneous steam turbine problems | Load Reduction #21Turbine performance. Turbine copper deposition. | Ghent | Derate | Coal | 3 | 2016 | 6 | 507.1167 | -2.9257 | -1421.8771 | 0 | 0
GH2 | D1 | 24 | 340 | 2016-06-20 05:19 | 2016-06-20 08:21 | 440 | 520 | 486 | Other pulverizer problems | Load Reduction #222-3 Mill north journal failed. | Ghent | Derate | Coal | 3 | 2016 | 6 | 3.0333 | 0.46667 | 226.8 | 74.7692 | 75
GH2 | D1 | 25 | 1420 | 2016-06-25 11:00 | 2016-06-25 11:42 | 511 | 520 | 486 | Other forced draft fan problems | F830Load Reduction #23FD fans were maxed out. | Ghent | Derate | Coal | 3 | 2016 | 6 | 0.7 | 0.012115 | 5.8881 | 8.4115 | 8
GH2 | PD | 26 | 3416 | 2016-06-25 23:00 | 2016-06-25 23:35 | 330 | 520 | 486 | Other feedwater pump problems | F590Load Reduction #242-1 BFPT EBOP switch repair and servo replacement. | Ghent | Derate | Coal | 3 | 2016 | 6 | 0.58333 | 0.21314 | 103.5865 | 177.5769 | 178
GH2 | PD | 27 | 3416 | 2016-06-25 23:35 | 2016-06-26 01:39 | 300 | 520 | 486 | Other feedwater pump problems | F590Load Reduction #252-1 BFPT EBOP switch repair and servo replacement. | Ghent | Derate | Coal | 3 | 2016 | 6 | 2.0667 | 0.87436 | 424.9385 | 205.6154 | 206
GH2 | D1 | 28 | 346 | 2016-07-07 07:02 | 2016-07-07 07:13 | 460 | 520 | 486 | Pulverizer pyrite removal system | F590Load Reduction #26OPS Took Mill 2-5 OOS to Unplug Pyrite Chute. Plugged Chute | Ghent | Derate | Coal | 3 | 2016 | 7 | 0.18333 | 0.021154 | 10.2808 | 56.0769 | 56
GH2 | D1 | 29 | 3121 | 2016-07-08 12:27 | 2016-07-08 14:27 | 325 | 520 | 486 | Expansion joint | Load Reduction #27Load was reduced due to high condenser backpressure. | Ghent | Derate | Coal | 3 | 2016 | 7 | 2 | 0.75 | 364.5 | 182.25 | 182
GH2 | U1 | 30 | 3121 | 2016-07-08 14:27 | 2016-07-10 11:25 | 0 | 520 | 486 | Expansion joint | F540Outage #3The unit was removed from service to repair a main condenser expansio | Ghent | Outage | Coal | 3 | 2016 | 7 | 44.9667 | 44.9667 | 21853.8 | 486 | 486
GH2 | D1 | 31 | 3669 | 2016-07-25 12:10 | 2016-07-25 13:07 | 260 | 520 | 486 | Other 4160-volt problems | Load Reduction #28U2 Coal handling bus cable shorted out and tripped the feed brea | Ghent | Derate | Coal | 3 | 2016 | 7 | 0.95 | 0.475 | 230.85 | 243 | 243
GH2 | D1 | 32 | 1470 | 2016-07-28 10:55 | 2016-07-28 11:38 | 285 | 520 | 486 | Induced draft fan motors and drives | Load Reduction #292-1 ID fan VFD tripped when coolant pump grounded out. | Ghent | Derate | Coal | 3 | 2016 | 7 | 0.71667 | 0.32388 | 157.4048 | 219.6346 | 220
GH2 | PD | 33 | 4261 | 2016-08-03 00:12 | 2016-08-03 00:34 | 340 | 520 | 486 | Control valves | F590Load Reduction #30Changing out servo on #4 control valve on main turbine. | Ghent | Derate | Coal | 3 | 2016 | 8 | 0.36667 | 0.12692 | 61.6846 | 168.2308 | 168
GH2 | D1 | 34 | 340 | 2016-08-12 10:22 | 2016-08-12 18:00 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #312-1 Mill was removed from service to inspect due to noise. | Ghent | Derate | Coal | 3 | 2016 | 8 | 7.6333 | 0.88077 | 428.0538 | 56.0769 | 56
GH2 | D1 | 35 | 1480 | 2016-09-02 21:26 | 2016-09-03 05:25 | 219 | 520 | 486 | Other induced draft fan problems | Load Reduction #32Loss of 2-2 ID fan due to coolant PLC going bad. | Ghent | Derate | Coal | 3 | 2016 | 9 | 7.9833 | 4.6211 | 2245.8652 | 281.3192 | 281
GH2 | D1 | 36 | 1480 | 2016-09-03 13:33 | 2016-09-03 20:06 | 250 | 520 | 486 | Other induced draft fan problems | Load Reduction #33Loss of 2-2 ID fan due to coolant PLC going bad and not controll | Ghent | Derate | Coal | 3 | 2016 | 9 | 6.55 | 3.401 | 1652.8673 | 252.3462 | 252
GH2 | D1 | 37 | 340 | 2016-09-06 09:02 | 2016-09-06 09:30 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #342-5 Mill had bad points and tripped when links were put back int | Ghent | Derate | Coal | 3 | 2016 | 9 | 0.46667 | 0.053846 | 26.1692 | 56.0769 | 56
GH2 | PD | 38 | 390 | 2016-09-06 22:21 | 2016-09-07 06:47 | 460 | 520 | 486 | Burner wind boxes and dampers | F700Load Reduction #352-5 Mill burner shut off damper limit switches had wires tha | Ghent | Derate | Coal | 3 | 2016 | 9 | 8.4333 | 0.97308 | 472.9154 | 56.0769 | 56
GH2 | PD | 39 | 1470 | 2016-09-09 23:00 | 2016-09-10 02:55 | 200 | 520 | 486 | Induced draft fan motors and drives | F540Load Reduction #362-1 ID fan VFD coolant leak. 2-2 ID fan PLC change out. | Ghent | Derate | Coal | 3 | 2016 | 9 | 3.9167 | 2.4103 | 1171.3846 | 299.0769 | 299
GH2 | D1 | 40 | 320 | 2016-09-13 14:56 | 2016-09-13 17:21 | 450 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #372-2 Mill was making loud noise and was not performing. | Ghent | Derate | Coal | 3 | 2016 | 9 | 2.4167 | 0.32532 | 158.1058 | 65.4231 | 65
GH2 | PO | 42 | 1801 | 2016-09-28 05:12 | 2016-10-23 17:06 | 0 | 520 | 486 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Outage #5Ghent 2 was removed from service for the Planned Fall Outage. | Ghent | Other | Coal | 3 | 2016 | 9 | 611.9 | 611.9 | 297383.4 | 486 | 486
GH2 | U1 | 43 | 9930 | 2016-10-24 08:27 | 2016-10-24 19:53 | 0 | 520 | 486 | Operating procedure error | F830Outage #6Unit 2 was forced off line to remove scaffold from 2-2 air heater. | Ghent | Outage | Coal | 3 | 2016 | 10 | 11.4333 | 11.4333 | 5556.6 | 486 | 486
GH2 | MO | 44 | 1488 | 2016-10-26 23:11 | 2016-10-29 02:13 | 0 | 520 | 486 | Air heater (regenerative) | F590Outage #7Unit 2 was removed from service to reverse rotation of the Air Heater | Ghent | Maintenance | Coal | 3 | 2016 | 10 | 51.0333 | 51.0333 | 24802.2 | 486 | 486
GH2 | D1 | 45 | 340 | 2016-11-17 01:34 | 2016-11-17 05:19 | 450 | 520 | 486 | Other pulverizer problems | Load Reduction #382-2 Mill was making noise. The mill was taken out of service an | Ghent | Derate | Coal | 3 | 2016 | 11 | 3.75 | 0.50481 | 245.3365 | 65.4231 | 65
GH2 | D1 | 46 | 340 | 2016-12-03 22:49 | 2016-12-04 03:37 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #392-1 Mill east journal failed due to bearings being wiped. | Ghent | Derate | Coal | 3 | 2016 | 12 | 4.8 | 0.55385 | 269.1692 | 56.0769 | 56
GH2 | D1 | 47 | 340 | 2016-12-14 04:19 | 2016-12-14 09:02 | 460 | 520 | 486 | Other pulverizer problems | Load Reduction #40Tripped 2-1 mill due to high temperature and pressure. | Ghent | Derate | Coal | 3 | 2016 | 12 | 4.7167 | 0.54423 | 264.4962 | 56.0769 | 56
GH2 | MO | 1 | 3110 | 2017-01-25 09:53 | 2017-01-26 06:29 | 0 | 520 | 486 | Condenser tube leaks | F540Outage #1Unit 2 was removed from service to repair main condenser tube leaks. | Ghent | Maintenance | Coal | 3 | 2017 | 1 | 20.6 | 20.6 | 10011.6 | 486 | 486
GH2 | D1 | 2 | 1850 | 2017-01-26 14:29 | 2017-01-26 19:00 | 455 | 520 | 486 | Boiler water condition (not feedwater water quality) | F830Load Reduction #1Boiler drum silica was high after coming back from a condense | Ghent | Derate | Coal | 3 | 2017 | 1 | 4.5167 | 0.56458 | 274.3875 | 60.75 | 61
GH2 | D1 | 3 | 340 | 2017-01-30 05:44 | 2017-01-30 06:15 | 470 | 520 | 486 | Other pulverizer problems | F830Load Reduction #22-3 Mill temperature spiked up. Operator tripped mill causin | Ghent | Derate | Coal | 3 | 2017 | 1 | 0.51667 | 0.049679 | 24.1442 | 46.7308 | 47
GH2 | D1 | 4 | 3410 | 2017-02-01 06:42 | 2017-02-01 06:57 | 350 | 520 | 486 | Feedwater pump | F830Load Reduction #32-2 BFP seal injection OB seal water temperature controller f | Ghent | Derate | Coal | 3 | 2017 | 2 | 0.25 | 0.081731 | 39.7212 | 158.8846 | 159
GH2 | MO | 5 | 3210 | 2017-02-18 11:29 | 2017-02-19 04:20 | 0 | 520 | 486 | Circulating water pumps | F860Outage #2U2 was removed from service to the 2-1 BCWP with spare. | Ghent | Maintenance | Coal | 3 | 2017 | 2 | 16.85 | 16.85 | 8189.1 | 486 | 486
GH2 | D1 | 6 | 1850 | 2017-02-19 16:00 | 2017-02-19 19:06 | 477 | 520 | 486 | Boiler water condition (not feedwater water quality) | Load Reduction #4Unit 2 was derated due to high silica after start up of the unit | Ghent | Derate | Coal | 3 | 2017 | 2 | 3.1 | 0.25635 | 124.5842 | 40.1885 | 40
GH2 | MO | 7 | 3110 | 2017-03-04 10:54 | 2017-03-05 10:36 | 0 | 520 | 486 | Condenser tube leaks | F540Outage #3Unit 2 was removed from service to repair tube leaks in the aux and m | Ghent | Maintenance | Coal | 3 | 2017 | 3 | 23.7 | 23.7 | 11518.2 | 486 | 486
GH2 | PD | 8 | 344 | 2017-03-09 22:02 | 2017-03-09 23:52 | 450 | 520 | 486 | Pulverizer inspection | F530Load Reduction #52-6 Mill was removed from service for a inspection. | Ghent | Derate | Coal | 3 | 2017 | 3 | 1.8333 | 0.24679 | 119.9423 | 65.4231 | 65
GH2 | D1 | 9 | 344 | 2017-03-11 01:43 | 2017-03-11 08:34 | 450 | 520 | 486 | Pulverizer inspection | F530Load Reduction #62-3 Mill got hot and was removed from service to inspect for | Ghent | Derate | Coal | 3 | 2017 | 3 | 6.85 | 0.92212 | 448.1481 | 65.4231 | 65
GH2 | D1 | 10 | 340 | 2017-03-31 07:40 | 2017-03-31 11:14 | 470 | 520 | 486 | Other pulverizer problems | Load Reduction #72-3 Mill discharge temperate increased quickly. | Ghent | Derate | Coal | 3 | 2017 | 3 | 3.5667 | 0.34295 | 166.6731 | 46.7308 | 47
GH2 | MO | 11 | 3110 | 2017-04-03 22:56 | 2017-04-04 23:14 | 0 | 520 | 486 | Condenser tube leaks | F540Outage #4Unit 2 was removed from service to repair a condenser tube leak. | Ghent | Maintenance | Coal | 3 | 2017 | 4 | 24.3 | 24.3 | 11809.8 | 486 | 486
GH2 | U1 | 12 | 1000 | 2017-04-13 10:15 | 2017-04-14 02:37 | 0 | 520 | 486 | Waterwall (Furnace wall) A | F540Outage #5The unit was forced off line due to a water wall tube leak. | Ghent | Outage | Coal | 3 | 2017 | 4 | 16.3667 | 16.3667 | 7954.2 | 486 | 486
GH2 | MO | 13 | 3110 | 2017-05-05 21:38 | 2017-05-06 14:40 | 0 | 520 | 486 | Condenser tube leaks | F540Outage #6GH2 was removed from service to repair a condenser tube leak. | Ghent | Maintenance | Coal | 3 | 2017 | 5 | 17.0333 | 17.0333 | 8278.2 | 486 | 486
GH2 | D1 | 15 | 1850 | 2017-05-09 16:58 | 2017-05-09 18:49 | 462 | 520 | 486 | Boiler water condition (not feedwater water quality) | F830Load Reduction #8Load was reduced after start up of the unit due to high boile | Ghent | Derate | Coal | 3 | 2017 | 5 | 1.85 | 0.20635 | 100.2842 | 54.2077 | 54
GH2 | PD | 16 | 340 | 2017-05-12 04:00 | 2017-05-12 05:09 | 465 | 520 | 486 | Other pulverizer problems | F590Load Reduction #92-5 Mill was removed from service to replace the primary air | Ghent | Derate | Coal | 3 | 2017 | 5 | 1.15 | 0.12163 | 59.1144 | 51.4038 | 51
GH2 | PD | 17 | 3408 | 2017-05-31 22:37 | 2017-06-01 01:10 | 330 | 520 | 486 | Feedwater pump drive - local controls | F590Load Reduction #10Planned derate to replace 2-2 BFPT vibration probe. | Ghent | Derate | Coal | 3 | 2017 | 5 | 2.55 | 0.93173 | 452.8212 | 177.5769 | 178
GH2 | PD | 18 | 340 | 2017-06-04 23:00 | 2017-06-05 02:48 | 448 | 520 | 486 | Other pulverizer problems | F590Load Reduction #11Planned derate to replaced 2-2 Mill north journal. | Ghent | Derate | Coal | 3 | 2017 | 6 | 3.8 | 0.52615 | 255.7108 | 67.2923 | 67
GH2 | D1 | 19 | 350 | 2017-07-05 14:26 | 2017-07-05 15:41 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #122-6C Burner line fire next to windbox. | Ghent | Derate | Coal | 3 | 2017 | 7 | 1.25 | 0.14423 | 70.0962 | 56.0769 | 56
GH2 | D1 | 20 | 9020 | 2017-07-07 18:37 | 2017-07-07 19:42 | 240 | 520 | 486 | Lightning | Load Reduction #132-1 ID Fan cooling pump tripped due to lightning strike. | Ghent | Derate | Coal | 3 | 2017 | 7 | 1.0833 | 0.58333 | 283.5 | 261.6923 | 262
GH2 | D1 | 21 | 3408 | 2017-07-24 04:53 | 2017-07-24 09:28 | 350 | 520 | 486 | Feedwater pump drive - local controls | Load Reduction #142-2 BFPT won't reset due to a bad LVDT card in DCS. | Ghent | Derate | Coal | 3 | 2017 | 7 | 4.5833 | 1.4984 | 728.2212 | 158.8846 | 159
GH2 | D1 | 22 | 250 | 2017-07-24 20:15 | 2017-07-24 21:16 | 460 | 520 | 486 | Pulverizer feeders | Load Reduction #152-2 Mill feeder had a piece of rebar stuck in the feeder belt. | Ghent | Derate | Coal | 3 | 2017 | 7 | 1.0167 | 0.11731 | 57.0115 | 56.0769 | 56
GH2 | PD | 23 | 344 | 2017-07-24 23:00 | 2017-07-25 01:56 | 460 | 520 | 486 | Pulverizer inspection | F590Load Reduction #16Removed and relocated air flow transmitter on 2-5 mill. | Ghent | Derate | Coal | 3 | 2017 | 7 | 2.9333 | 0.33846 | 164.4923 | 56.0769 | 56
GH2 | PD | 24 | 250 | 2017-07-25 23:00 | 2017-07-26 02:14 | 440 | 520 | 486 | Pulverizer feeders | F060Load Reduction #172-2 Mill feeder belt replacement. | Ghent | Derate | Coal | 3 | 2017 | 7 | 3.2333 | 0.49744 | 241.7538 | 74.7692 | 75
GH2 | PD | 25 | 250 | 2017-08-04 21:30 | 2017-08-05 00:16 | 460 | 520 | 486 | Pulverizer feeders | F090Load Reduction #182-1 Mill inspection and feeder calibration. | Ghent | Derate | Coal | 3 | 2017 | 8 | 2.7667 | 0.31923 | 155.1462 | 56.0769 | 56
GH2 | D1 | 26 | 320 | 2017-08-10 12:16 | 2017-08-10 13:48 | 460 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #192-2 Mill was removed from service to remove a piece of metal fro | Ghent | Derate | Coal | 3 | 2017 | 8 | 1.5333 | 0.17692 | 85.9846 | 56.0769 | 56
GH2 | MO | 28 | 3110 | 2017-08-26 06:00 | 2017-08-26 14:43 | 0 | 520 | 486 | Condenser tube leaks | F540Outage #9Reserve Outage changed to a Maintenance Outage to repair Condenser Tu | Ghent | Maintenance | Coal | 3 | 2017 | 8 | 8.7167 | 8.7167 | 4236.3 | 486 | 486
GH2 | D1 | 30 | 340 | 2017-09-07 18:42 | 2017-09-07 20:48 | 440 | 520 | 486 | Other pulverizer problems | Load Reduction #202-2 Mill was removed from service due to high amps and overheati | Ghent | Derate | Coal | 3 | 2017 | 9 | 2.1 | 0.32308 | 157.0154 | 74.7692 | 75
GH2 | D1 | 31 | 9920 | 2017-09-14 07:20 | 2017-09-14 09:36 | 325 | 520 | 486 | Contractor error | Load Reduction #21Contractors erecting scaffolding knocked an oil line off on the | Ghent | Derate | Coal | 3 | 2017 | 9 | 2.2667 | 0.85 | 413.1 | 182.25 | 182
GH2 | D1 | 32 | 1000 | 2017-09-27 11:07 | 2017-09-27 12:15 | 225 | 520 | 486 | Waterwall (Furnace wall) A | F540Load Reduction #22Load was reduced due to WW Tube Leak on east wall.*Capac | Ghent | Derate | Coal | 3 | 2017 | 9 | 1.1333 | 0.64295 | 312.4731 | 275.7115 | 276
GH2 | U1 | 33 | 1000 | 2017-09-27 12:15 | 2017-09-29 01:21 | 0 | 520 | 486 | Waterwall (Furnace wall) A | F540Outage # 11Water wall tube leak on east wall. | Ghent | Outage | Coal | 3 | 2017 | 9 | 37.1 | 37.1 | 18030.6 | 486 | 486
GH2 | D1 | 34 | 1471 | 2017-10-03 14:55 | 2017-10-03 16:20 | 200 | 520 | 486 | Induced draft fan motors - variable speed | Load Reduction # 232-2 ID Fan VFD trailer UPS went to ground tripping fan. | Ghent | Derate | Coal | 3 | 2017 | 10 | 1.4167 | 0.87179 | 423.6923 | 299.0769 | 299
GH2 | D1 | 35 | 1471 | 2017-10-03 16:20 | 2017-10-03 17:15 | 240 | 520 | 486 | Induced draft fan motors - variable speed | F820Load Reduction # 242-2 ID Fan VFD trailer UPS went to ground tripping fan. | Ghent | Derate | Coal | 3 | 2017 | 10 | 0.91667 | 0.49359 | 239.8846 | 261.6923 | 262
GH2 | D1 | 36 | 340 | 2017-10-10 20:24 | 2017-10-10 21:52 | 440 | 520 | 486 | Other pulverizer problems | F830Load Reduction #252-5 Coal Mill Journal issues. | Ghent | Derate | Coal | 3 | 2017 | 10 | 1.4667 | 0.22564 | 109.6615 | 74.7692 | 75
GH2 | D1 | 37 | 340 | 2017-10-10 21:52 | 2017-10-11 02:06 | 450 | 520 | 486 | Other pulverizer problems | F830Load Reduction #262-5 Coal Mill Journal Issue inspection. | Ghent | Derate | Coal | 3 | 2017 | 10 | 4.2333 | 0.56987 | 276.9577 | 65.4231 | 65
GH2 | D1 | 38 | 250 | 2017-10-14 16:09 | 2017-10-14 19:13 | 460 | 520 | 486 | Pulverizer feeders | F830Load Reduction #272-1 Mill feeder belt seperated. | Ghent | Derate | Coal | 3 | 2017 | 10 | 3.0667 | 0.35385 | 171.9692 | 56.0769 | 56
GH2 | PO | 39 | 1801 | 2017-10-20 22:35 | 2017-11-11 16:43 | 0 | 520 | 486 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Outage #12GH2 was removed from service for a Planned Outage. | Ghent | Other | Coal | 3 | 2017 | 10 | 522.1333 | 522.1333 | 253756.8 | 486 | 486
GH2 | U1 | 40 | 3441 | 2017-11-11 20:55 | 2017-11-12 09:33 | 0 | 520 | 486 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F540Outage #13Unit 2 was forced off line due to F heater inlet valve packing leak. | Ghent | Outage | Coal | 3 | 2017 | 11 | 12.6333 | 12.6333 | 6139.8 | 486 | 486
GH2 | D1 | 41 | 253 | 2017-11-13 04:38 | 2017-11-13 05:51 | 460 | 520 | 486 | Pulverizer feeder motor | F830Load Reduction #282-5 Mill Feeder motor would not start. | Ghent | Derate | Coal | 3 | 2017 | 11 | 1.2167 | 0.14038 | 68.2269 | 56.0769 | 56
GH2 | D1 | 42 | 320 | 2017-11-26 10:40 | 2017-11-26 12:15 | 460 | 520 | 486 | Foreign object in Pulverizers mill | Load Reduction #29 2-5 Mill was removed from service to remove a piece of metal. | Ghent | Derate | Coal | 3 | 2017 | 11 | 1.5833 | 0.18269 | 88.7885 | 56.0769 | 56
GH2 | D1 | 43 | 350 | 2017-12-01 09:13 | 2017-12-01 10:49 | 460 | 520 | 486 | Pulverized fuel and air piping (from pulverizer to wind box) | F830Load Reduction #302-5 Coal mill burner line Cgot hot and tripped mill for inspec | Ghent | Derate | Coal | 3 | 2017 | 12 | 1.6 | 0.18462 | 89.7231 | 56.0769 | 56
GH2 | D1 | 44 | 346 | 2017-12-06 00:40 | 2017-12-06 03:39 | 460 | 520 | 486 | Pulverizer pyrite removal system | F830Load Reduction #312-2 mill has broken pyrite scrappers. Noisy in pyrite secti | Ghent | Derate | Coal | 3 | 2017 | 12 | 2.9833 | 0.34423 | 167.2962 | 56.0769 | 56
GH2 | D1 | 45 | 340 | 2017-12-21 12:52 | 2017-12-21 15:31 | 460 | 520 | 486 | Other pulverizer problems | F830Load Reduction #32Removed 2-1 pulverizer from service for inspection. Washed | Ghent | Derate | Coal | 3 | 2017 | 12 | 2.65 | 0.30577 | 148.6038 | 56.0769 | 56
GH2 | D1 | 46 | 340 | 2017-12-30 18:03 | 2017-12-30 18:55 | 460 | 520 | 486 | Other pulverizer problems | F830Load Reduction #332-3 pulverizer loaded up and had very high discharge temp. | Ghent | Derate | Coal | 3 | 2017 | 12 | 0.86667 | 0.1 | 48.6 | 56.0769 | 56
GH2 | D1 | 1 | 340 | 2018-01-02 12:56 | 2018-01-02 13:30 | 460 | 520 | 486 | Other pulverizer problems | F830Load Reduction #12-1 mill feeder plugging under knife gate causing no coal on | Ghent | Derate | Coal | 3 | 2018 | 1 | 0.56667 | 0.065385 | 31.7769 | 56.0769 | 56
GH2 | D1 | 2 | 1470 | 2018-01-16 06:05 | 2018-01-16 06:58 | 220 | 520 | 486 | Induced draft fan motors and drives | F820Load Reduction #22-2 ID fan trip. | Ghent | Derate | Coal | 3 | 2018 | 1 | 0.88333 | 0.50962 | 247.6731 | 280.3846 | 280
GH2 | D1 | 3 | 3408 | 2018-01-22 03:28 | 2018-01-22 04:39 | 340 | 520 | 486 | Feedwater pump drive - local controls | F830Load Reduction #32-2 BFPT would not reset after doing feed pump test. | Ghent | Derate | Coal | 3 | 2018 | 1 | 1.1833 | 0.40962 | 199.0731 | 168.2308 | 168
GH2 | D1 | 4 | 346 | 2018-01-23 08:00 | 2018-01-23 09:32 | 450 | 520 | 486 | Pulverizer pyrite removal system | F830Load Reduction #4Excessive knocking noise in the pyrite section of 2-6 mill. | Ghent | Derate | Coal | 3 | 2018 | 1 | 1.5333 | 0.20641 | 100.3154 | 65.4231 | 65
GH2 | PD | 5 | 253 | 2018-01-26 | 2018-01-26 01:22 | 460 | 520 | 486 | Pulverizer feeder motor | F590Load Reduction #52-5 coal feeder maintenance. | Ghent | Derate | Coal | 3 | 2018 | 1 | 1.3667 | 0.15769 | 76.6385 | 56.0769 | 56
GH2 | PD | 6 | 255 | 2018-01-29 22:04 | 2018-01-30 03:56 | 460 | 520 | 486 | Pulverizer feeder coal scales | F590Load Reduction #6Calibrate feeders 2-1, 2-2, 2-3. | Ghent | Derate | Coal | 3 | 2018 | 1 | 5.8667 | 0.67692 | 328.9846 | 56.0769 | 56
GH2 | PD | 7 | 250 | 2018-01-30 22:00 | 2018-01-31 02:57 | 460 | 520 | 486 | Pulverizer feeders | F590Load Reduction #7Feeder cals 2-4, 2-5, 2-6 | Ghent | Derate | Coal | 3 | 2018 | 1 | 4.95 | 0.57115 | 277.5808 | 56.0769 | 56
GH2 | PD | 8 | 3690 | 2018-02-16 00:02 | 2018-02-16 02:50 | 300 | 520 | 486 | Station Service Power Distribution System - General | F590Load Reduction #8Took MCC out of service that had 2 mill feeders on it. | Ghent | Derate | Coal | 3 | 2018 | 2 | 2.8 | 1.1846 | 575.7231 | 205.6154 | 206
GH2 | D1 | 9 | 344 | 2018-02-18 03:55 | 2018-02-18 06:17 | 460 | 520 | 486 | Pulverizer inspection | F590Load Reduction #92-3 mill inspection. | Ghent | Derate | Coal | 3 | 2018 | 2 | 2.3667 | 0.27308 | 132.7154 | 56.0769 | 56
GH2 | D1 | 10 | 320 | 2018-02-18 14:04 | 2018-02-18 15:04 | 460 | 520 | 486 | Foreign object in Pulverizers mill | F590Load Reduction #102-6 mill inspection. | Ghent | Derate | Coal | 3 | 2018 | 2 | 1 | 0.11538 | 56.0769 | 56.0769 | 56
GH2 | MO | 11 | 4302 | 2018-02-19 11:10 | 2018-02-20 02:59 | 0 | 520 | 486 | Turbine trip devices (including instruments) | F590Outage #1Unit was removed from service on a maintenance outage to repair front | Ghent | Maintenance | Coal | 3 | 2018 | 2 | 15.8167 | 15.8167 | 7686.9 | 486 | 486
GH2 | D1 | 12 | 344 | 2018-02-25 16:48 | 2018-02-25 20:35 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #112-3 mill issues. | Ghent | Derate | Coal | 3 | 2018 | 2 | 3.7833 | 0.43654 | 212.1577 | 56.0769 | 56
GH2 | D1 | 13 | 344 | 2018-02-25 22:37 | 2018-02-25 23:52 | 460 | 520 | 486 | Pulverizer inspection | Load Reduction #122-3 mill issues | Ghent | Derate | Coal | 3 | 2018 | 2 | 1.25 | 0.14423 | 70.0962 | 56.0769 | 56
GH2 | D1 | 14 | 310 | 2018-02-25 23:52 | 2018-02-26 03:37 | 440 | 520 | 486 | Pulverizer mills | FW00Load Reduction #13Wet coal keeping 5 mills from getting to 460 mw and 2-3 mill | Ghent | Derate | Coal | 3 | 2018 | 2 | 3.75 | 0.57692 | 280.3846 | 74.7692 | 75
GH2 | D1 | 15 | 344 | 2018-02-26 03:37 | 2018-02-26 06:10 | 460 | 520 | 486 | Pulverizer inspection | F590Load Reduction #142-3 mill issues. | Ghent | Derate | Coal | 3 | 2018 | 2 | 2.55 | 0.29423 | 142.9962 | 56.0769 | 56
GH2 | D1 | 16 | 9270 | 2018-02-26 06:10 | 2018-02-27 10:22 | 424 | 520 | 486 | Wet coal | Load Reduction #152-3 mill out of service/wet coal issues. | Ghent | Derate | Coal | 3 | 2018 | 2 | 28.2 | 5.2062 | 2530.1908 | 89.7231 | 90
GH2 | MO | 17 | 270 | 2018-02-27 10:22 | 2018-02-27 22:16 | 0 | 520 | 486 | Primary air duct and dampers | Outage #2Unit was removed from service to repair 2-3 mill hot air duct that was da | Ghent | Maintenance | Coal | 3 | 2018 | 2 | 11.9 | 11.9 | 5783.4 | 486 | 486
GH2 | D1 | 18 | 270 | 2018-02-27 22:17 | 2018-03-01 10:45 | 392 | 520 | 486 | Primary air duct and dampers | Load Reduction #162-3 mill / #2 main steam stop valve. | Ghent | Derate | Coal | 3 | 2018 | 2 | 36.4667 | 8.9764 | 4362.5354 | 119.6308 | 120
GH2 | D1 | 19 | 310 | 2018-03-01 11:02 | 2018-03-01 20:01 | 450 | 520 | 486 | Pulverizer mills | F590Load Reduction #172-3 mill issues | Ghent | Derate | Coal | 3 | 2018 | 3 | 8.9833 | 1.2093 | 587.7173 | 65.4231 | 65
GH2 | D1 | 20 | 310 | 2018-03-01 20:22 | 2018-03-03 13:02 | 374 | 520 | 486 | Pulverizer mills | F590Load Reduction #182-3 mill issues. | Ghent | Derate | Coal | 3 | 2018 | 3 | 40.6667 | 11.4179 | 5549.1231 | 136.4538 | 136
GH2 | D1 | 21 | 331 | 2018-03-19 08:38 | 2018-03-19 10:23 | 460 | 520 | 486 | Pulverizer system coal leaks (other than pulverizers | F590Load Reduction #192-6 mill had a burner line leak. | Ghent | Derate | Coal | 3 | 2018 | 3 | 1.75 | 0.20192 | 98.1346 | 56.0769 | 56
GH2 | D1 | 22 | 320 | 2018-03-30 12:05 | 2018-03-30 12:30 | 460 | 520 | 486 | Foreign object in Pulverizers mill | F590Load Reduction #20Metal in 2-5 coal mill. | Ghent | Derate | Coal | 3 | 2018 | 3 | 0.41667 | 0.048077 | 23.3654 | 56.0769 | 56
GH2 | D1 | 23 | 1470 | 2018-04-05 14:12 | 2018-04-05 19:53 | 376 | 520 | 486 | Induced draft fan motors and drives | F820Load Reduction #21Loss of both IDs (2-1 & 2-2) due to voltage drop. | Ghent | Derate | Coal | 3 | 2018 | 4 | 5.6833 | 1.5738 | 764.8892 | 134.5846 | 135
GH2 | D1 | 24 | 253 | 2018-04-19 20:12 | 2018-04-20 01:57 | 460 | 520 | 486 | Pulverizer feeder motor | F060Load Reduction #222-6 mill feeder motor broken output shaft. | Ghent | Derate | Coal | 3 | 2018 | 4 | 5.75 | 0.66346 | 322.4423 | 56.0769 | 56
GH2 | D1 | 25 | 346 | 2018-04-22 02:00 | 2018-04-22 07:52 | 460 | 520 | 486 | Pulverizer pyrite removal system | F060Load Reduction #232-2 mill pyrite scraper failed and plugged the pyrite chute. | Ghent | Derate | Coal | 3 | 2018 | 4 | 5.8667 | 0.67692 | 328.9846 | 56.0769 | 56
GH2 | D1 | 26 | 346 | 2018-04-29 00:48 | 2018-04-29 08:46 | 465 | 520 | 486 | Pulverizer pyrite removal system | Load Reduction #242-2 mill pyrite scraper broken and damage to pyrite section floo | Ghent | Derate | Coal | 3 | 2018 | 4 | 7.9667 | 0.84263 | 409.5173 | 51.4038 | 51
GH3 | MO | 1 | 1455 | 2013-01-28 11:14 | 2013-01-31 08:42 | 0 | 528 | 479 | Induced draft fans | F850Outage #1Unit 3 3-2 ID fan inboard fan bearing vibration was high and increasi | Ghent | Maintenance | Coal | 3 | 2013 | 1 | 69.4667 | 69.4667 | 33274.5333 | 479 | 479
GH3 | D1 | 2 | 1455 | 2013-02-01 10:28 | 2013-02-01 11:33 | 400 | 528 | 479 | Induced draft fans | Load Reduction #13-2 ID fan outboard bearing temperature spiked. Operators droppe | Ghent | Derate | Coal | 3 | 2013 | 2 | 1.0833 | 0.26263 | 125.798 | 116.1212 | 116
GH3 | D1 | 3 | 1455 | 2013-03-24 19:15 | 2013-03-26 19:15 | 515 | 528 | 479 | Induced draft fans | Load Reduction #23-2 ID outboard bearing temperature spiked. | Ghent | Derate | Coal | 3 | 2013 | 3 | 48 | 1.1818 | 566.0909 | 11.7936 | 12
GH3 | D1 | 4 | 1493 | 2013-03-27 05:36 | 2013-04-04 14:09 | 515 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #3ID fan inlet duct pressure limit was exceeded due to air heater p | Ghent | Derate | Coal | 3 | 2013 | 3 | 200.55 | 4.9378 | 2365.1986 | 11.7936 | 12
GH3 | MO | 5 | 1493 | 2013-04-04 14:09 | 2013-04-07 19:57 | 0 | 528 | 479 | Air heater fouling (regenerative) | F320Outage #2Unit had been running high differential on Air Heaters. Removed unit | Ghent | Maintenance | Coal | 3 | 2013 | 4 | 77.8 | 77.8 | 37266.2 | 479 | 479
GH3 | D1 | 7 | 1455 | 2013-04-08 12:39 | 2013-04-08 12:50 | 530 | 528 | 479 | Induced draft fans | Load Reduction #5High ID fan amps. | Ghent | Derate | Coal | 3 | 2013 | 4 | 0.18333 | -0.00069444 | -0.33264 | 0 | 0
GH3 | MO | 8 | 1535 | 2013-04-12 23:56 | 2013-04-14 06:44 | 0 | 528 | 479 | Flue gas recirculating fan | F540Outage #33-2 ID fan was running with a fan internal oil leak on the OB fan bea | Ghent | Maintenance | Coal | 3 | 2013 | 4 | 30.8 | 30.8 | 14753.2 | 479 | 479
GH3 | D1 | 9 | 340 | 2013-04-17 22:34 | 2013-04-17 22:57 | 450 | 528 | 479 | Other pulverizer problems | Load Reduction #6Lost 3-3 mill. | Ghent | Derate | Coal | 3 | 2013 | 4 | 0.38333 | 0.056629 | 27.1252 | 70.7614 | 71
GH3 | D1 | 10 | 1493 | 2013-05-02 06:44 | 2013-05-03 07:38 | 514 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #7U3 ID fan inlet duct in high alarm due to air heater pluggage. | Ghent | Derate | Coal | 3 | 2013 | 5 | 24.9 | 0.66023 | 316.2489 | 12.7008 | 13
GH3 | D1 | 11 | 1493 | 2013-05-03 07:38 | 2013-05-03 10:32 | 520 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #8ID Fan inlet duct in high alarm. Derate changed from 514 to 520 | Ghent | Derate | Coal | 3 | 2013 | 5 | 2.9 | 0.043939 | 21.047 | 7.2576 | 7
GH3 | D1 | 12 | 1493 | 2013-05-03 10:32 | 2013-05-05 11:23 | 514 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #9ID Fan inlet duct in high alarm. Derate changed from 520 to 514 | Ghent | Derate | Coal | 3 | 2013 | 5 | 48.85 | 1.2953 | 620.432 | 12.7008 | 13
GH3 | D1 | 13 | 1493 | 2013-05-05 11:23 | 2013-05-05 19:45 | 514 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #10ID Fan inlet duct in high alarm. | Ghent | Derate | Coal | 3 | 2013 | 5 | 8.3667 | 0.22184 | 106.263 | 12.7008 | 13
GH3 | D1 | 14 | 1493 | 2013-05-05 19:45 | 2013-05-05 20:18 | 522 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #11ID Fan inlet duct in high alarm. | Ghent | Derate | Coal | 3 | 2013 | 5 | 0.55 | 0.00625 | 2.9938 | 5.4432 | 5
GH3 | D1 | 15 | 1493 | 2013-05-05 20:18 | 2013-05-07 11:03 | 518 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #12U3 ID fan inlet duct in high alarm. | Ghent | Derate | Coal | 3 | 2013 | 5 | 38.75 | 0.7339 | 351.5388 | 9.072 | 9
GH3 | D1 | 16 | 1493 | 2013-05-07 11:03 | 2013-05-10 11:25 | 508 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #13U3 ID fan inlet duct in high alarm. | Ghent | Derate | Coal | 3 | 2013 | 5 | 72.3667 | 2.7412 | 1313.0164 | 18.1439 | 18
GH3 | D1 | 17 | 1493 | 2013-05-10 11:25 | 2013-05-10 19:30 | 500 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #14U3 ID fan inlet duct in high alarm. | Ghent | Derate | Coal | 3 | 2013 | 5 | 8.0833 | 0.42866 | 205.3289 | 25.4015 | 25
GH3 | D1 | 18 | 1493 | 2013-05-10 19:30 | 2013-05-10 20:30 | 510 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #15U3 ID fan inlet duct in high alarm. | Ghent | Derate | Coal | 3 | 2013 | 5 | 1 | 0.034091 | 16.3295 | 16.3295 | 16
GH3 | D1 | 20 | 1493 | 2013-05-10 19:30 | 2013-05-10 20:30 | 510 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #17U3 ID fan inlet duct in high alarm. | Ghent | Derate | Coal | 3 | 2013 | 5 | 1 | 0.034091 | 16.3295 | 16.3295 | 16
GH3 | D1 | 21 | 1493 | 2013-05-10 20:30 | 2013-05-16 06:17 | 505 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #18U3 ID fan inlet duct in high alarm. | Ghent | Derate | Coal | 3 | 2013 | 5 | 129.7833 | 5.6534 | 2707.9981 | 20.8655 | 21
GH3 | D1 | 22 | 1493 | 2013-05-16 06:17 | 2013-05-16 16:05 | 505 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #19U3 ID fan inlet duct in high alarm. | Ghent | Derate | Coal | 3 | 2013 | 5 | 9.8 | 0.42689 | 204.4822 | 20.8655 | 21
GH3 | D1 | 23 | 1493 | 2013-05-16 16:05 | 2013-05-19 20:55 | 505 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #20U3 ID fan inlet duct in high alarm. | Ghent | Derate | Coal | 3 | 2013 | 5 | 76.8333 | 3.3469 | 1603.1682 | 20.8655 | 21
GH3 | D1 | 24 | 1493 | 2013-05-19 20:55 | 2013-05-23 23:50 | 490 | 528 | 479 | Air heater fouling (regenerative) | Load Reduction #21U3 ID fan inlet duct in high alarm. | Ghent | Derate | Coal | 3 | 2013 | 5 | 98.9167 | 7.119 | 3410.0022 | 34.4735 | 34
GH3 | MO | 25 | 1493 | 2013-05-23 23:50 | 2013-05-27 09:05 | 0 | 528 | 479 | Air heater fouling (regenerative) | F320Outage #4Air heater differentials have been increasing over the past weeks. R | Ghent | Maintenance | Coal | 3 | 2013 | 5 | 81.25 | 81.25 | 38918.75 | 479 | 479
GH3 | MO | 26 | 1500 | 2013-05-31 22:35 | 2013-06-02 18:59 | 0 | 528 | 479 | Air heater soot blowers | F060Outage #53-2 Air heater blower was not traveling correctly. Disconnected its | Ghent | Maintenance | Coal | 3 | 2013 | 5 | 44.4 | 44.4 | 21267.6 | 479 | 479
GH3 | D1 | 27 | 4499 | 2013-06-06 09:17 | 2013-06-13 11:30 | 528 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #22Turbine performance. | Ghent | Derate | Coal | 3 | 2013 | 6 | 170.2167 | 0 | 0 | 0 | 0
GH3 | D1 | 28 | 4499 | 2013-06-13 11:30 | 2013-06-17 18:10 | 520 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #23Turbine performance. | Ghent | Derate | Coal | 3 | 2013 | 6 | 102.6667 | 1.5556 | 745.1111 | 7.2576 | 7
GH3 | D1 | 29 | 1455 | 2013-06-17 18:10 | 2013-06-17 18:55 | 510 | 528 | 479 | Induced draft fans | Load Reduction #243-1 ID Fan inlet duct pressure became high. | Ghent | Derate | Coal | 3 | 2013 | 6 | 0.75 | 0.025568 | 12.2472 | 16.3295 | 16
GH3 | D1 | 30 | 4499 | 2013-06-17 18:55 | 2013-06-29 14:02 | 520 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #25Turbine performance. | Ghent | Derate | Coal | 3 | 2013 | 6 | 283.1167 | 4.2896 | 2054.7407 | 7.2576 | 7
GH3 | D1 | 31 | 4499 | 2013-06-29 14:02 | 2013-07-01 14:45 | 510 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #26Turbine degredation due to copper desposits. Also, 3-2 ID fan m | Ghent | Derate | Coal | 3 | 2013 | 6 | 48.7167 | 1.6608 | 795.521 | 16.3295 | 16
GH3 | D1 | 32 | 4499 | 2013-07-01 14:45 | 2013-07-04 17:45 | 520 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #27Turbine degredation due to copper desposits. Also, 3-2 ID fan m | Ghent | Derate | Coal | 3 | 2013 | 7 | 75 | 1.1364 | 544.3182 | 7.2576 | 7
GH3 | D1 | 33 | 260 | 2013-07-04 17:45 | 2013-07-04 18:20 | 410 | 528 | 479 | Primary air fan | Load Reduction #283-3 PA Fan inlet vane linkage broke. | Ghent | Derate | Coal | 3 | 2013 | 7 | 0.58333 | 0.13037 | 62.4454 | 107.0492 | 107
GH3 | D1 | 34 | 4499 | 2013-07-04 18:20 | 2013-07-05 15:27 | 520 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #29The unit derated due to turbine degredation. | Ghent | Derate | Coal | 3 | 2013 | 7 | 21.1167 | 0.31995 | 153.2558 | 7.2576 | 7
GH3 | D1 | 35 | 4499 | 2013-07-05 15:27 | 2013-07-26 10:50 | 515 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #30The unit derated due to turbine degredation. | Ghent | Derate | Coal | 3 | 2013 | 7 | 499.3833 | 12.2954 | 5889.5076 | 11.7936 | 12
GH3 | D1 | 36 | 250 | 2013-07-15 13:21 | 2013-07-15 13:48 | 415 | 528 | 479 | Pulverizer feeders | Load Reduction #313-6 Feeder tripped. | Ghent | Derate | Coal | 3 | 2013 | 7 | 0.45 | 0.096307 | 46.131 | 102.5133 | 103
GH3 | D1 | 37 | 4499 | 2013-07-26 10:50 | 2013-09-07 07:00 | 520 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #32The unit is derated due to turbine performance. | Ghent | Derate | Coal | 3 | 2013 | 7 | 1028.1667 | 15.5783 | 7461.9975 | 7.2576 | 7
GH3 | PD | 38 | 3440 | 2013-07-30 22:11 | 2013-08-01 23:00 | 511 | 528 | 479 | High pressure heater tube leaks | F540Load Reduction #33HP Heaters are out of service for leak repair. | Ghent | Derate | Coal | 3 | 2013 | 7 | 48.8167 | 1.5717 | 752.8676 | 15.4223 | 15
GH3 | D1 | 39 | 4499 | 2013-08-08 13:48 | 2013-08-28 15:10 | 515 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #34Turbine performance due to copper deposits. | Ghent | Derate | Coal | 3 | 2013 | 8 | 481.3667 | 11.8518 | 5677.027 | 11.7936 | 12
GH3 | D1 | 40 | 1455 | 2013-08-28 15:10 | 2013-08-29 09:55 | 10 | 528 | 479 | Induced draft fans | Load Reduction #35U3 ID Fans reached maximum limit. | Ghent | Derate | Coal | 3 | 2013 | 8 | 18.75 | 18.3949 | 8811.1506 | 469.928 | 470
GH3 | D1 | 41 | 1455 | 2013-08-31 12:00 | 2013-09-03 07:00 | 510 | 528 | 479 | Induced draft fans | Load Reduction #36ID Fan limited by duct pressure. | Ghent | Derate | Coal | 3 | 2013 | 8 | 67 | 2.2841 | 1094.0795 | 16.3295 | 16
GH3 | D1 | 42 | 4499 | 2013-09-07 07:00 | 2013-09-15 08:00 | 520 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #37Load is reduced due to Turbine performance. | Ghent | Derate | Coal | 3 | 2013 | 9 | 193 | 2.9242 | 1400.7121 | 7.2576 | 7
GH3 | D1 | 43 | 4499 | 2013-09-15 08:00 | 2013-09-20 12:08 | 520 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #38Turbine performance. | Ghent | Derate | Coal | 3 | 2013 | 9 | 124.1333 | 1.8808 | 900.9071 | 7.2576 | 7
GH3 | D1 | 44 | 4499 | 2013-09-20 12:08 | 2013-09-29 18:10 | 515 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #39Turbine performance. ID fan running at limit. | Ghent | Derate | Coal | 3 | 2013 | 9 | 222.0333 | 5.4667 | 2618.5636 | 11.7936 | 12
GH3 | D1 | 45 | 3210 | 2013-09-26 02:34 | 2013-09-26 04:10 | 460 | 528 | 479 | Circulating water pumps | Load Reduction #403-1 CWP was removed from service to repair the pressure gauge. | Ghent | Derate | Coal | 3 | 2013 | 9 | 1.6 | 0.20606 | 98.703 | 61.6894 | 62
GH3 | U1 | 46 | 4311 | 2013-09-29 18:10 | 2013-09-29 21:42 | 0 | 528 | 479 | Steam Turbine Control System - hardware problems (including card failure) | Outage #6While running the Main Turbine Front Standard Oil Trip Test, the Main Tur | Ghent | Outage | Coal | 3 | 2013 | 9 | 3.5333 | 3.5333 | 1692.4667 | 479 | 479
GH3 | D1 | 47 | 4499 | 2013-09-30 00:30 | 2013-10-10 23:05 | 515 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #41Turbine performance. ID fan limit. | Ghent | Derate | Coal | 3 | 2013 | 9 | 262.5833 | 6.4651 | 3096.7925 | 11.7936 | 12
GH3 | D1 | 48 | 9650 | 2013-10-06 07:35 | 2013-10-06 08:30 | 398 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #42H2 SO4 excursion. | Ghent | Derate | Coal | 3 | 2013 | 10 | 0.91667 | 0.22569 | 108.1076 | 117.9356 | 118
GH3 | D1 | 49 | 9650 | 2013-10-06 08:30 | 2013-10-06 09:00 | 375 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #43H2 SO4 excursion. | Ghent | Derate | Coal | 3 | 2013 | 10 | 0.5 | 0.14489 | 69.4006 | 138.8011 | 139
GH3 | D1 | 50 | 9650 | 2013-10-06 15:20 | 2013-10-06 17:10 | 375 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #44H2 SO4 excursion. | Ghent | Derate | Coal | 3 | 2013 | 10 | 1.8333 | 0.53125 | 254.4688 | 138.8011 | 139
GH3 | D1 | 51 | 1455 | 2013-10-08 01:20 | 2013-10-10 23:05 | 189 | 528 | 479 | Induced draft fans | Load Reduction #453-2 ID fan inboard bearing wiped. | Ghent | Derate | Coal | 3 | 2013 | 10 | 69.75 | 44.7827 | 21450.8991 | 307.5398 | 308
GH3 | MO | 52 | 1455 | 2013-10-10 23:05 | 2013-10-12 18:50 | 0 | 528 | 479 | Induced draft fans | F920Outage #73-2 ID fan had wiped its fan bearings on 10/8/13. Removed the fan fr | Ghent | Maintenance | Coal | 3 | 2013 | 10 | 43.75 | 43.75 | 20956.25 | 479 | 479
GH3 | SF | 53 | 4311 | 2013-10-12 18:50 | 2013-10-12 22:47 | 0 | 528 | 479 | Steam Turbine Control System - hardware problems (including card failure) | Outage #8Unit 3 was starting up after the 3-2 ID fan OB bearing replacement and ba | Ghent | Outage | Coal | 3 | 2013 | 10 | 3.95 | 3.95 | 1892.05 | 479 | 479
GH3 | D1 | 54 | 4499 | 2013-10-13 06:57 | 2013-10-25 20:43 | 515 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #46Turbine performance due to copper deposits. | Ghent | Derate | Coal | 3 | 2013 | 10 | 301.7667 | 7.4299 | 3558.9035 | 11.7936 | 12
GH3 | D1 | 55 | 1455 | 2013-10-15 07:45 | 2013-10-25 20:43 | 505 | 528 | 479 | Induced draft fans | Load Reduction #473-2 ID fan amps are running high due to 3-1 fan running in manua | Ghent | Derate | Coal | 3 | 2013 | 10 | 252.9667 | 11.0194 | 5278.2836 | 20.8655 | 21
GH3 | PO | 56 | 1801 | 2013-10-25 20:43 | 2013-11-14 10:38 | 0 | 528 | 479 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Outage #9Removed the unit from service for its 2013 Planned Fall Outage. | Ghent | Other | Coal | 3 | 2013 | 10 | 469.9167 | 469.9167 | 225090.0833 | 479 | 479
GH3 | PE | 57 | 1455 | 2013-11-14 10:38 | 2013-11-15 12:24 | 0 | 528 | 479 | Induced draft fans | F920Outage #10The unit was firing to start up. Turbine differential was running t | Ghent | Other | Coal | 3 | 2013 | 11 | 25.7667 | 25.7667 | 12342.2333 | 479 | 479
GH3 | U1 | 58 | 4470 | 2013-11-15 13:31 | 2013-11-16 06:16 | 0 | 528 | 479 | Differential expansion | Outage #11The unit had come on line with Turbine HP differential running high. Di | Ghent | Outage | Coal | 3 | 2013 | 11 | 16.75 | 16.75 | 8023.25 | 479 | 479
GH3 | D1 | 59 | 1850 | 2013-11-16 15:45 | 2013-11-16 19:52 | 433 | 528 | 479 | Boiler water condition (not feedwater water quality) | Load Reduction #48During start up of the unit, silica became high. | Ghent | Derate | Coal | 3 | 2013 | 11 | 4.1167 | 0.74069 | 354.7896 | 86.1837 | 86
GH3 | D1 | 60 | 9650 | 2013-11-17 19:07 | 2013-11-17 21:04 | 200 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #49Unit was limited to 200 MWs to get H2 SO4 emissions under contro | Ghent | Derate | Coal | 3 | 2013 | 11 | 1.95 | 1.2114 | 580.2432 | 297.5606 | 298
GH3 | D1 | 65 | 9650 | 2013-11-18 10:17 | 2013-11-18 10:56 | 450 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #54U3 H2SO4 was above limit. Had to drop load to get it under cont | Ghent | Derate | Coal | 3 | 2013 | 11 | 0.65 | 0.096023 | 45.9949 | 70.7614 | 71
GH3 | D1 | 61 | 9650 | 2013-11-18 13:10 | 2013-11-18 14:07 | 500 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #50Unit was limited to 500 MWs to get H2SO4 emissions under control | Ghent | Derate | Coal | 3 | 2013 | 11 | 0.95 | 0.050379 | 24.1314 | 25.4015 | 25
GH3 | D1 | 62 | 9650 | 2013-11-18 14:49 | 2013-11-19 09:00 | 515 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #51Unit was limited to 515 MWs to get H2SO4 emissions under control | Ghent | Derate | Coal | 3 | 2013 | 11 | 18.1833 | 0.4477 | 214.4462 | 11.7936 | 12
GH3 | D1 | 63 | 9650 | 2013-11-19 17:00 | 2013-11-20 06:23 | 515 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #52H2SO4 within limit. | Ghent | Derate | Coal | 3 | 2013 | 11 | 13.3833 | 0.32951 | 157.8372 | 11.7936 | 12
GH3 | PD | 64 | 1455 | 2013-11-21 09:14 | 2013-11-21 22:45 | 180 | 528 | 479 | Induced draft fans | F920Load Reduction #533-1 ID fan off to replace the IB motor bearing. | Ghent | Derate | Coal | 3 | 2013 | 11 | 13.5167 | 8.9087 | 4267.2731 | 315.7045 | 316
GH3 | D1 | 66 | 9650 | 2013-11-23 21:39 | 2013-11-24 01:04 | 510 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #55U3 H2SO4 was above limit. Had to drop load to get it under cont | Ghent | Derate | Coal | 3 | 2013 | 11 | 3.4167 | 0.11648 | 55.7926 | 16.3295 | 16
GH3 | D1 | 67 | 9650 | 2013-11-24 07:44 | 2013-11-24 08:24 | 510 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #56U3 H2SO4 was above limit. Had to drop load to get it under cont | Ghent | Derate | Coal | 3 | 2013 | 11 | 0.66667 | 0.022727 | 10.8864 | 16.3295 | 16
GH3 | U1 | 69 | 1455 | 2013-11-27 12:01 | 2013-11-27 14:08 | 0 | 528 | 479 | Induced draft fans | F920Outage #123-1 ID fan OB fan bearing metal temperature was rising. Tripped the | Ghent | Outage | Coal | 3 | 2013 | 11 | 2.1167 | 2.1167 | 1013.8833 | 479 | 479
GH3 | D1 | 68 | 1455 | 2013-11-27 16:55 | 2013-11-28 13:56 | 205 | 528 | 479 | Induced draft fans | Load Reduction #573-1 ID fan out of service due to OB ban bearing issues. | Ghent | Derate | Coal | 3 | 2013 | 11 | 21.0167 | 12.8568 | 6158.4008 | 293.0246 | 293
GH3 | MO | 70 | 1455 | 2013-11-28 13:56 | 2013-11-30 10:17 | 0 | 528 | 479 | Induced draft fans | F920Outage #13The unit had been running without the 3-1 ID fan due to a failed OB | Ghent | Maintenance | Coal | 3 | 2013 | 11 | 44.35 | 44.35 | 21243.65 | 479 | 479
GH3 | U1 | 71 | 4261 | 2013-12-09 00:53 | 2013-12-09 03:47 | 0 | 528 | 479 | Control valves | Outage #14During weekly Control Valve test, the #1 Control Valve would not open ba | Ghent | Outage | Coal | 3 | 2013 | 12 | 2.9 | 2.9 | 1389.1 | 479 | 479
GH3 | U3 | 72 | 3110 | 2013-12-14 01:29 | 2013-12-15 07:07 | 0 | 528 | 479 | Condenser tube leaks | Outage #15Unit 3 had been running with a suspected Condenser tube leak. Scheduled | Ghent | Outage | Coal | 3 | 2013 | 12 | 29.6333 | 29.6333 | 14194.3667 | 479 | 479
GH3 | D1 | 73 | 1850 | 2013-12-15 16:32 | 2013-12-15 18:26 | 482 | 528 | 479 | Boiler water condition (not feedwater water quality) | Load Reduction #58Following start up of Unit 3, silica was high. Reduced load to | Ghent | Derate | Coal | 3 | 2013 | 12 | 1.9 | 0.16553 | 79.289 | 41.7311 | 42
GH3 | D1 | 74 | 250 | 2013-12-18 00:15 | 2013-12-18 01:10 | 430 | 528 | 479 | Pulverizer feeders | Load Reduction #593-4 Feeder belt was cut by metal. Removed the feeder from servi | Ghent | Derate | Coal | 3 | 2013 | 12 | 0.91667 | 0.17014 | 81.4965 | 88.9053 | 89
GH3 | D1 | 75 | 9650 | 2013-12-20 03:25 | 2013-12-20 14:00 | 305 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #60Keeping H2S04 within limit. | Ghent | Derate | Coal | 3 | 2013 | 12 | 10.5833 | 4.4699 | 2141.0604 | 202.3049 | 202
GH3 | U1 | 1 | 1455 | 2014-01-07 21:20 | 2014-01-08 06:15 | 0 | 528 | 479 | Induced draft fans | F850Outage #13-2 ID fan tripped on high vibration on OB fan bearing. This caused | Ghent | Outage | Coal | 3 | 2014 | 1 | 8.9167 | 8.9167 | 4271.0833 | 479 | 479
GH3 | D1 | 2 | 1455 | 2014-01-08 06:15 | 2014-01-10 11:31 | 200 | 528 | 479 | Induced draft fans | Load Reduction #1Unit running with 3-2 ID fan out of service. | Ghent | Derate | Coal | 3 | 2014 | 1 | 53.2667 | 33.0899 | 15850.0616 | 297.5606 | 298
GH3 | MO | 3 | 1455 | 2014-01-10 11:31 | 2014-01-13 03:25 | 0 | 528 | 479 | Induced draft fans | F920Outage #2Unit 3 had been derated to minimum load due to 3-2 ID Fan tripping on | Ghent | Maintenance | Coal | 3 | 2014 | 1 | 63.9 | 63.9 | 30608.1 | 479 | 479
GH3 | SF | 4 | 4609 | 2014-01-13 03:25 | 2014-01-13 06:19 | 0 | 528 | 479 | Other exciter problems | Outage #3During the previous event, the unit had been rolled up to synchronise spe | Ghent | Outage | Coal | 3 | 2014 | 1 | 2.9 | 2.9 | 1389.1 | 479 | 479
GH3 | D1 | 5 | 1455 | 2014-01-21 23:18 | 2014-01-22 01:31 | 520 | 528 | 479 | Induced draft fans | Load Reduction #2Load was reduced when 3-1 ID Fan blade position feedback failed, | Ghent | Derate | Coal | 3 | 2014 | 1 | 2.2167 | 0.033586 | 16.0876 | 7.2576 | 7
GH3 | D1 | 6 | 9290 | 2014-01-24 23:19 | 2014-01-25 03:33 | 480 | 528 | 479 | Other fuel quality problems | Load Reduction #3Derate was reported as a coal quality issue. Actually, we were b | Ghent | Derate | Coal | 3 | 2014 | 1 | 4.2333 | 0.38485 | 184.3424 | 43.5455 | 44
GH3 | U1 | 7 | 1040 | 2014-01-25 03:33 | 2014-01-26 19:21 | 0 | 528 | 479 | First superheater B | Outage #4Unit 3 was taken off line after developing a boiler tube leak in the Prim | Ghent | Outage | Coal | 3 | 2014 | 1 | 39.8 | 39.8 | 19064.2 | 479 | 479
GH3 | D1 | 8 | 1455 | 2014-01-26 19:21 | 2014-01-26 20:47 | 200 | 528 | 479 | Induced draft fans | Load Reduction #4Unit 3 was derated during startup when 3-2 ID Fan OB bearing fail | Ghent | Derate | Coal | 3 | 2014 | 1 | 1.4333 | 0.8904 | 426.5035 | 297.5606 | 298
GH3 | MO | 9 | 1455 | 2014-01-26 20:47 | 2014-01-27 22:30 | 0 | 528 | 479 | Induced draft fans | F920Outage #5Unit 3 was taken off line to replace 3-2 ID Fan OB bearing. | Ghent | Maintenance | Coal | 3 | 2014 | 1 | 25.7167 | 25.7167 | 12318.2833 | 479 | 479
GH3 | D1 | 10 | 1455 | 2014-01-28 11:27 | 2014-01-30 14:13 | 500 | 528 | 479 | Induced draft fans | Load Reduction #53-2 ID Fan IB bearing running 9+ mils vibration. OB fan bearing | Ghent | Derate | Coal | 3 | 2014 | 1 | 50.7667 | 2.6922 | 1289.5503 | 25.4015 | 25
GH3 | MO | 11 | 1455 | 2014-01-30 14:13 | 2014-02-01 09:26 | 0 | 528 | 479 | Induced draft fans | F920Outage #6Unit 3 has been running with 3-2 ID Fan OB Fan bearing having periodi | Ghent | Maintenance | Coal | 3 | 2014 | 1 | 43.2167 | 43.2167 | 20700.7833 | 479 | 479
GH3 | D1 | 12 | 9650 | 2014-02-02 20:10 | 2014-02-02 20:45 | 400 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #63-2B SO3 injection blower pressure sensing line came off causing | Ghent | Derate | Coal | 3 | 2014 | 2 | 0.58333 | 0.14141 | 67.7374 | 116.1212 | 116
GH3 | D1 | 13 | 9650 | 2014-02-05 14:10 | 2014-02-05 15:00 | 350 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #7Reduced load to keep H2SO4 within limit. | Ghent | Derate | Coal | 3 | 2014 | 2 | 0.83333 | 0.28093 | 134.5676 | 161.4811 | 161
GH3 | D1 | 14 | 9650 | 2014-02-05 15:00 | 2014-02-05 19:50 | 208 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #8Reduced load to keep H2SO4 within limit. | Ghent | Derate | Coal | 3 | 2014 | 2 | 4.8333 | 2.9293 | 1403.1313 | 290.303 | 290
GH3 | D1 | 15 | 9650 | 2014-02-15 04:41 | 2014-02-15 07:07 | 400 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #9Reduced load to keep H2SO4 within limit. | Ghent | Derate | Coal | 3 | 2014 | 2 | 2.4333 | 0.5899 | 282.5616 | 116.1212 | 116
GH3 | D1 | 16 | 9650 | 2014-02-15 11:22 | 2014-02-15 14:52 | 215 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #10Reduced load to keep H2SO4 within limit. | Ghent | Derate | Coal | 3 | 2014 | 2 | 3.5 | 2.0748 | 993.8343 | 283.9527 | 284
GH3 | PD | 17 | 9510 | 2014-02-15 22:00 | 2014-02-16 13:04 | 200 | 528 | 479 | Plant modifications strictly for compliance with new or changed regulatory requirements (scrubbers | Load Reduction #11KBR electrical tie-in for Bag House and ID fan. | Ghent | Derate | Coal | 3 | 2014 | 2 | 15.0667 | 9.3596 | 4483.2465 | 297.5606 | 298
GH3 | D1 | 18 | 1455 | 2014-02-17 10:50 | 2014-02-17 12:00 | 470 | 528 | 479 | Induced draft fans | Load Reduction #12ID Fans out the top. Reduced load to swap mills. | Ghent | Derate | Coal | 3 | 2014 | 2 | 1.1667 | 0.12816 | 61.387 | 52.6174 | 53
GH3 | D1 | 19 | 9650 | 2014-02-17 13:35 | 2014-02-18 10:26 | 492 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #13H2SO4 out of limit for probe pluggage. | Ghent | Derate | Coal | 3 | 2014 | 2 | 20.85 | 1.4216 | 680.942 | 32.6591 | 33
GH3 | D1 | 20 | 1400 | 2014-02-18 10:26 | 2014-02-25 04:00 | 504 | 528 | 479 | Forced draft fans | Load Reduction #14FD fans were topping out. | Ghent | Derate | Coal | 3 | 2014 | 2 | 161.5667 | 7.3439 | 3517.747 | 21.7727 | 22
GH3 | D1 | 21 | 9650 | 2014-02-20 12:30 | 2014-02-20 13:05 | 390 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #15Reduced load to keep H2SO4 within limit. | Ghent | Derate | Coal | 3 | 2014 | 2 | 0.58333 | 0.15246 | 73.0294 | 125.1932 | 125
GH3 | D1 | 22 | 250 | 2014-02-20 13:50 | 2014-02-20 16:25 | 400 | 528 | 479 | Pulverizer feeders | Load Reductions #163-3 Feeder controls. | Ghent | Derate | Coal | 3 | 2014 | 2 | 2.5833 | 0.62626 | 299.9798 | 116.1212 | 116
GH3 | PD | 23 | 9650 | 2014-02-28 22:30 | 2014-03-01 03:08 | 230 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #17Keeping H2SO4 within limit. Working on sorbent blower. | Ghent | Derate | Coal | 3 | 2014 | 2 | 4.6333 | 2.615 | 1252.5971 | 270.3447 | 270
GH3 | D1 | 24 | 9650 | 2014-03-02 18:15 | 2014-03-02 21:00 | 350 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #18Keeping H2SO4 within limit. Low level on Silo feeding outlet i | Ghent | Derate | Coal | 3 | 2014 | 3 | 2.75 | 0.92708 | 444.0729 | 161.4811 | 161
GH3 | D1 | 25 | 9650 | 2014-03-05 07:08 | 2014-03-05 08:03 | 380 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #19H2SO4 running high due to outlet injection probe pluggage. Redu | Ghent | Derate | Coal | 3 | 2014 | 3 | 0.91667 | 0.25694 | 123.0764 | 134.2652 | 134
GH3 | D1 | 26 | 9650 | 2014-03-05 17:28 | 2014-03-06 01:30 | 450 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #20Keeping H2S04 within limit. Outlet injection lines plugged. | Ghent | Derate | Coal | 3 | 2014 | 3 | 8.0333 | 1.1867 | 568.4496 | 70.7614 | 71
GH3 | D1 | 27 | 9650 | 2014-03-07 04:20 | 2014-03-07 06:05 | 400 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #21Keeping H2SO4 within limit. 3-2B Blow through valve drive chain | Ghent | Derate | Coal | 3 | 2014 | 3 | 1.75 | 0.42424 | 203.2121 | 116.1212 | 116
GH3 | D1 | 28 | 9650 | 2014-03-07 07:30 | 2014-03-07 08:00 | 500 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #22Keeping H2S04 within limit. 3-2 Blow through drive chain valve | Ghent | Derate | Coal | 3 | 2014 | 3 | 0.5 | 0.026515 | 12.7008 | 25.4015 | 25
GH3 | D1 | 29 | 1400 | 2014-03-07 19:29 | 2014-03-07 23:10 | 517 | 528 | 479 | Forced draft fans | Load Reduction #23FD fans out the top. | Ghent | Derate | Coal | 3 | 2014 | 3 | 3.6833 | 0.076736 | 36.7566 | 9.9792 | 10
GH3 | D1 | 30 | 1400 | 2014-03-08 19:35 | 2014-03-09 05:28 | 518 | 528 | 479 | Forced draft fans | Load Reduction #24FD Fans out the top. | Ghent | Derate | Coal | 3 | 2014 | 3 | 9.8833 | 0.18718 | 89.6613 | 9.072 | 9
GH3 | D1 | 31 | 280 | 2014-03-13 22:40 | 2014-03-13 23:45 | 430 | 528 | 479 | Pulverizer fires | Load Reduction #253-5 Mill fire. | Ghent | Derate | Coal | 3 | 2014 | 3 | 1.0833 | 0.20107 | 96.3141 | 88.9053 | 89
GH3 | D1 | 32 | 9650 | 2014-03-14 03:36 | 2014-03-14 05:18 | 515 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #26Keeping H2SO4 within limits, ID Fan Injection Outlets plugged. | Ghent | Derate | Coal | 3 | 2014 | 3 | 1.7 | 0.041856 | 20.0491 | 11.7936 | 12
GH3 | D1 | 33 | 1400 | 2014-03-14 05:18 | 2014-03-14 09:57 | 525 | 528 | 479 | Forced draft fans | Load Reduction #27FD Fan Limit, 3-1 FD Fan Inlet Vane needs attention. | Ghent | Derate | Coal | 3 | 2014 | 3 | 4.65 | 0.02642 | 12.6554 | 2.7216 | 3
GH3 | D1 | 34 | 9650 | 2014-03-14 09:57 | 2014-03-14 11:08 | 490 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #28Keeping H2SO3 within limit. ID Fan Outlet Injection plugged. | Ghent | Derate | Coal | 3 | 2014 | 3 | 1.1833 | 0.085164 | 40.7936 | 34.4735 | 34
GH3 | D1 | 35 | 1400 | 2014-03-14 11:08 | 2014-03-14 12:26 | 520 | 528 | 479 | Forced draft fans | Load Reduction #29FD Fan Limit, 3-1 ID Fan Vane needs attention. | Ghent | Derate | Coal | 3 | 2014 | 3 | 1.3 | 0.019697 | 9.4348 | 7.2576 | 7
GH3 | D1 | 36 | 9650 | 2014-03-14 12:26 | 2014-03-15 05:15 | 454 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #30Keeping H2SO4 within limit. ID Fan Outlet Injection plugged. | Ghent | Derate | Coal | 3 | 2014 | 3 | 16.8167 | 2.3569 | 1128.9461 | 67.1326 | 67
GH3 | D1 | 37 | 9650 | 2014-03-15 06:24 | 2014-03-15 10:54 | 490 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #31Keeping H2SO4 within limit. ID Faan Outlet Injection plugged. | Ghent | Derate | Coal | 3 | 2014 | 3 | 4.5 | 0.32386 | 155.1307 | 34.4735 | 34
GH3 | D1 | 38 | 9650 | 2014-03-17 09:30 | 2014-03-17 11:03 | 400 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #32Keeping H2So4 within limit. 3-2B Drop Through Rotary valve driv | Ghent | Derate | Coal | 3 | 2014 | 3 | 1.55 | 0.37576 | 179.9879 | 116.1212 | 116
GH3 | D1 | 39 | 1400 | 2014-03-19 06:00 | 2014-03-20 07:00 | 510 | 528 | 479 | Forced draft fans | Load Reduction #33FD Fan limit, 3-1 FD Fan Inlet Vane needs attention. | Ghent | Derate | Coal | 3 | 2014 | 3 | 25 | 0.85227 | 408.2386 | 16.3295 | 16
GH3 | D1 | 40 | 280 | 2014-03-25 08:39 | 2014-03-25 09:56 | 465 | 528 | 479 | Pulverizer fires | Load Reduction #343-5 Mill fire in top of the mill. | Ghent | Derate | Coal | 3 | 2014 | 3 | 1.2833 | 0.15312 | 73.3469 | 57.1534 | 57
GH3 | D1 | 41 | 9650 | 2014-03-25 11:38 | 2014-03-25 12:35 | 450 | 528 | 479 | Other stack or exhaust emissions (fossil) | Load Reduction #35Reduced load to keep H2SO4 within limit. Inlet probes were plug | Ghent | Derate | Coal | 3 | 2014 | 3 | 0.95 | 0.14034 | 67.2233 | 70.7614 | 71
GH3 | PD | 42 | 855 | 2014-03-26 22:00 | 2014-03-27 00:36 | 485 | 528 | 479 | Drum relief/safety valves (Single drum only) | Load Reduction #36Precision to set drum safeties. | Ghent | Derate | Coal | 3 | 2014 | 3 | 2.6 | 0.21174 | 101.4246 | 39.0095 | 39
GH3 | PO | 43 | 1800 | 2014-03-28 22:07 | 2014-05-12 00:01 | 0 | 528 | 479 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | F590Outage #7Unit 3 was scheduled for a Planned Spring Outage. Removed the unit f | Ghent | Other | Coal | 3 | 2014 | 3 | 1057.9 | 1057.9 | 506734.1 | 479 | 479
GH3 | PE | 44 | 1800 | 2014-05-12 00:01 | 2014-05-17 16:17 | 0 | 528 | 479 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | F590Outage #8Planned outage work was not complete by the end of the Planned Outage | Ghent | Other | Coal | 3 | 2014 | 5 | 136.2667 | 136.2667 | 65271.7333 | 479 | 479
GH3 | SF | 45 | 4700 | 2014-05-17 16:17 | 2014-05-17 20:46 | 0 | 528 | 479 | Generator voltage control | Outage #9While trying to synchronize the unit after the Sping Outage the Generator | Ghent | Outage | Coal | 3 | 2014 | 5 | 4.4833 | 4.4833 | 2147.5167 | 479 | 479
GH3 | D1 | 46 | 1850 | 2014-05-18 14:30 | 2014-05-19 01:50 | 290 | 528 | 479 | Boiler water condition (not feedwater water quality) | Load Reduction #37Boiler silica was high following startup of Unit 3 following the | Ghent | Derate | Coal | 3 | 2014 | 5 | 11.3333 | 5.1086 | 2447.0126 | 215.9129 | 216
GH3 | D1 | 47 | 250 | 2014-05-19 05:00 | 2014-05-19 05:58 | 325 | 528 | 479 | Pulverizer feeders | Load Reduction #38U3 Coal feeders tripping, problems with motion monitors. Instru | Ghent | Derate | Coal | 3 | 2014 | 5 | 0.96667 | 0.37165 | 178.0223 | 184.161 | 184
GH3 | PD | 48 | 1470 | 2014-05-19 06:38 | 2014-05-20 13:45 | 459 | 528 | 479 | Induced draft fan motors and drives | Load Reduction #39Unit 3 started up with 3-1A ID fan unavailable due to motor vibr | Ghent | Derate | Coal | 3 | 2014 | 5 | 31.1167 | 4.0664 | 1947.7973 | 62.5966 | 63
GH3 | D1 | 49 | 3974 | 2014-05-20 13:45 | 2014-05-20 15:09 | 275 | 528 | 479 | DCS - logic problems | Load Reduction #403-2A ID fan tripped when inlet damper limit switch indicated clo | Ghent | Derate | Coal | 3 | 2014 | 5 | 1.4 | 0.67083 | 321.3292 | 229.5208 | 230
GH3 | PD | 50 | 1455 | 2014-05-20 15:09 | 2014-05-21 21:10 | 488 | 528 | 479 | Induced draft fans | Load Reduction #41Unit 3 started up with 3-1A ID fan unavailable due to motor vibr | Ghent | Derate | Coal | 3 | 2014 | 5 | 30.0167 | 2.274 | 1089.2412 | 36.2879 | 36
GH3 | D1 | 51 | 3410 | 2014-05-25 13:27 | 2014-05-25 17:05 | 300 | 528 | 479 | Feedwater pump | Load Reduction #423-1 BFP would not reset, latch mechanism would not stay latched. | Ghent | Derate | Coal | 3 | 2014 | 5 | 3.6333 | 1.5689 | 751.522 | 206.8409 | 207
GH3 | D1 | 52 | 1470 | 2014-05-25 20:47 | 2014-05-26 16:11 | 490 | 528 | 479 | Induced draft fan motors and drives | Load Reduction #433-2 A ID fan VFD cell failed causing fan to trip. | Ghent | Derate | Coal | 3 | 2014 | 5 | 19.4 | 1.3962 | 668.7856 | 34.4735 | 34
GH3 | D1 | 54 | 1400 | 2014-06-05 09:05 | 2014-06-05 10:00 | 502 | 528 | 479 | Forced draft fans | Load Reduction #443-1 FD fan shut off damper drive linkage rod broke. | Ghent | Derate | Coal | 3 | 2014 | 6 | 0.91667 | 0.045139 | 21.6215 | 23.5871 | 24
GH3 | MO | 53 | 775 | 2014-06-09 22:32 | 2014-06-14 04:32 | 0 | 528 | 479 | Economizer piping | F610Outage #10Economizer section had been added during Spring Planned outage to re | Ghent | Maintenance | Coal | 3 | 2014 | 6 | 102 | 102 | 48858 | 479 | 479
GH3 | D1 | 55 | 385 | 2014-06-14 15:20 | 2014-06-14 16:44 | 320 | 528 | 479 | Igniters | Load Reduction #45Ignitor fuel oil pressure regulator controller started to fail. | Ghent | Derate | Coal | 3 | 2014 | 6 | 1.4 | 0.55152 | 264.1758 | 188.697 | 189
GH3 | D1 | 56 | 385 | 2014-06-14 18:27 | 2014-06-14 19:31 | 420 | 528 | 479 | Igniters | Load Reduction #46Ignitor fuel oil pressure regulator controller failed. Unable t | Ghent | Derate | Coal | 3 | 2014 | 6 | 1.0667 | 0.21818 | 104.5091 | 97.9773 | 98
GH3 | D1 | 57 | 775 | 2014-06-17 00:05 | 2014-06-17 00:16 | 210 | 528 | 479 | Economizer piping | Load Reduction #47Dropped load to check stroke of the new economizer valve that wa | Ghent | Derate | Coal | 3 | 2014 | 6 | 0.18333 | 0.11042 | 52.8896 | 288.4886 | 288
GH3 | D1 | 58 | 530 | 2014-06-25 20:55 | 2014-06-25 22:21 | 525 | 528 | 479 | Other main steam system problems | Load Reduction #48Unable to make full load because of low RH and SH steam temperat | Ghent | Derate | Coal | 3 | 2014 | 6 | 1.4333 | 0.0081439 | 3.9009 | 2.7216 | 3
GH3 | D1 | 59 | 8125 | 2014-06-26 23:40 | 2014-06-27 00:05 | 380 | 528 | 479 | Scrubber recycle (liquid) pumps | Load Reduction #49Unable to make full load because 3-3 and 3-5 Recycle Pumps tripp | Ghent | Derate | Coal | 3 | 2014 | 6 | 0.41667 | 0.11679 | 55.9438 | 134.2652 | 134
GH3 | PD | 60 | 1455 | 2014-06-28 22:00 | 2014-06-28 23:30 | 490 | 528 | 479 | Induced draft fans | Load Reduction #503-2A ID Fan cooling system leaking. | Ghent | Derate | Coal | 3 | 2014 | 6 | 1.5 | 0.10795 | 51.7102 | 34.4735 | 34
GH3 | PD | 61 | 1455 | 2014-06-28 23:30 | 2014-06-29 04:28 | 450 | 528 | 479 | Induced draft fans | Load Reduction #513-2A ID Fan cooling system leaks. | Ghent | Derate | Coal | 3 | 2014 | 6 | 4.9667 | 0.73371 | 351.4481 | 70.7614 | 71
GH3 | D1 | 62 | 3412 | 2014-07-07 13:23 | 2014-07-07 14:53 | 300 | 528 | 479 | Feedwater pump drive - steam turbine | Load Reduction #523-2 BFPT tripped. | Ghent | Derate | Coal | 3 | 2014 | 7 | 1.5 | 0.64773 | 310.2614 | 206.8409 | 207
GH3 | D1 | 63 | 3440 | 2014-07-11 00:11 | 2014-07-13 04:10 | 511 | 528 | 479 | High pressure heater tube leaks | Load Reduction #53G High Pressure heater tube leak. | Ghent | Derate | Coal | 3 | 2014 | 7 | 51.9833 | 1.6737 | 801.7051 | 15.4223 | 15
GH3 | D1 | 64 | 1455 | 2014-07-11 12:44 | 2014-07-11 13:04 | 480 | 528 | 479 | Induced draft fans | Load Reduction #543-1B ID Fan tripped on loss of lube oil reservoir level indicati | Ghent | Derate | Coal | 3 | 2014 | 7 | 0.33333 | 0.030303 | 14.5152 | 43.5455 | 44
GH3 | D1 | 65 | 1455 | 2014-07-11 13:17 | 2014-07-11 13:54 | 480 | 528 | 479 | Induced draft fans | Load Reduction #553-1B ID Fan discharge damper hung up while at about 5% open. | Ghent | Derate | Coal | 3 | 2014 | 7 | 0.61667 | 0.056061 | 26.853 | 43.5455 | 44
GH3 | D4 | 66 | 1455 | 2014-07-11 22:00 | 2014-07-12 04:18 | 473 | 528 | 479 | Induced draft fans | Load Reduction #563-1 ID Fan out of service for VFD coolant system repairs. | Ghent | Derate | Coal | 3 | 2014 | 7 | 6.3 | 0.65625 | 314.3438 | 49.8958 | 50
GH3 | D4 | 67 | 1455 | 2014-07-12 22:00 | 2014-07-12 23:30 | 450 | 528 | 479 | Induced draft fans | Load Reduction #573-1 ID Fan OOS for VFD coolant system repairs. | Ghent | Derate | Coal | 3 | 2014 | 7 | 1.5 | 0.22159 | 106.142 | 70.7614 | 71
GH3 | D1 | 68 | 3441 | 2014-07-13 17:30 | 2014-07-15 04:05 | 511 | 528 | 479 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | Load Reduction #58G HP heater normal drain regulator failed. | Ghent | Derate | Coal | 3 | 2014 | 7 | 34.5833 | 1.1135 | 533.3562 | 15.4223 | 15
GH3 | D4 | 69 | 1455 | 2014-07-13 21:00 | 2014-07-14 05:41 | 473 | 528 | 479 | Induced draft fans | Load Reduction #593-1A ID Fan OOS for VFD coolant system repairs. | Ghent | Derate | Coal | 3 | 2014 | 7 | 8.6833 | 0.90451 | 433.2622 | 49.8958 | 50
GH3 | PD | 70 | 1470 | 2014-07-19 06:00 | 2014-07-19 16:10 | 450 | 528 | 479 | Induced draft fan motors and drives | Load Reduction #603-2A ID Fan OOS for VFD coolant system repairs and to check moto | Ghent | Derate | Coal | 3 | 2014 | 7 | 10.1667 | 1.5019 | 719.4072 | 70.7614 | 71
GH3 | D1 | 71 | 3410 | 2014-07-25 02:21 | 2014-07-25 03:06 | 300 | 528 | 479 | Feedwater pump | Load Reduction #613-2 BFPT tripped on high vibration when 3-4 mill loaded up and s | Ghent | Derate | Coal | 3 | 2014 | 7 | 0.75 | 0.32386 | 155.1307 | 206.8409 | 207
GH3 | PD | 72 | 3682 | 2014-07-29 05:00 | 2014-07-29 16:44 | 250 | 528 | 479 | Other voltage system conductors and buses | Load Reduction #62Unit 3 was limited due to North Bus outage to tie in for the new | Ghent | Derate | Coal | 3 | 2014 | 7 | 11.7333 | 6.1778 | 2959.1556 | 252.2008 | 252
GH3 | PD | 73 | 3441 | 2014-08-04 22:00 | 2014-08-05 05:19 | 511 | 528 | 479 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | Load Reduction #63Removed U3 HP Heater from service to replace 3F heater level con | Ghent | Derate | Coal | 3 | 2014 | 8 | 7.3167 | 0.23557 | 112.8402 | 15.4223 | 15
GH3 | PD | 74 | 1455 | 2014-08-08 22:00 | 2014-08-09 04:18 | 465 | 528 | 479 | Induced draft fans | Load Reduction #64Removed 3-2A ID fan from service to remove motor bearing hemp se | Ghent | Derate | Coal | 3 | 2014 | 8 | 6.3 | 0.7517 | 360.0665 | 57.1534 | 57
GH3 | D1 | 75 | 3410 | 2014-08-10 17:46 | 2014-08-10 19:20 | 285 | 528 | 479 | Feedwater pump | Load Reduction #653-2 BFPT tripped. No problem found. Will troubleshoot and chec | Ghent | Derate | Coal | 3 | 2014 | 8 | 1.5667 | 0.72102 | 345.3699 | 220.4489 | 220
GH3 | D1 | 76 | 1455 | 2014-08-11 08:07 | 2014-08-11 21:03 | 483 | 528 | 479 | Induced draft fans | Load Reduction #663-2A ID Fan tripped on high vibration and controls of remaining | Ghent | Derate | Coal | 3 | 2014 | 8 | 12.9333 | 1.1023 | 527.9886 | 40.8239 | 41
GH3 | D1 | 77 | 340 | 2014-08-21 17:40 | 2014-08-21 17:56 | 440 | 528 | 479 | Other pulverizer problems | Load Reduction #673-1 Mill tripped due to control card failure. | Ghent | Derate | Coal | 3 | 2014 | 8 | 0.26667 | 0.044444 | 21.2889 | 79.8333 | 80
GH3 | D1 | 78 | 4499 | 2014-08-29 14:13 | 2014-08-30 01:30 | 530 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #68Turbine copper deposition and low steam temperatures after desla | Ghent | Derate | Coal | 3 | 2014 | 8 | 11.2833 | -0.04274 | -20.4724 | 0 | 0
GH3 | D1 | 79 | 4499 | 2014-08-30 06:36 | 2014-08-31 11:10 | 522 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #69Turbine copper deposition and low steam temperatures after desla | Ghent | Derate | Coal | 3 | 2014 | 8 | 28.5667 | 0.32462 | 155.4936 | 5.4432 | 5
GH3 | PD | 80 | 1455 | 2014-09-05 22:00 | 2014-09-06 19:36 | 470 | 528 | 479 | Induced draft fans | Load Reduction #70Took 3-2A IDF out of service to address vibration issue. Change | Ghent | Derate | Coal | 3 | 2014 | 9 | 21.6 | 2.3727 | 1136.5364 | 52.6174 | 53
GH3 | D1 | 81 | 9210 | 2014-09-17 10:33 | 2014-09-17 23:53 | 480 | 528 | 479 | Low grindability | Load Reduction #71The unit was derated due to mill grinding and air flow issues du | Ghent | Derate | Coal | 3 | 2014 | 9 | 13.3333 | 1.2121 | 580.6061 | 43.5455 | 44
GH3 | D1 | 82 | 9210 | 2014-09-18 03:22 | 2014-09-18 04:25 | 490 | 528 | 479 | Low grindability | Load Reduction #72The unit was derated due to mill grinding and air flow issues du | Ghent | Derate | Coal | 3 | 2014 | 9 | 1.05 | 0.075568 | 36.1972 | 34.4735 | 34
GH3 | D1 | 83 | 1470 | 2014-09-24 09:51 | 2014-09-24 10:52 | 450 | 528 | 479 | Induced draft fan motors and drives | Load Reduction #733-2B ID Fan VFD tripped. | Ghent | Derate | Coal | 3 | 2014 | 9 | 1.0167 | 0.15019 | 71.9407 | 70.7614 | 71
GH3 | U1 | 84 | 3408 | 2014-09-25 13:42 | 2014-09-25 14:26 | 0 | 528 | 479 | Feedwater pump drive - local controls | Outage #11The unit tripped off line due to low drum level. This was caused by 3-2 | Ghent | Outage | Coal | 3 | 2014 | 9 | 0.73333 | 0.73333 | 351.2667 | 479 | 479
GH3 | MO | 85 | 1493 | 2014-10-03 16:43 | 2014-10-07 05:04 | 0 | 528 | 479 | Air heater fouling (regenerative) | F540Outage #12Unit 3 was running with leaks in the 3-2 Air Preheating Coil. Remov | Ghent | Maintenance | Coal | 3 | 2014 | 10 | 84.35 | 84.35 | 40403.65 | 479 | 479
GH3 | D1 | 86 | 3408 | 2014-10-08 09:00 | 2014-10-08 09:50 | 300 | 528 | 479 | Feedwater pump drive - local controls | Load Reduction #743-2 BFPT tripped on vibration when taking 3-5 Mill out of servic | Ghent | Derate | Coal | 3 | 2014 | 10 | 0.83333 | 0.35985 | 172.3674 | 206.8409 | 207
GH3 | D1 | 87 | 3408 | 2014-10-09 05:14 | 2014-10-09 05:34 | 300 | 528 | 479 | Feedwater pump drive - local controls | Load Reduction #753-2 BFPT tripped on vibration when 3-4 Mill experienced grinding | Ghent | Derate | Coal | 3 | 2014 | 10 | 0.33333 | 0.14394 | 68.947 | 206.8409 | 207
GH3 | D1 | 88 | 3408 | 2014-10-14 13:50 | 2014-10-14 14:15 | 260 | 528 | 479 | Feedwater pump drive - local controls | Load Reduction #763-1 BFPT tripped on loss of vacuum. Vacuum sensing line at pres | Ghent | Derate | Coal | 3 | 2014 | 10 | 0.41667 | 0.21149 | 101.3037 | 243.1288 | 243
GH3 | D1 | 89 | 3408 | 2014-10-14 14:15 | 2014-10-14 15:28 | 325 | 528 | 479 | Feedwater pump drive - local controls | Load Reduction #773-1 BFPT tripped on loss of vacuum. Vacuum sensing line at pres | Ghent | Derate | Coal | 3 | 2014 | 10 | 1.2167 | 0.46777 | 224.0625 | 184.161 | 184
GH3 | MO | 90 | 1080 | 2014-11-27 12:49 | 2014-11-28 13:15 | 0 | 528 | 479 | Economizer B | F540Outage #13Unit 3 had been running with a leak in the backpass of the boiler, b | Ghent | Maintenance | Coal | 3 | 2014 | 11 | 24.4333 | 24.4333 | 11703.5667 | 479 | 479
GH3 | D1 | 91 | 380 | 2014-12-23 09:55 | 2014-12-23 10:03 | 435 | 528 | 479 | Light-off (igniter) systems (including fuel supply) | Load Reduction #783-2 Mill tripped on loss of flame. Unit ran back (2 feeders off | Ghent | Derate | Coal | 3 | 2014 | 12 | 0.13333 | 0.023485 | 11.2492 | 84.3693 | 84
GH3 | D1 | 1 | 1455 | 2015-01-08 04:26 | 2015-01-08 07:50 | 210 | 528 | 479 | Induced draft fans | Load Reduction #13-2A and B ID fans tripped on IDF inlet pressure (2 out of 3 PT's | Ghent | Derate | Coal | 3 | 2015 | 1 | 3.4 | 2.0477 | 980.8614 | 288.4886 | 288
GH3 | D1 | 2 | 8325 | 2015-01-09 18:31 | 2015-01-10 00:06 | 200 | 528 | 479 | Ash disposal problems | Load Reduction #2U3 Wet ash line froze at ABS/ATB1 valve station. | Ghent | Derate | Coal | 3 | 2015 | 1 | 5.5833 | 3.4684 | 1661.3801 | 297.5606 | 298
GH3 | MO | 3 | 1488 | 2015-01-17 01:08 | 2015-01-20 04:45 | 0 | 528 | 479 | Air heater (regenerative) | Outage #1Unit 3 was running with leaking on the Air Heater seals that was causing | Ghent | Maintenance | Coal | 3 | 2015 | 1 | 75.6167 | 75.6167 | 36220.3833 | 479 | 479
GH3 | SF | 4 | 3613 | 2015-01-20 04:45 | 2015-01-20 11:29 | 0 | 528 | 479 | Switchyard system protection devices - (not outside management control) | F060Outage #2Unit 3 was removed from service to repair air heater seals. When the | Ghent | Outage | Coal | 3 | 2015 | 1 | 6.7333 | 6.7333 | 3225.2667 | 479 | 479
GH3 | D1 | 5 | 1500 | 2015-02-05 03:48 | 2015-02-05 05:40 | 125 | 528 | 479 | Air heater soot blowers | Load Reduction #3AH Sootblower steam supply line ruptured. Dropped boiler pressur | Ghent | Derate | Coal | 3 | 2015 | 2 | 1.8667 | 1.4247 | 682.454 | 365.6004 | 366
GH3 | D1 | 6 | 1455 | 2015-02-05 06:35 | 2015-02-05 11:46 | 475 | 528 | 479 | Induced draft fans | Load Reduction #43-1A ID fan was removed from service while dropping boiler pressu | Ghent | Derate | Coal | 3 | 2015 | 2 | 5.1833 | 0.5203 | 249.2221 | 48.0814 | 48
GH3 | D1 | 7 | 3410 | 2015-02-21 00:45 | 2015-02-21 01:25 | 424 | 528 | 479 | Feedwater pump | Load Reduction #53-2 BFPT servo valve failed. | Ghent | Derate | Coal | 3 | 2015 | 2 | 0.66667 | 0.13131 | 62.899 | 94.3485 | 94
GH3 | D1 | 8 | 3410 | 2015-02-21 01:25 | 2015-02-21 03:32 | 300 | 528 | 479 | Feedwater pump | Load Reduction #63-2 BFPT servo failed. | Ghent | Derate | Coal | 3 | 2015 | 2 | 2.1167 | 0.91402 | 437.8133 | 206.8409 | 207
GH3 | D1 | 9 | 250 | 2015-03-16 09:42 | 2015-03-16 10:05 | 390 | 528 | 479 | Pulverizer feeders | Load Reduction #73-3 Feeder tripped; plugged outlet due to wet coal. | Ghent | Derate | Coal | 3 | 2015 | 3 | 0.38333 | 0.10019 | 47.9907 | 125.1932 | 125
GH3 | PD | 10 | 1100 | 2015-03-21 | 2015-03-21 03:54 | 220 | 528 | 479 | Waterwall (Furnace wall) B | Load Reduction #8Load reduced for boiler deslag. | Ghent | Derate | Coal | 3 | 2015 | 3 | 3.9 | 2.275 | 1089.725 | 279.4167 | 279
GH3 | PD | 11 | 1100 | 2015-03-29 13:00 | 2015-03-29 16:33 | 220 | 528 | 479 | Waterwall (Furnace wall) B | Load Reduction #9Load reduced for boiler deslag. | Ghent | Derate | Coal | 3 | 2015 | 3 | 3.55 | 2.0708 | 991.9292 | 279.4167 | 279
GH3 | D1 | 12 | 4499 | 2015-04-01 06:42 | 2015-04-13 02:07 | 522 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #10Turbine copper deposition. | Ghent | Derate | Coal | 3 | 2015 | 4 | 283.4167 | 3.2206 | 1542.6884 | 5.4432 | 5
GH3 | D1 | 13 | 270 | 2015-04-13 02:07 | 2015-04-13 08:35 | 229 | 528 | 479 | Primary air duct and dampers | Load Reduction #11U3 Boiler tripped due to low PA duct pressure. | Ghent | Derate | Coal | 3 | 2015 | 4 | 6.4667 | 3.662 | 1754.0956 | 271.2519 | 271
GH3 | D1 | 14 | 4499 | 2015-04-13 08:35 | 2015-04-17 07:28 | 522 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #12Unable to make summer high rate because of turbine copper deposi | Ghent | Derate | Coal | 3 | 2015 | 4 | 94.8833 | 1.0782 | 516.4672 | 5.4432 | 5
GH3 | D1 | 15 | 250 | 2015-04-17 07:28 | 2015-04-17 08:18 | 434 | 528 | 479 | Pulverizer feeders | Load Reduction #133-1 Feeder tripped when the feeder belt splice failed. | Ghent | Derate | Coal | 3 | 2015 | 4 | 0.83333 | 0.14836 | 71.0638 | 85.2765 | 85
GH3 | D1 | 16 | 4499 | 2015-04-17 08:18 | 2015-04-18 09:23 | 515 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #14Unable to make summer high rate because of turbine copper deposi | Ghent | Derate | Coal | 3 | 2015 | 4 | 25.0833 | 0.61758 | 295.8218 | 11.7936 | 12
GH3 | U1 | 17 | 270 | 2015-04-18 09:23 | 2015-04-19 20:14 | 0 | 528 | 479 | Primary air duct and dampers | Outage #3Air Heater seals are leaking badly on the unit causing large swings in th | Ghent | Outage | Coal | 3 | 2015 | 4 | 34.85 | 34.85 | 16693.15 | 479 | 479
GH3 | D1 | 18 | 4499 | 2015-04-20 05:36 | 2015-05-11 08:42 | 516 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #15Unable to make summer high rate because of turbine copper deposi | Ghent | Derate | Coal | 3 | 2015 | 4 | 507.1 | 11.525 | 5520.475 | 10.8864 | 11
GH3 | MO | 19 | 1488 | 2015-05-11 08:42 | 2015-05-19 01:21 | 0 | 528 | 479 | Air heater (regenerative) | F060Outage #4Air heater seals are leaking badly causing large swings in furnace an | Ghent | Maintenance | Coal | 3 | 2015 | 5 | 184.65 | 184.65 | 88447.35 | 479 | 479
GH3 | D1 | 20 | 1850 | 2015-05-19 09:28 | 2015-05-19 14:30 | 458 | 528 | 479 | Boiler water condition (not feedwater water quality) | Load Reduction #16The unit was limited due to high boiler drum silica following st | Ghent | Derate | Coal | 3 | 2015 | 5 | 5.0333 | 0.6673 | 319.6357 | 63.5038 | 64
GH3 | D1 | 21 | 250 | 2015-05-24 19:43 | 2015-05-24 20:11 | 435 | 528 | 479 | Pulverizer feeders | Load Reduction #173-1 Feeder tripped for no apparent reason. | Ghent | Derate | Coal | 3 | 2015 | 5 | 0.46667 | 0.082197 | 39.3723 | 84.3693 | 84
GH3 | U1 | 22 | 1080 | 2015-06-10 22:27 | 2015-06-12 07:13 | 0 | 528 | 479 | Economizer B | F540Outage #5Unit 3 was removed from service after peak with an economizer tube le | Ghent | Outage | Coal | 3 | 2015 | 6 | 32.7667 | 32.7667 | 15695.2333 | 479 | 479
GH3 | U1 | 23 | 1000 | 2015-06-13 20:24 | 2015-06-14 23:41 | 0 | 528 | 479 | Waterwall (Furnace wall) A | Outage #6A tube leak could be heard, but location could not be detected in the upp | Ghent | Outage | Coal | 3 | 2015 | 6 | 27.2833 | 27.2833 | 13068.7167 | 479 | 479
GH3 | MO | 24 | 1000 | 2015-06-19 17:46 | 2015-06-21 14:24 | 0 | 528 | 479 | Waterwall (Furnace wall) A | F540Outage #7Small tube leak could be heard, but location could not be detected in | Ghent | Maintenance | Coal | 3 | 2015 | 6 | 44.6333 | 44.6333 | 21379.3667 | 479 | 479
GH3 | D1 | 25 | 3416 | 2015-07-13 01:23 | 2015-07-13 22:11 | 325 | 528 | 479 | Other feedwater pump problems | Load Reduction #183-1 BFPT expansion joint failed. | Ghent | Derate | Coal | 3 | 2015 | 7 | 20.8 | 7.997 | 3830.5485 | 184.161 | 184
GH3 | D1 | 26 | 250 | 2015-08-03 13:41 | 2015-08-03 14:57 | 410 | 528 | 479 | Pulverizer feeders | Load Reduction #193-3 Feeder tripped for no apparent reason. Motor overloads trip | Ghent | Derate | Coal | 3 | 2015 | 8 | 1.2667 | 0.28308 | 135.5957 | 107.0492 | 107
GH3 | U2 | 27 | 1040 | 2015-08-14 02:20 | 2015-08-15 21:10 | 0 | 528 | 479 | First superheater B | Outage #8Primary Superheater developed a tube leak that required the unit to be re | Ghent | Outage | Coal | 3 | 2015 | 8 | 42.8333 | 42.8333 | 20517.1667 | 479 | 479
GH3 | PD | 29 | 3410 | 2015-08-17 22:30 | 2015-08-17 23:57 | 300 | 528 | 479 | Feedwater pump | Load Reduction #203-1 BFP off to troubleshoot latching issues. | Ghent | Derate | Coal | 3 | 2015 | 8 | 1.45 | 0.62614 | 299.9193 | 206.8409 | 207
GH3 | D1 | 30 | 1415 | 2015-08-24 07:01 | 2015-08-24 07:16 | 500 | 528 | 479 | Forced draft fan controls | Load Reduction #213-1 FD fan inlet vane stopped operating. Controls locked out wh | Ghent | Derate | Coal | 3 | 2015 | 8 | 0.25 | 0.013258 | 6.3504 | 25.4015 | 25
GH3 | U1 | 31 | 1080 | 2015-08-30 10:52 | 2015-09-02 14:15 | 0 | 528 | 479 | Economizer B | Outage #10Unit 3 developed a tube leak in the Economizer section of the Boiler. R | Ghent | Outage | Coal | 3 | 2015 | 8 | 75.3833 | 75.3833 | 36108.6167 | 479 | 479
GH3 | U2 | 32 | 500 | 2015-09-02 16:17 | 2015-09-03 02:35 | 0 | 528 | 479 | Main steam piping up to turbine stop valves | Outage #11Unit 3 developed a leak in the Main Steam line drain line just before th | Ghent | Outage | Coal | 3 | 2015 | 9 | 10.3 | 10.3 | 4933.7 | 479 | 479
GH3 | PD | 33 | 1412 | 2015-10-06 23:45 | 2015-10-07 02:14 | 200 | 528 | 479 | Forced draft fan drives (other than motor) | F930Load Reduction #223-1 FD fan inlet vane drive unit failed. Had to gag damper | Ghent | Derate | Coal | 3 | 2015 | 10 | 2.4833 | 1.5427 | 738.9422 | 297.5606 | 298
GH3 | PO | 34 | 4402 | 2015-10-16 12:44 | 2015-11-16 01:15 | 0 | 528 | 479 | Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | F590Outage #12Unit 3 scheduled for Fall Planned Outage to do general maintenance a | Ghent | Other | Coal | 3 | 2015 | 10 | 732.5167 | 732.5167 | 350875.4833 | 479 | 479
GH3 | MO | 35 | 1050 | 2015-11-25 11:21 | 2015-11-26 07:07 | 0 | 528 | 479 | Second superheater B | F540Outage #13Unit 3 was removed form service to repair a tube leak in the partiti | Ghent | Maintenance | Coal | 3 | 2015 | 11 | 19.7667 | 19.7667 | 9468.2333 | 479 | 479
GH3 | D1 | 36 | 340 | 2015-12-03 15:56 | 2015-12-03 17:56 | 425 | 528 | 479 | Other pulverizer problems | Load Reduction #233-3 and 3-4 Mill worm gear packing failed. 3-4 Mill caught fire | Ghent | Derate | Coal | 3 | 2015 | 12 | 2 | 0.39015 | 186.8826 | 93.4413 | 93
GH3 | D1 | 37 | 340 | 2015-12-20 09:35 | 2015-12-20 11:47 | 480 | 528 | 479 | Other pulverizer problems | Load Reduction #243-3 Mill had blown fuses not allowing the feeder to go above min | Ghent | Derate | Coal | 3 | 2015 | 12 | 2.2 | 0.2 | 95.8 | 43.5455 | 44
GH3 | D1 | 1 | 250 | 2016-01-04 07:28 | 2016-01-04 08:33 | 450 | 528 | 479 | Pulverizer feeders | Load Reduction #13-5 Feeder speed sensor failed. Unable to get feeder above 50%. | Ghent | Derate | Coal | 3 | 2016 | 1 | 1.0833 | 0.16004 | 76.6581 | 70.7614 | 71
GH3 | MO | 2 | 1050 | 2016-01-08 22:19 | 2016-01-09 22:17 | 0 | 528 | 479 | Second superheater B | F540Outage #1Unit 3 was removed from service to repair a finishing superheat tube | Ghent | Maintenance | Coal | 3 | 2016 | 1 | 23.9667 | 23.9667 | 11480.0333 | 479 | 479
GH3 | U1 | 3 | 4800 | 2016-01-11 11:50 | 2016-01-13 01:20 | 0 | 528 | 479 | Generator main leads | Outage #2Unit 3 was removed from service due to generator bus duct overheating. | Ghent | Outage | Coal | 3 | 2016 | 1 | 37.5 | 37.5 | 17962.5 | 479 | 479
GH3 | MO | 5 | 1060 | 2016-03-08 14:26 | 2016-03-09 05:41 | 0 | 528 | 479 | First reheater A | F540Outage #4Unit 3 Reserve Outage was changed to a Maintenance Outage to repair a | Ghent | Maintenance | Coal | 3 | 2016 | 3 | 15.25 | 15.25 | 7304.75 | 479 | 479
GH3 | D1 | 7 | 1150 | 2016-04-08 23:00 | 2016-04-09 03:00 | 200 | 528 | 479 | Second superheater A | F830Load Reduction #2Load reduced to deslag the Finishing SH section of the boiler | Ghent | Derate | Coal | 3 | 2016 | 4 | 4 | 2.4848 | 1190.2424 | 297.5606 | 298
GH3 | MO | 8 | 1512 | 2016-05-05 08:31 | 2016-05-08 21:20 | 0 | 528 | 479 | Flue gas expansion joints | F540Outage #6Unit 3 came off line to repair expansion joint damage. | Ghent | Maintenance | Coal | 3 | 2016 | 5 | 84.8167 | 84.8167 | 40627.1833 | 479 | 479
GH3 | D1 | 9 | 346 | 2016-05-14 08:53 | 2016-05-14 12:30 | 420 | 528 | 479 | Pulverizer pyrite removal system | Load Reduction #33-4 Mill was making noise in the grinding and pyrite section. Th | Ghent | Derate | Coal | 3 | 2016 | 5 | 3.6167 | 0.73977 | 354.3511 | 97.9773 | 98
GH3 | D1 | 10 | 267 | 2016-05-19 14:11 | 2016-05-19 14:41 | 425 | 528 | 479 | Primary air flow instrumentation | Load Reduction #43-4 Mill was removed from service when the PA flow indication wen | Ghent | Derate | Coal | 3 | 2016 | 5 | 0.5 | 0.097538 | 46.7206 | 93.4413 | 93
GH3 | PD | 11 | 250 | 2016-05-20 01:30 | 2016-05-20 04:02 | 420 | 528 | 479 | Pulverizer feeders | Load Reduction #53-3 Feeder calibration. | Ghent | Derate | Coal | 3 | 2016 | 5 | 2.5333 | 0.51818 | 248.2091 | 97.9773 | 98
GH3 | MO | 12 | 1480 | 2016-05-20 09:43 | 2016-05-30 16:28 | 0 | 528 | 479 | Other induced draft fan problems | F590Outage #7Unit 3 was removed from service to replace the ID fan discharge duct | Ghent | Maintenance | Coal | 3 | 2016 | 5 | 246.75 | 246.75 | 118193.25 | 479 | 479
GH3 | D1 | 13 | 1850 | 2016-05-31 03:35 | 2016-05-31 07:40 | 508 | 528 | 479 | Boiler water condition (not feedwater water quality) | FA00Load Reduction #6Following unit start up the load was reduced due to high boil | Ghent | Derate | Coal | 3 | 2016 | 5 | 4.0833 | 0.15467 | 74.0878 | 18.1439 | 18
GH3 | D1 | 14 | 1470 | 2016-06-02 07:21 | 2016-06-02 08:54 | 460 | 528 | 479 | Induced draft fan motors and drives | Load Reduction #73-2A ID fan tripped due to a control problem. The fan tripped wh | Ghent | Derate | Coal | 3 | 2016 | 6 | 1.55 | 0.19962 | 95.6186 | 61.6894 | 62
GH3 | D1 | 15 | 4291 | 2016-06-08 22:00 | 2016-06-09 03:06 | 445 | 528 | 479 | Hydraulic system coolers | F830Load Reduction #8Unit 3 was derated to investigate an H2 cooler leaks, 1 coole | Ghent | Derate | Coal | 3 | 2016 | 6 | 5.1 | 0.8017 | 384.0165 | 75.2973 | 75
GH3 | U1 | 16 | 4291 | 2016-06-09 06:47 | 2016-06-09 18:19 | 0 | 528 | 479 | Hydraulic system coolers | F830Outage #8Unit 3 was removed from service to investigate an H2 cooler leak. | Ghent | Outage | Coal | 3 | 2016 | 6 | 11.5333 | 11.5333 | 5524.4667 | 479 | 479
GH3 | MO | 17 | 4291 | 2016-06-09 18:19 | 2016-06-10 09:20 | 0 | 528 | 479 | Hydraulic system coolers | F540Outage #9The unit was removed from service on a Forced outage for an H2 cooler | Ghent | Maintenance | Coal | 3 | 2016 | 6 | 15.0167 | 15.0167 | 7192.9833 | 479 | 479
GH3 | U1 | 18 | 4261 | 2016-06-11 17:43 | 2016-06-11 19:20 | 0 | 528 | 479 | Control valves | F830Outage #10Unit 3 was removed from service when an EH leak was detected at the | Ghent | Outage | Coal | 3 | 2016 | 6 | 1.6167 | 1.6167 | 774.3833 | 479 | 479
GH3 | U1 | 19 | 4500 | 2016-06-11 19:20 | 2016-06-15 17:45 | 0 | 528 | 479 | Rotor windings (including damper windings and fan blades on hydro units) | F540Outage #11Unit 3 generator could not be put in service due to a generator grou | Ghent | Outage | Coal | 3 | 2016 | 6 | 94.4167 | 94.4167 | 45225.5833 | 479 | 479
GH3 | D1 | 20 | 4291 | 2016-06-17 05:40 | 2016-06-17 07:58 | 445 | 528 | 479 | Hydraulic system coolers | Load Reduction #9Unit 3 was derated to investigate an H2 cooler leaks, 1 cooler at | Ghent | Derate | Coal | 3 | 2016 | 6 | 2.3 | 0.36155 | 173.1839 | 75.2973 | 75
GH3 | U1 | 21 | 1040 | 2016-07-01 21:22 | 2016-07-03 05:06 | 0 | 528 | 479 | First superheater B | F830Outage #12Unit 3 was removed from service due to a boiler superheat tube leak. | Ghent | Outage | Coal | 3 | 2016 | 7 | 31.7333 | 31.7333 | 15200.2667 | 479 | 479
GH3 | PD | 22 | 1470 | 2016-07-09 01:45 | 2016-07-09 03:00 | 400 | 528 | 479 | Induced draft fan motors and drives | F590Load Reduction #103-2B ID fan was removed from service to reset the VFD. Two | Ghent | Derate | Coal | 3 | 2016 | 7 | 1.25 | 0.30303 | 145.1515 | 116.1212 | 116
GH3 | D1 | 23 | 1040 | 2016-07-19 10:06 | 2016-07-19 21:37 | 378 | 528 | 479 | First superheater B | F830Load Reduction #11U3 Boiler drum pressure was dropped until after peak due to | Ghent | Derate | Coal | 3 | 2016 | 7 | 11.5167 | 3.2718 | 1567.1828 | 136.0795 | 136
GH3 | U2 | 24 | 1040 | 2016-07-19 21:37 | 2016-07-20 18:32 | 0 | 528 | 479 | First superheater B | F540Outage #13The unit was removed from service due to a Primary SH tube leak. The | Ghent | Outage | Coal | 3 | 2016 | 7 | 20.9167 | 20.9167 | 10019.0833 | 479 | 479
GH3 | D1 | 25 | 340 | 2016-08-06 16:07 | 2016-08-06 17:57 | 440 | 528 | 479 | Other pulverizer problems | Load Reduction #12Operations removed 3-2 Mill from service when a coal leak develo | Ghent | Derate | Coal | 3 | 2016 | 8 | 1.8333 | 0.30556 | 146.3611 | 79.8333 | 80
GH3 | U1 | 26 | 1040 | 2016-08-12 01:09 | 2016-08-13 03:35 | 0 | 528 | 479 | First superheater B | F830Outage #14The unit was removed from service due to a boiler Primary Superheat | Ghent | Outage | Coal | 3 | 2016 | 8 | 26.4333 | 26.4333 | 12661.5667 | 479 | 479
GH3 | D1 | 27 | 1457 | 2016-09-09 20:46 | 2016-09-10 00:20 | 450 | 528 | 479 | Induced draft fan lubrication systems | Load Reduction #133-1A ID fan tripped when the lube oil reservoir temperature tran | Ghent | Derate | Coal | 3 | 2016 | 9 | 3.5667 | 0.52689 | 252.3822 | 70.7614 | 71
GH3 | U1 | 28 | 1060 | 2016-09-22 02:36 | 2016-09-23 23:40 | 0 | 528 | 479 | First reheater A | F830Outage #15U3 came off line with a Reheat tube leak. | Ghent | Outage | Coal | 3 | 2016 | 9 | 45.0667 | 45.0667 | 21586.9333 | 479 | 479
GH3 | MO | 29 | 1060 | 2016-09-28 08:08 | 2016-09-29 15:29 | 0 | 528 | 479 | First reheater A | F540Outage #16U3 came off line on a Maintenance Outage due to a RH tube leak. | Ghent | Maintenance | Coal | 3 | 2016 | 9 | 31.35 | 31.35 | 15016.65 | 479 | 479
GH3 | D1 | 30 | 344 | 2016-10-18 06:45 | 2016-10-18 09:59 | 420 | 528 | 479 | Pulverizer inspection | Load Reduction #143-4 Mill was removed from service to inspect due to loud noise. | Ghent | Derate | Coal | 3 | 2016 | 10 | 3.2333 | 0.66136 | 316.7932 | 97.9773 | 98
GH3 | D1 | 31 | 340 | 2016-10-22 11:43 | 2016-10-29 15:54 | 425 | 528 | 479 | Other pulverizer problems | Load Reduction #153-5 Mill upper radail bearing failed. 1-3 Mill was out of servi | Ghent | Derate | Coal | 3 | 2016 | 10 | 172.1833 | 33.5888 | 16089.0324 | 93.4413 | 93
GH3 | PO | 32 | 1801 | 2016-10-29 15:54 | 2016-11-18 19:57 | 0 | 528 | 479 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Outage #17Unit 3 Planned Fall Outage. | Ghent | Other | Coal | 3 | 2016 | 10 | 484.05 | 484.05 | 231859.95 | 479 | 479
GH3 | PD | 33 | 250 | 2016-11-22 11:05 | 2016-11-22 12:10 | 410 | 528 | 479 | Pulverizer feeders | F060Load Reduction #163-1 Feeder belt splice came apart. | Ghent | Derate | Coal | 3 | 2016 | 11 | 1.0833 | 0.24211 | 115.97 | 107.0492 | 107
GH3 | D1 | 34 | 340 | 2016-11-25 09:21 | 2016-11-25 18:53 | 420 | 528 | 479 | Other pulverizer problems | Load Reduction #173-4 Mill loaded up during start up. Ops took the mill off and h | Ghent | Derate | Coal | 3 | 2016 | 11 | 9.5333 | 1.95 | 934.05 | 97.9773 | 98
GH3 | PD | 35 | 350 | 2016-11-27 22:00 | 2016-11-28 00:30 | 420 | 528 | 479 | Pulverized fuel and air piping (from pulverizer to wind box) | F540Load Reduction #183-4B Burner line coal leak. Removed mill from service to re | Ghent | Derate | Coal | 3 | 2016 | 11 | 2.5 | 0.51136 | 244.9432 | 97.9773 | 98
GH3 | PD | 36 | 8460 | 2016-12-09 21:45 | 2016-12-12 05:00 | 250 | 528 | 479 | Testing A | F790Load Reduction #19Unit 3 was derated to perform SCR testing. | Ghent | Derate | Coal | 3 | 2016 | 12 | 55.25 | 29.09 | 13934.0919 | 252.2008 | 252
GH3 | SF | 4 | 4899 | 2017-02-22 19:09 | 2017-02-22 22:42 | 0 | 528 | 479 | Other miscellaneous generator problems | F430Outage #3Generator exciter field ground detection issues resulted in a startup | Ghent | Outage | Coal | 3 | 2017 | 2 | 3.55 | 3.55 | 1700.45 | 479 | 479
GH3 | D1 | 3 | 1850 | 2017-02-23 06:44 | 2017-02-23 10:29 | 435 | 528 | 479 | Boiler water condition (not feedwater water quality) | FA00Load Reduction #1Load was reduced due to high silica levels following start up | Ghent | Derate | Coal | 3 | 2017 | 2 | 3.75 | 0.66051 | 316.3849 | 84.3693 | 84
GH3 | U1 | 5 | 1080 | 2017-04-15 16:24 | 2017-04-19 04:13 | 0 | 528 | 479 | Economizer B | F540Outage #4Unit 3 was forced off line due to a tube leak in the upper economizer | Ghent | Outage | Coal | 3 | 2017 | 4 | 83.8167 | 83.8167 | 40148.1833 | 479 | 479
GH3 | D1 | 7 | 4499 | 2017-06-10 15:41 | 2017-06-23 09:15 | 520 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #2Load was reduced due to turbine copper depostion. | Ghent | Derate | Coal | 3 | 2017 | 6 | 305.5667 | 4.6298 | 2217.6732 | 7.2576 | 7
GH3 | PD | 8 | 3408 | 2017-06-22 22:45 | 2017-06-22 23:34 | 340 | 528 | 479 | Feedwater pump drive - local controls | F590Load Reduction #3 3-2 BFPT lockout solenoid change out. | Ghent | Derate | Coal | 3 | 2017 | 6 | 0.81667 | 0.29078 | 139.285 | 170.553 | 171
GH3 | D1 | 9 | 3149 | 2017-07-22 11:08 | 2017-07-22 20:06 | 510 | 528 | 479 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | Load Reduction #4Load was reduced due to high backpressure. | Ghent | Derate | Coal | 3 | 2017 | 7 | 8.9667 | 0.30568 | 146.4216 | 16.3295 | 16
GH3 | D1 | 10 | 4499 | 2017-07-22 20:06 | 2017-07-24 14:42 | 526 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #5Load was reduced due to turbine performance. | Ghent | Derate | Coal | 3 | 2017 | 7 | 42.6 | 0.16136 | 77.2932 | 1.8144 | 2
GH3 | D1 | 11 | 3199 | 2017-07-24 14:42 | 2017-07-24 15:16 | 500 | 528 | 479 | Other miscellaneous condensing system problems | Load Reduction #6Condensate pump problems. | Ghent | Derate | Coal | 3 | 2017 | 7 | 0.56667 | 0.030051 | 14.3942 | 25.4015 | 25
GH3 | D1 | 12 | 3149 | 2017-08-17 10:52 | 2017-08-17 12:01 | 515 | 528 | 479 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | Load Reduction #7High backpressure due to ambient air temperatures. | Ghent | Derate | Coal | 3 | 2017 | 8 | 1.15 | 0.028314 | 13.5626 | 11.7936 | 12
GH3 | D1 | 13 | 3149 | 2017-08-17 12:01 | 2017-08-17 15:34 | 510 | 528 | 479 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | Load Reduction #8High backpressure due to ambient air temperatures. | Ghent | Derate | Coal | 3 | 2017 | 8 | 3.55 | 0.12102 | 57.9699 | 16.3295 | 16
GH3 | D1 | 14 | 4499 | 2017-08-17 15:34 | 2017-08-31 21:45 | 525 | 528 | 479 | Other miscellaneous steam turbine problems | Load Reduction #9Load reduced due to copper deposition. | Ghent | Derate | Coal | 3 | 2017 | 8 | 342.1833 | 1.9442 | 931.283 | 2.7216 | 3
GH3 | MO | 15 | 1040 | 2017-08-31 21:45 | 2017-09-01 19:22 | 0 | 528 | 479 | First superheater B | F540Outage # 6Unit 3 was forced off line due to tube leak in the Finishing Superhe | Ghent | Maintenance | Coal | 3 | 2017 | 8 | 21.6167 | 21.6167 | 10354.3833 | 479 | 479
GH3 | D1 | 17 | 3441 | 2017-09-12 05:07 | 2017-09-12 06:01 | 460 | 528 | 479 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F550Load Reduction #103F HP heater emergency drain wasn't repsonding. | Ghent | Derate | Coal | 3 | 2017 | 9 | 0.9 | 0.11591 | 55.5205 | 61.6894 | 62
GH3 | PD | 18 | 320 | 2017-09-22 | 2017-09-22 01:37 | 450 | 528 | 479 | Foreign object in Pulverizers mill | F530Load Reduction #11 3-1 Mill was removed from service to remove a piece of metal. | Ghent | Derate | Coal | 3 | 2017 | 9 | 1.6167 | 0.23883 | 114.3975 | 70.7614 | 71
GH3 | D1 | 19 | 320 | 2017-09-27 05:50 | 2017-09-27 09:11 | 420 | 528 | 479 | Foreign object in Pulverizers mill | Load Reduction #123-4 Mill was removed from service to remove a piece of metal fro | Ghent | Derate | Coal | 3 | 2017 | 9 | 3.35 | 0.68523 | 328.2239 | 97.9773 | 98
GH3 | PO | 20 | 1801 | 2017-10-13 20:49 | 2017-11-13 | 0 | 528 | 479 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Outage #8 Unit 3 was removed from service for Planned Outage. | Ghent | Other | Coal | 3 | 2017 | 10 | 723.1833 | 723.1833 | 346404.8167 | 479 | 479
GH3 | PE | 21 | 1801 | 2017-11-13 | 2017-11-15 10:07 | 0 | 528 | 479 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Outage #9 GH3 Planned Outage extension. | Ghent | Other | Coal | 3 | 2017 | 11 | 58.1167 | 58.1167 | 27837.8833 | 479 | 479
GH3 | SF | 24 | 800 | 2017-11-15 10:07 | 2017-11-15 21:32 | 0 | 528 | 479 | Drums and drum internals (single drum only) | F540SUF Outage #11Drum door gasket leaking. | Ghent | Outage | Coal | 3 | 2017 | 11 | 11.4167 | 11.4167 | 5468.5833 | 479 | 479
GH3 | D1 | 22 | 1140 | 2017-11-19 09:32 | 2017-11-19 10:36 | 200 | 528 | 479 | First superheater A | F540Load Reduction #13Unit 3 was derated due to superheat tube leak. | Ghent | Derate | Coal | 3 | 2017 | 11 | 1.0667 | 0.66263 | 317.398 | 297.5606 | 298
GH3 | U1 | 23 | 1040 | 2017-11-19 10:36 | 2017-11-23 00:15 | 0 | 528 | 479 | First superheater B | F540Outage #10 Unit 3 was forced off-line due to superheat tube leak. | Ghent | Outage | Coal | 3 | 2017 | 11 | 85.65 | 85.65 | 41026.35 | 479 | 479
GH3 | D1 | 25 | 1455 | 2017-12-05 10:10 | 2017-12-05 11:19 | 450 | 528 | 479 | Induced draft fans | F820Load Reduction #14Unit 3 was derated due to loss of 3-1A ID fan. | Ghent | Derate | Coal | 3 | 2017 | 12 | 1.15 | 0.16989 | 81.3756 | 70.7614 | 71
GH3 | PD | 1 | 920 | 2018-01-05 20:40 | 2018-01-05 23:15 | 240 | 528 | 479 | Other slag and ash removal problems A | F830Load Reduction #1Planned boiler deslag. | Ghent | Derate | Coal | 3 | 2018 | 1 | 2.5833 | 1.4091 | 674.9545 | 261.2727 | 261
GH3 | MO | 3 | 550 | 2018-02-24 07:46 | 2018-02-24 18:02 | 0 | 528 | 479 | Reheat steam relief/safety valves | Outage #2Unit was placed on a miantenance outage to repair a cold RH safety that w | Ghent | Maintenance | Coal | 3 | 2018 | 2 | 10.2667 | 10.2667 | 4917.7333 | 479 | 479
GH3 | U1 | 5 | 3220 | 2018-03-03 11:30 | 2018-03-04 03:22 | 0 | 528 | 479 | Circulating water piping | F540Outage #4Unit was forced off line due to Circulating water bypass line leak. | Ghent | Outage | Coal | 3 | 2018 | 3 | 15.8667 | 15.8667 | 7600.1333 | 479 | 479
GH3 | D1 | 6 | 1457 | 2018-03-26 08:48 | 2018-03-26 11:56 | 450 | 528 | 479 | Induced draft fan lubrication systems | F520Load Reduction #23-2A I.D. fan tripped due to lube oil reservoir T/C and tempe | Ghent | Derate | Coal | 3 | 2018 | 3 | 3.1333 | 0.46288 | 221.7189 | 70.7614 | 71
GH3 | D1 | 7 | 3412 | 2018-04-29 07:15 | 2018-04-29 07:41 | 155 | 528 | 479 | Feedwater pump drive - steam turbine | Load Reduction #33-2 BFPT tripped on high vibration when starting 3-4 pulverizer t | Ghent | Derate | Coal | 3 | 2018 | 4 | 0.43333 | 0.30612 | 146.6333 | 338.3845 | 338
GH3 | U1 | 8 | 3412 | 2018-04-29 07:41 | 2018-04-29 09:43 | 0 | 528 | 479 | Feedwater pump drive - steam turbine | Outage #5Boiler tripped on low drum level due to the loss of 3-2 BFPT. Unit was r | Ghent | Outage | Coal | 3 | 2018 | 4 | 2.0333 | 2.0333 | 973.9667 | 479 | 479
GH4 | MO | 1 | 1455 | 2013-01-01 | 2013-01-09 04:56 | 0 | 525 | 478 | Induced draft fans | Outage #1Both unit ID fans were having spikes on bearing temperatures on fan beari | Ghent | Maintenance | Coal | 3 | 2013 | 1 | 196.9333 | 196.9333 | 94134.1333 | 478 | 478
GH4 | D1 | 3 | 1455 | 2013-01-09 07:30 | 2013-01-09 15:24 | 200 | 525 | 478 | Induced draft fans | Load Reduction #14-2 ID fan OOS due to rotor replacement. | Ghent | Derate | Coal | 3 | 2013 | 1 | 7.9 | 4.8905 | 2337.6476 | 295.9048 | 296
GH4 | D1 | 4 | 1455 | 2013-01-09 15:24 | 2013-01-09 16:17 | 225 | 525 | 478 | Induced draft fans | Load Reduction #24-2 ID fan OOS due to rotor replacement. | Ghent | Derate | Coal | 3 | 2013 | 1 | 0.88333 | 0.50476 | 241.2762 | 273.1429 | 273
GH4 | D1 | 5 | 1455 | 2013-01-09 16:17 | 2013-01-09 20:00 | 230 | 525 | 478 | Induced draft fans | Load Reduction #34-2 ID fan OOS due to rotor replacement. | Ghent | Derate | Coal | 3 | 2013 | 1 | 3.7167 | 2.0884 | 998.2613 | 268.5905 | 269
GH4 | D1 | 6 | 1455 | 2013-01-09 20:00 | 2013-01-11 22:13 | 200 | 525 | 478 | Induced draft fans | Load Reduction #44-2 ID fan OOS due to rotor replacement. | Ghent | Derate | Coal | 3 | 2013 | 1 | 50.2167 | 31.0865 | 14859.3508 | 295.9048 | 296
GH4 | MO | 7 | 1455 | 2013-01-11 22:13 | 2013-01-16 16:17 | 0 | 525 | 478 | Induced draft fans | Outage #2The unit had been running at a reduced load with the 4-2 ID fan out of se | Ghent | Maintenance | Coal | 3 | 2013 | 1 | 114.0667 | 114.0667 | 54523.8667 | 478 | 478
GH4 | SF | 8 | 1455 | 2013-01-16 16:17 | 2013-01-17 16:07 | 0 | 525 | 478 | Induced draft fans | F850Outage #3The 4-2 ID fan could not be balanced during the Maint. Outage. Decide | Ghent | Outage | Coal | 3 | 2013 | 1 | 23.8333 | 23.8333 | 11392.3333 | 478 | 478
GH4 | D1 | 9 | 1455 | 2013-01-17 16:07 | 2013-01-19 12:39 | 200 | 525 | 478 | Induced draft fans | Load Reduction #54-2 ID fan off for to balance the fan rotor. | Ghent | Derate | Coal | 3 | 2013 | 1 | 44.5333 | 27.5683 | 13177.6254 | 295.9048 | 296
GH4 | MO | 10 | 1455 | 2013-01-19 12:39 | 2013-01-20 08:36 | 0 | 525 | 478 | Induced draft fans | F850Outage #4The unit was running with a derate due to 4-2 ID fan being out of ser | Ghent | Maintenance | Coal | 3 | 2013 | 1 | 19.95 | 19.95 | 9536.1 | 478 | 478
GH4 | D1 | 11 | 3440 | 2013-01-20 12:45 | 2013-01-21 21:05 | 511 | 525 | 478 | High pressure heater tube leaks | Load Reduction #6Unit 4 load was reduced to repair a tube leak in 4G HP heater. | Ghent | Derate | Coal | 3 | 2013 | 1 | 32.3333 | 0.86222 | 412.1422 | 12.7467 | 13
GH4 | U3 | 12 | 3110 | 2013-02-02 00:02 | 2013-02-02 22:18 | 0 | 525 | 478 | Condenser tube leaks | F540Outage #5The unit was running with a tube leak in 4-2 auxiliary condenser leak | Ghent | Outage | Coal | 3 | 2013 | 2 | 22.2667 | 22.2667 | 10643.4667 | 478 | 478
GH4 | D1 | 13 | 1488 | 2013-02-03 21:19 | 2013-02-08 23:01 | 190 | 525 | 478 | Air heater (regenerative) | Load Reduction #74-2 Air heater sector plate broke. | Ghent | Derate | Coal | 3 | 2013 | 2 | 121.7 | 77.6562 | 37119.659 | 305.0095 | 305
GH4 | MO | 14 | 1488 | 2013-02-08 23:01 | 2013-02-10 02:38 | 0 | 525 | 478 | Air heater (regenerative) | F050Outage #64-2 Air heater had a hard radial rub. Unit was operating with 4-2 ga | Ghent | Maintenance | Coal | 3 | 2013 | 2 | 27.6167 | 27.6167 | 13200.7667 | 478 | 478
GH4 | D1 | 15 | 346 | 2013-02-22 17:40 | 2013-02-22 18:44 | 403 | 525 | 478 | Pulverizer pyrite removal system | Load Reduction #84-5 Mill pyrite chute plugged. Removed the mill from service lon | Ghent | Derate | Coal | 3 | 2013 | 2 | 1.0667 | 0.24787 | 118.4833 | 111.0781 | 111
GH4 | D1 | 16 | 350 | 2013-03-03 03:30 | 2013-03-03 05:08 | 400 | 525 | 478 | Pulverized fuel and air piping (from pulverizer to wind box) | Load Reduction #94-6 Mill was dumping pyrites. | Ghent | Derate | Coal | 3 | 2013 | 3 | 1.6333 | 0.38889 | 185.8889 | 113.8095 | 114
GH4 | D1 | 17 | 1493 | 2013-03-04 06:25 | 2013-03-05 12:07 | 510 | 525 | 478 | Air heater fouling (regenerative) | F320Load Reduction #10High differential on 4-2 air heater. | Ghent | Derate | Coal | 3 | 2013 | 3 | 29.7 | 0.84857 | 405.6171 | 13.6571 | 14
GH4 | D1 | 18 | 1493 | 2013-03-05 12:07 | 2013-03-08 23:29 | 500 | 525 | 478 | Air heater fouling (regenerative) | F320Load Reduction #11High differential on 4-2 air heater. | Ghent | Derate | Coal | 3 | 2013 | 3 | 83.3667 | 3.9698 | 1897.5841 | 22.7619 | 23
GH4 | D1 | 20 | 3149 | 2013-04-08 10:51 | 2013-04-09 06:17 | 505 | 525 | 478 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | Load Reduction #12Condenser backpressure. | Ghent | Derate | Coal | 3 | 2013 | 4 | 19.4333 | 0.74032 | 353.8717 | 18.2095 | 18
GH4 | D1 | 21 | 3149 | 2013-04-09 11:26 | 2013-04-09 22:35 | 493 | 525 | 478 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | Load Reduction #13Condenser Backpressure. | Ghent | Derate | Coal | 3 | 2013 | 4 | 11.15 | 0.67962 | 324.8579 | 29.1352 | 29
GH4 | D1 | 22 | 3149 | 2013-04-10 08:39 | 2013-04-10 23:16 | 500 | 525 | 478 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | Load Reduction #14Condenser backpressure. | Ghent | Derate | Coal | 3 | 2013 | 4 | 14.6167 | 0.69603 | 332.7032 | 22.7619 | 23
GH4 | D1 | 23 | 3149 | 2013-04-11 08:12 | 2013-04-11 16:12 | 500 | 525 | 478 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | Load Reduction #15Condenser backpressure. | Ghent | Derate | Coal | 3 | 2013 | 4 | 8 | 0.38095 | 182.0952 | 22.7619 | 23
GH4 | D1 | 25 | 250 | 2013-04-17 10:25 | 2013-04-17 10:50 | 425 | 525 | 478 | Pulverizer feeders | Load Reduction #174-1 feeder coal flow switch. | Ghent | Derate | Coal | 3 | 2013 | 4 | 0.41667 | 0.079365 | 37.9365 | 91.0476 | 91
GH4 | D1 | 26 | 3149 | 2013-04-17 13:10 | 2013-04-17 23:37 | 493 | 525 | 478 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | Load Reduction #18Condenser backpressure. | Ghent | Derate | Coal | 3 | 2013 | 4 | 10.45 | 0.63695 | 304.4632 | 29.1352 | 29
GH4 | D1 | 27 | 250 | 2013-04-17 14:26 | 2013-04-17 15:00 | 445 | 525 | 478 | Pulverizer feeders | Load Reduction #194-1 feeder coal flow switch. | Ghent | Derate | Coal | 3 | 2013 | 4 | 0.56667 | 0.086349 | 41.2749 | 72.8381 | 73
GH4 | D1 | 28 | 3149 | 2013-04-18 08:00 | 2013-04-19 03:33 | 477 | 525 | 478 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | Load Reduction #20High condenser back pressure. | Ghent | Derate | Coal | 3 | 2013 | 4 | 19.55 | 1.7874 | 854.3909 | 43.7029 | 44
GH4 | D1 | 29 | 4260 | 2013-04-19 23:58 | 2013-04-20 00:06 | 460 | 525 | 478 | Main stop valves | Load Reduction #21Main turbine #2 stop valve stuck in mid travel during test. | Ghent | Derate | Coal | 3 | 2013 | 4 | 0.13333 | 0.016508 | 7.8908 | 59.181 | 59
GH4 | U1 | 30 | 4260 | 2013-04-20 00:06 | 2013-04-20 03:52 | 0 | 525 | 478 | Main stop valves | Outage #8Servo failed on main steam stop valve #2 causing valves to close on turbi | Ghent | Outage | Coal | 3 | 2013 | 4 | 3.7667 | 3.7667 | 1800.4667 | 478 | 478
GH4 | D1 | 31 | 1493 | 2013-04-24 01:16 | 2013-05-01 07:50 | 500 | 525 | 478 | Air heater fouling (regenerative) | Load Reduction #22U4 AH differentials are running high causing ID fan duct pressur | Ghent | Derate | Coal | 3 | 2013 | 4 | 174.5667 | 8.3127 | 3973.4698 | 22.7619 | 23
GH4 | D1 | 32 | 1493 | 2013-05-01 07:50 | 2013-05-01 16:18 | 510 | 525 | 478 | Air heater fouling (regenerative) | Load Reduction #23U4 AH differentials were running high causing ID fan duct pressu | Ghent | Derate | Coal | 3 | 2013 | 5 | 8.4667 | 0.2419 | 115.6305 | 13.6571 | 14
GH4 | MO | 33 | 1493 | 2013-05-03 22:24 | 2013-05-07 22:48 | 0 | 525 | 478 | Air heater fouling (regenerative) | F320Outage #9The unit was running with high differential on the air heaters. Remo | Ghent | Maintenance | Coal | 3 | 2013 | 5 | 96.4 | 96.4 | 46079.2 | 478 | 478
GH4 | D1 | 34 | 9900 | 2013-05-08 06:48 | 2013-05-08 07:50 | 360 | 525 | 478 | Operator error | Load Reduction #24The boiler windbox door was found open after the outage. Droppe | Ghent | Derate | Coal | 3 | 2013 | 5 | 1.0333 | 0.32476 | 155.2362 | 150.2286 | 150
GH4 | D1 | 35 | 385 | 2013-05-14 05:13 | 2013-05-14 05:26 | 409 | 525 | 478 | Igniters | Load Reduction #25Ignitor oil trip valve would not open. | Ghent | Derate | Coal | 3 | 2013 | 5 | 0.21667 | 0.047873 | 22.8833 | 105.6152 | 106
GH4 | MO | 36 | 1000 | 2013-05-17 23:07 | 2013-05-18 16:32 | 0 | 525 | 478 | Waterwall (Furnace wall) A | F540Outage #10The unit was running with an external water wall tube leak on the bo | Ghent | Maintenance | Coal | 3 | 2013 | 5 | 17.4167 | 17.4167 | 8325.1667 | 478 | 478
GH4 | D1 | 37 | 590 | 2013-05-22 04:56 | 2013-05-22 05:45 | 340 | 525 | 478 | Desuperheater/attemperator valves | Load Reduction #26The upper west superheat spray valve would not open due to the s | Ghent | Derate | Coal | 3 | 2013 | 5 | 0.81667 | 0.28778 | 137.5578 | 168.4381 | 168
GH4 | D1 | 38 | 250 | 2013-06-25 11:33 | 2013-06-25 11:47 | 450 | 525 | 478 | Pulverizer feeders | Load Reduction #274-6 Feeder tripped due to pluggage. | Ghent | Derate | Coal | 3 | 2013 | 6 | 0.23333 | 0.033333 | 15.9333 | 68.2857 | 68
GH4 | D1 | 39 | 1455 | 2013-06-26 04:23 | 2013-06-26 06:38 | 190 | 525 | 478 | Induced draft fans | Load Reduction #284-2 ID fan tripped due to vibration probe failure. | Ghent | Derate | Coal | 3 | 2013 | 6 | 2.25 | 1.4357 | 686.2714 | 305.0095 | 305
GH4 | D1 | 40 | 1455 | 2013-06-27 10:20 | 2013-06-27 11:12 | 180 | 525 | 478 | Induced draft fans | Load Reduction #294-1 ID fan tripped due to stall warning during boiler upset. | Ghent | Derate | Coal | 3 | 2013 | 6 | 0.86667 | 0.56952 | 272.2324 | 314.1143 | 314
GH4 | U1 | 41 | 3245 | 2013-07-12 04:36 | 2013-07-19 16:11 | 0 | 525 | 478 | Other cooling tower problems | Outage #11Cooling tower south distribution line failed at cell #4-1. Removed the | Ghent | Outage | Coal | 3 | 2013 | 7 | 179.5833 | 179.5833 | 85840.8333 | 478 | 478
GH4 | PD | 42 | 1455 | 2013-07-27 06:00 | 2013-07-27 12:30 | 160 | 525 | 478 | Induced draft fans | F850Load Reduction #304-2 ID fan off to replace IB bearing. | Ghent | Derate | Coal | 3 | 2013 | 7 | 6.5 | 4.519 | 2160.1048 | 332.3238 | 332
GH4 | D1 | 43 | 1999 | 2013-08-07 09:15 | 2013-08-07 15:50 | 495 | 525 | 478 | Boiler | Load Reduction #31High boiler exist gas temperature. | Ghent | Derate | Coal | 3 | 2013 | 8 | 6.5833 | 0.37619 | 179.819 | 27.3143 | 27
GH4 | MO | 44 | 1040 | 2013-08-19 04:10 | 2013-08-19 18:06 | 0 | 525 | 478 | First superheater B | F540Outage #12A leak developed in the Low Temperature Superheater HRA on 8th floor | Ghent | Maintenance | Coal | 3 | 2013 | 8 | 13.9333 | 13.9333 | 6660.1333 | 478 | 478
GH4 | PO | 45 | 1812 | 2013-09-27 22:07 | 2013-10-11 15:27 | 0 | 525 | 478 | Boiler Inspections - scheduled or routine | F590Outage #13Unit 4 was removed from service to perform Planned Fall Outage maint | Ghent | Other | Coal | 3 | 2013 | 9 | 329.3333 | 329.3333 | 157421.3333 | 478 | 478
GH4 | D1 | 46 | 1850 | 2013-10-12 03:35 | 2013-10-12 04:25 | 470 | 525 | 478 | Boiler water condition (not feedwater water quality) | Load Reduction #32Boiler silica was high after unit start up causing pressure to b | Ghent | Derate | Coal | 3 | 2013 | 10 | 0.83333 | 0.087302 | 41.7302 | 50.0762 | 50
GH4 | D1 | 47 | 3211 | 2013-10-12 05:29 | 2013-10-14 03:42 | 490 | 525 | 478 | Circulating water pump motors | Load Reduction #334-1 Circulating water pump is out of service due to the motor be | Ghent | Derate | Coal | 3 | 2013 | 10 | 46.2167 | 3.0811 | 1472.7711 | 31.8667 | 32
GH4 | U1 | 48 | 1080 | 2013-10-14 03:42 | 2013-10-15 02:15 | 0 | 525 | 478 | Economizer B | Outage #14A tube leak was located in the Economizer section of the boiler. Remove | Ghent | Outage | Coal | 3 | 2013 | 10 | 22.55 | 22.55 | 10778.9 | 478 | 478
GH4 | SF | 49 | 9910 | 2013-10-15 02:15 | 2013-10-15 06:13 | 0 | 525 | 478 | Maintenance personnel error | F430Outage #15When starting up after the previous tube leak event, the Generator V | Ghent | Outage | Coal | 3 | 2013 | 10 | 3.9667 | 3.9667 | 1896.0667 | 478 | 478
GH4 | D1 | 50 | 3211 | 2013-10-15 11:20 | 2013-10-18 15:45 | 500 | 525 | 478 | Circulating water pump motors | Load Reduction #34Back pressure is running high due to 4-1 Circulating Water Pump | Ghent | Derate | Coal | 3 | 2013 | 10 | 76.4167 | 3.6389 | 1739.3889 | 22.7619 | 23
GH4 | D1 | 51 | 9650 | 2013-10-20 19:03 | 2013-10-20 21:30 | 370 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #35H2 SO4 problems. Dropped load to stay under limit. | Ghent | Derate | Coal | 3 | 2013 | 10 | 2.45 | 0.72333 | 345.7533 | 141.1238 | 141
GH4 | D1 | 52 | 1455 | 2013-11-01 00:53 | 2013-11-01 11:10 | 190 | 525 | 478 | Induced draft fans | Load Reduction #364-1 ID fan tripped due to high vibration. | Ghent | Derate | Coal | 3 | 2013 | 11 | 10.2833 | 6.5617 | 3136.5146 | 305.0095 | 305
GH4 | U1 | 53 | 9910 | 2013-11-05 14:09 | 2013-11-06 15:02 | 0 | 525 | 478 | Maintenance personnel error | Outage #16While wiring up the new reserve feed watt hour meter a current transform | Ghent | Outage | Coal | 3 | 2013 | 11 | 24.8833 | 24.8833 | 11894.2333 | 478 | 478
GH4 | D1 | 54 | 9650 | 2013-11-13 09:20 | 2013-11-13 13:10 | 474 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #37H2 SO4 problems. Dropped load to stay under limit. | Ghent | Derate | Coal | 3 | 2013 | 11 | 3.8333 | 0.37238 | 177.9981 | 46.4343 | 46
GH4 | D1 | 55 | 8551 | 2013-11-14 08:25 | 2013-11-15 03:00 | 200 | 525 | 478 | Electrostatic precipitator field out of service | Load Reduction #38Load was reduced when ash holding systems became full. | Ghent | Derate | Coal | 3 | 2013 | 11 | 18.5833 | 11.504 | 5498.8968 | 295.9048 | 296
GH4 | D1 | 56 | 9650 | 2013-11-15 11:46 | 2013-11-15 13:17 | 414 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #39H2 SO4 problems. Dropped load to stay under limit. | Ghent | Derate | Coal | 3 | 2013 | 11 | 1.5167 | 0.32067 | 153.2787 | 101.0629 | 101
GH4 | D1 | 57 | 8825 | 2013-11-20 05:52 | 2013-11-20 07:54 | 515 | 525 | 478 | Other SCR NOx problems | Load Reduction #40SCR inlet temperature limit. | Ghent | Derate | Coal | 3 | 2013 | 11 | 2.0333 | 0.03873 | 18.513 | 9.1048 | 9
GH4 | D1 | 58 | 9650 | 2013-12-04 15:30 | 2013-12-04 18:46 | 470 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #41H2S04 was running high. The unit is running 2 top mills due to | Ghent | Derate | Coal | 3 | 2013 | 12 | 3.2667 | 0.34222 | 163.5822 | 50.0762 | 50
GH4 | D1 | 59 | 340 | 2013-12-08 10:00 | 2013-12-08 11:37 | 500 | 525 | 478 | Other pulverizer problems | Load Reduction #424-4 Mill tripped, loss of flame. | Ghent | Derate | Coal | 3 | 2013 | 12 | 1.6167 | 0.076984 | 36.7984 | 22.7619 | 23
GH4 | MO | 60 | 1455 | 2013-12-20 00:04 | 2013-12-21 07:33 | 0 | 525 | 478 | Induced draft fans | F850Outage #17Unit 4 had been running with 4-2 ID fan vibration getting worse. Se | Ghent | Maintenance | Coal | 3 | 2013 | 12 | 31.4833 | 31.4833 | 15049.0333 | 478 | 478
GH4 | U1 | 61 | 3611 | 2013-12-21 07:34 | 2013-12-21 09:12 | 0 | 525 | 478 | Switchyard circuit breakers - external | Outage #18Unit 4 had just come on line from the previous event when it had mixed i | Ghent | Outage | Coal | 3 | 2013 | 12 | 1.6333 | 1.6333 | 780.7333 | 478 | 478
GH4 | D1 | 62 | 280 | 2013-12-25 21:58 | 2013-12-25 22:38 | 420 | 525 | 478 | Pulverizer fires | Load Reduction #43Load was reduced due to a fire in 4-4 mill. | Ghent | Derate | Coal | 3 | 2013 | 12 | 0.66667 | 0.13333 | 63.7333 | 95.6 | 96
GH4 | MO | 63 | 1000 | 2013-12-31 12:07 | 2014-01-01 | 0 | 525 | 478 | Waterwall (Furnace wall) A | F540Outage #19Unit 4 developed a tube leak on 8 2/3 floor on the south side of the | Ghent | Maintenance | Coal | 3 | 2013 | 12 | 11.8833 | 11.8833 | 5680.2333 | 478 | 478
GH4 | MO | 3 | 1000 | 2014-01-01 | 2014-01-01 00:53 | 0 | 525 | 478 | Waterwall (Furnace wall) A | F540Outage #1Unit 4 developed a tube leak on 8 2/3 floor on the south side of the | Ghent | Maintenance | Coal | 3 | 2014 | 1 | 0.88333 | 0.88333 | 422.2333 | 478 | 478
GH4 | D1 | 2 | 250 | 2014-01-07 03:55 | 2014-01-07 04:36 | 400 | 525 | 478 | Pulverizer feeders | Load Reduction #14-4 Feeder tripped. | Ghent | Derate | Coal | 3 | 2014 | 1 | 0.68333 | 0.1627 | 77.7698 | 113.8095 | 114
GH4 | D1 | 5 | 9650 | 2014-02-03 00:50 | 2014-02-03 01:48 | 400 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #3Reduced load to keep H2SO4 within limit. | Ghent | Derate | Coal | 3 | 2014 | 2 | 0.96667 | 0.23016 | 110.0159 | 113.8095 | 114
GH4 | PD | 6 | 3416 | 2014-02-08 23:00 | 2014-02-09 00:20 | 300 | 525 | 478 | Other feedwater pump problems | Load Reduction #4Planned derate to inspect 4-2 BFP leak. Derate was planned with | Ghent | Derate | Coal | 3 | 2014 | 2 | 1.3333 | 0.57143 | 273.1429 | 204.8571 | 205
GH4 | U1 | 7 | 250 | 2014-02-09 03:51 | 2014-02-09 05:38 | 0 | 525 | 478 | Pulverizer feeders | Outage #24-6 Mill Feeder coal inlet plugged causing controls to see this feeder as | Ghent | Outage | Coal | 3 | 2014 | 2 | 1.7833 | 1.7833 | 852.4333 | 478 | 478
GH4 | PD | 8 | 250 | 2014-02-25 03:58 | 2014-02-25 05:33 | 520 | 525 | 478 | Pulverizer feeders | Load Reduction #5Boiler exit gas was high due to both top mills being in service w | Ghent | Derate | Coal | 3 | 2014 | 2 | 1.5833 | 0.015079 | 7.2079 | 4.5524 | 5
GH4 | D1 | 9 | 9650 | 2014-03-05 17:35 | 2014-03-05 18:09 | 450 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #6Temporary lime silo plugged at mixer. | Ghent | Derate | Coal | 3 | 2014 | 3 | 0.56667 | 0.080952 | 38.6952 | 68.2857 | 68
GH4 | D1 | 10 | 9650 | 2014-03-05 20:48 | 2014-03-05 22:01 | 500 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #7Temporary lime silo plugged at mixer. | Ghent | Derate | Coal | 3 | 2014 | 3 | 1.2167 | 0.057937 | 27.6937 | 22.7619 | 23
GH4 | D1 | 11 | 3440 | 2014-03-24 08:44 | 2014-03-26 02:30 | 511 | 525 | 478 | High pressure heater tube leaks | Load Reduction #8HP heaters are out of service to repair a tube leak in 'G' HP hea | Ghent | Derate | Coal | 3 | 2014 | 3 | 41.7667 | 1.1138 | 532.3858 | 12.7467 | 13
GH4 | D1 | 12 | 4499 | 2014-03-26 06:30 | 2014-04-01 | 530 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #9Turbine performance due to copper deposition. | Ghent | Derate | Coal | 3 | 2014 | 3 | 137.5 | -1.3095 | -625.9524 | 0 | 0
GH4 | PD | 13 | 920 | 2014-04-01 23:12 | 2014-04-02 03:55 | 215 | 525 | 478 | Other slag and ash removal problems A | Load Reduction #10Needed to deslag the boiler, drum level deviation was excessive. | Ghent | Derate | Coal | 3 | 2014 | 4 | 4.7167 | 2.7851 | 1331.2679 | 282.2476 | 282
GH4 | PD | 14 | 1100 | 2014-04-10 23:00 | 2014-04-11 04:00 | 220 | 525 | 478 | Waterwall (Furnace wall) B | Load Reduction #11Boiler exist gas temps were high. Planned derate for deslag. | Ghent | Derate | Coal | 3 | 2014 | 4 | 5 | 2.9048 | 1388.4762 | 277.6952 | 278
GH4 | D1 | 15 | 1100 | 2014-04-19 06:02 | 2014-04-19 08:00 | 500 | 525 | 478 | Waterwall (Furnace wall) B | Load Reduction #12Boiler exit gas temps running high. Able to get back to 512 MW | Ghent | Derate | Coal | 3 | 2014 | 4 | 1.9667 | 0.093651 | 44.7651 | 22.7619 | 23
GH4 | PD | 16 | 1100 | 2014-04-19 23:40 | 2014-04-20 04:00 | 210 | 525 | 478 | Waterwall (Furnace wall) B | Load Reduction #13Boiler exit gas temps running high. Planned derate for deslag. | Ghent | Derate | Coal | 3 | 2014 | 4 | 4.3333 | 2.6 | 1242.8 | 286.8 | 287
GH4 | U1 | 17 | 1475 | 2014-04-21 21:22 | 2014-04-22 00:08 | 0 | 525 | 478 | Induced draft fan controls | Outage #3Unit 4 is running with furnace pressure control on only the 4-2 ID Fan du | Ghent | Outage | Coal | 3 | 2014 | 4 | 2.7667 | 2.7667 | 1322.4667 | 478 | 478
GH4 | D1 | 18 | 8200 | 2014-04-26 05:53 | 2014-04-26 09:40 | 409 | 525 | 478 | Piping A | Load Reduction #14FGD Limestone Slurry Header plugged. | Ghent | Derate | Coal | 3 | 2014 | 4 | 3.7833 | 0.83594 | 399.5777 | 105.6152 | 106
GH4 | D1 | 19 | 8200 | 2014-04-28 09:28 | 2014-04-28 11:57 | 240 | 525 | 478 | Piping A | Load Reduction #15FGD Limestone Slurry Header plugged. | Ghent | Derate | Coal | 3 | 2014 | 4 | 2.4833 | 1.3481 | 644.3895 | 259.4857 | 259
GH4 | D1 | 20 | 8200 | 2014-04-28 11:57 | 2014-04-28 12:36 | 225 | 525 | 478 | Piping A | Load Reduction #16FGD Limestone Slurry Header plugged. | Ghent | Derate | Coal | 3 | 2014 | 4 | 0.65 | 0.37143 | 177.5429 | 273.1429 | 273
GH4 | MO | 21 | 1493 | 2014-05-01 23:35 | 2014-05-05 08:20 | 0 | 525 | 478 | Air heater fouling (regenerative) | F590Outage #4The unit was running with multiple issues. Dispatch aligned a window | Ghent | Maintenance | Coal | 3 | 2014 | 5 | 80.75 | 80.75 | 38598.5 | 478 | 478
GH4 | ME | 22 | 1455 | 2014-05-05 08:20 | 2014-05-06 04:15 | 0 | 525 | 478 | Induced draft fans | F850Outage #5While firing the boiler from the previous event, it was noticed that | Ghent | Maintenance | Coal | 3 | 2014 | 5 | 19.9167 | 19.9167 | 9520.1667 | 478 | 478
GH4 | D1 | 23 | 1200 | 2014-05-07 07:00 | 2014-05-07 08:16 | 500 | 525 | 478 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | F830Load Reduction #17Dropped load to keep boiler exist gas under limit. | Ghent | Derate | Coal | 3 | 2014 | 5 | 1.2667 | 0.060317 | 28.8317 | 22.7619 | 23
GH4 | D1 | 24 | 920 | 2014-05-20 08:05 | 2014-05-20 14:37 | 500 | 525 | 478 | Other slag and ash removal problems A | Load Reduction #18Boiler exit gas temperatures were high so load was reduced. Agg | Ghent | Derate | Coal | 3 | 2014 | 5 | 6.5333 | 0.31111 | 148.7111 | 22.7619 | 23
GH4 | D1 | 25 | 1455 | 2014-05-25 20:30 | 2014-05-26 06:30 | 425 | 525 | 478 | Induced draft fans | Load Reduction #194-2 ID fan hydraulic leak was causing tank reservoir to need to | Ghent | Derate | Coal | 3 | 2014 | 5 | 10 | 1.9048 | 910.4762 | 91.0476 | 91
GH4 | MO | 26 | 1455 | 2014-05-31 00:18 | 2014-06-01 21:37 | 0 | 525 | 478 | Induced draft fans | F540Outage #6Unit 4 was running with 4-2 ID Fan hydraulic leak on the blade pitch | Ghent | Maintenance | Coal | 3 | 2014 | 5 | 45.3167 | 45.3167 | 21661.3667 | 478 | 478
GH4 | D1 | 27 | 9650 | 2014-06-07 14:34 | 2014-06-07 18:05 | 279 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #20SO3 Mitigation Instrument Air Compressor failed causing loss of | Ghent | Derate | Coal | 3 | 2014 | 6 | 3.5167 | 1.6478 | 787.653 | 223.9771 | 224
GH4 | D1 | 28 | 9650 | 2014-06-16 15:34 | 2014-06-16 18:41 | 300 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #21U4 H2SO4 was high. Electrical feed tripped out and Dry Sorbent | Ghent | Derate | Coal | 3 | 2014 | 6 | 3.1167 | 1.3357 | 638.4714 | 204.8571 | 205
GH4 | D1 | 29 | 280 | 2014-06-26 08:20 | 2014-06-26 08:52 | 450 | 525 | 478 | Pulverizer fires | Load Reduction #224-4 Mill fire in pyrite section. | Ghent | Derate | Coal | 3 | 2014 | 6 | 0.53333 | 0.07619 | 36.419 | 68.2857 | 68
GH4 | D1 | 30 | 1160 | 2014-07-01 04:32 | 2014-07-01 05:10 | 500 | 525 | 478 | First reheater B | Load Reduction #23High boiler exit gas temperature. | Ghent | Derate | Coal | 3 | 2014 | 7 | 0.63333 | 0.030159 | 14.4159 | 22.7619 | 23
GH4 | D1 | 31 | 1160 | 2014-07-01 05:10 | 2014-07-01 07:20 | 507 | 525 | 478 | First reheater B | Load Reduction #24Boiler exist gas was high. Ran RH steam temperature lower to co | Ghent | Derate | Coal | 3 | 2014 | 7 | 2.1667 | 0.074286 | 35.5086 | 16.3886 | 16
GH4 | D1 | 32 | 9650 | 2014-07-12 17:30 | 2014-07-12 18:15 | 390 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #25H2SO4 temporary injection (SCR outlet) plugged. Dropped load to | Ghent | Derate | Coal | 3 | 2014 | 7 | 0.75 | 0.19286 | 92.1857 | 122.9143 | 123
GH4 | D1 | 33 | 9650 | 2014-07-12 18:15 | 2014-07-12 20:24 | 310 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #26H2SO4 temporary injection (SCR outlet) plugged. Dropped load to | Ghent | Derate | Coal | 3 | 2014 | 7 | 2.15 | 0.88048 | 420.8676 | 195.7524 | 196
GH4 | MO | 34 | 8160 | 2014-07-18 23:19 | 2014-07-21 06:34 | 0 | 525 | 478 | Mist eliminators/demisters and washdown | F120Outage #7FGD Absorber Tower Mist Eliminators showing high differential. Remov | Ghent | Maintenance | Coal | 3 | 2014 | 7 | 55.25 | 55.25 | 26409.5 | 478 | 478
GH4 | D1 | 35 | 250 | 2014-07-22 10:21 | 2014-07-22 11:02 | 450 | 525 | 478 | Pulverizer feeders | Load Reduction #274-3 Feeder plugged between feeder gate and feeder. | Ghent | Derate | Coal | 3 | 2014 | 7 | 0.68333 | 0.097619 | 46.6619 | 68.2857 | 68
GH4 | PD | 36 | 3682 | 2014-07-29 05:00 | 2014-07-29 16:44 | 333 | 525 | 478 | Other voltage system conductors and buses | Load Reduction #28Unit 4 was limited due to North Bus outage to tie in for the new | Ghent | Derate | Coal | 3 | 2014 | 7 | 11.7333 | 4.291 | 2051.1208 | 174.8114 | 175
GH4 | D1 | 37 | 280 | 2014-08-02 17:34 | 2014-08-02 18:39 | 430 | 525 | 478 | Pulverizer fires | Load Reduction #29A fire in 4-4 Mill damaged the 'D' burner line. The unit was de | Ghent | Derate | Coal | 3 | 2014 | 8 | 1.0833 | 0.19603 | 93.7032 | 86.4952 | 86
GH4 | D1 | 38 | 320 | 2014-08-06 14:20 | 2014-08-06 16:59 | 410 | 525 | 478 | Foreign object in Pulverizers mill | Load Reduction #304-5 Mill had metal in grinding section causing poor performance | Ghent | Derate | Coal | 3 | 2014 | 8 | 2.65 | 0.58048 | 277.4676 | 104.7048 | 105
GH4 | D1 | 39 | 1160 | 2014-08-10 18:47 | 2014-08-10 22:30 | 495 | 525 | 478 | First reheater B | Load Reduction #31Dropped load to keep boiler exit gas temp within limit. | Ghent | Derate | Coal | 3 | 2014 | 8 | 3.7167 | 0.21238 | 101.5181 | 27.3143 | 27
GH4 | D1 | 40 | 9650 | 2014-08-11 19:54 | 2014-08-12 00:55 | 495 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #32Unit 4 was being limited due to H2SO4 monitor being out of servi | Ghent | Derate | Coal | 3 | 2014 | 8 | 5.0167 | 0.28667 | 137.0267 | 27.3143 | 27
GH4 | D1 | 41 | 9650 | 2014-08-12 05:17 | 2014-08-12 05:59 | 495 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #33Unit 4 was limited due to H2SO4 monitor being out of service and | Ghent | Derate | Coal | 3 | 2014 | 8 | 0.7 | 0.04 | 19.12 | 27.3143 | 27
GH4 | D1 | 42 | 9650 | 2014-08-12 05:59 | 2014-08-12 10:37 | 445 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #34Unit 4 was limited due to H2SO4 monitor being out of service and | Ghent | Derate | Coal | 3 | 2014 | 8 | 4.6333 | 0.70603 | 337.4832 | 72.8381 | 73
GH4 | D1 | 43 | 1455 | 2014-08-20 01:44 | 2014-08-20 04:20 | 200 | 525 | 478 | Induced draft fans | Load Reduction #354-1 ID fan tripped. OB fan vibration transducer failed. | Ghent | Derate | Coal | 3 | 2014 | 8 | 2.6 | 1.6095 | 769.3524 | 295.9048 | 296
GH4 | D1 | 44 | 1599 | 2014-08-22 09:46 | 2014-08-22 23:21 | 505 | 525 | 478 | Other miscellaneous boiler air and gas system problems | Load Reduction #36High boiler exit gas temperature. | Ghent | Derate | Coal | 3 | 2014 | 8 | 13.5833 | 0.51746 | 247.346 | 18.2095 | 18
GH4 | D1 | 45 | 3631 | 2014-08-22 18:03 | 2014-08-22 18:24 | 450 | 525 | 478 | 480-volt circuit breakers | Load Reduction #374-2A auxiliary condensate pump tripped due to breaker issues. | Ghent | Derate | Coal | 3 | 2014 | 8 | 0.35 | 0.05 | 23.9 | 68.2857 | 68
GH4 | MO | 46 | 8160 | 2014-08-22 23:21 | 2014-08-25 01:01 | 0 | 525 | 478 | Mist eliminators/demisters and washdown | F120Outage #8Unit 4 had been running with differential across the FGD Mist Elimina | Ghent | Maintenance | Coal | 3 | 2014 | 8 | 49.6667 | 49.6667 | 23740.6667 | 478 | 478
GH4 | U1 | 47 | 1000 | 2014-08-25 10:14 | 2014-08-26 07:28 | 0 | 525 | 478 | Waterwall (Furnace wall) A | Outage #9Water wall tube blew out in boiler causing furnace to trip on high furnac | Ghent | Outage | Coal | 3 | 2014 | 8 | 21.2333 | 21.2333 | 10149.5333 | 478 | 478
GH4 | U1 | 48 | 1599 | 2014-08-26 09:53 | 2014-08-26 11:00 | 0 | 525 | 478 | Other miscellaneous boiler air and gas system problems | Outage #10While starting 4-4 mill soon after Unit 4 start up, a furnace pressure e | Ghent | Outage | Coal | 3 | 2014 | 8 | 1.1167 | 1.1167 | 533.7667 | 478 | 478
GH4 | U1 | 49 | 1000 | 2014-08-27 08:34 | 2014-08-29 21:18 | 0 | 525 | 478 | Waterwall (Furnace wall) A | Outage #11A water wall tube leak ruptured causing the furnace to trip on high furn | Ghent | Outage | Coal | 3 | 2014 | 8 | 60.7333 | 60.7333 | 29030.5333 | 478 | 478
GH4 | U1 | 50 | 3110 | 2014-09-04 17:31 | 2014-09-05 16:20 | 0 | 525 | 478 | Condenser tube leaks | F540Outage #12Conditions started showing signs of a bad Condenser tube leak. Remo | Ghent | Outage | Coal | 3 | 2014 | 9 | 22.8167 | 22.8167 | 10906.3667 | 478 | 478
GH4 | MO | 51 | 1050 | 2014-09-05 16:20 | 2014-09-06 15:59 | 0 | 525 | 478 | Second superheater B | F380Outage #13The unit had been running with a Superheat tube leak, but the unit w | Ghent | Maintenance | Coal | 3 | 2014 | 9 | 23.65 | 23.65 | 11304.7 | 478 | 478
GH4 | D1 | 52 | 3110 | 2014-09-07 07:25 | 2014-09-09 22:45 | 368 | 525 | 478 | Condenser tube leaks | Load Reduction #38U4 Derated due to high boiler drum silica after a Condenser CW t | Ghent | Derate | Coal | 3 | 2014 | 9 | 63.3333 | 18.9397 | 9053.1683 | 142.9448 | 143
GH4 | PD | 53 | 3110 | 2014-09-11 23:00 | 2014-09-12 05:47 | 290 | 525 | 478 | Condenser tube leaks | Load Reduction #39Unit 4 was derated due to a suspected condenser tube leak in the | Ghent | Derate | Coal | 3 | 2014 | 9 | 6.7833 | 3.0363 | 1451.3749 | 213.9619 | 214
GH4 | U1 | 54 | 9900 | 2014-09-12 05:47 | 2014-09-12 06:00 | 0 | 525 | 478 | Operator error | Outage #14Unit 4 was running with a suspected condenser tube leak in 4-2 auxiliary | Ghent | Outage | Coal | 3 | 2014 | 9 | 0.21667 | 0.21667 | 103.5667 | 478 | 478
GH4 | MO | 56 | 3110 | 2014-09-12 06:00 | 2014-09-12 19:39 | 0 | 525 | 478 | Condenser tube leaks | Outage #15Unit 4 tripped with a suspected condenser tube leak in 4-2 Auxiliary Con | Ghent | Maintenance | Coal | 3 | 2014 | 9 | 13.65 | 13.65 | 6524.7 | 478 | 478
GH4 | D1 | 57 | 1850 | 2014-09-13 08:26 | 2014-09-13 14:57 | 469 | 525 | 478 | Boiler water condition (not feedwater water quality) | Load Reduction #40Unit 4 was derated due to high boiler drum silica after the unit | Ghent | Derate | Coal | 3 | 2014 | 9 | 6.5167 | 0.69511 | 332.2631 | 50.9867 | 51
GH4 | D1 | 58 | 8817 | 2014-09-20 15:38 | 2014-09-20 19:04 | 344 | 525 | 478 | SCR NOx Control system | Load Reduction #41H2SO4 temporary injection (SCR Outlet) OOS. Equipment shut down | Ghent | Derate | Coal | 3 | 2014 | 9 | 3.4333 | 1.1837 | 565.8003 | 164.7962 | 165
GH4 | D1 | 59 | 4499 | 2014-10-01 10:48 | 2014-10-07 10:13 | 511 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #42Turbine degradation due to copper deposits. | Ghent | Derate | Coal | 3 | 2014 | 10 | 143.4167 | 3.8244 | 1828.0844 | 12.7467 | 13
GH4 | D1 | 60 | 4499 | 2014-10-07 10:13 | 2014-10-10 23:45 | 505 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #43Load reduced due to turbine degradation. | Ghent | Derate | Coal | 3 | 2014 | 10 | 85.5333 | 3.2584 | 1557.5213 | 18.2095 | 18
GH4 | PO | 61 | 4400 | 2014-10-10 23:45 | 2014-12-05 01:33 | 0 | 525 | 478 | Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | F590Outage #16Unit 4 came off line on a Planned Fall Outage. Outage work includes | Ghent | Other | Coal | 3 | 2014 | 10 | 1321.8 | 1321.8 | 631820.4 | 478 | 478
GH4 | U1 | 62 | 4470 | 2014-12-05 01:44 | 2014-12-05 06:51 | 0 | 525 | 478 | Differential expansion | Outage #17After start up of U4 after major overhaul on the turbine, the turbine wa | Ghent | Outage | Coal | 3 | 2014 | 12 | 5.1167 | 5.1167 | 2445.7667 | 478 | 478
GH4 | U1 | 63 | 4470 | 2014-12-05 07:31 | 2014-12-05 12:18 | 0 | 525 | 478 | Differential expansion | Outage #18After start up of U4 after major overhaul on the turbine, the turbine wa | Ghent | Outage | Coal | 3 | 2014 | 12 | 4.7833 | 4.7833 | 2286.4333 | 478 | 478
GH4 | U1 | 64 | 4470 | 2014-12-05 13:04 | 2014-12-05 14:06 | 0 | 525 | 478 | Differential expansion | Outage #19After start up of U4 after major overhaul on the turbine, the turbine wa | Ghent | Outage | Coal | 3 | 2014 | 12 | 1.0333 | 1.0333 | 493.9333 | 478 | 478
GH4 | D1 | 65 | 1850 | 2014-12-06 14:06 | 2014-12-07 15:18 | 441 | 525 | 478 | Boiler water condition (not feedwater water quality) | Load Reduction #44High boiler drum silica on start up after Fall Outage. | Ghent | Derate | Coal | 3 | 2014 | 12 | 25.2 | 4.032 | 1927.296 | 76.48 | 76
GH4 | U1 | 66 | 3431 | 2014-12-07 15:18 | 2014-12-08 09:46 | 0 | 525 | 478 | Other feedwater valves | Outage #20Packing blew out on the flue economizer inlet valve causing a tremendous | Ghent | Outage | Coal | 3 | 2014 | 12 | 18.4667 | 18.4667 | 8827.0667 | 478 | 478
GH4 | D1 | 67 | 3410 | 2014-12-08 17:46 | 2014-12-08 21:10 | 270 | 525 | 478 | Feedwater pump | Load Reduction #45Unit runback and 4-1 and 4-5 mills tripped after 4-2 BFPT trippe | Ghent | Derate | Coal | 3 | 2014 | 12 | 3.4 | 1.6514 | 789.3829 | 232.1714 | 232
GH4 | D1 | 68 | 1850 | 2014-12-08 21:10 | 2014-12-09 07:10 | 482 | 525 | 478 | Boiler water condition (not feedwater water quality) | Load Reduction #46Boiler drum silica was high on start up after Fall Outage. | Ghent | Derate | Coal | 3 | 2014 | 12 | 10 | 0.81905 | 391.5048 | 39.1505 | 39
GH4 | D1 | 69 | 3341 | 2014-12-09 18:05 | 2014-12-09 20:55 | 460 | 525 | 478 | Other LP heater - general | Load Reduction #47Low pressure heater extractions tripped. 'C' heater normal drai | Ghent | Derate | Coal | 3 | 2014 | 12 | 2.8333 | 0.35079 | 167.6794 | 59.181 | 59
GH4 | D1 | 72 | 1455 | 2014-12-09 20:55 | 2014-12-10 09:35 | 500 | 525 | 478 | Induced draft fans | Load Reduction #484-2 FD fan inlet vane control card failed. 4-2 FD fan inlet won | Ghent | Derate | Coal | 3 | 2014 | 12 | 12.6667 | 0.60317 | 288.3175 | 22.7619 | 23
GH4 | U1 | 71 | 1470 | 2014-12-10 09:35 | 2014-12-10 12:36 | 0 | 525 | 478 | Induced draft fan motors and drives | Outage #21U4 Boiler tripped on low furnace pressure while working on 4-2 FD fan in | Ghent | Outage | Coal | 3 | 2014 | 12 | 3.0167 | 3.0167 | 1441.9667 | 478 | 478
GH4 | D1 | 73 | 1850 | 2014-12-10 19:10 | 2014-12-11 06:55 | 492 | 525 | 478 | Boiler water condition (not feedwater water quality) | Load Reduction #49High boiler drum silica on start up after Fall Outage. | Ghent | Derate | Coal | 3 | 2014 | 12 | 11.75 | 0.73857 | 353.0371 | 30.0457 | 30
GH4 | D1 | 74 | 1475 | 2014-12-11 06:55 | 2014-12-11 12:15 | 500 | 525 | 478 | Induced draft fan controls | Load Reduction #50FD fan master was indicating 100%. | Ghent | Derate | Coal | 3 | 2014 | 12 | 5.3333 | 0.25397 | 121.3968 | 22.7619 | 23
GH4 | D1 | 75 | 3441 | 2014-12-11 12:15 | 2014-12-12 22:04 | 511 | 525 | 478 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | Load Reduction #51HP Heaters are out of service for level control investigation. | Ghent | Derate | Coal | 3 | 2014 | 12 | 33.8167 | 0.90178 | 431.0498 | 12.7467 | 13
GH4 | U1 | 76 | 1455 | 2014-12-12 23:03 | 2014-12-13 04:14 | 0 | 525 | 478 | Induced draft fans | Outage #22U4 Boiler tripped on "Low Furnace Pressure" when the 4-2A and 4-2B ID fa | Ghent | Outage | Coal | 3 | 2014 | 12 | 5.1833 | 5.1833 | 2477.6333 | 478 | 478
GH4 | PD | 77 | 3644 | 2014-12-14 07:21 | 2014-12-14 13:19 | 500 | 525 | 478 | AC Protection devices | Load Reduction #52Unit 4 was requested to stay at a steady state load while reserv | Ghent | Derate | Coal | 3 | 2014 | 12 | 5.9667 | 0.28413 | 135.8127 | 22.7619 | 23
GH4 | D1 | 78 | 3441 | 2014-12-15 16:47 | 2014-12-16 06:08 | 511 | 525 | 478 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | Load Reduction #53U4 HP heaters were out of service for level control investigatio | Ghent | Derate | Coal | 3 | 2014 | 12 | 13.35 | 0.356 | 170.168 | 12.7467 | 13
GH4 | MO | 79 | 4260 | 2014-12-23 10:30 | 2014-12-26 19:24 | 0 | 525 | 478 | Main stop valves | F590Outage #23Scheduled Unit 4 to come off line to repair several items on the uni | Ghent | Maintenance | Coal | 3 | 2014 | 12 | 80.9 | 80.9 | 38670.2 | 478 | 478
GH4 | D1 | 80 | 3441 | 2014-12-29 09:05 | 2014-12-29 11:18 | 490 | 525 | 478 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | Load Reduction #54HP Heaters were out of service for level control investigation. | Ghent | Derate | Coal | 3 | 2014 | 12 | 2.2167 | 0.14778 | 70.6378 | 31.8667 | 32
GH4 | D1 | 81 | 270 | 2014-12-30 05:36 | 2014-12-30 06:02 | 420 | 525 | 478 | Primary air duct and dampers | Load Reduction #554-2 Coal Feeder would not start on load increase. PA flow was > | Ghent | Derate | Coal | 3 | 2014 | 12 | 0.43333 | 0.086667 | 41.4267 | 95.6 | 96
GH4 | D1 | 82 | 9650 | 2014-12-31 09:04 | 2014-12-31 11:35 | 280 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #56Sorbent Inject Silo Loss in Weight hoppers plugged. Dropped loa | Ghent | Derate | Coal | 3 | 2014 | 12 | 2.5167 | 1.1744 | 561.3844 | 223.0667 | 223
GH4 | D1 | 1 | 9650 | 2015-01-16 03:50 | 2015-01-16 06:26 | 350 | 525 | 478 | Other stack or exhaust emissions (fossil) | Load Reduction #1Sorbent injection system to SCR Outlet ducts plugged, dropped load | Ghent | Derate | Coal | 3 | 2015 | 1 | 2.6 | 0.86667 | 414.2667 | 159.3333 | 159
GH4 | PD | 2 | 410 | 2015-01-22 21:37 | 2015-01-23 05:00 | 210 | 525 | 478 | Other burner problems | Load Reduction #2Derated unit to deslag U4 burner eyebrows. Thompson to water bla | Ghent | Derate | Coal | 3 | 2015 | 1 | 7.3833 | 4.43 | 2117.54 | 286.8 | 287
GH4 | MO | 3 | 3110 | 2015-01-24 13:21 | 2015-01-25 18:00 | 0 | 525 | 478 | Condenser tube leaks | Outage #1Unit 4 was showing signs of a Condenser tube leak. Removed the unit from | Ghent | Maintenance | Coal | 3 | 2015 | 1 | 28.65 | 28.65 | 13694.7 | 478 | 478
GH4 | U1 | 4 | 1310 | 2015-01-25 18:00 | 2015-01-27 00:22 | 0 | 525 | 478 | Water side cleaning (acid cleaning) | Outage #2While filling the boiler for startup from the previous Maintenance event, | Ghent | Outage | Coal | 3 | 2015 | 1 | 30.3667 | 30.3667 | 14515.2667 | 478 | 478
GH4 | U1 | 5 | 1475 | 2015-01-27 02:39 | 2015-01-27 04:11 | 0 | 525 | 478 | Induced draft fan controls | Outage #3After Unit 4 had just come back on line and while placing mills in servic | Ghent | Outage | Coal | 3 | 2015 | 1 | 1.5333 | 1.5333 | 732.9333 | 478 | 478
GH4 | U1 | 6 | 1080 | 2015-02-04 11:39 | 2015-02-05 12:57 | 0 | 525 | 478 | Economizer B | F540Outage #4Boiler developed leak in Economizer section of the boiler. Removed u | Ghent | Outage | Coal | 3 | 2015 | 2 | 25.3 | 25.3 | 12093.4 | 478 | 478
GH4 | PD | 7 | 410 | 2015-02-11 22:00 | 2015-02-12 03:22 | 200 | 525 | 478 | Other burner problems | Load Reduction #3Need to deslag U4. 4-3 & 4-5 Burners have large eyebrows. Thomps | Ghent | Derate | Coal | 3 | 2015 | 2 | 5.3667 | 3.3222 | 1588.0222 | 295.9048 | 296
GH4 | PD | 8 | 410 | 2015-02-12 21:30 | 2015-02-13 00:05 | 300 | 525 | 478 | Other burner problems | Load Reduction #4Need to deslag U4. 4-3 & 4-5 Burners have large eyebrows. Thomps | Ghent | Derate | Coal | 3 | 2015 | 2 | 2.5833 | 1.1071 | 529.2143 | 204.8571 | 205
GH4 | PD | 9 | 1100 | 2015-03-02 22:57 | 2015-03-03 04:04 | 200 | 525 | 478 | Waterwall (Furnace wall) B | FS00Load Reduction #5Dropped load to deslag boiler due to SH stem temperatures sag | Ghent | Derate | Coal | 3 | 2015 | 3 | 5.1167 | 3.1675 | 1514.046 | 295.9048 | 296
GH4 | PD | 10 | 8813 | 2015-03-08 11:00 | 2015-03-08 17:23 | 200 | 525 | 478 | SCR NOx Injection grid piping/valves | Load Reduction #6KBR installed new sorbent injection lines and valves. | Ghent | Derate | Coal | 3 | 2015 | 3 | 6.3833 | 3.9516 | 1888.8587 | 295.9048 | 296
GH4 | D1 | 11 | 8813 | 2015-03-08 17:23 | 2015-03-08 19:40 | 200 | 525 | 478 | SCR NOx Injection grid piping/valves | Load Reduction #7Kept load reduced to 200 MW to keep H2S04 within limit after sorb | Ghent | Derate | Coal | 3 | 2015 | 3 | 2.2833 | 1.4135 | 675.6492 | 295.9048 | 296
GH4 | D1 | 12 | 8813 | 2015-03-08 19:40 | 2015-03-08 21:31 | 480 | 525 | 478 | SCR NOx Injection grid piping/valves | Load Reduction #8Unit was unable to make full load after sorbent injection mainten | Ghent | Derate | Coal | 3 | 2015 | 3 | 1.85 | 0.15857 | 75.7971 | 40.9714 | 41
GH4 | D1 | 13 | 9270 | 2015-03-16 03:20 | 2015-03-16 03:48 | 440 | 525 | 478 | Wet coal | Load Reduction #9Boiler upset due to wet coal. Mill ran back on loss of flame. | Ghent | Derate | Coal | 3 | 2015 | 3 | 0.46667 | 0.075556 | 36.1156 | 77.3905 | 77
GH4 | PD | 14 | 1100 | 2015-03-22 | 2015-03-22 04:15 | 210 | 525 | 478 | Waterwall (Furnace wall) B | Load Reduction #10Boiler deslag. | Ghent | Derate | Coal | 3 | 2015 | 3 | 4.25 | 2.55 | 1218.9 | 286.8 | 287
GH4 | D1 | 15 | 3110 | 2015-03-23 05:09 | 2015-03-23 08:41 | 440 | 525 | 478 | Condenser tube leaks | Load Reduction #11Condenser CW leak; variable load according to silica \ drum pres | Ghent | Derate | Coal | 3 | 2015 | 3 | 3.5333 | 0.57206 | 273.4463 | 77.3905 | 77
GH4 | U1 | 16 | 3110 | 2015-03-23 08:41 | 2015-03-24 15:30 | 0 | 525 | 478 | Condenser tube leaks | Outage #5Unit 4 was experiencing signs of a bad condenser leak. Removed the unit | Ghent | Outage | Coal | 3 | 2015 | 3 | 30.8167 | 30.8167 | 14730.3667 | 478 | 478
GH4 | D1 | 17 | 1850 | 2015-03-24 23:46 | 2015-03-25 06:41 | 450 | 525 | 478 | Boiler water condition (not feedwater water quality) | Load Reduction #12Unit start up after outage to repair a condenser tube leak; Var | Ghent | Derate | Coal | 3 | 2015 | 3 | 6.9167 | 0.9881 | 472.3095 | 68.2857 | 68
GH4 | D1 | 18 | 1512 | 2015-03-25 06:41 | 2015-03-25 13:37 | 500 | 525 | 478 | Flue gas expansion joints | Load Reduction #13Unable to make full load due to ID fan VFD amp limitations due t | Ghent | Derate | Coal | 3 | 2015 | 3 | 6.9333 | 0.33016 | 157.8159 | 22.7619 | 23
GH4 | D1 | 19 | 1512 | 2015-03-25 13:37 | 2015-03-25 15:21 | 200 | 525 | 478 | Flue gas expansion joints | Load Reduction #14Unable to make full load due to ID fan VFD amp limitations due t | Ghent | Derate | Coal | 3 | 2015 | 3 | 1.7333 | 1.073 | 512.9016 | 295.9048 | 296
GH4 | PD | 20 | 1100 | 2015-04-12 22:00 | 2015-04-13 02:07 | 200 | 525 | 478 | Waterwall (Furnace wall) B | Load Reduction #15Load Reduced to deslag the boiler. | Ghent | Derate | Coal | 3 | 2015 | 4 | 4.1167 | 2.5484 | 1218.1413 | 295.9048 | 296
GH4 | D1 | 21 | 1850 | 2015-04-13 23:44 | 2015-04-14 09:59 | 447 | 525 | 478 | Boiler water condition (not feedwater water quality) | Load Reduction #16Suspected condenser CW leak. Variable load according to silica/ | Ghent | Derate | Coal | 3 | 2015 | 4 | 10.25 | 1.5229 | 727.9257 | 71.0171 | 71
GH4 | MO | 22 | 1488 | 2015-04-24 23:00 | 2015-05-01 03:28 | 0 | 525 | 478 | Air heater (regenerative) | F060Outage #6Air Heater seals were leaking badly causing large swings in the furna | Ghent | Maintenance | Coal | 3 | 2015 | 4 | 148.4667 | 148.4667 | 70967.0667 | 478 | 478
GH4 | D1 | 23 | 1850 | 2015-05-01 11:50 | 2015-05-01 18:16 | 441 | 525 | 478 | Boiler water condition (not feedwater water quality) | Load Reduction #17Boiler drum silica was high after air heater seal outage. Varia | Ghent | Derate | Coal | 3 | 2015 | 5 | 6.4333 | 1.0293 | 492.0213 | 76.48 | 76
GH4 | PD | 24 | 8601 | 2015-05-12 23:00 | 2015-05-13 02:52 | 450 | 525 | 478 | SO3 mitigation | F790Load Reduction #18Mid-load SAM test. | Ghent | Derate | Coal | 3 | 2015 | 5 | 3.8667 | 0.55238 | 264.0381 | 68.2857 | 68
GH4 | D1 | 25 | 1470 | 2015-05-13 07:56 | 2015-05-13 10:12 | 486 | 525 | 478 | Induced draft fan motors and drives | Load Reduction #194-1A ID Fan VFD tripped when drive controls lost communication w | Ghent | Derate | Coal | 3 | 2015 | 5 | 2.2667 | 0.16838 | 80.4861 | 35.5086 | 36
GH4 | PD | 26 | 8601 | 2015-05-13 23:00 | 2015-05-14 02:45 | 375 | 525 | 478 | SO3 mitigation | F790Load Reduction #20Low-load SAM test. | Ghent | Derate | Coal | 3 | 2015 | 5 | 3.75 | 1.0714 | 512.1429 | 136.5714 | 137
GH4 | D1 | 27 | 1470 | 2015-06-12 21:30 | 2015-06-13 02:25 | 310 | 525 | 478 | Induced draft fan motors and drives | Load Reduction #214-2A, then 4-1B ID fan VFDs tripped when drive controls faulted | Ghent | Derate | Coal | 3 | 2015 | 6 | 4.9167 | 2.0135 | 962.4492 | 195.7524 | 196
GH4 | PD | 28 | 1470 | 2015-06-26 00:58 | 2015-06-26 01:16 | 305 | 525 | 478 | Induced draft fan motors and drives | Load Reduction #224-1B ID fan off to reset the bypassed cell in the VFD. | Ghent | Derate | Coal | 3 | 2015 | 6 | 0.3 | 0.12571 | 60.0914 | 200.3048 | 200
GH4 | U1 | 29 | 4302 | 2015-07-03 01:12 | 2015-07-03 05:09 | 0 | 525 | 478 | Turbine trip devices (including instruments) | Outage #7Main Turbine thrust bearing showed movement about the trip point tripping | Ghent | Outage | Coal | 3 | 2015 | 7 | 3.95 | 3.95 | 1888.1 | 478 | 478
GH4 | PD | 30 | 1512 | 2015-07-06 23:00 | 2015-07-06 23:30 | 200 | 525 | 478 | Flue gas expansion joints | Load Reduction #23Dropped load for 4-1 AH outlet duct expansion joint repair. | Ghent | Derate | Coal | 3 | 2015 | 7 | 0.5 | 0.30952 | 147.9524 | 295.9048 | 296
GH4 | D1 | 31 | 1455 | 2015-07-07 09:36 | 2015-07-07 09:53 | 500 | 525 | 478 | Induced draft fans | Load Reduction #24Boiler swing. FD fans out the top, and furnace pressure was get | Ghent | Derate | Coal | 3 | 2015 | 7 | 0.28333 | 0.013492 | 6.4492 | 22.7619 | 23
GH4 | D1 | 32 | 1470 | 2015-07-07 10:28 | 2015-07-07 11:18 | 480 | 525 | 478 | Induced draft fan motors and drives | Load Reduction #25Dropped load to swap out mills. FD fans were running out the to | Ghent | Derate | Coal | 3 | 2015 | 7 | 0.83333 | 0.071429 | 34.1429 | 40.9714 | 41
GH4 | D1 | 33 | 1470 | 2015-07-10 13:07 | 2015-07-10 19:43 | 450 | 525 | 478 | Induced draft fan motors and drives | Load Reduction #264-1A ID fan VFD developed a coolant leak in the transformer. | Ghent | Derate | Coal | 3 | 2015 | 7 | 6.6 | 0.94286 | 450.6857 | 68.2857 | 68
GH4 | MO | 34 | 1493 | 2015-08-05 23:19 | 2015-08-08 00:15 | 0 | 525 | 478 | Air heater fouling (regenerative) | F540Outage #8Air Heater seals continuing to get worse. Removed unit from service | Ghent | Maintenance | Coal | 3 | 2015 | 8 | 48.9333 | 48.9333 | 23390.1333 | 478 | 478
GH4 | D1 | 35 | 1850 | 2015-08-08 08:28 | 2015-08-08 09:55 | 450 | 525 | 478 | Boiler water condition (not feedwater water quality) | Load Reduction #27Unit start up after outage to repair air heater seals: Variable | Ghent | Derate | Coal | 3 | 2015 | 8 | 1.45 | 0.20714 | 99.0143 | 68.2857 | 68
GH4 | D1 | 36 | 1850 | 2015-08-08 09:55 | 2015-08-08 12:43 | 480 | 525 | 478 | Boiler water condition (not feedwater water quality) | Load Reduction #28Unit start up after outage to repair air heater seals: Variable | Ghent | Derate | Coal | 3 | 2015 | 8 | 2.8 | 0.24 | 114.72 | 40.9714 | 41
GH4 | U1 | 37 | 3430 | 2015-08-14 13:47 | 2015-08-14 15:08 | 0 | 525 | 478 | Feedwater regulating (boiler level control) valve | Outage #9Adjustments were being made to HP heater level controls and the HP heater | Ghent | Outage | Coal | 3 | 2015 | 8 | 1.35 | 1.35 | 645.3 | 478 | 478
GH4 | D1 | 38 | 3441 | 2015-08-28 15:28 | 2015-08-28 15:55 | 490 | 525 | 478 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | Load Reduction #29Boiler excursion due to putting HP heater extraction steam in se | Ghent | Derate | Coal | 3 | 2015 | 8 | 0.45 | 0.03 | 14.34 | 31.8667 | 32
GH4 | D1 | 39 | 3441 | 2015-08-29 12:25 | 2015-08-29 13:07 | 490 | 525 | 478 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | Load Reduction #30Boiler excursion due to HP heaters tripping. | Ghent | Derate | Coal | 3 | 2015 | 8 | 0.7 | 0.046667 | 22.3067 | 31.8667 | 32
GH4 | D1 | 40 | 9900 | 2015-09-05 23:59 | 2015-09-06 01:47 | 113 | 525 | 478 | Operator error | Load Reduction #31Boiler tripped; feeders went <40% during load drop. Derate was | Ghent | Derate | Coal | 3 | 2015 | 9 | 1.8 | 1.4126 | 675.2091 | 375.1162 | 375
GH4 | D1 | 42 | 4499 | 2015-10-01 13:17 | 2015-10-24 08:21 | 521 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #32Turbine copper deposition. Derate started after going from summ | Ghent | Derate | Coal | 3 | 2015 | 10 | 547.0667 | 4.1681 | 1992.3647 | 3.6419 | 4
GH4 | D1 | 43 | 4499 | 2015-10-24 08:21 | 2015-11-27 12:16 | 515 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #33Load reduced due to turbine copper deposition. | Ghent | Derate | Coal | 3 | 2015 | 10 | 819.9167 | 15.6175 | 7465.146 | 9.1048 | 9
GH4 | D1 | 44 | 8199 | 2015-11-13 22:23 | 2015-11-14 00:07 | 405 | 525 | 478 | Other scrubber problems | Load Reduction #34Gypsum Farm electrical outage (lost power due to 138 substation | Ghent | Derate | Coal | 3 | 2015 | 11 | 1.7333 | 0.39619 | 189.379 | 109.2571 | 109
GH4 | D1 | 45 | 8199 | 2015-11-14 00:07 | 2015-11-14 01:14 | 300 | 525 | 478 | Other scrubber problems | Load Reduction #35Gypsum Farm electrical outage (lost power due to 138 substation | Ghent | Derate | Coal | 3 | 2015 | 11 | 1.1167 | 0.47857 | 228.7571 | 204.8571 | 205
GH4 | MO | 46 | 1493 | 2015-11-27 12:16 | 2015-11-29 20:06 | 0 | 525 | 478 | Air heater fouling (regenerative) | FF00Outage #11Unit 4 was removed from service to repair Air Heater seals. | Ghent | Maintenance | Coal | 3 | 2015 | 11 | 55.8333 | 55.8333 | 26688.3333 | 478 | 478
GH4 | D1 | 47 | 4499 | 2015-11-29 20:06 | 2015-12-10 12:30 | 515 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #36Load reduced due to turbine copper deposition. | Ghent | Derate | Coal | 3 | 2015 | 11 | 256.4 | 4.8838 | 2334.461 | 9.1048 | 9
GH4 | D1 | 49 | 1850 | 2015-12-17 09:18 | 2015-12-17 12:20 | 425 | 525 | 478 | Boiler water condition (not feedwater water quality) | Load Reduction #37Unit 4 was limited due to boiler chemistry after startup. | Ghent | Derate | Coal | 3 | 2015 | 12 | 3.0333 | 0.57778 | 276.1778 | 91.0476 | 91
GH4 | D1 | 50 | 4499 | 2015-12-17 12:20 | 2016-01-01 | 515 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #38Unit 4 is limited due to copper build up on the turbine blades. | Ghent | Derate | Coal | 3 | 2015 | 12 | 347.6667 | 6.6222 | 3165.4222 | 9.1048 | 9
GH4 | D1 | 1 | 4499 | 2016-01-01 | 2016-02-29 23:59 | 515 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #1Unit 4 is limited due to copper build up on the turbine blades. | Ghent | Derate | Coal | 3 | 2016 | 1 | 1439.9833 | 27.4283 | 13110.7054 | 9.1048 | 9
GH4 | PD | 2 | 3414 | 2016-02-05 11:30 | 2016-02-05 12:30 | 330 | 525 | 478 | Feedwater pump local controls | Load Reduction #2Took Unit down to 1 BFP for tuner to check and make adjustments t | Ghent | Derate | Coal | 3 | 2016 | 2 | 1 | 0.37143 | 177.5429 | 177.5429 | 178
GH4 | D1 | 3 | 340 | 2016-02-12 18:11 | 2016-02-12 18:38 | 431 | 525 | 478 | Other pulverizer problems | Load Reduction #3Maintenance found a roll stationary liner had broken off and was | Ghent | Derate | Coal | 3 | 2016 | 2 | 0.45 | 0.080571 | 38.5131 | 85.5848 | 86
GH4 | D1 | 4 | 340 | 2016-02-20 09:00 | 2016-02-20 12:18 | 440 | 525 | 478 | Other pulverizer problems | Load Reduction #44-1 Feeder motion monitor and 4-5 mill BSO limit switch bracket b | Ghent | Derate | Coal | 3 | 2016 | 2 | 3.3 | 0.53429 | 255.3886 | 77.3905 | 77
GH4 | D1 | 5 | 4499 | 2016-03-01 | 2016-03-14 06:18 | 515 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #5Unit 4 is limited due to copper build up on the turbine blades. | Ghent | Derate | Coal | 3 | 2016 | 3 | 318.3 | 6.0629 | 2898.0457 | 9.1048 | 9
GH4 | U1 | 6 | 1080 | 2016-03-14 06:18 | 2016-03-17 13:19 | 0 | 525 | 478 | Economizer B | Outage #1Unit 4 came off line due to a leak in the economizer. | Ghent | Outage | Coal | 3 | 2016 | 3 | 79.0167 | 79.0167 | 37769.9667 | 478 | 478
GH4 | D1 | 7 | 1080 | 2016-03-17 20:59 | 2016-03-20 07:55 | 512 | 525 | 478 | Economizer B | Load Reduction #6Load reduced due to Turbine copper deposition. Derate started aft | Ghent | Derate | Coal | 3 | 2016 | 3 | 58.9333 | 1.4593 | 697.5462 | 11.8362 | 12
GH4 | PO | 8 | 3341 | 2016-03-30 23:02 | 2016-04-23 12:25 | 0 | 525 | 478 | Other LP heater - general | F590Outage #2Unit removed from service for the Planned Spring Outage. | Ghent | Other | Coal | 3 | 2016 | 3 | 565.3833 | 565.3833 | 270253.2333 | 478 | 478
GH4 | D1 | 9 | 9910 | 2016-04-25 09:33 | 2016-04-25 10:16 | 460 | 525 | 478 | Maintenance personnel error | Load Reduction #7B, C, and D LP heaters tripped while making level adjustment. B | Ghent | Derate | Coal | 3 | 2016 | 4 | 0.71667 | 0.08873 | 42.413 | 59.181 | 59
GH4 | D1 | 10 | 3341 | 2016-04-27 06:35 | 2016-04-27 08:00 | 460 | 525 | 478 | Other LP heater - general | Load Reduction #8B, C, and D LP heaters tripped on shell side level. B and C heat | Ghent | Derate | Coal | 3 | 2016 | 4 | 1.4167 | 0.1754 | 83.8397 | 59.181 | 59
GH4 | MO | 11 | 1488 | 2016-04-29 22:06 | 2016-04-30 22:10 | 0 | 525 | 478 | Air heater (regenerative) | F530Outage #3Unit 4 was removed from line to inspect the air heaters. | Ghent | Maintenance | Coal | 3 | 2016 | 4 | 24.0667 | 24.0667 | 11503.8667 | 478 | 478
GH4 | PD | 12 | 250 | 2016-05-19 21:20 | 2016-05-20 01:30 | 400 | 525 | 478 | Pulverizer feeders | Load Reduction #94-4 Feeder calibration. | Ghent | Derate | Coal | 3 | 2016 | 5 | 4.1667 | 0.99206 | 474.2063 | 113.8095 | 114
GH4 | D1 | 13 | 1470 | 2016-05-30 13:46 | 2016-05-30 20:30 | 471 | 525 | 478 | Induced draft fan motors and drives | F700Load Reduction #104-1B ID fan tripped. | Ghent | Derate | Coal | 3 | 2016 | 5 | 6.7333 | 0.69257 | 331.0491 | 49.1657 | 49
GH4 | D1 | 14 | 1470 | 2016-05-31 09:30 | 2016-05-31 12:50 | 467 | 525 | 478 | Induced draft fan motors and drives | F550Load Reduction #114-1B ID fan tripped. | Ghent | Derate | Coal | 3 | 2016 | 5 | 3.3333 | 0.36825 | 176.0254 | 52.8076 | 53
GH4 | D1 | 15 | 250 | 2016-06-07 02:05 | 2016-06-07 12:23 | 425 | 525 | 478 | Pulverizer feeders | Load Reduction #124-6 Feeder clean out conveyor failed. | Ghent | Derate | Coal | 3 | 2016 | 6 | 10.3 | 1.9619 | 937.7905 | 91.0476 | 91
GH4 | D1 | 16 | 250 | 2016-06-13 20:09 | 2016-06-13 20:33 | 450 | 525 | 478 | Pulverizer feeders | Load Reduction #134-6 Feeder belt was torn by foreign metal. | Ghent | Derate | Coal | 3 | 2016 | 6 | 0.4 | 0.057143 | 27.3143 | 68.2857 | 68
GH4 | D1 | 17 | 346 | 2016-07-15 10:27 | 2016-07-15 12:40 | 450 | 525 | 478 | Pulverizer pyrite removal system | F350Load Reduction #144-2 Mill was OOS for CCR maintenance on pyrite system. Ops | Ghent | Derate | Coal | 3 | 2016 | 7 | 2.2167 | 0.31667 | 151.3667 | 68.2857 | 68
GH4 | U1 | 18 | 3220 | 2016-07-23 15:02 | 2016-07-30 21:06 | 0 | 525 | 478 | Circulating water piping | F830Outage #4GH4 off line due to failure of the U4 cooling tower south distributio | Ghent | Outage | Coal | 3 | 2016 | 7 | 174.0667 | 174.0667 | 83203.8667 | 478 | 478
GH4 | D1 | 19 | 3441 | 2016-07-31 16:49 | 2016-07-31 17:45 | 500 | 525 | 478 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | Load Reduction #15U4 lost High Pressure heaters causing the unit to derate. | Ghent | Derate | Coal | 3 | 2016 | 7 | 0.93333 | 0.044444 | 21.2444 | 22.7619 | 23
GH4 | MO | 20 | 3220 | 2016-08-31 22:06 | 2016-09-02 18:15 | 0 | 525 | 478 | Circulating water piping | F540Outage #5Unit 4 was removed from service to repair a circulating water line le | Ghent | Maintenance | Coal | 3 | 2016 | 8 | 44.15 | 44.15 | 21103.7 | 478 | 478
GH4 | D1 | 22 | 3431 | 2016-10-10 05:39 | 2016-10-10 23:15 | 511 | 525 | 478 | Other feedwater valves | F540Load Reduction #16Removed HP heaters from service due to a leak on water side | Ghent | Derate | Coal | 3 | 2016 | 10 | 17.6 | 0.46933 | 224.3413 | 12.7467 | 13
GH4 | MO | 23 | 3220 | 2016-10-12 22:57 | 2016-10-15 08:30 | 0 | 525 | 478 | Circulating water piping | F540Outage #7Unit 4 was removed from service to repair a Circulating Water line le | Ghent | Maintenance | Coal | 3 | 2016 | 10 | 57.55 | 57.55 | 27508.9 | 478 | 478
GH4 | D1 | 24 | 8601 | 2016-10-30 10:25 | 2016-10-30 15:06 | 350 | 525 | 478 | SO3 mitigation | Load Reduction #17DSI was taken out of service. The system was found to be plugge | Ghent | Derate | Coal | 3 | 2016 | 10 | 4.6833 | 1.5611 | 746.2111 | 159.3333 | 159
GH4 | D1 | 25 | 4499 | 2016-11-08 06:23 | 2016-11-08 06:33 | 518 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #18Not able to make Fall MW high (523). Several CT's out of servic | Ghent | Derate | Coal | 3 | 2016 | 11 | 0.16667 | 0.0022222 | 1.0622 | 6.3733 | 6
GH4 | D1 | 26 | 1480 | 2016-11-08 09:09 | 2016-11-08 09:29 | 450 | 525 | 478 | Other induced draft fan problems | Load Reduction #194-1 A ID fan tripped while swapping lube oil filters. | Ghent | Derate | Coal | 3 | 2016 | 11 | 0.33333 | 0.047619 | 22.7619 | 68.2857 | 68
GH4 | D1 | 27 | 3441 | 2016-11-12 06:45 | 2016-11-12 18:07 | 511 | 525 | 478 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | Load Reduction #20G-Heater shell side vent to condenser leak. | Ghent | Derate | Coal | 3 | 2016 | 11 | 11.3667 | 0.30311 | 144.8871 | 12.7467 | 13
GH4 | D1 | 29 | 380 | 2016-11-28 07:13 | 2016-11-28 07:39 | 433 | 525 | 478 | Light-off (igniter) systems (including fuel supply) | Load Reduction #214-4C Ignitor wouldn't go in. | Ghent | Derate | Coal | 3 | 2016 | 11 | 0.43333 | 0.075937 | 36.2977 | 83.7638 | 84
GH4 | D1 | 30 | 4499 | 2016-12-01 11:10 | 2016-12-19 08:00 | 531 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #22Not able to make winter MW high (534). Several CT's out of serv | Ghent | Derate | Coal | 3 | 2016 | 12 | 428.8333 | -4.901 | -2342.6552 | 0 | 0
GH4 | D1 | 31 | 4499 | 2016-12-19 08:00 | 2016-12-20 08:18 | 515 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #23Not able to make winter MW high (534). Several CT's out of serv | Ghent | Derate | Coal | 3 | 2016 | 12 | 24.3 | 0.46286 | 221.2457 | 9.1048 | 9
GH4 | D1 | 32 | 4499 | 2016-12-20 08:18 | 2017-01-01 | 526 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #24Not able to make winter MW high (534). Several CT's out of serv | Ghent | Derate | Coal | 3 | 2016 | 12 | 279.7 | -0.53276 | -254.6602 | 0 | 0
GH4 | D1 | 1 | 4499 | 2017-01-01 | 2017-01-06 08:29 | 526 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #1Not able to make winter MW high (534). Several CT's out of servi | Ghent | Derate | Coal | 3 | 2017 | 1 | 128.4833 | -0.24473 | -116.981 | 0 | 0
GH4 | D1 | 2 | 4499 | 2017-01-06 08:29 | 2017-01-06 11:30 | 511 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #2Not able to make winter MW high due to turbine performance | Ghent | Derate | Coal | 3 | 2017 | 1 | 3.0167 | 0.080444 | 38.4524 | 12.7467 | 13
GH4 | D1 | 3 | 4499 | 2017-01-06 11:30 | 2017-02-12 07:58 | 515 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #3Not able to make winter MW high due to turbine performance. | Ghent | Derate | Coal | 3 | 2017 | 1 | 884.4667 | 16.847 | 8052.8584 | 9.1048 | 9
GH4 | D1 | 4 | 340 | 2017-02-03 07:16 | 2017-02-03 08:54 | 430 | 525 | 478 | Other pulverizer problems | F830Load Reduction #44-5 Mill temperature was running high and tripped. 4-6 Mill | Ghent | Derate | Coal | 3 | 2017 | 2 | 1.6333 | 0.29556 | 141.2756 | 86.4952 | 86
GH4 | D1 | 6 | 4499 | 2017-02-12 03:47 | 2017-02-12 07:58 | 515 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #5Unit 4 is derated due to turbine performance. | Ghent | Derate | Coal | 3 | 2017 | 2 | 4.1833 | 0.079683 | 38.0883 | 9.1048 | 9
GH4 | D1 | 5 | 3412 | 2017-02-12 07:10 | 2017-02-12 07:58 | 200 | 525 | 478 | Feedwater pump drive - steam turbine | F540Load Reduction #6Unit load was reduced due to 4-2 Boiler Feed Pump Turbine hig | Ghent | Derate | Coal | 3 | 2017 | 2 | 0.8 | 0.49524 | 236.7238 | 295.9048 | 296
GH4 | U1 | 7 | 3412 | 2017-02-12 07:58 | 2017-02-12 23:26 | 0 | 525 | 478 | Feedwater pump drive - steam turbine | F540Outage #1Unit 4 was forced off line due to 4-2 Boiler Feed Pump Turbine high p | Ghent | Outage | Coal | 3 | 2017 | 2 | 15.4667 | 15.4667 | 7393.0667 | 478 | 478
GH4 | D1 | 8 | 4499 | 2017-02-12 23:26 | 2017-02-28 23:59 | 515 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #7Not able to make full load due to turbine performance issues. | Ghent | Derate | Coal | 3 | 2017 | 2 | 384.55 | 7.3248 | 3501.2362 | 9.1048 | 9
GH4 | D1 | 9 | 4499 | 2017-03-01 | 2017-03-01 13:04 | 515 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #8Unable to make Spring MW high due to turbine performance issues. | Ghent | Derate | Coal | 3 | 2017 | 3 | 13.0667 | 0.24889 | 118.9689 | 9.1048 | 9
GH4 | D1 | 10 | 4499 | 2017-03-01 13:04 | 2017-03-01 16:22 | 505 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #9Unable to make Spring MW high due to turbine performance issues. | Ghent | Derate | Coal | 3 | 2017 | 3 | 3.3 | 0.12571 | 60.0914 | 18.2095 | 18
GH4 | D1 | 11 | 4499 | 2017-03-01 16:22 | 2017-03-07 06:51 | 515 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #10Unable to make Spring MW high due to turbine performance issues. | Ghent | Derate | Coal | 3 | 2017 | 3 | 134.4833 | 2.5616 | 1224.4387 | 9.1048 | 9
GH4 | D1 | 12 | 4499 | 2017-03-07 06:51 | 2017-03-07 08:47 | 509 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #11Unable to make Spring MW high due to turbine performance issues. | Ghent | Derate | Coal | 3 | 2017 | 3 | 1.9333 | 0.058921 | 28.1641 | 14.5676 | 15
GH4 | D1 | 13 | 4499 | 2017-03-07 08:47 | 2017-04-07 23:51 | 510 | 525 | 478 | Other miscellaneous steam turbine problems | Load Reduction #12Unable to make Spring MW high due to turbine performance issues. | Ghent | Derate | Coal | 3 | 2017 | 3 | 759.0667 | 21.6876 | 10366.6819 | 13.6571 | 14
GH4 | PD | 14 | 1980 | 2017-04-05 22:45 | 2017-04-06 00:06 | 440 | 525 | 478 | Boiler safety valve test | F790Load Reduction #13Reduced load to check main steam and drum safeties. | Ghent | Derate | Coal | 3 | 2017 | 4 | 1.35 | 0.21857 | 104.4771 | 77.3905 | 77
GH4 | PO | 15 | 1801 | 2017-04-07 23:51 | 2017-04-28 05:38 | 0 | 525 | 478 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Outage #2Unit 4 was removed from service for the Planned Spring Outage. | Ghent | Other | Coal | 3 | 2017 | 4 | 485.7833 | 485.7833 | 232204.4333 | 478 | 478
GH4 | U1 | 16 | 1040 | 2017-05-03 01:57 | 2017-05-04 20:34 | 0 | 525 | 478 | First superheater B | Outage #3GH4 was removed from service due to a tube leak in the PSH area of the bo | Ghent | Outage | Coal | 3 | 2017 | 5 | 42.6167 | 42.6167 | 20370.7667 | 478 | 478
GH4 | D1 | 17 | 3661 | 2017-05-17 09:29 | 2017-05-17 09:43 | 411 | 525 | 478 | 4160-volt circuit breakers | F700Load Reduction #144-2 Circulating water pump 4KV breaker tripped due to a shor | Ghent | Derate | Coal | 3 | 2017 | 5 | 0.23333 | 0.050667 | 24.2187 | 103.7943 | 104
GH4 | D1 | 18 | 335 | 2017-06-14 03:19 | 2017-06-14 09:14 | 420 | 525 | 478 | Pulverizer lube oil system | F070Load Reductions #154-4 Mill lube oil pump MCC breaker coil went to ground and | Ghent | Derate | Coal | 3 | 2017 | 6 | 5.9167 | 1.1833 | 565.6333 | 95.6 | 96
GH4 | U1 | 19 | 1040 | 2017-07-15 18:33 | 2017-07-17 20:03 | 0 | 525 | 478 | First superheater B | Outage #4Unit 4 came off one due to a tube leak in the Primary Superheat section o | Ghent | Outage | Coal | 3 | 2017 | 7 | 49.5 | 49.5 | 23661 | 478 | 478
GH4 | U1 | 20 | 1040 | 2017-07-25 02:30 | 2017-07-26 17:26 | 0 | 525 | 478 | First superheater B | F830Outage #5GH4 was brought off line due to a tube leak in the Superheat section | Ghent | Outage | Coal | 3 | 2017 | 7 | 38.9333 | 38.9333 | 18610.1333 | 478 | 478
GH4 | D1 | 21 | 1470 | 2017-09-15 12:19 | 2017-09-15 12:53 | 450 | 525 | 478 | Induced draft fan motors and drives | F490Load Reduction #164-2 B ID fan A5 cell tripped the breaker. | Ghent | Derate | Coal | 3 | 2017 | 9 | 0.56667 | 0.080952 | 38.6952 | 68.2857 | 68
GH4 | D1 | 22 | 1470 | 2017-09-15 12:53 | 2017-09-15 14:44 | 425 | 525 | 478 | Induced draft fan motors and drives | F490Load Reduction #174-2 B ID fan A5 cell tripped the breaker. | Ghent | Derate | Coal | 3 | 2017 | 9 | 1.85 | 0.35238 | 168.4381 | 91.0476 | 91
GH4 | D1 | 23 | 320 | 2017-09-19 20:22 | 2017-09-20 00:39 | 420 | 525 | 478 | Foreign object in Pulverizers mill | Load Reduction #184-3 Mill was taken out of service to remove a piece of metal. | Ghent | Derate | Coal | 3 | 2017 | 9 | 4.2833 | 0.85667 | 409.4867 | 95.6 | 96
GH4 | U1 | 24 | 3220 | 2017-11-18 17:32 | 2017-11-21 07:34 | 0 | 525 | 478 | Circulating water piping | F540Outage #6GH4 was Forced off line due to Circulating water line leak. | Ghent | Outage | Coal | 3 | 2017 | 11 | 62.0333 | 62.0333 | 29651.9333 | 478 | 478
GH4 | U1 | 25 | 4800 | 2017-12-07 15:08 | 2017-12-07 20:23 | 0 | 525 | 478 | Generator main leads | FV00Outage # 7 GH 4 Forced off line due to vibration in generator lead box. | Ghent | Outage | Coal | 3 | 2017 | 12 | 5.25 | 5.25 | 2509.5 | 478 | 478
GH4 | PD | 1 | 920 | 2018-01-06 21:25 | 2018-01-07 00:15 | 240 | 525 | 478 | Other slag and ash removal problems A | F830Load Reduction #1Planned deslag. | Ghent | Derate | Coal | 3 | 2018 | 1 | 2.8333 | 1.5381 | 735.2095 | 259.4857 | 259
GH4 | PO | 2 | 1801 | 2018-04-06 21:41 | 2018-04-30 23:59 | 0 | 525 | 478 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Outage #1 | Ghent | Other | Coal | 3 | 2018 | 4 | 578.3 | 578.3 | 276427.4 | 478 | 478
MC1 | D1 | 1 | 250 | 2013-01-01 04:19 | 2013-01-01 05:12 | 250 | 330 | 300 | Pulverizer feeders | FW001B Coal Feeder - Wet Coal Issues | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 0.88333 | 0.21414 | 64.2424 | 72.7273 | 73
MC1 | NC | 2 | 1160 | 2013-01-01 22:31 | 2013-01-02 04:49 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2013 | 1 | 6.3 | 6.3 | 1890 | 300 | 300
MC1 | D1 | 3 | 250 | 2013-01-03 14:23 | 2013-01-03 15:52 | 255 | 330 | 300 | Pulverizer feeders | F1201A Coal Feeder - Rock on Belt | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 1.4833 | 0.33712 | 101.1364 | 68.1818 | 68
MC1 | NC | 4 | 360 | 2013-01-10 | 2013-01-10 02:46 | 0 | 330 | 300 | Burners | F530Coal Burners - Inspection | Mill Creek | Other | Coal | 2 | 2013 | 1 | 2.7667 | 2.7667 | 830 | 300 | 300
MC1 | D1 | 5 | 9270 | 2013-01-14 11:10 | 2013-01-14 13:29 | 200 | 330 | 300 | Wet coal | FW00Wet Coal Issues | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 2.3167 | 0.91263 | 273.7879 | 118.1818 | 118
MC1 | D1 | 6 | 9270 | 2013-01-15 08:25 | 2013-01-15 08:57 | 254 | 330 | 300 | Wet coal | FW001C Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 0.53333 | 0.12283 | 36.8485 | 69.0909 | 69
MC1 | D1 | 7 | 9270 | 2013-01-15 13:00 | 2013-01-15 13:25 | 235 | 330 | 300 | Wet coal | FW00Wet Coal - Plugged Feeder | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 0.41667 | 0.11995 | 35.9848 | 86.3636 | 86
MC1 | D1 | 8 | 9270 | 2013-01-15 13:25 | 2013-01-15 16:00 | 200 | 330 | 300 | Wet coal | FW00Wet Coal - Feeder Issues | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 2.5833 | 1.0177 | 305.303 | 118.1818 | 118
MC1 | D1 | 9 | 9270 | 2013-01-16 01:30 | 2013-01-16 02:15 | 240 | 330 | 300 | Wet coal | FW001D Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 0.75 | 0.20455 | 61.3636 | 81.8182 | 82
MC1 | D1 | 10 | 9270 | 2013-01-16 02:15 | 2013-01-16 07:35 | 120 | 330 | 300 | Wet coal | FW00Wet Coal Issues | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 5.3333 | 3.3939 | 1018.1818 | 190.9091 | 191
MC1 | U1 | 11 | 360 | 2013-01-16 07:35 | 2013-01-19 08:29 | 0 | 330 | 300 | Burners | F0701C4 Coal Burner - Fire & Windbox Damage | Mill Creek | Outage | Coal | 2 | 2013 | 1 | 72.9 | 72.9 | 21870 | 300 | 300
MC1 | NC | 12 | 1850 | 2013-01-19 08:29 | 2013-01-19 16:30 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2013 | 1 | 8.0167 | 8.0167 | 2405 | 300 | 300
MC1 | D1 | 13 | 1850 | 2013-01-19 16:30 | 2013-01-19 21:35 | 250 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 5.0833 | 1.2323 | 369.697 | 72.7273 | 73
MC1 | D4 | 14 | 360 | 2013-01-20 22:00 | 2013-01-21 00:40 | 225 | 330 | 300 | Burners | F530Coal Burners - Inspections | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 2.6667 | 0.84848 | 254.5455 | 95.4545 | 95
MC1 | D1 | 15 | 9270 | 2013-01-21 06:37 | 2013-01-21 12:08 | 240 | 330 | 300 | Wet coal | FW001C Coal Feeder - Plugged, Wet Coal | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 5.5167 | 1.5045 | 451.3636 | 81.8182 | 82
MC1 | D1 | 16 | 310 | 2013-01-23 23:00 | 2013-01-24 03:05 | 225 | 330 | 300 | Pulverizer mills | F5901B Coal Mill Primary Air Fan - Repair Damper | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 4.0833 | 1.2992 | 389.7727 | 95.4545 | 95
MC1 | D1 | 17 | 9270 | 2013-01-24 21:25 | 2013-01-24 23:00 | 260 | 330 | 300 | Wet coal | FW001C Coal Feeder - Plugged, Wet Coal | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 1.5833 | 0.33586 | 100.7576 | 63.6364 | 64
MC1 | D4 | 18 | 360 | 2013-01-24 23:00 | 2013-01-25 02:50 | 230 | 330 | 300 | Burners | F530Coal Burners - Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 3.8333 | 1.1616 | 348.4848 | 90.9091 | 91
MC1 | NC | 19 | 3230 | 2013-01-26 22:20 | 2013-01-26 23:07 | 0 | 330 | 300 | Circulating water valves | F5901A Circulating Water Pump - Discharge Valve Issue | Mill Creek | Other | Coal | 2 | 2013 | 1 | 0.78333 | 0.78333 | 235 | 300 | 300
MC1 | NC | 20 | 3230 | 2013-01-27 23:15 | 2013-01-28 00:21 | 0 | 330 | 300 | Circulating water valves | F5901A Circulating Water Pump - Discharge Valve Issue | Mill Creek | Other | Coal | 2 | 2013 | 1 | 1.1 | 1.1 | 330 | 300 | 300
MC1 | D1 | 21 | 250 | 2013-01-28 00:21 | 2013-01-28 00:58 | 240 | 330 | 300 | Pulverizer feeders | F5901A Coal Feeder - Repair Cleanout Conveyor | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 0.61667 | 0.16818 | 50.4545 | 81.8182 | 82
MC1 | NC | 22 | 1160 | 2013-01-31 23:00 | 2013-02-01 05:00 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2013 | 1 | 6 | 6 | 1800 | 300 | 300
MC1 | D1 | 23 | 8262 | 2013-02-01 06:18 | 2013-02-03 10:02 | 310 | 330 | 300 | Scrubber booster I.D. fan vibration (fan specific to the scrubber) | F8501B SDRS Booster Fan - High Vibration | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 51.7333 | 3.1354 | 940.6061 | 18.1818 | 18
MC1 | D1 | 24 | 250 | 2013-02-02 19:28 | 2013-02-02 22:12 | 240 | 330 | 300 | Pulverizer feeders | F0101D Coal Feeder - Belt Alignment | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 2.7333 | 0.74545 | 223.6364 | 81.8182 | 82
MC1 | MO | 25 | 8262 | 2013-02-03 10:02 | 2013-02-05 02:45 | 0 | 330 | 300 | Scrubber booster I.D. fan vibration (fan specific to the scrubber) | F3201B SDRS Booster Fan - Wash due to Vibration Issue | Mill Creek | Maintenance | Coal | 2 | 2013 | 2 | 40.7167 | 40.7167 | 12215 | 300 | 300
MC1 | NC | 26 | 1850 | 2013-02-05 02:45 | 2013-02-05 11:45 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 2 | 9 | 9 | 2700 | 300 | 300
MC1 | D1 | 27 | 320 | 2013-02-05 15:20 | 2013-02-05 16:00 | 270 | 330 | 300 | Foreign object in Pulverizers mill | F1201D Coal Mill - Foreign Metal in Mill | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 0.66667 | 0.12121 | 36.3636 | 54.5455 | 55
MC1 | NC | 28 | 310 | 2013-02-05 22:53 | 2013-02-06 00:14 | 0 | 330 | 300 | Pulverizer mills | F7901A Coal Mill - Air Flow Test | Mill Creek | Other | Coal | 2 | 2013 | 2 | 1.35 | 1.35 | 405 | 300 | 300
MC1 | NC | 29 | 310 | 2013-02-06 22:23 | 2013-02-06 23:22 | 0 | 330 | 300 | Pulverizer mills | F7901B Coal Mill - Air Flow Test | Mill Creek | Other | Coal | 2 | 2013 | 2 | 0.98333 | 0.98333 | 295 | 300 | 300
MC1 | NC | 30 | 310 | 2013-02-07 22:24 | 2013-02-07 23:00 | 0 | 330 | 300 | Pulverizer mills | F7901D Coal Mill - Air Flow Test | Mill Creek | Other | Coal | 2 | 2013 | 2 | 0.6 | 0.6 | 180 | 300 | 300
MC1 | NC | 31 | 1160 | 2013-02-10 22:45 | 2013-02-11 05:00 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2013 | 2 | 6.25 | 6.25 | 1875 | 300 | 300
MC1 | D1 | 32 | 300 | 2013-02-11 06:02 | 2013-02-11 10:15 | 250 | 330 | 300 | Pulverizer motors and drives | F5901A Coal Feeder Motor - Replace | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 4.2167 | 1.0222 | 306.6667 | 72.7273 | 73
MC1 | D1 | 33 | 300 | 2013-02-11 10:15 | 2013-02-11 12:14 | 275 | 330 | 300 | Pulverizer motors and drives | F5901A Coal Feeder Motor - Replace, Gas Guns in Service | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 1.9833 | 0.33056 | 99.1667 | 50 | 50
MC1 | D1 | 34 | 300 | 2013-02-11 12:48 | 2013-02-11 15:46 | 277 | 330 | 300 | Pulverizer motors and drives | F5901A Coal Feeder Motor - Wiring Issues, Gas Guns in Service | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 2.9667 | 0.47646 | 142.9394 | 48.1818 | 48
MC1 | D1 | 35 | 300 | 2013-02-11 15:46 | 2013-02-11 18:30 | 250 | 330 | 300 | Pulverizer motors and drives | F5901A Coal Feeder Motor - Wiring Issues | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 2.7333 | 0.66263 | 198.7879 | 72.7273 | 73
MC1 | D1 | 36 | 300 | 2013-02-11 18:30 | 2013-02-11 20:30 | 280 | 330 | 300 | Pulverizer motors and drives | F5901A Coal Feeder Motor - Wiring Issues, Gas Guns in Service | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 2 | 0.30303 | 90.9091 | 45.4545 | 45
MC1 | D1 | 37 | 9270 | 2013-02-13 12:06 | 2013-02-13 12:50 | 250 | 330 | 300 | Wet coal | FW001C Coal Feeder - Plugged, Wet Coal | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 0.73333 | 0.17778 | 53.3333 | 72.7273 | 73
MC1 | D1 | 38 | 250 | 2013-02-13 23:55 | 2013-02-14 02:52 | 240 | 330 | 300 | Pulverizer feeders | F0101A & 1B Coal Feeders - Belt Alignment | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 2.95 | 0.80455 | 241.3636 | 81.8182 | 82
MC1 | D4 | 39 | 310 | 2013-02-14 23:00 | 2013-02-15 04:58 | 250 | 330 | 300 | Pulverizer mills | F5301C Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 5.9667 | 1.4465 | 433.9394 | 72.7273 | 73
MC1 | D1 | 40 | 310 | 2013-02-15 01:30 | 2013-02-15 04:58 | 175 | 330 | 300 | Pulverizer mills | F5901D Coal Mill - Repair Holes in Pant Leg Duct | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 3.4667 | 1.6283 | 488.4848 | 140.9091 | 141
MC1 | U1 | 41 | 3149 | 2013-02-15 15:45 | 2013-02-15 16:53 | 0 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F420Lost Vacuum - 1B Circulating Water Pump Trip, Operator Error | Mill Creek | Outage | Coal | 2 | 2013 | 2 | 1.1333 | 1.1333 | 340 | 300 | 300
MC1 | NC | 42 | 1850 | 2013-02-15 16:53 | 2013-02-15 23:10 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 2 | 6.2833 | 6.2833 | 1885 | 300 | 300
MC1 | D1 | 43 | 310 | 2013-02-19 05:35 | 2013-02-19 06:37 | 240 | 330 | 300 | Pulverizer mills | F4001C Coal Mill - Exhauster Discharge Damper Issue | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 1.0333 | 0.28182 | 84.5455 | 81.8182 | 82
MC1 | D1 | 44 | 9600 | 2013-02-21 19:12 | 2013-02-21 20:00 | 260 | 330 | 300 | SO2 stack emissions (fossil) | FE00SO2 Limit - Reactant Feed Valve Plugged | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 0.8 | 0.1697 | 50.9091 | 63.6364 | 64
MC1 | NC | 45 | 1160 | 2013-02-21 23:00 | 2013-02-22 04:05 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheat | Mill Creek | Other | Coal | 2 | 2013 | 2 | 5.0833 | 5.0833 | 1525 | 300 | 300
MC1 | D1 | 46 | 1160 | 2013-02-28 02:10 | 2013-02-28 04:10 | 240 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheat | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 2 | 0.54545 | 163.6364 | 81.8182 | 82
MC1 | D1 | 47 | 1480 | 2013-02-28 13:52 | 2013-03-01 01:55 | 320 | 330 | 300 | Other induced draft fan problems | F400ID Fans Maxed Out - High Amps | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 12.05 | 0.36515 | 109.5455 | 9.0909 | 9
MC1 | NC | 48 | 1160 | 2013-03-03 11:00 | 2013-03-03 18:30 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2013 | 3 | 7.5 | 7.5 | 2250 | 300 | 300
MC1 | D1 | 49 | 1160 | 2013-03-04 19:50 | 2013-03-04 22:30 | 300 | 330 | 300 | First reheater B | F320Boiler Slag Buildup - First Reheater | Mill Creek | Derate | Coal | 2 | 2013 | 3 | 2.6667 | 0.24242 | 72.7273 | 27.2727 | 27
MC1 | NC | 50 | 1160 | 2013-03-04 22:30 | 2013-03-05 04:15 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2013 | 3 | 5.75 | 5.75 | 1725 | 300 | 300
MC1 | NC | 51 | 1160 | 2013-03-05 11:45 | 2013-03-05 16:20 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2013 | 3 | 4.5833 | 4.5833 | 1375 | 300 | 300
MC1 | D1 | 52 | 310 | 2013-03-06 14:05 | 2013-03-06 15:40 | 250 | 330 | 300 | Pulverizer mills | F5901D Coal Mill - Roller Adjustment | Mill Creek | Derate | Coal | 2 | 2013 | 3 | 1.5833 | 0.38384 | 115.1515 | 72.7273 | 73
MC1 | NC | 53 | 1160 | 2013-03-06 23:30 | 2013-03-07 05:00 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2013 | 3 | 5.5 | 5.5 | 1650 | 300 | 300
MC1 | NC | 54 | 1160 | 2013-03-08 14:15 | 2013-03-08 19:50 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2013 | 3 | 5.5833 | 5.5833 | 1675 | 300 | 300
MC1 | NC | 55 | 1160 | 2013-03-14 22:00 | 2013-03-15 03:45 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2013 | 3 | 5.75 | 5.75 | 1725 | 300 | 300
MC1 | D1 | 56 | 310 | 2013-03-15 05:40 | 2013-03-15 10:14 | 260 | 330 | 300 | Pulverizer mills | F5901D Coal Mill - Replaced Roller | Mill Creek | Derate | Coal | 2 | 2013 | 3 | 4.5667 | 0.96869 | 290.6061 | 63.6364 | 64
MC1 | PO | 57 | 4400 | 2013-03-16 00:46 | 2013-05-13 06:00 | 0 | 330 | 300 | Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | F590Planned 8 Week Outage | Mill Creek | Other | Coal | 2 | 2013 | 3 | 1397.2333 | 1397.2333 | 419170 | 300 | 300
MC1 | PE | 58 | 4400 | 2013-05-13 06:00 | 2013-06-08 01:16 | 0 | 330 | 300 | Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | F590Turbine Overhaul Extension | Mill Creek | Other | Coal | 2 | 2013 | 5 | 619.2667 | 619.2667 | 185780 | 300 | 300
MC1 | U1 | 59 | 3611 | 2013-06-08 01:23 | 2013-06-09 00:58 | 0 | 330 | 300 | Switchyard circuit breakers - external | F430Bus Tie Failure 4501 - Generator Lockout | Mill Creek | Outage | Coal | 2 | 2013 | 6 | 23.5833 | 23.5833 | 7075 | 300 | 300
MC1 | U1 | 60 | 800 | 2013-06-09 01:59 | 2013-06-09 06:39 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F660Low Drum Level | Mill Creek | Outage | Coal | 2 | 2013 | 6 | 4.6667 | 4.6667 | 1400 | 300 | 300
MC1 | U1 | 61 | 800 | 2013-06-09 07:27 | 2013-06-09 13:55 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F660Low Drum Level | Mill Creek | Outage | Coal | 2 | 2013 | 6 | 6.4667 | 6.4667 | 1940 | 300 | 300
MC1 | U1 | 62 | 4560 | 2013-06-09 15:15 | 2013-06-10 06:32 | 0 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing Vibration | Mill Creek | Outage | Coal | 2 | 2013 | 6 | 15.2833 | 15.2833 | 4585 | 300 | 300
MC1 | D1 | 63 | 1850 | 2013-06-10 20:32 | 2013-06-11 05:55 | 146 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica (Variable Derate) | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 9.3833 | 5.2319 | 1569.5758 | 167.2727 | 167
MC1 | D1 | 64 | 4560 | 2013-06-11 05:55 | 2013-06-11 09:12 | 212 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing Vibration | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 3.2833 | 1.174 | 352.2121 | 107.2727 | 107
MC1 | D4 | 65 | 4560 | 2013-06-11 09:12 | 2013-06-11 09:42 | 200 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing vibration | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 0.5 | 0.19697 | 59.0909 | 118.1818 | 118
MC1 | U1 | 66 | 4560 | 2013-06-11 09:42 | 2013-06-11 11:25 | 0 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing Vibration | Mill Creek | Outage | Coal | 2 | 2013 | 6 | 1.7167 | 1.7167 | 515 | 300 | 300
MC1 | D1 | 67 | 4560 | 2013-06-11 12:00 | 2013-06-11 13:10 | 100 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing Vibration | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 1.1667 | 0.81313 | 243.9394 | 209.0909 | 209
MC1 | D1 | 68 | 4560 | 2013-06-11 13:10 | 2013-06-11 14:09 | 200 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing Vibration | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 0.98333 | 0.38737 | 116.2121 | 118.1818 | 118
MC1 | D1 | 69 | 4560 | 2013-06-11 14:09 | 2013-06-11 15:30 | 260 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing Vibration | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 1.35 | 0.28636 | 85.9091 | 63.6364 | 64
MC1 | D1 | 70 | 4560 | 2013-06-11 15:30 | 2013-06-11 20:02 | 185 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing Vibration | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 4.5333 | 1.9919 | 597.5758 | 131.8182 | 132
MC1 | D1 | 71 | 4560 | 2013-06-11 20:02 | 2013-06-11 22:02 | 230 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing Vibration | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 2 | 0.60606 | 181.8182 | 90.9091 | 91
MC1 | D1 | 72 | 4560 | 2013-06-11 22:02 | 2013-06-11 23:05 | 260 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing Vibration | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 1.05 | 0.22273 | 66.8182 | 63.6364 | 64
MC1 | D1 | 73 | 4560 | 2013-06-11 23:05 | 2013-06-12 00:49 | 290 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing Vibration | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 1.7333 | 0.2101 | 63.0303 | 36.3636 | 36
MC1 | D1 | 74 | 4560 | 2013-06-12 00:49 | 2013-06-12 02:35 | 302 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing Vibration | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 1.7667 | 0.1499 | 44.9697 | 25.4545 | 25
MC1 | D1 | 75 | 4560 | 2013-06-12 02:35 | 2013-06-12 03:05 | 315 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing Vibration | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 0.5 | 0.022727 | 6.8182 | 13.6364 | 14
MC1 | D1 | 76 | 1850 | 2013-06-12 03:05 | 2013-06-12 05:45 | 317 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 2.6667 | 0.10505 | 31.5152 | 11.8182 | 12
MC1 | D1 | 77 | 4560 | 2013-06-12 05:45 | 2013-06-14 00:12 | 270 | 330 | 300 | Generator vibration (excluding vibration due to failed bearing and other components) | F850#5 Bearing Vibration | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 42.45 | 7.7182 | 2315.4545 | 54.5455 | 55
MC1 | D1 | 78 | 310 | 2013-06-15 08:51 | 2013-06-15 09:29 | 250 | 330 | 300 | Pulverizer mills | F5901A Coal Mill - Replace Breaker | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 0.63333 | 0.15354 | 46.0606 | 72.7273 | 73
MC1 | D1 | 79 | 310 | 2013-06-16 23:00 | 2013-06-17 01:10 | 250 | 330 | 300 | Pulverizer mills | F5401B Coal Mill - B4 Coal Conduit Leak | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 2.1667 | 0.52525 | 157.5758 | 72.7273 | 73
MC1 | D4 | 80 | 310 | 2013-06-17 22:00 | 2013-06-18 01:05 | 250 | 330 | 300 | Pulverizer mills | F5901C Coal Mill - Install Test Ports | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 3.0833 | 0.74747 | 224.2424 | 72.7273 | 73
MC1 | D4 | 81 | 310 | 2013-06-18 21:43 | 2013-06-19 03:23 | 240 | 330 | 300 | Pulverizer mills | F5901C Coal Mill - Rearrange Distributors | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 5.6667 | 1.5455 | 463.6364 | 81.8182 | 82
MC1 | MO | 82 | 1000 | 2013-06-20 00:18 | 2013-06-20 21:08 | 0 | 330 | 300 | Waterwall (Furnace wall) A | F540Boiler Tube Leak - Waterwall | Mill Creek | Maintenance | Coal | 2 | 2013 | 6 | 20.8333 | 20.8333 | 6250 | 300 | 300
MC1 | NC | 83 | 1850 | 2013-06-20 21:08 | 2013-06-21 08:39 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 6 | 11.5167 | 11.5167 | 3455 | 300 | 300
MC1 | D1 | 84 | 250 | 2013-06-22 16:18 | 2013-06-22 17:21 | 200 | 330 | 300 | Pulverizer feeders | F4001B Coal Feeder - Stopped Running | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 1.05 | 0.41364 | 124.0909 | 118.1818 | 118
MC1 | D4 | 85 | 310 | 2013-06-24 21:00 | 2013-06-25 05:07 | 250 | 330 | 300 | Pulverizer mills | F5901C Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 8.1167 | 1.9677 | 590.303 | 72.7273 | 73
MC1 | D1 | 86 | 250 | 2013-06-25 17:10 | 2013-06-25 18:10 | 290 | 330 | 300 | Pulverizer feeders | F4301B Coal Feeder - Tripping Out, Loose Wire on Tachometer | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 1 | 0.12121 | 36.3636 | 36.3636 | 36
MC1 | D1 | 87 | 250 | 2013-06-25 18:10 | 2013-06-25 21:07 | 230 | 330 | 300 | Pulverizer feeders | F4301B Coal Feeder - Tripping Out, Loose Wire on Tachometer | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 2.95 | 0.89394 | 268.1818 | 90.9091 | 91
MC1 | D4 | 88 | 310 | 2013-06-25 22:00 | 2013-06-26 05:58 | 230 | 330 | 300 | Pulverizer mills | F5901B Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 7.9667 | 2.4141 | 724.2424 | 90.9091 | 91
MC1 | D4 | 89 | 310 | 2013-06-27 22:00 | 2013-06-28 06:59 | 230 | 330 | 300 | Pulverizer mills | F5901C Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 8.9833 | 2.7222 | 816.6667 | 90.9091 | 91
MC1 | D4 | 90 | 310 | 2013-06-30 23:00 | 2013-07-01 05:27 | 230 | 330 | 300 | Pulverizer mills | F5901A Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 6.45 | 1.9545 | 586.3636 | 90.9091 | 91
MC1 | D4 | 91 | 310 | 2013-07-01 22:30 | 2013-07-02 06:18 | 230 | 330 | 300 | Pulverizer mills | F5901B Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 7.8 | 2.3636 | 709.0909 | 90.9091 | 91
MC1 | D4 | 92 | 310 | 2013-07-02 22:00 | 2013-07-03 03:50 | 230 | 330 | 300 | Pulverizer mills | F5901B Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 5.8333 | 1.7677 | 530.303 | 90.9091 | 91
MC1 | MO | 93 | 3441 | 2013-07-03 23:33 | 2013-07-05 01:29 | 0 | 330 | 300 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F590High Pressure (HP) Feedwater Heater #6 - Replace Channel Side Safety Relief Valve | Mill Creek | Maintenance | Coal | 2 | 2013 | 7 | 25.9333 | 25.9333 | 7780 | 300 | 300
MC1 | NC | 94 | 1850 | 2013-07-05 01:29 | 2013-07-05 09:35 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 7 | 8.1 | 8.1 | 2430 | 300 | 300
MC1 | D1 | 95 | 1850 | 2013-07-05 09:35 | 2013-07-05 15:00 | 298 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 5.4167 | 0.52525 | 157.5758 | 29.0909 | 29
MC1 | D4 | 96 | 310 | 2013-07-07 22:25 | 2013-07-08 02:40 | 250 | 330 | 300 | Pulverizer mills | F5901A Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 4.25 | 1.0303 | 309.0909 | 72.7273 | 73
MC1 | D4 | 97 | 310 | 2013-07-08 22:00 | 2013-07-09 02:54 | 250 | 330 | 300 | Pulverizer mills | F5901C Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 4.9 | 1.1879 | 356.3636 | 72.7273 | 73
MC1 | D4 | 98 | 310 | 2013-07-09 23:00 | 2013-07-10 03:00 | 250 | 330 | 300 | Pulverizer mills | F5901C Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 4 | 0.9697 | 290.9091 | 72.7273 | 73
MC1 | D4 | 99 | 310 | 2013-07-11 22:00 | 2013-07-12 03:25 | 250 | 330 | 300 | Pulverizer mills | F5301C Coal Mill - Inspect Distributors & Burner Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 5.4167 | 1.3131 | 393.9394 | 72.7273 | 73
MC1 | D1 | 100 | 8280 | 2013-07-13 19:16 | 2013-07-13 19:32 | 300 | 330 | 300 | Reagent feed piping | F120Reactant Feed Valve - Plugged | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 0.26667 | 0.024242 | 7.2727 | 27.2727 | 27
MC1 | D1 | 101 | 253 | 2013-07-15 17:28 | 2013-07-15 21:45 | 278 | 330 | 300 | Pulverizer feeder motor | F5901B Coal Feeder Motor - Repaired Mashed Wire | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 4.2833 | 0.67495 | 202.4848 | 47.2727 | 47
MC1 | U1 | 102 | 1000 | 2013-07-17 19:41 | 2013-07-19 03:53 | 0 | 330 | 300 | Waterwall (Furnace wall) A | F540Boiler Tube Leak - Waterwall | Mill Creek | Outage | Coal | 2 | 2013 | 7 | 32.2 | 32.2 | 9660 | 300 | 300
MC1 | NC | 103 | 1850 | 2013-07-19 03:53 | 2013-07-19 11:52 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 7 | 7.9833 | 7.9833 | 2395 | 300 | 300
MC1 | D1 | 104 | 4261 | 2013-07-22 07:25 | 2013-07-22 08:05 | 260 | 330 | 300 | Control valves | F540Turbine #4 Control Valve - EHC Leak | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 0.66667 | 0.14141 | 42.4242 | 63.6364 | 64
MC1 | D1 | 105 | 4261 | 2013-07-22 10:30 | 2013-07-22 13:00 | 260 | 330 | 300 | Control valves | F540Turbine #4 Control Valve - EHC Leak | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 2.5 | 0.5303 | 159.0909 | 63.6364 | 64
MC1 | D4 | 106 | 310 | 2013-07-22 22:00 | 2013-07-23 04:45 | 250 | 330 | 300 | Pulverizer mills | F5901C Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 6.75 | 1.6364 | 490.9091 | 72.7273 | 73
MC1 | D1 | 107 | 250 | 2013-07-23 17:05 | 2013-07-23 20:37 | 290 | 330 | 300 | Pulverizer feeders | F4001B Coal Feeder - Tripping Out | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 3.5333 | 0.42828 | 128.4848 | 36.3636 | 36
MC1 | D4 | 108 | 310 | 2013-07-23 22:30 | 2013-07-24 03:20 | 260 | 330 | 300 | Pulverizer mills | F5901C Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 4.8333 | 1.0253 | 307.5758 | 63.6364 | 64
MC1 | D1 | 109 | 330 | 2013-07-24 11:10 | 2013-07-24 11:30 | 250 | 330 | 300 | Pulverizer coal leak (pulverizers only) | F5401C Coal Mill - Coal Leak | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 0.33333 | 0.080808 | 24.2424 | 72.7273 | 73
MC1 | D4 | 110 | 310 | 2013-07-24 22:00 | 2013-07-25 04:45 | 250 | 330 | 300 | Pulverizer mills | F5901A Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 6.75 | 1.6364 | 490.9091 | 72.7273 | 73
MC1 | NC | 113 | 9999 | 2013-07-29 09:00 | 2013-07-29 13:00 | 0 | 330 | 300 | Total unit performance testing (use appropriate codes for individual component testing) | F790Full Load Capability Test | Mill Creek | Other | Coal | 2 | 2013 | 7 | 4 | 4 | 1200 | 300 | 300
MC1 | D4 | 111 | 310 | 2013-07-29 22:00 | 2013-07-30 03:52 | 250 | 330 | 300 | Pulverizer mills | F5901B Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 5.8667 | 1.4222 | 426.6667 | 72.7273 | 73
MC1 | D1 | 112 | 3415 | 2013-07-30 00:05 | 2013-07-30 03:08 | 190 | 330 | 300 | Feedwater pump/drive lube oil system | F5901A Boiler Feed Pump Lube Oil Pump - Replace Switch | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 3.05 | 1.2939 | 388.1818 | 127.2727 | 127
MC1 | D4 | 114 | 250 | 2013-07-30 22:00 | 2013-07-31 03:49 | 250 | 330 | 300 | Pulverizer feeders | F0901B Coal Feeder - Calibration & Mill Riffles Replaced | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 5.8167 | 1.4101 | 423.0303 | 72.7273 | 73
MC1 | D4 | 115 | 310 | 2013-07-31 22:00 | 2013-08-01 03:31 | 250 | 330 | 300 | Pulverizer mills | F5901B Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 5.5167 | 1.3374 | 401.2121 | 72.7273 | 73
MC1 | D4 | 116 | 310 | 2013-08-01 22:00 | 2013-08-02 03:10 | 250 | 330 | 300 | Pulverizer mills | F5901B Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 5.1667 | 1.2525 | 375.7576 | 72.7273 | 73
MC1 | D4 | 117 | 310 | 2013-08-04 22:00 | 2013-08-05 03:23 | 250 | 330 | 300 | Pulverizer mills | F5901B Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 5.3833 | 1.3051 | 391.5152 | 72.7273 | 73
MC1 | D4 | 118 | 310 | 2013-08-05 22:00 | 2013-08-06 04:05 | 250 | 330 | 300 | Pulverizer mills | F5901C Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 6.0833 | 1.4747 | 442.4242 | 72.7273 | 73
MC1 | D4 | 119 | 310 | 2013-08-06 22:00 | 2013-08-07 04:00 | 240 | 330 | 300 | Pulverizer mills | F5901C Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 6 | 1.6364 | 490.9091 | 81.8182 | 82
MC1 | D4 | 120 | 310 | 2013-08-07 22:00 | 2013-08-08 03:49 | 250 | 330 | 300 | Pulverizer mills | F5901C Coal Mill - Replace Riffles | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 5.8167 | 1.4101 | 423.0303 | 72.7273 | 73
MC1 | D1 | 121 | 30 | 2013-08-15 14:15 | 2013-08-15 17:34 | 230 | 330 | 300 | Coal conveyors and feeders | F430C Coal Conveyor - Wiring Issue | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 3.3167 | 1.0051 | 301.5152 | 90.9091 | 91
MC1 | D4 | 122 | 360 | 2013-08-19 21:30 | 2013-08-19 22:55 | 250 | 330 | 300 | Burners | F5301C3 Coal Burner - Inspected & Cleaned | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 1.4167 | 0.34343 | 103.0303 | 72.7273 | 73
MC1 | D4 | 123 | 250 | 2013-08-25 22:00 | 2013-08-26 03:48 | 250 | 330 | 300 | Pulverizer feeders | F5901B Coal Feeder - Replace Power Supply Board | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 5.8 | 1.4061 | 421.8182 | 72.7273 | 73
MC1 | D4 | 124 | 360 | 2013-08-29 22:15 | 2013-08-30 05:10 | 250 | 330 | 300 | Burners | F5301C3 Coal Burner - Inspection & Clean Out | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 6.9167 | 1.6768 | 503.0303 | 72.7273 | 73
MC1 | D1 | 125 | 250 | 2013-08-30 16:33 | 2013-08-30 23:00 | 300 | 330 | 300 | Pulverizer feeders | F5901B Coal Feeder - Variable Frequency Drive Issue | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 6.45 | 0.58636 | 175.9091 | 27.2727 | 27
MC1 | D4 | 126 | 250 | 2013-08-30 23:00 | 2013-08-31 03:51 | 125 | 330 | 300 | Pulverizer feeders | F5901A & 1B Coal Feeders - Swap Variable Frequency Drives | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 4.85 | 3.0129 | 903.8636 | 186.3636 | 186
MC1 | D4 | 127 | 250 | 2013-08-31 03:51 | 2013-08-31 04:32 | 240 | 330 | 300 | Pulverizer feeders | F5901A Coal Feeder - Variable Frequency Drive Issue | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 0.68333 | 0.18636 | 55.9091 | 81.8182 | 82
MC1 | D1 | 128 | 250 | 2013-09-01 14:50 | 2013-09-01 21:17 | 304 | 330 | 300 | Pulverizer feeders | F4101D Coal Feeder - Replace Relays | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 6.45 | 0.50818 | 152.4545 | 23.6364 | 24
MC1 | D1 | 129 | 8260 | 2013-09-06 18:08 | 2013-09-06 18:45 | 150 | 330 | 300 | Scrubber booster I.D. fan (fan specific to the scrubber) | F6601B FGD Booster Fan Trip - Low Lube Oil Pressure | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 0.61667 | 0.33636 | 100.9091 | 163.6364 | 164
MC1 | D1 | 130 | 8260 | 2013-09-06 18:45 | 2013-09-06 22:00 | 215 | 330 | 300 | Scrubber booster I.D. fan (fan specific to the scrubber) | F6601B FGD Booster Fan - Low Lube Oil Pressure | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 3.25 | 1.1326 | 339.7727 | 104.5455 | 105
MC1 | D4 | 131 | 250 | 2013-09-15 20:45 | 2013-09-16 03:15 | 250 | 330 | 300 | Pulverizer feeders | F0901A Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 6.5 | 1.5758 | 472.7273 | 72.7273 | 73
MC1 | D4 | 132 | 310 | 2013-09-16 20:15 | 2013-09-17 00:20 | 250 | 330 | 300 | Pulverizer mills | F5901B Coal Mill - Change Oil in Gearbox | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 4.0833 | 0.9899 | 296.9697 | 72.7273 | 73
MC1 | D4 | 133 | 250 | 2013-09-17 22:00 | 2013-09-18 03:30 | 250 | 330 | 300 | Pulverizer feeders | F0901B Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 5.5 | 1.3333 | 400 | 72.7273 | 73
MC1 | D4 | 134 | 250 | 2013-09-18 22:00 | 2013-09-19 03:33 | 250 | 330 | 300 | Pulverizer feeders | F0901C Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 5.55 | 1.3455 | 403.6364 | 72.7273 | 73
MC1 | D4 | 135 | 250 | 2013-09-19 23:00 | 2013-09-20 03:38 | 250 | 330 | 300 | Pulverizer feeders | F0901D Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 4.6333 | 1.1232 | 336.9697 | 72.7273 | 73
MC1 | MO | 136 | 4270 | 2013-09-23 16:56 | 2013-09-27 15:56 | 0 | 330 | 300 | Crossover or under piping | F540Turbine Crossover - Piping Leak Repair | Mill Creek | Maintenance | Coal | 2 | 2013 | 9 | 95 | 95 | 28500 | 300 | 300
MC1 | NC | 137 | 1850 | 2013-09-27 15:56 | 2013-09-28 00:30 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2013 | 9 | 8.5667 | 8.5667 | 2570 | 300 | 300
MC1 | U1 | 138 | 800 | 2013-09-30 03:53 | 2013-09-30 07:31 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F820Low Drum Level Trip | Mill Creek | Outage | Coal | 2 | 2013 | 9 | 3.6333 | 3.6333 | 1090 | 300 | 300
MC1 | NC | 139 | 1850 | 2013-09-30 07:31 | 2013-09-30 14:29 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 9 | 6.9667 | 6.9667 | 2090 | 300 | 300
MC1 | D1 | 140 | 250 | 2013-10-07 22:50 | 2013-10-08 02:09 | 250 | 330 | 300 | Pulverizer feeders | FW001D Coal Feeder - Wet Coal Issue | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 3.3167 | 0.80404 | 241.2121 | 72.7273 | 73
MC1 | U1 | 141 | 250 | 2013-10-08 04:09 | 2013-10-08 10:10 | 0 | 330 | 300 | Pulverizer feeders | FW00Boiler Trip - High Drum Level Trip due to Wet Coal Issues | Mill Creek | Outage | Coal | 2 | 2013 | 10 | 6.0167 | 6.0167 | 1805 | 300 | 300
MC1 | NC | 142 | 1850 | 2013-10-08 10:10 | 2013-10-08 16:10 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 10 | 6 | 6 | 1800 | 300 | 300
MC1 | D1 | 143 | 250 | 2013-10-08 16:10 | 2013-10-09 04:25 | 250 | 330 | 300 | Pulverizer feeders | FW00Wet Coal Issues | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 12.25 | 2.9697 | 890.9091 | 72.7273 | 73
MC1 | D1 | 144 | 250 | 2013-10-09 04:25 | 2013-10-09 05:30 | 270 | 330 | 300 | Pulverizer feeders | FW00Wet Coal Issues | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 1.0833 | 0.19697 | 59.0909 | 54.5455 | 55
MC1 | D1 | 145 | 250 | 2013-10-09 05:30 | 2013-10-09 06:15 | 275 | 330 | 300 | Pulverizer feeders | FW00Wet Coal Issues | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 0.75 | 0.125 | 37.5 | 50 | 50
MC1 | D4 | 146 | 310 | 2013-10-13 21:21 | 2013-10-14 03:11 | 240 | 330 | 300 | Pulverizer mills | F5301D Coal Mill - Inspection, Metal in Scraper Section | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 5.8333 | 1.5909 | 477.2727 | 81.8182 | 82
MC1 | D4 | 147 | 310 | 2013-10-14 22:35 | 2013-10-15 01:39 | 250 | 330 | 300 | Pulverizer mills | F5901D Coal Mill - Scraper Repairs | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 3.0667 | 0.74343 | 223.0303 | 72.7273 | 73
MC1 | D4 | 148 | 310 | 2013-10-20 22:00 | 2013-10-21 06:25 | 250 | 330 | 300 | Pulverizer mills | F5301B Coal Mill - Inspection & Exhauster Balanced | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 8.4167 | 2.0404 | 612.1212 | 72.7273 | 73
MC1 | D4 | 149 | 250 | 2013-10-29 23:00 | 2013-10-29 23:47 | 245 | 330 | 300 | Pulverizer feeders | F5901A Coal Feeder - Clean Out Conveyor Repair | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 0.78333 | 0.20177 | 60.5303 | 77.2727 | 77
MC1 | D4 | 150 | 250 | 2013-11-04 23:00 | 2013-11-05 02:24 | 245 | 330 | 300 | Pulverizer feeders | F5901D Coal Feeder - Replace Power Cord | Mill Creek | Derate | Coal | 2 | 2013 | 11 | 3.4 | 0.87576 | 262.7273 | 77.2727 | 77
MC1 | NC | 151 | 8460 | 2013-11-05 08:15 | 2013-11-05 19:00 | 0 | 330 | 300 | Testing A | F790Full Load RATA Testing. | Mill Creek | Other | Coal | 2 | 2013 | 11 | 10.75 | 10.75 | 3225 | 300 | 300
MC1 | NC | 152 | 8460 | 2013-11-06 08:00 | 2013-11-06 14:21 | 0 | 330 | 300 | Testing A | F790Full Load RATA Testing | Mill Creek | Other | Coal | 2 | 2013 | 11 | 6.35 | 6.35 | 1905 | 300 | 300
MC1 | D1 | 153 | 310 | 2013-11-09 04:30 | 2013-11-09 08:04 | 320 | 330 | 300 | Pulverizer mills | F0501B Coal Mill - Roller Locked up | Mill Creek | Derate | Coal | 2 | 2013 | 11 | 3.5667 | 0.10808 | 32.4242 | 9.0909 | 9
MC1 | D1 | 154 | 310 | 2013-11-09 08:04 | 2013-11-09 15:13 | 260 | 330 | 300 | Pulverizer mills | F0501B Coal Mill - Replace Roller | Mill Creek | Derate | Coal | 2 | 2013 | 11 | 7.15 | 1.5167 | 455 | 63.6364 | 64
MC1 | D4 | 155 | 550 | 2013-11-11 22:30 | 2013-11-11 23:40 | 290 | 330 | 300 | Reheat steam relief/safety valves | F590Set Safeties - Reheater | Mill Creek | Derate | Coal | 2 | 2013 | 11 | 1.1667 | 0.14141 | 42.4242 | 36.3636 | 36
MC1 | D1 | 156 | 250 | 2013-11-13 21:20 | 2013-11-13 22:05 | 270 | 330 | 300 | Pulverizer feeders | F8201D Coal Feeder Tripped | Mill Creek | Derate | Coal | 2 | 2013 | 11 | 0.75 | 0.13636 | 40.9091 | 54.5455 | 55
MC1 | D1 | 157 | 250 | 2013-11-14 02:48 | 2013-11-14 08:11 | 250 | 330 | 300 | Pulverizer feeders | F8201D Coal Feeder, Continuous Tripping (x25) | Mill Creek | Derate | Coal | 2 | 2013 | 11 | 5.3833 | 1.3051 | 391.5152 | 72.7273 | 73
MC1 | D4 | 158 | 250 | 2013-11-17 22:00 | 2013-11-18 04:57 | 260 | 330 | 300 | Pulverizer feeders | F5901D Coal Feeder - Replace VFD (variable frequency drive) | Mill Creek | Derate | Coal | 2 | 2013 | 11 | 6.95 | 1.4742 | 442.2727 | 63.6364 | 64
MC1 | D1 | 159 | 3149 | 2013-11-18 07:09 | 2013-11-18 10:21 | 300 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure - Condenser Pluggage | Mill Creek | Derate | Coal | 2 | 2013 | 11 | 3.2 | 0.29091 | 87.2727 | 27.2727 | 27
MC1 | MO | 160 | 3110 | 2013-11-18 10:21 | 2013-11-20 04:39 | 0 | 330 | 300 | Condenser tube leaks | F540Condenser Tube Leak | Mill Creek | Maintenance | Coal | 2 | 2013 | 11 | 42.3 | 42.3 | 12690 | 300 | 300
MC1 | NC | 161 | 1850 | 2013-11-20 04:39 | 2013-11-20 10:45 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 11 | 6.1 | 6.1 | 1830 | 300 | 300
MC1 | D1 | 162 | 1850 | 2013-11-20 10:45 | 2013-11-20 11:35 | 315 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 11 | 0.83333 | 0.037879 | 11.3636 | 13.6364 | 14
MC1 | D4 | 163 | 250 | 2013-11-20 22:00 | 2013-11-21 04:56 | 250 | 330 | 300 | Pulverizer feeders | F5901D Coal Feeder - Trip Issue Repair | Mill Creek | Derate | Coal | 2 | 2013 | 11 | 6.9333 | 1.6808 | 504.2424 | 72.7273 | 73
MC1 | D4 | 164 | 360 | 2013-12-04 21:37 | 2013-12-05 04:32 | 145 | 330 | 300 | Burners | F790Burners & Igniters - Tuning | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 6.9167 | 3.8775 | 1163.2576 | 168.1818 | 168
MC1 | D1 | 165 | 250 | 2013-12-11 00:58 | 2013-12-11 03:19 | 230 | 330 | 300 | Pulverizer feeders | F8301D Coal Feeder - Trip | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 2.35 | 0.71212 | 213.6364 | 90.9091 | 91
MC1 | D1 | 166 | 250 | 2013-12-11 09:28 | 2013-12-11 10:01 | 230 | 330 | 300 | Pulverizer feeders | F4001D Coal Feeder - Troubleshooting Trip Issue | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 0.55 | 0.16667 | 50 | 90.9091 | 91
MC1 | D4 | 167 | 250 | 2013-12-11 12:30 | 2013-12-11 14:21 | 230 | 330 | 300 | Pulverizer feeders | F4301D Coal Feeder - Installing New Wiring | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 1.85 | 0.56061 | 168.1818 | 90.9091 | 91
MC1 | D1 | 168 | 250 | 2013-12-11 21:48 | 2013-12-11 23:05 | 270 | 330 | 300 | Pulverizer feeders | F4001D Coal Feeder - Troubleshooting Trip Issue | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 1.2833 | 0.23333 | 70 | 54.5455 | 55
MC1 | D1 | 169 | 250 | 2013-12-11 23:35 | 2013-12-12 03:00 | 270 | 330 | 300 | Pulverizer feeders | F4001D Coal Feeder - Troubleshooting Trip Issue | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 3.4167 | 0.62121 | 186.3636 | 54.5455 | 55
MC1 | D1 | 170 | 250 | 2013-12-12 06:31 | 2013-12-12 06:54 | 270 | 330 | 300 | Pulverizer feeders | F4001D Coal Feeder - Troubleshooting Trip Issue | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 0.38333 | 0.069697 | 20.9091 | 54.5455 | 55
MC1 | D1 | 171 | 250 | 2013-12-12 07:52 | 2013-12-12 08:01 | 270 | 330 | 300 | Pulverizer feeders | F4001D Coal Feeder - Troubleshooting Trip Issue | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 0.15 | 0.027273 | 8.1818 | 54.5455 | 55
MC1 | D1 | 172 | 250 | 2013-12-12 08:15 | 2013-12-12 08:29 | 270 | 330 | 300 | Pulverizer feeders | F4001D Coal Feeder - Troubleshooting Trip Issue | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 0.23333 | 0.042424 | 12.7273 | 54.5455 | 55
MC1 | D1 | 173 | 250 | 2013-12-12 11:00 | 2013-12-12 11:12 | 270 | 330 | 300 | Pulverizer feeders | F4001D Coal Feeder - Troubleshooting Trip Issue | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 0.2 | 0.036364 | 10.9091 | 54.5455 | 55
MC1 | D1 | 174 | 250 | 2013-12-12 14:15 | 2013-12-12 15:18 | 260 | 330 | 300 | Pulverizer feeders | F5901D Coal Feeder - Replace Speed Pick Up Cable | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 1.05 | 0.22273 | 66.8182 | 63.6364 | 64
MC1 | D1 | 175 | 3149 | 2013-12-12 20:24 | 2013-12-13 06:41 | 315 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 10.2833 | 0.46742 | 140.2273 | 13.6364 | 14
MC1 | D1 | 176 | 3149 | 2013-12-13 06:41 | 2013-12-14 00:09 | 305 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 17.4667 | 1.3232 | 396.9697 | 22.7273 | 23
MC1 | MO | 177 | 3113 | 2013-12-14 00:09 | 2013-12-15 08:47 | 0 | 330 | 300 | Condenser tube and water box cleaning (including circulating water flow reversal) | F320Condenser - Clean Water Boxes | Mill Creek | Maintenance | Coal | 2 | 2013 | 12 | 32.6333 | 32.6333 | 9790 | 300 | 300
MC1 | NC | 178 | 1850 | 2013-12-15 08:47 | 2013-12-15 15:53 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 12 | 7.1 | 7.1 | 2130 | 300 | 300
MC1 | D1 | 179 | 1850 | 2013-12-15 15:53 | 2013-12-15 16:57 | 270 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 1.0667 | 0.19394 | 58.1818 | 54.5455 | 55
MC1 | D1 | 180 | 250 | 2013-12-16 21:37 | 2013-12-16 22:08 | 250 | 330 | 300 | Pulverizer feeders | F5301D Coal Feeder - Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 0.51667 | 0.12525 | 37.5758 | 72.7273 | 73
MC1 | D1 | 181 | 250 | 2013-12-16 23:11 | 2013-12-17 04:29 | 250 | 330 | 300 | Pulverizer feeders | F8201D Coal Feeder Motor - Starter Trip | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 5.3 | 1.2848 | 385.4545 | 72.7273 | 73
MC1 | D4 | 182 | 310 | 2013-12-17 22:30 | 2013-12-18 03:00 | 250 | 330 | 300 | Pulverizer mills | F5301B Coal Mill - Inspect Exhauster Discharge Gate | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 4.5 | 1.0909 | 327.2727 | 72.7273 | 73
MC1 | D1 | 183 | 250 | 2013-12-19 20:30 | 2013-12-20 00:20 | 265 | 330 | 300 | Pulverizer feeders | F8201D Coal Feeder - Trip | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 3.8333 | 0.75505 | 226.5152 | 59.0909 | 59
MC1 | D1 | 184 | 250 | 2013-12-20 00:20 | 2013-12-20 06:36 | 315 | 330 | 300 | Pulverizer feeders | F8201D Coal Feeder - Trip | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 6.2667 | 0.28485 | 85.4545 | 13.6364 | 14
MC1 | D1 | 185 | 250 | 2013-12-20 09:29 | 2013-12-20 11:20 | 275 | 330 | 300 | Pulverizer feeders | F5901D Coal Feeder - Replaced Circuit Board | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 1.85 | 0.30833 | 92.5 | 50 | 50
MC1 | D1 | 186 | 3149 | 2013-12-26 18:28 | 2013-12-27 06:30 | 310 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 12.0333 | 0.72929 | 218.7879 | 18.1818 | 18
MC1 | D1 | 187 | 3149 | 2013-12-27 06:30 | 2013-12-27 21:28 | 300 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 14.9667 | 1.3606 | 408.1818 | 27.2727 | 27
MC1 | MO | 188 | 3113 | 2013-12-27 21:28 | 2013-12-28 04:04 | 0 | 330 | 300 | Condenser tube and water box cleaning (including circulating water flow reversal) | F320Condenser - Cleaned Water Boxes | Mill Creek | Maintenance | Coal | 2 | 2013 | 12 | 6.6 | 6.6 | 1980 | 300 | 300
MC1 | SF | 189 | 9320 | 2013-12-28 04:04 | 2013-12-28 12:18 | 0 | 330 | 300 | Other miscellaneous external problems | F460Start-up Failure - Water in UPS Cabinet | Mill Creek | Outage | Coal | 2 | 2013 | 12 | 8.2333 | 8.2333 | 2470 | 300 | 300
MC1 | D1 | 190 | 200 | 2013-12-28 19:30 | 2013-12-29 01:00 | 255 | 330 | 300 | Pulverizer exhauster fan (for indirect firing) | F8501B Mill Exhauster Vent - High Vibration in bearings | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 5.5 | 1.25 | 375 | 68.1818 | 68
MC1 | D1 | 1 | 8280 | 2014-01-07 07:15 | 2014-01-07 08:58 | 260 | 330 | 300 | Reagent feed piping | F540FGD Reactant Feed Line - Leak | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 1.7167 | 0.36414 | 109.2424 | 63.6364 | 64
MC1 | D1 | 2 | 250 | 2014-01-07 16:50 | 2014-01-07 18:06 | 260 | 330 | 300 | Pulverizer feeders | FW001D Coal Feeder - Plugged, Frozen/Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 1.2667 | 0.26869 | 80.6061 | 63.6364 | 64
MC1 | D1 | 3 | 250 | 2014-01-08 05:45 | 2014-01-08 06:43 | 240 | 330 | 300 | Pulverizer feeders | FW001D Coal Feeder - Plugged, Frozen/Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 0.96667 | 0.26364 | 79.0909 | 81.8182 | 82
MC1 | D4 | 4 | 310 | 2014-01-09 21:26 | 2014-01-10 01:17 | 245 | 330 | 300 | Pulverizer mills | F5901A Coal Mill - Roller Adjustment | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 3.85 | 0.99167 | 297.5 | 77.2727 | 77
MC1 | D4 | 5 | 310 | 2014-01-13 22:00 | 2014-01-14 07:17 | 240 | 330 | 300 | Pulverizer mills | F5301D Coal Mill & Feeder - Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 9.2833 | 2.5318 | 759.5455 | 81.8182 | 82
MC1 | D4 | 6 | 310 | 2014-01-14 22:34 | 2014-01-15 04:42 | 240 | 330 | 300 | Pulverizer mills | F5301A Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 6.1333 | 1.6727 | 501.8182 | 81.8182 | 82
MC1 | D4 | 7 | 250 | 2014-01-15 23:00 | 2014-01-16 06:17 | 240 | 330 | 300 | Pulverizer feeders | F0901B Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 7.2833 | 1.9864 | 595.9091 | 81.8182 | 82
MC1 | D4 | 8 | 250 | 2014-01-16 23:00 | 2014-01-17 04:14 | 240 | 330 | 300 | Pulverizer feeders | F0901C Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 5.2333 | 1.4273 | 428.1818 | 81.8182 | 82
MC1 | D1 | 9 | 4261 | 2014-01-17 21:42 | 2014-01-18 08:33 | 300 | 330 | 300 | Control valves | F130Turbine #2 Control Valve - Would Not Open during Valve Test | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 10.85 | 0.98636 | 295.9091 | 27.2727 | 27
MC1 | U1 | 10 | 800 | 2014-01-18 08:33 | 2014-01-18 11:21 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F820High Drum Level Trip due to Turbine #2 Control Valve Issue, Replaced Fast Acting S | Mill Creek | Outage | Coal | 2 | 2014 | 1 | 2.8 | 2.8 | 840 | 300 | 300
MC1 | NC | 11 | 1850 | 2014-01-18 11:21 | 2014-01-18 15:45 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 2 | 2014 | 1 | 4.4 | 4.4 | 1320 | 300 | 300
MC1 | D1 | 12 | 1850 | 2014-01-18 15:45 | 2014-01-18 16:36 | 285 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 0.85 | 0.11591 | 34.7727 | 40.9091 | 41
MC1 | D1 | 13 | 1850 | 2014-01-18 16:36 | 2014-01-18 18:40 | 300 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 2.0667 | 0.18788 | 56.3636 | 27.2727 | 27
MC1 | D4 | 14 | 250 | 2014-01-20 22:08 | 2014-01-21 04:20 | 240 | 330 | 300 | Pulverizer feeders | F0901A Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 6.2 | 1.6909 | 507.2727 | 81.8182 | 82
MC1 | D1 | 15 | 250 | 2014-01-24 02:53 | 2014-01-24 03:08 | 225 | 330 | 300 | Pulverizer feeders | FW001D Coal Feeder - Plugged, Frozen Coal | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 0.25 | 0.079545 | 23.8636 | 95.4545 | 95
MC1 | D1 | 16 | 250 | 2014-01-24 03:08 | 2014-01-24 03:45 | 250 | 330 | 300 | Pulverizer feeders | FW001D Coal Feeder - Plugged, Frozen Coal | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 0.61667 | 0.14949 | 44.8485 | 72.7273 | 73
MC1 | D1 | 17 | 250 | 2014-01-24 07:43 | 2014-01-24 09:04 | 240 | 330 | 300 | Pulverizer feeders | FW001D Coal Feeder - Plugged, Frozen Coal | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 1.35 | 0.36818 | 110.4545 | 81.8182 | 82
MC1 | D1 | 18 | 4261 | 2014-02-01 21:20 | 2014-02-02 08:50 | 120 | 330 | 300 | Control valves | F130Turbine #2 Control Valve - Stuck Closed | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 11.5 | 7.3182 | 2195.4545 | 190.9091 | 191
MC1 | NC | 19 | 1160 | 2014-02-04 23:00 | 2014-02-05 04:15 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater. Full load available if needed. | Mill Creek | Other | Coal | 2 | 2014 | 2 | 5.25 | 5.25 | 1575 | 300 | 300
MC1 | D1 | 20 | 250 | 2014-02-05 07:28 | 2014-02-05 09:30 | 265 | 330 | 300 | Pulverizer feeders | FW001C Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 2.0333 | 0.40051 | 120.1515 | 59.0909 | 59
MC1 | D4 | 21 | 250 | 2014-02-06 | 2014-02-06 03:12 | 240 | 330 | 300 | Pulverizer feeders | F5901C Coal Feeder - Repair Discharge Flapper | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 3.2 | 0.87273 | 261.8182 | 81.8182 | 82
MC1 | D1 | 22 | 1160 | 2014-02-08 07:15 | 2014-02-08 08:27 | 300 | 330 | 300 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 1.2 | 0.10909 | 32.7273 | 27.2727 | 27
MC1 | D1 | 23 | 1160 | 2014-02-08 08:27 | 2014-02-08 15:05 | 250 | 330 | 300 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 6.6333 | 1.6081 | 482.4242 | 72.7273 | 73
MC1 | NC | 24 | 1160 | 2014-02-08 22:00 | 2014-02-09 04:00 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 2 | 6 | 6 | 1800 | 300 | 300
MC1 | D1 | 25 | 1488 | 2014-02-10 23:05 | 2014-02-11 06:25 | 323 | 330 | 300 | Air heater (regenerative) | F320Air Heater - High Differential | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 7.3333 | 0.15556 | 46.6667 | 6.3636 | 6
MC1 | D1 | 26 | 1488 | 2014-02-11 06:25 | 2014-02-11 10:00 | 320 | 330 | 300 | Air heater (regenerative) | F320Air Heater - High Differential | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 3.5833 | 0.10859 | 32.5758 | 9.0909 | 9
MC1 | D1 | 27 | 1488 | 2014-02-11 10:00 | 2014-02-12 10:30 | 324 | 330 | 300 | Air heater (regenerative) | F3201A Air Heater - High Differential | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 24.5 | 0.44545 | 133.6364 | 5.4545 | 5
MC1 | NC | 28 | 8460 | 2014-02-11 12:45 | 2014-02-11 16:00 | 0 | 330 | 300 | Testing A | F790Particulate Matter Testing | Mill Creek | Other | Coal | 2 | 2014 | 2 | 3.25 | 3.25 | 975 | 300 | 300
MC1 | NC | 29 | 8460 | 2014-02-12 07:00 | 2014-02-12 22:45 | 0 | 330 | 300 | Testing A | F790Particulate Matter Testing | Mill Creek | Other | Coal | 2 | 2014 | 2 | 15.75 | 15.75 | 4725 | 300 | 300
MC1 | D1 | 30 | 1488 | 2014-02-12 10:30 | 2014-02-12 22:45 | 320 | 330 | 300 | Air heater (regenerative) | F3201A Air heater - High Differential | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 12.25 | 0.37121 | 111.3636 | 9.0909 | 9
MC1 | D1 | 31 | 1488 | 2014-02-12 22:45 | 2014-02-13 07:26 | 310 | 330 | 300 | Air heater (regenerative) | F3201A Air Heater - High Differential | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 8.6833 | 0.52626 | 157.8788 | 18.1818 | 18
MC1 | D1 | 32 | 1488 | 2014-02-13 07:26 | 2014-02-13 22:00 | 324 | 330 | 300 | Air heater (regenerative) | F3201A Air Heater - High Differential | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 14.5667 | 0.26485 | 79.4545 | 5.4545 | 5
MC1 | NC | 33 | 8460 | 2014-02-13 13:40 | 2014-02-13 22:00 | 0 | 330 | 300 | Testing A | F790Particulate Matter Testing | Mill Creek | Other | Coal | 2 | 2014 | 2 | 8.3333 | 8.3333 | 2500 | 300 | 300
MC1 | D4 | 34 | 310 | 2014-02-13 22:00 | 2014-02-14 03:00 | 240 | 330 | 300 | Pulverizer mills | F5301A Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 5 | 1.3636 | 409.0909 | 81.8182 | 82
MC1 | D1 | 35 | 250 | 2014-02-14 03:00 | 2014-02-14 05:05 | 240 | 330 | 300 | Pulverizer feeders | F5901C Coal Feeder - Replace Clean Out Conveyor Gearbox | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 2.0833 | 0.56818 | 170.4545 | 81.8182 | 82
MC1 | D1 | 36 | 250 | 2014-02-14 05:05 | 2014-02-14 06:50 | 250 | 330 | 300 | Pulverizer feeders | F5901C Coal Feeder - Replace Clean Out Conveyor Gearbox | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 1.75 | 0.42424 | 127.2727 | 72.7273 | 73
MC1 | D1 | 37 | 250 | 2014-02-14 06:50 | 2014-02-14 12:00 | 280 | 330 | 300 | Pulverizer feeders | F5901C Coal Feeder - Replace Clean Out Conveyor GearboxGas Guns in Service | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 5.1667 | 0.78283 | 234.8485 | 45.4545 | 45
MC1 | D1 | 38 | 1488 | 2014-02-15 06:54 | 2014-02-16 06:20 | 325 | 330 | 300 | Air heater (regenerative) | F3201A Air Heater - High Differential | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 23.4333 | 0.35505 | 106.5152 | 4.5455 | 5
MC1 | D1 | 39 | 1488 | 2014-02-16 06:20 | 2014-02-17 09:00 | 320 | 330 | 300 | Air heater (regenerative) | F3201A Air Heater - High Differential | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 26.6667 | 0.80808 | 242.4242 | 9.0909 | 9
MC1 | D1 | 40 | 1488 | 2014-02-17 09:00 | 2014-02-18 22:26 | 310 | 330 | 300 | Air heater (regenerative) | F3201A Air Heater - High Differential | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 37.4333 | 2.2687 | 680.6061 | 18.1818 | 18
MC1 | MO | 41 | 1488 | 2014-02-18 22:26 | 2014-02-21 22:16 | 0 | 330 | 300 | Air heater (regenerative) | F320Air Heater Wash | Mill Creek | Maintenance | Coal | 2 | 2014 | 2 | 71.8333 | 71.8333 | 21550 | 300 | 300
MC1 | SF | 42 | 4261 | 2014-02-21 22:16 | 2014-02-22 17:58 | 0 | 330 | 300 | Control valves | F590Turbine #2 & #3 Control Valves - Cleaned Servovalves | Mill Creek | Outage | Coal | 2 | 2014 | 2 | 19.7 | 19.7 | 5910 | 300 | 300
MC1 | NC | 43 | 1850 | 2014-02-22 17:58 | 2014-02-23 03:16 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2014 | 2 | 9.3 | 9.3 | 2790 | 300 | 300
MC1 | D1 | 44 | 1850 | 2014-02-23 03:16 | 2014-02-23 04:11 | 275 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 0.91667 | 0.15278 | 45.8333 | 50 | 50
MC1 | D1 | 45 | 1850 | 2014-02-23 04:11 | 2014-02-23 04:39 | 285 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 0.46667 | 0.063636 | 19.0909 | 40.9091 | 41
MC1 | D1 | 46 | 1850 | 2014-02-23 04:39 | 2014-02-23 05:36 | 295 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 0.95 | 0.10076 | 30.2273 | 31.8182 | 32
MC1 | NC | 47 | 4490 | 2014-02-27 07:00 | 2014-02-27 13:18 | 0 | 330 | 300 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Capability Test - Full Load | Mill Creek | Other | Coal | 2 | 2014 | 2 | 6.3 | 6.3 | 1890 | 300 | 300
MC1 | D4 | 48 | 310 | 2014-02-27 22:00 | 2014-02-28 02:02 | 240 | 330 | 300 | Pulverizer mills | F5901A Coal Mill - Inspection & Adjust Rollers | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 4.0333 | 1.1 | 330 | 81.8182 | 82
MC1 | NC | 49 | 1160 | 2014-03-05 23:20 | 2014-03-06 01:00 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2014 | 3 | 1.6667 | 1.6667 | 500 | 300 | 300
MC1 | NC | 50 | 1160 | 2014-03-06 22:45 | 2014-03-07 03:30 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2014 | 3 | 4.75 | 4.75 | 1425 | 300 | 300
MC1 | NC | 51 | 1160 | 2014-03-07 13:45 | 2014-03-07 17:40 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2014 | 3 | 3.9167 | 3.9167 | 1175 | 300 | 300
MC1 | D4 | 52 | 310 | 2014-03-11 21:30 | 2014-03-12 03:40 | 240 | 330 | 300 | Pulverizer mills | F5901A Coal Mill - Adjust Rollers & Mill Inspection1B Coal Feeder - Replace Integrat | Mill Creek | Derate | Coal | 2 | 2014 | 3 | 6.1667 | 1.6818 | 504.5455 | 81.8182 | 82
MC1 | NC | 53 | 1160 | 2014-03-16 00:30 | 2014-03-16 05:41 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 3 | 5.1833 | 5.1833 | 1555 | 300 | 300
MC1 | D4 | 54 | 250 | 2014-03-19 23:00 | 2014-03-20 04:15 | 240 | 330 | 300 | Pulverizer feeders | F5901D Coal Feeder - Repair Skirt | Mill Creek | Derate | Coal | 2 | 2014 | 3 | 5.25 | 1.4318 | 429.5455 | 81.8182 | 82
MC1 | D1 | 55 | 360 | 2014-03-22 13:40 | 2014-03-22 14:10 | 240 | 330 | 300 | Burners | F7801B Mill - 1B4 Coal Burner High Temperature | Mill Creek | Derate | Coal | 2 | 2014 | 3 | 0.5 | 0.13636 | 40.9091 | 81.8182 | 82
MC1 | D4 | 56 | 1160 | 2014-04-01 23:55 | 2014-04-02 03:10 | 132 | 330 | 300 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 3.25 | 1.95 | 585 | 180 | 180
MC1 | D1 | 57 | 1160 | 2014-04-03 00:10 | 2014-04-03 03:45 | 140 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 3.5833 | 2.0631 | 618.9394 | 172.7273 | 173
MC1 | D1 | 58 | 360 | 2014-04-04 18:20 | 2014-04-04 19:18 | 240 | 330 | 300 | Burners | F7801B Mill - 1B4 Coal Burner High Temperature | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 0.96667 | 0.26364 | 79.0909 | 81.8182 | 82
MC1 | D1 | 59 | 250 | 2014-04-05 04:30 | 2014-04-05 05:00 | 240 | 330 | 300 | Pulverizer feeders | F1201C Coal Feeder - Clean Out Conveyor Plugged | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 0.5 | 0.13636 | 40.9091 | 81.8182 | 82
MC1 | D1 | 60 | 9270 | 2014-04-05 05:00 | 2014-04-05 11:12 | 150 | 330 | 300 | Wet coal | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 6.2 | 3.3818 | 1014.5455 | 163.6364 | 164
MC1 | D1 | 61 | 9270 | 2014-04-05 11:12 | 2014-04-05 13:44 | 280 | 330 | 300 | Wet coal | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 2.5333 | 0.38384 | 115.1515 | 45.4545 | 45
MC1 | D1 | 62 | 1850 | 2014-04-05 13:44 | 2014-04-05 15:00 | 250 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 1.2667 | 0.30707 | 92.1212 | 72.7273 | 73
MC1 | D1 | 63 | 1850 | 2014-04-05 15:00 | 2014-04-07 07:30 | 240 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 40.5 | 11.0455 | 3313.6364 | 81.8182 | 82
MC1 | D1 | 64 | 250 | 2014-04-07 09:41 | 2014-04-07 10:20 | 255 | 330 | 300 | Pulverizer feeders | FW001D Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 0.65 | 0.14773 | 44.3182 | 68.1818 | 68
MC1 | D1 | 65 | 250 | 2014-04-07 13:11 | 2014-04-07 14:38 | 255 | 330 | 300 | Pulverizer feeders | FW001D Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 1.45 | 0.32955 | 98.8636 | 68.1818 | 68
MC1 | D1 | 66 | 250 | 2014-04-07 17:45 | 2014-04-07 23:00 | 165 | 330 | 300 | Pulverizer feeders | FW001C & 1D Coal Feeders - Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 5.25 | 2.625 | 787.5 | 150 | 150
MC1 | D1 | 67 | 9270 | 2014-04-07 23:00 | 2014-04-08 01:10 | 250 | 330 | 300 | Wet coal | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 2.1667 | 0.52525 | 157.5758 | 72.7273 | 73
MC1 | D1 | 68 | 250 | 2014-04-08 01:10 | 2014-04-08 02:15 | 180 | 330 | 300 | Pulverizer feeders | FW001D Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 1.0833 | 0.49242 | 147.7273 | 136.3636 | 136
MC1 | D1 | 69 | 250 | 2014-04-08 02:15 | 2014-04-08 03:53 | 125 | 330 | 300 | Pulverizer feeders | FW001A & 1D Coal Feeders - Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 1.6333 | 1.0146 | 304.3939 | 186.3636 | 186
MC1 | U1 | 70 | 9270 | 2014-04-08 03:53 | 2014-04-08 06:50 | 0 | 330 | 300 | Wet coal | F820Boiler Trip - Wet Coal Issues | Mill Creek | Outage | Coal | 2 | 2014 | 4 | 2.95 | 2.95 | 885 | 300 | 300
MC1 | NC | 71 | 1850 | 2014-04-08 06:50 | 2014-04-08 11:05 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 2 | 2014 | 4 | 4.25 | 4.25 | 1275 | 300 | 300
MC1 | D1 | 72 | 9270 | 2014-04-08 11:05 | 2014-04-08 12:20 | 160 | 330 | 300 | Wet coal | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 1.25 | 0.64394 | 193.1818 | 154.5455 | 155
MC1 | D1 | 73 | 250 | 2014-04-08 12:20 | 2014-04-08 13:03 | 130 | 330 | 300 | Pulverizer feeders | FW001C Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 0.71667 | 0.43434 | 130.303 | 181.8182 | 182
MC1 | D1 | 74 | 9270 | 2014-04-08 13:03 | 2014-04-08 14:31 | 160 | 330 | 300 | Wet coal | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 1.4667 | 0.75556 | 226.6667 | 154.5455 | 155
MC1 | D1 | 75 | 9270 | 2014-04-08 14:31 | 2014-04-08 15:20 | 210 | 330 | 300 | Wet coal | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 0.81667 | 0.29697 | 89.0909 | 109.0909 | 109
MC1 | D1 | 76 | 9270 | 2014-04-08 15:20 | 2014-04-08 17:10 | 195 | 330 | 300 | Wet coal | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 1.8333 | 0.75 | 225 | 122.7273 | 123
MC1 | D1 | 77 | 9270 | 2014-04-08 17:10 | 2014-04-08 19:29 | 280 | 330 | 300 | Wet coal | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 2.3167 | 0.35101 | 105.303 | 45.4545 | 45
MC1 | D1 | 78 | 250 | 2014-04-08 19:29 | 2014-04-08 20:10 | 220 | 330 | 300 | Pulverizer feeders | FW001C Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 0.68333 | 0.22778 | 68.3333 | 100 | 100
MC1 | D1 | 79 | 250 | 2014-04-08 20:10 | 2014-04-08 23:35 | 175 | 330 | 300 | Pulverizer feeders | FW001B & 1C Coal Feeders - Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 3.4167 | 1.6048 | 481.4394 | 140.9091 | 141
MC1 | D1 | 80 | 9270 | 2014-04-08 23:35 | 2014-04-09 00:46 | 290 | 330 | 300 | Wet coal | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 1.1833 | 0.14343 | 43.0303 | 36.3636 | 36
MC1 | D1 | 81 | 250 | 2014-04-09 00:46 | 2014-04-09 03:50 | 220 | 330 | 300 | Pulverizer feeders | FW001D Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 3.0667 | 1.0222 | 306.6667 | 100 | 100
MC1 | D1 | 82 | 9270 | 2014-04-09 03:50 | 2014-04-09 04:45 | 280 | 330 | 300 | Wet coal | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 0.91667 | 0.13889 | 41.6667 | 45.4545 | 45
MC1 | D1 | 83 | 9270 | 2014-04-09 04:45 | 2014-04-09 06:47 | 160 | 330 | 300 | Wet coal | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 2.0333 | 1.0475 | 314.2424 | 154.5455 | 155
MC1 | D1 | 84 | 9270 | 2014-04-09 06:47 | 2014-04-10 04:00 | 220 | 330 | 300 | Wet coal | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 21.2167 | 7.0722 | 2121.6667 | 100 | 100
MC1 | D1 | 85 | 9270 | 2014-04-10 04:00 | 2014-04-10 10:49 | 290 | 330 | 300 | Wet coal | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 6.8167 | 0.82626 | 247.8788 | 36.3636 | 36
MC1 | D1 | 86 | 1850 | 2014-04-10 23:41 | 2014-04-11 07:00 | 285 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 7.3167 | 0.99773 | 299.3182 | 40.9091 | 41
MC1 | PO | 87 | 1801 | 2014-04-12 11:55 | 2014-04-19 10:38 | 0 | 330 | 300 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Planned One Week Outage | Mill Creek | Other | Coal | 2 | 2014 | 4 | 166.7167 | 166.7167 | 50015 | 300 | 300
MC1 | NC | 88 | 1850 | 2014-04-19 10:38 | 2014-04-19 14:45 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 2 | 2014 | 4 | 4.1167 | 4.1167 | 1235 | 300 | 300
MC1 | U1 | 89 | 3662 | 2014-04-19 14:45 | 2014-04-19 17:39 | 0 | 330 | 300 | 4160-volt conductors and buses | F870B Bus Undervoltage - Blown Fuse | Mill Creek | Outage | Coal | 2 | 2014 | 4 | 2.9 | 2.9 | 870 | 300 | 300
MC1 | NC | 90 | 1850 | 2014-04-19 17:39 | 2014-04-19 17:49 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 2 | 2014 | 4 | 0.16667 | 0.16667 | 50 | 300 | 300
MC1 | U1 | 91 | 4309 | 2014-04-19 17:49 | 2014-04-19 19:43 | 0 | 330 | 300 | Other turbine instrument and control problems | F820Turbine Trip - Unknown Reason | Mill Creek | Outage | Coal | 2 | 2014 | 4 | 1.9 | 1.9 | 570 | 300 | 300
MC1 | NC | 92 | 1850 | 2014-04-19 19:43 | 2014-04-20 05:20 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Start Up | Mill Creek | Other | Coal | 2 | 2014 | 4 | 9.6167 | 9.6167 | 2885 | 300 | 300
MC1 | D4 | 93 | 310 | 2014-04-24 22:00 | 2014-04-25 05:55 | 240 | 330 | 300 | Pulverizer mills | F5901D Coal Mill - Adjust Rollers | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 7.9167 | 2.1591 | 647.7273 | 81.8182 | 82
MC1 | D4 | 94 | 310 | 2014-04-27 22:00 | 2014-04-28 02:00 | 240 | 330 | 300 | Pulverizer mills | F5901A Coal Mill - Inspection & Roller Adjustment | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 4 | 1.0909 | 327.2727 | 81.8182 | 82
MC1 | D1 | 95 | 310 | 2014-04-28 04:45 | 2014-04-28 08:00 | 230 | 330 | 300 | Pulverizer mills | F5901A Coal Mill - Repair Cone @ Bowl | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 3.25 | 0.98485 | 295.4545 | 90.9091 | 91
MC1 | D1 | 96 | 250 | 2014-04-28 20:45 | 2014-04-29 00:20 | 250 | 330 | 300 | Pulverizer feeders | F5901A Coal Feeder - Replace Clean Out Conveyor Shear Pin | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 3.5833 | 0.86869 | 260.6061 | 72.7273 | 73
MC1 | D4 | 97 | 310 | 2014-04-30 23:00 | 2014-05-01 01:32 | 240 | 330 | 300 | Pulverizer mills | F5901D Coal Mill - Roller Adjustment | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 2.5333 | 0.69091 | 207.2727 | 81.8182 | 82
MC1 | D1 | 98 | 4266 | 2014-05-06 03:10 | 2014-05-06 05:05 | 135 | 330 | 300 | Main stop valve testing | F720Turbine #1 Main Stop Valve - Fast Acting Solenoid Would Not Open During Valve Test | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 1.9167 | 1.1326 | 339.7727 | 177.2727 | 177
MC1 | D4 | 99 | 250 | 2014-05-12 22:28 | 2014-05-13 04:05 | 213 | 330 | 300 | Pulverizer feeders | F5901A Coal Feeder - Repair Clean Out Conveyor Gearbox | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 5.6167 | 1.9914 | 597.4091 | 106.3636 | 106
MC1 | MO | 100 | 3110 | 2014-05-23 22:40 | 2014-05-24 21:59 | 0 | 330 | 300 | Condenser tube leaks | F540Condenser Tube Leak | Mill Creek | Maintenance | Coal | 2 | 2014 | 5 | 23.3167 | 23.3167 | 6995 | 300 | 300
MC1 | NC | 101 | 1850 | 2014-05-24 21:59 | 2014-05-24 22:30 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2014 | 5 | 0.51667 | 0.51667 | 155 | 300 | 300
MC1 | U1 | 102 | 800 | 2014-05-24 22:30 | 2014-05-24 23:30 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F820High Drum Level Trip - Turbine Controls | Mill Creek | Outage | Coal | 2 | 2014 | 5 | 1 | 1 | 300 | 300 | 300
MC1 | NC | 103 | 1850 | 2014-05-24 23:30 | 2014-05-25 05:30 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2014 | 5 | 6 | 6 | 1800 | 300 | 300
MC1 | D1 | 104 | 1850 | 2014-05-25 05:30 | 2014-05-25 07:10 | 250 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 1.6667 | 0.40404 | 121.2121 | 72.7273 | 73
MC1 | D4 | 105 | 250 | 2014-05-27 23:00 | 2014-05-28 04:00 | 240 | 330 | 300 | Pulverizer feeders | F5901A Coal Feeder - Calibration & Mill Roller Adjustment | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 5 | 1.3636 | 409.0909 | 81.8182 | 82
MC1 | NC | 106 | 4842 | 2014-06-02 09:00 | 2014-06-02 11:09 | 0 | 330 | 300 | Reactive and capability testing | F790Generator Reactive Power Capability Test | Mill Creek | Other | Coal | 2 | 2014 | 6 | 2.15 | 2.15 | 645 | 300 | 300
MC1 | D1 | 107 | 8260 | 2014-06-06 12:33 | 2014-06-07 07:03 | 275 | 330 | 300 | Scrubber booster I.D. fan (fan specific to the scrubber) | F4301A Booster Fan Motor Lead - Replace Lugs | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 18.5 | 3.0833 | 925 | 50 | 50
MC1 | D1 | 108 | 8280 | 2014-06-19 03:40 | 2014-06-19 05:05 | 125 | 330 | 300 | Reagent feed piping | F540FGD "A" Reactant Feed Supply Line - Leak | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 1.4167 | 0.88005 | 264.0152 | 186.3636 | 186
MC1 | D1 | 109 | 250 | 2014-06-19 23:50 | 2014-06-20 00:55 | 230 | 330 | 300 | Pulverizer feeders | F1201D Coal Feeder - Plugged | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 1.0833 | 0.32828 | 98.4848 | 90.9091 | 91
MC1 | D1 | 110 | 4309 | 2014-06-20 00:55 | 2014-06-20 02:05 | 80 | 330 | 300 | Other turbine instrument and control problems | F400Turbine Controls Issue | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 1.1667 | 0.88384 | 265.1515 | 227.2727 | 227
MC1 | D1 | 111 | 250 | 2014-06-20 12:13 | 2014-06-20 14:12 | 250 | 330 | 300 | Pulverizer feeders | F8201A Coal Feeder - Keeps Tripping, electrical issue | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 1.9833 | 0.48081 | 144.2424 | 72.7273 | 73
MC1 | D1 | 112 | 250 | 2014-06-20 15:03 | 2014-06-20 19:37 | 250 | 330 | 300 | Pulverizer feeders | F8201A Coal Feeder - keeps tripping, electrical issue | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 4.5667 | 1.1071 | 332.1212 | 72.7273 | 73
MC1 | D4 | 113 | 4260 | 2014-06-20 22:00 | 2014-06-21 01:19 | 200 | 330 | 300 | Main stop valves | F590Turbine Valve Maintenace - Transferred Valves | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 3.3167 | 1.3066 | 391.9697 | 118.1818 | 118
MC1 | D1 | 114 | 250 | 2014-06-21 14:55 | 2014-06-21 16:37 | 250 | 330 | 300 | Pulverizer feeders | F8201A Coal Feeder - keeps tripping, electrical issue | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 1.7 | 0.41212 | 123.6364 | 72.7273 | 73
MC1 | D1 | 115 | 250 | 2014-06-23 13:10 | 2014-06-23 15:00 | 285 | 330 | 300 | Pulverizer feeders | F1201B Coal Feeder - Plugged | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 1.8333 | 0.25 | 75 | 40.9091 | 41
MC1 | NC | 116 | 8460 | 2014-06-23 16:00 | 2014-06-23 23:00 | 0 | 330 | 300 | Testing A | F790RATA Test - Full Load | Mill Creek | Other | Coal | 2 | 2014 | 6 | 7 | 7 | 2100 | 300 | 300
MC1 | D4 | 117 | 310 | 2014-06-23 23:00 | 2014-06-24 04:25 | 240 | 330 | 300 | Pulverizer mills | F5901A Coal Mill - Inspection & Roller Adjustment | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 5.4167 | 1.4773 | 443.1818 | 81.8182 | 82
MC1 | NC | 118 | 8460 | 2014-06-24 08:00 | 2014-06-24 15:15 | 0 | 330 | 300 | Testing A | F790RATA Test - Full Load | Mill Creek | Other | Coal | 2 | 2014 | 6 | 7.25 | 7.25 | 2175 | 300 | 300
MC1 | D4 | 119 | 310 | 2014-06-24 22:45 | 2014-06-25 08:00 | 235 | 330 | 300 | Pulverizer mills | F5901B Coal Mill - Replace Roller | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 9.25 | 2.6629 | 798.8636 | 86.3636 | 86
MC1 | D4 | 120 | 250 | 2014-06-25 22:05 | 2014-06-26 03:29 | 235 | 330 | 300 | Pulverizer feeders | F0901C Coal Feeder - Calibrate | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 5.4 | 1.5545 | 466.3636 | 86.3636 | 86
MC1 | U1 | 121 | 800 | 2014-06-29 17:28 | 2014-06-29 19:33 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F820High Drum Level Trip due to Control Logic Issue | Mill Creek | Outage | Coal | 2 | 2014 | 6 | 2.0833 | 2.0833 | 625 | 300 | 300
MC1 | NC | 122 | 1850 | 2014-06-29 19:33 | 2014-06-29 23:33 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 2 | 2014 | 6 | 4 | 4 | 1200 | 300 | 300
MC1 | D1 | 123 | 1850 | 2014-06-29 23:33 | 2014-06-30 02:45 | 148 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 3.2 | 1.7648 | 529.4545 | 165.4545 | 165
MC1 | D1 | 124 | 1850 | 2014-06-30 02:45 | 2014-06-30 03:44 | 240 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 0.98333 | 0.26818 | 80.4545 | 81.8182 | 82
MC1 | D1 | 125 | 1850 | 2014-06-30 03:44 | 2014-06-30 06:03 | 290 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 2.3167 | 0.28081 | 84.2424 | 36.3636 | 36
MC1 | NC | 126 | 1990 | 2014-07-02 08:25 | 2014-07-02 10:54 | 0 | 330 | 300 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Capability Test - Max Fire/Max Load | Mill Creek | Other | Coal | 2 | 2014 | 7 | 2.4833 | 2.4833 | 745 | 300 | 300
MC1 | MO | 127 | 1180 | 2014-07-03 22:43 | 2014-07-07 06:00 | 0 | 330 | 300 | Economizer A | F320Economizer Wash | Mill Creek | Maintenance | Coal | 2 | 2014 | 7 | 79.2833 | 79.2833 | 23785 | 300 | 300
MC1 | ME | 128 | 1493 | 2014-07-07 06:00 | 2014-07-08 05:49 | 0 | 330 | 300 | Air heater fouling (regenerative) | F320Air Heater Wash | Mill Creek | Maintenance | Coal | 2 | 2014 | 7 | 23.8167 | 23.8167 | 7145 | 300 | 300
MC1 | D1 | 129 | 360 | 2014-07-09 20:18 | 2014-07-09 21:29 | 250 | 330 | 300 | Burners | F7801C3 Burner - High Temperature | Mill Creek | Derate | Coal | 2 | 2014 | 7 | 1.1833 | 0.28687 | 86.0606 | 72.7273 | 73
MC1 | D1 | 130 | 4261 | 2014-07-12 00:33 | 2014-07-12 02:15 | 260 | 330 | 300 | Control valves | F690#1 Turbine Control Valve stuck closed | Mill Creek | Derate | Coal | 2 | 2014 | 7 | 1.7 | 0.36061 | 108.1818 | 63.6364 | 64
MC1 | D1 | 131 | 360 | 2014-07-17 15:38 | 2014-07-17 16:05 | 250 | 330 | 300 | Burners | F7801C3 Burner - High Temperature | Mill Creek | Derate | Coal | 2 | 2014 | 7 | 0.45 | 0.10909 | 32.7273 | 72.7273 | 73
MC1 | NC | 132 | 8460 | 2014-07-23 09:45 | 2014-07-23 13:58 | 0 | 330 | 300 | Testing A | F790SO3 Test - Full Load | Mill Creek | Other | Coal | 2 | 2014 | 7 | 4.2167 | 4.2167 | 1265 | 300 | 300
MC1 | D1 | 133 | 250 | 2014-07-27 17:40 | 2014-07-27 20:20 | 298 | 330 | 300 | Pulverizer feeders | F5901A Coal Feeder - Reset Microprocessor, gas in | Mill Creek | Derate | Coal | 2 | 2014 | 7 | 2.6667 | 0.25859 | 77.5758 | 29.0909 | 29
MC1 | U1 | 134 | 4499 | 2014-07-29 02:10 | 2014-07-29 06:13 | 0 | 330 | 300 | Other miscellaneous steam turbine problems | F830Turbine Manual Trip | Mill Creek | Outage | Coal | 2 | 2014 | 7 | 4.05 | 4.05 | 1215 | 300 | 300
MC1 | NC | 135 | 1850 | 2014-07-29 06:13 | 2014-07-29 10:10 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 2 | 2014 | 7 | 3.95 | 3.95 | 1185 | 300 | 300
MC1 | D4 | 136 | 310 | 2014-07-30 23:00 | 2014-07-31 03:50 | 240 | 330 | 300 | Pulverizer mills | F5901A Coal Mill - Tempering Air Damper Repair | Mill Creek | Derate | Coal | 2 | 2014 | 7 | 4.8333 | 1.3182 | 395.4545 | 81.8182 | 82
MC1 | D4 | 137 | 310 | 2014-07-31 22:00 | 2014-08-01 03:25 | 240 | 330 | 300 | Pulverizer mills | F5401B Coal Mill - Repair 1B4 Coal Conduit Leak | Mill Creek | Derate | Coal | 2 | 2014 | 7 | 5.4167 | 1.4773 | 443.1818 | 81.8182 | 82
MC1 | NC | 138 | 4490 | 2014-08-07 09:45 | 2014-08-07 17:30 | 0 | 330 | 300 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Full Load - Heat Rate Test | Mill Creek | Other | Coal | 2 | 2014 | 8 | 7.75 | 7.75 | 2325 | 300 | 300
MC1 | NC | 139 | 4490 | 2014-08-08 05:00 | 2014-08-08 07:34 | 0 | 330 | 300 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Heat Rate Test @ 235 MW | Mill Creek | Other | Coal | 2 | 2014 | 8 | 2.5667 | 2.5667 | 770 | 300 | 300
MC1 | NC | 140 | 4490 | 2014-08-08 07:34 | 2014-08-08 11:54 | 0 | 330 | 300 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Heat Rate Test @ 285 MW | Mill Creek | Other | Coal | 2 | 2014 | 8 | 4.3333 | 4.3333 | 1300 | 300 | 300
MC1 | MO | 141 | 8650 | 2014-08-08 22:43 | 2014-08-10 07:56 | 0 | 330 | 300 | Baghouse systems | F590Construction Project Transmission Line Clearance - Install PAC (Powder Activated C | Mill Creek | Maintenance | Coal | 2 | 2014 | 8 | 33.2167 | 33.2167 | 9965 | 300 | 300
MC1 | NC | 142 | 1850 | 2014-08-10 07:56 | 2014-08-10 14:31 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2014 | 8 | 6.5833 | 6.5833 | 1975 | 300 | 300
MC1 | D4 | 143 | 250 | 2014-08-11 22:00 | 2014-08-12 01:32 | 213 | 330 | 300 | Pulverizer feeders | F5901A Coal Feeder - Replace Microprocessor | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 3.5333 | 1.2527 | 375.8182 | 106.3636 | 106
MC1 | NC | 144 | 4490 | 2014-08-12 08:00 | 2014-08-12 12:30 | 0 | 330 | 300 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Full Load Capability Test | Mill Creek | Other | Coal | 2 | 2014 | 8 | 4.5 | 4.5 | 1350 | 300 | 300
MC1 | U1 | 145 | 800 | 2014-08-17 03:38 | 2014-08-17 09:45 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F820High Drum Level Trip - Lost 1D Coal Feeder | Mill Creek | Outage | Coal | 2 | 2014 | 8 | 6.1167 | 6.1167 | 1835 | 300 | 300
MC1 | NC | 146 | 1850 | 2014-08-17 09:45 | 2014-08-17 14:13 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2014 | 8 | 4.4667 | 4.4667 | 1340 | 300 | 300
MC1 | D1 | 147 | 250 | 2014-08-18 20:05 | 2014-08-18 20:30 | 250 | 330 | 300 | Pulverizer feeders | F1201B Coal Feeder - Plugged, Foreign Material | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 0.41667 | 0.10101 | 30.303 | 72.7273 | 73
MC1 | D4 | 148 | 310 | 2014-08-20 23:00 | 2014-08-21 01:01 | 240 | 330 | 300 | Pulverizer mills | F1201A Coal Mill - Foreign Material in Pyrite Chute | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 2.0167 | 0.55 | 165 | 81.8182 | 82
MC1 | NC | 149 | 1160 | 2014-08-23 00:30 | 2014-08-23 04:40 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater, Full Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 8 | 4.1667 | 4.1667 | 1250 | 300 | 300
MC1 | NC | 150 | 1160 | 2014-08-23 22:30 | 2014-08-24 05:18 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater, Full Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 8 | 6.8 | 6.8 | 2040 | 300 | 300
MC1 | D1 | 151 | 3210 | 2014-08-24 23:35 | 2014-08-25 01:14 | 160 | 330 | 300 | Circulating water pumps | F7801A Circulating Water Pump - Upper Guide Bearing High Temperature | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 1.65 | 0.85 | 255 | 154.5455 | 155
MC1 | D1 | 152 | 3211 | 2014-08-25 01:14 | 2014-08-25 08:12 | 260 | 330 | 300 | Circulating water pump motors | F5401A Circulating Water Pump Motor - Cooler Leak Repair | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 6.9667 | 1.4778 | 443.3333 | 63.6364 | 64
MC1 | D1 | 153 | 3211 | 2014-08-25 08:12 | 2014-08-25 15:27 | 290 | 330 | 300 | Circulating water pump motors | F5401A Circulating Water Pump Motor - Cooler Leak Repair | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 7.25 | 0.87879 | 263.6364 | 36.3636 | 36
MC1 | D1 | 154 | 3149 | 2014-08-25 15:27 | 2014-08-26 02:00 | 280 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 10.55 | 1.5985 | 479.5455 | 45.4545 | 45
MC1 | D1 | 155 | 3149 | 2014-08-26 02:00 | 2014-08-26 14:33 | 291 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 12.55 | 1.4832 | 444.9545 | 35.4545 | 35
MC1 | D1 | 156 | 3149 | 2014-08-26 14:33 | 2014-08-26 17:27 | 280 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 2.9 | 0.43939 | 131.8182 | 45.4545 | 45
MC1 | D1 | 157 | 3149 | 2014-08-26 17:27 | 2014-08-26 18:12 | 270 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 0.75 | 0.13636 | 40.9091 | 54.5455 | 55
MC1 | D1 | 158 | 3149 | 2014-08-26 18:12 | 2014-08-26 20:30 | 275 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 2.3 | 0.38333 | 115 | 50 | 50
MC1 | D1 | 159 | 3149 | 2014-08-26 20:30 | 2014-08-26 23:45 | 280 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 3.25 | 0.49242 | 147.7273 | 45.4545 | 45
MC1 | D1 | 160 | 3149 | 2014-08-26 23:45 | 2014-08-27 10:37 | 290 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 10.8667 | 1.3172 | 395.1515 | 36.3636 | 36
MC1 | D1 | 161 | 3149 | 2014-08-27 10:37 | 2014-08-27 12:02 | 286 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 1.4167 | 0.18889 | 56.6667 | 40 | 40
MC1 | D1 | 162 | 3149 | 2014-08-27 12:02 | 2014-08-27 13:57 | 280 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 1.9167 | 0.2904 | 87.1212 | 45.4545 | 45
MC1 | D1 | 163 | 3149 | 2014-08-27 13:57 | 2014-08-27 21:00 | 275 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 7.05 | 1.175 | 352.5 | 50 | 50
MC1 | D4 | 164 | 310 | 2014-08-27 21:00 | 2014-08-28 03:35 | 240 | 330 | 300 | Pulverizer mills | F5901A Coal Mill - Adjust Rollers | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 6.5833 | 1.7955 | 538.6364 | 81.8182 | 82
MC1 | D1 | 165 | 3149 | 2014-08-28 03:35 | 2014-08-28 09:56 | 275 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 6.35 | 1.0583 | 317.5 | 50 | 50
MC1 | D1 | 166 | 3149 | 2014-08-28 09:56 | 2014-08-28 15:31 | 270 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 5.5833 | 1.0152 | 304.5455 | 54.5455 | 55
MC1 | D1 | 167 | 3149 | 2014-08-28 15:31 | 2014-08-28 23:11 | 265 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 7.6667 | 1.5101 | 453.0303 | 59.0909 | 59
MC1 | D1 | 168 | 3149 | 2014-08-28 23:11 | 2014-08-29 12:30 | 275 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 13.3167 | 2.2194 | 665.8333 | 50 | 50
MC1 | D4 | 169 | 3210 | 2014-08-29 01:00 | 2014-08-29 02:26 | 150 | 330 | 300 | Circulating water pumps | F6301A Circulating Water Pump - Put in Service | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 1.4333 | 0.78182 | 234.5455 | 163.6364 | 164
MC1 | D1 | 170 | 3149 | 2014-08-29 12:30 | 2014-08-29 22:10 | 260 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 9.6667 | 2.0505 | 615.1515 | 63.6364 | 64
MC1 | D1 | 171 | 3149 | 2014-08-29 22:10 | 2014-08-30 10:21 | 270 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 12.1833 | 2.2152 | 664.5455 | 54.5455 | 55
MC1 | D1 | 172 | 3149 | 2014-08-30 10:21 | 2014-08-30 12:25 | 265 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 2.0667 | 0.40707 | 122.1212 | 59.0909 | 59
MC1 | D1 | 173 | 3149 | 2014-08-30 12:25 | 2014-08-31 00:30 | 260 | 330 | 300 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 12.0833 | 2.5631 | 768.9394 | 63.6364 | 64
MC1 | D4 | 174 | 250 | 2014-09-02 22:00 | 2014-09-03 00:15 | 240 | 330 | 300 | Pulverizer feeders | F1201C Coal Feeder - Foreign Metal in Chute | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 2.25 | 0.61364 | 184.0909 | 81.8182 | 82
MC1 | D1 | 175 | 310 | 2014-09-18 22:25 | 2014-09-19 01:56 | 240 | 330 | 300 | Pulverizer mills | F5301C Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 3.5167 | 0.95909 | 287.7273 | 81.8182 | 82
MC1 | D1 | 176 | 310 | 2014-09-22 10:36 | 2014-09-22 12:03 | 300 | 330 | 300 | Pulverizer mills | F5301C Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 1.45 | 0.13182 | 39.5455 | 27.2727 | 27
MC1 | D1 | 177 | 310 | 2014-09-22 12:03 | 2014-09-22 14:58 | 250 | 330 | 300 | Pulverizer mills | F5901C Coal Mill - Adjusted Rollers | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 2.9167 | 0.70707 | 212.1212 | 72.7273 | 73
MC1 | D1 | 178 | 310 | 2014-09-23 01:06 | 2014-09-23 02:57 | 250 | 330 | 300 | Pulverizer mills | F5301A Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 1.85 | 0.44848 | 134.5455 | 72.7273 | 73
MC1 | D4 | 179 | 250 | 2014-09-23 22:00 | 2014-09-24 04:04 | 250 | 330 | 300 | Pulverizer feeders | F0901A Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 6.0667 | 1.4707 | 441.2121 | 72.7273 | 73
MC1 | D4 | 180 | 250 | 2014-09-24 22:00 | 2014-09-25 03:38 | 250 | 330 | 300 | Pulverizer feeders | F0901B Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 5.6333 | 1.3657 | 409.697 | 72.7273 | 73
MC1 | D4 | 181 | 250 | 2014-09-25 22:00 | 2014-09-26 03:59 | 240 | 330 | 300 | Pulverizer feeders | F0901C Coal Feeder - Calibration | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 5.9833 | 1.6318 | 489.5455 | 81.8182 | 82
MC1 | D4 | 182 | 310 | 2014-09-28 21:00 | 2014-09-29 03:25 | 240 | 330 | 300 | Pulverizer mills | F5901D Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 6.4167 | 1.75 | 525 | 81.8182 | 82
MC1 | D4 | 183 | 250 | 2014-09-29 22:00 | 2014-09-30 05:49 | 240 | 330 | 300 | Pulverizer feeders | F0901D Coal Feeder - Calibration | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 7.8167 | 2.1318 | 639.5455 | 81.8182 | 82
MC1 | D1 | 184 | 1488 | 2014-10-09 23:05 | 2014-10-10 00:30 | 240 | 330 | 300 | Air heater (regenerative) | F7801B Air Heater Guide Bearing - High Temperature due to Low Oil Flow | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 1.4167 | 0.38636 | 115.9091 | 81.8182 | 82
MC1 | D1 | 185 | 1488 | 2014-10-10 00:30 | 2014-10-10 03:25 | 205 | 330 | 300 | Air heater (regenerative) | F7801B Air Heater Guide Bearing - High Temperature due to Low Oil Flow | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 2.9167 | 1.1048 | 331.4394 | 113.6364 | 114
MC1 | D4 | 186 | 310 | 2014-10-19 21:00 | 2014-10-20 00:27 | 240 | 330 | 300 | Pulverizer mills | F5901A Coal Mill - Adjusted Rollers | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 3.45 | 0.94091 | 282.2727 | 81.8182 | 82
MC1 | D1 | 187 | 1475 | 2014-10-26 08:50 | 2014-10-26 10:20 | 226 | 330 | 300 | Induced draft fan controls | F5901B Induced Draft Fan - Beck Drive Issues | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 1.5 | 0.47273 | 141.8182 | 94.5455 | 95
MC1 | D1 | 188 | 360 | 2014-10-27 05:55 | 2014-10-27 06:47 | 250 | 330 | 300 | Burners | F7801B Coal Mill - 1B1 Burner High Temperature | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 0.86667 | 0.2101 | 63.0303 | 72.7273 | 73
MC1 | D4 | 189 | 1475 | 2014-10-28 22:56 | 2014-10-29 02:15 | 135 | 330 | 300 | Induced draft fan controls | F5901B Induced Draft Fan - Replace Beck Drive, Gas In Service | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 3.3167 | 1.9598 | 587.9545 | 177.2727 | 177
MC1 | D1 | 190 | 1475 | 2014-10-29 05:30 | 2014-10-29 07:20 | 250 | 330 | 300 | Induced draft fan controls | F5901B Induced Draft Fan - Beck Drive Calibration Adjustment | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 1.8333 | 0.44444 | 133.3333 | 72.7273 | 73
MC1 | D1 | 191 | 1475 | 2014-10-29 07:20 | 2014-10-29 23:07 | 320 | 330 | 300 | Induced draft fan controls | F4001B Induced Draft Fan - Beck Drive Maxed | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 15.7833 | 0.47828 | 143.4848 | 9.0909 | 9
MC1 | D4 | 192 | 1475 | 2014-10-29 23:07 | 2014-10-30 02:27 | 135 | 330 | 300 | Induced draft fan controls | F0901B Induced Draft Fan - Beck Drive Calibrated | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 3.3333 | 1.9697 | 590.9091 | 177.2727 | 177
MC1 | D1 | 193 | 1160 | 2014-10-30 17:54 | 2014-10-30 19:22 | 305 | 330 | 300 | First reheater B | F320Boiler Pluggage - First Reheater Slag | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 1.4667 | 0.11111 | 33.3333 | 22.7273 | 23
MC1 | D1 | 194 | 1160 | 2014-10-30 19:22 | 2014-10-30 20:06 | 280 | 330 | 300 | First reheater B | F320Boiler Pluggage - First Reheater Slag | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 0.73333 | 0.11111 | 33.3333 | 45.4545 | 45
MC1 | NC | 195 | 1160 | 2014-10-30 20:06 | 2014-10-30 23:00 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater, Gas In Service, Full Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 10 | 2.9 | 2.9 | 870 | 300 | 300
MC1 | D1 | 196 | 1160 | 2014-10-30 23:00 | 2014-10-31 03:36 | 295 | 330 | 300 | First reheater B | F320Boiler Pluggage - First Reheater Slag | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 4.6 | 0.48788 | 146.3636 | 31.8182 | 32
MC1 | D1 | 197 | 1160 | 2014-10-31 05:20 | 2014-10-31 05:52 | 295 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 0.53333 | 0.056566 | 16.9697 | 31.8182 | 32
MC1 | D1 | 198 | 1160 | 2014-10-31 05:52 | 2014-10-31 08:27 | 275 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 2.5833 | 0.43056 | 129.1667 | 50 | 50
MC1 | D1 | 199 | 1160 | 2014-10-31 08:27 | 2014-10-31 14:43 | 250 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 10 | 6.2667 | 1.5192 | 455.7576 | 72.7273 | 73
MC1 | D1 | 200 | 4261 | 2014-11-01 00:02 | 2014-11-01 01:32 | 224 | 330 | 300 | Control valves | F720Turbine #1 Control Valve - Stuck Closed | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 1.5 | 0.48182 | 144.5455 | 96.3636 | 96
MC1 | D1 | 201 | 4261 | 2014-11-05 06:30 | 2014-11-05 08:22 | 194 | 330 | 300 | Control valves | F400Turbine Control Valves - Position Indication Feedback | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 1.8667 | 0.76929 | 230.7879 | 123.6364 | 124
MC1 | D1 | 202 | 250 | 2014-11-05 13:20 | 2014-11-05 17:32 | 268 | 330 | 300 | Pulverizer feeders | F1201D Coal Feeder - Rock on Belt | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 4.2 | 0.78909 | 236.7273 | 56.3636 | 56
MC1 | D4 | 203 | 310 | 2014-11-05 22:00 | 2014-11-06 03:02 | 250 | 330 | 300 | Pulverizer mills | F5301D Coal Mill - Inspect Hot Air Damper | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 5.0333 | 1.2202 | 366.0606 | 72.7273 | 73
MC1 | D1 | 204 | 250 | 2014-11-06 09:44 | 2014-11-06 11:18 | 275 | 330 | 300 | Pulverizer feeders | F1201D Coal Feeder - Rock on Belt | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 1.5667 | 0.26111 | 78.3333 | 50 | 50
MC1 | D1 | 205 | 1160 | 2014-11-19 07:21 | 2014-11-19 12:32 | 270 | 330 | 300 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 5.1833 | 0.94242 | 282.7273 | 54.5455 | 55
MC1 | D1 | 206 | 1160 | 2014-11-19 12:32 | 2014-11-19 20:30 | 240 | 330 | 300 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 7.9667 | 2.1727 | 651.8182 | 81.8182 | 82
MC1 | D4 | 207 | 1160 | 2014-11-19 20:30 | 2014-11-20 00:43 | 150 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 4.2167 | 2.3 | 690 | 163.6364 | 164
MC1 | D1 | 208 | 1160 | 2014-11-20 10:14 | 2014-11-20 10:34 | 300 | 330 | 300 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 0.33333 | 0.030303 | 9.0909 | 27.2727 | 27
MC1 | D1 | 209 | 1160 | 2014-11-20 10:34 | 2014-11-20 11:00 | 264 | 330 | 300 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 0.43333 | 0.086667 | 26 | 60 | 60
MC1 | NC | 210 | 1160 | 2014-11-20 11:00 | 2014-11-20 17:47 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2014 | 11 | 6.7833 | 6.7833 | 2035 | 300 | 300
MC1 | D1 | 211 | 1160 | 2014-11-20 17:47 | 2014-11-20 23:30 | 266 | 330 | 300 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 5.7167 | 1.1087 | 332.6061 | 58.1818 | 58
MC1 | D1 | 212 | 1160 | 2014-11-20 23:30 | 2014-11-21 06:05 | 150 | 330 | 300 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 6.5833 | 3.5909 | 1077.2727 | 163.6364 | 164
MC1 | D1 | 213 | 1160 | 2014-11-21 06:05 | 2014-11-21 12:29 | 250 | 330 | 300 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 6.4 | 1.5515 | 465.4545 | 72.7273 | 73
MC1 | MO | 214 | 3344 | 2014-11-22 13:17 | 2014-11-29 09:04 | 0 | 330 | 300 | Deaerator (including level control) | F590Deaerator Heater - Leak Repair | Mill Creek | Maintenance | Coal | 2 | 2014 | 11 | 163.7833 | 163.7833 | 49135 | 300 | 300
MC1 | NC | 215 | 1850 | 2014-11-29 09:04 | 2014-11-30 01:00 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 2 | 2014 | 11 | 15.9333 | 15.9333 | 4780 | 300 | 300
MC1 | D4 | 216 | 310 | 2014-12-04 23:00 | 2014-12-05 04:15 | 250 | 330 | 300 | Pulverizer mills | F5901C Coal Mill Exhauster - Clean | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 5.25 | 1.2727 | 381.8182 | 72.7273 | 73
MC1 | D1 | 217 | 1850 | 2014-12-09 06:10 | 2014-12-09 08:10 | 300 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 2 | 0.18182 | 54.5455 | 27.2727 | 27
MC1 | D1 | 218 | 1850 | 2014-12-09 08:10 | 2014-12-09 16:00 | 255 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 7.8333 | 1.7803 | 534.0909 | 68.1818 | 68
MC1 | D1 | 219 | 1850 | 2014-12-09 16:00 | 2014-12-10 20:22 | 280 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 28.3667 | 4.298 | 1289.3939 | 45.4545 | 45
MC1 | D1 | 220 | 1850 | 2014-12-10 20:22 | 2014-12-12 04:08 | 236 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 31.7667 | 9.0487 | 2714.6061 | 85.4545 | 85
MC1 | D1 | 221 | 1850 | 2014-12-12 04:08 | 2014-12-14 16:30 | 230 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 60.3667 | 18.2929 | 5487.8788 | 90.9091 | 91
MC1 | D1 | 222 | 1850 | 2014-12-14 16:30 | 2014-12-15 02:38 | 280 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 10.1333 | 1.5354 | 460.6061 | 45.4545 | 45
MC1 | D1 | 223 | 1850 | 2014-12-15 02:38 | 2014-12-15 10:50 | 295 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 8.2 | 0.8697 | 260.9091 | 31.8182 | 32
MC1 | D1 | 224 | 1850 | 2014-12-15 10:50 | 2014-12-18 08:50 | 315 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 70 | 3.1818 | 954.5455 | 13.6364 | 14
MC1 | D1 | 225 | 1850 | 2014-12-18 08:50 | 2014-12-18 10:20 | 325 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 1.5 | 0.022727 | 6.8182 | 4.5455 | 5
MC1 | MO | 226 | 9720 | 2014-12-20 23:25 | 2014-12-23 00:49 | 0 | 330 | 300 | Other safety problems | FX00FGD Ductwork - Zachry Making Lift | Mill Creek | Maintenance | Coal | 2 | 2014 | 12 | 49.4 | 49.4 | 14820 | 300 | 300
MC1 | D1 | 227 | 1850 | 2014-12-23 09:34 | 2014-12-23 14:51 | 268 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 5.2833 | 0.99263 | 297.7879 | 56.3636 | 56
MC1 | D1 | 228 | 1850 | 2014-12-23 14:51 | 2014-12-24 00:53 | 300 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 10.0333 | 0.91212 | 273.6364 | 27.2727 | 27
MC1 | MO | 1 | 3344 | 2015-01-14 23:46 | 2015-01-16 23:13 | 0 | 330 | 300 | Deaerator (including level control) | F540Deaerator Heater Leak | Mill Creek | Maintenance | Coal | 2 | 2015 | 1 | 47.45 | 47.45 | 14235 | 300 | 300
MC1 | NC | 2 | 1850 | 2015-01-16 23:13 | 2015-01-17 06:32 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2015 | 1 | 7.3167 | 7.3167 | 2195 | 300 | 300
MC1 | D1 | 3 | 1850 | 2015-01-17 06:32 | 2015-01-17 09:47 | 265 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 1 | 3.25 | 0.64015 | 192.0455 | 59.0909 | 59
MC1 | NC | 4 | 9999 | 2015-02-02 06:47 | 2015-02-02 13:06 | 0 | 330 | 300 | Total unit performance testing (use appropriate codes for individual component testing) | F790Winter full load capability test | Mill Creek | Other | Coal | 2 | 2015 | 2 | 6.3167 | 6.3167 | 1895 | 300 | 300
MC1 | MO | 5 | 3110 | 2015-02-07 00:32 | 2015-02-08 10:15 | 0 | 330 | 300 | Condenser tube leaks | F540Condenser tube leak | Mill Creek | Maintenance | Coal | 2 | 2015 | 2 | 33.7167 | 33.7167 | 10115 | 300 | 300
MC1 | NC | 6 | 1850 | 2015-02-08 10:15 | 2015-02-08 16:25 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica at hot start up | Mill Creek | Other | Coal | 2 | 2015 | 2 | 6.1667 | 6.1667 | 1850 | 300 | 300
MC1 | D1 | 7 | 1850 | 2015-02-08 16:25 | 2015-02-08 18:39 | 234 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2015 | 2 | 2.2333 | 0.6497 | 194.9091 | 87.2727 | 87
MC1 | D1 | 8 | 1850 | 2015-02-08 18:39 | 2015-02-08 23:00 | 270 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2015 | 2 | 4.35 | 0.79091 | 237.2727 | 54.5455 | 55
MC1 | D1 | 9 | 250 | 2015-02-10 03:24 | 2015-02-10 05:04 | 255 | 330 | 300 | Pulverizer feeders | F5901D Feeder - Replaced belt | Mill Creek | Derate | Coal | 2 | 2015 | 2 | 1.6667 | 0.37879 | 113.6364 | 68.1818 | 68
MC1 | D1 | 10 | 8260 | 2015-02-21 20:10 | 2015-02-21 21:39 | 240 | 330 | 300 | Scrubber booster I.D. fan (fan specific to the scrubber) | F5401A Booster Fan - service water leak | Mill Creek | Derate | Coal | 2 | 2015 | 2 | 1.4833 | 0.40455 | 121.3636 | 81.8182 | 82
MC1 | NC | 11 | 9690 | 2015-02-25 09:00 | 2015-02-25 11:47 | 0 | 330 | 300 | Other miscellaneous operational environmental limits (fossil and nuclear) | F790MATS Testing - Full Load | Mill Creek | Other | Coal | 2 | 2015 | 2 | 2.7833 | 2.7833 | 835 | 300 | 300
MC1 | D1 | 12 | 8127 | 2015-03-01 11:16 | 2015-03-01 14:06 | 290 | 330 | 300 | Scrubber recycle (liquid) pump motors | F5901B1 Recycle Pump - Oil Change | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 2.8333 | 0.34343 | 103.0303 | 36.3636 | 36
MC1 | D1 | 13 | 8127 | 2015-03-02 08:37 | 2015-03-02 08:59 | 320 | 330 | 300 | Scrubber recycle (liquid) pump motors | F590Recycle pump issues | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 0.36667 | 0.011111 | 3.3333 | 9.0909 | 9
MC1 | D1 | 14 | 8127 | 2015-03-02 09:39 | 2015-03-02 12:00 | 180 | 330 | 300 | Scrubber recycle (liquid) pump motors | F590Recycle Pump Issues | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 2.35 | 1.0682 | 320.4545 | 136.3636 | 136
MC1 | D1 | 15 | 8127 | 2015-03-02 12:00 | 2015-03-03 22:00 | 300 | 330 | 300 | Scrubber recycle (liquid) pump motors | F590Recycle pump issues | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 34 | 3.0909 | 927.2727 | 27.2727 | 27
MC1 | D4 | 16 | 8280 | 2015-03-03 22:00 | 2015-03-04 02:23 | 150 | 330 | 300 | Reagent feed piping | F590Reactant Feed Line Repair | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 4.3833 | 2.3909 | 717.2727 | 163.6364 | 164
MC1 | D1 | 17 | 8127 | 2015-03-04 02:23 | 2015-03-04 23:36 | 300 | 330 | 300 | Scrubber recycle (liquid) pump motors | F590Recycle Pump issues | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 21.2167 | 1.9288 | 578.6364 | 27.2727 | 27
MC1 | D1 | 18 | 250 | 2015-03-04 23:36 | 2015-03-05 18:58 | 230 | 330 | 300 | Pulverizer feeders | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 19.3667 | 5.8687 | 1760.6061 | 90.9091 | 91
MC1 | D1 | 19 | 8127 | 2015-03-05 18:58 | 2015-03-06 04:30 | 230 | 330 | 300 | Scrubber recycle (liquid) pump motors | F590Recycle Pump Issues | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 9.5333 | 2.8889 | 866.6667 | 90.9091 | 91
MC1 | D1 | 20 | 250 | 2015-03-06 04:30 | 2015-03-07 08:08 | 237 | 330 | 300 | Pulverizer feeders | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 27.6333 | 7.7876 | 2336.2727 | 84.5455 | 85
MC1 | D1 | 21 | 8127 | 2015-03-07 08:08 | 2015-03-07 14:41 | 260 | 330 | 300 | Scrubber recycle (liquid) pump motors | F590Recycle Pump Issues | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 6.55 | 1.3894 | 416.8182 | 63.6364 | 64
MC1 | D1 | 22 | 250 | 2015-03-12 16:45 | 2015-03-12 17:10 | 230 | 330 | 300 | Pulverizer feeders | F120B Mill Coal Feeder Pluggage | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 0.41667 | 0.12626 | 37.8788 | 90.9091 | 91
MC1 | D1 | 23 | 250 | 2015-03-12 17:10 | 2015-03-12 23:00 | 100 | 330 | 300 | Pulverizer feeders | F120B,C,D Mill Coal Feeders Plugged | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 5.8333 | 4.0657 | 1219.697 | 209.0909 | 209
MC1 | D1 | 24 | 8125 | 2015-03-14 14:52 | 2015-03-14 19:40 | 270 | 330 | 300 | Scrubber recycle (liquid) pumps | F590FGD 1B1 Recycle Pump - Belts Burnt Off | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 4.8 | 0.87273 | 261.8182 | 54.5455 | 55
MC1 | D1 | 25 | 250 | 2015-03-14 22:45 | 2015-03-15 00:21 | 250 | 330 | 300 | Pulverizer feeders | F5901D Coal Feeder - Belt Tracking Issue | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 1.6 | 0.38788 | 116.3636 | 72.7273 | 73
MC1 | D1 | 26 | 8125 | 2015-03-15 02:55 | 2015-03-15 14:40 | 270 | 330 | 300 | Scrubber recycle (liquid) pumps | F540FGD 1B3 Recycle Pump - Seal Leaking | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 11.75 | 2.1364 | 640.9091 | 54.5455 | 55
MC1 | D1 | 27 | 8125 | 2015-03-16 03:50 | 2015-03-23 10:16 | 270 | 330 | 300 | Scrubber recycle (liquid) pumps | F060FGD 1B3 Recycle Pump - Bearing Issue | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 174.4333 | 31.7152 | 9514.5455 | 54.5455 | 55
MC1 | PO | 28 | 8440 | 2015-03-23 10:16 | 2015-05-18 | 0 | 330 | 300 | Major overhaul C | F590Planned 8 Week Outage | Mill Creek | Other | Coal | 2 | 2015 | 3 | 1333.7333 | 1333.7333 | 400120 | 300 | 300
MC1 | U1 | 29 | 1488 | 2015-05-18 | 2015-05-23 07:35 | 0 | 330 | 300 | Air heater (regenerative) | F080Air pre-heater baskets | Mill Creek | Outage | Coal | 2 | 2015 | 5 | 127.5833 | 127.5833 | 38275 | 300 | 300
MC1 | NC | 30 | 1850 | 2015-05-23 07:35 | 2015-05-24 16:31 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica at cold start | Mill Creek | Other | Coal | 2 | 2015 | 5 | 32.9333 | 32.9333 | 9880 | 300 | 300
MC1 | U1 | 31 | 4630 | 2015-05-24 16:31 | 2015-05-24 23:31 | 0 | 330 | 300 | Liquid cooling system | F890Generator Stator manual drain weld | Mill Creek | Outage | Coal | 2 | 2015 | 5 | 7 | 7 | 2100 | 300 | 300
MC1 | NC | 32 | 1850 | 2015-05-24 23:31 | 2015-05-26 08:00 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ start-up | Mill Creek | Other | Coal | 2 | 2015 | 5 | 32.4833 | 32.4833 | 9745 | 300 | 300
MC1 | NC | 33 | 8650 | 2015-05-26 08:00 | 2015-05-26 20:14 | 0 | 330 | 300 | Baghouse systems | F790Baghouse Testing | Mill Creek | Other | Coal | 2 | 2015 | 5 | 12.2333 | 12.2333 | 3670 | 300 | 300
MC1 | U1 | 34 | 4630 | 2015-05-26 21:22 | 2015-05-27 05:04 | 0 | 330 | 300 | Liquid cooling system | F890Generator stator manual drain weld | Mill Creek | Outage | Coal | 2 | 2015 | 5 | 7.7 | 7.7 | 2310 | 300 | 300
MC1 | NC | 35 | 1850 | 2015-05-27 05:04 | 2015-05-27 11:22 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica @ hot start-up | Mill Creek | Other | Coal | 2 | 2015 | 5 | 6.3 | 6.3 | 1890 | 300 | 300
MC1 | D1 | 36 | 1850 | 2015-05-27 11:22 | 2015-05-27 13:48 | 255 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 2.4333 | 0.55303 | 165.9091 | 68.1818 | 68
MC1 | D1 | 37 | 1850 | 2015-05-27 13:48 | 2015-05-28 03:22 | 292 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 13.5667 | 1.5622 | 468.6667 | 34.5455 | 35
MC1 | D1 | 38 | 1850 | 2015-05-28 03:22 | 2015-05-28 05:58 | 303 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 2.6 | 0.21273 | 63.8182 | 24.5455 | 25
MC1 | NC | 39 | 8650 | 2015-05-28 08:00 | 2015-05-28 19:18 | 0 | 330 | 300 | Baghouse systems | F790Baghouse testing | Mill Creek | Other | Coal | 2 | 2015 | 5 | 11.3 | 11.3 | 3390 | 300 | 300
MC1 | D4 | 40 | 310 | 2015-05-28 23:00 | 2015-05-29 01:29 | 240 | 330 | 300 | Pulverizer mills | F5901A Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 2.4833 | 0.67727 | 203.1818 | 81.8182 | 82
MC1 | NC | 41 | 8650 | 2015-05-29 08:00 | 2015-05-29 13:05 | 0 | 330 | 300 | Baghouse systems | F790Baghouse testing | Mill Creek | Other | Coal | 2 | 2015 | 5 | 5.0833 | 5.0833 | 1525 | 300 | 300
MC1 | NC | 42 | 8650 | 2015-05-30 08:00 | 2015-05-30 17:12 | 0 | 330 | 300 | Baghouse systems | F790Baghouse testing | Mill Creek | Other | Coal | 2 | 2015 | 5 | 9.2 | 9.2 | 2760 | 300 | 300
MC1 | MO | 43 | 775 | 2015-06-02 09:51 | 2015-06-03 04:46 | 0 | 330 | 300 | Economizer piping | F540Economizer recirc line repair | Mill Creek | Maintenance | Coal | 2 | 2015 | 6 | 18.9167 | 18.9167 | 5675 | 300 | 300
MC1 | NC | 44 | 1850 | 2015-06-03 04:46 | 2015-06-03 13:33 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ hot start | Mill Creek | Other | Coal | 2 | 2015 | 6 | 8.7833 | 8.7833 | 2635 | 300 | 300
MC1 | D1 | 45 | 310 | 2015-06-03 19:10 | 2015-06-04 00:47 | 250 | 330 | 300 | Pulverizer mills | F5901B Coal Mill | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 5.6167 | 1.3616 | 408.4848 | 72.7273 | 73
MC1 | NC | 46 | 1990 | 2015-06-04 08:10 | 2015-06-04 19:43 | 0 | 330 | 300 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Boiler tuning | Mill Creek | Other | Coal | 2 | 2015 | 6 | 11.55 | 11.55 | 3465 | 300 | 300
MC1 | NC | 47 | 8460 | 2015-06-05 07:06 | 2015-06-05 15:26 | 0 | 330 | 300 | Testing A | F790Full Load testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 8.3333 | 8.3333 | 2500 | 300 | 300
MC1 | NC | 48 | 8460 | 2015-06-06 11:42 | 2015-06-06 12:25 | 0 | 330 | 300 | Testing A | F790Full load testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 0.71667 | 0.71667 | 215 | 300 | 300
MC1 | D1 | 49 | 310 | 2015-06-06 12:25 | 2015-06-06 14:55 | 245 | 330 | 300 | Pulverizer mills | F590B Mill roller maintenance | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 2.5 | 0.64394 | 193.1818 | 77.2727 | 77
MC1 | NC | 50 | 8460 | 2015-06-06 14:55 | 2015-06-06 17:30 | 0 | 330 | 300 | Testing A | F790Full Load testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 2.5833 | 2.5833 | 775 | 300 | 300
MC1 | D1 | 51 | 4262 | 2015-06-06 18:30 | 2015-06-06 21:25 | 300 | 330 | 300 | Intercept valves | F720#2 Reheat intercept valve stuck | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 2.9167 | 0.26515 | 79.5455 | 27.2727 | 27
MC1 | NC | 52 | 8460 | 2015-06-07 08:30 | 2015-06-07 17:23 | 0 | 330 | 300 | Testing A | F790Low load testing. Full load available if load dispatch needed it. | Mill Creek | Other | Coal | 2 | 2015 | 6 | 8.8833 | 8.8833 | 2665 | 300 | 300
MC1 | U1 | 53 | 800 | 2015-06-08 02:28 | 2015-06-08 03:47 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F660Pressure swing bringing mill online | Mill Creek | Outage | Coal | 2 | 2015 | 6 | 1.3167 | 1.3167 | 395 | 300 | 300
MC1 | NC | 54 | 1850 | 2015-06-08 03:47 | 2015-06-08 08:49 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica @ very hot start | Mill Creek | Other | Coal | 2 | 2015 | 6 | 5.0333 | 5.0333 | 1510 | 300 | 300
MC1 | NC | 55 | 8460 | 2015-06-08 11:15 | 2015-06-08 18:25 | 0 | 330 | 300 | Testing A | F790Full Load Testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 7.1667 | 7.1667 | 2150 | 300 | 300
MC1 | D1 | 56 | 310 | 2015-06-08 19:35 | 2015-06-08 23:00 | 250 | 330 | 300 | Pulverizer mills | F5901B Coal Mill roller | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 3.4167 | 0.82828 | 248.4848 | 72.7273 | 73
MC1 | NC | 57 | 8460 | 2015-06-09 12:00 | 2015-06-09 14:08 | 0 | 330 | 300 | Testing A | F790Full Load Testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 2.1333 | 2.1333 | 640 | 300 | 300
MC1 | D4 | 58 | 310 | 2015-06-09 22:00 | 2015-06-10 02:16 | 250 | 330 | 300 | Pulverizer mills | F590Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 4.2667 | 1.0343 | 310.303 | 72.7273 | 73
MC1 | NC | 59 | 8460 | 2015-06-10 02:16 | 2015-06-10 04:23 | 0 | 330 | 300 | Testing A | F790Low Load RATA Testing - Load available if needed | Mill Creek | Other | Coal | 2 | 2015 | 6 | 2.1167 | 2.1167 | 635 | 300 | 300
MC1 | NC | 60 | 8460 | 2015-06-10 04:23 | 2015-06-10 05:30 | 0 | 330 | 300 | Testing A | F790Mid Load RATA Testing - Load available if needed | Mill Creek | Other | Coal | 2 | 2015 | 6 | 1.1167 | 1.1167 | 335 | 300 | 300
MC1 | D1 | 61 | 310 | 2015-06-10 05:30 | 2015-06-10 06:10 | 250 | 330 | 300 | Pulverizer mills | F5901B Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 0.66667 | 0.16162 | 48.4848 | 72.7273 | 73
MC1 | D1 | 62 | 310 | 2015-06-10 06:49 | 2015-06-10 09:07 | 270 | 330 | 300 | Pulverizer mills | F5901B Coal Mill | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 2.3 | 0.41818 | 125.4545 | 54.5455 | 55
MC1 | NC | 63 | 8460 | 2015-06-10 09:07 | 2015-06-10 15:53 | 0 | 330 | 300 | Testing A | F790Full Load Testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 6.7667 | 6.7667 | 2030 | 300 | 300
MC1 | D4 | 64 | 310 | 2015-06-10 23:22 | 2015-06-11 01:46 | 250 | 330 | 300 | Pulverizer mills | F5901A Coal Mill | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 2.4 | 0.58182 | 174.5455 | 72.7273 | 73
MC1 | NC | 65 | 8460 | 2015-06-11 01:46 | 2015-06-11 04:15 | 0 | 330 | 300 | Testing A | F790Low Load RATA Testing - Load available if needed | Mill Creek | Other | Coal | 2 | 2015 | 6 | 2.4833 | 2.4833 | 745 | 300 | 300
MC1 | NC | 66 | 8460 | 2015-06-11 04:15 | 2015-06-11 07:34 | 0 | 330 | 300 | Testing A | F790Mid Load RATA Testing - Load available if needed | Mill Creek | Other | Coal | 2 | 2015 | 6 | 3.3167 | 3.3167 | 995 | 300 | 300
MC1 | D4 | 67 | 310 | 2015-06-11 23:00 | 2015-06-12 04:08 | 250 | 330 | 300 | Pulverizer mills | F5901D Coal Mill General Maintenance | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 5.1333 | 1.2444 | 373.3333 | 72.7273 | 73
MC1 | D4 | 68 | 310 | 2015-06-15 23:00 | 2015-06-16 04:38 | 250 | 330 | 300 | Pulverizer mills | F5901D Coal Mill - Adjusted Rollers | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 5.6333 | 1.3657 | 409.697 | 72.7273 | 73
MC1 | D4 | 69 | 310 | 2015-06-17 23:00 | 2015-06-18 05:36 | 240 | 330 | 300 | Pulverizer mills | F5901B Coal Mill - Adjusted Roller | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 6.6 | 1.8 | 540 | 81.8182 | 82
MC1 | NC | 70 | 8650 | 2015-06-23 08:00 | 2015-06-23 17:26 | 0 | 330 | 300 | Baghouse systems | F790Full Load testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 9.4333 | 9.4333 | 2830 | 300 | 300
MC1 | NC | 71 | 1160 | 2015-06-23 23:30 | 2015-06-24 04:24 | 0 | 330 | 300 | First reheater B | F320Boiler Deslag - Load available as needed | Mill Creek | Other | Coal | 2 | 2015 | 6 | 4.9 | 4.9 | 1470 | 300 | 300
MC1 | NC | 72 | 8460 | 2015-06-24 09:00 | 2015-06-24 17:24 | 0 | 330 | 300 | Testing A | F790Full load testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 8.4 | 8.4 | 2520 | 300 | 300
MC1 | NC | 73 | 8650 | 2015-06-25 08:00 | 2015-06-25 14:26 | 0 | 330 | 300 | Baghouse systems | F790Full load PM testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 6.4333 | 6.4333 | 1930 | 300 | 300
MC1 | MO | 74 | 3110 | 2015-06-26 20:41 | 2015-06-27 20:13 | 0 | 330 | 300 | Condenser tube leaks | F540Condenser leak | Mill Creek | Maintenance | Coal | 2 | 2015 | 6 | 23.5333 | 23.5333 | 7060 | 300 | 300
MC1 | NC | 76 | 1850 | 2015-06-29 06:08 | 2015-06-29 14:13 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica @ warm start | Mill Creek | Other | Coal | 2 | 2015 | 6 | 8.0833 | 8.0833 | 2425 | 300 | 300
MC1 | D1 | 77 | 1850 | 2015-06-29 14:13 | 2015-06-29 14:44 | 309 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 0.51667 | 0.032879 | 9.8636 | 19.0909 | 19
MC1 | D1 | 78 | 1850 | 2015-06-29 14:44 | 2015-06-29 15:48 | 325 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 1.0667 | 0.016162 | 4.8485 | 4.5455 | 5
MC1 | NC | 79 | 1488 | 2015-07-08 12:00 | 2015-07-08 13:15 | 0 | 330 | 300 | Air heater (regenerative) | F790Full Load Testing - Air heater | Mill Creek | Other | Coal | 2 | 2015 | 7 | 1.25 | 1.25 | 375 | 300 | 300
MC1 | NC | 80 | 9999 | 2015-07-09 08:10 | 2015-07-09 14:36 | 0 | 330 | 300 | Total unit performance testing (use appropriate codes for individual component testing) | F790Summer Full Load Capability Test | Mill Creek | Other | Coal | 2 | 2015 | 7 | 6.4333 | 6.4333 | 1930 | 300 | 300
MC1 | D4 | 81 | 310 | 2015-07-19 23:00 | 2015-07-20 01:10 | 250 | 330 | 300 | Pulverizer mills | F5901D Mill Adjust Rollers | Mill Creek | Derate | Coal | 2 | 2015 | 7 | 2.1667 | 0.52525 | 157.5758 | 72.7273 | 73
MC1 | NC | 82 | 8460 | 2015-07-23 09:18 | 2015-07-23 13:00 | 0 | 330 | 300 | Testing A | F790Mercury Air Toxic Standard (MATS) Testing | Mill Creek | Other | Coal | 2 | 2015 | 7 | 3.7 | 3.7 | 1110 | 300 | 300
MC1 | D1 | 83 | 250 | 2015-07-27 02:48 | 2015-07-27 03:11 | 250 | 330 | 300 | Pulverizer feeders | F7001B Coal Feeder - Replaced Action Pack Relay | Mill Creek | Derate | Coal | 2 | 2015 | 7 | 0.38333 | 0.092929 | 27.8788 | 72.7273 | 73
MC1 | D1 | 84 | 250 | 2015-07-29 17:25 | 2015-07-29 18:08 | 280 | 330 | 300 | Pulverizer feeders | F8201B Coal Feeder - Electrical Issues, keeps tripping. Investigating cause. | Mill Creek | Derate | Coal | 2 | 2015 | 7 | 0.71667 | 0.10859 | 32.5758 | 45.4545 | 45
MC1 | D1 | 85 | 250 | 2015-07-29 19:40 | 2015-07-30 12:45 | 280 | 330 | 300 | Pulverizer feeders | F8201B Coal Feeder - Electrical Issues, keeps tripping. Investigating cause. | Mill Creek | Derate | Coal | 2 | 2015 | 7 | 17.0833 | 2.5884 | 776.5152 | 45.4545 | 45
MC1 | D1 | 86 | 250 | 2015-07-30 13:12 | 2015-07-30 15:26 | 280 | 330 | 300 | Pulverizer feeders | F8201B Coal Feeder - Electrical Issues, Tripping | Mill Creek | Derate | Coal | 2 | 2015 | 7 | 2.2333 | 0.33838 | 101.5152 | 45.4545 | 45
MC1 | D1 | 87 | 310 | 2015-08-05 06:40 | 2015-08-05 08:15 | 260 | 330 | 300 | Pulverizer mills | FW001D Coal Mill - Wet Coal | Mill Creek | Derate | Coal | 2 | 2015 | 8 | 1.5833 | 0.33586 | 100.7576 | 63.6364 | 64
MC1 | NC | 88 | 3623 | 2015-08-10 10:00 | 2015-08-10 12:30 | 0 | 330 | 300 | Auxiliary generators | F790VAR Testing | Mill Creek | Other | Coal | 2 | 2015 | 8 | 2.5 | 2.5 | 750 | 300 | 300
MC1 | D1 | 89 | 4263 | 2015-08-11 01:04 | 2015-08-11 06:35 | 200 | 330 | 300 | Reheat stop valves | F720Turbine #2 Reheat Stop Valve - Stuck Closed from Valve Test | Mill Creek | Derate | Coal | 2 | 2015 | 8 | 5.5167 | 2.1732 | 651.9697 | 118.1818 | 118
MC1 | MO | 90 | 4263 | 2015-08-11 23:31 | 2015-08-15 12:45 | 0 | 330 | 300 | Reheat stop valves | F590Turbine Reheat Stop Valves - Remove Screens/Baskets | Mill Creek | Maintenance | Coal | 2 | 2015 | 8 | 85.2333 | 85.2333 | 25570 | 300 | 300
MC1 | NC | 91 | 1850 | 2015-08-15 12:45 | 2015-08-15 13:06 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2015 | 8 | 0.35 | 0.35 | 105 | 300 | 300
MC1 | U1 | 92 | 800 | 2015-08-15 13:06 | 2015-08-15 13:59 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F820High Drum Level Trip | Mill Creek | Outage | Coal | 2 | 2015 | 8 | 0.88333 | 0.88333 | 265 | 300 | 300
MC1 | NC | 93 | 1850 | 2015-08-15 13:59 | 2015-08-15 14:35 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2015 | 8 | 0.6 | 0.6 | 180 | 300 | 300
MC1 | U1 | 94 | 800 | 2015-08-15 14:35 | 2015-08-15 15:13 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F820High Drum Level Trip | Mill Creek | Outage | Coal | 2 | 2015 | 8 | 0.63333 | 0.63333 | 190 | 300 | 300
MC1 | SF | 95 | 3644 | 2015-08-15 15:13 | 2015-08-15 19:02 | 0 | 330 | 300 | AC Protection devices | F400Generator Lockout - Protective Relays | Mill Creek | Outage | Coal | 2 | 2015 | 8 | 3.8167 | 3.8167 | 1145 | 300 | 300
MC1 | NC | 96 | 1850 | 2015-08-15 19:02 | 2015-08-16 07:12 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2015 | 8 | 12.1667 | 12.1667 | 3650 | 300 | 300
MC1 | U1 | 97 | 800 | 2015-08-18 06:30 | 2015-08-18 08:11 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F820High Drum Level Trip | Mill Creek | Outage | Coal | 2 | 2015 | 8 | 1.6833 | 1.6833 | 505 | 300 | 300
MC1 | NC | 98 | 1850 | 2015-08-18 08:11 | 2015-08-18 12:26 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 2 | 2015 | 8 | 4.25 | 4.25 | 1275 | 300 | 300
MC1 | D1 | 99 | 1850 | 2015-08-18 12:26 | 2015-08-18 14:11 | 226 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 8 | 1.75 | 0.55152 | 165.4545 | 94.5455 | 95
MC1 | D1 | 100 | 1850 | 2015-08-18 14:11 | 2015-08-18 15:25 | 300 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 8 | 1.2333 | 0.11212 | 33.6364 | 27.2727 | 27
MC1 | MO | 101 | 8160 | 2015-08-19 22:23 | 2015-08-21 21:37 | 0 | 330 | 300 | Mist eliminators/demisters and washdown | F590FGD Demister Wash Maintenance | Mill Creek | Maintenance | Coal | 2 | 2015 | 8 | 47.2333 | 47.2333 | 14170 | 300 | 300
MC1 | NC | 103 | 1850 | 2015-08-22 10:00 | 2015-08-22 17:57 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2015 | 8 | 7.95 | 7.95 | 2385 | 300 | 300
MC1 | NC | 104 | 310 | 2015-08-26 11:40 | 2015-08-26 15:12 | 0 | 330 | 300 | Pulverizer mills | F790Coal Mill Testing & NOx Readings for Baghouse | Mill Creek | Other | Coal | 2 | 2015 | 8 | 3.5333 | 3.5333 | 1060 | 300 | 300
MC1 | D4 | 105 | 250 | 2015-08-30 22:00 | 2015-08-31 04:11 | 250 | 330 | 300 | Pulverizer feeders | F0901A Coal Mill - Calibrate | Mill Creek | Derate | Coal | 2 | 2015 | 8 | 6.1833 | 1.499 | 449.697 | 72.7273 | 73
MC1 | D1 | 106 | 570 | 2015-09-17 07:55 | 2015-09-17 10:43 | 155 | 330 | 300 | Other reheat steam problems | F590Reheat Spray Regulator - Repair Line Leak | Mill Creek | Derate | Coal | 2 | 2015 | 9 | 2.8 | 1.4848 | 445.4545 | 159.0909 | 159
MC1 | NC | 107 | 8460 | 2015-09-22 10:30 | 2015-09-22 19:30 | 0 | 330 | 300 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 9 | 9 | 9 | 2700 | 300 | 300
MC1 | NC | 108 | 8460 | 2015-09-23 09:00 | 2015-09-23 18:00 | 0 | 330 | 300 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 9 | 9 | 9 | 2700 | 300 | 300
MC1 | NC | 109 | 8460 | 2015-09-24 11:00 | 2015-09-24 18:00 | 0 | 330 | 300 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 9 | 7 | 7 | 2100 | 300 | 300
MC1 | NC | 110 | 8460 | 2015-09-28 07:30 | 2015-09-28 21:00 | 0 | 330 | 300 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 9 | 13.5 | 13.5 | 4050 | 300 | 300
MC1 | NC | 111 | 8460 | 2015-09-29 09:00 | 2015-09-29 17:30 | 0 | 330 | 300 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 9 | 8.5 | 8.5 | 2550 | 300 | 300
MC1 | NC | 112 | 8460 | 2015-09-30 08:40 | 2015-09-30 17:00 | 0 | 330 | 300 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 9 | 8.3333 | 8.3333 | 2500 | 300 | 300
MC1 | NC | 113 | 8460 | 2015-10-01 07:04 | 2015-10-01 17:10 | 0 | 330 | 300 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 10 | 10.1 | 10.1 | 3030 | 300 | 300
MC1 | U1 | 114 | 4750 | 2015-10-12 17:43 | 2015-10-14 19:35 | 0 | 330 | 300 | Other generator controls and metering problems | F490Generator Lockout | Mill Creek | Outage | Coal | 2 | 2015 | 10 | 49.8667 | 49.8667 | 14960 | 300 | 300
MC1 | NC | 115 | 1850 | 2015-10-14 19:35 | 2015-10-15 03:05 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2015 | 10 | 7.5 | 7.5 | 2250 | 300 | 300
MC1 | D4 | 116 | 250 | 2015-10-29 01:00 | 2015-10-29 04:00 | 250 | 330 | 300 | Pulverizer feeders | F5901D Coal Feeder clean out conveyor maintenance | Mill Creek | Derate | Coal | 2 | 2015 | 10 | 3 | 0.72727 | 218.1818 | 72.7273 | 73
MC1 | D1 | 117 | 310 | 2015-11-03 11:30 | 2015-11-03 12:06 | 210 | 330 | 300 | Pulverizer mills | F8301 B and D mills breaker trip. | Mill Creek | Derate | Coal | 2 | 2015 | 11 | 0.6 | 0.21818 | 65.4545 | 109.0909 | 109
MC1 | NC | 118 | 8460 | 2015-11-16 08:00 | 2015-11-16 17:00 | 0 | 330 | 300 | Testing A | F790Full load Mercury testing | Mill Creek | Other | Coal | 2 | 2015 | 11 | 9 | 9 | 2700 | 300 | 300
MC1 | NC | 119 | 8460 | 2015-11-17 07:40 | 2015-11-17 17:00 | 0 | 330 | 300 | Testing A | F790Full load Mercury testing | Mill Creek | Other | Coal | 2 | 2015 | 11 | 9.3333 | 9.3333 | 2800 | 300 | 300
MC1 | NC | 120 | 8460 | 2015-11-18 08:15 | 2015-11-18 17:00 | 0 | 330 | 300 | Testing A | F790Full load Mercury testing | Mill Creek | Other | Coal | 2 | 2015 | 11 | 8.75 | 8.75 | 2625 | 300 | 300
MC1 | NC | 121 | 8460 | 2015-11-19 07:30 | 2015-11-19 17:00 | 0 | 330 | 300 | Testing A | F790Full load Mercury testing | Mill Creek | Other | Coal | 2 | 2015 | 11 | 9.5 | 9.5 | 2850 | 300 | 300
MC1 | NC | 122 | 8460 | 2015-11-20 09:00 | 2015-11-20 19:00 | 0 | 330 | 300 | Testing A | F790Full load Mercury testing | Mill Creek | Other | Coal | 2 | 2015 | 11 | 10 | 10 | 3000 | 300 | 300
MC1 | NC | 123 | 8460 | 2015-11-21 08:00 | 2015-11-21 19:17 | 0 | 330 | 300 | Testing A | F790Full load Mercury testing | Mill Creek | Other | Coal | 2 | 2015 | 11 | 11.2833 | 11.2833 | 3385 | 300 | 300
MC1 | D1 | 124 | 30 | 2015-11-24 23:05 | 2015-11-25 01:28 | 125 | 330 | 300 | Coal conveyors and feeders | F010G1 Tripper out of alignment | Mill Creek | Derate | Coal | 2 | 2015 | 11 | 2.3833 | 1.4806 | 444.1667 | 186.3636 | 186
MC1 | D4 | 125 | 310 | 2015-11-26 01:07 | 2015-11-26 03:02 | 240 | 330 | 300 | Pulverizer mills | F3301D Coal mill hot air gate would not stay closed | Mill Creek | Derate | Coal | 2 | 2015 | 11 | 1.9167 | 0.52273 | 156.8182 | 81.8182 | 82
MC1 | NC | 126 | 3190 | 2015-12-14 23:00 | 2015-12-15 03:51 | 0 | 330 | 300 | Air leakage (for losses not attributable to previously noted equipment related codes) | F790Condenser air in leakage check | Mill Creek | Other | Coal | 2 | 2015 | 12 | 4.85 | 4.85 | 1455 | 300 | 300
MC1 | MO | 127 | 8499 | 2015-12-19 12:39 | 2015-12-23 12:20 | 0 | 330 | 300 | Other miscellaneous wet scrubber problems | F590FGD maintenance - replace oriface plates in hydrocylone system | Mill Creek | Maintenance | Coal | 2 | 2015 | 12 | 95.6833 | 95.6833 | 28705 | 300 | 300
MC1 | D1 | 128 | 1850 | 2015-12-23 22:30 | 2015-12-24 01:52 | 250 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 3.3667 | 0.81616 | 244.8485 | 72.7273 | 73
MC1 | D1 | 129 | 1850 | 2015-12-24 01:52 | 2015-12-24 03:40 | 290 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 1.8 | 0.21818 | 65.4545 | 36.3636 | 36
MC1 | D1 | 130 | 1850 | 2015-12-24 03:40 | 2015-12-24 04:35 | 318 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170HIgh Silica | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 0.91667 | 0.033333 | 10 | 10.9091 | 11
MC1 | NC | 131 | 8460 | 2015-12-28 08:00 | 2015-12-28 16:36 | 0 | 330 | 300 | Testing A | F790Full Load Testing off AGC | Mill Creek | Other | Coal | 2 | 2015 | 12 | 8.6 | 8.6 | 2580 | 300 | 300
MC1 | D1 | 132 | 250 | 2015-12-28 16:36 | 2015-12-28 17:48 | 232 | 330 | 300 | Pulverizer feeders | FW00Wet coal | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 1.2 | 0.35636 | 106.9091 | 89.0909 | 89
MC1 | D1 | 133 | 250 | 2015-12-28 20:51 | 2015-12-28 21:55 | 225 | 330 | 300 | Pulverizer feeders | FW00Wet coal | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 1.0667 | 0.33939 | 101.8182 | 95.4545 | 95
MC1 | U1 | 134 | 800 | 2015-12-29 02:21 | 2015-12-29 06:18 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F820Drum level trip | Mill Creek | Outage | Coal | 2 | 2015 | 12 | 3.95 | 3.95 | 1185 | 300 | 300
MC1 | NC | 135 | 1850 | 2015-12-29 06:18 | 2015-12-29 10:39 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica @ very hot start | Mill Creek | Other | Coal | 2 | 2015 | 12 | 4.35 | 4.35 | 1305 | 300 | 300
MC1 | D1 | 136 | 250 | 2015-12-29 10:39 | 2015-12-29 13:04 | 239 | 330 | 300 | Pulverizer feeders | FW00Wet coal | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 2.4167 | 0.66641 | 199.9242 | 82.7273 | 83
MC1 | D1 | 137 | 1850 | 2015-12-29 13:04 | 2015-12-29 14:16 | 290 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 1.2 | 0.14545 | 43.6364 | 36.3636 | 36
MC1 | D1 | 138 | 250 | 2015-12-30 08:23 | 2015-12-30 09:56 | 235 | 330 | 300 | Pulverizer feeders | FW00Wet coal | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 1.55 | 0.44621 | 133.8636 | 86.3636 | 86
MC1 | D4 | 1 | 310 | 2016-01-04 23:00 | 2016-01-05 01:42 | 240 | 330 | 300 | Pulverizer mills | F5901D Mill scraper maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 1 | 2.7 | 0.73636 | 220.9091 | 81.8182 | 82
MC1 | D1 | 2 | 550 | 2016-01-05 01:42 | 2016-01-05 08:26 | 195 | 330 | 300 | Reheat steam relief/safety valves | F720RH Intercept valve sticking closed | Mill Creek | Derate | Coal | 2 | 2016 | 1 | 6.7333 | 2.7545 | 826.3636 | 122.7273 | 123
MC1 | NC | 3 | 8700 | 2016-01-19 08:00 | 2016-01-19 17:20 | 0 | 330 | 300 | CEMS Certification and Recertification | F790Full load RATA testing | Mill Creek | Other | Coal | 2 | 2016 | 1 | 9.3333 | 9.3333 | 2800 | 300 | 300
MC1 | NC | 4 | 8700 | 2016-01-19 22:00 | 2016-01-20 01:37 | 0 | 330 | 300 | CEMS Certification and Recertification | F790Mid load RATA testing | Mill Creek | Other | Coal | 2 | 2016 | 1 | 3.6167 | 3.6167 | 1085 | 300 | 300
MC1 | D1 | 5 | 1450 | 2016-01-20 06:55 | 2016-01-20 07:35 | 240 | 330 | 300 | Other air supply problems | F590A mill high burner temps due to air flow issue | Mill Creek | Derate | Coal | 2 | 2016 | 1 | 0.66667 | 0.18182 | 54.5455 | 81.8182 | 82
MC1 | NC | 6 | 8700 | 2016-01-20 10:00 | 2016-01-20 13:30 | 0 | 330 | 300 | CEMS Certification and Recertification | F790Full Load RATA testing | Mill Creek | Other | Coal | 2 | 2016 | 1 | 3.5 | 3.5 | 1050 | 300 | 300
MC1 | NC | 7 | 1599 | 2016-01-20 14:16 | 2016-01-20 15:40 | 0 | 330 | 300 | Other miscellaneous boiler air and gas system problems | F790Alstom getting readings from the boiler, needed steady load | Mill Creek | Other | Coal | 2 | 2016 | 1 | 1.4 | 1.4 | 420 | 300 | 300
MC1 | D4 | 8 | 250 | 2016-01-20 23:00 | 2016-01-21 06:11 | 240 | 330 | 300 | Pulverizer feeders | F5301B feeder inspection and calibration | Mill Creek | Derate | Coal | 2 | 2016 | 1 | 7.1833 | 1.9591 | 587.7273 | 81.8182 | 82
MC1 | D4 | 9 | 250 | 2016-01-21 23:00 | 2016-01-22 04:38 | 240 | 330 | 300 | Pulverizer feeders | F5301C Mill feeder inspection and calibration | Mill Creek | Derate | Coal | 2 | 2016 | 1 | 5.6333 | 1.5364 | 460.9091 | 81.8182 | 82
MC1 | D1 | 10 | 250 | 2016-02-01 04:00 | 2016-02-01 04:18 | 120 | 330 | 300 | Pulverizer feeders | F8201B Feeder tripped at low load | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 0.3 | 0.19091 | 57.2727 | 190.9091 | 191
MC1 | D1 | 11 | 360 | 2016-02-02 07:36 | 2016-02-02 08:52 | 250 | 330 | 300 | Burners | F7801A Mill burner temps | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 1.2667 | 0.30707 | 92.1212 | 72.7273 | 73
MC1 | D4 | 12 | 253 | 2016-02-02 23:00 | 2016-02-03 02:29 | 158 | 330 | 300 | Pulverizer feeder motor | F5901A & 1B Coal Feeder motor swap. | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 3.4833 | 1.8156 | 544.6667 | 156.3636 | 156
MC1 | NC | 13 | 9999 | 2016-02-03 08:00 | 2016-02-03 14:00 | 0 | 330 | 300 | Total unit performance testing (use appropriate codes for individual component testing) | F790Full Load winter capability testing | Mill Creek | Other | Coal | 2 | 2016 | 2 | 6 | 6 | 1800 | 300 | 300
MC1 | D4 | 14 | 250 | 2016-02-03 23:00 | 2016-02-04 07:24 | 240 | 330 | 300 | Pulverizer feeders | F0901A mill feeder calibration | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 8.4 | 2.2909 | 687.2727 | 81.8182 | 82
MC1 | D1 | 15 | 250 | 2016-02-04 09:51 | 2016-02-04 10:04 | 270 | 330 | 300 | Pulverizer feeders | F8201A Mill feeder tripped | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 0.21667 | 0.039394 | 11.8182 | 54.5455 | 55
MC1 | D1 | 16 | 1850 | 2016-02-04 13:00 | 2016-02-04 19:47 | 309 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 6.7833 | 0.43167 | 129.5 | 19.0909 | 19
MC1 | MO | 17 | 3110 | 2016-02-05 21:42 | 2016-02-07 15:35 | 0 | 330 | 300 | Condenser tube leaks | F540Condenser tube leak | Mill Creek | Maintenance | Coal | 2 | 2016 | 2 | 41.8833 | 41.8833 | 12565 | 300 | 300
MC1 | NC | 18 | 1850 | 2016-02-07 15:35 | 2016-02-07 21:35 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica @ hot start | Mill Creek | Other | Coal | 2 | 2016 | 2 | 6 | 6 | 1800 | 300 | 300
MC1 | D1 | 19 | 1850 | 2016-02-07 21:35 | 2016-02-07 23:59 | 275 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 2.4 | 0.4 | 120 | 50 | 50
MC1 | NC | 20 | 1990 | 2016-02-08 07:30 | 2016-02-08 12:16 | 0 | 330 | 300 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Boiler exit gas temperature testing | Mill Creek | Other | Coal | 2 | 2016 | 2 | 4.7667 | 4.7667 | 1430 | 300 | 300
MC1 | NC | 21 | 8700 | 2016-02-09 07:30 | 2016-02-09 18:00 | 0 | 330 | 300 | CEMS Certification and Recertification | F790Full load PM/RRA Testing | Mill Creek | Other | Coal | 2 | 2016 | 2 | 10.5 | 10.5 | 3150 | 300 | 300
MC1 | D1 | 22 | 1850 | 2016-02-21 17:22 | 2016-02-22 05:33 | 263 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 12.1833 | 2.4736 | 742.0758 | 60.9091 | 61
MC1 | D1 | 23 | 1850 | 2016-02-22 05:33 | 2016-02-22 06:40 | 252 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 1.1167 | 0.26394 | 79.1818 | 70.9091 | 71
MC1 | D1 | 24 | 1850 | 2016-02-22 06:40 | 2016-02-22 09:05 | 247 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 2.4167 | 0.60783 | 182.3485 | 75.4545 | 75
MC1 | MO | 25 | 3110 | 2016-02-22 09:05 | 2016-02-23 09:17 | 0 | 330 | 300 | Condenser tube leaks | F540Condenser tube leak | Mill Creek | Maintenance | Coal | 2 | 2016 | 2 | 24.2 | 24.2 | 7260 | 300 | 300
MC1 | NC | 26 | 1850 | 2016-02-23 09:17 | 2016-02-23 15:17 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica @ hot start | Mill Creek | Other | Coal | 2 | 2016 | 2 | 6 | 6 | 1800 | 300 | 300
MC1 | D1 | 27 | 1850 | 2016-02-23 15:17 | 2016-02-23 16:08 | 250 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 0.85 | 0.20606 | 61.8182 | 72.7273 | 73
MC1 | D1 | 28 | 1850 | 2016-02-23 16:08 | 2016-02-23 19:50 | 280 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 3.7 | 0.56061 | 168.1818 | 45.4545 | 45
MC1 | D1 | 29 | 360 | 2016-03-04 06:58 | 2016-03-04 09:00 | 240 | 330 | 300 | Burners | F7801B4 Mill burner temps high. | Mill Creek | Derate | Coal | 2 | 2016 | 3 | 2.0333 | 0.55455 | 166.3636 | 81.8182 | 82
MC1 | D4 | 30 | 310 | 2016-03-07 23:00 | 2016-03-08 04:45 | 240 | 330 | 300 | Pulverizer mills | F5301D Mill inspect scraper and hot air gate. | Mill Creek | Derate | Coal | 2 | 2016 | 3 | 5.75 | 1.5682 | 470.4545 | 81.8182 | 82
MC1 | D4 | 31 | 310 | 2016-03-08 23:00 | 2016-03-09 04:43 | 250 | 330 | 300 | Pulverizer mills | F5901D Mill maintenance, replace solenoid on hot air gate | Mill Creek | Derate | Coal | 2 | 2016 | 3 | 5.7167 | 1.3859 | 415.7576 | 72.7273 | 73
MC1 | D4 | 32 | 310 | 2016-03-10 23:00 | 2016-03-11 04:31 | 240 | 330 | 300 | Pulverizer mills | F5301B Coal Mill Inspection | Mill Creek | Derate | Coal | 2 | 2016 | 3 | 5.5167 | 1.5045 | 451.3636 | 81.8182 | 82
MC1 | PO | 33 | 3998 | 2016-03-20 21:23 | 2016-03-29 10:55 | 0 | 330 | 300 | Balance of plant overhaul/outage | F590Planned outage | Mill Creek | Other | Coal | 2 | 2016 | 3 | 205.5333 | 205.5333 | 61660 | 300 | 300
MC1 | NC | 34 | 1850 | 2016-03-29 10:55 | 2016-03-29 11:31 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica @ cold start | Mill Creek | Other | Coal | 2 | 2016 | 3 | 0.6 | 0.6 | 180 | 300 | 300
MC1 | U1 | 35 | 800 | 2016-03-29 11:31 | 2016-03-29 13:07 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F820Drum level trip | Mill Creek | Outage | Coal | 2 | 2016 | 3 | 1.6 | 1.6 | 480 | 300 | 300
MC1 | NC | 36 | 1850 | 2016-03-29 13:07 | 2016-03-30 05:23 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica @ cold start-up | Mill Creek | Other | Coal | 2 | 2016 | 3 | 16.2667 | 16.2667 | 4880 | 300 | 300
MC1 | NC | 37 | 1990 | 2016-04-01 06:00 | 2016-04-01 21:00 | 0 | 330 | 300 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Full load testing prior to Nalco feed | Mill Creek | Other | Coal | 2 | 2016 | 4 | 15 | 15 | 4500 | 300 | 300
MC1 | NC | 38 | 1710 | 2016-04-04 23:00 | 2016-04-05 00:27 | 0 | 330 | 300 | Combustion/steam condition controls (report local controls --- burners | F7901A Mill clean air flow testing | Mill Creek | Other | Coal | 2 | 2016 | 4 | 1.45 | 1.45 | 435 | 300 | 300
MC1 | NC | 39 | 1710 | 2016-04-05 23:00 | 2016-04-06 03:03 | 0 | 330 | 300 | Combustion/steam condition controls (report local controls --- burners | F7901B Mill clean air flow testing | Mill Creek | Other | Coal | 2 | 2016 | 4 | 4.05 | 4.05 | 1215 | 300 | 300
MC1 | NC | 40 | 1710 | 2016-04-12 09:36 | 2016-04-12 11:35 | 0 | 330 | 300 | Combustion/steam condition controls (report local controls --- burners | F790Air flow testing | Mill Creek | Other | Coal | 2 | 2016 | 4 | 1.9833 | 1.9833 | 595 | 300 | 300
MC1 | NC | 41 | 1710 | 2016-04-12 13:45 | 2016-04-12 15:45 | 0 | 330 | 300 | Combustion/steam condition controls (report local controls --- burners | F790Air flow testing | Mill Creek | Other | Coal | 2 | 2016 | 4 | 2 | 2 | 600 | 300 | 300
MC1 | NC | 42 | 8460 | 2016-04-16 15:00 | 2016-04-16 18:00 | 0 | 330 | 300 | Testing A | F790Hg compliance testing | Mill Creek | Other | Coal | 2 | 2016 | 4 | 3 | 3 | 900 | 300 | 300
MC1 | NC | 43 | 1710 | 2016-04-21 23:00 | 2016-04-22 00:07 | 0 | 330 | 300 | Combustion/steam condition controls (report local controls --- burners | F790Low load air flow testing | Mill Creek | Other | Coal | 2 | 2016 | 4 | 1.1167 | 1.1167 | 335 | 300 | 300
MC1 | D4 | 44 | 331 | 2016-04-25 21:05 | 2016-04-26 04:57 | 240 | 330 | 300 | Pulverizer system coal leaks (other than pulverizers | F540Coal leak on mill exhauster | Mill Creek | Derate | Coal | 2 | 2016 | 4 | 7.8667 | 2.1455 | 643.6364 | 81.8182 | 82
MC1 | D1 | 45 | 320 | 2016-04-26 06:42 | 2016-04-26 09:38 | 250 | 330 | 300 | Foreign object in Pulverizers mill | F5301D Mill had rocks under the roller | Mill Creek | Derate | Coal | 2 | 2016 | 4 | 2.9333 | 0.71111 | 213.3333 | 72.7273 | 73
MC1 | D1 | 46 | 310 | 2016-04-26 10:17 | 2016-04-26 12:48 | 250 | 330 | 300 | Pulverizer mills | F5901D Mill roller adjustment | Mill Creek | Derate | Coal | 2 | 2016 | 4 | 2.5167 | 0.6101 | 183.0303 | 72.7273 | 73
MC1 | D4 | 47 | 740 | 2016-04-27 20:00 | 2016-04-27 22:22 | 180 | 330 | 300 | Boiler recirculation pumps | F5901A BCP maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 4 | 2.3667 | 1.0758 | 322.7273 | 136.3636 | 136
MC1 | D4 | 48 | 740 | 2016-05-05 21:00 | 2016-05-06 01:20 | 130 | 330 | 300 | Boiler recirculation pumps | F5901A BCP troublehsoot isolation problems | Mill Creek | Derate | Coal | 2 | 2016 | 5 | 4.3333 | 2.6263 | 787.8788 | 181.8182 | 182
MC1 | D4 | 49 | 310 | 2016-05-08 22:00 | 2016-05-09 05:14 | 240 | 330 | 300 | Pulverizer mills | F5301A Mill Inspection | Mill Creek | Derate | Coal | 2 | 2016 | 5 | 7.2333 | 1.9727 | 591.8182 | 81.8182 | 82
MC1 | D4 | 50 | 250 | 2016-05-09 23:00 | 2016-05-10 04:46 | 240 | 330 | 300 | Pulverizer feeders | F0901B feeder calibration | Mill Creek | Derate | Coal | 2 | 2016 | 5 | 5.7667 | 1.5727 | 471.8182 | 81.8182 | 82
MC1 | D4 | 51 | 250 | 2016-05-10 23:00 | 2016-05-11 03:48 | 240 | 330 | 300 | Pulverizer feeders | F0901C Feeder Calibration & Inspection | Mill Creek | Derate | Coal | 2 | 2016 | 5 | 4.8 | 1.3091 | 392.7273 | 81.8182 | 82
MC1 | D4 | 52 | 253 | 2016-05-11 23:00 | 2016-05-12 05:05 | 240 | 330 | 300 | Pulverizer feeder motor | F0901D Feeder Calibration & Inspection | Mill Creek | Derate | Coal | 2 | 2016 | 5 | 6.0833 | 1.6591 | 497.7273 | 81.8182 | 82
MC1 | MO | 53 | 741 | 2016-05-13 23:34 | 2016-05-14 13:02 | 0 | 330 | 300 | Boiler recirculation pumps - motors | F5901A BCWP Motor | Mill Creek | Maintenance | Coal | 2 | 2016 | 5 | 13.4667 | 13.4667 | 4040 | 300 | 300
MC1 | SF | 55 | 4263 | 2016-05-15 20:30 | 2016-05-17 20:06 | 0 | 330 | 300 | Reheat stop valves | F720RH Valve would not open | Mill Creek | Outage | Coal | 2 | 2016 | 5 | 47.6 | 47.6 | 14280 | 300 | 300
MC1 | D1 | 56 | 250 | 2016-05-18 03:19 | 2016-05-18 06:05 | 225 | 330 | 300 | Pulverizer feeders | F1201C Mill out of service due to wet coal. (Sprinkler Issue) | Mill Creek | Derate | Coal | 2 | 2016 | 5 | 2.7667 | 0.8803 | 264.0909 | 95.4545 | 95
MC1 | D1 | 57 | 250 | 2016-05-18 06:05 | 2016-05-18 14:35 | 255 | 330 | 300 | Pulverizer feeders | F1201C Mill out of service due to wet coal. (Sprinkler Issue) | Mill Creek | Derate | Coal | 2 | 2016 | 5 | 8.5 | 1.9318 | 579.5455 | 68.1818 | 68
MC1 | D1 | 58 | 250 | 2016-05-18 19:00 | 2016-05-18 20:34 | 255 | 330 | 300 | Pulverizer feeders | F1201C Mill out of service due to wet coal. (Sprinkler Issue) | Mill Creek | Derate | Coal | 2 | 2016 | 5 | 1.5667 | 0.35606 | 106.8182 | 68.1818 | 68
MC1 | D1 | 59 | 8199 | 2016-05-30 15:58 | 2016-05-30 16:38 | 280 | 330 | 300 | Other scrubber problems | F750High flue gas temps | Mill Creek | Derate | Coal | 2 | 2016 | 5 | 0.66667 | 0.10101 | 30.303 | 45.4545 | 45
MC1 | D1 | 60 | 8199 | 2016-05-30 16:38 | 2016-05-30 20:08 | 250 | 330 | 300 | Other scrubber problems | F750High flue gas temps | Mill Creek | Derate | Coal | 2 | 2016 | 5 | 3.5 | 0.84848 | 254.5455 | 72.7273 | 73
MC1 | D1 | 61 | 1488 | 2016-06-04 13:50 | 2016-06-05 01:00 | 250 | 330 | 300 | Air heater (regenerative) | F1201A air heater support bearing running hot | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 11.1667 | 2.7071 | 812.1212 | 72.7273 | 73
MC1 | D1 | 62 | 1488 | 2016-06-05 01:00 | 2016-06-05 03:44 | 135 | 330 | 300 | Air heater (regenerative) | F1201A air heater support bearing running hot | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 2.7333 | 1.6152 | 484.5455 | 177.2727 | 177
MC1 | NC | 63 | 8010 | 2016-06-15 00:50 | 2016-06-15 04:42 | 0 | 330 | 300 | Crushers/mills | F430Lost feed to limestone crusher, cant make slurry | Mill Creek | Other | Coal | 2 | 2016 | 6 | 3.8667 | 3.8667 | 1160 | 300 | 300
MC1 | D4 | 64 | 310 | 2016-06-29 | 2016-06-29 04:56 | 250 | 330 | 300 | Pulverizer mills | F5901D Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 4.9333 | 1.196 | 358.7879 | 72.7273 | 73
MC1 | D4 | 65 | 270 | 2016-06-29 23:00 | 2016-06-30 05:20 | 250 | 330 | 300 | Primary air duct and dampers | F590D Coal Mill Exhauster Damper Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 6.3333 | 1.5354 | 460.6061 | 72.7273 | 73
MC1 | MO | 66 | 3110 | 2016-06-30 22:19 | 2016-07-02 | 0 | 330 | 300 | Condenser tube leaks | F540Boiler and condenser tube leaks repairs | Mill Creek | Maintenance | Coal | 2 | 2016 | 6 | 25.6833 | 25.6833 | 7705 | 300 | 300
MC1 | MO | 67 | 1060 | 2016-07-02 | 2016-07-03 09:18 | 0 | 330 | 300 | First reheater A | F540Boiler and condenser tube leaks (Boiler Tube Repair Time) | Mill Creek | Maintenance | Coal | 2 | 2016 | 7 | 33.3 | 33.3 | 9990 | 300 | 300
MC1 | D1 | 68 | 1850 | 2016-07-03 17:34 | 2016-07-03 19:16 | 302 | 330 | 300 | Boiler water condition (not feedwater water quality) | F540High Silica | Mill Creek | Derate | Coal | 2 | 2016 | 7 | 1.7 | 0.14424 | 43.2727 | 25.4545 | 25
MC1 | MO | 69 | 1070 | 2016-07-15 23:21 | 2016-07-18 06:29 | 0 | 330 | 300 | Second reheater B | F540Boiler Tube Leak - Reheat | Mill Creek | Maintenance | Coal | 2 | 2016 | 7 | 55.1333 | 55.1333 | 16540 | 300 | 300
MC1 | NC | 70 | 1999 | 2016-07-27 23:00 | 2016-07-28 02:20 | 0 | 330 | 300 | Boiler | F790O2 Testing | Mill Creek | Other | Coal | 2 | 2016 | 7 | 3.3333 | 3.3333 | 1000 | 300 | 300
MC1 | MO | 71 | 4293 | 2016-07-29 21:55 | 2016-07-30 03:20 | 0 | 330 | 300 | Hydraulic system pipes and valves | F540Repair EHC Leaks | Mill Creek | Maintenance | Coal | 2 | 2016 | 7 | 5.4167 | 5.4167 | 1625 | 300 | 300
MC1 | D1 | 72 | 310 | 2016-08-09 13:23 | 2016-08-09 15:02 | 250 | 330 | 300 | Pulverizer mills | F3001D Coal Mill (Metal in mill) | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 1.65 | 0.4 | 120 | 72.7273 | 73
MC1 | D1 | 73 | 250 | 2016-08-15 10:39 | 2016-08-15 11:08 | 250 | 330 | 300 | Pulverizer feeders | F820C Feeder Tripped | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 0.48333 | 0.11717 | 35.1515 | 72.7273 | 73
MC1 | D4 | 74 | 310 | 2016-08-15 23:00 | 2016-08-16 04:18 | 250 | 330 | 300 | Pulverizer mills | F5901B Mill Inspection | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 5.3 | 1.2848 | 385.4545 | 72.7273 | 73
MC1 | NC | 75 | 4490 | 2016-08-16 21:00 | 2016-08-16 23:00 | 0 | 330 | 300 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Heat Rate Testing | Mill Creek | Other | Coal | 2 | 2016 | 8 | 2 | 2 | 600 | 300 | 300
MC1 | D4 | 76 | 344 | 2016-08-16 23:00 | 2016-08-17 01:00 | 250 | 330 | 300 | Pulverizer inspection | F5901D Mill Inspection | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 2 | 0.48485 | 145.4545 | 72.7273 | 73
MC1 | D4 | 77 | 344 | 2016-08-17 01:00 | 2016-08-17 04:50 | 250 | 330 | 300 | Pulverizer inspection | F5901D Mill Inspection | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 3.8333 | 0.92929 | 278.7879 | 72.7273 | 73
MC1 | D4 | 78 | 344 | 2016-08-17 23:00 | 2016-08-18 04:54 | 250 | 330 | 300 | Pulverizer inspection | F590A Mill Inspection | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 5.9 | 1.4303 | 429.0909 | 72.7273 | 73
MC1 | D1 | 79 | 3415 | 2016-08-21 23:05 | 2016-08-22 02:05 | 190 | 330 | 300 | Feedwater pump/drive lube oil system | F7801A BFP Outboard bearing temp | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 3 | 1.2727 | 381.8182 | 127.2727 | 127
MC1 | D1 | 80 | 3661 | 2016-08-22 02:05 | 2016-08-22 07:13 | 120 | 330 | 300 | 4160-volt circuit breakers | F8701A2 4kv bus-breaker would not close | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 5.1333 | 3.2667 | 980 | 190.9091 | 191
MC1 | D1 | 81 | 3410 | 2016-08-22 07:13 | 2016-08-22 10:35 | 230 | 330 | 300 | Feedwater pump | F7801A BFP Outboard Pump Bearing | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 3.3667 | 1.0202 | 306.0606 | 90.9091 | 91
MC1 | D1 | 82 | 3410 | 2016-08-22 10:35 | 2016-08-22 11:15 | 240 | 330 | 300 | Feedwater pump | F7801A BFP Outboard Pump Bearing | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 0.66667 | 0.18182 | 54.5455 | 81.8182 | 82
MC1 | D1 | 83 | 3230 | 2016-08-22 11:15 | 2016-08-22 11:37 | 260 | 330 | 300 | Circulating water valves | F1301A CWP Discharge Valve Stuck Closed | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 0.36667 | 0.077778 | 23.3333 | 63.6364 | 64
MC1 | D1 | 84 | 3230 | 2016-08-22 11:37 | 2016-08-22 23:05 | 250 | 330 | 300 | Circulating water valves | F1301A CWP Discharge Valve Stuck Closed | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 11.4667 | 2.7798 | 833.9394 | 72.7273 | 73
MC1 | D4 | 85 | 310 | 2016-08-22 23:05 | 2016-08-23 04:09 | 240 | 330 | 300 | Pulverizer mills | F5901C Mill Maintinance | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 5.0667 | 1.3818 | 414.5455 | 81.8182 | 82
MC1 | D4 | 86 | 310 | 2016-08-24 23:00 | 2016-08-25 03:44 | 240 | 330 | 300 | Pulverizer mills | F5901B Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 4.7333 | 1.2909 | 387.2727 | 81.8182 | 82
MC1 | MO | 87 | 1000 | 2016-09-17 01:18 | 2016-09-19 04:46 | 0 | 330 | 300 | Waterwall (Furnace wall) A | F540Boiler Tube Leak | Mill Creek | Maintenance | Coal | 2 | 2016 | 9 | 51.4667 | 51.4667 | 15440 | 300 | 300
MC1 | D4 | 88 | 250 | 2016-09-29 23:00 | 2016-09-30 05:10 | 240 | 330 | 300 | Pulverizer feeders | F590'1B Mill Inspection and Feeder Calibration | Mill Creek | Derate | Coal | 2 | 2016 | 9 | 6.1667 | 1.6818 | 504.5455 | 81.8182 | 82
MC1 | D1 | 89 | 3110 | 2016-10-06 12:49 | 2016-10-06 15:26 | 285 | 330 | 300 | Condenser tube leaks | F540Condenser Tube Leak | Mill Creek | Derate | Coal | 2 | 2016 | 10 | 2.6167 | 0.35682 | 107.0455 | 40.9091 | 41
MC1 | U1 | 90 | 3110 | 2016-10-06 15:26 | 2016-10-07 07:13 | 0 | 330 | 300 | Condenser tube leaks | F540Condenser Tube Leak | Mill Creek | Outage | Coal | 2 | 2016 | 10 | 15.7833 | 15.7833 | 4735 | 300 | 300
MC1 | D1 | 91 | 3110 | 2016-10-07 14:55 | 2016-10-07 15:35 | 280 | 330 | 300 | Condenser tube leaks | F170High Silica (Startup after a condenser tube leak) | Mill Creek | Derate | Coal | 2 | 2016 | 10 | 0.66667 | 0.10101 | 30.303 | 45.4545 | 45
MC1 | D4 | 93 | 250 | 2016-10-10 23:00 | 2016-10-11 01:05 | 240 | 330 | 300 | Pulverizer feeders | F5901B Feeder Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 10 | 2.0833 | 0.56818 | 170.4545 | 81.8182 | 82
MC1 | D4 | 94 | 250 | 2016-10-12 23:00 | 2016-10-13 03:14 | 240 | 330 | 300 | Pulverizer feeders | F5901B Feeder Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 10 | 4.2333 | 1.1545 | 346.3636 | 81.8182 | 82
MC1 | D1 | 95 | 331 | 2016-10-19 23:30 | 2016-10-20 01:36 | 240 | 330 | 300 | Pulverizer system coal leaks (other than pulverizers | F5401C Coal Leak | Mill Creek | Derate | Coal | 2 | 2016 | 10 | 2.1 | 0.57273 | 171.8182 | 81.8182 | 82
MC1 | D4 | 96 | 253 | 2016-11-08 23:00 | 2016-11-09 04:17 | 240 | 330 | 300 | Pulverizer feeder motor | F4001B Mill Feeder motor VFD replaced | Mill Creek | Derate | Coal | 2 | 2016 | 11 | 5.2833 | 1.4409 | 432.2727 | 81.8182 | 82
MC1 | D4 | 97 | 250 | 2016-11-15 23:00 | 2016-11-16 06:09 | 240 | 330 | 300 | Pulverizer feeders | F5901B Coal Feeder Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 11 | 7.15 | 1.95 | 585 | 81.8182 | 82
MC1 | D4 | 98 | 250 | 2016-11-16 22:00 | 2016-11-17 04:59 | 240 | 330 | 300 | Pulverizer feeders | F5901A Coal Feeder Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 11 | 6.9833 | 1.9045 | 571.3636 | 81.8182 | 82
MC1 | NC | 99 | 920 | 2016-11-21 22:05 | 2016-11-22 04:43 | 0 | 330 | 300 | Other slag and ash removal problems A | FS00Deslag | Mill Creek | Other | Coal | 2 | 2016 | 11 | 6.6333 | 6.6333 | 1990 | 300 | 300
MC1 | NC | 100 | 920 | 2016-11-22 22:30 | 2016-11-23 04:00 | 0 | 330 | 300 | Other slag and ash removal problems A | FS00Deslag | Mill Creek | Other | Coal | 2 | 2016 | 11 | 5.5 | 5.5 | 1650 | 300 | 300
MC1 | D1 | 101 | 250 | 2016-11-23 07:02 | 2016-11-23 19:25 | 240 | 330 | 300 | Pulverizer feeders | F8201B Feeder tripping | Mill Creek | Derate | Coal | 2 | 2016 | 11 | 12.3833 | 3.3773 | 1013.1818 | 81.8182 | 82
MC1 | D4 | 102 | 250 | 2016-11-26 12:17 | 2016-11-26 13:30 | 250 | 330 | 300 | Pulverizer feeders | F5901B Feeder maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 11 | 1.2167 | 0.29495 | 88.4848 | 72.7273 | 73
MC1 | D4 | 103 | 250 | 2016-11-29 22:30 | 2016-11-30 05:07 | 240 | 330 | 300 | Pulverizer feeders | F5301C Feeder calibration and inspection | Mill Creek | Derate | Coal | 2 | 2016 | 11 | 6.6167 | 1.8045 | 541.3636 | 81.8182 | 82
MC1 | D4 | 104 | 338 | 2016-11-30 22:30 | 2016-12-01 05:08 | 240 | 330 | 300 | Pulverizer control systems (temperature and pressure) | F5901B Mill hot air gate and linkage | Mill Creek | Derate | Coal | 2 | 2016 | 11 | 6.6333 | 1.8091 | 542.7273 | 81.8182 | 82
MC1 | D4 | 105 | 250 | 2016-12-01 22:30 | 2016-12-02 05:14 | 240 | 330 | 300 | Pulverizer feeders | F5901D Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 12 | 6.7333 | 1.8364 | 550.9091 | 81.8182 | 82
MC1 | D4 | 106 | 310 | 2016-12-05 22:30 | 2016-12-06 04:11 | 240 | 330 | 300 | Pulverizer mills | F5901B Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 12 | 5.6833 | 1.55 | 465 | 81.8182 | 82
MC1 | D1 | 107 | 250 | 2016-12-09 05:47 | 2016-12-09 11:22 | 240 | 330 | 300 | Pulverizer feeders | F8201B Feeder Tripped | Mill Creek | Derate | Coal | 2 | 2016 | 12 | 5.5833 | 1.5227 | 456.8182 | 81.8182 | 82
MC1 | D4 | 108 | 310 | 2016-12-12 23:09 | 2016-12-13 00:45 | 240 | 330 | 300 | Pulverizer mills | F5901C & 1D Mill Roller Adjustments | Mill Creek | Derate | Coal | 2 | 2016 | 12 | 1.6 | 0.43636 | 130.9091 | 81.8182 | 82
MC1 | D1 | 109 | 250 | 2016-12-15 14:09 | 2016-12-15 15:51 | 250 | 330 | 300 | Pulverizer feeders | F8201B Feeder Tripped | Mill Creek | Derate | Coal | 2 | 2016 | 12 | 1.7 | 0.41212 | 123.6364 | 72.7273 | 73
MC1 | NC | 110 | 1190 | 2016-12-16 23:00 | 2016-12-17 12:00 | 0 | 330 | 300 | Other tube slagging or fouling | FS00Deslag | Mill Creek | Other | Coal | 2 | 2016 | 12 | 13 | 13 | 3900 | 300 | 300
MC1 | D1 | 111 | 3111 | 2016-12-18 16:06 | 2016-12-19 19:28 | 270 | 330 | 300 | Condenser tube fouling shell side | FF00Condenser Fouled (High Back Pressure) | Mill Creek | Derate | Coal | 2 | 2016 | 12 | 27.3667 | 4.9758 | 1492.7273 | 54.5455 | 55
MC1 | D1 | 112 | 250 | 2016-12-19 19:28 | 2016-12-19 21:00 | 250 | 330 | 300 | Pulverizer feeders | F1201A Feeder Maintenance - Cleared debris blocking flow | Mill Creek | Derate | Coal | 2 | 2016 | 12 | 1.5333 | 0.37172 | 111.5152 | 72.7273 | 73
MC1 | D1 | 113 | 3111 | 2016-12-19 21:00 | 2016-12-19 23:00 | 270 | 330 | 300 | Condenser tube fouling shell side | FF00Condenser Fouled - High Back Pressure | Mill Creek | Derate | Coal | 2 | 2016 | 12 | 2 | 0.36364 | 109.0909 | 54.5455 | 55
MC1 | D4 | 114 | 250 | 2016-12-19 23:00 | 2016-12-20 04:55 | 270 | 330 | 300 | Pulverizer feeders | F5901B Feeder Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 12 | 5.9167 | 1.0758 | 322.7273 | 54.5455 | 55
MC1 | D1 | 115 | 3111 | 2016-12-20 04:55 | 2016-12-21 14:26 | 270 | 330 | 300 | Condenser tube fouling shell side | FF00Condenser Fouled - High Back Pressure | Mill Creek | Derate | Coal | 2 | 2016 | 12 | 33.5167 | 6.0939 | 1828.1818 | 54.5455 | 55
MC1 | MO | 116 | 3111 | 2016-12-21 14:26 | 2016-12-21 20:29 | 0 | 330 | 300 | Condenser tube fouling shell side | FF00Condenser Fouled - Cleaned Tubesheets | Mill Creek | Maintenance | Coal | 2 | 2016 | 12 | 6.05 | 6.05 | 1815 | 300 | 300
MC1 | D1 | 117 | 250 | 2016-12-27 10:48 | 2016-12-27 14:39 | 245 | 330 | 300 | Pulverizer feeders | F3401C Feeder will not start | Mill Creek | Derate | Coal | 2 | 2016 | 12 | 3.85 | 0.99167 | 297.5 | 77.2727 | 77
MC1 | D1 | 118 | 280 | 2016-12-27 15:48 | 2017-01-01 | 245 | 330 | 300 | Pulverizer fires | F4401C Mill puffed | Mill Creek | Derate | Coal | 2 | 2016 | 12 | 104.2 | 26.8394 | 8051.8182 | 77.2727 | 77
MC1 | D1 | 1 | 280 | 2017-01-01 | 2017-01-03 01:05 | 245 | 330 | 300 | Pulverizer fires | F4401C Mill Puff (Event started in 2016) | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 49.0833 | 12.6427 | 3792.803 | 77.2727 | 77
MC1 | D1 | 2 | 280 | 2017-01-03 01:05 | 2017-01-03 04:56 | 175 | 330 | 300 | Pulverizer fires | F4401C Coal Mill Puff & 1A Feeder | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 3.85 | 1.8083 | 542.5 | 140.9091 | 141
MC1 | D1 | 3 | 280 | 2017-01-03 04:56 | 2017-01-07 00:51 | 245 | 330 | 300 | Pulverizer fires | F4401C Mill Puff | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 91.9167 | 23.6755 | 7102.6515 | 77.2727 | 77
MC1 | NC | 4 | 1100 | 2017-01-08 12:50 | 2017-01-08 16:36 | 0 | 330 | 300 | Waterwall (Furnace wall) B | FS00Deslag | Mill Creek | Other | Coal | 2 | 2017 | 1 | 3.7667 | 3.7667 | 1130 | 300 | 300
MC1 | NC | 5 | 1160 | 2017-01-10 | 2017-01-10 05:45 | 0 | 330 | 300 | First reheater B | FS00Deslag | Mill Creek | Other | Coal | 2 | 2017 | 1 | 5.75 | 5.75 | 1725 | 300 | 300
MC1 | D1 | 6 | 1160 | 2017-01-10 18:56 | 2017-01-11 09:20 | 130 | 330 | 300 | First reheater B | FS00Deslag | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 14.4 | 8.7273 | 2618.1818 | 181.8182 | 182
MC1 | U1 | 7 | 1160 | 2017-01-11 09:20 | 2017-01-13 20:07 | 0 | 330 | 300 | First reheater B | FS00Deslag | Mill Creek | Outage | Coal | 2 | 2017 | 1 | 58.7833 | 58.7833 | 17635 | 300 | 300
MC1 | NC | 8 | 1850 | 2017-01-13 20:07 | 2017-01-14 04:32 | 0 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm start | Mill Creek | Other | Coal | 2 | 2017 | 1 | 8.4167 | 8.4167 | 2525 | 300 | 300
MC1 | D1 | 9 | 1850 | 2017-01-14 04:32 | 2017-01-14 04:52 | 261 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 0.33333 | 0.069697 | 20.9091 | 62.7273 | 63
MC1 | D1 | 10 | 1850 | 2017-01-14 04:52 | 2017-01-14 09:30 | 275 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 4.6333 | 0.77222 | 231.6667 | 50 | 50
MC1 | NC | 11 | 8460 | 2017-01-18 22:40 | 2017-01-19 01:35 | 0 | 330 | 300 | Testing A | F790Low Load RATA - 215 MW | Mill Creek | Other | Coal | 2 | 2017 | 1 | 2.9167 | 2.9167 | 875 | 300 | 300
MC1 | D4 | 12 | 310 | 2017-01-24 23:00 | 2017-01-25 04:50 | 240 | 330 | 300 | Pulverizer mills | F5901C Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 5.8333 | 1.5909 | 477.2727 | 81.8182 | 82
MC1 | D4 | 13 | 310 | 2017-01-25 23:00 | 2017-01-26 01:31 | 240 | 330 | 300 | Pulverizer mills | F5901C Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 2.5167 | 0.68636 | 205.9091 | 81.8182 | 82
MC1 | D4 | 14 | 310 | 2017-01-26 23:00 | 2017-01-27 03:58 | 245 | 330 | 300 | Pulverizer mills | F5901A Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 4.9667 | 1.2793 | 383.7879 | 77.2727 | 77
MC1 | D1 | 15 | 360 | 2017-01-27 03:58 | 2017-01-27 04:52 | 176 | 330 | 300 | Burners | F7801C Mill Burner Temperatures | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 0.9 | 0.42 | 126 | 140 | 140
MC1 | D1 | 16 | 360 | 2017-01-27 04:52 | 2017-01-27 08:51 | 250 | 330 | 300 | Burners | F7801C Mill Burner Temperatures | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 3.9833 | 0.96566 | 289.697 | 72.7273 | 73
MC1 | D4 | 17 | 310 | 2017-01-30 23:00 | 2017-01-31 04:30 | 240 | 330 | 300 | Pulverizer mills | F5901B Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 5.5 | 1.5 | 450 | 81.8182 | 82
MC1 | D4 | 18 | 310 | 2017-01-31 23:00 | 2017-02-01 04:28 | 240 | 330 | 300 | Pulverizer mills | F5901D Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 5.4667 | 1.4909 | 447.2727 | 81.8182 | 82
MC1 | MO | 19 | 4293 | 2017-02-03 11:36 | 2017-02-04 04:06 | 0 | 330 | 300 | Hydraulic system pipes and valves | F540EHC Leak Repair (& Condenser Dye Test) | Mill Creek | Maintenance | Coal | 2 | 2017 | 2 | 16.5 | 16.5 | 4950 | 300 | 300
MC1 | D4 | 20 | 310 | 2017-02-22 23:25 | 2017-02-23 04:29 | 240 | 330 | 300 | Pulverizer mills | F5901A Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 2 | 5.0667 | 1.3818 | 414.5455 | 81.8182 | 82
MC1 | D4 | 21 | 310 | 2017-02-23 23:00 | 2017-02-24 04:28 | 240 | 330 | 300 | Pulverizer mills | F5901D Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 2 | 5.4667 | 1.4909 | 447.2727 | 81.8182 | 82
MC1 | D1 | 22 | 1493 | 2017-02-24 17:03 | 2017-02-24 22:55 | 250 | 330 | 300 | Air heater fouling (regenerative) | F660High Air Heater Differential (A Side) | Mill Creek | Derate | Coal | 2 | 2017 | 2 | 5.8667 | 1.4222 | 426.6667 | 72.7273 | 73
MC1 | D1 | 23 | 1493 | 2017-02-24 22:55 | 2017-02-27 16:15 | 240 | 330 | 300 | Air heater fouling (regenerative) | F660High Air Heater Differential (A Side) | Mill Creek | Derate | Coal | 2 | 2017 | 2 | 65.3333 | 17.8182 | 5345.4545 | 81.8182 | 82
MC1 | U1 | 24 | 1455 | 2017-02-27 16:15 | 2017-02-27 21:38 | 0 | 330 | 300 | Induced draft fans | F820ID Fan Index Trip | Mill Creek | Outage | Coal | 2 | 2017 | 2 | 5.3833 | 5.3833 | 1615 | 300 | 300
MC1 | D1 | 25 | 1493 | 2017-02-28 02:06 | 2017-02-28 04:22 | 240 | 330 | 300 | Air heater fouling (regenerative) | F660'High Air Heater Differential (A Side) | Mill Creek | Derate | Coal | 2 | 2017 | 2 | 2.2667 | 0.61818 | 185.4545 | 81.8182 | 82
MC1 | D1 | 26 | 1493 | 2017-02-28 04:22 | 2017-02-28 21:40 | 230 | 330 | 300 | Air heater fouling (regenerative) | F660High Air Heater Differential (A Side) | Mill Creek | Derate | Coal | 2 | 2017 | 2 | 17.3 | 5.2424 | 1572.7273 | 90.9091 | 91
MC1 | MO | 27 | 1493 | 2017-02-28 21:40 | 2017-03-03 19:36 | 0 | 330 | 300 | Air heater fouling (regenerative) | F660Air Heater Wash | Mill Creek | Maintenance | Coal | 2 | 2017 | 2 | 69.9333 | 69.9333 | 20980 | 300 | 300
MC1 | NC | 28 | 9999 | 2017-03-07 08:00 | 2017-03-07 12:23 | 0 | 330 | 300 | Total unit performance testing (use appropriate codes for individual component testing) | F790MATS Testing - Full Load | Mill Creek | Other | Coal | 2 | 2017 | 3 | 4.3833 | 4.3833 | 1315 | 300 | 300
MC1 | D4 | 29 | 310 | 2017-03-23 22:00 | 2017-03-23 22:25 | 240 | 330 | 300 | Pulverizer mills | F5901D Coal Mill Maintinance | Mill Creek | Derate | Coal | 2 | 2017 | 3 | 0.41667 | 0.11364 | 34.0909 | 81.8182 | 82
MC1 | D4 | 30 | 740 | 2017-03-23 22:25 | 2017-03-24 01:31 | 150 | 330 | 300 | Boiler recirculation pumps | F590Removing BCWP an CWP from service | Mill Creek | Derate | Coal | 2 | 2017 | 3 | 3.1 | 1.6909 | 507.2727 | 163.6364 | 164
MC1 | D4 | 31 | 310 | 2017-03-24 01:31 | 2017-03-24 04:00 | 240 | 330 | 300 | Pulverizer mills | F5901D Coal Mill Maintinance | Mill Creek | Derate | Coal | 2 | 2017 | 3 | 2.4833 | 0.67727 | 203.1818 | 81.8182 | 82
MC1 | D1 | 33 | 270 | 2017-03-24 04:42 | 2017-03-24 04:48 | 250 | 330 | 300 | Primary air duct and dampers | F7201D Mill Hot Air Gate Issues (Sticking Open) | Mill Creek | Derate | Coal | 2 | 2017 | 3 | 0.1 | 0.024242 | 7.2727 | 72.7273 | 73
MC1 | PO | 34 | 4402 | 2017-04-01 00:36 | 2017-05-01 | 0 | 330 | 300 | Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | F590Planned Outage - Spring 2017 | Mill Creek | Other | Coal | 2 | 2017 | 4 | 719.4 | 719.4 | 215820 | 300 | 300
MC1 | PE | 40 | 4402 | 2017-05-01 | 2017-05-01 07:24 | 0 | 330 | 300 | Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | F590Planned Outage - Spring 2017 (Extension) | Mill Creek | Other | Coal | 2 | 2017 | 5 | 7.4 | 7.4 | 2220 | 300 | 300
MC1 | U1 | 35 | 800 | 2017-05-01 07:41 | 2017-05-01 10:59 | 0 | 330 | 300 | Drums and drum internals (single drum only) | F820Drum Level Trip | Mill Creek | Outage | Coal | 2 | 2017 | 5 | 3.3 | 3.3 | 990 | 300 | 300
MC1 | D1 | 36 | 8650 | 2017-05-02 09:19 | 2017-05-02 14:08 | 300 | 330 | 300 | Baghouse systems | F660High Baghouse Differential | Mill Creek | Derate | Coal | 2 | 2017 | 5 | 4.8167 | 0.43788 | 131.3636 | 27.2727 | 27
MC1 | D1 | 37 | 250 | 2017-05-02 14:08 | 2017-05-02 18:25 | 235 | 330 | 300 | Pulverizer feeders | F1201C Feeder Tripped (Foreign Material) | Mill Creek | Derate | Coal | 2 | 2017 | 5 | 4.2833 | 1.2331 | 369.9242 | 86.3636 | 86
MC1 | U1 | 38 | 770 | 2017-05-05 10:45 | 2017-05-05 11:57 | 0 | 330 | 300 | Other boiler recirculation problems | F420'Loss of BCP's (Breaker Switching Error) | Mill Creek | Outage | Coal | 2 | 2017 | 5 | 1.2 | 1.2 | 360 | 300 | 300
MC1 | D1 | 39 | 1850 | 2017-05-05 16:19 | 2017-05-05 17:20 | 250 | 330 | 300 | Boiler water condition (not feedwater water quality) | F170High Silica - Startup | Mill Creek | Derate | Coal | 2 | 2017 | 5 | 1.0167 | 0.24646 | 73.9394 | 72.7273 | 73
MC1 | D4 | 41 | 310 | 2017-05-11 22:00 | 2017-05-12 04:01 | 240 | 330 | 300 | Pulverizer mills | F5901C Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 5 | 6.0167 | 1.6409 | 492.2727 | 81.8182 | 82
MC1 | D4 | 43 | 310 | 2017-06-15 23:00 | 2017-06-16 04:13 | 250 | 330 | 300 | Pulverizer mills | F5901B Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 5.2167 | 1.2646 | 379.3939 | 72.7273 | 73
MC1 | D4 | 44 | 310 | 2017-06-19 23:00 | 2017-06-20 04:00 | 240 | 330 | 300 | Pulverizer mills | F5901A Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 5 | 1.3636 | 409.0909 | 81.8182 | 82
MC1 | D4 | 46 | 310 | 2017-06-20 23:00 | 2017-06-21 04:08 | 240 | 330 | 300 | Pulverizer mills | F5901C Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 5.1333 | 1.4 | 420 | 81.8182 | 82
MC1 | D4 | 47 | 310 | 2017-06-21 23:00 | 2017-06-22 03:46 | 240 | 330 | 300 | Pulverizer mills | F5901D Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 4.7667 | 1.3 | 390 | 81.8182 | 82
MC1 | D4 | 48 | 310 | 2017-07-06 23:00 | 2017-07-07 04:00 | 240 | 330 | 300 | Pulverizer mills | F5901A Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 5 | 1.3636 | 409.0909 | 81.8182 | 82
MC1 | D1 | 49 | 9930 | 2017-07-09 07:44 | 2017-07-09 08:33 | 65 | 330 | 300 | Operating procedure error | F690Lost C Mill & Igniter Issue On Other Mills | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 0.81667 | 0.65581 | 196.7424 | 240.9091 | 241
MC1 | D1 | 50 | 95 | 2017-07-09 08:33 | 2017-07-09 10:32 | 250 | 330 | 300 | Bunker flow problems | F1201C Coal Silo Flow Issues | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 1.9833 | 0.48081 | 144.2424 | 72.7273 | 73
MC1 | D4 | 51 | 310 | 2017-07-26 23:00 | 2017-07-27 04:03 | 250 | 330 | 300 | Pulverizer mills | F5901B Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 5.05 | 1.2242 | 367.2727 | 72.7273 | 73
MC1 | D4 | 52 | 310 | 2017-07-27 23:00 | 2017-07-28 03:58 | 250 | 330 | 300 | Pulverizer mills | F5901C Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 4.9667 | 1.204 | 361.2121 | 72.7273 | 73
MC1 | D4 | 53 | 8620 | 2017-07-28 22:00 | 2017-07-29 00:35 | 125 | 330 | 300 | Mercury Abatement Equipment | F610FGD Controls - Nalco System Installation | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 2.5833 | 1.6048 | 481.4394 | 186.3636 | 186
MC1 | D1 | 54 | 250 | 2017-08-09 05:48 | 2017-08-09 07:45 | 50 | 330 | 300 | Pulverizer feeders | F8201C Feeder Trip - Variable Derate | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 1.95 | 1.6545 | 496.3636 | 254.5455 | 255
MC1 | D1 | 55 | 250 | 2017-08-09 07:45 | 2017-08-09 08:26 | 250 | 330 | 300 | Pulverizer feeders | F5301C Mill and Feeder Inspection | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 0.68333 | 0.16566 | 49.697 | 72.7273 | 73
MC1 | D4 | 56 | 310 | 2017-08-09 23:00 | 2017-08-10 03:59 | 240 | 330 | 300 | Pulverizer mills | F5901A Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 4.9833 | 1.3591 | 407.7273 | 81.8182 | 82
MC1 | D4 | 57 | 310 | 2017-08-10 22:00 | 2017-08-11 04:00 | 240 | 330 | 300 | Pulverizer mills | F5901D Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 6 | 1.6364 | 490.9091 | 81.8182 | 82
MC1 | D4 | 58 | 310 | 2017-08-17 21:45 | 2017-08-17 23:30 | 240 | 330 | 300 | Pulverizer mills | F5901D Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 1.75 | 0.47727 | 143.1818 | 81.8182 | 82
MC1 | D4 | 59 | 310 | 2017-08-17 23:30 | 2017-08-18 03:26 | 240 | 330 | 300 | Pulverizer mills | F5901C Coal Mill & Feeder Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 3.9333 | 1.0727 | 321.8182 | 81.8182 | 82
MC1 | NC | 60 | 9997 | 2017-08-20 00:49 | 2017-08-21 02:50 | 0 | 330 | 300 | NERC Reliability Standards requirements | F790Low Load VAR Testing | Mill Creek | Other | Coal | 2 | 2017 | 8 | 26.0167 | 26.0167 | 7805 | 300 | 300
MC1 | D1 | 61 | 250 | 2017-08-20 10:38 | 2017-08-20 11:40 | 240 | 330 | 300 | Pulverizer feeders | F1201B Feeder Plugged | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 1.0333 | 0.28182 | 84.5455 | 81.8182 | 82
MC1 | D1 | 62 | 250 | 2017-08-20 23:32 | 2017-08-21 03:10 | 245 | 330 | 300 | Pulverizer feeders | F1201C Feeder Plugged | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 3.6333 | 0.93586 | 280.7576 | 77.2727 | 77
MC1 | D4 | 63 | 310 | 2017-08-24 22:00 | 2017-08-25 01:51 | 240 | 330 | 300 | Pulverizer mills | F5901D Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 3.85 | 1.05 | 315 | 81.8182 | 82
MC1 | D4 | 64 | 310 | 2017-08-27 22:00 | 2017-08-28 02:31 | 240 | 330 | 300 | Pulverizer mills | F5901C Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 4.5167 | 1.2318 | 369.5455 | 81.8182 | 82
MC1 | D4 | 65 | 310 | 2017-08-28 22:00 | 2017-08-29 01:56 | 240 | 330 | 300 | Pulverizer mills | F5901B Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 3.9333 | 1.0727 | 321.8182 | 81.8182 | 82
MC1 | U1 | 66 | 4460 | 2017-09-02 00:23 | 2017-09-02 02:16 | 0 | 330 | 300 | Turbine overspeed trip test | F820Weekly Mechanical Over Speed Trip Test Malfunction | Mill Creek | Outage | Coal | 2 | 2017 | 9 | 1.8833 | 1.8833 | 565 | 300 | 300
MC1 | D4 | 67 | 310 | 2017-09-06 22:00 | 2017-09-07 02:59 | 240 | 330 | 300 | Pulverizer mills | F5901A Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 9 | 4.9833 | 1.3591 | 407.7273 | 81.8182 | 82
MC1 | D1 | 68 | 3415 | 2017-09-12 07:20 | 2017-09-12 11:59 | 200 | 330 | 300 | Feedwater pump/drive lube oil system | F6601B BFP Tripped - Low Oil Pressure | Mill Creek | Derate | Coal | 2 | 2017 | 9 | 4.65 | 1.8318 | 549.5455 | 118.1818 | 118
MC1 | D4 | 69 | 310 | 2017-09-12 23:00 | 2017-09-13 04:00 | 240 | 330 | 300 | Pulverizer mills | F5901B Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 9 | 5 | 1.3636 | 409.0909 | 81.8182 | 82
MC1 | D1 | 71 | 250 | 2017-09-18 20:28 | 2017-09-18 20:35 | 240 | 330 | 300 | Pulverizer feeders | F1201B Coal Feeder - Debris Removal | Mill Creek | Derate | Coal | 2 | 2017 | 9 | 0.11667 | 0.031818 | 9.5455 | 81.8182 | 82
MC1 | D4 | 72 | 1990 | 2017-09-19 23:00 | 2017-09-19 23:55 | 240 | 330 | 300 | Boiler performance testing (use code 9999 for total unit performance testing) | F7901C Air Flow Testing | Mill Creek | Derate | Coal | 2 | 2017 | 9 | 0.91667 | 0.25 | 75 | 81.8182 | 82
MC1 | D4 | 73 | 310 | 2017-09-25 22:00 | 2017-09-26 03:33 | 245 | 330 | 300 | Pulverizer mills | F5901A Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 9 | 5.55 | 1.4295 | 428.8636 | 77.2727 | 77
MC1 | D1 | 74 | 312 | 2017-10-09 09:58 | 2017-10-09 13:27 | 250 | 330 | 300 | Pulverizer mill classifiers | F8501B Coal Mill Vibration | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 3.4833 | 0.84444 | 253.3333 | 72.7273 | 73
MC1 | D1 | 75 | 312 | 2017-10-09 18:03 | 2017-10-10 05:47 | 250 | 330 | 300 | Pulverizer mill classifiers | F8501B Coal Mill Vibration - Inspect and Cleanout Debris | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 11.7333 | 2.8444 | 853.3333 | 72.7273 | 73
MC1 | D4 | 76 | 310 | 2017-10-10 23:42 | 2017-10-11 04:00 | 250 | 330 | 300 | Pulverizer mills | F5901B Coal Mill Maintenance - Vibration | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 4.3 | 1.0424 | 312.7273 | 72.7273 | 73
MC1 | D4 | 78 | 310 | 2017-10-16 23:00 | 2017-10-17 03:34 | 240 | 330 | 300 | Pulverizer mills | F5901D Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 4.5667 | 1.2455 | 373.6364 | 81.8182 | 82
MC1 | D4 | 79 | 310 | 2017-10-17 22:00 | 2017-10-18 04:00 | 250 | 330 | 300 | Pulverizer mills | F5901C Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 6 | 1.4545 | 436.3636 | 72.7273 | 73
MC1 | D4 | 81 | 310 | 2017-10-18 22:00 | 2017-10-19 03:53 | 250 | 330 | 300 | Pulverizer mills | F5901B Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 5.8833 | 1.4263 | 427.8788 | 72.7273 | 73
MC1 | D4 | 82 | 310 | 2017-10-19 22:00 | 2017-10-20 03:21 | 250 | 330 | 300 | Pulverizer mills | F5901A Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 5.35 | 1.297 | 389.0909 | 72.7273 | 73
MC1 | D4 | 83 | 310 | 2017-11-05 22:00 | 2017-11-06 03:50 | 235 | 330 | 300 | Pulverizer mills | F5901D Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 11 | 5.8333 | 1.6793 | 503.7879 | 86.3636 | 86
MC1 | NC | 84 | 3415 | 2017-11-07 | 2017-11-07 02:49 | 0 | 330 | 300 | Feedwater pump/drive lube oil system | F790B BFP Low Oil Pressure Testing | Mill Creek | Other | Coal | 2 | 2017 | 11 | 2.8167 | 2.8167 | 845 | 300 | 300
MC1 | NC | 85 | 1190 | 2017-11-08 10:57 | 2017-11-08 16:24 | 0 | 330 | 300 | Other tube slagging or fouling | FS00Deslag | Mill Creek | Other | Coal | 2 | 2017 | 11 | 5.45 | 5.45 | 1635 | 300 | 300
MC1 | NC | 86 | 1190 | 2017-11-09 15:05 | 2017-11-09 17:09 | 0 | 330 | 300 | Other tube slagging or fouling | FS00Deslag | Mill Creek | Other | Coal | 2 | 2017 | 11 | 2.0667 | 2.0667 | 620 | 300 | 300
MC1 | NC | 87 | 1190 | 2017-11-12 23:15 | 2017-11-13 04:45 | 0 | 330 | 300 | Other tube slagging or fouling | FS00Deslag | Mill Creek | Other | Coal | 2 | 2017 | 11 | 5.5 | 5.5 | 1650 | 300 | 300
MC1 | NC | 88 | 1190 | 2017-11-14 | 2017-11-14 05:25 | 0 | 330 | 300 | Other tube slagging or fouling | FS00Deslag | Mill Creek | Other | Coal | 2 | 2017 | 11 | 5.4167 | 5.4167 | 1625 | 300 | 300
MC1 | D1 | 89 | 1190 | 2017-11-15 20:43 | 2017-11-16 00:33 | 140 | 330 | 300 | Other tube slagging or fouling | FS00Deslag | Mill Creek | Derate | Coal | 2 | 2017 | 11 | 3.8333 | 2.2071 | 662.1212 | 172.7273 | 173
MC1 | D1 | 90 | 1493 | 2017-11-19 11:53 | 2017-11-23 01:27 | 310 | 330 | 300 | Air heater fouling (regenerative) | F6601A Air Heater High DP | Mill Creek | Derate | Coal | 2 | 2017 | 11 | 85.5667 | 5.1859 | 1555.7576 | 18.1818 | 18
MC1 | MO | 91 | 1493 | 2017-11-23 01:27 | 2017-11-26 07:34 | 0 | 330 | 300 | Air heater fouling (regenerative) | F660Air Heater Wash | Mill Creek | Maintenance | Coal | 2 | 2017 | 11 | 78.1167 | 78.1167 | 23435 | 300 | 300
MC1 | MO | 92 | 1000 | 2017-11-28 11:36 | 2017-11-29 08:12 | 0 | 330 | 300 | Waterwall (Furnace wall) A | F540External Boiler Tube Leak | Mill Creek | Maintenance | Coal | 2 | 2017 | 11 | 20.6 | 20.6 | 6180 | 300 | 300
MC1 | NC | 93 | 250 | 2017-11-30 21:00 | 2017-12-01 03:00 | 0 | 330 | 300 | Pulverizer feeders | F5901D Feeder Maintinance (Setting Rollers) | Mill Creek | Other | Coal | 2 | 2017 | 11 | 6 | 6 | 1800 | 300 | 300
MC1 | NC | 94 | 4842 | 2017-12-05 10:05 | 2017-12-05 11:55 | 0 | 330 | 300 | Reactive and capability testing | F790MOD 27 Testing - Out of AGC | Mill Creek | Other | Coal | 2 | 2017 | 12 | 1.8333 | 1.8333 | 550 | 300 | 300
MC1 | NC | 95 | 8460 | 2017-12-10 23:00 | 2017-12-11 05:15 | 0 | 330 | 300 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2017 | 12 | 6.25 | 6.25 | 1875 | 300 | 300
MC1 | D1 | 96 | 250 | 2017-12-13 01:50 | 2017-12-13 02:30 | 240 | 330 | 300 | Pulverizer feeders | F1201C Coal Mill Feeder Plugged | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 0.66667 | 0.18182 | 54.5455 | 81.8182 | 82
MC1 | D4 | 97 | 310 | 2017-12-13 02:30 | 2017-12-13 04:40 | 240 | 330 | 300 | Pulverizer mills | F5901C Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 2.1667 | 0.59091 | 177.2727 | 81.8182 | 82
MC1 | D4 | 98 | 310 | 2017-12-13 22:00 | 2017-12-13 23:00 | 240 | 330 | 300 | Pulverizer mills | F5901D Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 1 | 0.27273 | 81.8182 | 81.8182 | 82
MC1 | NC | 99 | 8460 | 2017-12-13 23:00 | 2017-12-14 03:40 | 0 | 330 | 300 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2017 | 12 | 4.6667 | 4.6667 | 1400 | 300 | 300
MC1 | D4 | 100 | 310 | 2017-12-14 23:00 | 2017-12-15 04:00 | 240 | 330 | 300 | Pulverizer mills | F5901D Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 5 | 1.3636 | 409.0909 | 81.8182 | 82
MC1 | D4 | 102 | 310 | 2017-12-18 22:00 | 2017-12-19 02:11 | 240 | 330 | 300 | Pulverizer mills | F5901C Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 4.1833 | 1.1409 | 342.2727 | 81.8182 | 82
MC1 | D1 | 103 | 250 | 2017-12-26 13:12 | 2017-12-26 14:26 | 235 | 330 | 300 | Pulverizer feeders | F1201D Coal Feeder - Foreign Material | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 1.2333 | 0.35505 | 106.5152 | 86.3636 | 86
MC1 | NC | 1 | 8020 | 2018-01-01 11:32 | 2018-01-02 06:35 | 0 | 330 | 300 | Mill slurry tanks supply problems | F930Limestone Slurry Levels | Mill Creek | Other | Coal | 2 | 2018 | 1 | 19.05 | 19.05 | 5715 | 300 | 300
MC1 | D1 | 2 | 310 | 2018-01-18 02:18 | 2018-01-18 05:43 | 250 | 330 | 300 | Pulverizer mills | F5901D Coal Mill - Foreign Material In Mill | Mill Creek | Derate | Coal | 2 | 2018 | 1 | 3.4167 | 0.82828 | 248.4848 | 72.7273 | 73
MC1 | D4 | 3 | 310 | 2018-01-29 22:09 | 2018-01-30 03:22 | 240 | 330 | 300 | Pulverizer mills | F5901A Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2018 | 1 | 5.2167 | 1.4227 | 426.8182 | 81.8182 | 82
MC1 | NC | 4 | 360 | 2018-02-08 | 2018-02-08 00:38 | 0 | 330 | 300 | Burners | F5301B Coal Mill Off - Check Burners | Mill Creek | Other | Coal | 2 | 2018 | 2 | 0.63333 | 0.63333 | 190 | 300 | 300
MC1 | D4 | 5 | 310 | 2018-02-22 00:29 | 2018-02-22 00:53 | 240 | 330 | 300 | Pulverizer mills | F5901D Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2018 | 2 | 0.4 | 0.10909 | 32.7273 | 81.8182 | 82
MC1 | D1 | 6 | 250 | 2018-02-25 01:36 | 2018-02-25 03:39 | 245 | 330 | 300 | Pulverizer feeders | F1201D Coal Feeder Plugged - Wet Coal | Mill Creek | Derate | Coal | 2 | 2018 | 2 | 2.05 | 0.52803 | 158.4091 | 77.2727 | 77
MC1 | D1 | 7 | 250 | 2018-02-25 05:04 | 2018-02-25 06:42 | 245 | 330 | 300 | Pulverizer feeders | F1201B Coal Feeder Plugged - Wet Coal | Mill Creek | Derate | Coal | 2 | 2018 | 2 | 1.6333 | 0.42071 | 126.2121 | 77.2727 | 77
MC1 | D1 | 8 | 253 | 2018-03-04 23:47 | 2018-03-05 00:28 | 250 | 330 | 300 | Pulverizer feeder motor | F3401B Coal Feeder Motor Start Alarm | Mill Creek | Derate | Coal | 2 | 2018 | 3 | 0.68333 | 0.16566 | 49.697 | 72.7273 | 73
MC1 | PO | 9 | 8450 | 2018-03-09 21:38 | 2018-03-26 | 0 | 330 | 300 | Inspection B | F590Planned Outage - Spring 2018 - 2 Weeks | Mill Creek | Other | Coal | 2 | 2018 | 3 | 386.3667 | 386.3667 | 115910 | 300 | 300
MC1 | PE | 10 | 8450 | 2018-03-26 | 2018-03-26 10:51 | 0 | 330 | 300 | Inspection B | F590Planned Outage Extension - Spring 2018 | Mill Creek | Other | Coal | 2 | 2018 | 3 | 10.85 | 10.85 | 3255 | 300 | 300
MC1 | U1 | 11 | 3344 | 2018-03-26 12:53 | 2018-03-26 17:48 | 0 | 330 | 300 | Deaerator (including level control) | F830Deaerator Door Leak | Mill Creek | Outage | Coal | 2 | 2018 | 3 | 4.9167 | 4.9167 | 1475 | 300 | 300
MC1 | D1 | 12 | 250 | 2018-04-02 18:47 | 2018-04-02 22:12 | 250 | 330 | 300 | Pulverizer feeders | F1201D Coal Feeder Plugged | Mill Creek | Derate | Coal | 2 | 2018 | 4 | 3.4167 | 0.82828 | 248.4848 | 72.7273 | 73
MC1 | D4 | 13 | 310 | 2018-04-02 22:34 | 2018-04-03 01:34 | 250 | 330 | 300 | Pulverizer mills | F5901B Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2018 | 4 | 3 | 0.72727 | 218.1818 | 72.7273 | 73
MC1 | D4 | 14 | 310 | 2018-04-11 21:00 | 2018-04-12 05:03 | 250 | 330 | 300 | Pulverizer mills | F5901C Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2018 | 4 | 8.05 | 1.9515 | 585.4545 | 72.7273 | 73
MC1 | D4 | 15 | 255 | 2018-04-26 22:00 | 2018-04-27 02:55 | 250 | 330 | 300 | Pulverizer feeder coal scales | F0901A Coal Feeder Calibration | Mill Creek | Derate | Coal | 2 | 2018 | 4 | 4.9167 | 1.1919 | 357.5758 | 72.7273 | 73
MC1 | D4 | 16 | 255 | 2018-04-27 22:20 | 2018-04-28 00:49 | 240 | 330 | 300 | Pulverizer feeder coal scales | F0901B Coal Feeder Calibration | Mill Creek | Derate | Coal | 2 | 2018 | 4 | 2.4833 | 0.67727 | 203.1818 | 81.8182 | 82
MC1 | D4 | 17 | 255 | 2018-04-28 22:35 | 2018-04-29 01:06 | 240 | 330 | 300 | Pulverizer feeder coal scales | F0901C Coal Feeder Calibration | Mill Creek | Derate | Coal | 2 | 2018 | 4 | 2.5167 | 0.68636 | 205.9091 | 81.8182 | 82
MC1 | D4 | 18 | 255 | 2018-04-29 22:25 | 2018-04-30 00:58 | 240 | 330 | 300 | Pulverizer feeder coal scales | F0901D Coal Feeder Calibration | Mill Creek | Derate | Coal | 2 | 2018 | 4 | 2.55 | 0.69545 | 208.6364 | 81.8182 | 82
MC2 | MO | 1 | 1060 | 2013-01-05 02:02 | 2013-01-06 10:47 | 0 | 330 | 296 | First reheater A | F540Boiler Tube Leak - Primary tube failure occurred at the first tube (front to back) | Mill Creek | Maintenance | Coal | 2 | 2013 | 1 | 32.75 | 32.75 | 9694 | 296 | 296
MC2 | NC | 2 | 1850 | 2013-01-06 10:47 | 2013-01-06 20:15 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 1 | 9.4667 | 9.4667 | 2802.1333 | 296 | 296
MC2 | D4 | 3 | 250 | 2013-01-07 23:30 | 2013-01-08 04:09 | 235 | 330 | 296 | Pulverizer feeders | F0902A Coal Feeder - Calibration | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 4.65 | 1.3386 | 396.2364 | 85.2121 | 85
MC2 | D1 | 4 | 3661 | 2013-01-08 14:15 | 2013-01-08 15:34 | 180 | 330 | 296 | 4160-volt circuit breakers | F7802B2 4KV Bus Breaker - Hot Spot | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 1.3167 | 0.59848 | 177.1515 | 134.5455 | 135
MC2 | D1 | 5 | 3661 | 2013-01-08 15:34 | 2013-01-08 16:32 | 240 | 330 | 296 | 4160-volt circuit breakers | F7802B2 4KV Bus Breaker - Hot Spot | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 0.96667 | 0.26364 | 78.0364 | 80.7273 | 81
MC2 | D4 | 6 | 250 | 2013-01-08 23:00 | 2013-01-09 04:31 | 235 | 330 | 296 | Pulverizer feeders | F0902B Coal Feeder - Calibration | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 5.5167 | 1.5881 | 470.0869 | 85.2121 | 85
MC2 | D4 | 7 | 250 | 2013-01-09 23:40 | 2013-01-10 02:41 | 240 | 330 | 296 | Pulverizer feeders | F0902C Coal Feeder - Calibration Cancelled | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 3.0167 | 0.82273 | 243.5273 | 80.7273 | 81
MC2 | D4 | 8 | 250 | 2013-01-10 23:00 | 2013-01-11 04:38 | 240 | 330 | 296 | Pulverizer feeders | F0902C Coal Feeder - Calibration | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 5.6333 | 1.5364 | 454.7636 | 80.7273 | 81
MC2 | D4 | 9 | 250 | 2013-01-13 23:00 | 2013-01-14 01:35 | 240 | 330 | 296 | Pulverizer feeders | F0902D Coal Feeder - Calibration | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 2.5833 | 0.70455 | 208.5455 | 80.7273 | 81
MC2 | D1 | 10 | 9270 | 2013-01-14 01:35 | 2013-01-14 03:10 | 120 | 330 | 296 | Wet coal | FW00Wet Coal Issues | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 1.5833 | 1.0076 | 298.2424 | 188.3636 | 188
MC2 | D1 | 11 | 9270 | 2013-01-14 03:10 | 2013-01-14 06:05 | 185 | 330 | 296 | Wet coal | FW00Wet Coal Issues | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 2.9167 | 1.2816 | 379.3434 | 130.0606 | 130
MC2 | D1 | 12 | 9270 | 2013-01-14 06:05 | 2013-01-15 21:36 | 184 | 330 | 296 | Wet coal | FW00Wet Coal Issues | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 39.5167 | 17.4831 | 5175.0069 | 130.9576 | 131
MC2 | U1 | 13 | 3235 | 2013-01-15 21:36 | 2013-01-17 02:37 | 0 | 330 | 296 | Cooling tower booster pump | F5402B Cooling Tower Pump - Discharge Line Hatch Leak | Mill Creek | Outage | Coal | 2 | 2013 | 1 | 29.0167 | 29.0167 | 8588.9333 | 296 | 296
MC2 | NC | 14 | 1850 | 2013-01-17 02:37 | 2013-01-17 08:40 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 1 | 6.05 | 6.05 | 1790.8 | 296 | 296
MC2 | D1 | 15 | 9270 | 2013-01-17 08:40 | 2013-01-17 12:53 | 200 | 330 | 296 | Wet coal | FW00Wet Coal Issues | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 4.2167 | 1.6611 | 491.6889 | 116.6061 | 117
MC2 | D1 | 16 | 9270 | 2013-01-17 14:47 | 2013-01-17 15:10 | 250 | 330 | 296 | Wet coal | FW002D Coal Feeder - Plugged, Wet Coal | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 0.38333 | 0.092929 | 27.5071 | 71.7576 | 72
MC2 | D1 | 17 | 250 | 2013-01-18 04:40 | 2013-01-18 08:39 | 240 | 330 | 296 | Pulverizer feeders | F5902A Coal Feeder - Align Belt & Repair Clean Out Conveyor | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 3.9833 | 1.0864 | 321.5636 | 80.7273 | 81
MC2 | D1 | 18 | 4261 | 2013-01-22 18:58 | 2013-01-22 20:00 | 300 | 330 | 296 | Control valves | F530Turbine #4 Control Valve - Low Voltage Differential Transmitter Issue | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 1.0333 | 0.093939 | 27.8061 | 26.9091 | 27
MC2 | D1 | 19 | 4261 | 2013-01-22 20:00 | 2013-01-23 01:30 | 225 | 330 | 296 | Control valves | F590Turbine #4 Control Valve - Repair Low Voltage Differential Transmitter Cable | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 5.5 | 1.75 | 518 | 94.1818 | 94
MC2 | D4 | 20 | 310 | 2013-01-27 22:00 | 2013-01-28 05:19 | 230 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Adjust Rollers | Mill Creek | Derate | Coal | 2 | 2013 | 1 | 7.3167 | 2.2172 | 656.2828 | 89.697 | 90
MC2 | NC | 21 | 1160 | 2013-02-05 22:10 | 2013-02-06 03:22 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2013 | 2 | 5.2 | 5.2 | 1539.2 | 296 | 296
MC2 | NC | 22 | 1160 | 2013-02-06 22:14 | 2013-02-07 04:36 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2013 | 2 | 6.3667 | 6.3667 | 1884.5333 | 296 | 296
MC2 | D1 | 23 | 310 | 2013-02-07 13:20 | 2013-02-07 16:40 | 240 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Exhauster Discharge Damper Repair | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 3.3333 | 0.90909 | 269.0909 | 80.7273 | 81
MC2 | NC | 24 | 310 | 2013-02-12 | 2013-02-12 00:39 | 0 | 330 | 296 | Pulverizer mills | F7902A Coal Mill - Air Flow Test | Mill Creek | Other | Coal | 2 | 2013 | 2 | 0.65 | 0.65 | 192.4 | 296 | 296
MC2 | D4 | 25 | 310 | 2013-02-13 22:33 | 2013-02-14 02:03 | 240 | 330 | 296 | Pulverizer mills | F7902B,C &D Coal Mills - Air Flow Test | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 3.5 | 0.95455 | 282.5455 | 80.7273 | 81
MC2 | D4 | 26 | 310 | 2013-02-17 22:20 | 2013-02-18 03:08 | 230 | 330 | 296 | Pulverizer mills | F5902A Coal Mill - Replace Solenoid on Exhauster Discharge Valve | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 4.8 | 1.4545 | 430.5455 | 89.697 | 90
MC2 | D1 | 27 | 310 | 2013-02-18 04:35 | 2013-02-18 05:16 | 245 | 330 | 296 | Pulverizer mills | F5902A Coal Mill - Repair Breaker Racking Mechanism | Mill Creek | Derate | Coal | 2 | 2013 | 2 | 0.68333 | 0.17601 | 52.099 | 76.2424 | 76
MC2 | NC | 28 | 740 | 2013-02-24 08:00 | 2013-02-24 12:00 | 0 | 330 | 296 | Boiler recirculation pumps | F570"B" BCP could not be placed in service due to lube oil pump not starting. | Mill Creek | Other | Coal | 2 | 2013 | 2 | 4 | 4 | 1184 | 296 | 296
MC2 | U1 | 29 | 740 | 2013-03-09 04:13 | 2013-03-09 05:38 | 0 | 330 | 296 | Boiler recirculation pumps | F6602B Boiler Circulating Water Pump - Differential Trip | Mill Creek | Outage | Coal | 2 | 2013 | 3 | 1.4167 | 1.4167 | 419.3333 | 296 | 296
MC2 | NC | 30 | 1850 | 2013-03-09 05:38 | 2013-03-09 09:38 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 3 | 4 | 4 | 1184 | 296 | 296
MC2 | D1 | 31 | 1850 | 2013-03-09 09:38 | 2013-03-09 11:40 | 320 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 3 | 2.0333 | 0.061616 | 18.2384 | 8.9697 | 9
MC2 | D4 | 32 | 310 | 2013-03-11 23:00 | 2013-03-12 01:26 | 235 | 330 | 296 | Pulverizer mills | F5902B Coal Mill - Adjust Rollers | Mill Creek | Derate | Coal | 2 | 2013 | 3 | 2.4333 | 0.70051 | 207.3495 | 85.2121 | 85
MC2 | D4 | 33 | 310 | 2013-03-12 23:00 | 2013-03-13 03:30 | 235 | 330 | 296 | Pulverizer mills | F5902B Coal Mill - Repair Cone | Mill Creek | Derate | Coal | 2 | 2013 | 3 | 4.5 | 1.2955 | 383.4545 | 85.2121 | 85
MC2 | D1 | 34 | 9270 | 2013-03-18 12:45 | 2013-03-18 14:05 | 285 | 330 | 296 | Wet coal | FW002C Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 2 | 2013 | 3 | 1.3333 | 0.18182 | 53.8182 | 40.3636 | 40
MC2 | D1 | 35 | 9270 | 2013-03-18 15:10 | 2013-03-18 17:00 | 255 | 330 | 296 | Wet coal | FW002C Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 2 | 2013 | 3 | 1.8333 | 0.41667 | 123.3333 | 67.2727 | 67
MC2 | D4 | 36 | 310 | 2013-03-18 22:39 | 2013-03-19 03:21 | 235 | 330 | 296 | Pulverizer mills | F5302C Coal Mill - Inspection, Adjust Rollers | Mill Creek | Derate | Coal | 2 | 2013 | 3 | 4.7 | 1.353 | 400.497 | 85.2121 | 85
MC2 | D4 | 37 | 310 | 2013-03-19 22:00 | 2013-03-20 02:06 | 235 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Adjust Rollers | Mill Creek | Derate | Coal | 2 | 2013 | 3 | 4.1 | 1.1803 | 349.3697 | 85.2121 | 85
MC2 | MO | 38 | 3344 | 2013-04-05 10:11 | 2013-04-06 00:48 | 0 | 330 | 296 | Deaerator (including level control) | F590Deaerator Storage Tank - Replace Door Gasket | Mill Creek | Maintenance | Coal | 2 | 2013 | 4 | 14.6167 | 14.6167 | 4326.5333 | 296 | 296
MC2 | NC | 39 | 1850 | 2013-04-06 00:48 | 2013-04-06 07:35 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 4 | 6.7833 | 6.7833 | 2007.8667 | 296 | 296
MC2 | D4 | 40 | 310 | 2013-04-25 22:00 | 2013-04-26 02:30 | 220 | 330 | 296 | Pulverizer mills | F5902C Coal Mill - Clean Distributor | Mill Creek | Derate | Coal | 2 | 2013 | 4 | 4.5 | 1.5 | 444 | 98.6667 | 99
MC2 | U1 | 41 | 3344 | 2013-04-27 11:29 | 2013-04-27 22:57 | 0 | 330 | 296 | Deaerator (including level control) | F280Deaerator Heater - Crack in Shell, Steam Leak | Mill Creek | Outage | Coal | 2 | 2013 | 4 | 11.4667 | 11.4667 | 3394.1333 | 296 | 296
MC2 | PO | 42 | 1801 | 2013-04-27 22:57 | 2013-04-30 14:43 | 0 | 330 | 296 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Planned Outage | Mill Creek | Other | Coal | 2 | 2013 | 4 | 63.7667 | 63.7667 | 18874.9333 | 296 | 296
MC2 | NC | 43 | 1850 | 2013-04-30 14:43 | 2013-04-30 22:43 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2013 | 4 | 8 | 8 | 2368 | 296 | 296
MC2 | D1 | 44 | 590 | 2013-04-30 22:43 | 2013-04-30 23:45 | 260 | 330 | 296 | Desuperheater/attemperator valves | F720Reheat Spray Block Valve - Stuck Closed | Mill Creek | Derate | Coal | 2 | 2013 | 4 | 1.0333 | 0.21919 | 64.8808 | 62.7879 | 63
MC2 | D1 | 45 | 590 | 2013-04-30 23:45 | 2013-05-01 04:30 | 220 | 330 | 296 | Desuperheater/attemperator valves | F720Reheat Spray Block Valve - Stuck Closed | Mill Creek | Derate | Coal | 2 | 2013 | 4 | 4.75 | 1.5833 | 468.6667 | 98.6667 | 99
MC2 | D1 | 46 | 310 | 2013-05-02 23:59 | 2013-05-03 09:02 | 240 | 330 | 296 | Pulverizer mills | F4302D Coal Mill Exhauster - Gate Closed, Wiring Issue | Mill Creek | Derate | Coal | 2 | 2013 | 5 | 9.05 | 2.4682 | 730.5818 | 80.7273 | 81
MC2 | U1 | 47 | 1050 | 2013-05-07 11:22 | 2013-05-08 06:54 | 0 | 330 | 296 | Second superheater B | F540Boiler Tube Leak - Second Superheater | Mill Creek | Outage | Coal | 2 | 2013 | 5 | 19.5333 | 19.5333 | 5781.8667 | 296 | 296
MC2 | NC | 48 | 1850 | 2013-05-08 06:54 | 2013-05-08 12:38 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 5 | 5.7333 | 5.7333 | 1697.0667 | 296 | 296
MC2 | D1 | 49 | 3410 | 2013-05-26 08:23 | 2013-05-26 09:32 | 206 | 330 | 296 | Feedwater pump | F5902B Boiler Feed Pump - Breaker Repair | Mill Creek | Derate | Coal | 2 | 2013 | 5 | 1.15 | 0.43212 | 127.9079 | 111.2242 | 111
MC2 | D4 | 50 | 310 | 2013-05-27 21:00 | 2013-05-28 00:10 | 240 | 330 | 296 | Pulverizer mills | F5302C Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 5 | 3.1667 | 0.86364 | 255.6364 | 80.7273 | 81
MC2 | D4 | 51 | 310 | 2013-05-30 23:00 | 2013-05-31 01:21 | 240 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Roller Adjustment | Mill Creek | Derate | Coal | 2 | 2013 | 5 | 2.35 | 0.64091 | 189.7091 | 80.7273 | 81
MC2 | D1 | 52 | 300 | 2013-06-02 00:09 | 2013-06-02 00:54 | 240 | 330 | 296 | Pulverizer motors and drives | F5902B Coal Mill Motor - Stator Temperature Indication, Thermocouple Repair | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 0.75 | 0.20455 | 60.5455 | 80.7273 | 81
MC2 | D4 | 53 | 200 | 2013-06-10 23:00 | 2013-06-11 04:15 | 240 | 330 | 296 | Pulverizer exhauster fan (for indirect firing) | F5902C Coal Mill Exhauster Fan Maintenance | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 5.25 | 1.4318 | 423.8182 | 80.7273 | 81
MC2 | U1 | 54 | 9320 | 2013-06-26 20:39 | 2013-06-27 22:23 | 0 | 330 | 296 | Other miscellaneous external problems | F820Loss of Fuel Trip - Rainwater in UPS (Un-interruptable Power Supply) | Mill Creek | Outage | Coal | 2 | 2013 | 6 | 25.7333 | 25.7333 | 7617.0667 | 296 | 296
MC2 | NC | 55 | 1850 | 2013-06-27 22:23 | 2013-06-28 05:10 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 6 | 6.7833 | 6.7833 | 2007.8667 | 296 | 296
MC2 | D1 | 56 | 1850 | 2013-06-28 05:10 | 2013-06-28 05:55 | 256 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 0.75 | 0.16818 | 49.7818 | 66.3758 | 66
MC2 | D1 | 57 | 1850 | 2013-06-28 05:55 | 2013-06-28 06:42 | 321 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 0.78333 | 0.021364 | 6.3236 | 8.0727 | 8
MC2 | D1 | 58 | 100 | 2013-06-30 10:55 | 2013-06-30 13:52 | 255 | 330 | 296 | Bunker gates | F1202D Coal Feeder - Lost, Bunker Valve Plugged | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 2.95 | 0.67045 | 198.4545 | 67.2727 | 67
MC2 | D4 | 59 | 310 | 2013-06-30 23:00 | 2013-07-01 03:26 | 230 | 330 | 296 | Pulverizer mills | F5302B & 2C Coal Mills - Inspect Exhausters | Mill Creek | Derate | Coal | 2 | 2013 | 6 | 4.4333 | 1.3434 | 397.6566 | 89.697 | 90
MC2 | D4 | 60 | 250 | 2013-07-02 23:00 | 2013-07-03 03:50 | 250 | 330 | 296 | Pulverizer feeders | F0902D Coal Feeder - Calibration | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 4.8333 | 1.1717 | 346.8283 | 71.7576 | 72
MC2 | D1 | 61 | 1080 | 2013-07-04 09:30 | 2013-07-04 10:38 | 215 | 330 | 296 | Economizer B | F540Boiler Tube Leak - Economizer, Reduced Boiler Pressure | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 1.1333 | 0.39495 | 116.9051 | 103.1515 | 103
MC2 | U2 | 62 | 1080 | 2013-07-04 10:38 | 2013-07-05 08:38 | 0 | 330 | 296 | Economizer B | F540Boiler Tube Leak - Economizer | Mill Creek | Outage | Coal | 2 | 2013 | 7 | 22 | 22 | 6512 | 296 | 296
MC2 | NC | 63 | 1850 | 2013-07-05 08:38 | 2013-07-05 15:00 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 7 | 6.3667 | 6.3667 | 1884.5333 | 296 | 296
MC2 | D1 | 64 | 1850 | 2013-07-05 15:00 | 2013-07-05 19:25 | 264 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 4.4167 | 0.88333 | 261.4667 | 59.2 | 59
MC2 | D4 | 65 | 570 | 2013-07-10 23:00 | 2013-07-11 00:48 | 140 | 330 | 296 | Other reheat steam problems | F590Reheat Spray System - Repair Air Supply Line to #2 Reheat Block Valve | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 1.8 | 1.0364 | 306.7636 | 170.4242 | 170
MC2 | NC | 66 | 310 | 2013-07-21 22:00 | 2013-07-22 03:14 | 0 | 330 | 296 | Pulverizer mills | F5902A,C & D Coal Mills - Adjusted Rollers | Mill Creek | Other | Coal | 2 | 2013 | 7 | 5.2333 | 5.2333 | 1549.0667 | 296 | 296
MC2 | MO | 67 | 8260 | 2013-07-25 08:20 | 2013-07-27 02:32 | 0 | 330 | 296 | Scrubber booster I.D. fan (fan specific to the scrubber) | F320FGD Booster Fans - Wash & Balance | Mill Creek | Maintenance | Coal | 2 | 2013 | 7 | 42.2 | 42.2 | 12491.2 | 296 | 296
MC2 | NC | 68 | 1850 | 2013-07-27 02:32 | 2013-07-27 11:26 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 7 | 8.9 | 8.9 | 2634.4 | 296 | 296
MC2 | D1 | 69 | 310 | 2013-07-28 22:36 | 2013-07-29 | 245 | 330 | 296 | Pulverizer mills | F5302C Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 1.4 | 0.36061 | 106.7394 | 76.2424 | 76
MC2 | D4 | 70 | 310 | 2013-07-29 23:00 | 2013-07-30 02:00 | 240 | 330 | 296 | Pulverizer mills | F5302C Coal Mill - Inspect Journal | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 3 | 0.81818 | 242.1818 | 80.7273 | 81
MC2 | NC | 71 | 9999 | 2013-07-30 09:00 | 2013-07-30 13:08 | 0 | 330 | 296 | Total unit performance testing (use appropriate codes for individual component testing) | F790Full Load Capability Test | Mill Creek | Other | Coal | 2 | 2013 | 7 | 4.1333 | 4.1333 | 1223.4667 | 296 | 296
MC2 | D4 | 72 | 310 | 2013-07-30 22:00 | 2013-07-31 03:09 | 250 | 330 | 296 | Pulverizer mills | F5902C Coal Mill - Cancel Journal Replacement, Crane Issue | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 5.15 | 1.2485 | 369.5515 | 71.7576 | 72
MC2 | D4 | 73 | 310 | 2013-07-31 22:00 | 2013-08-01 02:45 | 250 | 330 | 296 | Pulverizer mills | F5902C Coal Mill - Replace Journal | Mill Creek | Derate | Coal | 2 | 2013 | 7 | 4.75 | 1.1515 | 340.8485 | 71.7576 | 72
MC2 | D4 | 74 | 310 | 2013-08-01 22:00 | 2013-08-02 02:39 | 250 | 330 | 296 | Pulverizer mills | F5302D Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 4.65 | 1.1273 | 333.6727 | 71.7576 | 72
MC2 | D1 | 75 | 30 | 2013-08-15 14:15 | 2013-08-15 17:34 | 230 | 330 | 296 | Coal conveyors and feeders | F430C Coal Conveyor - Wiring Issue | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 3.3167 | 1.0051 | 297.4949 | 89.697 | 90
MC2 | D4 | 76 | 310 | 2013-08-15 20:45 | 2013-08-15 23:55 | 250 | 330 | 296 | Pulverizer mills | F3202C Coal Mill Exhauster - High Differential, Cleaned | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 3.1667 | 0.76768 | 227.2323 | 71.7576 | 72
MC2 | D1 | 77 | 310 | 2013-08-20 00:55 | 2013-08-20 02:20 | 250 | 330 | 296 | Pulverizer mills | F3202D Coal Mill - Clean Out Classifiers | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 1.4167 | 0.34343 | 101.6566 | 71.7576 | 72
MC2 | D4 | 78 | 310 | 2013-08-27 23:00 | 2013-08-28 03:45 | 250 | 330 | 296 | Pulverizer mills | F3202C Coal Mill - Clean Classifiers | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 4.75 | 1.1515 | 340.8485 | 71.7576 | 72
MC2 | D4 | 79 | 310 | 2013-08-28 23:00 | 2013-08-29 03:50 | 250 | 330 | 296 | Pulverizer mills | F5902B Coal Mill - Repair Bowl Differential Reference Line | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 4.8333 | 1.1717 | 346.8283 | 71.7576 | 72
MC2 | D1 | 80 | 870 | 2013-08-30 06:06 | 2013-08-30 06:53 | 235 | 330 | 296 | Soot blowers - steam | F8202C8 Wallblower - 480V Feed Trip | Mill Creek | Derate | Coal | 2 | 2013 | 8 | 0.78333 | 0.22551 | 66.7495 | 85.2121 | 85
MC2 | D1 | 81 | 250 | 2013-09-03 19:16 | 2013-09-03 19:53 | 300 | 330 | 296 | Pulverizer feeders | F1202C Coal Feeder - Removed Foreign Material | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 0.61667 | 0.056061 | 16.5939 | 26.9091 | 27
MC2 | D4 | 82 | 310 | 2013-09-03 22:00 | 2013-09-03 23:39 | 250 | 330 | 296 | Pulverizer mills | F3202C Coal Mill - Clean Classifiers | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 1.65 | 0.4 | 118.4 | 71.7576 | 72
MC2 | D4 | 83 | 310 | 2013-09-04 22:00 | 2013-09-05 00:59 | 250 | 330 | 296 | Pulverizer mills | F3202D Coal Mill - Clean Classifiers | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 2.9833 | 0.72323 | 214.0768 | 71.7576 | 72
MC2 | MO | 84 | 8100 | 2013-09-05 20:50 | 2013-09-09 02:07 | 0 | 330 | 296 | Scrubber/absorber tower or module | F590FGD Module and Duct Leak Repairs | Mill Creek | Maintenance | Coal | 2 | 2013 | 9 | 77.2833 | 77.2833 | 22875.8667 | 296 | 296
MC2 | NC | 85 | 1850 | 2013-09-09 02:07 | 2013-09-09 12:05 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2013 | 9 | 9.9667 | 9.9667 | 2950.1333 | 296 | 296
MC2 | D1 | 86 | 800 | 2013-09-09 12:45 | 2013-09-09 13:40 | 240 | 330 | 296 | Drums and drum internals (single drum only) | F420Drum Level Issue - Operator Error | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 0.91667 | 0.25 | 74 | 80.7273 | 81
MC2 | D1 | 87 | 1000 | 2013-09-09 13:50 | 2013-09-09 15:05 | 150 | 330 | 296 | Waterwall (Furnace wall) A | F540Reduced Boiler Pressure - Boiler Tube Leak Waterwall | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 1.25 | 0.68182 | 201.8182 | 161.4545 | 161
MC2 | U2 | 88 | 1000 | 2013-09-09 15:05 | 2013-09-11 00:31 | 0 | 330 | 296 | Waterwall (Furnace wall) A | F540Boiler Tube Leak - Waterwall | Mill Creek | Outage | Coal | 2 | 2013 | 9 | 33.4333 | 33.4333 | 9896.2667 | 296 | 296
MC2 | NC | 89 | 1850 | 2013-09-11 00:31 | 2013-09-11 06:42 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 9 | 6.1833 | 6.1833 | 1830.2667 | 296 | 296
MC2 | D4 | 90 | 310 | 2013-09-19 23:00 | 2013-09-20 00:20 | 250 | 330 | 296 | Pulverizer mills | F5902C Coal Mill - Inspect & Clean Distributors | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 1.3333 | 0.32323 | 95.6768 | 71.7576 | 72
MC2 | D4 | 91 | 250 | 2013-09-22 22:00 | 2013-09-23 03:23 | 250 | 330 | 296 | Pulverizer feeders | F0902B Coal Feeder - Calibration | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 5.3833 | 1.3051 | 386.2949 | 71.7576 | 72
MC2 | D4 | 92 | 250 | 2013-09-23 22:00 | 2013-09-24 03:08 | 250 | 330 | 296 | Pulverizer feeders | F0902A Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 5.1333 | 1.2444 | 368.3556 | 71.7576 | 72
MC2 | D1 | 93 | 1799 | 2013-09-30 05:12 | 2013-09-30 05:51 | 234 | 330 | 296 | Other boiler instrumentation and control problems | F660Boiler Control - Pressure Swing | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 0.65 | 0.18909 | 55.9709 | 86.1091 | 86
MC2 | D4 | 94 | 310 | 2013-09-30 22:00 | 2013-10-01 04:57 | 250 | 330 | 296 | Pulverizer mills | F5902C Coal Mill - Adjust Rollers | Mill Creek | Derate | Coal | 2 | 2013 | 9 | 6.95 | 1.6848 | 498.7152 | 71.7576 | 72
MC2 | D4 | 95 | 250 | 2013-10-01 23:00 | 2013-10-02 04:05 | 250 | 330 | 296 | Pulverizer feeders | F0902D Coal Feeder - Calibration & Mill Rollers Adjustment | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 5.0833 | 1.2323 | 364.7677 | 71.7576 | 72
MC2 | U1 | 96 | 3110 | 2013-10-04 17:32 | 2013-10-06 00:26 | 0 | 330 | 296 | Condenser tube leaks | F540Condenser Tube Leak | Mill Creek | Outage | Coal | 2 | 2013 | 10 | 30.9 | 30.9 | 9146.4 | 296 | 296
MC2 | NC | 97 | 1850 | 2013-10-06 00:26 | 2013-10-06 12:30 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 10 | 12.0667 | 12.0667 | 3571.7333 | 296 | 296
MC2 | D1 | 98 | 1850 | 2013-10-06 12:30 | 2013-10-06 17:00 | 200 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 4.5 | 1.7727 | 524.7273 | 116.6061 | 117
MC2 | D1 | 99 | 1850 | 2013-10-06 17:00 | 2013-10-07 05:02 | 230 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 12.0333 | 3.6465 | 1079.3535 | 89.697 | 90
MC2 | D1 | 100 | 1850 | 2013-10-07 05:02 | 2013-10-07 07:42 | 213 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 2.6667 | 0.94545 | 279.8545 | 104.9455 | 105
MC2 | D1 | 101 | 1850 | 2013-10-07 07:42 | 2013-10-07 10:10 | 235 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 2.4667 | 0.7101 | 210.1899 | 85.2121 | 85
MC2 | D1 | 102 | 1850 | 2013-10-07 10:10 | 2013-10-08 02:18 | 240 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 16.1333 | 4.4 | 1302.4 | 80.7273 | 81
MC2 | D1 | 103 | 1850 | 2013-10-08 02:18 | 2013-10-08 05:14 | 220 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 2.9333 | 0.97778 | 289.4222 | 98.6667 | 99
MC2 | D1 | 104 | 1850 | 2013-10-08 05:14 | 2013-10-08 06:15 | 230 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 1.0167 | 0.30808 | 91.1919 | 89.697 | 90
MC2 | D1 | 105 | 1850 | 2013-10-08 06:15 | 2013-10-08 07:23 | 250 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 1.1333 | 0.27475 | 81.3253 | 71.7576 | 72
MC2 | D1 | 106 | 1850 | 2013-10-08 07:23 | 2013-10-09 05:15 | 251 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica/Wet Coal Issues | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 21.8667 | 5.2347 | 1549.4853 | 70.8606 | 71
MC2 | D1 | 107 | 1850 | 2013-10-09 05:15 | 2013-10-10 05:00 | 285 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica/Wet Coal Issues | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 23.75 | 3.2386 | 958.6364 | 40.3636 | 40
MC2 | D1 | 108 | 1850 | 2013-10-10 05:00 | 2013-10-10 08:29 | 290 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 3.4833 | 0.42222 | 124.9778 | 35.8788 | 36
MC2 | D1 | 109 | 1850 | 2013-10-10 11:23 | 2013-10-10 12:56 | 301 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 1.55 | 0.13621 | 40.3188 | 26.0121 | 26
MC2 | D1 | 110 | 1850 | 2013-10-10 12:56 | 2013-10-10 13:20 | 275 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 0.4 | 0.066667 | 19.7333 | 49.3333 | 49
MC2 | D1 | 111 | 1850 | 2013-10-10 13:20 | 2013-10-11 03:10 | 270 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 13.8333 | 2.5152 | 744.4848 | 53.8182 | 54
MC2 | D1 | 112 | 1850 | 2013-10-11 03:10 | 2013-10-11 09:57 | 310 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 6.7833 | 0.41111 | 121.6889 | 17.9394 | 18
MC2 | MO | 113 | 1000 | 2013-10-13 10:35 | 2013-10-15 04:57 | 0 | 330 | 296 | Waterwall (Furnace wall) A | F540Boiler Tube Leak - Waterwall | Mill Creek | Maintenance | Coal | 2 | 2013 | 10 | 42.3667 | 42.3667 | 12540.5333 | 296 | 296
MC2 | NC | 114 | 1850 | 2013-10-14 04:57 | 2013-10-15 13:00 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2013 | 10 | 32.05 | 32.05 | 9486.8 | 296 | 296
MC2 | D1 | 115 | 1850 | 2013-10-15 13:00 | 2013-10-15 15:00 | 205 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 2 | 0.75758 | 224.2424 | 112.1212 | 112
MC2 | D1 | 116 | 1850 | 2013-10-15 15:00 | 2013-10-16 03:08 | 300 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 12.1333 | 1.103 | 326.497 | 26.9091 | 27
MC2 | D1 | 117 | 1850 | 2013-10-16 08:40 | 2013-10-16 17:53 | 315 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 9.2167 | 0.41894 | 124.0061 | 13.4545 | 13
MC2 | D1 | 118 | 250 | 2013-10-17 07:40 | 2013-10-17 08:05 | 240 | 330 | 296 | Pulverizer feeders | F1202A Coal Feeder - Rock on Belt | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 0.41667 | 0.11364 | 33.6364 | 80.7273 | 81
MC2 | D1 | 119 | 1850 | 2013-10-17 08:45 | 2013-10-17 22:40 | 300 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 13.9167 | 1.2652 | 374.4848 | 26.9091 | 27
MC2 | D1 | 120 | 1850 | 2013-10-17 22:40 | 2013-10-18 06:56 | 317 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 8.2667 | 0.32566 | 96.3943 | 11.6606 | 12
MC2 | D1 | 121 | 1850 | 2013-10-18 10:35 | 2013-10-18 12:48 | 315 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 2.2167 | 0.10076 | 29.8242 | 13.4545 | 13
MC2 | MO | 122 | 4619 | 2013-10-19 13:47 | 2013-10-22 06:29 | 0 | 330 | 296 | Other hydrogen system problems | F540Generator - Hydrogen Leak Repair | Mill Creek | Maintenance | Coal | 2 | 2013 | 10 | 64.7 | 64.7 | 19151.2 | 296 | 296
MC2 | NC | 123 | 1850 | 2013-10-22 06:29 | 2013-10-22 14:50 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2013 | 10 | 8.35 | 8.35 | 2471.6 | 296 | 296
MC2 | D1 | 124 | 1850 | 2013-10-22 14:50 | 2013-10-22 19:35 | 260 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 4.75 | 1.0076 | 298.2424 | 62.7879 | 63
MC2 | D1 | 125 | 1850 | 2013-10-22 19:35 | 2013-10-23 00:42 | 295 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 5.1167 | 0.54268 | 160.6323 | 31.3939 | 31
MC2 | D1 | 126 | 1850 | 2013-10-23 00:42 | 2013-10-23 06:27 | 320 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 5.75 | 0.17424 | 51.5758 | 8.9697 | 9
MC2 | D1 | 127 | 1850 | 2013-10-23 08:00 | 2013-10-23 17:06 | 270 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 9.1 | 1.6545 | 489.7455 | 53.8182 | 54
MC2 | D1 | 128 | 1850 | 2013-10-23 17:06 | 2013-10-23 21:54 | 300 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 4.8 | 0.43636 | 129.1636 | 26.9091 | 27
MC2 | D1 | 129 | 1850 | 2013-10-23 21:54 | 2013-10-24 03:49 | 315 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 5.9167 | 0.26894 | 79.6061 | 13.4545 | 13
MC2 | D4 | 130 | 310 | 2013-10-24 22:00 | 2013-10-25 01:43 | 250 | 330 | 296 | Pulverizer mills | F5302C Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 3.7167 | 0.90101 | 266.699 | 71.7576 | 72
MC2 | D4 | 131 | 310 | 2013-10-27 20:00 | 2013-10-28 02:55 | 250 | 330 | 296 | Pulverizer mills | F5902C Coal Mill - Replace Roller and Adjust All Rollers | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 6.9167 | 1.6768 | 496.3232 | 71.7576 | 72
MC2 | D1 | 132 | 310 | 2013-10-29 22:06 | 2013-10-29 23:31 | 245 | 330 | 296 | Pulverizer mills | F5902A Coal Mill - Exhauster Damper Linkage Repair | Mill Creek | Derate | Coal | 2 | 2013 | 10 | 1.4167 | 0.3649 | 108.0101 | 76.2424 | 76
MC2 | NC | 133 | 8460 | 2013-11-11 12:00 | 2013-11-11 17:55 | 0 | 330 | 296 | Testing A | F790Full Load RATA Testing | Mill Creek | Other | Coal | 2 | 2013 | 11 | 5.9167 | 5.9167 | 1751.3333 | 296 | 296
MC2 | NC | 134 | 8460 | 2013-11-12 13:55 | 2013-11-12 23:00 | 0 | 330 | 296 | Testing A | F790Full Load RATA Testing | Mill Creek | Other | Coal | 2 | 2013 | 11 | 9.0833 | 9.0833 | 2688.6667 | 296 | 296
MC2 | NC | 135 | 8460 | 2013-11-13 01:00 | 2013-11-13 04:14 | 0 | 330 | 296 | Testing A | F790Mid Load RATA Testing. Full load available if needed. | Mill Creek | Other | Coal | 2 | 2013 | 11 | 3.2333 | 3.2333 | 957.0667 | 296 | 296
MC2 | NC | 136 | 8460 | 2013-11-13 08:05 | 2013-11-13 13:28 | 0 | 330 | 296 | Testing A | F790Full Load RATA Testing | Mill Creek | Other | Coal | 2 | 2013 | 11 | 5.3833 | 5.3833 | 1593.4667 | 296 | 296
MC2 | MO | 137 | 3344 | 2013-11-22 11:10 | 2013-11-24 11:55 | 0 | 330 | 296 | Deaerator (including level control) | F590Deaerator Heater - Repair Shell Steam Leak | Mill Creek | Maintenance | Coal | 2 | 2013 | 11 | 48.75 | 48.75 | 14430 | 296 | 296
MC2 | NC | 138 | 1850 | 2013-11-24 11:55 | 2013-11-24 14:41 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2013 | 11 | 2.7667 | 2.7667 | 818.9333 | 296 | 296
MC2 | U1 | 139 | 400 | 2013-11-24 14:41 | 2013-11-28 00:08 | 0 | 330 | 296 | Burner wind box fires | F070Windbox Fire - C/D #2 Corner | Mill Creek | Outage | Coal | 2 | 2013 | 11 | 81.45 | 81.45 | 24109.2 | 296 | 296
MC2 | NC | 140 | 1850 | 2013-11-28 00:08 | 2013-11-28 08:50 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2013 | 11 | 8.7 | 8.7 | 2575.2 | 296 | 296
MC2 | D1 | 141 | 1850 | 2013-11-28 08:50 | 2013-11-28 15:20 | 148 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 11 | 6.5 | 3.5848 | 1061.1152 | 163.2485 | 163
MC2 | D1 | 142 | 1850 | 2013-11-28 15:20 | 2013-11-30 06:42 | 175 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 11 | 39.3667 | 18.4904 | 5473.1596 | 139.0303 | 139
MC2 | D1 | 143 | 1850 | 2013-11-30 06:42 | 2013-12-01 14:02 | 155 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 11 | 31.3333 | 16.6162 | 4918.3838 | 156.9697 | 157
MC2 | D1 | 144 | 1850 | 2013-12-01 14:02 | 2013-12-02 03:53 | 190 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 13.85 | 5.8758 | 1739.2242 | 125.5758 | 126
MC2 | D1 | 145 | 1850 | 2013-12-02 03:53 | 2013-12-02 09:14 | 213 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 5.35 | 1.8968 | 561.4582 | 104.9455 | 105
MC2 | D1 | 146 | 1850 | 2013-12-02 09:14 | 2013-12-02 23:00 | 175 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 13.7667 | 6.4662 | 1913.9838 | 139.0303 | 139
MC2 | D1 | 147 | 1850 | 2013-12-02 23:00 | 2013-12-03 08:00 | 218 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 9 | 3.0545 | 904.1455 | 100.4606 | 100
MC2 | D1 | 148 | 1850 | 2013-12-03 08:00 | 2013-12-03 12:20 | 245 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 4.3333 | 1.1162 | 330.3838 | 76.2424 | 76
MC2 | D1 | 149 | 1850 | 2013-12-03 12:20 | 2013-12-04 08:25 | 222 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 20.0833 | 6.5727 | 1945.5273 | 96.8727 | 97
MC2 | D1 | 150 | 1850 | 2013-12-04 08:25 | 2013-12-04 10:25 | 233 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 2 | 0.58788 | 174.0121 | 87.0061 | 87
MC2 | D1 | 151 | 1850 | 2013-12-04 10:25 | 2013-12-05 04:37 | 236 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 18.2 | 5.1842 | 1534.5358 | 84.3152 | 84
MC2 | D1 | 152 | 1850 | 2013-12-05 04:37 | 2013-12-06 07:23 | 247 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 26.7667 | 6.7322 | 1992.7378 | 74.4485 | 74
MC2 | D1 | 153 | 1850 | 2013-12-06 07:23 | 2013-12-06 21:05 | 230 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 13.7 | 4.1515 | 1228.8485 | 89.697 | 90
MC2 | D1 | 154 | 1850 | 2013-12-06 21:05 | 2013-12-08 02:25 | 250 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 29.3333 | 7.1111 | 2104.8889 | 71.7576 | 72
MC2 | D1 | 155 | 1850 | 2013-12-08 02:25 | 2013-12-09 03:55 | 240 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 25.5 | 6.9545 | 2058.5455 | 80.7273 | 81
MC2 | D1 | 156 | 1850 | 2013-12-09 03:55 | 2013-12-09 18:11 | 254 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 14.2667 | 3.2857 | 972.5543 | 68.1697 | 68
MC2 | D1 | 157 | 1850 | 2013-12-09 18:11 | 2013-12-10 03:07 | 269 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 8.9333 | 1.6513 | 488.7887 | 54.7152 | 55
MC2 | D4 | 158 | 360 | 2013-12-09 23:00 | 2013-12-09 23:40 | 220 | 330 | 296 | Burners | F5302A Mill - Burners Inspection | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 0.66667 | 0.22222 | 65.7778 | 98.6667 | 99
MC2 | D1 | 159 | 1850 | 2013-12-10 03:07 | 2013-12-10 06:14 | 221 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 3.1167 | 1.0294 | 304.7156 | 97.7697 | 98
MC2 | D1 | 160 | 1850 | 2013-12-10 06:14 | 2013-12-10 16:30 | 256 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 10.2667 | 2.3022 | 681.4578 | 66.3758 | 66
MC2 | D1 | 161 | 1850 | 2013-12-10 16:30 | 2013-12-11 10:56 | 272 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 18.4333 | 3.2398 | 958.9802 | 52.0242 | 52
MC2 | D1 | 162 | 1850 | 2013-12-11 10:56 | 2013-12-11 18:33 | 290 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 7.6167 | 0.92323 | 273.2768 | 35.8788 | 36
MC2 | D1 | 163 | 1850 | 2013-12-11 18:33 | 2013-12-13 00:01 | 270 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 29.4667 | 5.3576 | 1585.8424 | 53.8182 | 54
MC2 | D1 | 164 | 1850 | 2013-12-13 00:01 | 2013-12-13 05:50 | 190 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 5.8167 | 2.4677 | 730.4323 | 125.5758 | 126
MC2 | D1 | 165 | 1850 | 2013-12-13 05:50 | 2013-12-13 12:00 | 260 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 6.1667 | 1.3081 | 387.1919 | 62.7879 | 63
MC2 | D1 | 166 | 1850 | 2013-12-13 12:00 | 2013-12-14 16:12 | 285 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 28.2 | 3.8455 | 1138.2545 | 40.3636 | 40
MC2 | D1 | 167 | 1850 | 2013-12-14 16:12 | 2013-12-16 22:45 | 280 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 54.55 | 8.2652 | 2446.4848 | 44.8485 | 45
MC2 | D1 | 168 | 1850 | 2013-12-16 22:45 | 2013-12-17 02:00 | 310 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 3.25 | 0.19697 | 58.303 | 17.9394 | 18
MC2 | D1 | 169 | 1850 | 2013-12-17 02:00 | 2013-12-18 03:18 | 265 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 25.3 | 4.9833 | 1475.0667 | 58.303 | 58
MC2 | D1 | 170 | 1850 | 2013-12-18 03:18 | 2013-12-19 06:59 | 255 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 27.6833 | 6.2917 | 1862.3333 | 67.2727 | 67
MC2 | D1 | 171 | 1850 | 2013-12-19 06:59 | 2013-12-23 08:12 | 290 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 97.2167 | 11.7838 | 3488.0162 | 35.8788 | 36
MC2 | D1 | 172 | 1850 | 2013-12-23 08:12 | 2013-12-23 13:00 | 235 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 4.8 | 1.3818 | 409.0182 | 85.2121 | 85
MC2 | D1 | 173 | 250 | 2013-12-23 13:00 | 2013-12-23 15:10 | 170 | 330 | 296 | Pulverizer feeders | FW00High Silica and Wet Coal - 2A Coal Mill Feeder | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 2.1667 | 1.0505 | 310.9495 | 143.5152 | 144
MC2 | D1 | 174 | 250 | 2013-12-23 15:10 | 2013-12-23 16:30 | 80 | 330 | 296 | Pulverizer feeders | FW00High Silica and Wet Coal Issues - 2A, 2B and 2C Coal Mill Feeders | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 1.3333 | 1.0101 | 298.9899 | 224.2424 | 224
MC2 | D1 | 175 | 250 | 2013-12-23 16:30 | 2013-12-23 22:22 | 160 | 330 | 296 | Pulverizer feeders | F060High Silica / 2B Coal Mill Feeder Clean Out Conveyor Repairs | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 5.8667 | 3.0222 | 894.5778 | 152.4848 | 152
MC2 | MO | 176 | 1850 | 2013-12-23 22:22 | 2013-12-26 02:10 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170Maintenance Outage - Boiler Chemistry | Mill Creek | Maintenance | Coal | 2 | 2013 | 12 | 51.8 | 51.8 | 15332.8 | 296 | 296
MC2 | D1 | 177 | 1850 | 2013-12-26 10:27 | 2013-12-26 16:00 | 166 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 5.55 | 2.7582 | 816.4218 | 147.103 | 147
MC2 | D1 | 178 | 1850 | 2013-12-26 16:00 | 2013-12-26 18:28 | 220 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 2.4667 | 0.82222 | 243.3778 | 98.6667 | 99
MC2 | D1 | 179 | 1850 | 2013-12-26 18:28 | 2013-12-26 22:35 | 204 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 4.1167 | 1.5718 | 465.2582 | 113.0182 | 113
MC2 | D1 | 180 | 1850 | 2013-12-26 22:35 | 2013-12-27 08:30 | 230 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 9.9167 | 3.0051 | 889.4949 | 89.697 | 90
MC2 | D1 | 181 | 1850 | 2013-12-27 08:30 | 2013-12-28 01:29 | 250 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 16.9833 | 4.1172 | 1218.6828 | 71.7576 | 72
MC2 | D1 | 182 | 1850 | 2013-12-28 01:29 | 2013-12-28 04:04 | 306 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 2.5833 | 0.18788 | 55.6121 | 21.5273 | 22
MC2 | U1 | 183 | 9320 | 2013-12-28 04:04 | 2013-12-28 13:43 | 0 | 330 | 296 | Other miscellaneous external problems | F820Water in UPS Cabinet | Mill Creek | Outage | Coal | 2 | 2013 | 12 | 9.65 | 9.65 | 2856.4 | 296 | 296
MC2 | D1 | 184 | 1850 | 2013-12-28 19:30 | 2013-12-29 03:35 | 165 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 8.0833 | 4.0417 | 1196.3333 | 148 | 148
MC2 | D1 | 185 | 1850 | 2013-12-29 03:35 | 2013-12-30 01:36 | 205 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 22.0167 | 8.3396 | 2468.5354 | 112.1212 | 112
MC2 | D1 | 186 | 1850 | 2013-12-30 01:36 | 2013-12-30 08:30 | 224 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 6.9 | 2.2164 | 656.0436 | 95.0788 | 95
MC2 | D1 | 187 | 1850 | 2013-12-30 08:30 | 2013-12-30 16:13 | 245 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 7.7167 | 1.9876 | 588.3374 | 76.2424 | 76
MC2 | D1 | 188 | 1850 | 2013-12-30 16:13 | 2013-12-30 23:00 | 256 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 6.7833 | 1.5211 | 450.2489 | 66.3758 | 66
MC2 | D1 | 189 | 1850 | 2013-12-30 23:00 | 2013-12-31 08:55 | 276 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 9.9167 | 1.6227 | 480.3273 | 48.4364 | 48
MC2 | D1 | 190 | 1850 | 2013-12-31 08:55 | 2013-12-31 12:19 | 325 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 3.4 | 0.051515 | 15.2485 | 4.4848 | 4
MC2 | D1 | 191 | 1850 | 2013-12-31 12:19 | 2013-12-31 16:20 | 300 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 4.0167 | 0.36515 | 108.0848 | 26.9091 | 27
MC2 | D1 | 192 | 1850 | 2013-12-31 16:20 | 2013-12-31 21:40 | 280 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 5.3333 | 0.80808 | 239.1919 | 44.8485 | 45
MC2 | D1 | 193 | 1850 | 2013-12-31 21:40 | 2013-12-31 22:30 | 325 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 0.83333 | 0.012626 | 3.7374 | 4.4848 | 4
MC2 | D1 | 194 | 250 | 2013-12-31 22:30 | 2014-01-01 | 250 | 330 | 296 | Pulverizer feeders | F5902B Coal Feeder - Replace Belt | Mill Creek | Derate | Coal | 2 | 2013 | 12 | 1.5 | 0.36364 | 107.6364 | 71.7576 | 72
MC2 | D1 | 1 | 250 | 2014-01-01 | 2014-01-01 10:30 | 250 | 330 | 296 | Pulverizer feeders | F5902B Coal Feeder - Replace Belt | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 10.5 | 2.5455 | 753.4545 | 71.7576 | 72
MC2 | D1 | 2 | 1850 | 2014-01-01 10:30 | 2014-01-01 15:30 | 310 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 5 | 0.30303 | 89.697 | 17.9394 | 18
MC2 | D1 | 3 | 250 | 2014-01-02 04:15 | 2014-01-02 05:24 | 250 | 330 | 296 | Pulverizer feeders | F7202B Coal Feeder - Belt Slipping | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 1.15 | 0.27879 | 82.5212 | 71.7576 | 72
MC2 | MO | 4 | 1000 | 2014-01-02 10:39 | 2014-01-04 11:51 | 0 | 330 | 296 | Waterwall (Furnace wall) A | F540Boiler Tube Leak - Waterwall | Mill Creek | Maintenance | Coal | 2 | 2014 | 1 | 49.2 | 49.2 | 14563.2 | 296 | 296
MC2 | NC | 5 | 1850 | 2014-01-04 11:51 | 2014-01-04 21:11 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2014 | 1 | 9.3333 | 9.3333 | 2762.6667 | 296 | 296
MC2 | D1 | 6 | 1850 | 2014-01-04 21:11 | 2014-01-05 05:35 | 205 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 8.4 | 3.1818 | 941.8182 | 112.1212 | 112
MC2 | D1 | 7 | 1850 | 2014-01-05 05:35 | 2014-01-06 01:00 | 260 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 19.4167 | 4.1187 | 1219.1313 | 62.7879 | 63
MC2 | D1 | 8 | 1850 | 2014-01-06 01:00 | 2014-01-06 09:28 | 280 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 8.4667 | 1.2828 | 379.7172 | 44.8485 | 45
MC2 | D1 | 9 | 1850 | 2014-01-06 09:28 | 2014-01-06 19:00 | 320 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 9.5333 | 0.28889 | 85.5111 | 8.9697 | 9
MC2 | D1 | 10 | 1850 | 2014-01-06 19:00 | 2014-01-06 22:36 | 300 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 3.6 | 0.32727 | 96.8727 | 26.9091 | 27
MC2 | D1 | 11 | 250 | 2014-01-07 05:45 | 2014-01-07 07:15 | 240 | 330 | 296 | Pulverizer feeders | FW002A Coal Feeder - Plugged, Frozen/Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 1.5 | 0.40909 | 121.0909 | 80.7273 | 81
MC2 | D1 | 12 | 1850 | 2014-01-07 12:15 | 2014-01-08 09:50 | 280 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 21.5833 | 3.2702 | 967.9798 | 44.8485 | 45
MC2 | D1 | 13 | 1850 | 2014-01-08 09:50 | 2014-01-08 12:15 | 295 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 2.4167 | 0.25631 | 75.8687 | 31.3939 | 31
MC2 | D1 | 14 | 1850 | 2014-01-08 12:15 | 2014-01-09 09:35 | 315 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 21.3333 | 0.9697 | 287.0303 | 13.4545 | 13
MC2 | D4 | 15 | 250 | 2014-01-09 21:02 | 2014-01-10 04:09 | 225 | 330 | 296 | Pulverizer feeders | F0902B Coal Feeder - Calibration | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 7.1167 | 2.2644 | 670.2606 | 94.1818 | 94
MC2 | D4 | 16 | 250 | 2014-01-13 00:35 | 2014-01-13 05:00 | 245 | 330 | 296 | Pulverizer feeders | F0902D Coal Feeder - Calibration | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 4.4167 | 1.1376 | 336.7374 | 76.2424 | 76
MC2 | NC | 17 | 1160 | 2014-01-16 23:00 | 2014-01-17 04:00 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater. Full load available in needed. | Mill Creek | Other | Coal | 2 | 2014 | 1 | 5 | 5 | 1480 | 296 | 296
MC2 | NC | 18 | 1160 | 2014-01-17 22:15 | 2014-01-18 05:00 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater. Full load available if needed. | Mill Creek | Other | Coal | 2 | 2014 | 1 | 6.75 | 6.75 | 1998 | 296 | 296
MC2 | NC | 19 | 1160 | 2014-01-18 21:05 | 2014-01-19 05:00 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater. Full load available if needed. | Mill Creek | Other | Coal | 2 | 2014 | 1 | 7.9167 | 7.9167 | 2343.3333 | 296 | 296
MC2 | D4 | 20 | 310 | 2014-01-19 23:30 | 2014-01-20 04:26 | 245 | 330 | 296 | Pulverizer mills | F5302D Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 4.9333 | 1.2707 | 376.1293 | 76.2424 | 76
MC2 | D1 | 21 | 250 | 2014-01-23 22:08 | 2014-01-23 23:28 | 240 | 330 | 296 | Pulverizer feeders | FW002B Coal Feeder - Plugged, Frozen Coal | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 1.3333 | 0.36364 | 107.6364 | 80.7273 | 81
MC2 | D1 | 22 | 250 | 2014-01-24 05:33 | 2014-01-24 07:30 | 240 | 330 | 296 | Pulverizer feeders | FW002B Coal Feeder - Plugged, Frozen Coal | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 1.95 | 0.53182 | 157.4182 | 80.7273 | 81
MC2 | NC | 23 | 1160 | 2014-01-24 23:00 | 2014-01-25 06:50 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater. Full load available if needed. | Mill Creek | Other | Coal | 2 | 2014 | 1 | 7.8333 | 7.8333 | 2318.6667 | 296 | 296
MC2 | U1 | 24 | 4267 | 2014-01-25 22:11 | 2014-01-26 12:32 | 0 | 330 | 296 | Control valve testing | F820Turbine Control Valve Test - Trip | Mill Creek | Outage | Coal | 2 | 2014 | 1 | 14.35 | 14.35 | 4247.6 | 296 | 296
MC2 | D1 | 27 | 1850 | 2014-01-26 06:15 | 2014-01-27 08:08 | 160 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 25.8833 | 13.3338 | 3946.8162 | 152.4848 | 152
MC2 | D1 | 25 | 310 | 2014-01-26 12:32 | 2014-01-26 18:32 | 240 | 330 | 296 | Pulverizer mills | F4502D Coal Mill - Explosion, Ductwork Repair | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 6 | 1.6364 | 484.3636 | 80.7273 | 81
MC2 | D1 | 26 | 1850 | 2014-01-26 18:32 | 2014-01-27 06:15 | 165 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 11.7167 | 5.8583 | 1734.0667 | 148 | 148
MC2 | D1 | 28 | 1850 | 2014-01-27 08:08 | 2014-01-27 09:55 | 190 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 1.7833 | 0.75657 | 223.9434 | 125.5758 | 126
MC2 | D1 | 29 | 310 | 2014-01-27 09:55 | 2014-01-27 13:56 | 245 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Ductwork Repair | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 4.0167 | 1.0346 | 306.2404 | 76.2424 | 76
MC2 | D1 | 30 | 310 | 2014-01-27 13:56 | 2014-01-27 15:52 | 270 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Ductwork Repair | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 1.9333 | 0.35152 | 104.0485 | 53.8182 | 54
MC2 | D1 | 31 | 310 | 2014-01-27 15:52 | 2014-01-27 16:39 | 240 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Ductwork Repair | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 0.78333 | 0.21364 | 63.2364 | 80.7273 | 81
MC2 | D1 | 32 | 310 | 2014-01-27 16:39 | 2014-01-27 20:39 | 270 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Ductwork Repair | Mill Creek | Derate | Coal | 2 | 2014 | 1 | 4 | 0.72727 | 215.2727 | 53.8182 | 54
MC2 | NC | 33 | 1160 | 2014-01-29 21:00 | 2014-01-30 01:55 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater. Full load available if needed. | Mill Creek | Other | Coal | 2 | 2014 | 1 | 4.9167 | 4.9167 | 1455.3333 | 296 | 296
MC2 | NC | 34 | 1160 | 2014-01-30 22:15 | 2014-01-31 04:00 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 1 | 5.75 | 5.75 | 1702 | 296 | 296
MC2 | U1 | 35 | 3149 | 2014-02-01 23:37 | 2014-02-02 06:35 | 0 | 330 | 296 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F820Condenser Vacuum Trip | Mill Creek | Outage | Coal | 2 | 2014 | 2 | 6.9667 | 6.9667 | 2062.1333 | 296 | 296
MC2 | NC | 36 | 1850 | 2014-02-02 06:35 | 2014-02-02 14:15 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2014 | 2 | 7.6667 | 7.6667 | 2269.3333 | 296 | 296
MC2 | D1 | 37 | 1850 | 2014-02-02 14:15 | 2014-02-02 22:00 | 260 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 7.75 | 1.6439 | 486.6061 | 62.7879 | 63
MC2 | D4 | 38 | 310 | 2014-02-02 22:00 | 2014-02-03 06:25 | 240 | 330 | 296 | Pulverizer mills | F5302A Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 8.4167 | 2.2955 | 679.4545 | 80.7273 | 81
MC2 | D1 | 39 | 1700 | 2014-02-03 08:15 | 2014-02-03 10:23 | 280 | 330 | 296 | Feedwater controls (report local controls --- feedwater pump | F400Feedwater Flow Issue | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 2.1333 | 0.32323 | 95.6768 | 44.8485 | 45
MC2 | D1 | 40 | 1850 | 2014-02-03 10:23 | 2014-02-03 21:05 | 320 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 10.7 | 0.32424 | 95.9758 | 8.9697 | 9
MC2 | D4 | 41 | 310 | 2014-02-03 23:00 | 2014-02-04 04:15 | 240 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Adjust Rollers & Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 5.25 | 1.4318 | 423.8182 | 80.7273 | 81
MC2 | D4 | 42 | 310 | 2014-02-04 23:00 | 2014-02-05 04:45 | 240 | 330 | 296 | Pulverizer mills | F5302B Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 5.75 | 1.5682 | 464.1818 | 80.7273 | 81
MC2 | D1 | 43 | 250 | 2014-02-05 03:53 | 2014-02-05 04:29 | 190 | 330 | 296 | Pulverizer feeders | FW002A Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 0.6 | 0.25455 | 75.3455 | 125.5758 | 126
MC2 | D1 | 44 | 250 | 2014-02-05 05:48 | 2014-02-05 07:56 | 250 | 330 | 296 | Pulverizer feeders | FW002B Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 2.1333 | 0.51717 | 153.0828 | 71.7576 | 72
MC2 | D1 | 45 | 1850 | 2014-02-05 07:56 | 2014-02-05 09:43 | 305 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 1.7833 | 0.1351 | 39.9899 | 22.4242 | 22
MC2 | D1 | 46 | 1850 | 2014-02-05 09:43 | 2014-02-05 13:25 | 314 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 3.7 | 0.17939 | 53.1006 | 14.3515 | 14
MC2 | NC | 47 | 1160 | 2014-02-07 23:00 | 2014-02-08 05:30 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 2 | 6.5 | 6.5 | 1924 | 296 | 296
MC2 | D1 | 48 | 1160 | 2014-02-08 05:30 | 2014-02-08 07:35 | 140 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 2.0833 | 1.1995 | 355.0505 | 170.4242 | 170
MC2 | D1 | 49 | 1160 | 2014-02-08 07:35 | 2014-02-08 09:28 | 240 | 330 | 296 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 1.8833 | 0.51364 | 152.0364 | 80.7273 | 81
MC2 | NC | 50 | 1160 | 2014-02-08 22:00 | 2014-02-09 04:00 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 2 | 6 | 6 | 1776 | 296 | 296
MC2 | NC | 51 | 1160 | 2014-02-09 21:12 | 2014-02-10 03:17 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 2 | 6.0833 | 6.0833 | 1800.6667 | 296 | 296
MC2 | NC | 52 | 8460 | 2014-02-11 08:00 | 2014-02-11 12:20 | 0 | 330 | 296 | Testing A | F790Particulate Matter Testing - Full Load | Mill Creek | Other | Coal | 2 | 2014 | 2 | 4.3333 | 4.3333 | 1282.6667 | 296 | 296
MC2 | NC | 53 | 1160 | 2014-02-11 12:21 | 2014-02-11 16:30 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 2 | 4.15 | 4.15 | 1228.4 | 296 | 296
MC2 | NC | 54 | 1160 | 2014-02-12 22:00 | 2014-02-13 04:50 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 2 | 6.8333 | 6.8333 | 2022.6667 | 296 | 296
MC2 | NC | 55 | 8460 | 2014-02-13 08:00 | 2014-02-13 13:11 | 0 | 330 | 296 | Testing A | F790Particulate Matter Testing - Full Load | Mill Creek | Other | Coal | 2 | 2014 | 2 | 5.1833 | 5.1833 | 1534.2667 | 296 | 296
MC2 | D1 | 56 | 1160 | 2014-02-14 11:25 | 2014-02-15 00:32 | 275 | 330 | 296 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 13.1167 | 2.1861 | 647.0889 | 49.3333 | 49
MC2 | MO | 57 | 1050 | 2014-02-15 00:32 | 2014-02-17 22:00 | 0 | 330 | 296 | Second superheater B | F540Boiler Tube Leak - Second Superheater | Mill Creek | Maintenance | Coal | 2 | 2014 | 2 | 69.4667 | 69.4667 | 20562.1333 | 296 | 296
MC2 | SF | 58 | 380 | 2014-02-17 22:00 | 2014-02-18 13:40 | 0 | 330 | 296 | Light-off (igniter) systems (including fuel supply) | F400Gas Igniter Issues | Mill Creek | Outage | Coal | 2 | 2014 | 2 | 15.6667 | 15.6667 | 4637.3333 | 296 | 296
MC2 | NC | 59 | 1850 | 2014-02-18 13:40 | 2014-02-18 22:15 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2014 | 2 | 8.5833 | 8.5833 | 2540.6667 | 296 | 296
MC2 | D1 | 60 | 1850 | 2014-02-18 22:15 | 2014-02-19 02:00 | 240 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 3.75 | 1.0227 | 302.7273 | 80.7273 | 81
MC2 | D1 | 61 | 1850 | 2014-02-19 02:00 | 2014-02-19 04:15 | 270 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 2.25 | 0.40909 | 121.0909 | 53.8182 | 54
MC2 | D1 | 62 | 1850 | 2014-02-19 04:15 | 2014-02-19 07:00 | 285 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 2.75 | 0.375 | 111 | 40.3636 | 40
MC2 | D1 | 63 | 1850 | 2014-02-19 07:00 | 2014-02-19 08:50 | 306 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 1.8333 | 0.13333 | 39.4667 | 21.5273 | 22
MC2 | D1 | 64 | 1850 | 2014-02-19 08:50 | 2014-02-19 21:41 | 320 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 12.85 | 0.38939 | 115.2606 | 8.9697 | 9
MC2 | D1 | 65 | 1850 | 2014-02-20 02:40 | 2014-02-20 08:09 | 321 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 5.4833 | 0.14955 | 44.2655 | 8.0727 | 8
MC2 | D1 | 66 | 250 | 2014-02-24 00:16 | 2014-02-24 03:46 | 315 | 330 | 296 | Pulverizer feeders | F1202B Coal Feeder - Plugged, Foreign Material | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 3.5 | 0.15909 | 47.0909 | 13.4545 | 13
MC2 | MO | 67 | 1000 | 2014-02-24 09:31 | 2014-02-25 19:47 | 0 | 330 | 296 | Waterwall (Furnace wall) A | F540Boiler Tube Leak - Waterwall | Mill Creek | Maintenance | Coal | 2 | 2014 | 2 | 34.2667 | 34.2667 | 10142.9333 | 296 | 296
MC2 | NC | 68 | 1850 | 2014-02-25 19:47 | 2014-02-26 05:39 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2014 | 2 | 9.8667 | 9.8667 | 2920.5333 | 296 | 296
MC2 | D1 | 69 | 1850 | 2014-02-26 05:39 | 2014-02-26 11:21 | 321 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 5.7 | 0.15545 | 46.0145 | 8.0727 | 8
MC2 | D1 | 70 | 1850 | 2014-02-26 11:21 | 2014-02-26 15:29 | 293 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 4.1333 | 0.46343 | 137.1766 | 33.1879 | 33
MC2 | D1 | 71 | 1850 | 2014-02-26 15:29 | 2014-02-26 16:46 | 321 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 2 | 1.2833 | 0.035 | 10.36 | 8.0727 | 8
MC2 | NC | 72 | 1160 | 2014-03-04 23:30 | 2014-03-05 04:30 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2014 | 3 | 5 | 5 | 1480 | 296 | 296
MC2 | NC | 73 | 4490 | 2014-03-05 06:00 | 2014-03-05 12:05 | 0 | 330 | 296 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Capability Test - Full Load | Mill Creek | Other | Coal | 2 | 2014 | 3 | 6.0833 | 6.0833 | 1800.6667 | 296 | 296
MC2 | NC | 74 | 1160 | 2014-03-06 00:30 | 2014-03-06 01:00 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2014 | 3 | 0.5 | 0.5 | 148 | 296 | 296
MC2 | NC | 75 | 1160 | 2014-03-06 22:45 | 2014-03-07 03:20 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2014 | 3 | 4.5833 | 4.5833 | 1356.6667 | 296 | 296
MC2 | D1 | 76 | 1455 | 2014-03-07 05:45 | 2014-03-07 07:23 | 312 | 330 | 296 | Induced draft fans | F4002B Induced Draft Fan - Run Back | Mill Creek | Derate | Coal | 2 | 2014 | 3 | 1.6333 | 0.089091 | 26.3709 | 16.1455 | 16
MC2 | D1 | 77 | 1455 | 2014-03-07 07:23 | 2014-03-07 11:52 | 323 | 330 | 296 | Induced draft fans | F4002B Induced Draft Fan - Run Back | Mill Creek | Derate | Coal | 2 | 2014 | 3 | 4.4833 | 0.095101 | 28.1499 | 6.2788 | 6
MC2 | NC | 78 | 1160 | 2014-03-07 13:45 | 2014-03-07 17:40 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2014 | 3 | 3.9167 | 3.9167 | 1159.3333 | 296 | 296
MC2 | NC | 79 | 1160 | 2014-03-15 23:00 | 2014-03-16 04:47 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 3 | 5.7833 | 5.7833 | 1711.8667 | 296 | 296
MC2 | NC | 80 | 1160 | 2014-03-16 22:30 | 2014-03-17 03:45 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 3 | 5.25 | 5.25 | 1554 | 296 | 296
MC2 | D4 | 81 | 310 | 2014-03-24 23:00 | 2014-03-25 02:09 | 240 | 330 | 296 | Pulverizer mills | F5902C Coal Mill - Bowl Differential Reference Line Repair | Mill Creek | Derate | Coal | 2 | 2014 | 3 | 3.15 | 0.85909 | 254.2909 | 80.7273 | 81
MC2 | NC | 82 | 1160 | 2014-03-25 22:45 | 2014-03-26 03:30 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 3 | 4.75 | 4.75 | 1406 | 296 | 296
MC2 | NC | 83 | 1160 | 2014-03-30 22:35 | 2014-03-31 03:04 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 3 | 4.4833 | 4.4833 | 1327.0667 | 296 | 296
MC2 | D4 | 84 | 1160 | 2014-03-31 22:00 | 2014-04-01 03:34 | 140 | 330 | 296 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Derate | Coal | 2 | 2014 | 3 | 5.5667 | 3.2051 | 948.6949 | 170.4242 | 170
MC2 | D4 | 85 | 1160 | 2014-04-01 23:55 | 2014-04-02 03:10 | 140 | 330 | 296 | First reheater B | F320Boiler Deslag - First ReheaterFull Load available as Needed | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 3.25 | 1.8712 | 553.8788 | 170.4242 | 170
MC2 | D1 | 86 | 1160 | 2014-04-03 00:05 | 2014-04-03 03:45 | 140 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 4 | 3.6667 | 2.1111 | 624.8889 | 170.4242 | 170
MC2 | PO | 87 | 1800 | 2014-04-05 01:51 | 2014-05-04 22:22 | 0 | 330 | 296 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | F590Planned 4 Week Outage | Mill Creek | Other | Coal | 2 | 2014 | 4 | 716.5167 | 716.5167 | 212088.9333 | 296 | 296
MC2 | D4 | 88 | 345 | 2014-05-04 22:22 | 2014-05-06 03:39 | 240 | 330 | 296 | Pulverizer overhaul | F5902A Coal Mill - Overhaul | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 29.2833 | 7.9864 | 2363.9636 | 80.7273 | 81
MC2 | D4 | 89 | 345 | 2014-05-06 03:39 | 2014-05-07 07:59 | 257 | 330 | 296 | Pulverizer overhaul | F5902A Coal Mill - Overhaul | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 28.3333 | 6.2677 | 1855.2323 | 65.4788 | 65
MC2 | D4 | 90 | 350 | 2014-05-06 23:00 | 2014-05-07 04:09 | 145 | 330 | 296 | Pulverized fuel and air piping (from pulverizer to wind box) | F1202D Coal Mill - D2 Coal Conduit Plugged | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 5.15 | 2.8871 | 854.5879 | 165.9394 | 166
MC2 | D4 | 91 | 345 | 2014-05-07 07:59 | 2014-05-07 17:55 | 268 | 330 | 296 | Pulverizer overhaul | F5902A Coal Mill - Overhaul | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 9.9333 | 1.8663 | 552.4137 | 55.6121 | 56
MC2 | D4 | 92 | 310 | 2014-05-07 22:00 | 2014-05-08 01:20 | 250 | 330 | 296 | Pulverizer mills | F790Coal Mill Air Flow Testing | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 3.3333 | 0.80808 | 239.1919 | 71.7576 | 72
MC2 | D4 | 93 | 310 | 2014-05-08 22:00 | 2014-05-09 02:10 | 240 | 330 | 296 | Pulverizer mills | F5902A Coal Mill - Classifier Adjustment | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 4.1667 | 1.1364 | 336.3636 | 80.7273 | 81
MC2 | D4 | 94 | 310 | 2014-05-14 21:27 | 2014-05-15 04:55 | 240 | 330 | 296 | Pulverizer mills | F5902B Coal Mill - Adjusted Riffles | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 7.4667 | 2.0364 | 602.7636 | 80.7273 | 81
MC2 | D4 | 95 | 310 | 2014-05-15 21:51 | 2014-05-16 01:41 | 240 | 330 | 296 | Pulverizer mills | F5902B Coal Mill - Adjusted Riffles | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 3.8333 | 1.0455 | 309.4545 | 80.7273 | 81
MC2 | D1 | 96 | 3133 | 2014-05-15 22:35 | 2014-05-16 01:27 | 141 | 330 | 296 | Vacuum pumps | F8202B Condenser Vacuum Pump - Trip due to Motor Control Center (MCC) Leads to Breaker | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 2.8667 | 1.6418 | 485.9782 | 169.5273 | 170
MC2 | D1 | 97 | 3133 | 2014-05-16 01:41 | 2014-05-16 07:17 | 141 | 330 | 296 | Vacuum pumps | F8202B Condenser Vacuum Pump - Trip Due to Motor Control Center (MCC) Leads to Breaker | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 5.6 | 3.2073 | 949.3527 | 169.5273 | 170
MC2 | D1 | 98 | 3414 | 2014-05-16 10:24 | 2014-05-16 11:06 | 300 | 330 | 296 | Feedwater pump local controls | F400Feedwater Master Issue | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 0.7 | 0.063636 | 18.8364 | 26.9091 | 27
MC2 | D4 | 99 | 310 | 2014-05-18 22:21 | 2014-05-19 04:22 | 240 | 330 | 296 | Pulverizer mills | F5902B Coal Mill - Adjusted Riffles | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 6.0167 | 1.6409 | 485.7091 | 80.7273 | 81
MC2 | D4 | 100 | 310 | 2014-05-19 22:00 | 2014-05-20 03:44 | 240 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Adjusted Riffles | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 5.7333 | 1.5636 | 462.8364 | 80.7273 | 81
MC2 | D4 | 101 | 310 | 2014-05-20 22:00 | 2014-05-21 04:07 | 240 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Adjusted Riffles | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 6.1167 | 1.6682 | 493.7818 | 80.7273 | 81
MC2 | D4 | 102 | 310 | 2014-05-21 22:00 | 2014-05-22 00:42 | 240 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Adjusted Riffles | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 2.7 | 0.73636 | 217.9636 | 80.7273 | 81
MC2 | D4 | 103 | 310 | 2014-05-22 22:00 | 2014-05-23 02:23 | 240 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Adjusted Riffles | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 4.3833 | 1.1955 | 353.8545 | 80.7273 | 81
MC2 | D4 | 104 | 310 | 2014-05-26 22:00 | 2014-05-27 03:22 | 240 | 330 | 296 | Pulverizer mills | F5902B Coal Mill - Adjusted Riffles | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 5.3667 | 1.4636 | 433.2364 | 80.7273 | 81
MC2 | D4 | 105 | 310 | 2014-05-27 23:00 | 2014-05-28 02:37 | 240 | 330 | 296 | Pulverizer mills | F5902B Coal Mill - Adjusted Riffles | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 3.6167 | 0.98636 | 291.9636 | 80.7273 | 81
MC2 | D4 | 106 | 310 | 2014-05-28 22:00 | 2014-05-29 05:00 | 240 | 330 | 296 | Pulverizer mills | F5902A Coal Mill - Adjusted Riffles | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 7 | 1.9091 | 565.0909 | 80.7273 | 81
MC2 | D1 | 107 | 310 | 2014-05-29 05:00 | 2014-05-29 05:40 | 240 | 330 | 296 | Pulverizer mills | F5902A Coal Mill - Roller Adjustment & Air Flow Test | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 0.66667 | 0.18182 | 53.8182 | 80.7273 | 81
MC2 | D4 | 108 | 310 | 2014-05-29 23:00 | 2014-05-30 03:16 | 240 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Adjusted Riffles | Mill Creek | Derate | Coal | 2 | 2014 | 5 | 4.2667 | 1.1636 | 344.4364 | 80.7273 | 81
MC2 | D4 | 109 | 3410 | 2014-06-01 22:00 | 2014-06-02 03:55 | 185 | 330 | 296 | Feedwater pump | F5902B Boiler Feed Pump - Injection Water Line Leak Repair | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 5.9167 | 2.5997 | 769.5253 | 130.0606 | 130
MC2 | NC | 110 | 4842 | 2014-06-03 09:00 | 2014-06-03 10:45 | 0 | 330 | 296 | Reactive and capability testing | F790Generator Reactive Power Capability Test | Mill Creek | Other | Coal | 2 | 2014 | 6 | 1.75 | 1.75 | 518 | 296 | 296
MC2 | D4 | 111 | 310 | 2014-06-03 21:10 | 2014-06-04 03:56 | 240 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Adjusted Riffles | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 6.7667 | 1.8455 | 546.2545 | 80.7273 | 81
MC2 | D4 | 112 | 310 | 2014-06-04 20:30 | 2014-06-05 03:37 | 240 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Adjusted Riffles | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 7.1167 | 1.9409 | 574.5091 | 80.7273 | 81
MC2 | D4 | 113 | 310 | 2014-06-10 22:00 | 2014-06-11 05:00 | 240 | 330 | 296 | Pulverizer mills | F5902C Coal Mill - Replace North Roller Door Assembly | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 7 | 1.9091 | 565.0909 | 80.7273 | 81
MC2 | D1 | 114 | 8280 | 2014-06-19 03:40 | 2014-06-19 05:05 | 125 | 330 | 296 | Reagent feed piping | F540FGD "A" Reactant Feed Supply Line - Leak | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 1.4167 | 0.88005 | 260.4949 | 183.8788 | 184
MC2 | D4 | 115 | 310 | 2014-06-19 23:00 | 2014-06-20 06:02 | 240 | 330 | 296 | Pulverizer mills | F0402C Coal Mill - Balance Exhauster | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 7.0333 | 1.9182 | 567.7818 | 80.7273 | 81
MC2 | D1 | 116 | 360 | 2014-06-22 15:37 | 2014-06-22 17:15 | 295 | 330 | 296 | Burners | F5402B3 Burner - Coal Leak | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 1.6333 | 0.17323 | 51.2768 | 31.3939 | 31
MC2 | D4 | 117 | 310 | 2014-06-26 22:24 | 2014-06-27 03:27 | 235 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Adjust Rollers | Mill Creek | Derate | Coal | 2 | 2014 | 6 | 5.05 | 1.4538 | 430.3212 | 85.2121 | 85
MC2 | NC | 118 | 1990 | 2014-07-02 11:45 | 2014-07-02 12:20 | 0 | 330 | 296 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Capability Test - Max Fire/Max Load | Mill Creek | Other | Coal | 2 | 2014 | 7 | 0.58333 | 0.58333 | 172.6667 | 296 | 296
MC2 | NC | 119 | 1990 | 2014-07-10 22:00 | 2014-07-11 01:18 | 0 | 330 | 296 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Boiler Tuning. Full load if load dispatch needed it. | Mill Creek | Other | Coal | 2 | 2014 | 7 | 3.3 | 3.3 | 976.8 | 296 | 296
MC2 | NC | 120 | 1990 | 2014-07-14 23:00 | 2014-07-15 01:45 | 0 | 330 | 296 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Boiler Tuning. Full load if load dispatch needed it. | Mill Creek | Other | Coal | 2 | 2014 | 7 | 2.75 | 2.75 | 814 | 296 | 296
MC2 | MO | 121 | 3344 | 2014-07-15 08:48 | 2014-07-17 01:49 | 0 | 330 | 296 | Deaerator (including level control) | F540Deaerator Heater Leak | Mill Creek | Maintenance | Coal | 2 | 2014 | 7 | 41.0167 | 41.0167 | 12140.9333 | 296 | 296
MC2 | NC | 122 | 1990 | 2014-07-17 02:50 | 2014-07-17 05:04 | 0 | 330 | 296 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Combustion Testing | Mill Creek | Other | Coal | 2 | 2014 | 7 | 2.2333 | 2.2333 | 661.0667 | 296 | 296
MC2 | D1 | 123 | 1850 | 2014-07-17 09:49 | 2014-07-17 15:43 | 240 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 7 | 5.9 | 1.6091 | 476.2909 | 80.7273 | 81
MC2 | D1 | 124 | 1850 | 2014-07-17 15:43 | 2014-07-17 17:00 | 300 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 7 | 1.2833 | 0.11667 | 34.5333 | 26.9091 | 27
MC2 | D1 | 125 | 1850 | 2014-07-17 17:00 | 2014-07-17 21:00 | 315 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 7 | 4 | 0.18182 | 53.8182 | 13.4545 | 13
MC2 | MO | 126 | 3344 | 2014-07-28 00:06 | 2014-07-29 00:43 | 0 | 330 | 296 | Deaerator (including level control) | F540Deaerator Heater - Leak Repair | Mill Creek | Maintenance | Coal | 2 | 2014 | 7 | 24.6167 | 24.6167 | 7286.5333 | 296 | 296
MC2 | NC | 127 | 1850 | 2014-07-29 00:43 | 2014-07-29 06:23 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2014 | 7 | 5.6667 | 5.6667 | 1677.3333 | 296 | 296
MC2 | D1 | 128 | 3410 | 2014-07-29 22:40 | 2014-07-30 09:50 | 190 | 330 | 296 | Feedwater pump | F5902A Boiler Feed Pump - Flow Transmitter Issue | Mill Creek | Derate | Coal | 2 | 2014 | 7 | 11.1667 | 4.7374 | 1402.2626 | 125.5758 | 126
MC2 | D1 | 129 | 3620 | 2014-07-31 10:08 | 2014-07-31 11:34 | 120 | 330 | 296 | Main transformer | F5402B Main Transformer - Oil Leak | Mill Creek | Derate | Coal | 2 | 2014 | 7 | 1.4333 | 0.91212 | 269.9879 | 188.3636 | 188
MC2 | D1 | 130 | 3620 | 2014-07-31 11:34 | 2014-07-31 12:48 | 230 | 330 | 296 | Main transformer | F5402B Main Transformer - Oil Leak | Mill Creek | Derate | Coal | 2 | 2014 | 7 | 1.2333 | 0.37374 | 110.6263 | 89.697 | 90
MC2 | MO | 131 | 3620 | 2014-08-01 23:15 | 2014-08-02 07:31 | 0 | 330 | 296 | Main transformer | F5902B Main Transformer - Replace Oil Pump | Mill Creek | Maintenance | Coal | 2 | 2014 | 8 | 8.2667 | 8.2667 | 2446.9333 | 296 | 296
MC2 | NC | 132 | 1850 | 2014-08-02 07:31 | 2014-08-02 15:15 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2014 | 8 | 7.7333 | 7.7333 | 2289.0667 | 296 | 296
MC2 | NC | 133 | 4490 | 2014-08-13 08:15 | 2014-08-13 13:03 | 0 | 330 | 296 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Full Load Capability Test | Mill Creek | Other | Coal | 2 | 2014 | 8 | 4.8 | 4.8 | 1420.8 | 296 | 296
MC2 | D1 | 134 | 310 | 2014-08-15 05:57 | 2014-08-15 08:00 | 100 | 330 | 296 | Pulverizer mills | F4402D Coal Mill - Puff, Lost C & D Coal Feeders | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 2.05 | 1.4288 | 422.9212 | 206.303 | 206
MC2 | D1 | 135 | 310 | 2014-08-15 08:00 | 2014-08-15 18:30 | 260 | 330 | 296 | Pulverizer mills | F4402D Coal Mill - Puff, Repairs | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 10.5 | 2.2273 | 659.2727 | 62.7879 | 63
MC2 | D1 | 136 | 310 | 2014-08-16 12:23 | 2014-08-17 10:08 | 265 | 330 | 296 | Pulverizer mills | F5402A Coal Mill - Discharge Conduit Leak Repair | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 21.75 | 4.2841 | 1268.0909 | 58.303 | 58
MC2 | D4 | 137 | 310 | 2014-08-20 23:00 | 2014-08-21 00:57 | 240 | 330 | 296 | Pulverizer mills | F5902B Coal Mill - Repaired Cooling Water Line | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 1.95 | 0.53182 | 157.4182 | 80.7273 | 81
MC2 | D4 | 138 | 310 | 2014-08-24 22:00 | 2014-08-24 23:00 | 240 | 330 | 296 | Pulverizer mills | F5902B Coal Mill Exhauster - Flushed Oil | Mill Creek | Derate | Coal | 2 | 2014 | 8 | 1 | 0.27273 | 80.7273 | 80.7273 | 81
MC2 | NC | 139 | 1160 | 2014-08-24 23:00 | 2014-08-25 03:09 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater, Full Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 8 | 4.15 | 4.15 | 1228.4 | 296 | 296
MC2 | NC | 140 | 1160 | 2014-08-28 21:43 | 2014-08-29 00:54 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater, Full Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 8 | 3.1833 | 3.1833 | 942.2667 | 296 | 296
MC2 | D1 | 141 | 310 | 2014-09-03 23:18 | 2014-09-04 00:09 | 240 | 330 | 296 | Pulverizer mills | F5902C Coal Mill - Exhauster Bearing Oil Change | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 0.85 | 0.23182 | 68.6182 | 80.7273 | 81
MC2 | MO | 142 | 3612 | 2014-09-06 00:02 | 2014-09-08 01:30 | 0 | 330 | 296 | Switchyard system protection devices - external | F590MC 4532 - Relay Work | Mill Creek | Maintenance | Coal | 2 | 2014 | 9 | 49.4667 | 49.4667 | 14642.1333 | 296 | 296
MC2 | NC | 143 | 1850 | 2014-09-08 01:30 | 2014-09-08 09:30 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2014 | 9 | 8 | 8 | 2368 | 296 | 296
MC2 | D1 | 144 | 1850 | 2014-09-08 09:30 | 2014-09-08 13:08 | 250 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 3.6333 | 0.88081 | 260.7192 | 71.7576 | 72
MC2 | D1 | 145 | 1850 | 2014-09-08 13:08 | 2014-09-08 17:42 | 284 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 4.5667 | 0.63657 | 188.4234 | 41.2606 | 41
MC2 | D4 | 146 | 310 | 2014-09-08 22:00 | 2014-09-09 02:45 | 240 | 330 | 296 | Pulverizer mills | F5902D Coal Mill - Exhauster Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 4.75 | 1.2955 | 383.4545 | 80.7273 | 81
MC2 | NC | 147 | 8460 | 2014-09-09 08:00 | 2014-09-09 16:38 | 0 | 330 | 296 | Testing A | F790RATA Test - Full Load | Mill Creek | Other | Coal | 2 | 2014 | 9 | 8.6333 | 8.6333 | 2555.4667 | 296 | 296
MC2 | NC | 148 | 8460 | 2014-09-09 22:00 | 2014-09-10 00:50 | 0 | 330 | 296 | Testing A | F790RATA Test - Mid Load @ 220 MW | Mill Creek | Other | Coal | 2 | 2014 | 9 | 2.8333 | 2.8333 | 838.6667 | 296 | 296
MC2 | NC | 149 | 8460 | 2014-09-10 08:00 | 2014-09-10 11:25 | 0 | 330 | 296 | Testing A | F790RATA Test - Full Load | Mill Creek | Other | Coal | 2 | 2014 | 9 | 3.4167 | 3.4167 | 1011.3333 | 296 | 296
MC2 | D4 | 150 | 3611 | 2014-09-12 23:00 | 2014-09-13 00:14 | 200 | 330 | 296 | Switchyard circuit breakers - external | F590MC 4502 Breaker Maintenance - Closed In | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 1.2333 | 0.48586 | 143.8141 | 116.6061 | 117
MC2 | D4 | 151 | 3410 | 2014-09-17 21:15 | 2014-09-18 03:36 | 190 | 330 | 296 | Feedwater pump | F5902B Boiler Feed Pump - Replace Lube Oil Filter | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 6.35 | 2.6939 | 797.4061 | 125.5758 | 126
MC2 | D4 | 152 | 250 | 2014-09-18 03:36 | 2014-09-18 05:37 | 240 | 330 | 296 | Pulverizer feeders | F0902A Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 2.0167 | 0.55 | 162.8 | 80.7273 | 81
MC2 | D4 | 153 | 310 | 2014-09-18 22:00 | 2014-09-19 05:27 | 240 | 330 | 296 | Pulverizer mills | F5302B Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 7.45 | 2.0318 | 601.4182 | 80.7273 | 81
MC2 | D1 | 154 | 310 | 2014-09-19 08:28 | 2014-09-19 11:37 | 250 | 330 | 296 | Pulverizer mills | F5302B Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 3.15 | 0.76364 | 226.0364 | 71.7576 | 72
MC2 | D4 | 155 | 250 | 2014-09-21 22:00 | 2014-09-22 03:13 | 250 | 330 | 296 | Pulverizer feeders | F0902C Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 5.2167 | 1.2646 | 374.3354 | 71.7576 | 72
MC2 | D4 | 156 | 250 | 2014-09-22 23:00 | 2014-09-23 05:33 | 250 | 330 | 296 | Pulverizer feeders | F0902D Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 6.55 | 1.5879 | 470.0121 | 71.7576 | 72
MC2 | D1 | 157 | 310 | 2014-09-23 02:58 | 2014-09-23 04:14 | 160 | 330 | 296 | Pulverizer mills | F5902B Coal Mill - Replaced Scraper | Mill Creek | Derate | Coal | 2 | 2014 | 9 | 1.2667 | 0.65253 | 193.1475 | 152.4848 | 152
MC2 | NC | 158 | 1160 | 2014-10-05 22:30 | 2014-10-06 03:15 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater, Full Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 10 | 4.75 | 4.75 | 1406 | 296 | 296
MC2 | NC | 159 | 1160 | 2014-11-03 23:00 | 2014-11-04 02:30 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater, Full Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 11 | 3.5 | 3.5 | 1036 | 296 | 296
MC2 | D1 | 160 | 250 | 2014-11-04 16:54 | 2014-11-04 19:37 | 240 | 330 | 296 | Pulverizer feeders | F1202D Coal Feeder - Chute Plugged with Rock | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 2.7167 | 0.74091 | 219.3091 | 80.7273 | 81
MC2 | D1 | 161 | 1160 | 2014-11-19 07:21 | 2014-11-19 12:32 | 270 | 330 | 296 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 5.1833 | 0.94242 | 278.9576 | 53.8182 | 54
MC2 | D1 | 162 | 1160 | 2014-11-19 12:32 | 2014-11-19 22:00 | 240 | 330 | 296 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 9.4667 | 2.5818 | 764.2182 | 80.7273 | 81
MC2 | D4 | 163 | 1160 | 2014-11-19 22:00 | 2014-11-20 02:40 | 140 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 4.6667 | 2.6869 | 795.3131 | 170.4242 | 170
MC2 | NC | 164 | 1160 | 2014-11-20 12:00 | 2014-11-20 16:45 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 2 | 2014 | 11 | 4.75 | 4.75 | 1406 | 296 | 296
MC2 | D1 | 165 | 1160 | 2014-11-20 16:45 | 2014-11-20 18:33 | 264 | 330 | 296 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 1.8 | 0.36 | 106.56 | 59.2 | 59
MC2 | D1 | 166 | 300 | 2014-11-20 19:15 | 2014-11-20 20:44 | 264 | 330 | 296 | Pulverizer motors and drives | F5902A Coal Mill Motor - Replace Breaker | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 1.4833 | 0.29667 | 87.8133 | 59.2 | 59
MC2 | D4 | 167 | 1160 | 2014-11-21 23:00 | 2014-11-22 05:10 | 150 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 6.1667 | 3.3636 | 995.6364 | 161.4545 | 161
MC2 | D1 | 168 | 1160 | 2014-11-25 03:18 | 2014-11-25 05:18 | 200 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 2 | 0.78788 | 233.2121 | 116.6061 | 117
MC2 | D1 | 169 | 1160 | 2014-11-25 19:20 | 2014-11-25 23:00 | 300 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 3.6667 | 0.33333 | 98.6667 | 26.9091 | 27
MC2 | D4 | 170 | 1160 | 2014-11-25 23:00 | 2014-11-26 04:20 | 150 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 5.3333 | 2.9091 | 861.0909 | 161.4545 | 161
MC2 | NC | 171 | 1160 | 2014-11-26 23:00 | 2014-11-27 04:30 | 0 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater, Full Load Available as Needed | Mill Creek | Other | Coal | 2 | 2014 | 11 | 5.5 | 5.5 | 1628 | 296 | 296
MC2 | D1 | 172 | 1160 | 2014-11-27 10:10 | 2014-11-27 12:00 | 275 | 330 | 296 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 1.8333 | 0.30556 | 90.4444 | 49.3333 | 49
MC2 | D1 | 173 | 1160 | 2014-11-27 12:00 | 2014-11-27 15:30 | 240 | 330 | 296 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 3.5 | 0.95455 | 282.5455 | 80.7273 | 81
MC2 | D1 | 174 | 1160 | 2014-11-27 15:30 | 2014-11-27 20:55 | 200 | 330 | 296 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 5.4167 | 2.1338 | 631.6162 | 116.6061 | 117
MC2 | D1 | 175 | 1160 | 2014-11-27 20:55 | 2014-11-27 23:00 | 180 | 330 | 296 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 2.0833 | 0.94697 | 280.303 | 134.5455 | 135
MC2 | D1 | 176 | 1160 | 2014-11-27 23:00 | 2014-11-28 05:28 | 150 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 6.4667 | 3.5273 | 1044.0727 | 161.4545 | 161
MC2 | D1 | 177 | 1160 | 2014-11-28 16:45 | 2014-11-28 19:50 | 275 | 330 | 296 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 3.0833 | 0.51389 | 152.1111 | 49.3333 | 49
MC2 | D1 | 178 | 1160 | 2014-11-28 19:50 | 2014-11-28 23:00 | 245 | 330 | 296 | First reheater B | F320Boiler Slag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 3.1667 | 0.81566 | 241.4343 | 76.2424 | 76
MC2 | D1 | 179 | 1160 | 2014-11-28 23:00 | 2014-11-29 03:12 | 150 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 4.2 | 2.2909 | 678.1091 | 161.4545 | 161
MC2 | D1 | 180 | 1160 | 2014-11-29 21:00 | 2014-11-30 02:55 | 150 | 330 | 296 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 5.9167 | 3.2273 | 955.2727 | 161.4545 | 161
MC2 | D1 | 181 | 1850 | 2014-11-30 17:59 | 2014-11-30 18:27 | 310 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 0.46667 | 0.028283 | 8.3717 | 17.9394 | 18
MC2 | D1 | 182 | 1850 | 2014-11-30 18:27 | 2014-11-30 20:54 | 175 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 11 | 2.45 | 1.1508 | 340.6242 | 139.0303 | 139
MC2 | U1 | 183 | 3110 | 2014-11-30 20:54 | 2014-12-01 12:58 | 0 | 330 | 296 | Condenser tube leaks | F540Condenser Tube Leak | Mill Creek | Outage | Coal | 2 | 2014 | 11 | 16.0667 | 16.0667 | 4755.7333 | 296 | 296
MC2 | MO | 184 | 8230 | 2014-12-01 12:58 | 2014-12-04 22:21 | 0 | 330 | 296 | Ducting A | F590FGD Expansion Joint Repair/ Boiler Deslag | Mill Creek | Maintenance | Coal | 2 | 2014 | 12 | 81.3833 | 81.3833 | 24089.4667 | 296 | 296
MC2 | SF | 185 | 3619 | 2014-12-04 22:21 | 2014-12-05 12:06 | 0 | 330 | 296 | Other switchyard equipment - external | F400Relay & Switchyard Issues - Problem Synchronizing | Mill Creek | Outage | Coal | 2 | 2014 | 12 | 13.75 | 13.75 | 4070 | 296 | 296
MC2 | NC | 186 | 1850 | 2014-12-05 12:06 | 2014-12-05 15:19 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2014 | 12 | 3.2167 | 3.2167 | 952.1333 | 296 | 296
MC2 | U1 | 187 | 3110 | 2014-12-05 15:19 | 2014-12-07 16:26 | 0 | 330 | 296 | Condenser tube leaks | F540Condenser Tube Leak | Mill Creek | Outage | Coal | 2 | 2014 | 12 | 49.1167 | 49.1167 | 14538.5333 | 296 | 296
MC2 | NC | 188 | 1850 | 2014-12-07 16:26 | 2014-12-08 04:00 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 2 | 2014 | 12 | 11.5667 | 11.5667 | 3423.7333 | 296 | 296
MC2 | D1 | 189 | 1850 | 2014-12-08 04:00 | 2014-12-09 09:00 | 170 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 29 | 14.0606 | 4161.9394 | 143.5152 | 144
MC2 | D1 | 190 | 1850 | 2014-12-09 09:00 | 2014-12-10 20:22 | 240 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 35.3667 | 9.6455 | 2855.0545 | 80.7273 | 81
MC2 | D1 | 191 | 1850 | 2014-12-10 20:22 | 2014-12-10 23:55 | 210 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 3.55 | 1.2909 | 382.1091 | 107.6364 | 108
MC2 | D1 | 192 | 1850 | 2014-12-10 23:55 | 2014-12-12 04:08 | 226 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 28.2167 | 8.8925 | 2632.1875 | 93.2848 | 93
MC2 | D1 | 193 | 1850 | 2014-12-12 04:08 | 2014-12-12 13:00 | 230 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 8.8667 | 2.6869 | 795.3131 | 89.697 | 90
MC2 | D1 | 194 | 1850 | 2014-12-12 13:00 | 2014-12-14 07:42 | 260 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 42.7 | 9.0576 | 2681.0424 | 62.7879 | 63
MC2 | D1 | 195 | 1850 | 2014-12-14 07:42 | 2014-12-14 17:30 | 230 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 9.8 | 2.9697 | 879.0303 | 89.697 | 90
MC2 | D1 | 196 | 1850 | 2014-12-14 17:30 | 2014-12-15 02:38 | 260 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 9.1333 | 1.9374 | 573.4626 | 62.7879 | 63
MC2 | D1 | 197 | 1850 | 2014-12-15 02:38 | 2014-12-17 04:08 | 270 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 49.5 | 9 | 2664 | 53.8182 | 54
MC2 | D1 | 198 | 1850 | 2014-12-17 04:08 | 2014-12-17 22:25 | 310 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 18.2833 | 1.1081 | 327.9919 | 17.9394 | 18
MC2 | D1 | 199 | 1850 | 2014-12-17 22:25 | 2014-12-18 08:50 | 273 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 10.4167 | 1.7992 | 532.5758 | 51.1273 | 51
MC2 | D1 | 200 | 1850 | 2014-12-18 08:50 | 2014-12-19 21:05 | 320 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 36.25 | 1.0985 | 325.1515 | 8.9697 | 9
MC2 | D1 | 201 | 1850 | 2014-12-20 00:40 | 2014-12-20 14:49 | 310 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2014 | 12 | 14.15 | 0.85758 | 253.8424 | 17.9394 | 18
MC2 | MO | 202 | 9720 | 2014-12-21 01:01 | 2014-12-22 22:26 | 0 | 330 | 296 | Other safety problems | FX00FGD Ductwork - Zachry making lift | Mill Creek | Maintenance | Coal | 2 | 2014 | 12 | 45.4167 | 45.4167 | 13443.3333 | 296 | 296
MC2 | SF | 203 | 3620 | 2014-12-22 22:26 | 2015-01-01 | 0 | 330 | 296 | Main transformer | F700Main Transformer A Phase | Mill Creek | Outage | Coal | 2 | 2014 | 12 | 217.5667 | 217.5667 | 64399.7333 | 296 | 296
MC2 | SF | 1 | 3620 | 2015-01-01 | 2015-01-05 19:15 | 0 | 330 | 296 | Main transformer | F700Main Transformer Replacement | Mill Creek | Outage | Coal | 2 | 2015 | 1 | 115.25 | 115.25 | 34114 | 296 | 296
MC2 | NC | 2 | 1850 | 2015-01-05 19:15 | 2015-01-05 20:57 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 2 | 2015 | 1 | 1.7 | 1.7 | 503.2 | 296 | 296
MC2 | U1 | 3 | 4700 | 2015-01-05 20:57 | 2015-01-06 08:19 | 0 | 330 | 296 | Generator voltage control | F400Generator Field - Voltage Regulator Issues | Mill Creek | Outage | Coal | 2 | 2015 | 1 | 11.3667 | 11.3667 | 3364.5333 | 296 | 296
MC2 | NC | 4 | 1850 | 2015-01-06 08:19 | 2015-01-07 02:46 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 2 | 2015 | 1 | 18.45 | 18.45 | 5461.2 | 296 | 296
MC2 | D1 | 5 | 1850 | 2015-01-07 08:02 | 2015-01-07 21:50 | 262 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 1 | 13.8 | 2.8436 | 841.7164 | 60.9939 | 61
MC2 | D1 | 6 | 1850 | 2015-01-07 21:50 | 2015-01-08 04:52 | 275 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 1 | 7.0333 | 1.1722 | 346.9778 | 49.3333 | 49
MC2 | D1 | 7 | 1850 | 2015-01-08 04:52 | 2015-01-08 12:15 | 300 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 1 | 7.3833 | 0.67121 | 198.6788 | 26.9091 | 27
MC2 | D1 | 8 | 1850 | 2015-01-08 12:15 | 2015-01-08 16:13 | 277 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 1 | 3.9667 | 0.63707 | 188.5729 | 47.5394 | 48
MC2 | D1 | 9 | 1850 | 2015-01-08 16:13 | 2015-01-09 07:45 | 296 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 1 | 15.5333 | 1.6004 | 473.7196 | 30.497 | 30
MC2 | D1 | 10 | 1850 | 2015-01-09 07:45 | 2015-01-12 07:44 | 315 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 1 | 71.9833 | 3.272 | 968.503 | 13.4545 | 13
MC2 | D1 | 11 | 1850 | 2015-01-12 07:44 | 2015-01-13 06:03 | 322 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 1 | 22.3167 | 0.54101 | 160.139 | 7.1758 | 7
MC2 | D1 | 12 | 1850 | 2015-01-13 09:37 | 2015-01-13 16:38 | 300 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 1 | 7.0167 | 0.63788 | 188.8121 | 26.9091 | 27
MC2 | MO | 13 | 4619 | 2015-01-17 10:27 | 2015-01-19 01:38 | 0 | 330 | 296 | Other hydrogen system problems | F540Generator Bushing Box - Hydrogen Leak Repair | Mill Creek | Maintenance | Coal | 2 | 2015 | 1 | 39.1833 | 39.1833 | 11598.2667 | 296 | 296
MC2 | NC | 14 | 1850 | 2015-01-19 01:38 | 2015-01-19 07:38 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 2 | 2015 | 1 | 6 | 6 | 1776 | 296 | 296
MC2 | D1 | 15 | 1850 | 2015-01-19 07:38 | 2015-01-20 03:00 | 190 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 1 | 19.3667 | 8.2162 | 2431.9838 | 125.5758 | 126
MC2 | D1 | 16 | 1850 | 2015-01-20 03:00 | 2015-01-20 09:55 | 240 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 1 | 6.9167 | 1.8864 | 558.3636 | 80.7273 | 81
MC2 | D1 | 17 | 1850 | 2015-01-20 09:55 | 2015-01-21 01:56 | 295 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 1 | 16.0167 | 1.6987 | 502.8263 | 31.3939 | 31
MC2 | D1 | 18 | 4700 | 2015-01-21 01:56 | 2015-01-21 08:01 | 235 | 330 | 296 | Generator voltage control | F400Voltage Regulator Issue | Mill Creek | Derate | Coal | 2 | 2015 | 1 | 6.0833 | 1.7513 | 518.3737 | 85.2121 | 85
MC2 | NC | 19 | 9999 | 2015-02-03 07:00 | 2015-02-03 14:13 | 0 | 330 | 296 | Total unit performance testing (use appropriate codes for individual component testing) | F790Winter full load capability test | Mill Creek | Other | Coal | 2 | 2015 | 2 | 7.2167 | 7.2167 | 2136.1333 | 296 | 296
MC2 | NC | 20 | 1160 | 2015-02-22 08:00 | 2015-02-22 12:54 | 0 | 330 | 296 | First reheater B | FS00Deslag 1st Reheat | Mill Creek | Other | Coal | 2 | 2015 | 2 | 4.9 | 4.9 | 1450.4 | 296 | 296
MC2 | D1 | 21 | 250 | 2015-03-01 00:39 | 2015-03-01 02:52 | 250 | 330 | 296 | Pulverizer feeders | F1202D Coal Feeder Plugged | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 2.2167 | 0.53737 | 159.0626 | 71.7576 | 72
MC2 | D4 | 22 | 8280 | 2015-03-03 22:00 | 2015-03-04 02:23 | 150 | 330 | 296 | Reagent feed piping | F590Reactant Feed Line Repair | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 4.3833 | 2.3909 | 707.7091 | 161.4545 | 161
MC2 | D1 | 23 | 250 | 2015-03-04 22:30 | 2015-03-05 00:33 | 230 | 330 | 296 | Pulverizer feeders | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 2.05 | 0.62121 | 183.8788 | 89.697 | 90
MC2 | D1 | 24 | 250 | 2015-03-05 00:33 | 2015-03-05 02:01 | 170 | 330 | 296 | Pulverizer feeders | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 1.4667 | 0.71111 | 210.4889 | 143.5152 | 144
MC2 | D1 | 25 | 250 | 2015-03-05 02:01 | 2015-03-05 18:58 | 230 | 330 | 296 | Pulverizer feeders | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 16.95 | 5.1364 | 1520.3636 | 89.697 | 90
MC2 | D1 | 26 | 250 | 2015-03-05 20:36 | 2015-03-06 04:30 | 230 | 330 | 296 | Pulverizer feeders | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 7.9 | 2.3939 | 708.6061 | 89.697 | 90
MC2 | D1 | 27 | 250 | 2015-03-06 04:30 | 2015-03-07 10:29 | 214 | 330 | 296 | Pulverizer feeders | FW00Wet Coal | Mill Creek | Derate | Coal | 2 | 2015 | 3 | 29.9833 | 10.5396 | 3119.7204 | 104.0485 | 104
MC2 | PO | 28 | 8440 | 2015-03-07 10:29 | 2015-05-03 20:30 | 0 | 330 | 296 | Major overhaul C | F590Planned 8 week Outage | Mill Creek | Other | Coal | 2 | 2015 | 3 | 1378.0167 | 1378.0167 | 407892.9333 | 296 | 296
MC2 | NC | 29 | 1850 | 2015-05-03 20:30 | 2015-05-04 03:54 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start | Mill Creek | Other | Coal | 2 | 2015 | 5 | 7.4 | 7.4 | 2190.4 | 296 | 296
MC2 | MO | 30 | 4460 | 2015-05-04 03:54 | 2015-05-04 13:15 | 0 | 330 | 296 | Turbine overspeed trip test | F590Turbine overspeed trip test | Mill Creek | Maintenance | Coal | 2 | 2015 | 5 | 9.35 | 9.35 | 2767.6 | 296 | 296
MC2 | MO | 31 | 4283 | 2015-05-04 13:15 | 2015-05-04 14:00 | 0 | 330 | 296 | Lube oil system valves and piping | F540#7 Bearing turbine oil leak | Mill Creek | Maintenance | Coal | 2 | 2015 | 5 | 0.75 | 0.75 | 222 | 296 | 296
MC2 | MO | 32 | 4283 | 2015-05-04 14:00 | 2015-05-05 19:47 | 0 | 330 | 296 | Lube oil system valves and piping | F540# 7 Bearing turbine oil leak | Mill Creek | Maintenance | Coal | 2 | 2015 | 5 | 29.7833 | 29.7833 | 8815.8667 | 296 | 296
MC2 | U1 | 33 | 3620 | 2015-05-05 19:47 | 2015-05-09 09:32 | 0 | 330 | 296 | Main transformer | F5902 B phase Main Transformer - Filter and clean the oil | Mill Creek | Outage | Coal | 2 | 2015 | 5 | 85.75 | 85.75 | 25382 | 296 | 296
MC2 | NC | 34 | 1850 | 2015-05-09 09:32 | 2015-05-12 02:00 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High silica @ Warm Start-up | Mill Creek | Other | Coal | 2 | 2015 | 5 | 64.4667 | 64.4667 | 19082.1333 | 296 | 296
MC2 | D1 | 35 | 1850 | 2015-05-12 09:08 | 2015-05-12 10:40 | 275 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 1.5333 | 0.25556 | 75.6444 | 49.3333 | 49
MC2 | D1 | 36 | 1850 | 2015-05-12 10:40 | 2015-05-12 14:00 | 260 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 3.3333 | 0.70707 | 209.2929 | 62.7879 | 63
MC2 | D1 | 37 | 1850 | 2015-05-12 14:00 | 2015-05-12 17:40 | 290 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 3.6667 | 0.44444 | 131.5556 | 35.8788 | 36
MC2 | D1 | 38 | 310 | 2015-05-13 00:02 | 2015-05-13 01:10 | 250 | 330 | 296 | Pulverizer mills | F5302A Mill Inspection | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 1.1333 | 0.27475 | 81.3253 | 71.7576 | 72
MC2 | D1 | 39 | 310 | 2015-05-13 08:00 | 2015-05-13 11:33 | 265 | 330 | 296 | Pulverizer mills | F5902A mill breaker - replace | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 3.55 | 0.69924 | 206.9758 | 58.303 | 58
MC2 | NC | 40 | 8460 | 2015-05-14 05:45 | 2015-05-14 20:00 | 0 | 330 | 296 | Testing A | F790FGD and Baghouse testing | Mill Creek | Other | Coal | 2 | 2015 | 5 | 14.25 | 14.25 | 4218 | 296 | 296
MC2 | D4 | 41 | 310 | 2015-05-18 22:50 | 2015-05-19 00:02 | 240 | 330 | 296 | Pulverizer mills | F5902C coal mill roller adjustment | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 1.2 | 0.32727 | 96.8727 | 80.7273 | 81
MC2 | D4 | 42 | 310 | 2015-05-19 00:02 | 2015-05-19 01:03 | 240 | 330 | 296 | Pulverizer mills | F5902D coal mill roller adjustment | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 1.0167 | 0.27727 | 82.0727 | 80.7273 | 81
MC2 | MO | 43 | 8450 | 2015-05-19 09:45 | 2015-05-21 07:57 | 0 | 330 | 296 | Inspection B | F530WFGD Inspection | Mill Creek | Maintenance | Coal | 2 | 2015 | 5 | 46.2 | 46.2 | 13675.2 | 296 | 296
MC2 | NC | 44 | 1850 | 2015-05-21 07:57 | 2015-05-21 14:10 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High silica @ Hot Start | Mill Creek | Other | Coal | 2 | 2015 | 5 | 6.2167 | 6.2167 | 1840.1333 | 296 | 296
MC2 | D1 | 45 | 1850 | 2015-05-21 14:10 | 2015-05-21 16:00 | 220 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 1.8333 | 0.61111 | 180.8889 | 98.6667 | 99
MC2 | D1 | 46 | 1850 | 2015-05-21 16:00 | 2015-05-21 23:40 | 250 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 7.6667 | 1.8586 | 550.1414 | 71.7576 | 72
MC2 | D1 | 47 | 8499 | 2015-05-22 06:05 | 2015-05-22 06:20 | 300 | 330 | 296 | Other miscellaneous wet scrubber problems | F590Loss of clearwell pumps | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 0.25 | 0.022727 | 6.7273 | 26.9091 | 27
MC2 | D1 | 48 | 250 | 2015-05-22 21:42 | 2015-05-22 23:05 | 230 | 330 | 296 | Pulverizer feeders | F5902B Feeder issues | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 1.3833 | 0.41919 | 124.0808 | 89.697 | 90
MC2 | D1 | 49 | 250 | 2015-05-25 04:53 | 2015-05-25 08:03 | 240 | 330 | 296 | Pulverizer feeders | F5902B feeder issues | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 3.1667 | 0.86364 | 255.6364 | 80.7273 | 81
MC2 | NC | 50 | 8460 | 2015-05-26 08:00 | 2015-05-26 20:14 | 0 | 330 | 296 | Testing A | F790WFGD and Baghouse testing | Mill Creek | Other | Coal | 2 | 2015 | 5 | 12.2333 | 12.2333 | 3621.0667 | 296 | 296
MC2 | D4 | 51 | 310 | 2015-05-27 23:00 | 2015-05-28 00:36 | 240 | 330 | 296 | Pulverizer mills | F5302D Coal Mill - Inspection | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 1.6 | 0.43636 | 129.1636 | 80.7273 | 81
MC2 | NC | 52 | 8650 | 2015-05-28 08:00 | 2015-05-28 19:18 | 0 | 330 | 296 | Baghouse systems | F790Baghouse Testing | Mill Creek | Other | Coal | 2 | 2015 | 5 | 11.3 | 11.3 | 3344.8 | 296 | 296
MC2 | NC | 53 | 8650 | 2015-05-29 08:00 | 2015-05-29 13:05 | 0 | 330 | 296 | Baghouse systems | F790Baghouse testing | Mill Creek | Other | Coal | 2 | 2015 | 5 | 5.0833 | 5.0833 | 1504.6667 | 296 | 296
MC2 | NC | 54 | 8650 | 2015-05-30 08:21 | 2015-05-31 23:00 | 0 | 330 | 296 | Baghouse systems | F790Baghouse testing | Mill Creek | Other | Coal | 2 | 2015 | 5 | 38.65 | 38.65 | 11440.4 | 296 | 296
MC2 | D4 | 55 | 250 | 2015-05-31 23:00 | 2015-06-01 03:41 | 240 | 330 | 296 | Pulverizer feeders | F5302B Feeder Inspection | Mill Creek | Derate | Coal | 2 | 2015 | 5 | 4.6833 | 1.2773 | 378.0727 | 80.7273 | 81
MC2 | NC | 56 | 1990 | 2015-06-04 08:10 | 2015-06-04 19:43 | 0 | 330 | 296 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Boiler tuning | Mill Creek | Other | Coal | 2 | 2015 | 6 | 11.55 | 11.55 | 3418.8 | 296 | 296
MC2 | NC | 57 | 8460 | 2015-06-05 07:06 | 2015-06-05 15:26 | 0 | 330 | 296 | Testing A | F790Full Load Testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 8.3333 | 8.3333 | 2466.6667 | 296 | 296
MC2 | NC | 58 | 8460 | 2015-06-06 11:42 | 2015-06-06 17:30 | 0 | 330 | 296 | Testing A | F790Full Load Testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 5.8 | 5.8 | 1716.8 | 296 | 296
MC2 | NC | 59 | 8460 | 2015-06-07 08:30 | 2015-06-07 17:23 | 0 | 330 | 296 | Testing A | F790Low load testing - load available if needed | Mill Creek | Other | Coal | 2 | 2015 | 6 | 8.8833 | 8.8833 | 2629.4667 | 296 | 296
MC2 | D1 | 60 | 310 | 2015-06-08 06:40 | 2015-06-08 11:01 | 260 | 330 | 296 | Pulverizer mills | F5902A Coal Mill maintenance | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 4.35 | 0.92273 | 273.1273 | 62.7879 | 63
MC2 | NC | 61 | 8460 | 2015-06-08 11:15 | 2015-06-08 18:25 | 0 | 330 | 296 | Testing A | F790Full load testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 7.1667 | 7.1667 | 2121.3333 | 296 | 296
MC2 | NC | 62 | 8460 | 2015-06-09 12:00 | 2015-06-09 14:08 | 0 | 330 | 296 | Testing A | F790Full Load Testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 2.1333 | 2.1333 | 631.4667 | 296 | 296
MC2 | NC | 63 | 8460 | 2015-06-10 02:16 | 2015-06-10 04:23 | 0 | 330 | 296 | Testing A | F790Low Load RATA Testing - Load available if needed | Mill Creek | Other | Coal | 2 | 2015 | 6 | 2.1167 | 2.1167 | 626.5333 | 296 | 296
MC2 | NC | 64 | 8460 | 2015-06-10 04:23 | 2015-06-10 05:48 | 0 | 330 | 296 | Testing A | F790Mid Load RATA Testing - Load available if needed | Mill Creek | Other | Coal | 2 | 2015 | 6 | 1.4167 | 1.4167 | 419.3333 | 296 | 296
MC2 | D1 | 65 | 310 | 2015-06-10 06:35 | 2015-06-10 07:43 | 267 | 330 | 296 | Pulverizer mills | F5902A Coal Mill | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 1.1333 | 0.21636 | 64.0436 | 56.5091 | 57
MC2 | NC | 66 | 8460 | 2015-06-10 08:00 | 2015-06-10 15:53 | 0 | 330 | 296 | Testing A | F790Full Load Testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 7.8833 | 7.8833 | 2333.4667 | 296 | 296
MC2 | NC | 67 | 8460 | 2015-06-11 01:46 | 2015-06-11 03:57 | 0 | 330 | 296 | Testing A | F790Low Load RATA Testing - Load available if needed | Mill Creek | Other | Coal | 2 | 2015 | 6 | 2.1833 | 2.1833 | 646.2667 | 296 | 296
MC2 | D1 | 68 | 310 | 2015-06-11 03:57 | 2015-06-11 10:39 | 250 | 330 | 296 | Pulverizer mills | F5902A Coal Mill | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 6.7 | 1.6242 | 480.7758 | 71.7576 | 72
MC2 | D1 | 69 | 320 | 2015-06-23 05:25 | 2015-06-23 07:19 | 250 | 330 | 296 | Foreign object in Pulverizers mill | F5302B Coal Mill - Sand in the bowl | Mill Creek | Derate | Coal | 2 | 2015 | 6 | 1.9 | 0.46061 | 136.3394 | 71.7576 | 72
MC2 | NC | 70 | 8650 | 2015-06-23 08:00 | 2015-06-23 17:26 | 0 | 330 | 296 | Baghouse systems | F790Full load PM testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 9.4333 | 9.4333 | 2792.2667 | 296 | 296
MC2 | NC | 71 | 8460 | 2015-06-24 09:00 | 2015-06-24 17:24 | 0 | 330 | 296 | Testing A | F790Full load testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 8.4 | 8.4 | 2486.4 | 296 | 296
MC2 | NC | 72 | 8650 | 2015-06-25 08:00 | 2015-06-25 14:26 | 0 | 330 | 296 | Baghouse systems | F790Full load PM testing | Mill Creek | Other | Coal | 2 | 2015 | 6 | 6.4333 | 6.4333 | 1904.2667 | 296 | 296
MC2 | NC | 73 | 9999 | 2015-07-10 09:00 | 2015-07-10 15:25 | 0 | 330 | 296 | Total unit performance testing (use appropriate codes for individual component testing) | F790Summer Full load Capability Test | Mill Creek | Other | Coal | 2 | 2015 | 7 | 6.4167 | 6.4167 | 1899.3333 | 296 | 296
MC2 | D1 | 74 | 310 | 2015-08-03 12:52 | 2015-08-03 15:57 | 275 | 330 | 296 | Pulverizer mills | F5902C Coal Mill - Replaced Roller | Mill Creek | Derate | Coal | 2 | 2015 | 8 | 3.0833 | 0.51389 | 152.1111 | 49.3333 | 49
MC2 | NC | 75 | 3623 | 2015-08-11 11:32 | 2015-08-11 14:00 | 0 | 330 | 296 | Auxiliary generators | F790VAR Testing | Mill Creek | Other | Coal | 2 | 2015 | 8 | 2.4667 | 2.4667 | 730.1333 | 296 | 296
MC2 | D4 | 76 | 3410 | 2015-08-11 23:00 | 2015-08-12 07:33 | 190 | 330 | 296 | Feedwater pump | F5902B Boiler Feedwater Pump Warm Up Line - Repair Leak | Mill Creek | Derate | Coal | 2 | 2015 | 8 | 8.55 | 3.6273 | 1073.6727 | 125.5758 | 126
MC2 | MO | 77 | 4263 | 2015-08-17 22:18 | 2015-08-22 00:04 | 0 | 330 | 296 | Reheat stop valves | F590Turbine Reheat & Main Stop Valves - Remove Screens/Baskets | Mill Creek | Maintenance | Coal | 2 | 2015 | 8 | 97.7667 | 97.7667 | 28938.9333 | 296 | 296
MC2 | NC | 79 | 1850 | 2015-08-23 08:18 | 2015-08-24 02:18 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 2 | 2015 | 8 | 18 | 18 | 5328 | 296 | 296
MC2 | D1 | 80 | 1850 | 2015-08-24 02:18 | 2015-08-24 07:51 | 313 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 2 | 2015 | 8 | 5.55 | 0.28591 | 84.6291 | 15.2485 | 15
MC2 | D4 | 81 | 1455 | 2015-08-28 22:00 | 2015-08-29 00:25 | 100 | 330 | 296 | Induced draft fans | F5402A Induced Draft Fan - Oil Leak | Mill Creek | Derate | Coal | 2 | 2015 | 8 | 2.4167 | 1.6843 | 498.5657 | 206.303 | 206
MC2 | D1 | 82 | 250 | 2015-09-10 17:25 | 2015-09-10 18:54 | 250 | 330 | 296 | Pulverizer feeders | F1202B Coal Feeder - Plugged | Mill Creek | Derate | Coal | 2 | 2015 | 9 | 1.4833 | 0.3596 | 106.4404 | 71.7576 | 72
MC2 | D1 | 83 | 250 | 2015-09-10 19:03 | 2015-09-10 21:58 | 250 | 330 | 296 | Pulverizer feeders | F1202B Coal Feeder - Plugged, Removed Foreign Metal | Mill Creek | Derate | Coal | 2 | 2015 | 9 | 2.9167 | 0.70707 | 209.2929 | 71.7576 | 72
MC2 | D4 | 84 | 1457 | 2015-09-15 21:15 | 2015-09-16 02:55 | 114 | 330 | 296 | Induced draft fan lubrication systems | F5902A Induced Draft Fan - Repair Oil Leaks | Mill Creek | Derate | Coal | 2 | 2015 | 9 | 5.6667 | 3.7091 | 1097.8909 | 193.7455 | 194
MC2 | NC | 85 | 8460 | 2015-09-21 10:00 | 2015-09-21 11:51 | 0 | 330 | 296 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 9 | 1.85 | 1.85 | 547.6 | 296 | 296
MC2 | D1 | 86 | 1475 | 2015-09-21 11:51 | 2015-09-21 14:23 | 150 | 330 | 296 | Induced draft fan controls | F8202B Induced Draft Fan Trip - VFD Fault | Mill Creek | Derate | Coal | 2 | 2015 | 9 | 2.5333 | 1.3818 | 409.0182 | 161.4545 | 161
MC2 | NC | 87 | 8460 | 2015-09-22 10:30 | 2015-09-22 19:30 | 0 | 330 | 296 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 9 | 9 | 9 | 2664 | 296 | 296
MC2 | NC | 88 | 8460 | 2015-09-23 09:00 | 2015-09-23 18:00 | 0 | 330 | 296 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 9 | 9 | 9 | 2664 | 296 | 296
MC2 | D1 | 89 | 250 | 2015-09-24 02:57 | 2015-09-24 05:27 | 250 | 330 | 296 | Pulverizer feeders | F5902C Coal Feeder - Cleanout Conveyor Gearbox Issue | Mill Creek | Derate | Coal | 2 | 2015 | 9 | 2.5 | 0.60606 | 179.3939 | 71.7576 | 72
MC2 | NC | 90 | 8460 | 2015-09-24 11:00 | 2015-09-24 18:00 | 0 | 330 | 296 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 9 | 7 | 7 | 2072 | 296 | 296
MC2 | D4 | 91 | 250 | 2015-09-24 23:00 | 2015-09-25 06:58 | 250 | 330 | 296 | Pulverizer feeders | F5902C Coal Feeder Cleanout Conveyor - Replace Gearbox | Mill Creek | Derate | Coal | 2 | 2015 | 9 | 7.9667 | 1.9313 | 571.6687 | 71.7576 | 72
MC2 | NC | 92 | 8460 | 2015-09-28 07:30 | 2015-09-28 21:00 | 0 | 330 | 296 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 9 | 13.5 | 13.5 | 3996 | 296 | 296
MC2 | NC | 93 | 8460 | 2015-09-29 09:00 | 2015-09-29 17:30 | 0 | 330 | 296 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 9 | 8.5 | 8.5 | 2516 | 296 | 296
MC2 | NC | 94 | 8460 | 2015-09-30 08:40 | 2015-09-30 17:00 | 0 | 330 | 296 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 9 | 8.3333 | 8.3333 | 2466.6667 | 296 | 296
MC2 | NC | 95 | 8460 | 2015-10-01 07:04 | 2015-10-01 17:10 | 0 | 330 | 296 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2015 | 10 | 10.1 | 10.1 | 2989.6 | 296 | 296
MC2 | D1 | 96 | 310 | 2015-10-15 13:40 | 2015-10-15 17:36 | 240 | 330 | 296 | Pulverizer mills | F1202B Coal Mill - Raw Coal Conduit Plugged with Foreign Metal | Mill Creek | Derate | Coal | 2 | 2015 | 10 | 3.9333 | 1.0727 | 317.5273 | 80.7273 | 81
MC2 | D4 | 97 | 250 | 2015-10-15 23:00 | 2015-10-16 03:46 | 250 | 330 | 296 | Pulverizer feeders | F5902A Coal Feeder - Replace Cleanout Conveyor | Mill Creek | Derate | Coal | 2 | 2015 | 10 | 4.7667 | 1.1556 | 342.0444 | 71.7576 | 72
MC2 | MO | 98 | 590 | 2015-10-20 23:10 | 2015-10-21 13:56 | 0 | 330 | 296 | Desuperheater/attemperator valves | F590Superheater attemperator spray valve leak | Mill Creek | Maintenance | Coal | 2 | 2015 | 10 | 14.7667 | 14.7667 | 4370.9333 | 296 | 296
MC2 | NC | 99 | 1850 | 2015-10-21 13:36 | 2015-10-21 21:58 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ hot start | Mill Creek | Other | Coal | 2 | 2015 | 10 | 8.3667 | 8.3667 | 2476.5333 | 296 | 296
MC2 | D4 | 100 | 250 | 2015-10-22 22:00 | 2015-10-23 03:50 | 245 | 330 | 296 | Pulverizer feeders | F5902A Mill Coal Feeder Cleanout will not run | Mill Creek | Derate | Coal | 2 | 2015 | 10 | 5.8333 | 1.5025 | 444.7475 | 76.2424 | 76
MC2 | D4 | 101 | 310 | 2015-11-02 23:14 | 2015-11-03 04:10 | 230 | 330 | 296 | Pulverizer mills | F5302A Mill Inpspection and adjust rollers | Mill Creek | Derate | Coal | 2 | 2015 | 11 | 4.9333 | 1.4949 | 442.5051 | 89.697 | 90
MC2 | D4 | 102 | 310 | 2015-11-03 23:00 | 2015-11-04 05:01 | 230 | 330 | 296 | Pulverizer mills | F5302B mill inspection | Mill Creek | Derate | Coal | 2 | 2015 | 11 | 6.0167 | 1.8232 | 539.6768 | 89.697 | 90
MC2 | D4 | 103 | 310 | 2015-11-05 23:00 | 2015-11-06 05:38 | 230 | 330 | 296 | Pulverizer mills | F5302C Mill Roller adjustment | Mill Creek | Derate | Coal | 2 | 2015 | 11 | 6.6333 | 2.0101 | 594.9899 | 89.697 | 90
MC2 | D4 | 104 | 310 | 2015-11-09 23:00 | 2015-11-10 04:26 | 230 | 330 | 296 | Pulverizer mills | F5902D Coal Mill Roller adjustment | Mill Creek | Derate | Coal | 2 | 2015 | 11 | 5.4333 | 1.6465 | 487.3535 | 89.697 | 90
MC2 | NC | 105 | 8460 | 2015-11-16 08:00 | 2015-11-16 17:00 | 0 | 330 | 296 | Testing A | F790Full load Mercury testing | Mill Creek | Other | Coal | 2 | 2015 | 11 | 9 | 9 | 2664 | 296 | 296
MC2 | NC | 106 | 8460 | 2015-11-17 07:40 | 2015-11-17 17:00 | 0 | 330 | 296 | Testing A | F790Full load Mercury testing | Mill Creek | Other | Coal | 2 | 2015 | 11 | 9.3333 | 9.3333 | 2762.6667 | 296 | 296
MC2 | D1 | 107 | 95 | 2015-11-18 06:00 | 2015-11-18 07:45 | 240 | 330 | 296 | Bunker flow problems | F1202B Coal Bunker valve stuck | Mill Creek | Derate | Coal | 2 | 2015 | 11 | 1.75 | 0.47727 | 141.2727 | 80.7273 | 81
MC2 | NC | 108 | 8460 | 2015-11-18 08:15 | 2015-11-18 17:00 | 0 | 330 | 296 | Testing A | F790Full load Mercury testing | Mill Creek | Other | Coal | 2 | 2015 | 11 | 8.75 | 8.75 | 2590 | 296 | 296
MC2 | NC | 109 | 8460 | 2015-11-19 07:30 | 2015-11-19 17:00 | 0 | 330 | 296 | Testing A | F790Full load Mercury testing | Mill Creek | Other | Coal | 2 | 2015 | 11 | 9.5 | 9.5 | 2812 | 296 | 296
MC2 | NC | 110 | 8460 | 2015-11-20 09:00 | 2015-11-20 19:00 | 0 | 330 | 296 | Testing A | F790Full load Mercury testing | Mill Creek | Other | Coal | 2 | 2015 | 11 | 10 | 10 | 2960 | 296 | 296
MC2 | NC | 111 | 8460 | 2015-11-21 08:00 | 2015-11-21 18:25 | 0 | 330 | 296 | Testing A | F790Full load Mercury testing | Mill Creek | Other | Coal | 2 | 2015 | 11 | 10.4167 | 10.4167 | 3083.3333 | 296 | 296
MC2 | D1 | 112 | 95 | 2015-11-21 18:25 | 2015-11-21 18:46 | 240 | 330 | 296 | Bunker flow problems | F120Coal clogged in bunker chute | Mill Creek | Derate | Coal | 2 | 2015 | 11 | 0.35 | 0.095455 | 28.2545 | 80.7273 | 81
MC2 | NC | 113 | 8460 | 2015-11-21 18:46 | 2015-11-21 19:17 | 0 | 330 | 296 | Testing A | F790Full load Mercury testing | Mill Creek | Other | Coal | 2 | 2015 | 11 | 0.51667 | 0.51667 | 152.9333 | 296 | 296
MC2 | D1 | 114 | 110 | 2015-11-24 23:05 | 2015-11-25 01:28 | 125 | 330 | 296 | Other coal fuel supply problems up through bunkers | F590G2 Tripper motor out | Mill Creek | Derate | Coal | 2 | 2015 | 11 | 2.3833 | 1.4806 | 438.2444 | 183.8788 | 184
MC2 | D4 | 115 | 250 | 2015-11-30 22:13 | 2015-12-01 05:12 | 240 | 330 | 296 | Pulverizer feeders | F5902B coal feeder - I/E replaced micro switch | Mill Creek | Derate | Coal | 2 | 2015 | 11 | 6.9833 | 1.9045 | 563.7455 | 80.7273 | 81
MC2 | D4 | 116 | 310 | 2015-12-04 23:00 | 2015-12-05 02:41 | 245 | 330 | 296 | Pulverizer mills | F5302B Coal Mill Inspection | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 3.6833 | 0.94874 | 280.8263 | 76.2424 | 76
MC2 | D4 | 117 | 310 | 2015-12-07 23:00 | 2015-12-08 04:31 | 245 | 330 | 296 | Pulverizer mills | F5902B Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 5.5167 | 1.421 | 420.604 | 76.2424 | 76
MC2 | NC | 118 | 3190 | 2015-12-15 07:23 | 2015-12-15 11:04 | 0 | 330 | 296 | Air leakage (for losses not attributable to previously noted equipment related codes) | F790Condenser air in-leakage check | Mill Creek | Other | Coal | 2 | 2015 | 12 | 3.6833 | 3.6833 | 1090.2667 | 296 | 296
MC2 | U1 | 119 | 770 | 2015-12-18 09:27 | 2015-12-18 12:16 | 0 | 330 | 296 | Other boiler recirculation problems | F6402B boiler circ. pump lube oil pump motor overloads | Mill Creek | Outage | Coal | 2 | 2015 | 12 | 2.8167 | 2.8167 | 833.7333 | 296 | 296
MC2 | NC | 120 | 1850 | 2015-12-18 12:16 | 2015-12-18 16:46 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High silica at very hot start | Mill Creek | Other | Coal | 2 | 2015 | 12 | 4.5 | 4.5 | 1332 | 296 | 296
MC2 | D1 | 121 | 1850 | 2015-12-18 16:46 | 2015-12-19 01:05 | 257 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 8.3167 | 1.8397 | 544.5653 | 65.4788 | 65
MC2 | D1 | 122 | 1850 | 2015-12-19 01:05 | 2015-12-19 04:24 | 290 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 3.3167 | 0.40202 | 118.998 | 35.8788 | 36
MC2 | MO | 123 | 8499 | 2015-12-19 22:51 | 2015-12-23 16:53 | 0 | 330 | 296 | Other miscellaneous wet scrubber problems | F590FGD maintenance - replace orifaces in hydrocyclone system | Mill Creek | Maintenance | Coal | 2 | 2015 | 12 | 90.0333 | 90.0333 | 26649.8667 | 296 | 296
MC2 | SF | 124 | 1455 | 2015-12-23 16:53 | 2015-12-24 09:46 | 0 | 330 | 296 | Induced draft fans | F060Loss of ID Fan Alarm - Blown Fuse in HPM | Mill Creek | Outage | Coal | 2 | 2015 | 12 | 16.8833 | 16.8833 | 4997.4667 | 296 | 296
MC2 | NC | 125 | 8460 | 2015-12-28 08:00 | 2015-12-28 10:50 | 0 | 330 | 296 | Testing A | F790Full Load Testing of AGC | Mill Creek | Other | Coal | 2 | 2015 | 12 | 2.8333 | 2.8333 | 838.6667 | 296 | 296
MC2 | D1 | 126 | 250 | 2015-12-28 21:23 | 2015-12-28 22:02 | 225 | 330 | 296 | Pulverizer feeders | FW00Wet coal | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 0.65 | 0.20682 | 61.2182 | 94.1818 | 94
MC2 | D1 | 127 | 250 | 2015-12-29 14:00 | 2015-12-29 15:23 | 215 | 330 | 296 | Pulverizer feeders | FW00Wet coal | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 1.3833 | 0.48207 | 142.6929 | 103.1515 | 103
MC2 | D1 | 128 | 250 | 2015-12-29 15:23 | 2015-12-29 20:10 | 275 | 330 | 296 | Pulverizer feeders | FW00Wet coal | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 4.7833 | 0.79722 | 235.9778 | 49.3333 | 49
MC2 | D1 | 129 | 250 | 2015-12-29 20:10 | 2015-12-29 22:04 | 230 | 330 | 296 | Pulverizer feeders | FW00Wet coal | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 1.9 | 0.57576 | 170.4242 | 89.697 | 90
MC2 | D1 | 130 | 250 | 2015-12-29 22:04 | 2015-12-30 02:35 | 150 | 330 | 296 | Pulverizer feeders | FW00Wet coal | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 4.5167 | 2.4636 | 729.2364 | 161.4545 | 161
MC2 | D1 | 131 | 250 | 2015-12-30 02:35 | 2015-12-30 03:38 | 230 | 330 | 296 | Pulverizer feeders | FW00Wet coal | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 1.05 | 0.31818 | 94.1818 | 89.697 | 90
MC2 | D4 | 132 | 250 | 2015-12-30 09:05 | 2015-12-30 16:18 | 245 | 330 | 296 | Pulverizer feeders | F5902D Feeder clean-out conveyor maintenance | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 7.2167 | 1.8588 | 550.2162 | 76.2424 | 76
MC2 | D1 | 133 | 250 | 2015-12-31 08:47 | 2015-12-31 08:56 | 240 | 330 | 296 | Pulverizer feeders | F5902C coal feeder clean out conveyor maintenance | Mill Creek | Derate | Coal | 2 | 2015 | 12 | 0.15 | 0.040909 | 12.1091 | 80.7273 | 81
MC2 | D4 | 1 | 250 | 2016-01-05 23:00 | 2016-01-06 04:58 | 240 | 330 | 296 | Pulverizer feeders | F5902A Coal feeder clean out conveyor maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 1 | 5.9667 | 1.6273 | 481.6727 | 80.7273 | 81
MC2 | D4 | 2 | 250 | 2016-01-06 23:00 | 2016-01-07 05:44 | 240 | 330 | 296 | Pulverizer feeders | F5902A coal feeder clean out conveyor maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 1 | 6.7333 | 1.8364 | 543.5636 | 80.7273 | 81
MC2 | D1 | 3 | 95 | 2016-01-07 06:10 | 2016-01-07 06:38 | 210 | 330 | 296 | Bunker flow problems | F1202D Coal feeder no coal flow. | Mill Creek | Derate | Coal | 2 | 2016 | 1 | 0.46667 | 0.1697 | 50.2303 | 107.6364 | 108
MC2 | D1 | 4 | 250 | 2016-01-13 11:21 | 2016-01-13 12:07 | 235 | 330 | 296 | Pulverizer feeders | F5902B Coal feeder maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 1 | 0.76667 | 0.22071 | 65.3293 | 85.2121 | 85
MC2 | NC | 5 | 8700 | 2016-01-19 08:00 | 2016-01-19 17:20 | 0 | 330 | 296 | CEMS Certification and Recertification | F790Full load RATA testing | Mill Creek | Other | Coal | 2 | 2016 | 1 | 9.3333 | 9.3333 | 2762.6667 | 296 | 296
MC2 | NC | 6 | 8700 | 2016-01-19 22:00 | 2016-01-20 01:37 | 0 | 330 | 296 | CEMS Certification and Recertification | F790Mid load RATA testing | Mill Creek | Other | Coal | 2 | 2016 | 1 | 3.6167 | 3.6167 | 1070.5333 | 296 | 296
MC2 | NC | 7 | 8700 | 2016-01-20 10:00 | 2016-01-20 13:30 | 0 | 330 | 296 | CEMS Certification and Recertification | F790Full load RATA testing | Mill Creek | Other | Coal | 2 | 2016 | 1 | 3.5 | 3.5 | 1036 | 296 | 296
MC2 | D1 | 8 | 4261 | 2016-01-27 00:46 | 2016-01-27 01:53 | 308 | 330 | 296 | Control valves | F060Control Valve 3 valve stem broken | Mill Creek | Derate | Coal | 2 | 2016 | 1 | 1.1167 | 0.074444 | 22.0356 | 19.7333 | 20
MC2 | D1 | 9 | 4261 | 2016-01-27 01:53 | 2016-01-27 04:24 | 308 | 330 | 296 | Control valves | F060Control Valve 3 valve stem broken | Mill Creek | Derate | Coal | 2 | 2016 | 1 | 2.5167 | 0.16778 | 49.6622 | 19.7333 | 20
MC2 | D1 | 10 | 4261 | 2016-01-27 04:24 | 2016-01-29 10:18 | 308 | 330 | 296 | Control valves | F060Control valve #3 valve stem broken | Mill Creek | Derate | Coal | 2 | 2016 | 1 | 53.9 | 3.5933 | 1063.6267 | 19.7333 | 20
MC2 | MO | 11 | 4261 | 2016-01-29 10:18 | 2016-01-31 04:16 | 0 | 330 | 296 | Control valves | F060#3 control valve stem broken | Mill Creek | Maintenance | Coal | 2 | 2016 | 1 | 41.9667 | 41.9667 | 12422.1333 | 296 | 296
MC2 | NC | 12 | 1850 | 2016-01-31 04:16 | 2016-01-31 10:22 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start | Mill Creek | Other | Coal | 2 | 2016 | 1 | 6.1 | 6.1 | 1805.6 | 296 | 296
MC2 | NC | 13 | 9999 | 2016-02-04 08:00 | 2016-02-04 13:31 | 0 | 330 | 296 | Total unit performance testing (use appropriate codes for individual component testing) | F790Full Load winter capability test | Mill Creek | Other | Coal | 2 | 2016 | 2 | 5.5167 | 5.5167 | 1632.9333 | 296 | 296
MC2 | D4 | 14 | 253 | 2016-02-08 23:00 | 2016-02-09 06:21 | 240 | 330 | 296 | Pulverizer feeder motor | F5902A coal feeder gearbox motor replaced | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 7.35 | 2.0045 | 593.3455 | 80.7273 | 81
MC2 | NC | 15 | 8700 | 2016-02-09 07:30 | 2016-02-09 18:00 | 0 | 330 | 296 | CEMS Certification and Recertification | F790Full load PM/RRA testing | Mill Creek | Other | Coal | 2 | 2016 | 2 | 10.5 | 10.5 | 3108 | 296 | 296
MC2 | D4 | 16 | 340 | 2016-02-17 23:00 | 2016-02-18 03:51 | 240 | 330 | 296 | Other pulverizer problems | F5902D Mill pyrite hopper maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 2 | 4.85 | 1.3227 | 391.5273 | 80.7273 | 81
MC2 | NC | 17 | 8460 | 2016-03-08 09:00 | 2016-03-08 11:30 | 0 | 330 | 296 | Testing A | F790Full load MATS testing | Mill Creek | Other | Coal | 2 | 2016 | 3 | 2.5 | 2.5 | 740 | 296 | 296
MC2 | PO | 18 | 3998 | 2016-03-20 20:19 | 2016-03-29 15:33 | 0 | 330 | 296 | Balance of plant overhaul/outage | F590Planned outage | Mill Creek | Other | Coal | 2 | 2016 | 3 | 211.2333 | 211.2333 | 62525.0667 | 296 | 296
MC2 | NC | 19 | 1850 | 2016-03-29 15:33 | 2016-03-30 05:23 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High silica @ cold start | Mill Creek | Other | Coal | 2 | 2016 | 3 | 13.8333 | 13.8333 | 4094.6667 | 296 | 296
MC2 | NC | 20 | 1990 | 2016-04-01 06:00 | 2016-04-01 21:00 | 0 | 330 | 296 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Full load testing prior to Nalco feed | Mill Creek | Other | Coal | 2 | 2016 | 4 | 15 | 15 | 4440 | 296 | 296
MC2 | D1 | 21 | 360 | 2016-04-04 11:28 | 2016-04-04 12:06 | 240 | 330 | 296 | Burners | F7802A1 Burner temps | Mill Creek | Derate | Coal | 2 | 2016 | 4 | 0.63333 | 0.17273 | 51.1273 | 80.7273 | 81
MC2 | NC | 22 | 1710 | 2016-04-05 01:00 | 2016-04-05 01:40 | 0 | 330 | 296 | Combustion/steam condition controls (report local controls --- burners | F7902A mill clean air flow test | Mill Creek | Other | Coal | 2 | 2016 | 4 | 0.66667 | 0.66667 | 197.3333 | 296 | 296
MC2 | NC | 23 | 1710 | 2016-04-06 01:00 | 2016-04-06 02:42 | 0 | 330 | 296 | Combustion/steam condition controls (report local controls --- burners | F7902B mill clean air flow test | Mill Creek | Other | Coal | 2 | 2016 | 4 | 1.7 | 1.7 | 503.2 | 296 | 296
MC2 | D1 | 24 | 360 | 2016-04-08 05:04 | 2016-04-08 05:37 | 245 | 330 | 296 | Burners | F7802A1 burner temps | Mill Creek | Derate | Coal | 2 | 2016 | 4 | 0.55 | 0.14167 | 41.9333 | 76.2424 | 76
MC2 | NC | 25 | 1710 | 2016-04-13 08:17 | 2016-04-13 09:30 | 0 | 330 | 296 | Combustion/steam condition controls (report local controls --- burners | F790Air flow testing | Mill Creek | Other | Coal | 2 | 2016 | 4 | 1.2167 | 1.2167 | 360.1333 | 296 | 296
MC2 | NC | 26 | 1710 | 2016-04-14 08:32 | 2016-04-14 10:04 | 0 | 330 | 296 | Combustion/steam condition controls (report local controls --- burners | F790Air flow testing | Mill Creek | Other | Coal | 2 | 2016 | 4 | 1.5333 | 1.5333 | 453.8667 | 296 | 296
MC2 | NC | 27 | 1710 | 2016-04-14 12:00 | 2016-04-14 14:36 | 0 | 330 | 296 | Combustion/steam condition controls (report local controls --- burners | F790Air flow testing | Mill Creek | Other | Coal | 2 | 2016 | 4 | 2.6 | 2.6 | 769.6 | 296 | 296
MC2 | NC | 28 | 8460 | 2016-04-16 15:00 | 2016-04-16 18:00 | 0 | 330 | 296 | Testing A | F790Hg compliance testing | Mill Creek | Other | Coal | 2 | 2016 | 4 | 3 | 3 | 888 | 296 | 296
MC2 | NC | 29 | 1710 | 2016-04-22 00:07 | 2016-04-22 01:58 | 0 | 330 | 296 | Combustion/steam condition controls (report local controls --- burners | F790Air flow testing low load | Mill Creek | Other | Coal | 2 | 2016 | 4 | 1.85 | 1.85 | 547.6 | 296 | 296
MC2 | NC | 30 | 1710 | 2016-05-09 14:45 | 2016-05-09 16:24 | 0 | 330 | 296 | Combustion/steam condition controls (report local controls --- burners | F790Mid load air flow testing | Mill Creek | Other | Coal | 2 | 2016 | 5 | 1.65 | 1.65 | 488.4 | 296 | 296
MC2 | NC | 31 | 1710 | 2016-05-11 11:55 | 2016-05-11 15:00 | 0 | 330 | 296 | Combustion/steam condition controls (report local controls --- burners | F790Full load air flow testing | Mill Creek | Other | Coal | 2 | 2016 | 5 | 3.0833 | 3.0833 | 912.6667 | 296 | 296
MC2 | NC | 32 | 1710 | 2016-05-13 02:00 | 2016-05-13 03:00 | 0 | 330 | 296 | Combustion/steam condition controls (report local controls --- burners | F790Low load air flow testing | Mill Creek | Other | Coal | 2 | 2016 | 5 | 1 | 1 | 296 | 296 | 296
MC2 | D4 | 33 | 250 | 2016-06-06 23:00 | 2016-06-07 05:05 | 240 | 330 | 296 | Pulverizer feeders | F0902A Feeder Calibration & Inspection | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 6.0833 | 1.6591 | 491.0909 | 80.7273 | 81
MC2 | D1 | 34 | 1520 | 2016-06-07 10:50 | 2016-06-07 12:41 | 240 | 330 | 296 | Flue gas dampers (except recirculation) | F6902A mill damper issues | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 1.85 | 0.50455 | 149.3455 | 80.7273 | 81
MC2 | D4 | 35 | 250 | 2016-06-07 23:00 | 2016-06-08 04:20 | 240 | 330 | 296 | Pulverizer feeders | F0902B Mill inspection & calibration | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 5.3333 | 1.4545 | 430.5455 | 80.7273 | 81
MC2 | D4 | 42 | 310 | 2016-06-08 23:12 | 2016-06-09 03:16 | 240 | 330 | 296 | Pulverizer mills | F0902A Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 4.0667 | 1.1091 | 328.2909 | 80.7273 | 81
MC2 | D4 | 36 | 250 | 2016-06-09 22:00 | 2016-06-10 04:16 | 240 | 330 | 296 | Pulverizer feeders | F0902D Mill inspection & calibration | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 6.2667 | 1.7091 | 505.8909 | 80.7273 | 81
MC2 | D1 | 37 | 250 | 2016-06-12 21:00 | 2016-06-13 01:59 | 245 | 330 | 296 | Pulverizer feeders | F8102C Coal Feeder Belt | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 4.9833 | 1.2836 | 379.9414 | 76.2424 | 76
MC2 | D1 | 43 | 250 | 2016-06-13 07:46 | 2016-06-13 11:48 | 290 | 330 | 296 | Pulverizer feeders | F8102C Coal Feeder Issue | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 4.0333 | 0.48889 | 144.7111 | 35.8788 | 36
MC2 | NC | 38 | 8010 | 2016-06-15 00:50 | 2016-06-15 04:42 | 0 | 330 | 296 | Crushers/mills | F430Lost feed to limestone crusher, cant make slurry | Mill Creek | Other | Coal | 2 | 2016 | 6 | 3.8667 | 3.8667 | 1144.5333 | 296 | 296
MC2 | D4 | 39 | 310 | 2016-06-19 22:00 | 2016-06-20 02:45 | 240 | 330 | 296 | Pulverizer mills | F090C Mill Inspection | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 4.75 | 1.2955 | 383.4545 | 80.7273 | 81
MC2 | D1 | 40 | 250 | 2016-06-20 02:45 | 2016-06-20 03:16 | 125 | 330 | 296 | Pulverizer feeders | F820Lost 2A/B Feeders | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 0.51667 | 0.32096 | 95.004 | 183.8788 | 184
MC2 | D1 | 41 | 320 | 2016-06-20 03:16 | 2016-06-20 05:04 | 240 | 330 | 296 | Foreign object in Pulverizers mill | F1202C Mill Inspection | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 1.8 | 0.49091 | 145.3091 | 80.7273 | 81
MC2 | D1 | 44 | 3411 | 2016-06-20 16:55 | 2016-06-20 19:00 | 160 | 330 | 296 | Feedwater pump drive - motor | F4902A MDBFP - motor | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 2.0833 | 1.0732 | 317.6768 | 152.4848 | 152
MC2 | D1 | 45 | 3411 | 2016-06-20 19:00 | 2016-06-21 02:10 | 190 | 330 | 296 | Feedwater pump drive - motor | F4902A MDBFP - motor | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 7.1667 | 3.0404 | 899.9596 | 125.5758 | 126
MC2 | D1 | 46 | 3411 | 2016-06-21 02:10 | 2016-06-21 05:30 | 205 | 330 | 296 | Feedwater pump drive - motor | F4902A MDBFP - motor | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 3.3333 | 1.2626 | 373.7374 | 112.1212 | 112
MC2 | D1 | 47 | 3411 | 2016-06-21 05:30 | 2016-06-28 05:54 | 240 | 330 | 296 | Feedwater pump drive - motor | F4902A MDBFP - motor | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 168.4 | 45.9273 | 13594.4727 | 80.7273 | 81
MC2 | D1 | 48 | 95 | 2016-06-28 05:54 | 2016-06-28 06:21 | 204 | 330 | 296 | Bunker flow problems | F1202C Coal Mill Lost (Lack of coal flow from bunker) | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 0.45 | 0.17182 | 50.8582 | 113.0182 | 113
MC2 | D1 | 49 | 3411 | 2016-06-28 06:21 | 2016-07-03 22:37 | 240 | 330 | 296 | Feedwater pump drive - motor | F4902A MDBFP - motor | Mill Creek | Derate | Coal | 2 | 2016 | 6 | 136.2667 | 37.1636 | 11000.4364 | 80.7273 | 81
MC2 | D4 | 50 | 310 | 2016-07-26 23:08 | 2016-07-27 03:58 | 240 | 330 | 296 | Pulverizer mills | F5902B Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 7 | 4.8333 | 1.3182 | 390.1818 | 80.7273 | 81
MC2 | D4 | 51 | 310 | 2016-08-07 22:00 | 2016-08-08 04:01 | 250 | 330 | 296 | Pulverizer mills | F590A Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 6.0167 | 1.4586 | 431.7414 | 71.7576 | 72
MC2 | D4 | 52 | 310 | 2016-08-08 23:04 | 2016-08-09 05:21 | 250 | 330 | 296 | Pulverizer mills | F590C Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 6.2833 | 1.5232 | 450.8768 | 71.7576 | 72
MC2 | NC | 53 | 4490 | 2016-08-09 20:10 | 2016-08-10 01:12 | 0 | 330 | 296 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Heat Rate Testing (various loads) | Mill Creek | Other | Coal | 2 | 2016 | 8 | 5.0333 | 5.0333 | 1489.8667 | 296 | 296
MC2 | D4 | 54 | 310 | 2016-08-10 23:00 | 2016-08-11 04:56 | 240 | 330 | 296 | Pulverizer mills | F590D Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 5.9333 | 1.6182 | 478.9818 | 80.7273 | 81
MC2 | D4 | 55 | 344 | 2016-08-18 22:57 | 2016-08-19 03:57 | 250 | 330 | 296 | Pulverizer inspection | F5902A Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 8 | 5 | 1.2121 | 358.7879 | 71.7576 | 72
MC2 | D4 | 56 | 310 | 2016-09-07 23:00 | 2016-09-08 03:24 | 240 | 330 | 296 | Pulverizer mills | F5302D Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 9 | 4.4 | 1.2 | 355.2 | 80.7273 | 81
MC2 | MO | 57 | 1080 | 2016-09-09 22:23 | 2016-09-11 13:01 | 0 | 330 | 296 | Economizer B | F540Boiler Leak Repair - Economizer | Mill Creek | Maintenance | Coal | 2 | 2016 | 9 | 38.6333 | 38.6333 | 11435.4667 | 296 | 296
MC2 | D1 | 58 | 1850 | 2016-09-11 22:58 | 2016-09-12 07:48 | 280 | 330 | 296 | Boiler water condition (not feedwater water quality) | FA00High Silica - After Startup | Mill Creek | Derate | Coal | 2 | 2016 | 9 | 8.8333 | 1.3384 | 396.1616 | 44.8485 | 45
MC2 | D4 | 59 | 310 | 2016-09-14 23:00 | 2016-09-15 05:34 | 240 | 330 | 296 | Pulverizer mills | F5902A Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 9 | 6.5667 | 1.7909 | 530.1091 | 80.7273 | 81
MC2 | D4 | 60 | 310 | 2016-09-15 23:00 | 2016-09-16 05:49 | 240 | 330 | 296 | Pulverizer mills | F5902A Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 9 | 6.8167 | 1.8591 | 550.2909 | 80.7273 | 81
MC2 | D4 | 61 | 310 | 2016-09-18 23:06 | 2016-09-19 05:08 | 240 | 330 | 296 | Pulverizer mills | F5902C Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 9 | 6.0333 | 1.6455 | 487.0545 | 80.7273 | 81
MC2 | D4 | 62 | 310 | 2016-09-19 23:00 | 2016-09-20 04:39 | 250 | 330 | 296 | Pulverizer mills | F5902D Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 9 | 5.65 | 1.3697 | 405.4303 | 71.7576 | 72
MC2 | MO | 63 | 4609 | 2016-09-30 17:51 | 2016-09-30 20:36 | 0 | 330 | 296 | Other exciter problems | F540Alterex Oil Cooler Gasket Leak - Exciter System | Mill Creek | Maintenance | Coal | 2 | 2016 | 9 | 2.75 | 2.75 | 814 | 296 | 296
MC2 | D4 | 64 | 250 | 2016-10-11 23:00 | 2016-10-12 03:24 | 240 | 330 | 296 | Pulverizer feeders | F5902B Feeder Maintenance | Mill Creek | Derate | Coal | 2 | 2016 | 10 | 4.4 | 1.2 | 355.2 | 80.7273 | 81
MC2 | U1 | 65 | 3220 | 2016-10-22 10:51 | 2016-10-23 10:45 | 0 | 330 | 296 | Circulating water piping | F540Cooling Tower Header Rupture | Mill Creek | Outage | Coal | 2 | 2016 | 10 | 23.9 | 23.9 | 7074.4 | 296 | 296
MC2 | D1 | 66 | 340 | 2016-11-01 18:30 | 2016-11-01 18:55 | 190 | 330 | 296 | Other pulverizer problems | F700Lost B Mill - Breaker Issue | Mill Creek | Derate | Coal | 2 | 2016 | 11 | 0.41667 | 0.17677 | 52.3232 | 125.5758 | 126
MC2 | D1 | 67 | 340 | 2016-11-01 18:55 | 2016-11-01 19:40 | 255 | 330 | 296 | Other pulverizer problems | F700Lost B Mill - Breaker Issue | Mill Creek | Derate | Coal | 2 | 2016 | 11 | 0.75 | 0.17045 | 50.4545 | 67.2727 | 67
MC2 | D1 | 68 | 340 | 2016-11-01 19:40 | 2016-11-02 01:13 | 263 | 330 | 296 | Other pulverizer problems | F700Lost B Mill - Breaker Issue | Mill Creek | Derate | Coal | 2 | 2016 | 11 | 5.55 | 1.1268 | 333.5382 | 60.097 | 60
MC2 | PO | 69 | 1800 | 2016-11-05 00:58 | 2016-12-02 19:42 | 0 | 330 | 296 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | F590Planned Outage | Mill Creek | Other | Coal | 2 | 2016 | 11 | 666.7333 | 666.7333 | 197353.0667 | 296 | 296
MC2 | NC | 70 | 1850 | 2016-12-02 19:42 | 2016-12-05 06:49 | 0 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High silica at cold start-up | Mill Creek | Other | Coal | 2 | 2016 | 12 | 59.1167 | 59.1167 | 17498.5333 | 296 | 296
MC2 | D4 | 1 | 310 | 2017-01-16 23:00 | 2017-01-17 05:09 | 240 | 330 | 296 | Pulverizer mills | F5902A Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 6.15 | 1.6773 | 496.4727 | 80.7273 | 81
MC2 | D4 | 2 | 310 | 2017-01-17 23:20 | 2017-01-18 05:19 | 240 | 330 | 296 | Pulverizer mills | F5902B Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 5.9833 | 1.6318 | 483.0182 | 80.7273 | 81
MC2 | NC | 3 | 8460 | 2017-01-18 22:40 | 2017-01-19 01:35 | 0 | 330 | 296 | Testing A | F790Low Load RATA - 215 MW | Mill Creek | Other | Coal | 2 | 2017 | 1 | 2.9167 | 2.9167 | 863.3333 | 296 | 296
MC2 | D4 | 4 | 310 | 2017-01-20 | 2017-01-20 05:50 | 240 | 330 | 296 | Pulverizer mills | F5902C Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 5.8333 | 1.5909 | 470.9091 | 80.7273 | 81
MC2 | D1 | 5 | 4261 | 2017-01-20 08:00 | 2017-01-20 23:13 | 280 | 330 | 296 | Control valves | F720#4 Control Valve Stuck Closed | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 15.2167 | 2.3056 | 682.4444 | 44.8485 | 45
MC2 | MO | 6 | 4261 | 2017-01-20 23:13 | 2017-01-22 21:34 | 0 | 330 | 296 | Control valves | F540#4 Control Valve Stuck Closed (and WW repair) | Mill Creek | Maintenance | Coal | 2 | 2017 | 1 | 46.35 | 46.35 | 13719.6 | 296 | 296
MC2 | D4 | 7 | 310 | 2017-01-22 23:30 | 2017-01-23 04:05 | 240 | 330 | 296 | Pulverizer mills | F5902D Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 1 | 4.5833 | 1.25 | 370 | 80.7273 | 81
MC2 | NC | 8 | 4490 | 2017-02-02 07:30 | 2017-02-02 13:45 | 0 | 330 | 296 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Full Load Capability Testing | Mill Creek | Other | Coal | 2 | 2017 | 2 | 6.25 | 6.25 | 1850 | 296 | 296
MC2 | D1 | 9 | 1488 | 2017-02-13 21:30 | 2017-02-13 22:07 | 200 | 330 | 296 | Air heater (regenerative) | F7802A Air Heater Guide Bearing Tempeature | Mill Creek | Derate | Coal | 2 | 2017 | 2 | 0.61667 | 0.24293 | 71.9071 | 116.6061 | 117
MC2 | D1 | 10 | 360 | 2017-02-14 08:17 | 2017-02-14 09:13 | 240 | 330 | 296 | Burners | F7802B Coal Mill Burner Tempeature (B4) | Mill Creek | Derate | Coal | 2 | 2017 | 2 | 0.93333 | 0.25455 | 75.3455 | 80.7273 | 81
MC2 | D1 | 11 | 580 | 2017-03-06 02:58 | 2017-03-06 06:35 | 150 | 330 | 296 | Desuperheater/attemperator piping | F540Reheat spray line leak | Mill Creek | Derate | Coal | 2 | 2017 | 3 | 3.6167 | 1.9727 | 583.9273 | 161.4545 | 161
MC2 | NC | 12 | 4490 | 2017-03-06 08:00 | 2017-03-06 13:13 | 0 | 330 | 296 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Full Load Capability Testing | Mill Creek | Other | Coal | 2 | 2017 | 3 | 5.2167 | 5.2167 | 1544.1333 | 296 | 296
MC2 | PO | 13 | 4402 | 2017-04-07 23:10 | 2017-04-24 14:19 | 0 | 330 | 296 | Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | F590Planned Outage - Spring 2017 | Mill Creek | Other | Coal | 2 | 2017 | 4 | 399.15 | 399.15 | 118148.4 | 296 | 296
MC2 | D1 | 14 | 1850 | 2017-04-25 08:19 | 2017-04-25 11:15 | 300 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica - Startup | Mill Creek | Derate | Coal | 2 | 2017 | 4 | 2.9333 | 0.26667 | 78.9333 | 26.9091 | 27
MC2 | D1 | 15 | 3133 | 2017-04-25 11:15 | 2017-04-25 12:09 | 205 | 330 | 296 | Vacuum pumps | F660High Backpressure (Cond. Vac. Pump Operational Issue) | Mill Creek | Derate | Coal | 2 | 2017 | 4 | 0.9 | 0.34091 | 100.9091 | 112.1212 | 112
MC2 | D1 | 16 | 3133 | 2017-04-25 12:09 | 2017-04-25 14:28 | 114 | 330 | 296 | Vacuum pumps | F660High Backpressure (Cond. Vac. Pump Operational Issue) | Mill Creek | Derate | Coal | 2 | 2017 | 4 | 2.3167 | 1.5164 | 448.8436 | 193.7455 | 194
MC2 | D1 | 17 | 580 | 2017-04-26 04:40 | 2017-04-26 08:03 | 225 | 330 | 296 | Desuperheater/attemperator piping | F540RH spray line steam leak at weld | Mill Creek | Derate | Coal | 2 | 2017 | 4 | 3.3833 | 1.0765 | 318.6485 | 94.1818 | 94
MC2 | U1 | 18 | 800 | 2017-04-29 07:44 | 2017-04-29 12:29 | 0 | 330 | 296 | Drums and drum internals (single drum only) | F820Drum Level Trip | Mill Creek | Outage | Coal | 2 | 2017 | 4 | 4.75 | 4.75 | 1406 | 296 | 296
MC2 | D1 | 19 | 1850 | 2017-04-29 17:09 | 2017-04-30 01:40 | 265 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica - Startup | Mill Creek | Derate | Coal | 2 | 2017 | 4 | 8.5167 | 1.6775 | 496.5475 | 58.303 | 58
MC2 | D1 | 20 | 1850 | 2017-04-30 01:40 | 2017-04-30 05:52 | 315 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica - Startup | Mill Creek | Derate | Coal | 2 | 2017 | 4 | 4.2 | 0.19091 | 56.5091 | 13.4545 | 13
MC2 | MO | 21 | 3344 | 2017-05-02 21:20 | 2017-05-03 23:37 | 0 | 330 | 296 | Deaerator (including level control) | F540Deaerator Heater Access Door Repair | Mill Creek | Maintenance | Coal | 2 | 2017 | 5 | 26.2833 | 26.2833 | 7779.8667 | 296 | 296
MC2 | D1 | 22 | 9940 | 2017-05-04 05:35 | 2017-05-04 06:54 | 200 | 330 | 296 | Maintenance procdure error | FP002B BFP Unavailable (LOTO issue) | Mill Creek | Derate | Coal | 2 | 2017 | 5 | 1.3167 | 0.51869 | 153.5313 | 116.6061 | 117
MC2 | D1 | 23 | 4499 | 2017-06-03 13:27 | 2017-06-04 11:45 | 280 | 330 | 296 | Other miscellaneous steam turbine problems | F660Steam/Feedwater Flow Differential Running High | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 22.3 | 3.3788 | 1000.1212 | 44.8485 | 45
MC2 | D1 | 24 | 4099 | 2017-06-04 11:45 | 2017-06-05 13:37 | 320 | 330 | 296 | Other high pressure turbine problems | F660Steam/Feedwater Flow Differential Running High | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 25.8667 | 0.78384 | 232.0162 | 8.9697 | 9
MC2 | D1 | 25 | 4099 | 2017-06-05 13:37 | 2017-06-06 06:17 | 310 | 330 | 296 | Other high pressure turbine problems | F660Steam/Feedwater Flow Differential Running High | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 16.6667 | 1.0101 | 298.9899 | 17.9394 | 18
MC2 | D4 | 26 | 4266 | 2017-06-06 06:17 | 2017-06-06 07:20 | 65 | 330 | 296 | Main stop valve testing | F790Valve Testing | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 1.05 | 0.84318 | 249.5818 | 237.697 | 238
MC2 | D1 | 27 | 4099 | 2017-06-06 07:20 | 2017-06-06 09:40 | 310 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction (Under Investigation) | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 2.3333 | 0.14141 | 41.8586 | 17.9394 | 18
MC2 | D1 | 28 | 4099 | 2017-06-07 07:20 | 2017-06-07 08:30 | 320 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction (Under Investigation) | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 1.1667 | 0.035354 | 10.4646 | 8.9697 | 9
MC2 | D1 | 29 | 4099 | 2017-06-07 08:30 | 2017-06-13 23:04 | 310 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 158.5667 | 9.6101 | 2844.5899 | 17.9394 | 18
MC2 | D4 | 30 | 310 | 2017-06-13 23:04 | 2017-06-14 02:05 | 240 | 330 | 296 | Pulverizer mills | F5902A Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 3.0167 | 0.82273 | 243.5273 | 80.7273 | 81
MC2 | D1 | 31 | 4099 | 2017-06-14 02:05 | 2017-06-18 09:24 | 310 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 103.3167 | 6.2616 | 1853.4384 | 17.9394 | 18
MC2 | D1 | 32 | 250 | 2017-06-18 09:24 | 2017-06-18 12:01 | 235 | 330 | 296 | Pulverizer feeders | F1202B Mill Feeder Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 2.6167 | 0.75328 | 222.9717 | 85.2121 | 85
MC2 | D1 | 33 | 4099 | 2017-06-18 12:01 | 2017-06-21 11:47 | 310 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 71.7667 | 4.3495 | 1287.4505 | 17.9394 | 18
MC2 | D1 | 34 | 4099 | 2017-06-21 11:47 | 2017-06-22 14:10 | 315 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 26.3833 | 1.1992 | 354.9758 | 13.4545 | 13
MC2 | D1 | 35 | 4099 | 2017-06-22 14:10 | 2017-06-22 23:00 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 8.8333 | 0.29444 | 87.1556 | 9.8667 | 10
MC2 | D4 | 36 | 310 | 2017-06-22 23:00 | 2017-06-23 04:05 | 240 | 330 | 296 | Pulverizer mills | F5902A Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 5.0833 | 1.3864 | 410.3636 | 80.7273 | 81
MC2 | D1 | 37 | 4099 | 2017-06-23 04:05 | 2017-06-25 23:00 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 66.9167 | 2.2306 | 660.2444 | 9.8667 | 10
MC2 | D4 | 38 | 310 | 2017-06-25 23:00 | 2017-06-26 04:12 | 240 | 330 | 296 | Pulverizer mills | F5902B Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 5.2 | 1.4182 | 419.7818 | 80.7273 | 81
MC2 | D1 | 39 | 4099 | 2017-06-26 04:12 | 2017-06-26 23:00 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 18.8 | 0.62667 | 185.4933 | 9.8667 | 10
MC2 | D4 | 40 | 310 | 2017-06-26 23:00 | 2017-06-27 04:00 | 240 | 330 | 296 | Pulverizer mills | F5902C Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 5 | 1.3636 | 403.6364 | 80.7273 | 81
MC2 | D1 | 41 | 4099 | 2017-06-27 04:00 | 2017-06-27 23:00 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 19 | 0.63333 | 187.4667 | 9.8667 | 10
MC2 | D4 | 42 | 310 | 2017-06-27 23:00 | 2017-06-28 04:02 | 240 | 330 | 296 | Pulverizer mills | F5902D Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 5.0333 | 1.3727 | 406.3273 | 80.7273 | 81
MC2 | D1 | 43 | 4099 | 2017-06-28 04:02 | 2017-07-07 12:09 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 6 | 224.1167 | 7.4706 | 2211.2844 | 9.8667 | 10
MC2 | D1 | 44 | 250 | 2017-07-07 12:09 | 2017-07-07 15:48 | 250 | 330 | 296 | Pulverizer feeders | F8102A Feeder Belt | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 3.65 | 0.88485 | 261.9152 | 71.7576 | 72
MC2 | D1 | 45 | 4099 | 2017-07-07 15:48 | 2017-07-13 22:23 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 150.5833 | 5.0194 | 1485.7556 | 9.8667 | 10
MC2 | D1 | 46 | 270 | 2017-07-13 22:23 | 2017-07-14 04:10 | 245 | 330 | 296 | Primary air duct and dampers | F5202D Mill Maintenance - Bad PV on Hot Air Gate | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 5.7833 | 1.4896 | 440.9354 | 76.2424 | 76
MC2 | D1 | 47 | 4099 | 2017-07-14 04:10 | 2017-07-21 17:49 | 319 | 330 | 296 | Other high pressure turbine problems | F660'HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 181.65 | 6.055 | 1792.28 | 9.8667 | 10
MC2 | D1 | 48 | 3620 | 2017-07-21 17:49 | 2017-07-21 19:15 | 245 | 330 | 296 | Main transformer | F700'2A Main Transformer Cooling Fan & Oil Pump - Replaced Breaker | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 1.4333 | 0.36919 | 109.2808 | 76.2424 | 76
MC2 | D1 | 49 | 4099 | 2017-07-21 19:15 | 2017-07-24 07:52 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 60.6167 | 2.0206 | 598.0844 | 9.8667 | 10
MC2 | U1 | 50 | 9930 | 2017-07-24 07:52 | 2017-07-24 09:07 | 0 | 330 | 296 | Operating procedure error | F820Tripped - Steam/Feedwater Flow | Mill Creek | Outage | Coal | 2 | 2017 | 7 | 1.25 | 1.25 | 370 | 296 | 296
MC2 | D1 | 51 | 4099 | 2017-07-24 09:07 | 2017-07-24 13:17 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 4.1667 | 0.13889 | 41.1111 | 9.8667 | 10
MC2 | D1 | 52 | 4099 | 2017-07-24 13:17 | 2017-07-24 20:59 | 308 | 330 | 296 | Other high pressure turbine problems | F660'HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 7.7 | 0.51333 | 151.9467 | 19.7333 | 20
MC2 | D1 | 53 | 4099 | 2017-07-24 20:59 | 2017-07-24 22:00 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 1.0167 | 0.033889 | 10.0311 | 9.8667 | 10
MC2 | D4 | 54 | 310 | 2017-07-24 22:00 | 2017-07-25 03:55 | 240 | 330 | 296 | Pulverizer mills | F5902A Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 5.9167 | 1.6136 | 477.6364 | 80.7273 | 81
MC2 | D1 | 55 | 4099 | 2017-07-25 03:55 | 2017-07-25 23:00 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 19.0833 | 0.63611 | 188.2889 | 9.8667 | 10
MC2 | D4 | 56 | 310 | 2017-07-25 23:00 | 2017-07-26 04:16 | 250 | 330 | 296 | Pulverizer mills | F5902B Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 5.2667 | 1.2768 | 377.9232 | 71.7576 | 72
MC2 | D1 | 57 | 4099 | 2017-07-26 04:16 | 2017-07-28 22:00 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 65.7333 | 2.1911 | 648.5689 | 9.8667 | 10
MC2 | D4 | 58 | 8620 | 2017-07-28 22:00 | 2017-07-29 00:35 | 125 | 330 | 296 | Mercury Abatement Equipment | F610FGD Controls - Nalco System Installation | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 2.5833 | 1.6048 | 475.0202 | 183.8788 | 184
MC2 | D1 | 59 | 4099 | 2017-07-29 00:35 | 2017-07-30 22:00 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 45.4167 | 1.5139 | 448.1111 | 9.8667 | 10
MC2 | D4 | 60 | 310 | 2017-07-30 22:00 | 2017-07-31 03:57 | 250 | 330 | 296 | Pulverizer mills | F5902C Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 5.95 | 1.4424 | 426.9576 | 71.7576 | 72
MC2 | D1 | 61 | 4099 | 2017-07-31 03:57 | 2017-07-31 22:00 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 18.05 | 0.60167 | 178.0933 | 9.8667 | 10
MC2 | D4 | 62 | 310 | 2017-07-31 22:00 | 2017-08-01 03:47 | 250 | 330 | 296 | Pulverizer mills | F5902C Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 7 | 5.7833 | 1.402 | 414.998 | 71.7576 | 72
MC2 | D1 | 63 | 4099 | 2017-08-01 03:47 | 2017-08-08 08:27 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 172.6667 | 5.7556 | 1703.6444 | 9.8667 | 10
MC2 | D1 | 64 | 255 | 2017-08-08 08:27 | 2017-08-08 10:42 | 250 | 330 | 296 | Pulverizer feeder coal scales | F5202C Mill Feeder - No Coal Flow Indication Caused By Debris | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 2.25 | 0.54545 | 161.4545 | 71.7576 | 72
MC2 | D1 | 65 | 4099 | 2017-08-08 10:42 | 2017-08-19 00:27 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 253.75 | 8.4583 | 2503.6667 | 9.8667 | 10
MC2 | D1 | 66 | 4099 | 2017-08-19 00:27 | 2017-08-19 02:24 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction (Also Low Load VAR Testing) | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 1.95 | 0.065 | 19.24 | 9.8667 | 10
MC2 | D1 | 67 | 4099 | 2017-08-19 02:24 | 2017-08-22 22:00 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 91.6 | 3.0533 | 903.7867 | 9.8667 | 10
MC2 | D4 | 68 | 310 | 2017-08-22 22:00 | 2017-08-23 00:39 | 240 | 330 | 296 | Pulverizer mills | F5902C Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 2.65 | 0.72273 | 213.9273 | 80.7273 | 81
MC2 | D1 | 69 | 4099 | 2017-08-23 00:39 | 2017-08-24 22:00 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 45.35 | 1.5117 | 447.4533 | 9.8667 | 10
MC2 | D4 | 70 | 310 | 2017-08-24 22:00 | 2017-08-25 01:51 | 240 | 330 | 296 | Pulverizer mills | F5902C Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 3.85 | 1.05 | 310.8 | 80.7273 | 81
MC2 | D1 | 71 | 4099 | 2017-08-25 01:51 | 2017-08-29 04:02 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction (OPEN) | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 98.1833 | 3.2728 | 968.7422 | 9.8667 | 10
MC2 | U1 | 72 | 250 | 2017-08-29 04:02 | 2017-08-29 04:59 | 0 | 330 | 296 | Pulverizer feeders | F820Loss of Flame - Debris in Coal Feeder | Mill Creek | Outage | Coal | 2 | 2017 | 8 | 0.95 | 0.95 | 281.2 | 296 | 296
MC2 | D1 | 73 | 250 | 2017-08-29 05:53 | 2017-08-29 13:03 | 175 | 330 | 296 | Pulverizer feeders | F1202B Mill Plugged W/Debris & C Mill Unavailable | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 7.1667 | 3.3662 | 996.3838 | 139.0303 | 139
MC2 | D1 | 74 | 4099 | 2017-08-29 13:03 | 2017-08-30 22:51 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 33.8 | 1.1267 | 333.4933 | 9.8667 | 10
MC2 | D4 | 75 | 310 | 2017-08-30 22:51 | 2017-08-31 04:24 | 240 | 330 | 296 | Pulverizer mills | F5902B Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 5.55 | 1.5136 | 448.0364 | 80.7273 | 81
MC2 | D1 | 76 | 4099 | 2017-08-31 04:24 | 2017-09-05 21:27 | 319 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 8 | 137.05 | 4.5683 | 1352.2267 | 9.8667 | 10
MC2 | D1 | 78 | 4099 | 2017-09-05 21:27 | 2017-09-15 00:38 | 319 | 330 | 296 | Other high pressure turbine problems | F660Reserve Shutdown (With 11MW Derate Due To HP Turbine) - D1 Hours | Mill Creek | Derate | Coal | 2 | 2017 | 9 | 219.1833 | 7.3061 | 2162.6089 | 9.8667 | 10
MC2 | D1 | 79 | 4099 | 2017-09-15 00:38 | 2017-09-15 15:23 | 317 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 9 | 14.75 | 0.58106 | 171.9939 | 11.6606 | 12
MC2 | D1 | 80 | 4099 | 2017-09-15 15:23 | 2017-09-24 12:08 | 320 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 9 | 212.75 | 6.447 | 1908.303 | 8.9697 | 9
MC2 | D1 | 81 | 270 | 2017-09-24 12:08 | 2017-09-24 12:55 | 250 | 330 | 296 | Primary air duct and dampers | F3402A Mill Hot Air Gate Damper | Mill Creek | Derate | Coal | 2 | 2017 | 9 | 0.78333 | 0.1899 | 56.2101 | 71.7576 | 72
MC2 | D1 | 82 | 4099 | 2017-09-24 12:55 | 2017-10-09 16:32 | 320 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 9 | 363.6167 | 11.0187 | 3261.5313 | 8.9697 | 9
MC2 | D1 | 83 | 4099 | 2017-10-09 16:32 | 2017-10-10 13:48 | 310 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 21.2667 | 1.2889 | 381.5111 | 17.9394 | 18
MC2 | D1 | 84 | 4099 | 2017-10-10 13:48 | 2017-10-14 23:43 | 320 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 105.9167 | 3.2096 | 950.0404 | 8.9697 | 9
MC2 | D1 | 85 | 250 | 2017-10-14 23:43 | 2017-10-14 23:58 | 250 | 330 | 296 | Pulverizer feeders | F1202B Feeder - Coal Flow - Silo Pipe Plugged | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 0.25 | 0.060606 | 17.9394 | 71.7576 | 72
MC2 | D1 | 86 | 4099 | 2017-10-14 23:58 | 2017-10-23 22:25 | 320 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 214.45 | 6.4985 | 1923.5515 | 8.9697 | 9
MC2 | D4 | 87 | 310 | 2017-10-23 22:25 | 2017-10-24 03:46 | 240 | 330 | 296 | Pulverizer mills | F5902D Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 5.35 | 1.4591 | 431.8909 | 80.7273 | 81
MC2 | D1 | 88 | 4099 | 2017-10-24 03:46 | 2017-10-26 10:26 | 320 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 54.6667 | 1.6566 | 490.3434 | 8.9697 | 9
MC2 | D1 | 89 | 4099 | 2017-10-26 10:26 | 2017-10-26 14:52 | 323 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 4.4333 | 0.09404 | 27.836 | 6.2788 | 6
MC2 | D1 | 90 | 310 | 2017-10-26 14:52 | 2017-10-26 17:05 | 250 | 330 | 296 | Pulverizer mills | F7802C Coal Mill - High Temperature | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 2.2167 | 0.53737 | 159.0626 | 71.7576 | 72
MC2 | D1 | 91 | 4099 | 2017-10-26 17:05 | 2017-10-26 17:40 | 320 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 0.58333 | 0.017677 | 5.2323 | 8.9697 | 9
MC2 | D1 | 92 | 4099 | 2017-10-26 17:40 | 2017-11-01 | 324 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction (SPLITTING EVENT AT EOM, CARRIED TO EVENT 116) | Mill Creek | Derate | Coal | 2 | 2017 | 10 | 126.3333 | 2.297 | 679.903 | 5.3818 | 5
MC2 | D1 | 116 | 4099 | 2017-11-01 | 2017-11-14 22:00 | 324 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction (SPLITTING EVENT AT EOM, CARRIED FROM EVENT 92) | Mill Creek | Derate | Coal | 2 | 2017 | 11 | 334 | 6.0727 | 1797.5273 | 5.3818 | 5
MC2 | D1 | 93 | 1190 | 2017-11-14 22:00 | 2017-11-15 03:50 | 240 | 330 | 296 | Other tube slagging or fouling | FS00Deslag | Mill Creek | Derate | Coal | 2 | 2017 | 11 | 5.8333 | 1.5909 | 470.9091 | 80.7273 | 81
MC2 | D1 | 94 | 4099 | 2017-11-15 03:50 | 2017-11-15 21:30 | 324 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 11 | 17.6667 | 0.32121 | 95.0788 | 5.3818 | 5
MC2 | D1 | 95 | 1190 | 2017-11-15 21:30 | 2017-11-16 03:00 | 140 | 330 | 296 | Other tube slagging or fouling | FS00Deslag | Mill Creek | Derate | Coal | 2 | 2017 | 11 | 5.5 | 3.1667 | 937.3333 | 170.4242 | 170
MC2 | D1 | 96 | 4099 | 2017-11-16 03:00 | 2017-12-01 | 324 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 11 | 357 | 6.4909 | 1921.3091 | 5.3818 | 5
MC2 | D1 | 97 | 4099 | 2017-12-01 | 2017-12-03 23:00 | 324 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 71 | 1.2909 | 382.1091 | 5.3818 | 5
MC2 | D4 | 98 | 310 | 2017-12-03 23:00 | 2017-12-04 04:13 | 250 | 330 | 296 | Pulverizer mills | F5902D Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 5.2167 | 1.2646 | 374.3354 | 71.7576 | 72
MC2 | D1 | 99 | 4099 | 2017-12-04 04:13 | 2017-12-04 22:00 | 324 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 17.7833 | 0.32333 | 95.7067 | 5.3818 | 5
MC2 | D4 | 100 | 310 | 2017-12-04 22:00 | 2017-12-05 04:01 | 250 | 330 | 296 | Pulverizer mills | F5902C Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 6.0167 | 1.4586 | 431.7414 | 71.7576 | 72
MC2 | D1 | 102 | 4099 | 2017-12-05 06:15 | 2017-12-05 13:20 | 324 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 7.0833 | 0.12879 | 38.1212 | 5.3818 | 5
MC2 | NC | 103 | 4842 | 2017-12-05 13:20 | 2017-12-05 13:46 | 0 | 330 | 296 | Reactive and capability testing | F790MOD 26 Testing - Out of AGC | Mill Creek | Other | Coal | 2 | 2017 | 12 | 0.43333 | 0.43333 | 128.2667 | 296 | 296
MC2 | D1 | 104 | 4099 | 2017-12-05 13:46 | 2017-12-05 23:00 | 324 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 9.2333 | 0.16788 | 49.6921 | 5.3818 | 5
MC2 | D4 | 105 | 310 | 2017-12-05 23:00 | 2017-12-06 05:00 | 250 | 330 | 296 | Pulverizer mills | F5902B Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 6 | 1.4545 | 430.5455 | 71.7576 | 72
MC2 | D1 | 107 | 4099 | 2017-12-06 06:35 | 2017-12-06 22:41 | 324 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 16.1 | 0.29273 | 86.6473 | 5.3818 | 5
MC2 | D4 | 108 | 310 | 2017-12-06 22:41 | 2017-12-07 03:53 | 250 | 330 | 296 | Pulverizer mills | F5902B Mill Maintenance & Feeder Calibration | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 5.2 | 1.2606 | 373.1394 | 71.7576 | 72
MC2 | D1 | 109 | 4099 | 2017-12-07 03:53 | 2017-12-07 22:00 | 324 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 18.1167 | 0.32939 | 97.5006 | 5.3818 | 5
MC2 | D4 | 110 | 310 | 2017-12-07 22:00 | 2017-12-08 03:05 | 250 | 330 | 296 | Pulverizer mills | F5902A Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 5.0833 | 1.2323 | 364.7677 | 71.7576 | 72
MC2 | D1 | 111 | 4099 | 2017-12-08 03:05 | 2017-12-08 09:34 | 324 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 6.4833 | 0.11788 | 34.8921 | 5.3818 | 5
MC2 | D1 | 112 | 4099 | 2017-12-08 09:34 | 2017-12-08 13:00 | 316 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 3.4333 | 0.14566 | 43.1143 | 12.5576 | 13
MC2 | D1 | 113 | 4099 | 2017-12-08 13:00 | 2017-12-11 22:00 | 318 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 81 | 2.9455 | 871.8545 | 10.7636 | 11
MC2 | NC | 114 | 8460 | 2017-12-11 22:00 | 2017-12-12 05:30 | 0 | 330 | 296 | Testing A | F790Mercury Testing | Mill Creek | Other | Coal | 2 | 2017 | 12 | 7.5 | 7.5 | 2220 | 296 | 296
MC2 | D1 | 115 | 4099 | 2017-12-12 05:30 | 2017-12-19 23:00 | 318 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 185.5 | 6.7455 | 1996.6545 | 10.7636 | 11
MC2 | D4 | 117 | 310 | 2017-12-19 23:00 | 2017-12-20 04:01 | 240 | 330 | 296 | Pulverizer mills | F5902B Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 5.0167 | 1.3682 | 404.9818 | 80.7273 | 81
MC2 | D1 | 119 | 4099 | 2017-12-20 04:18 | 2017-12-31 11:30 | 318 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 271.2 | 9.8618 | 2919.0982 | 10.7636 | 11
MC2 | NC | 120 | 1190 | 2017-12-31 11:30 | 2017-12-31 15:45 | 0 | 330 | 296 | Other tube slagging or fouling | FS00Deslag | Mill Creek | Other | Coal | 2 | 2017 | 12 | 4.25 | 4.25 | 1258 | 296 | 296
MC2 | D1 | 121 | 4099 | 2017-12-31 15:45 | 2018-01-01 | 318 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction (YEAR END - CARRYING OVER TO EVENT 1-2018) | Mill Creek | Derate | Coal | 2 | 2017 | 12 | 8.25 | 0.3 | 88.8 | 10.7636 | 11
MC2 | D1 | 1 | 4099 | 2018-01-01 | 2018-01-01 11:32 | 318 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction (YEAR START - CARRYING OVER TO EVENT 121-2017) | Mill Creek | Derate | Coal | 2 | 2018 | 1 | 11.5333 | 0.41939 | 124.1406 | 10.7636 | 11
MC2 | NC | 2 | 8020 | 2018-01-01 11:32 | 2018-01-02 06:35 | 0 | 330 | 296 | Mill slurry tanks supply problems | F930Limestone Slurry Levels | Mill Creek | Other | Coal | 2 | 2018 | 1 | 19.05 | 19.05 | 5638.8 | 296 | 296
MC2 | D1 | 3 | 4099 | 2018-01-02 06:35 | 2018-02-01 | 318 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction (ENDED AND STARTED EVENT 4) | Mill Creek | Derate | Coal | 2 | 2018 | 1 | 713.4167 | 25.9424 | 7678.9576 | 10.7636 | 11
MC2 | D1 | 4 | 4099 | 2018-02-01 | 2018-02-12 23:45 | 318 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2018 | 2 | 287.75 | 10.4636 | 3097.2364 | 10.7636 | 11
MC2 | D4 | 5 | 310 | 2018-02-12 23:45 | 2018-02-13 03:38 | 240 | 330 | 296 | Pulverizer mills | F5302B Coal Mill Inspection | Mill Creek | Derate | Coal | 2 | 2018 | 2 | 3.8833 | 1.0591 | 313.4909 | 80.7273 | 81
MC2 | D1 | 6 | 4099 | 2018-02-13 03:38 | 2018-02-19 10:23 | 318 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2018 | 2 | 150.75 | 5.4818 | 1622.6182 | 10.7636 | 11
MC2 | U1 | 7 | 3211 | 2018-02-19 10:23 | 2018-02-20 15:03 | 0 | 330 | 296 | Circulating water pump motors | F8204KV Under Voltage - Lost Both Cooling Tower Pumps (Electrical) | Mill Creek | Outage | Coal | 2 | 2018 | 2 | 28.6667 | 28.6667 | 8485.3333 | 296 | 296
MC2 | D1 | 8 | 1850 | 2018-02-20 21:03 | 2018-02-20 23:43 | 240 | 330 | 296 | Boiler water condition (not feedwater water quality) | F170High Silica - Startup | Mill Creek | Derate | Coal | 2 | 2018 | 2 | 2.6667 | 0.72727 | 215.2727 | 80.7273 | 81
MC2 | D1 | 9 | 4099 | 2018-02-20 23:43 | 2018-02-22 00:18 | 318 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2018 | 2 | 24.5833 | 0.89394 | 264.6061 | 10.7636 | 11
MC2 | D4 | 10 | 310 | 2018-02-22 00:18 | 2018-02-22 00:29 | 240 | 330 | 296 | Pulverizer mills | F5902A Coal Mill Maintenance | Mill Creek | Derate | Coal | 2 | 2018 | 2 | 0.18333 | 0.05 | 14.8 | 80.7273 | 81
MC2 | D1 | 11 | 4099 | 2018-02-22 00:29 | 2018-03-01 | 318 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction (CLOSED FOR EOM, STARTED EVENT 12) | Mill Creek | Derate | Coal | 2 | 2018 | 2 | 167.5167 | 6.0915 | 1803.0885 | 10.7636 | 11
MC2 | D1 | 12 | 4099 | 2018-03-01 | 2018-03-01 23:02 | 318 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2018 | 3 | 23.0333 | 0.83758 | 247.9224 | 10.7636 | 11
MC2 | D4 | 13 | 250 | 2018-03-01 23:02 | 2018-03-02 04:28 | 235 | 330 | 296 | Pulverizer feeders | F5902C Coal Feeder Inspection | Mill Creek | Derate | Coal | 2 | 2018 | 3 | 5.4333 | 1.5641 | 462.9859 | 85.2121 | 85
MC2 | D1 | 14 | 4099 | 2018-03-02 04:28 | 2018-03-09 22:37 | 318 | 330 | 296 | Other high pressure turbine problems | F660HP Turbine Restriction | Mill Creek | Derate | Coal | 2 | 2018 | 3 | 186.15 | 6.7691 | 2003.6509 | 10.7636 | 11
MC3 | D4 | 1 | 876 | 2013-01-02 23:30 | 2013-01-03 06:37 | 280 | 423 | 393 | Soot blower controls | F590Sootblower Regulator - Repair | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 7.1167 | 2.4059 | 945.5072 | 132.8582 | 133
MC3 | D1 | 2 | 310 | 2013-01-06 20:30 | 2013-01-06 22:10 | 325 | 423 | 393 | Pulverizer mills | F4003C Coal Mill - Low Primary Air Flow | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 1.6667 | 0.38613 | 151.7494 | 91.0496 | 91
MC3 | D1 | 3 | 250 | 2013-01-06 23:20 | 2013-01-07 04:25 | 325 | 423 | 393 | Pulverizer feeders | F5903B Coal Feeder - Replace Belt & Inspect Hot Air Damper | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 5.0833 | 1.1777 | 462.8357 | 91.0496 | 91
MC3 | D1 | 4 | 250 | 2013-01-07 02:20 | 2013-01-07 04:25 | 240 | 423 | 393 | Pulverizer feeders | F1203A Coal Feeder - Rock on Belt | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 2.0833 | 0.9013 | 354.211 | 170.0213 | 170
MC3 | D1 | 5 | 250 | 2013-01-08 16:14 | 2013-01-08 16:50 | 333 | 423 | 393 | Pulverizer feeders | F8203A Coal Feeder - Trip | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 0.6 | 0.12766 | 50.1702 | 83.617 | 84
MC3 | D1 | 6 | 9270 | 2013-01-14 08:00 | 2013-01-14 13:10 | 350 | 423 | 393 | Wet coal | FW00Wet Coal Issues | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 5.1667 | 0.89165 | 350.4173 | 67.8227 | 68
MC3 | D1 | 7 | 1710 | 2013-01-15 06:00 | 2013-01-15 07:28 | 412 | 423 | 393 | Combustion/steam condition controls (report local controls --- burners | F400Air Flow Issues | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 1.4667 | 0.03814 | 14.9891 | 10.2199 | 10
MC3 | D1 | 8 | 1710 | 2013-01-15 07:28 | 2013-01-15 16:35 | 400 | 423 | 393 | Combustion/steam condition controls (report local controls --- burners | F400Air Flow Issues | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 9.1167 | 0.49571 | 194.8122 | 21.3688 | 21
MC3 | D1 | 9 | 280 | 2013-01-15 14:31 | 2013-01-15 16:35 | 300 | 423 | 393 | Pulverizer fires | F0703B Coal Mill - Fire & Inspection | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 2.0667 | 0.60095 | 236.1716 | 114.2766 | 114
MC3 | D1 | 10 | 1710 | 2013-01-15 16:35 | 2013-01-16 05:10 | 393 | 423 | 393 | Combustion/steam condition controls (report local controls --- burners | F400Air Flow Issues | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 12.5833 | 0.89243 | 350.727 | 27.8723 | 28
MC3 | D1 | 11 | 9270 | 2013-01-16 05:10 | 2013-01-16 08:28 | 320 | 423 | 393 | Wet coal | FW00Wet Coal Issues | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 3.3 | 0.80355 | 315.7936 | 95.695 | 96
MC3 | D1 | 12 | 310 | 2013-01-21 10:00 | 2013-01-21 12:49 | 315 | 423 | 393 | Pulverizer mills | F5903D Coal Mill - Primary Air Fan Damper Inspection, Clean Pitot Tubes and Repair Coa | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 2.8167 | 0.71915 | 282.6255 | 100.3404 | 100
MC3 | D4 | 13 | 310 | 2013-01-31 12:25 | 2013-01-31 15:30 | 320 | 423 | 393 | Pulverizer mills | F5303A Coal Mill Primary Air Fan - Damper Inspection | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 3.0833 | 0.75079 | 295.0597 | 95.695 | 96
MC3 | U1 | 14 | 1040 | 2013-02-06 23:56 | 2013-02-08 23:32 | 0 | 423 | 393 | First superheater B | F540Boiler Tube Leak - First Superheater | Mill Creek | Outage | Coal | 3 | 2013 | 2 | 47.6 | 47.6 | 18706.8 | 393 | 393
MC3 | NC | 15 | 1850 | 2013-02-08 23:32 | 2013-02-09 13:10 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2013 | 2 | 13.6333 | 13.6333 | 5357.9 | 393 | 393
MC3 | U1 | 16 | 1050 | 2013-02-10 05:33 | 2013-02-11 16:45 | 0 | 423 | 393 | Second superheater B | F540Boiler Tube Leak - Second Superheater | Mill Creek | Outage | Coal | 3 | 2013 | 2 | 35.2 | 35.2 | 13833.6 | 393 | 393
MC3 | NC | 17 | 1850 | 2013-02-11 16:45 | 2013-02-12 04:45 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 2 | 12 | 12 | 4716 | 393 | 393
MC3 | U1 | 18 | 3235 | 2013-02-14 03:30 | 2013-02-14 06:42 | 0 | 423 | 393 | Cooling tower booster pump | F8203A Cooling Tower Pump - Trip, Water in E-Stop Button | Mill Creek | Outage | Coal | 3 | 2013 | 2 | 3.2 | 3.2 | 1257.6 | 393 | 393
MC3 | NC | 19 | 1850 | 2013-02-14 06:42 | 2013-02-14 13:04 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 2 | 6.3667 | 6.3667 | 2502.1 | 393 | 393
MC3 | U1 | 20 | 1799 | 2013-02-16 16:24 | 2013-02-16 21:33 | 0 | 423 | 393 | Other boiler instrumentation and control problems | F400HPM Power Loss - Boiler Controls | Mill Creek | Outage | Coal | 3 | 2013 | 2 | 5.15 | 5.15 | 2023.95 | 393 | 393
MC3 | NC | 21 | 1850 | 2013-02-16 21:33 | 2013-02-16 21:49 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 2 | 0.26667 | 0.26667 | 104.8 | 393 | 393
MC3 | U1 | 22 | 800 | 2013-02-16 21:49 | 2013-02-16 23:03 | 0 | 423 | 393 | Drums and drum internals (single drum only) | F420Low Drum Level Trip - Operator Error | Mill Creek | Outage | Coal | 3 | 2013 | 2 | 1.2333 | 1.2333 | 484.7 | 393 | 393
MC3 | NC | 23 | 1850 | 2013-02-16 23:03 | 2013-02-17 04:50 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 2 | 5.7833 | 5.7833 | 2272.85 | 393 | 393
MC3 | D4 | 24 | 267 | 2013-02-25 23:00 | 2013-02-26 02:43 | 325 | 423 | 393 | Primary air flow instrumentation | F1203C Coal Mill PA fan - cleaned pitot tubes. | Mill Creek | Derate | Coal | 3 | 2013 | 2 | 3.7167 | 0.86107 | 338.4012 | 91.0496 | 91
MC3 | D4 | 25 | 264 | 2013-02-26 23:00 | 2013-02-27 01:15 | 325 | 423 | 393 | Other primary air fan problems | F7803D Mill Maintenance - checked stator temperature on PA Fan. | Mill Creek | Derate | Coal | 3 | 2013 | 2 | 2.25 | 0.52128 | 204.8617 | 91.0496 | 91
MC3 | PO | 26 | 1801 | 2013-03-01 23:23 | 2013-03-11 06:23 | 0 | 423 | 393 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Planned Outage | Mill Creek | Other | Coal | 3 | 2013 | 3 | 223 | 223 | 87639 | 393 | 393
MC3 | NC | 27 | 1850 | 2013-03-11 06:23 | 2013-03-11 23:13 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 3 | 2013 | 3 | 16.8333 | 16.8333 | 6615.5 | 393 | 393
MC3 | U1 | 28 | 3620 | 2013-03-12 10:20 | 2013-03-12 13:26 | 0 | 423 | 393 | Main transformer | F8203-1 Main Aux Transformer - Sudden Pressure Relay Trip | Mill Creek | Outage | Coal | 3 | 2013 | 3 | 3.1 | 3.1 | 1218.3 | 393 | 393
MC3 | NC | 29 | 1850 | 2013-03-12 13:26 | 2013-03-12 20:40 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 3 | 7.2333 | 7.2333 | 2842.7 | 393 | 393
MC3 | D4 | 30 | 310 | 2013-03-12 23:00 | 2013-03-13 03:00 | 325 | 423 | 393 | Pulverizer mills | F5903B Coal Mill - Repair Coal Leak | Mill Creek | Derate | Coal | 3 | 2013 | 3 | 4 | 0.92671 | 364.1986 | 91.0496 | 91
MC3 | D1 | 31 | 876 | 2013-03-13 22:00 | 2013-03-14 04:30 | 325 | 423 | 393 | Soot blower controls | F590Sootblower Regulator Repair | Mill Creek | Derate | Coal | 3 | 2013 | 3 | 6.5 | 1.5059 | 591.8227 | 91.0496 | 91
MC3 | D1 | 32 | 876 | 2013-03-14 04:30 | 2013-03-14 07:45 | 315 | 423 | 393 | Soot blower controls | F590Sootblower Regulator Repair | Mill Creek | Derate | Coal | 3 | 2013 | 3 | 3.25 | 0.82979 | 326.1064 | 100.3404 | 100
MC3 | D1 | 33 | 876 | 2013-03-14 07:45 | 2013-03-14 12:42 | 300 | 423 | 393 | Soot blower controls | F590Sootblower Regulator Repair | Mill Creek | Derate | Coal | 3 | 2013 | 3 | 4.95 | 1.4394 | 565.6691 | 114.2766 | 114
MC3 | U1 | 34 | 3235 | 2013-03-26 02:29 | 2013-03-26 07:36 | 0 | 423 | 393 | Cooling tower booster pump | F8203B Cooling Tower Pump - Trip | Mill Creek | Outage | Coal | 3 | 2013 | 3 | 5.1167 | 5.1167 | 2010.85 | 393 | 393
MC3 | NC | 35 | 1850 | 2013-03-26 07:36 | 2013-03-26 16:05 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 3 | 8.4833 | 8.4833 | 3333.95 | 393 | 393
MC3 | D4 | 36 | 310 | 2013-04-01 20:30 | 2013-04-02 02:40 | 280 | 423 | 393 | Pulverizer mills | F5303A Coal Mill - Inspection | Mill Creek | Derate | Coal | 3 | 2013 | 4 | 6.1667 | 2.0847 | 819.292 | 132.8582 | 133
MC3 | D1 | 37 | 310 | 2013-04-02 13:00 | 2013-04-02 15:33 | 330 | 423 | 393 | Pulverizer mills | F0503A Coal Mill - Trouble with rollers | Mill Creek | Derate | Coal | 3 | 2013 | 4 | 2.55 | 0.56064 | 220.3309 | 86.4043 | 86
MC3 | D4 | 38 | 8040 | 2013-04-02 22:00 | 2013-04-03 00:28 | 280 | 423 | 393 | Slurry transfer pumps and motors B | F590Place blank in 3A-1 Recycle Pump Header | Mill Creek | Derate | Coal | 3 | 2013 | 4 | 2.4667 | 0.83388 | 327.7168 | 132.8582 | 133
MC3 | D1 | 39 | 260 | 2013-04-07 12:32 | 2013-04-08 02:57 | 335 | 423 | 393 | Primary air fan | F9203B Coal Mill Primary Air Fan - Inboard Bearing Wiped | Mill Creek | Derate | Coal | 3 | 2013 | 4 | 14.4167 | 2.9992 | 1178.6903 | 81.7589 | 82
MC3 | D4 | 40 | 8125 | 2013-05-06 22:30 | 2013-05-07 02:45 | 285 | 423 | 393 | Scrubber recycle (liquid) pumps | F590FGD 3A1 Recycle Pump - Removed Blank | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 4.25 | 1.3865 | 544.9043 | 128.2128 | 128
MC3 | D4 | 41 | 8125 | 2013-05-08 22:00 | 2013-05-09 00:24 | 285 | 423 | 393 | Scrubber recycle (liquid) pumps | F590FGD 3A1 Recycle Pump - Installed Blank | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 2.4 | 0.78298 | 307.7106 | 128.2128 | 128
MC3 | D1 | 42 | 260 | 2013-05-14 19:20 | 2013-05-14 19:53 | 355 | 423 | 393 | Primary air fan | F4003D Primary Air Fan - Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 0.55 | 0.088416 | 34.7475 | 63.1773 | 63
MC3 | D4 | 43 | 310 | 2013-05-14 23:00 | 2013-05-15 02:59 | 335 | 423 | 393 | Pulverizer mills | F5903D Coal Mill - Clean Pitot Tubes & Check Dampers | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 3.9833 | 0.82868 | 325.6728 | 81.7589 | 82
MC3 | NC | 44 | 870 | 2013-05-15 02:59 | 2013-05-15 04:40 | 0 | 423 | 393 | Soot blowers - steam | F590Wallblowers R1 - R10 Removed Power | Mill Creek | Other | Coal | 3 | 2013 | 5 | 1.6833 | 1.6833 | 661.55 | 393 | 393
MC3 | D4 | 45 | 876 | 2013-05-16 22:00 | 2013-05-17 00:31 | 280 | 423 | 393 | Soot blower controls | F590Sootblower Regulator - Repack | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 2.5167 | 0.85079 | 334.3597 | 132.8582 | 133
MC3 | D4 | 46 | 8125 | 2013-05-23 21:30 | 2013-05-24 03:30 | 280 | 423 | 393 | Scrubber recycle (liquid) pumps | F590FGD 3A1 Recycle Pump - Remove Blank | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 6 | 2.0284 | 797.1489 | 132.8582 | 133
MC3 | D4 | 47 | 8125 | 2013-05-27 21:00 | 2013-05-28 02:10 | 280 | 423 | 393 | Scrubber recycle (liquid) pumps | F590FGD 3A1 Recycle Pump - Install Blank | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 5.1667 | 1.7467 | 686.4338 | 132.8582 | 133
MC3 | U1 | 48 | 1455 | 2013-05-31 00:51 | 2013-05-31 03:44 | 0 | 423 | 393 | Induced draft fans | F8203A Induced Draft Fan - Suction Pressure High Trip | Mill Creek | Outage | Coal | 3 | 2013 | 5 | 2.8833 | 2.8833 | 1133.15 | 393 | 393
MC3 | NC | 49 | 1850 | 2013-05-31 03:44 | 2013-05-31 07:30 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 5 | 3.7667 | 3.7667 | 1480.3 | 393 | 393
MC3 | D1 | 50 | 8825 | 2013-05-31 07:30 | 2013-05-31 11:00 | 190 | 423 | 393 | Other SCR NOx problems | F090SCR Dampers - Calibrate | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 3.5 | 1.9279 | 757.6631 | 216.4752 | 216
MC3 | D1 | 51 | 8127 | 2013-06-11 18:47 | 2013-06-12 08:10 | 330 | 423 | 393 | Scrubber recycle (liquid) pump motors | F7803A1 & 3B3 recycle pumps not available - SO2 compliance | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 13.3833 | 2.9424 | 1156.377 | 86.4043 | 86
MC3 | D4 | 52 | 8125 | 2013-06-12 23:00 | 2013-06-12 23:50 | 280 | 423 | 393 | Scrubber recycle (liquid) pumps | F590Removed Blank from 3A1 recycle pump | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 0.83333 | 0.28172 | 110.7151 | 132.8582 | 133
MC3 | U1 | 53 | 4460 | 2013-06-16 23:46 | 2013-06-17 01:18 | 0 | 423 | 393 | Turbine overspeed trip test | F820Tripped during Turbine Overspeed Test | Mill Creek | Outage | Coal | 3 | 2013 | 6 | 1.5333 | 1.5333 | 602.6 | 393 | 393
MC3 | NC | 54 | 1850 | 2013-06-17 01:18 | 2013-06-17 10:47 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 6 | 9.4833 | 9.4833 | 3726.95 | 393 | 393
MC3 | U1 | 55 | 1000 | 2013-06-17 21:30 | 2013-06-19 20:26 | 0 | 423 | 393 | Waterwall (Furnace wall) A | F540Boiler Tube Leak - Waterwall | Mill Creek | Outage | Coal | 3 | 2013 | 6 | 46.9333 | 46.9333 | 18444.8 | 393 | 393
MC3 | NC | 56 | 1850 | 2013-06-19 20:26 | 2013-06-19 20:59 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 6 | 0.55 | 0.55 | 216.15 | 393 | 393
MC3 | U1 | 57 | 800 | 2013-06-19 20:59 | 2013-06-19 21:47 | 0 | 423 | 393 | Drums and drum internals (single drum only) | F420Low Drum Level Trip - Operator Error | Mill Creek | Outage | Coal | 3 | 2013 | 6 | 0.8 | 0.8 | 314.4 | 393 | 393
MC3 | NC | 58 | 1850 | 2013-06-19 21:47 | 2013-06-20 08:30 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 6 | 10.7167 | 10.7167 | 4211.65 | 393 | 393
MC3 | D1 | 59 | 3412 | 2013-06-22 17:50 | 2013-06-22 21:10 | 200 | 423 | 393 | Feedwater pump drive - steam turbine | F540Turbine Driven Boiler Feed Pump - EHC Leak at High Pressure Stop Valve o-ring | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 3.3333 | 1.7573 | 690.6147 | 207.1844 | 207
MC3 | D1 | 60 | 3412 | 2013-06-22 21:10 | 2013-06-22 23:38 | 170 | 423 | 393 | Feedwater pump drive - steam turbine | F540Turbine Driven Boiler Feed Pump - EHC Leak at High Pressure Stop Valve o-ring | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 2.4667 | 1.4753 | 579.8066 | 235.0567 | 235
MC3 | D4 | 61 | 250 | 2013-06-24 22:00 | 2013-06-25 03:00 | 325 | 423 | 393 | Pulverizer feeders | F0903A Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 5 | 1.1584 | 455.2482 | 91.0496 | 91
MC3 | D4 | 62 | 250 | 2013-06-25 22:00 | 2013-06-26 00:40 | 325 | 423 | 393 | Pulverizer feeders | F0903B Coal Feeder - Calibration Cancelled | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 2.6667 | 0.61781 | 242.7991 | 91.0496 | 91
MC3 | D4 | 63 | 250 | 2013-06-27 22:00 | 2013-06-28 04:05 | 325 | 423 | 393 | Pulverizer feeders | F0903B Coal Feeder - Calibration & Clean Out Lower Bunker Valve | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 6.0833 | 1.4094 | 553.8853 | 91.0496 | 91
MC3 | D4 | 64 | 250 | 2013-06-30 23:00 | 2013-07-01 03:50 | 325 | 423 | 393 | Pulverizer feeders | F0903C Coal Feeder - Calibration | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 4.8333 | 1.1198 | 440.0733 | 91.0496 | 91
MC3 | D4 | 65 | 250 | 2013-07-01 22:30 | 2013-07-02 04:16 | 325 | 423 | 393 | Pulverizer feeders | F0903D Coal Feeder - Calibration | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 5.7667 | 1.336 | 525.053 | 91.0496 | 91
MC3 | D1 | 66 | 320 | 2013-07-05 05:34 | 2013-07-05 08:06 | 330 | 423 | 393 | Foreign object in Pulverizers mill | F1203A Coal Mill - Foreign Object in Mill | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 2.5333 | 0.55697 | 218.8908 | 86.4043 | 86
MC3 | D1 | 67 | 1400 | 2013-07-14 16:49 | 2013-07-14 20:39 | 415 | 423 | 393 | Forced draft fans | F400Forced Draft Fans - Maxed Out | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 3.8333 | 0.072498 | 28.4917 | 7.4326 | 7
MC3 | D4 | 68 | 350 | 2013-07-16 23:00 | 2013-07-17 03:00 | 325 | 423 | 393 | Pulverized fuel and air piping (from pulverizer to wind box) | F5903C Coal Mill - Install Duct Port | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 4 | 0.92671 | 364.1986 | 91.0496 | 91
MC3 | D1 | 69 | 1710 | 2013-07-23 12:40 | 2013-07-23 14:35 | 408 | 423 | 393 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 1.9167 | 0.067967 | 26.711 | 13.9362 | 14
MC3 | D1 | 70 | 1710 | 2013-07-23 14:35 | 2013-07-23 18:04 | 416 | 423 | 393 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 3.4833 | 0.057644 | 22.654 | 6.5035 | 7
MC3 | NC | 71 | 9999 | 2013-07-31 09:00 | 2013-07-31 13:00 | 0 | 423 | 393 | Total unit performance testing (use appropriate codes for individual component testing) | F790Full Load Capability Test | Mill Creek | Other | Coal | 3 | 2013 | 7 | 4 | 4 | 1572 | 393 | 393
MC3 | D1 | 72 | 360 | 2013-08-02 02:00 | 2013-08-02 02:43 | 330 | 423 | 393 | Burners | F7803C3 Coal Burner - Inspection, High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 0.71667 | 0.15757 | 61.923 | 86.4043 | 86
MC3 | MO | 73 | 3110 | 2013-08-02 21:24 | 2013-08-04 03:27 | 0 | 423 | 393 | Condenser tube leaks | F540Condenser Tube Leak | Mill Creek | Maintenance | Coal | 3 | 2013 | 8 | 30.05 | 30.05 | 11809.65 | 393 | 393
MC3 | NC | 74 | 1850 | 2013-08-04 03:27 | 2013-08-04 16:11 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 8 | 12.7333 | 12.7333 | 5004.2 | 393 | 393
MC3 | D1 | 75 | 3412 | 2013-08-05 03:26 | 2013-08-05 07:01 | 140 | 423 | 393 | Feedwater pump drive - steam turbine | F590Boiler Feed Pump Turbine Driven - Mechanical Overspeed Trip Solenoid Stuck | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 3.5833 | 2.3974 | 942.1625 | 262.9291 | 263
MC3 | D1 | 76 | 360 | 2013-08-05 08:43 | 2013-08-05 09:42 | 330 | 423 | 393 | Burners | F5303B10 Coal Burner - Inspection | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 0.98333 | 0.21619 | 84.9642 | 86.4043 | 86
MC3 | D1 | 77 | 360 | 2013-08-07 01:57 | 2013-08-07 06:32 | 320 | 423 | 393 | Burners | F5903C8 Coal Burner - Blank Installed | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 4.5833 | 1.116 | 438.6022 | 95.695 | 96
MC3 | D1 | 78 | 3149 | 2013-08-07 18:37 | 2013-08-07 20:23 | 410 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure due to 3G & 3H Cooling Tower Fans being out of service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 1.7667 | 0.054295 | 21.3378 | 12.078 | 12
MC3 | D1 | 79 | 3149 | 2013-08-09 13:58 | 2013-08-09 15:50 | 417 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 1.8667 | 0.026478 | 10.4057 | 5.5745 | 6
MC3 | D1 | 80 | 3149 | 2013-08-09 15:50 | 2013-08-09 16:05 | 410 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 0.25 | 0.0076832 | 3.0195 | 12.078 | 12
MC3 | D1 | 81 | 3149 | 2013-08-09 16:05 | 2013-08-09 18:52 | 405 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 2.7833 | 0.11844 | 46.5468 | 16.7234 | 17
MC3 | U1 | 82 | 3662 | 2013-08-23 02:03 | 2013-08-23 12:47 | 0 | 423 | 393 | 4160-volt conductors and buses | F8203A2 4KV Bus Undervoltage Trip | Mill Creek | Outage | Coal | 3 | 2013 | 8 | 10.7333 | 10.7333 | 4218.2 | 393 | 393
MC3 | D4 | 83 | 260 | 2013-08-23 12:47 | 2013-08-23 22:49 | 325 | 423 | 393 | Primary air fan | F5903B Coal Mill - Replace Primary Air Fan Venturi | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 10.0333 | 2.3245 | 913.5314 | 91.0496 | 91
MC3 | D4 | 84 | 260 | 2013-08-23 22:49 | 2013-08-25 10:55 | 335 | 423 | 393 | Primary air fan | F5903B Coal Mill - Replace Primary Air Fan Venturi | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 36.1 | 7.5102 | 2951.495 | 81.7589 | 82
MC3 | D1 | 85 | 3236 | 2013-08-25 13:00 | 2013-08-26 03:35 | 360 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 14.5833 | 2.172 | 853.5904 | 58.5319 | 59
MC3 | D1 | 86 | 3236 | 2013-08-26 03:35 | 2013-08-26 05:00 | 385 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 1.4167 | 0.12727 | 50.0154 | 35.305 | 35
MC3 | D1 | 87 | 3236 | 2013-08-26 05:00 | 2013-08-26 10:12 | 365 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 5.2 | 0.713 | 280.2099 | 53.8865 | 54
MC3 | D1 | 88 | 3236 | 2013-08-26 10:12 | 2013-08-26 13:06 | 355 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 2.9 | 0.46619 | 183.2142 | 63.1773 | 63
MC3 | D1 | 89 | 3236 | 2013-08-26 13:06 | 2013-08-27 03:40 | 350 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 14.5667 | 2.5139 | 987.9506 | 67.8227 | 68
MC3 | D1 | 90 | 3236 | 2013-08-27 03:40 | 2013-08-27 05:03 | 370 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 1.3833 | 0.17333 | 68.1169 | 49.2411 | 49
MC3 | D1 | 91 | 3236 | 2013-08-27 05:03 | 2013-08-27 05:55 | 350 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 0.86667 | 0.14957 | 58.7797 | 67.8227 | 68
MC3 | D1 | 92 | 3236 | 2013-08-27 05:55 | 2013-08-27 10:50 | 360 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 4.9167 | 0.73227 | 287.7819 | 58.5319 | 59
MC3 | D1 | 93 | 3236 | 2013-08-27 10:50 | 2013-08-27 13:47 | 370 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 2.95 | 0.36962 | 145.2613 | 49.2411 | 49
MC3 | D1 | 94 | 3236 | 2013-08-27 13:47 | 2013-08-28 08:55 | 350 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 19.1333 | 3.302 | 1297.6742 | 67.8227 | 68
MC3 | D1 | 95 | 3236 | 2013-08-28 08:55 | 2013-08-28 11:50 | 362 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 2.9167 | 0.42061 | 165.2985 | 56.6738 | 57
MC3 | D1 | 96 | 3236 | 2013-08-28 11:50 | 2013-08-28 15:27 | 335 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 3.6167 | 0.7524 | 295.6946 | 81.7589 | 82
MC3 | D1 | 97 | 3236 | 2013-08-28 15:27 | 2013-08-29 05:20 | 345 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 13.8833 | 2.56 | 1006.0986 | 72.4681 | 72
MC3 | D1 | 98 | 3236 | 2013-08-29 05:20 | 2013-08-29 09:45 | 362 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 4.4167 | 0.63692 | 250.3091 | 56.6738 | 57
MC3 | D1 | 99 | 3236 | 2013-08-29 09:45 | 2013-08-29 11:05 | 345 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 1.3333 | 0.24586 | 96.6241 | 72.4681 | 72
MC3 | D1 | 100 | 3236 | 2013-08-29 11:05 | 2013-08-29 14:11 | 336 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 3.1 | 0.63759 | 250.5723 | 80.8298 | 81
MC3 | D1 | 101 | 3236 | 2013-08-29 14:11 | 2013-08-29 18:30 | 296 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 4.3167 | 1.296 | 509.3361 | 117.9929 | 118
MC3 | D1 | 102 | 3236 | 2013-08-29 18:30 | 2013-08-30 05:34 | 320 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 11.0667 | 2.6947 | 1059.0251 | 95.695 | 96
MC3 | D1 | 103 | 3236 | 2013-08-30 05:34 | 2013-08-30 09:56 | 345 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 4.3667 | 0.8052 | 316.444 | 72.4681 | 72
MC3 | D1 | 104 | 3236 | 2013-08-30 09:56 | 2013-08-30 13:26 | 335 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 3.5 | 0.72813 | 286.156 | 81.7589 | 82
MC3 | D1 | 105 | 3236 | 2013-08-30 13:26 | 2013-08-30 19:57 | 329 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 6.5167 | 1.4481 | 569.1222 | 87.3333 | 87
MC3 | D1 | 106 | 3236 | 2013-08-30 19:57 | 2013-09-01 09:24 | 319 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 37.45 | 9.2076 | 3618.573 | 96.6241 | 97
MC3 | D1 | 107 | 3236 | 2013-09-01 09:24 | 2013-09-01 13:00 | 344 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 3.6 | 0.67234 | 264.2298 | 73.3972 | 73
MC3 | D1 | 108 | 3236 | 2013-09-01 13:00 | 2013-09-01 15:52 | 337 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 2.8667 | 0.58282 | 229.0487 | 79.9007 | 80
MC3 | D1 | 109 | 3236 | 2013-09-01 15:52 | 2013-09-02 17:52 | 320 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 26 | 6.331 | 2488.0709 | 95.695 | 96
MC3 | D1 | 110 | 3236 | 2013-09-02 17:52 | 2013-09-03 17:18 | 330 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 23.4333 | 5.152 | 2024.7397 | 86.4043 | 86
MC3 | D1 | 111 | 3236 | 2013-09-03 17:18 | 2013-09-04 08:00 | 343 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 14.7 | 2.7801 | 1092.5957 | 74.3262 | 74
MC3 | D1 | 112 | 3236 | 2013-09-04 08:00 | 2013-09-04 13:50 | 360 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 5.8333 | 0.86879 | 341.4362 | 58.5319 | 59
MC3 | D1 | 113 | 3236 | 2013-09-04 13:50 | 2013-09-04 17:45 | 375 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 3.9167 | 0.44444 | 174.6667 | 44.5957 | 45
MC3 | D1 | 114 | 3236 | 2013-09-04 17:45 | 2013-09-05 07:27 | 344 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 13.7 | 2.5586 | 1005.5411 | 73.3972 | 73
MC3 | D1 | 115 | 3236 | 2013-09-05 07:27 | 2013-09-05 08:58 | 365 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 1.5167 | 0.20796 | 81.7279 | 53.8865 | 54
MC3 | D1 | 116 | 3236 | 2013-09-05 08:58 | 2013-09-05 11:36 | 355 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 2.6333 | 0.42333 | 166.3669 | 63.1773 | 63
MC3 | D1 | 117 | 3236 | 2013-09-05 11:36 | 2013-09-05 19:51 | 335 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 8.25 | 1.7163 | 674.5106 | 81.7589 | 82
MC3 | D1 | 118 | 3236 | 2013-09-05 19:51 | 2013-09-08 09:40 | 350 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 61.8167 | 10.6681 | 4192.5729 | 67.8227 | 68
MC3 | D1 | 119 | 3236 | 2013-09-08 09:40 | 2013-09-09 08:23 | 315 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 22.7167 | 5.8 | 2279.4 | 100.3404 | 100
MC3 | D1 | 120 | 3236 | 2013-09-09 08:23 | 2013-09-09 09:11 | 340 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 0.8 | 0.15697 | 61.6908 | 77.1135 | 77
MC3 | D1 | 121 | 3236 | 2013-09-09 09:11 | 2013-09-09 11:08 | 326 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 1.95 | 0.44716 | 175.7351 | 90.1206 | 90
MC3 | D1 | 122 | 3236 | 2013-09-09 11:08 | 2013-09-09 12:26 | 292 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 1.3 | 0.4026 | 158.222 | 121.7092 | 122
MC3 | D1 | 123 | 3236 | 2013-09-09 12:26 | 2013-09-09 22:50 | 303 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 10.4 | 2.9504 | 1159.4894 | 111.4894 | 111
MC3 | D1 | 124 | 3236 | 2013-09-09 22:50 | 2013-09-09 23:20 | 330 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 0.5 | 0.10993 | 43.2021 | 86.4043 | 86
MC3 | D1 | 125 | 3236 | 2013-09-09 23:20 | 2013-09-10 10:21 | 320 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 11.0167 | 2.6825 | 1054.2403 | 95.695 | 96
MC3 | D1 | 126 | 3236 | 2013-09-10 10:21 | 2013-09-10 10:31 | 315 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 0.16667 | 0.042553 | 16.7234 | 100.3404 | 100
MC3 | D1 | 127 | 3236 | 2013-09-10 10:31 | 2013-09-10 12:19 | 310 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 1.8 | 0.48085 | 188.9745 | 104.9858 | 105
MC3 | D1 | 128 | 3236 | 2013-09-10 12:19 | 2013-09-10 12:50 | 305 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 0.51667 | 0.14413 | 56.6428 | 109.6312 | 110
MC3 | D1 | 129 | 3236 | 2013-09-10 12:50 | 2013-09-11 01:56 | 300 | 423 | 393 | Cooling tower booster motor | F660High Back Pressure due to 3A Cooling Tower Pump Motor Out of Service | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 13.1 | 3.8092 | 1497.0234 | 114.2766 | 114
MC3 | D1 | 130 | 385 | 2013-09-12 21:41 | 2013-09-12 22:11 | 230 | 423 | 393 | Igniters | F5903D1 Coal Burner - Igniter Issue | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 0.5 | 0.22813 | 89.656 | 179.3121 | 179
MC3 | D4 | 131 | 310 | 2013-09-12 22:11 | 2013-09-13 00:55 | 325 | 423 | 393 | Pulverizer mills | F5303B Coal Mill - Inspection | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 2.7333 | 0.63325 | 248.869 | 91.0496 | 91
MC3 | D4 | 132 | 350 | 2013-09-13 22:00 | 2013-09-14 09:45 | 370 | 423 | 393 | Pulverized fuel and air piping (from pulverizer to wind box) | F5903A Coal Mill - Replace Venturi | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 11.75 | 1.4722 | 578.5833 | 49.2411 | 49
MC3 | D4 | 133 | 350 | 2013-09-14 09:45 | 2013-09-14 17:45 | 345 | 423 | 393 | Pulverized fuel and air piping (from pulverizer to wind box) | F5903A Coal Mill - Replace Venturi | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 8 | 1.4752 | 579.7447 | 72.4681 | 72
MC3 | D4 | 134 | 350 | 2013-09-14 17:45 | 2013-09-15 13:30 | 375 | 423 | 393 | Pulverized fuel and air piping (from pulverizer to wind box) | F5903A Coal Mill - Replace Venturi | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 19.75 | 2.2411 | 880.766 | 44.5957 | 45
MC3 | D4 | 135 | 350 | 2013-09-16 22:00 | 2013-09-17 11:55 | 335 | 423 | 393 | Pulverized fuel and air piping (from pulverizer to wind box) | F5903C Coal Mill - Replace Venturi | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 13.9167 | 2.8952 | 1137.8109 | 81.7589 | 82
MC3 | D1 | 136 | 8280 | 2013-09-16 23:55 | 2013-09-17 00:36 | 275 | 423 | 393 | Reagent feed piping | F120FGD Reactant Feed Line Plugged | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 0.68333 | 0.23909 | 93.9608 | 137.5035 | 138
MC3 | D4 | 137 | 350 | 2013-09-17 11:55 | 2013-09-17 22:01 | 350 | 423 | 393 | Pulverized fuel and air piping (from pulverizer to wind box) | F5903C Coal Mill - Replace Venturi | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 10.1 | 1.743 | 685.0092 | 67.8227 | 68
MC3 | D4 | 138 | 350 | 2013-09-18 06:00 | 2013-09-18 23:21 | 350 | 423 | 393 | Pulverized fuel and air piping (from pulverizer to wind box) | F5903D Coal Mill - Replace Venturi | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 17.35 | 2.9942 | 1176.7238 | 67.8227 | 68
MC3 | U1 | 139 | 4270 | 2013-09-18 23:46 | 2013-10-20 00:45 | 0 | 423 | 393 | Crossover or under piping | F540Turbine Crossover - Expansion Joint Failure | Mill Creek | Outage | Coal | 3 | 2013 | 9 | 744.9833 | 744.9833 | 292778.45 | 393 | 393
MC3 | PO | 140 | 1800 | 2013-10-20 00:45 | 2013-11-13 23:47 | 0 | 423 | 393 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | F590Planned Outage | Mill Creek | Other | Coal | 3 | 2013 | 10 | 599.0333 | 599.0333 | 235420.1 | 393 | 393
MC3 | NC | 141 | 1850 | 2013-11-13 23:47 | 2013-11-14 23:47 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 3 | 2013 | 11 | 24 | 24 | 9432 | 393 | 393
MC3 | D1 | 142 | 3412 | 2013-11-14 23:47 | 2013-11-15 04:18 | 155 | 423 | 393 | Feedwater pump drive - steam turbine | F920Turbine Driven Boiler Feed Pump - Low Pressure Journal Bearing Wiped | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 4.5167 | 2.8616 | 1124.618 | 248.9929 | 249
MC3 | D1 | 143 | 3412 | 2013-11-15 04:18 | 2013-11-17 04:23 | 168 | 423 | 393 | Feedwater pump drive - steam turbine | F920Turbine Driven Boiler Feed Pump - Low Pressure Journal Bearing Wiped | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 48.0833 | 28.9864 | 11391.6578 | 236.9149 | 237
MC3 | D1 | 144 | 3412 | 2013-11-17 04:23 | 2013-11-19 02:21 | 178 | 423 | 393 | Feedwater pump drive - steam turbine | F920Turbine Driven Boiler Feed Pump - Low Pressure Journal Bearing Wiped | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 45.9667 | 26.6237 | 10463.1217 | 227.6241 | 228
MC3 | D1 | 145 | 75 | 2013-11-19 02:21 | 2013-11-19 04:02 | 305 | 423 | 393 | Storage silos/hoppers | F1203A Mill - Silo Plugged | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 1.6833 | 0.46958 | 184.5459 | 109.6312 | 110
MC3 | D1 | 146 | 1850 | 2013-11-19 04:02 | 2013-11-19 08:50 | 333 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 4.8 | 1.0213 | 401.3617 | 83.617 | 84
MC3 | D1 | 147 | 1850 | 2013-11-19 08:50 | 2013-11-19 15:02 | 355 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 6.2 | 0.99669 | 391.6993 | 63.1773 | 63
MC3 | D1 | 148 | 1850 | 2013-11-19 15:02 | 2013-11-19 18:00 | 360 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 2.9667 | 0.44184 | 173.6447 | 58.5319 | 59
MC3 | D1 | 149 | 310 | 2013-11-19 18:00 | 2013-11-19 18:20 | 365 | 423 | 393 | Pulverizer mills | F5903B Coal Mill - Gearbox Low Oil | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 0.33333 | 0.045705 | 17.9622 | 53.8865 | 54
MC3 | D4 | 150 | 360 | 2013-11-20 22:00 | 2013-11-21 02:00 | 320 | 423 | 393 | Burners | F5903D Mill - Burner Taps Repair | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 4 | 0.974 | 382.7801 | 95.695 | 96
MC3 | D1 | 151 | 310 | 2013-11-23 06:38 | 2013-11-23 09:18 | 330 | 423 | 393 | Pulverizer mills | F4003C Coal Mill - Alarm Logic Issue | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 2.6667 | 0.58629 | 230.4113 | 86.4043 | 86
MC3 | D1 | 152 | 360 | 2013-11-23 18:37 | 2013-11-23 20:49 | 355 | 423 | 393 | Burners | F7803A Mill - A2 & A3 Burners High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 2.2 | 0.35366 | 138.9901 | 63.1773 | 63
MC3 | D1 | 153 | 360 | 2013-11-23 20:49 | 2013-11-24 04:04 | 347 | 423 | 393 | Burners | F7803A Mill - A2 & A3 Burners High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 7.25 | 1.3026 | 511.922 | 70.6099 | 71
MC3 | D1 | 154 | 360 | 2013-11-24 19:05 | 2013-11-24 20:08 | 390 | 423 | 393 | Burners | F7803A Mill - A2 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 1.05 | 0.081915 | 32.1926 | 30.6596 | 31
MC3 | D4 | 155 | 260 | 2013-11-25 08:10 | 2013-11-25 09:56 | 320 | 423 | 393 | Primary air fan | F5303A Mill Primary Air Fan - Inspect Dampers | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 1.7667 | 0.43018 | 169.0612 | 95.695 | 96
MC3 | D4 | 156 | 260 | 2013-11-25 09:56 | 2013-11-25 15:26 | 330 | 423 | 393 | Primary air fan | F5303A Mill Primary Air Fan - Inspect Dampers | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 5.5 | 1.2092 | 475.2234 | 86.4043 | 86
MC3 | D4 | 157 | 260 | 2013-11-25 22:00 | 2013-11-26 04:11 | 330 | 423 | 393 | Primary air fan | F5303A Mill Primary Air Fan - Inspection Cancelled | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 6.1833 | 1.3595 | 534.2663 | 86.4043 | 86
MC3 | D1 | 158 | 360 | 2013-11-27 09:43 | 2013-11-27 12:35 | 344 | 423 | 393 | Burners | F7803A Mill - 3A3 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 2.8667 | 0.53538 | 210.4052 | 73.3972 | 73
MC3 | MO | 159 | 1060 | 2013-11-28 13:07 | 2013-12-01 07:10 | 0 | 423 | 393 | First reheater A | F540Boiler Tube Leak - First Reheater | Mill Creek | Maintenance | Coal | 3 | 2013 | 11 | 66.05 | 66.05 | 25957.65 | 393 | 393
MC3 | NC | 160 | 1850 | 2013-12-01 07:10 | 2013-12-01 07:17 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2013 | 12 | 0.11667 | 0.11667 | 45.85 | 393 | 393
MC3 | U1 | 161 | 800 | 2013-12-01 07:17 | 2013-12-01 09:05 | 0 | 423 | 393 | Drums and drum internals (single drum only) | F420Low Drum Level Trip - Operator Error | Mill Creek | Outage | Coal | 3 | 2013 | 12 | 1.8 | 1.8 | 707.4 | 393 | 393
MC3 | NC | 162 | 1850 | 2013-12-01 09:05 | 2013-12-01 21:04 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Srart Up | Mill Creek | Other | Coal | 3 | 2013 | 12 | 11.9833 | 11.9833 | 4709.45 | 393 | 393
MC3 | NC | 163 | 8460 | 2013-12-02 13:30 | 2013-12-02 18:22 | 0 | 423 | 393 | Testing A | F790Full Load RATA Testing | Mill Creek | Other | Coal | 3 | 2013 | 12 | 4.8667 | 4.8667 | 1912.6 | 393 | 393
MC3 | D4 | 164 | 260 | 2013-12-03 09:49 | 2013-12-03 11:53 | 330 | 423 | 393 | Primary air fan | F5303A Mill Primary Air Fan - Inspection | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 2.0667 | 0.45437 | 178.5688 | 86.4043 | 86
MC3 | D4 | 165 | 350 | 2013-12-03 23:23 | 2013-12-04 03:45 | 330 | 423 | 393 | Pulverized fuel and air piping (from pulverizer to wind box) | F5903A Mill - Inspect Coal Pipe Orifices | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 4.3667 | 0.96005 | 377.2986 | 86.4043 | 86
MC3 | D4 | 166 | 350 | 2013-12-04 09:00 | 2013-12-04 19:13 | 330 | 423 | 393 | Pulverized fuel and air piping (from pulverizer to wind box) | F5903A Coal Mill - Adjust Coal Pipe Orifices | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 10.2167 | 2.2462 | 882.7635 | 86.4043 | 86
MC3 | D4 | 167 | 100 | 2013-12-05 09:00 | 2013-12-05 11:53 | 330 | 423 | 393 | Bunker gates | F5903B Mill - Lower Bunker Valve Repair | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 2.8833 | 0.63392 | 249.1323 | 86.4043 | 86
MC3 | D1 | 168 | 310 | 2013-12-05 16:45 | 2013-12-05 17:03 | 340 | 423 | 393 | Pulverizer mills | F4003C Coal Mill - Breaker Issue | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.3 | 0.058865 | 23.134 | 77.1135 | 77
MC3 | D1 | 169 | 360 | 2013-12-06 18:22 | 2013-12-06 19:35 | 330 | 423 | 393 | Burners | F7803A Mill - 3A10 Burner High Temperature Trip | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 1.2167 | 0.26749 | 105.1252 | 86.4043 | 86
MC3 | D1 | 170 | 360 | 2013-12-06 19:35 | 2013-12-06 23:43 | 305 | 423 | 393 | Burners | F1303A Mill - 3A10 Burner Blank Installed 3A6 Burner Blank Removed | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 4.1333 | 1.153 | 453.1423 | 109.6312 | 110
MC3 | D1 | 171 | 360 | 2013-12-07 16:28 | 2013-12-07 17:42 | 320 | 423 | 393 | Burners | F7803C Mill - 3C4 Burner High Temperature Trip | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 1.2333 | 0.30032 | 118.0239 | 95.695 | 96
MC3 | D1 | 172 | 360 | 2013-12-07 17:48 | 2013-12-07 22:30 | 375 | 423 | 393 | Burners | F7803C Mill - 3C4 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 4.7 | 0.53333 | 209.6 | 44.5957 | 45
MC3 | D1 | 173 | 360 | 2013-12-07 22:30 | 2013-12-08 09:52 | 405 | 423 | 393 | Burners | F7803C Mill - 3C4 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 11.3667 | 0.48369 | 190.0894 | 16.7234 | 17
MC3 | D1 | 174 | 360 | 2013-12-08 09:52 | 2013-12-08 17:11 | 324 | 423 | 393 | Burners | F7803C Mill - 3C4 Burner High Temperature Trip | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 7.3167 | 1.7124 | 672.9777 | 91.9787 | 92
MC3 | NC | 175 | 360 | 2013-12-09 08:00 | 2013-12-09 18:00 | 0 | 423 | 393 | Burners | F790Full Load - Burner Tuning | Mill Creek | Other | Coal | 3 | 2013 | 12 | 10 | 10 | 3930 | 393 | 393
MC3 | D4 | 176 | 360 | 2013-12-09 22:30 | 2013-12-10 05:57 | 330 | 423 | 393 | Burners | F6303A Mill - 3A1 & 3A5 Burners Removed Blanks | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 7.45 | 1.6379 | 643.7117 | 86.4043 | 86
MC3 | D1 | 177 | 360 | 2013-12-10 07:15 | 2013-12-10 11:15 | 340 | 423 | 393 | Burners | F7803A Mill - 3A3 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 4 | 0.78487 | 308.4539 | 77.1135 | 77
MC3 | D4 | 178 | 310 | 2013-12-10 23:30 | 2013-12-11 03:07 | 320 | 423 | 393 | Pulverizer mills | F5903C Coal Mill - Pyrite Hopper Repairs | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 3.6167 | 0.88065 | 346.097 | 95.695 | 96
MC3 | D1 | 179 | 360 | 2013-12-11 07:08 | 2013-12-11 09:11 | 330 | 423 | 393 | Burners | F7803D Mill - 3D1 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 2.05 | 0.45071 | 177.1287 | 86.4043 | 86
MC3 | D1 | 180 | 360 | 2013-12-11 21:01 | 2013-12-11 23:50 | 320 | 423 | 393 | Burners | F7803A Mill - 3A1 & 3A9 Burners High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 2.8167 | 0.68586 | 269.541 | 95.695 | 96
MC3 | D1 | 181 | 360 | 2013-12-11 23:50 | 2013-12-12 03:47 | 320 | 423 | 393 | Burners | F1303A Mill - 3A1 Burner Installed Blank 3A5 Burner Removed Blank | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 3.95 | 0.96182 | 377.9954 | 95.695 | 96
MC3 | D1 | 182 | 310 | 2013-12-12 04:09 | 2013-12-12 04:41 | 320 | 423 | 393 | Pulverizer mills | F5903A Coal Mill - Breaker Issue | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.53333 | 0.12987 | 51.0374 | 95.695 | 96
MC3 | D1 | 183 | 1850 | 2013-12-12 07:52 | 2013-12-12 08:03 | 410 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.18333 | 0.0056344 | 2.2143 | 12.078 | 12
MC3 | D1 | 184 | 360 | 2013-12-12 08:03 | 2013-12-12 10:10 | 330 | 423 | 393 | Burners | F5303A Mill - 3A8 Burner Inspection | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 2.1167 | 0.46537 | 182.889 | 86.4043 | 86
MC3 | D1 | 185 | 1850 | 2013-12-12 10:10 | 2013-12-12 12:10 | 400 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 2 | 0.10875 | 42.7376 | 21.3688 | 21
MC3 | D1 | 186 | 1850 | 2013-12-12 12:10 | 2013-12-12 13:37 | 355 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica/3C Mill Breaker Issue | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 1.45 | 0.2331 | 91.6071 | 63.1773 | 63
MC3 | D1 | 187 | 1850 | 2013-12-12 13:37 | 2013-12-12 19:57 | 330 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica/3C Mill Breaker Issue | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 6.3333 | 1.3924 | 547.227 | 86.4043 | 86
MC3 | D1 | 188 | 1850 | 2013-12-12 19:57 | 2013-12-12 20:37 | 385 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica/3C Mill Breaker Issue | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.66667 | 0.05989 | 23.5366 | 35.305 | 35
MC3 | D4 | 189 | 310 | 2013-12-12 22:00 | 2013-12-13 04:43 | 330 | 423 | 393 | Pulverizer mills | F5903C Coal Mill - Replace Pyrite Jet Pulsion | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 6.7167 | 1.4767 | 580.3486 | 86.4043 | 86
MC3 | D1 | 190 | 360 | 2013-12-13 11:36 | 2013-12-13 12:28 | 330 | 423 | 393 | Burners | F7803B Mill - 3B7 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.86667 | 0.19054 | 74.8837 | 86.4043 | 86
MC3 | D1 | 191 | 360 | 2013-12-13 14:11 | 2013-12-13 15:00 | 350 | 423 | 393 | Burners | F7803A Mill - 3A2 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.81667 | 0.14094 | 55.3885 | 67.8227 | 68
MC3 | D1 | 192 | 310 | 2013-12-13 15:00 | 2013-12-13 18:00 | 240 | 423 | 393 | Pulverizer mills | F8303C Mill - Burner High Temperature Trip3D Mill - Coal Feeder Trip | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 3 | 1.2979 | 510.0638 | 170.0213 | 170
MC3 | D1 | 193 | 360 | 2013-12-13 18:00 | 2013-12-13 19:42 | 304 | 423 | 393 | Burners | F7803A Mill - 3A2 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 1.7 | 0.47825 | 187.9525 | 110.5603 | 111
MC3 | D1 | 194 | 360 | 2013-12-15 04:06 | 2013-12-15 04:52 | 340 | 423 | 393 | Burners | F7803A Mill - 3A2 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.76667 | 0.15043 | 59.1203 | 77.1135 | 77
MC3 | D1 | 195 | 1850 | 2013-12-15 08:45 | 2013-12-15 12:00 | 400 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 3.25 | 0.17671 | 69.4486 | 21.3688 | 21
MC3 | D1 | 196 | 360 | 2013-12-15 12:00 | 2013-12-15 16:20 | 350 | 423 | 393 | Burners | F7803A Mill - 3A8 Burner High Temperature & High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 4.3333 | 0.74783 | 293.8983 | 67.8227 | 68
MC3 | D1 | 197 | 360 | 2013-12-15 16:20 | 2013-12-16 02:54 | 350 | 423 | 393 | Burners | F1303C Mill - 3C4 Burner Installed Blank & High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 10.5667 | 1.8236 | 716.6598 | 67.8227 | 68
MC3 | D1 | 198 | 360 | 2013-12-16 10:46 | 2013-12-16 14:23 | 335 | 423 | 393 | Burners | F7803D Mill - 3D4 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 3.6167 | 0.7524 | 295.6946 | 81.7589 | 82
MC3 | D1 | 199 | 310 | 2013-12-20 03:47 | 2013-12-20 04:28 | 335 | 423 | 393 | Pulverizer mills | F5903A Coal Mill - Breaker Issue | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.68333 | 0.14216 | 55.8686 | 81.7589 | 82
MC3 | D1 | 200 | 360 | 2013-12-20 13:25 | 2013-12-20 14:58 | 330 | 423 | 393 | Burners | F7803B Mill - 3B9 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 1.55 | 0.34078 | 133.9266 | 86.4043 | 86
MC3 | D1 | 201 | 250 | 2013-12-23 08:30 | 2013-12-23 09:00 | 330 | 423 | 393 | Pulverizer feeders | F0103D Coal Mill Feeder - Belt off track | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.5 | 0.10993 | 43.2021 | 86.4043 | 86
MC3 | D1 | 202 | 310 | 2013-12-23 09:00 | 2013-12-23 11:00 | 225 | 423 | 393 | Pulverizer mills | F4003C and 3D Coal Mill Failed to start | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 2 | 0.93617 | 367.9149 | 183.9574 | 184
MC3 | D1 | 203 | 250 | 2013-12-23 11:00 | 2013-12-23 15:18 | 330 | 423 | 393 | Pulverizer feeders | F0103D Coal Mill Feeder - Belt off track | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 4.3 | 0.94539 | 371.5383 | 86.4043 | 86
MC3 | D1 | 204 | 360 | 2013-12-24 06:56 | 2013-12-24 09:30 | 330 | 423 | 393 | Burners | F7803A Mill - 3A9 Burner high temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 2.5667 | 0.5643 | 221.7709 | 86.4043 | 86
MC3 | D1 | 205 | 1850 | 2013-12-24 09:30 | 2013-12-25 08:15 | 325 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 22.75 | 5.2707 | 2071.3794 | 91.0496 | 91
MC3 | D1 | 206 | 360 | 2013-12-25 08:15 | 2013-12-25 11:30 | 330 | 423 | 393 | Burners | F7803A and 3D Mill - 3D2 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 3.25 | 0.71454 | 280.8138 | 86.4043 | 86
MC3 | MO | 207 | 3110 | 2013-12-26 10:54 | 2013-12-29 10:41 | 0 | 423 | 393 | Condenser tube leaks | F540Condenser Tube Leak Repairs | Mill Creek | Maintenance | Coal | 3 | 2013 | 12 | 71.7833 | 71.7833 | 28210.85 | 393 | 393
MC3 | D1 | 208 | 1850 | 2013-12-29 23:05 | 2013-12-30 04:08 | 313 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 5.05 | 1.3132 | 516.1028 | 102.1986 | 102
MC3 | D4 | 1 | 310 | 2014-01-01 23:20 | 2014-01-02 01:35 | 320 | 423 | 393 | Pulverizer mills | F5303A Coal Mill - Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 2.25 | 0.54787 | 215.3138 | 95.695 | 96
MC3 | D1 | 2 | 360 | 2014-01-05 23:16 | 2014-01-06 02:00 | 330 | 423 | 393 | Burners | F7803A Mill - Burners High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 2.7333 | 0.60095 | 236.1716 | 86.4043 | 86
MC3 | NC | 6 | 1990 | 2014-01-14 08:00 | 2014-01-14 16:40 | 0 | 423 | 393 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Full Load Winter Capability Test | Mill Creek | Other | Coal | 3 | 2014 | 1 | 8.6667 | 8.6667 | 3406 | 393 | 393
MC3 | NC | 3 | 8460 | 2014-01-15 | 2014-01-15 03:06 | 0 | 423 | 393 | Testing A | F790Mid Flow RATA Test | Mill Creek | Other | Coal | 3 | 2014 | 1 | 3.1 | 3.1 | 1218.3 | 393 | 393
MC3 | D4 | 4 | 360 | 2014-01-15 03:06 | 2014-01-15 08:13 | 310 | 423 | 393 | Burners | F5903C Mill - Coal Burner Logic Change | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 5.1167 | 1.3669 | 537.1774 | 104.9858 | 105
MC3 | D4 | 5 | 360 | 2014-01-15 08:13 | 2014-01-15 09:42 | 372 | 423 | 393 | Burners | F7903C Mill - Coal Burner Logic Testing | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 1.4833 | 0.17884 | 70.2848 | 47.383 | 47
MC3 | NC | 7 | 8460 | 2014-01-15 09:42 | 2014-01-15 12:09 | 0 | 423 | 393 | Testing A | F790Full Load RATA Test | Mill Creek | Other | Coal | 3 | 2014 | 1 | 2.45 | 2.45 | 962.85 | 393 | 393
MC3 | D1 | 8 | 360 | 2014-01-15 12:09 | 2014-01-15 13:13 | 355 | 423 | 393 | Burners | F7803D Mill - 3D7 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 1.0667 | 0.17147 | 67.3891 | 63.1773 | 63
MC3 | NC | 9 | 8460 | 2014-01-15 13:14 | 2014-01-15 16:42 | 0 | 423 | 393 | Testing A | F790Full Load RATA Test | Mill Creek | Other | Coal | 3 | 2014 | 1 | 3.4667 | 3.4667 | 1362.4 | 393 | 393
MC3 | D4 | 10 | 310 | 2014-01-17 04:00 | 2014-01-17 05:15 | 330 | 423 | 393 | Pulverizer mills | F5903B Mill - Coal Burner Logic Change | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 1.25 | 0.27482 | 108.0053 | 86.4043 | 86
MC3 | D1 | 11 | 360 | 2014-01-20 08:37 | 2014-01-20 09:20 | 335 | 423 | 393 | Burners | F7803C Mill - 3C3 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 0.71667 | 0.14909 | 58.5939 | 81.7589 | 82
MC3 | D4 | 12 | 360 | 2014-01-20 21:00 | 2014-01-21 00:55 | 325 | 423 | 393 | Burners | F5903A & 3D Mills - Coal Burner Logic Change Over | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 3.9167 | 0.90741 | 356.6111 | 91.0496 | 91
MC3 | D1 | 13 | 300 | 2014-01-23 17:19 | 2014-01-23 23:03 | 335 | 423 | 393 | Pulverizer motors and drives | F5903C Coal Mill Motor - Failed to Start, Breaker Issue | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 5.7333 | 1.1928 | 468.7508 | 81.7589 | 82
MC3 | D1 | 14 | 360 | 2014-01-23 22:08 | 2014-01-23 23:03 | 225 | 423 | 393 | Burners | F7803D Mill - 3D7 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 0.91667 | 0.42908 | 168.6277 | 183.9574 | 184
MC3 | D1 | 15 | 300 | 2014-01-23 23:03 | 2014-01-23 23:23 | 330 | 423 | 393 | Pulverizer motors and drives | F5903C Coal Mill Motor - Failed to Start, Breaker Issue | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 0.33333 | 0.073286 | 28.8014 | 86.4043 | 86
MC3 | D1 | 16 | 360 | 2014-01-24 23:56 | 2014-01-25 01:35 | 360 | 423 | 393 | Burners | F7803D Mill - 3D10 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 1.65 | 0.24574 | 96.5777 | 58.5319 | 59
MC3 | D1 | 17 | 360 | 2014-01-28 09:43 | 2014-01-28 10:42 | 360 | 423 | 393 | Burners | F7803C Mill - 3C2 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 0.98333 | 0.14645 | 57.5564 | 58.5319 | 59
MC3 | D1 | 18 | 360 | 2014-01-28 16:30 | 2014-01-28 17:05 | 360 | 423 | 393 | Burners | F7803B Mill - 3B6 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 0.58333 | 0.086879 | 34.1436 | 58.5319 | 59
MC3 | D1 | 19 | 360 | 2014-01-31 08:09 | 2014-01-31 09:12 | 340 | 423 | 393 | Burners | F7803C Mill - 3C2 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 1.05 | 0.20603 | 80.9691 | 77.1135 | 77
MC3 | D1 | 20 | 250 | 2014-02-07 18:02 | 2014-02-08 05:30 | 325 | 423 | 393 | Pulverizer feeders | F5903C Coal Feeder - Replace Speed Sensor | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 11.4667 | 2.6566 | 1044.0359 | 91.0496 | 91
MC3 | D1 | 21 | 360 | 2014-02-09 09:05 | 2014-02-09 10:25 | 330 | 423 | 393 | Burners | F7803C Mill - 3C3 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 1.3333 | 0.29314 | 115.2057 | 86.4043 | 86
MC3 | D1 | 22 | 360 | 2014-02-09 10:50 | 2014-02-09 16:36 | 330 | 423 | 393 | Burners | F7803C Mill - 3C10 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 5.7667 | 1.2678 | 498.2645 | 86.4043 | 86
MC3 | D1 | 23 | 310 | 2014-02-09 21:52 | 2014-02-10 07:58 | 320 | 423 | 393 | Pulverizer mills | F5903C Primary Air Fan Housing InspectionRepair Suction Box & Hot Air Damper Linkage | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 10.1 | 2.4593 | 966.5199 | 95.695 | 96
MC3 | D4 | 24 | 250 | 2014-02-10 11:00 | 2014-02-10 16:05 | 330 | 423 | 393 | Pulverizer feeders | F0903C Coal Feeder - Calibration | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 5.0833 | 1.1176 | 439.2216 | 86.4043 | 86
MC3 | D1 | 25 | 360 | 2014-02-10 19:42 | 2014-02-10 19:57 | 320 | 423 | 393 | Burners | F7803D Mill - 3D4 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 0.25 | 0.060875 | 23.9238 | 95.695 | 96
MC3 | D1 | 26 | 360 | 2014-02-15 11:11 | 2014-02-15 12:43 | 360 | 423 | 393 | Burners | F7803C Mill - 3C1 & 3C3 Coal Burners High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 1.5333 | 0.22837 | 89.7489 | 58.5319 | 59
MC3 | D1 | 27 | 360 | 2014-02-15 13:28 | 2014-02-15 14:20 | 360 | 423 | 393 | Burners | F7803A Mill - 3A4 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 0.86667 | 0.12908 | 50.7277 | 58.5319 | 59
MC3 | D4 | 28 | 8160 | 2014-02-17 20:00 | 2014-02-18 00:46 | 330 | 423 | 393 | Mist eliminators/demisters and washdown | F590FGD Demister Wash Line - Relocation | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 4.7667 | 1.048 | 411.8603 | 86.4043 | 86
MC3 | D1 | 29 | 360 | 2014-02-21 14:09 | 2014-02-21 15:29 | 330 | 423 | 393 | Burners | F7803D Mill - 3D1 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 1.3333 | 0.29314 | 115.2057 | 86.4043 | 86
MC3 | D1 | 30 | 360 | 2014-02-21 18:21 | 2014-02-21 19:10 | 340 | 423 | 393 | Burners | F7803A Mill - 3A4 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 0.81667 | 0.16024 | 62.976 | 77.1135 | 77
MC3 | D1 | 31 | 360 | 2014-02-22 09:20 | 2014-02-22 11:18 | 330 | 423 | 393 | Burners | F7803C Mill - 3C3 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 1.9667 | 0.43239 | 169.9284 | 86.4043 | 86
MC3 | D1 | 32 | 360 | 2014-02-22 14:45 | 2014-02-22 16:15 | 220 | 423 | 393 | Burners | F7803D Mill - 3D1 Coal Burner High Temperature3B Mill - 3B7 Coal Burner Fire | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 1.5 | 0.71986 | 282.9043 | 188.6028 | 189
MC3 | D1 | 33 | 360 | 2014-02-22 16:15 | 2014-02-22 17:00 | 330 | 423 | 393 | Burners | F7803D Mill - 3D1 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 0.75 | 0.16489 | 64.8032 | 86.4043 | 86
MC3 | D1 | 34 | 360 | 2014-02-22 19:25 | 2014-02-22 20:28 | 330 | 423 | 393 | Burners | F7803D Mill - 3D2 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 1.05 | 0.23085 | 90.7245 | 86.4043 | 86
MC3 | D4 | 35 | 310 | 2014-02-24 23:00 | 2014-02-25 06:39 | 320 | 423 | 393 | Pulverizer mills | F5903C Coal Mill Pyrite Hopper - Replace Top Gate | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 7.65 | 1.8628 | 732.067 | 95.695 | 96
MC3 | D4 | 36 | 876 | 2014-02-25 20:00 | 2014-02-26 04:28 | 215 | 423 | 393 | Soot blower controls | F590Sootblower Regulator - Rebuilt | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 8.4667 | 4.1633 | 1636.1683 | 193.2482 | 193
MC3 | D1 | 37 | 310 | 2014-03-05 05:15 | 2014-03-05 05:48 | 335 | 423 | 393 | Pulverizer mills | F5903A Coal Mill - Breaker Issue | Mill Creek | Derate | Coal | 3 | 2014 | 3 | 0.55 | 0.11442 | 44.9674 | 81.7589 | 82
MC3 | D4 | 38 | 8160 | 2014-03-08 23:30 | 2014-03-09 06:36 | 325 | 423 | 393 | Mist eliminators/demisters and washdown | F590FGD Mist Eliminator - Wash Line Tie In | Mill Creek | Derate | Coal | 3 | 2014 | 3 | 7.1 | 1.6449 | 646.4525 | 91.0496 | 91
MC3 | D1 | 39 | 260 | 2014-03-23 17:17 | 2014-03-23 19:18 | 320 | 423 | 393 | Primary air fan | F5903C Primary Air Fan Outboard Bearing - High Temperature, Changed Oil | Mill Creek | Derate | Coal | 3 | 2014 | 3 | 2.0167 | 0.49106 | 192.985 | 95.695 | 96
MC3 | D1 | 40 | 380 | 2014-03-24 03:18 | 2014-03-24 03:51 | 375 | 423 | 393 | Light-off (igniter) systems (including fuel supply) | F4003D Coal Mill - 3D2 Lighter Could Not Get in Service | Mill Creek | Derate | Coal | 3 | 2014 | 3 | 0.55 | 0.062411 | 24.5277 | 44.5957 | 45
MC3 | PO | 41 | 1801 | 2014-04-01 00:39 | 2014-04-04 18:43 | 0 | 423 | 393 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Planned 1 Week Outage | Mill Creek | Other | Coal | 3 | 2014 | 4 | 90.0667 | 90.0667 | 35396.2 | 393 | 393
MC3 | NC | 42 | 1850 | 2014-04-04 18:43 | 2014-04-05 18:44 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2014 | 4 | 24.0167 | 24.0167 | 9438.55 | 393 | 393
MC3 | D1 | 43 | 1850 | 2014-04-05 18:44 | 2014-04-05 20:21 | 340 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 1.6167 | 0.31722 | 124.6668 | 77.1135 | 77
MC3 | D1 | 44 | 1850 | 2014-04-05 20:21 | 2014-04-06 04:30 | 380 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 8.15 | 0.82849 | 325.5954 | 39.9504 | 40
MC3 | D4 | 45 | 360 | 2014-04-06 04:30 | 2014-04-06 07:08 | 350 | 423 | 393 | Burners | F7803D Mill - 3D7 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 2.6333 | 0.45445 | 178.5998 | 67.8227 | 68
MC3 | D1 | 46 | 1455 | 2014-04-06 12:45 | 2014-04-07 07:30 | 400 | 423 | 393 | Induced draft fans | F8503A Induced Draft Fan - Outboard Bearing High Vibration | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 18.75 | 1.0195 | 400.6649 | 21.3688 | 21
MC3 | D1 | 47 | 1455 | 2014-04-07 07:30 | 2014-04-07 17:45 | 415 | 423 | 393 | Induced draft fans | F8503A Induced Draft Fan - Outboard Bearing High Vibration | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 10.25 | 0.19385 | 76.1844 | 7.4326 | 7
MC3 | D1 | 48 | 1455 | 2014-04-07 17:45 | 2014-04-09 13:19 | 395 | 423 | 393 | Induced draft fans | F8503A Induced Draft Fan - Outboard Bearing High Vibration | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 43.5667 | 2.8838 | 1133.3513 | 26.0142 | 26
MC3 | D1 | 49 | 250 | 2014-04-09 13:19 | 2014-04-10 01:00 | 310 | 423 | 393 | Pulverizer feeders | FW003C Coal Feeder - Plugged, Wet Coal | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 11.6833 | 3.1211 | 1226.5843 | 104.9858 | 105
MC3 | D1 | 50 | 310 | 2014-04-10 01:00 | 2014-04-10 05:33 | 310 | 423 | 393 | Pulverizer mills | F5303D Coal Mill - Fire, Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 4.55 | 1.2155 | 477.6855 | 104.9858 | 105
MC3 | D1 | 51 | 250 | 2014-04-11 00:44 | 2014-04-11 01:09 | 375 | 423 | 393 | Pulverizer feeders | F5903C Coal Feeder - Replaced Shear Pin on Clean Out Conveyor | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 0.41667 | 0.047281 | 18.5816 | 44.5957 | 45
MC3 | D1 | 52 | 360 | 2014-04-11 14:41 | 2014-04-11 15:00 | 340 | 423 | 393 | Burners | F7803D Mill - 3D1 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 0.31667 | 0.062136 | 24.4193 | 77.1135 | 77
MC3 | D1 | 53 | 1455 | 2014-04-14 06:14 | 2014-04-14 10:41 | 355 | 423 | 393 | Induced draft fans | F8503A Induced Draft Fan - Outboard Bearing High Vibration & Air Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 4.45 | 0.71537 | 281.139 | 63.1773 | 63
MC3 | D1 | 54 | 1455 | 2014-04-14 10:41 | 2014-04-14 15:30 | 380 | 423 | 393 | Induced draft fans | F8503A Induced Draft Fan - Outboard Bearing High Vibration & Air Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 4.8167 | 0.48964 | 192.4275 | 39.9504 | 40
MC3 | D1 | 55 | 1455 | 2014-04-14 17:47 | 2014-04-14 20:10 | 400 | 423 | 393 | Induced draft fans | F8503A Induced Draft Fan - Outboard Bearing High Vibration | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 2.3833 | 0.12959 | 50.929 | 21.3688 | 21
MC3 | D1 | 56 | 1455 | 2014-04-14 20:10 | 2014-04-14 21:30 | 406 | 423 | 393 | Induced draft fans | F8503A Induced Draft Fan - Outboard Bearing High Vibration | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 1.3333 | 0.053586 | 21.0591 | 15.7943 | 16
MC3 | D4 | 57 | 876 | 2014-04-14 21:30 | 2014-04-15 07:43 | 260 | 423 | 393 | Soot blower controls | F590Sootblower Regulator - Rebuilt | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 10.2167 | 3.9369 | 1547.2091 | 151.4397 | 151
MC3 | D1 | 58 | 1455 | 2014-04-15 07:43 | 2014-04-15 11:45 | 406 | 423 | 393 | Induced draft fans | F8503A Induced Draft Fan - Outboard Bearing High Vibration | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 4.0333 | 0.1621 | 63.7038 | 15.7943 | 16
MC3 | D1 | 59 | 1455 | 2014-04-15 11:45 | 2014-04-15 15:15 | 418 | 423 | 393 | Induced draft fans | F8503A Induced Draft Fan - Outboard Bearing High Vibration | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 3.5 | 0.041371 | 16.2589 | 4.6454 | 5
MC3 | D1 | 60 | 1455 | 2014-04-17 03:28 | 2014-04-17 06:38 | 410 | 423 | 393 | Induced draft fans | F8503A Induced Draft Fan - Outboard Bearing High Vibration | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 3.1667 | 0.097321 | 38.247 | 12.078 | 12
MC3 | D1 | 61 | 360 | 2014-04-20 21:12 | 2014-04-20 23:05 | 320 | 423 | 393 | Burners | F7803A Mill - 3A1 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 1.8833 | 0.45859 | 180.2257 | 95.695 | 96
MC3 | D1 | 62 | 3412 | 2014-04-21 09:58 | 2014-04-21 23:40 | 400 | 423 | 393 | Feedwater pump drive - steam turbine | F400Turbine Driven Boiler Feed Pump - Surging, Control Issue | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 13.7 | 0.74492 | 292.7525 | 21.3688 | 21
MC3 | D4 | 63 | 3412 | 2014-04-21 23:40 | 2014-04-22 00:20 | 335 | 423 | 393 | Feedwater pump drive - steam turbine | F130Turbine Driven Boiler Feed Pump - High Pressure Steam Supply Isolation | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 0.66667 | 0.13869 | 54.5059 | 81.7589 | 82
MC3 | D1 | 64 | 3412 | 2014-04-22 00:20 | 2014-04-22 09:36 | 400 | 423 | 393 | Feedwater pump drive - steam turbine | F400Turbine Driven Boiler Feed Pump - Surging, Control Issue | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 9.2667 | 0.50386 | 198.0175 | 21.3688 | 21
MC3 | MO | 65 | 1455 | 2014-04-22 09:36 | 2014-04-24 03:07 | 0 | 423 | 393 | Induced draft fans | F3203A & 3B Induced Draft Fans - Clean & Balance | Mill Creek | Maintenance | Coal | 3 | 2014 | 4 | 41.5167 | 41.5167 | 16316.05 | 393 | 393
MC3 | NC | 66 | 1850 | 2014-04-24 03:07 | 2014-04-24 11:07 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2014 | 4 | 8 | 8 | 3144 | 393 | 393
MC3 | D1 | 67 | 3412 | 2014-04-24 11:07 | 2014-04-24 13:17 | 335 | 423 | 393 | Feedwater pump drive - steam turbine | F400Turbine Driven Boiler Feed Pump - Swinging, Control Valve Issue | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 2.1667 | 0.45075 | 177.1442 | 81.7589 | 82
MC3 | D1 | 68 | 1850 | 2014-04-24 13:17 | 2014-04-24 13:47 | 375 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 0.5 | 0.056738 | 22.2979 | 44.5957 | 45
MC3 | D1 | 69 | 1850 | 2014-04-24 13:47 | 2014-04-24 14:29 | 395 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 0.7 | 0.046336 | 18.2099 | 26.0142 | 26
MC3 | D1 | 70 | 3412 | 2014-04-24 15:34 | 2014-04-24 19:30 | 325 | 423 | 393 | Feedwater pump drive - steam turbine | F790Turbine Driven Boiler Feed Pump - Testing | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 3.9333 | 0.91127 | 358.1286 | 91.0496 | 91
MC3 | D1 | 71 | 3149 | 2014-04-28 06:26 | 2014-04-28 06:42 | 405 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 0.26667 | 0.011348 | 4.4596 | 16.7234 | 17
MC3 | D1 | 72 | 250 | 2014-04-28 15:17 | 2014-04-28 19:00 | 320 | 423 | 393 | Pulverizer feeders | F5903C Coal Feeder - Breaker Issue, Water in Cabinet | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 3.7167 | 0.905 | 355.6665 | 95.695 | 96
MC3 | D4 | 73 | 310 | 2014-04-28 22:00 | 2014-04-28 22:40 | 340 | 423 | 393 | Pulverizer mills | F5903C Mill Primary Air Fan - Maintenance Cancelled | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 0.66667 | 0.13081 | 51.409 | 77.1135 | 77
MC3 | D1 | 74 | 250 | 2014-04-29 05:00 | 2014-04-29 05:30 | 325 | 423 | 393 | Pulverizer feeders | F5903C Coal Feeder - Breaker Trip Button Issue | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 0.5 | 0.11584 | 45.5248 | 91.0496 | 91
MC3 | D4 | 75 | 310 | 2014-04-29 23:00 | 2014-04-30 02:50 | 325 | 423 | 393 | Pulverizer mills | F5903C Coal Mill - Primary Air Fan Outboard Bearing Replaced Oil | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 3.8333 | 0.8881 | 349.0236 | 91.0496 | 91
MC3 | D1 | 76 | 3149 | 2014-05-02 10:00 | 2014-05-02 12:15 | 360 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 2.25 | 0.33511 | 131.6968 | 58.5319 | 59
MC3 | D1 | 77 | 3242 | 2014-05-02 12:15 | 2014-05-02 13:41 | 275 | 423 | 393 | Cooling tower fill damage | F1203A Cooling Tower Pump - Backflush | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 1.4333 | 0.5015 | 197.0884 | 137.5035 | 138
MC3 | U1 | 78 | 1710 | 2014-05-03 02:37 | 2014-05-03 08:04 | 0 | 423 | 393 | Combustion/steam condition controls (report local controls --- burners | F420High Furnace Pressure Trip - Operator Error | Mill Creek | Outage | Coal | 3 | 2014 | 5 | 5.45 | 5.45 | 2141.85 | 393 | 393
MC3 | NC | 79 | 1850 | 2014-05-03 08:04 | 2014-05-03 16:20 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2014 | 5 | 8.2667 | 8.2667 | 3248.8 | 393 | 393
MC3 | D1 | 80 | 1850 | 2014-05-03 16:20 | 2014-05-03 19:56 | 410 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 3.6 | 0.11064 | 43.4809 | 12.078 | 12
MC3 | D4 | 81 | 310 | 2014-05-04 22:05 | 2014-05-05 03:59 | 320 | 423 | 393 | Pulverizer mills | F5903C Coal Mill Primary Air Fan - Changed Oil in Outboard Bearing | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 5.9 | 1.4366 | 564.6007 | 95.695 | 96
MC3 | D1 | 82 | 250 | 2014-05-05 09:51 | 2014-05-05 10:33 | 385 | 423 | 393 | Pulverizer feeders | F8203D Coal Feeder - Trip | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 0.7 | 0.062884 | 24.7135 | 35.305 | 35
MC3 | D1 | 83 | 3149 | 2014-05-06 14:34 | 2014-05-06 22:00 | 390 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 7.4333 | 0.57991 | 227.9028 | 30.6596 | 31
MC3 | D1 | 84 | 3149 | 2014-05-07 09:13 | 2014-05-07 10:11 | 400 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 0.96667 | 0.052561 | 20.6565 | 21.3688 | 21
MC3 | D1 | 85 | 3149 | 2014-05-07 10:11 | 2014-05-07 20:20 | 378 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 10.15 | 1.0798 | 424.3564 | 41.8085 | 42
MC3 | D1 | 86 | 3149 | 2014-05-07 20:20 | 2014-05-08 08:30 | 400 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 12.1667 | 0.66154 | 259.987 | 21.3688 | 21
MC3 | D1 | 87 | 3149 | 2014-05-08 08:30 | 2014-05-08 10:30 | 370 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 2 | 0.25059 | 98.4823 | 49.2411 | 49
MC3 | D4 | 88 | 620 | 2014-05-08 22:00 | 2014-05-09 04:41 | 230 | 423 | 393 | Other desuperheater/attemperator problems | F590Superheat Spray Regulator - Replace Bonnet Gasket | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 6.6833 | 3.0494 | 1198.4022 | 179.3121 | 179
MC3 | D4 | 89 | 310 | 2014-05-11 22:00 | 2014-05-12 01:59 | 325 | 423 | 393 | Pulverizer mills | F5903C Coal Mill - Primary Air Fan Bearing Changed Oil | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 3.9833 | 0.92285 | 362.6811 | 91.0496 | 91
MC3 | D1 | 90 | 360 | 2014-05-15 14:05 | 2014-05-15 16:56 | 350 | 423 | 393 | Burners | F7803C Coal Mill - 3C3 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 2.85 | 0.49184 | 193.2947 | 67.8227 | 68
MC3 | D4 | 91 | 310 | 2014-05-16 03:16 | 2014-05-16 04:01 | 355 | 423 | 393 | Pulverizer mills | F5903B Coal Mill - Replaced Motor Overload Relay | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 0.75 | 0.12057 | 47.383 | 63.1773 | 63
MC3 | U1 | 92 | 1080 | 2014-05-20 05:32 | 2014-05-23 18:02 | 0 | 423 | 393 | Economizer B | F540Boiler Tube Leak - Economizer Inlet | Mill Creek | Outage | Coal | 3 | 2014 | 5 | 84.5 | 84.5 | 33208.5 | 393 | 393
MC3 | NC | 93 | 1850 | 2014-05-23 18:02 | 2014-05-24 08:51 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2014 | 5 | 14.8167 | 14.8167 | 5822.95 | 393 | 393
MC3 | D1 | 94 | 1799 | 2014-05-24 09:46 | 2014-05-24 11:55 | 250 | 423 | 393 | Other boiler instrumentation and control problems | F400Boiler Swing | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 2.15 | 0.87931 | 345.5706 | 160.7305 | 161
MC3 | D1 | 95 | 360 | 2014-06-03 08:57 | 2014-06-03 10:17 | 325 | 423 | 393 | Burners | F7803C Coal Mill - 3C1 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 1.3333 | 0.3089 | 121.3995 | 91.0496 | 91
MC3 | U1 | 96 | 1080 | 2014-06-05 18:39 | 2014-06-09 02:50 | 0 | 423 | 393 | Economizer B | F540Boiler Tube Leak - Economizer | Mill Creek | Outage | Coal | 3 | 2014 | 6 | 80.1833 | 80.1833 | 31512.05 | 393 | 393
MC3 | U1 | 97 | 4302 | 2014-06-09 02:51 | 2014-06-09 07:03 | 0 | 423 | 393 | Turbine trip devices (including instruments) | F400Unit Trip - 2% Load Set Timer Issues | Mill Creek | Outage | Coal | 3 | 2014 | 6 | 4.2 | 4.2 | 1650.6 | 393 | 393
MC3 | NC | 98 | 4842 | 2014-06-11 10:00 | 2014-06-11 12:47 | 0 | 423 | 393 | Reactive and capability testing | F790Generator Reactive Power Capability Test | Mill Creek | Other | Coal | 3 | 2014 | 6 | 2.7833 | 2.7833 | 1093.85 | 393 | 393
MC3 | U1 | 99 | 1799 | 2014-07-02 18:54 | 2014-07-03 08:30 | 0 | 423 | 393 | Other boiler instrumentation and control problems | F820Master Fuel Trip | Mill Creek | Outage | Coal | 3 | 2014 | 7 | 13.6 | 13.6 | 5344.8 | 393 | 393
MC3 | U1 | 100 | 3431 | 2014-07-03 16:04 | 2014-07-03 19:02 | 0 | 423 | 393 | Other feedwater valves | F690Low Drum Level - TDBFP Recirc Valve Issues | Mill Creek | Outage | Coal | 3 | 2014 | 7 | 2.9667 | 2.9667 | 1165.9 | 393 | 393
MC3 | D1 | 101 | 1850 | 2014-07-04 05:18 | 2014-07-04 08:35 | 390 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 3.2833 | 0.25615 | 100.6656 | 30.6596 | 31
MC3 | D1 | 102 | 1850 | 2014-07-04 08:35 | 2014-07-04 09:21 | 410 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 0.76667 | 0.023562 | 9.2598 | 12.078 | 12
MC3 | D4 | 103 | 260 | 2014-07-06 21:00 | 2014-07-07 00:25 | 320 | 423 | 393 | Primary air fan | F530C Coal Mill PA Fan Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 3.4167 | 0.83195 | 326.958 | 95.695 | 96
MC3 | NC | 104 | 9656 | 2014-07-07 12:13 | 2014-07-07 15:17 | 0 | 423 | 393 | Other stack or exhaust emissions testing - fossil | F790Full Load SO3 Testing | Mill Creek | Other | Coal | 3 | 2014 | 7 | 3.0667 | 3.0667 | 1205.2 | 393 | 393
MC3 | D4 | 105 | 310 | 2014-07-08 22:00 | 2014-07-09 03:32 | 320 | 423 | 393 | Pulverizer mills | F5303A Coal Mill Maintenance - Inspection and Feeder Calibration | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 5.5333 | 1.3474 | 529.5125 | 95.695 | 96
MC3 | D4 | 106 | 310 | 2014-07-09 22:00 | 2014-07-10 04:08 | 320 | 423 | 393 | Pulverizer mills | F5303B Coal Mill Maintenance - Inspection and Feeder Calibration | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 6.1333 | 1.4935 | 586.9296 | 95.695 | 96
MC3 | D1 | 107 | 310 | 2014-07-10 17:16 | 2014-07-10 18:33 | 320 | 423 | 393 | Pulverizer mills | F5303D Coal Mill Maintenance - Inspection and Feeder Calibration | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 1.2833 | 0.31249 | 122.8086 | 95.695 | 96
MC3 | D4 | 108 | 312 | 2014-07-10 22:00 | 2014-07-11 03:59 | 320 | 423 | 393 | Pulverizer mill classifiers | F5303C Coal Mill Maintenance - Inspection and Feeder Calibration | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 5.9833 | 1.4569 | 572.5753 | 95.695 | 96
MC3 | D1 | 109 | 360 | 2014-07-13 09:56 | 2014-07-13 10:51 | 320 | 423 | 393 | Burners | F7803C8 Burner - High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 0.91667 | 0.22321 | 87.7204 | 95.695 | 96
MC3 | D1 | 110 | 360 | 2014-07-15 10:08 | 2014-07-15 11:28 | 320 | 423 | 393 | Burners | F7803D10 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 1.3333 | 0.32467 | 127.5934 | 95.695 | 96
MC3 | D4 | 111 | 310 | 2014-07-20 21:15 | 2014-07-21 01:12 | 320 | 423 | 393 | Pulverizer mills | F5903C Coal Mill - Inspect Primary Air Fan Dampers | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 3.95 | 0.96182 | 377.9954 | 95.695 | 96
MC3 | NC | 112 | 4490 | 2014-07-21 10:30 | 2014-07-21 12:00 | 0 | 423 | 393 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Reactive Power Capability Test - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 7 | 1.5 | 1.5 | 589.5 | 393 | 393
MC3 | NC | 113 | 8460 | 2014-07-24 10:10 | 2014-07-24 12:53 | 0 | 423 | 393 | Testing A | F790SO3 Test - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 7 | 2.7167 | 2.7167 | 1067.65 | 393 | 393
MC3 | D1 | 114 | 360 | 2014-07-25 21:28 | 2014-07-25 22:19 | 320 | 423 | 393 | Burners | F7803C Coal Mill - 3C1 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 0.85 | 0.20697 | 81.3408 | 95.695 | 96
MC3 | D1 | 115 | 3149 | 2014-07-27 17:00 | 2014-07-27 19:25 | 400 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure - 3A Cooling Tower Fan Trip | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 2.4167 | 0.1314 | 51.6413 | 21.3688 | 21
MC3 | D4 | 116 | 310 | 2014-08-05 22:00 | 2014-08-06 04:00 | 320 | 423 | 393 | Pulverizer mills | F5903B Coal Mill - Repair Seal Air Line | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 6 | 1.461 | 574.1702 | 95.695 | 96
MC3 | MO | 117 | 3110 | 2014-08-07 21:34 | 2014-08-09 01:52 | 0 | 423 | 393 | Condenser tube leaks | F540Condenser Tube Leak | Mill Creek | Maintenance | Coal | 3 | 2014 | 8 | 28.3 | 28.3 | 11121.9 | 393 | 393
MC3 | NC | 118 | 1850 | 2014-08-09 01:52 | 2014-08-09 10:55 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2014 | 8 | 9.05 | 9.05 | 3556.65 | 393 | 393
MC3 | D1 | 119 | 1850 | 2014-08-09 10:55 | 2014-08-09 12:15 | 385 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 1.3333 | 0.11978 | 47.0733 | 35.305 | 35
MC3 | NC | 120 | 4490 | 2014-08-14 08:27 | 2014-08-14 13:11 | 0 | 423 | 393 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Full Load Capability Test | Mill Creek | Other | Coal | 3 | 2014 | 8 | 4.7333 | 4.7333 | 1860.2 | 393 | 393
MC3 | U1 | 121 | 1400 | 2014-08-14 23:41 | 2014-08-15 01:25 | 0 | 423 | 393 | Forced draft fans | F820High Furnace Vacuum Trip - 3B Forced Draft Fan Inlet Damper Stuck | Mill Creek | Outage | Coal | 3 | 2014 | 8 | 1.7333 | 1.7333 | 681.2 | 393 | 393
MC3 | NC | 122 | 1850 | 2014-08-15 01:25 | 2014-08-15 06:32 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2014 | 8 | 5.1167 | 5.1167 | 2010.85 | 393 | 393
MC3 | D1 | 123 | 250 | 2014-08-19 09:38 | 2014-08-19 11:04 | 320 | 423 | 393 | Pulverizer feeders | F8203D Coal Feeder - Trip | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 1.4333 | 0.34901 | 137.1629 | 95.695 | 96
MC3 | D1 | 124 | 360 | 2014-08-25 18:04 | 2014-08-25 21:12 | 320 | 423 | 393 | Burners | F7803C Coal Mill - 3C1 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 3.1333 | 0.76296 | 299.8444 | 95.695 | 96
MC3 | D4 | 125 | 310 | 2014-08-25 21:24 | 2014-08-26 06:24 | 340 | 423 | 393 | Pulverizer mills | F5903C Coal Mill & Primary Air Fan - Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 9 | 1.766 | 694.0213 | 77.1135 | 77
MC3 | D1 | 126 | 9620 | 2014-08-26 18:09 | 2014-08-26 18:33 | 385 | 423 | 393 | Particulate stack emissions (fossil) | F400Particulate Matter Monitor - Faulty Readings | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 0.4 | 0.035934 | 14.122 | 35.305 | 35
MC3 | D1 | 127 | 9620 | 2014-08-26 18:33 | 2014-08-26 19:15 | 330 | 423 | 393 | Particulate stack emissions (fossil) | F400Particulate Matter Monitor - Faulty Readings | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 0.7 | 0.1539 | 60.483 | 86.4043 | 86
MC3 | D1 | 128 | 9620 | 2014-08-26 19:15 | 2014-08-26 20:10 | 285 | 423 | 393 | Particulate stack emissions (fossil) | F400Particulate Matter Monitor - Faulty Readings | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 0.91667 | 0.29905 | 117.5284 | 128.2128 | 128
MC3 | D4 | 129 | 310 | 2014-08-26 23:00 | 2014-08-27 02:26 | 320 | 423 | 393 | Pulverizer mills | F5903C Coal Mill PA Fan - Replace Amp Reading Transducer | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 3.4333 | 0.83601 | 328.553 | 95.695 | 96
MC3 | D4 | 130 | 310 | 2014-09-10 00:01 | 2014-09-10 04:33 | 340 | 423 | 393 | Pulverizer mills | F5903A Coal Mill - Clean Lube Oil Pump Motor | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 4.5333 | 0.88952 | 349.5811 | 77.1135 | 77
MC3 | D4 | 131 | 8125 | 2014-09-12 23:00 | 2014-09-13 03:16 | 300 | 423 | 393 | Scrubber recycle (liquid) pumps | F590FGD 3A1 Recycle Pump - Installed Blank | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 4.2667 | 1.2407 | 487.5801 | 114.2766 | 114
MC3 | NC | 132 | 8460 | 2014-09-16 08:00 | 2014-09-16 14:00 | 0 | 423 | 393 | Testing A | F790RATA Test - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 9 | 6 | 6 | 2358 | 393 | 393
MC3 | NC | 133 | 8460 | 2014-09-16 22:00 | 2014-09-17 01:00 | 0 | 423 | 393 | Testing A | F790RATA Test - Mid Load @ 310 MW | Mill Creek | Other | Coal | 3 | 2014 | 9 | 3 | 3 | 1179 | 393 | 393
MC3 | NC | 134 | 8460 | 2014-09-17 08:00 | 2014-09-17 19:08 | 0 | 423 | 393 | Testing A | F790RATA Test - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 9 | 11.1333 | 11.1333 | 4375.4 | 393 | 393
MC3 | D1 | 135 | 8125 | 2014-09-22 23:29 | 2014-09-23 00:15 | 300 | 423 | 393 | Scrubber recycle (liquid) pumps | F590FGD 3A1 Recycle Pump - Remove Blank | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 0.76667 | 0.22293 | 87.6121 | 114.2766 | 114
MC3 | D4 | 136 | 8125 | 2014-09-23 23:00 | 2014-09-24 | 330 | 423 | 393 | Scrubber recycle (liquid) pumps | F590FGD 3A1 Recycle Pump - Installed Blank | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 1 | 0.21986 | 86.4043 | 86.4043 | 86
MC3 | D1 | 137 | 310 | 2014-09-28 13:32 | 2014-09-28 14:18 | 320 | 423 | 393 | Pulverizer mills | F8203D Coal Mill - Tripped | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 0.76667 | 0.18668 | 73.3662 | 95.695 | 96
MC3 | D1 | 138 | 360 | 2014-09-28 16:28 | 2014-09-29 00:06 | 320 | 423 | 393 | Burners | F7803D Coal Mill - 3D7 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 7.6333 | 1.8587 | 730.4721 | 95.695 | 96
MC3 | D1 | 139 | 310 | 2014-09-29 00:12 | 2014-09-29 03:56 | 320 | 423 | 393 | Pulverizer mills | F5903D Coal Mill - Primary Air Fan Trip, Replaced Light Resistor | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 3.7333 | 0.90906 | 357.2615 | 95.695 | 96
MC3 | D1 | 140 | 360 | 2014-09-30 07:38 | 2014-09-30 08:40 | 320 | 423 | 393 | Burners | F7803B Coal Mill - 3B7 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 1.0333 | 0.25162 | 98.8849 | 95.695 | 96
MC3 | D1 | 141 | 310 | 2014-10-01 05:58 | 2014-10-01 06:50 | 331 | 423 | 393 | Pulverizer mills | F8203D Coal Mill - Primary Air Fan Trip | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 0.86667 | 0.18849 | 74.0785 | 85.4752 | 85
MC3 | D4 | 142 | 250 | 2014-10-01 22:00 | 2014-10-02 03:49 | 326 | 423 | 393 | Pulverizer feeders | F0903C Coal Feeder - Calibration | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 5.8167 | 1.3338 | 524.2013 | 90.1206 | 90
MC3 | D4 | 143 | 250 | 2014-10-02 22:00 | 2014-10-03 03:30 | 320 | 423 | 393 | Pulverizer feeders | F0903B Coal Feeder - Calibration | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 5.5 | 1.3392 | 526.3227 | 95.695 | 96
MC3 | D1 | 144 | 360 | 2014-10-03 14:40 | 2014-10-03 15:30 | 325 | 423 | 393 | Burners | F7803D Coal Mill - 3D7 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 0.83333 | 0.19307 | 75.8747 | 91.0496 | 91
MC3 | PO | 145 | 1801 | 2014-10-03 23:16 | 2014-10-12 09:07 | 0 | 423 | 393 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Planned One Week Outage | Mill Creek | Other | Coal | 3 | 2014 | 10 | 201.85 | 201.85 | 79327.05 | 393 | 393
MC3 | SF | 146 | 4309 | 2014-10-12 09:07 | 2014-10-12 10:10 | 0 | 423 | 393 | Other turbine instrument and control problems | F820Turbine Master Trip | Mill Creek | Outage | Coal | 3 | 2014 | 10 | 1.05 | 1.05 | 412.65 | 393 | 393
MC3 | NC | 147 | 1850 | 2014-10-12 10:10 | 2014-10-13 10:27 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 3 | 2014 | 10 | 24.2833 | 24.2833 | 9543.35 | 393 | 393
MC3 | D1 | 148 | 1850 | 2014-10-13 10:27 | 2014-10-13 11:50 | 337 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 1.3833 | 0.28125 | 110.5293 | 79.9007 | 80
MC3 | D1 | 149 | 1850 | 2014-10-13 11:50 | 2014-10-13 14:48 | 315 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 2.9667 | 0.75745 | 297.6766 | 100.3404 | 100
MC3 | D1 | 150 | 1850 | 2014-10-13 14:48 | 2014-10-13 15:43 | 291 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica/Recycle Pump Trip - Reaction Tank Low Level | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 0.91667 | 0.28605 | 112.4184 | 122.6383 | 123
MC3 | D1 | 151 | 1850 | 2014-10-13 15:43 | 2014-10-14 00:39 | 312 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 8.9333 | 2.3442 | 921.2738 | 103.1277 | 103
MC3 | D1 | 152 | 1850 | 2014-10-14 00:39 | 2014-10-14 02:30 | 390 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 1.85 | 0.14433 | 56.7202 | 30.6596 | 31
MC3 | D1 | 153 | 1850 | 2014-10-14 02:30 | 2014-10-14 09:47 | 410 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 7.2833 | 0.22384 | 87.9682 | 12.078 | 12
MC3 | D4 | 154 | 8125 | 2014-10-15 23:00 | 2014-10-15 23:46 | 300 | 423 | 393 | Scrubber recycle (liquid) pumps | F130FGD 3A1 Recycle Pump - Installed Blank | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 0.76667 | 0.22293 | 87.6121 | 114.2766 | 114
MC3 | D4 | 155 | 360 | 2014-10-21 22:00 | 2014-10-22 04:01 | 340 | 423 | 393 | Burners | F5303D Coal Mill - 3D5 Burner Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 6.0167 | 1.1806 | 463.9661 | 77.1135 | 77
MC3 | D1 | 156 | 360 | 2014-10-22 04:01 | 2014-10-22 08:13 | 340 | 423 | 393 | Burners | F1203D Coal Mill - 3D5 Conduit Plugged, Installing Blank at Burner | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 4.2 | 0.82411 | 323.8766 | 77.1135 | 77
MC3 | D4 | 157 | 360 | 2014-10-23 22:00 | 2014-10-24 06:20 | 340 | 423 | 393 | Burners | F6303D Coal Mill - 3D5 Burner Removed Blank after Conduit Cleaned Out | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 8.3333 | 1.6351 | 642.6123 | 77.1135 | 77
MC3 | D1 | 158 | 360 | 2014-10-24 08:05 | 2014-10-24 08:45 | 320 | 423 | 393 | Burners | F7803D Coal Mill - 3D10 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 0.66667 | 0.16233 | 63.7967 | 95.695 | 96
MC3 | D1 | 159 | 331 | 2014-10-27 23:16 | 2014-10-28 03:21 | 320 | 423 | 393 | Pulverizer system coal leaks (other than pulverizers | F5403C Coal Mill - Raw Coal Conduit Leak | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 4.0833 | 0.99429 | 390.7547 | 95.695 | 96
MC3 | D1 | 160 | 260 | 2014-10-29 06:55 | 2014-10-29 10:43 | 330 | 423 | 393 | Primary air fan | F5903D Coal Mill Primary Air Fan - Breaker Issue | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 3.8 | 0.83546 | 328.3362 | 86.4043 | 86
MC3 | D1 | 161 | 260 | 2014-10-30 05:25 | 2014-10-30 05:58 | 330 | 423 | 393 | Primary air fan | F5903D Coal Mill Primary Air Fan - Breaker Issue | Mill Creek | Derate | Coal | 3 | 2014 | 10 | 0.55 | 0.12092 | 47.5223 | 86.4043 | 86
MC3 | D4 | 162 | 250 | 2014-11-05 23:00 | 2014-11-06 03:36 | 330 | 423 | 393 | Pulverizer feeders | F5903D Coal Feeder - Replace Door Gasket | Mill Creek | Derate | Coal | 3 | 2014 | 11 | 4.6 | 1.0113 | 397.4596 | 86.4043 | 86
MC3 | D1 | 163 | 360 | 2014-11-08 13:44 | 2014-11-08 15:05 | 330 | 423 | 393 | Burners | F7803C Coal Mill - 3C8 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 11 | 1.35 | 0.29681 | 116.6457 | 86.4043 | 86
MC3 | D1 | 164 | 360 | 2014-11-09 02:45 | 2014-11-09 03:40 | 330 | 423 | 393 | Burners | F7803C Coal Mill - 3C8 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 11 | 0.91667 | 0.20154 | 79.2039 | 86.4043 | 86
MC3 | D1 | 165 | 260 | 2014-11-09 18:00 | 2014-11-09 21:00 | 320 | 423 | 393 | Primary air fan | F5903D Coal Mill Primary Air Fan - Breaker Issues | Mill Creek | Derate | Coal | 3 | 2014 | 11 | 3 | 0.7305 | 287.0851 | 95.695 | 96
MC3 | D4 | 166 | 260 | 2014-11-11 | 2014-11-11 04:03 | 320 | 423 | 393 | Primary air fan | F5903D Coal Mill Primary Air Fan - Replaced Breaker | Mill Creek | Derate | Coal | 3 | 2014 | 11 | 4.05 | 0.98617 | 387.5649 | 95.695 | 96
MC3 | NC | 167 | 8700 | 2014-11-12 07:16 | 2014-11-12 18:41 | 0 | 423 | 393 | CEMS Certification and Recertification | F790Particulate Matter Test - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 11 | 11.4167 | 11.4167 | 4486.75 | 393 | 393
MC3 | NC | 168 | 8700 | 2014-11-13 07:20 | 2014-11-13 17:20 | 0 | 423 | 393 | CEMS Certification and Recertification | F790Particulate Matter Test - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 11 | 10 | 10 | 3930 | 393 | 393
MC3 | NC | 169 | 8700 | 2014-11-14 07:00 | 2014-11-14 12:42 | 0 | 423 | 393 | CEMS Certification and Recertification | F790Particulate Matter Test @ Full Load | Mill Creek | Other | Coal | 3 | 2014 | 11 | 5.7 | 5.7 | 2240.1 | 393 | 393
MC3 | D1 | 170 | 360 | 2014-11-25 09:52 | 2014-11-25 10:40 | 335 | 423 | 393 | Burners | F7803C Coal Mill - 3C8 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 11 | 0.8 | 0.16643 | 65.4071 | 81.7589 | 82
MC3 | D1 | 171 | 360 | 2014-11-25 14:39 | 2014-11-25 16:16 | 335 | 423 | 393 | Burners | F7803C Coal Mill - 3C8 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 11 | 1.6167 | 0.33633 | 132.1768 | 81.7589 | 82
MC3 | D1 | 172 | 360 | 2014-11-25 18:40 | 2014-11-25 19:32 | 330 | 423 | 393 | Burners | F7803C Coal Mill - 3C8 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 11 | 0.86667 | 0.19054 | 74.8837 | 86.4043 | 86
MC3 | D1 | 173 | 360 | 2014-11-29 20:50 | 2014-11-29 22:11 | 330 | 423 | 393 | Burners | F7803B Coal Mill - 3B7 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 11 | 1.35 | 0.29681 | 116.6457 | 86.4043 | 86
MC3 | D4 | 174 | 1160 | 2014-12-04 23:59 | 2014-12-05 04:00 | 300 | 423 | 393 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 4.0167 | 1.168 | 459.011 | 114.2766 | 114
MC3 | NC | 175 | 1160 | 2014-12-05 23:28 | 2014-12-06 02:20 | 0 | 423 | 393 | First reheater B | F320Boiler Deslag - First Reheater, Full Load Available as Needed | Mill Creek | Other | Coal | 3 | 2014 | 12 | 2.8667 | 2.8667 | 1126.6 | 393 | 393
MC3 | NC | 176 | 1160 | 2014-12-07 | 2014-12-07 04:12 | 0 | 423 | 393 | First reheater B | F320Boiler Deslag - First Reheater, Full Load Available as Needed | Mill Creek | Other | Coal | 3 | 2014 | 12 | 4.2 | 4.2 | 1650.6 | 393 | 393
MC3 | D1 | 177 | 360 | 2014-12-09 16:04 | 2014-12-09 17:50 | 320 | 423 | 393 | Burners | F7803C Coal Mill - 3C8 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 1.7667 | 0.43018 | 169.0612 | 95.695 | 96
MC3 | D1 | 178 | 1850 | 2014-12-10 15:00 | 2014-12-10 20:22 | 388 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 5.3667 | 0.44405 | 174.5118 | 32.5177 | 33
MC3 | D1 | 179 | 1850 | 2014-12-10 20:22 | 2014-12-10 21:43 | 367 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 1.35 | 0.17872 | 70.2383 | 52.0284 | 52
MC3 | D1 | 180 | 1850 | 2014-12-10 21:43 | 2014-12-14 01:40 | 325 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 75.95 | 17.596 | 6915.2206 | 91.0496 | 91
MC3 | D1 | 181 | 8280 | 2014-12-10 22:20 | 2014-12-10 22:55 | 215 | 423 | 393 | Reagent feed piping | F590FGD Reactive Feed Return Line - Broken, Demo Issue | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 0.58333 | 0.28684 | 112.7281 | 193.2482 | 193
MC3 | MO | 182 | 3110 | 2014-12-14 01:40 | 2014-12-16 00:31 | 0 | 423 | 393 | Condenser tube leaks | F540Condenser Tube Leaks | Mill Creek | Maintenance | Coal | 3 | 2014 | 12 | 46.85 | 46.85 | 18412.05 | 393 | 393
MC3 | NC | 183 | 1850 | 2014-12-16 00:31 | 2014-12-16 12:31 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2014 | 12 | 12 | 12 | 4716 | 393 | 393
MC3 | D1 | 184 | 1850 | 2014-12-16 12:31 | 2014-12-16 14:06 | 240 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 1.5833 | 0.68499 | 269.2004 | 170.0213 | 170
MC3 | D1 | 185 | 1850 | 2014-12-16 14:06 | 2014-12-16 22:37 | 335 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 8.5167 | 1.7718 | 696.313 | 81.7589 | 82
MC3 | D1 | 186 | 1850 | 2014-12-16 22:37 | 2014-12-17 08:00 | 400 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 9.3833 | 0.5102 | 200.5105 | 21.3688 | 21
MC3 | D1 | 187 | 1160 | 2014-12-19 23:45 | 2014-12-20 04:35 | 210 | 423 | 393 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 4.8333 | 2.4338 | 956.4858 | 197.8936 | 198
MC3 | D1 | 188 | 360 | 2014-12-20 06:51 | 2014-12-20 08:29 | 320 | 423 | 393 | Burners | F7803C Coal Mill - 3C8 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 1.6333 | 0.39771 | 156.3019 | 95.695 | 96
MC3 | D1 | 189 | 360 | 2014-12-21 17:20 | 2014-12-21 18:20 | 320 | 423 | 393 | Burners | F7803D Coal Mill - 3D6 & 3D7 Burner High Temperature - blanked | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 1 | 0.2435 | 95.695 | 95.695 | 96
MC3 | D1 | 190 | 360 | 2014-12-21 18:47 | 2014-12-21 20:11 | 320 | 423 | 393 | Burners | F7803D Coal Mill - 3D6 & 3D7 Burner High Temperature - blanked | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 1.4 | 0.3409 | 133.973 | 95.695 | 96
MC3 | D1 | 191 | 360 | 2014-12-22 16:06 | 2014-12-22 17:11 | 340 | 423 | 393 | Burners | F7803C Coal Mill - 3C8 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 1.0833 | 0.21257 | 83.5396 | 77.1135 | 77
MC3 | D1 | 192 | 360 | 2014-12-28 10:10 | 2014-12-28 11:00 | 320 | 423 | 393 | Burners | F7803C Coal Mill - 3C3 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 0.83333 | 0.20292 | 79.7459 | 95.695 | 96
MC3 | NC | 193 | 8825 | 2014-12-30 09:00 | 2014-12-30 14:18 | 0 | 423 | 393 | Other SCR NOx problems | F790SCR Tuniing - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 12 | 5.3 | 5.3 | 2082.9 | 393 | 393
MC3 | D1 | 194 | 95 | 2014-12-30 17:20 | 2014-12-30 17:33 | 320 | 423 | 393 | Bunker flow problems | F1203C Coal Feeder - Plugged in Silo | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 0.21667 | 0.052758 | 20.7339 | 95.695 | 96
MC3 | D1 | 1 | 8657 | 2015-01-08 07:36 | 2015-01-09 11:45 | 400 | 423 | 393 | Ash handling system and hoppers | F480Particulate Matter Issue - Frozen Air Lines | Mill Creek | Derate | Coal | 3 | 2015 | 1 | 28.15 | 1.5306 | 601.5316 | 21.3688 | 21
MC3 | D1 | 2 | 250 | 2015-02-02 22:24 | 2015-02-03 04:23 | 230 | 423 | 393 | Pulverizer feeders | F1203B Mill coal feeder conduit plugged | Mill Creek | Derate | Coal | 3 | 2015 | 2 | 5.9833 | 2.73 | 1072.8838 | 179.3121 | 179
MC3 | D4 | 3 | 250 | 2015-02-02 22:24 | 2015-02-03 06:43 | 330 | 423 | 393 | Pulverizer feeders | F0903A mill feeder planned calibration | Mill Creek | Derate | Coal | 3 | 2015 | 2 | 8.3167 | 1.8285 | 718.5954 | 86.4043 | 86
MC3 | D4 | 5 | 250 | 2015-02-03 23:00 | 2015-02-04 04:38 | 320 | 423 | 393 | Pulverizer feeders | F0903B Mill feeder planned calibration and mill inspection | Mill Creek | Derate | Coal | 3 | 2015 | 2 | 5.6333 | 1.3717 | 539.082 | 95.695 | 96
MC3 | NC | 4 | 9999 | 2015-02-04 07:00 | 2015-02-04 13:35 | 0 | 423 | 393 | Total unit performance testing (use appropriate codes for individual component testing) | F790Winter Full Load Capability Test | Mill Creek | Other | Coal | 3 | 2015 | 2 | 6.5833 | 6.5833 | 2587.25 | 393 | 393
MC3 | D4 | 6 | 250 | 2015-02-04 23:00 | 2015-02-05 04:35 | 320 | 423 | 393 | Pulverizer feeders | F0903C Coal Feeder - Calibration & Mill Inspection | Mill Creek | Derate | Coal | 3 | 2015 | 2 | 5.5833 | 1.3595 | 534.2973 | 95.695 | 96
MC3 | D4 | 7 | 250 | 2015-02-05 23:00 | 2015-02-06 04:58 | 320 | 423 | 393 | Pulverizer feeders | F0903D Feeder - Calibration and mill inspection | Mill Creek | Derate | Coal | 3 | 2015 | 2 | 5.9667 | 1.4529 | 570.9804 | 95.695 | 96
MC3 | D1 | 8 | 360 | 2015-02-11 20:31 | 2015-02-11 22:46 | 330 | 423 | 393 | Burners | F7803B Coal Mill - 3B6 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2015 | 2 | 2.25 | 0.49468 | 194.4096 | 86.4043 | 86
MC3 | D1 | 9 | 250 | 2015-02-22 21:37 | 2015-02-23 00:02 | 320 | 423 | 393 | Pulverizer feeders | F4003A coal feeder. Feeder kept tripping. | Mill Creek | Derate | Coal | 3 | 2015 | 2 | 2.4167 | 0.58846 | 231.263 | 95.695 | 96
MC3 | D1 | 10 | 9620 | 2015-02-27 01:07 | 2015-02-27 09:15 | 375 | 423 | 393 | Particulate stack emissions (fossil) | FE00PM Compliance - Fly Ash Hoppers Full | Mill Creek | Derate | Coal | 3 | 2015 | 2 | 8.1333 | 0.92293 | 362.7121 | 44.5957 | 45
MC3 | D1 | 11 | 9620 | 2015-02-27 09:15 | 2015-02-27 14:54 | 400 | 423 | 393 | Particulate stack emissions (fossil) | FE00PM Compliance - Fly Ash Hoppers full | Mill Creek | Derate | Coal | 3 | 2015 | 2 | 5.65 | 0.30721 | 120.7337 | 21.3688 | 21
MC3 | MO | 12 | 3110 | 2015-02-28 10:27 | 2015-03-03 01:17 | 0 | 423 | 393 | Condenser tube leaks | F540Condenser leak | Mill Creek | Maintenance | Coal | 3 | 2015 | 2 | 62.8333 | 62.8333 | 24693.5 | 393 | 393
MC3 | NC | 13 | 1850 | 2015-03-03 01:17 | 2015-03-03 13:17 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica @ Warm Start-up | Mill Creek | Other | Coal | 3 | 2015 | 3 | 12 | 12 | 4716 | 393 | 393
MC3 | D1 | 14 | 1850 | 2015-03-03 13:17 | 2015-03-03 18:11 | 228 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 4.9 | 2.2589 | 887.734 | 181.1702 | 181
MC3 | D1 | 15 | 1850 | 2015-03-03 18:11 | 2015-03-03 18:48 | 323 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 0.61667 | 0.14578 | 57.2931 | 92.9078 | 93
MC3 | D1 | 16 | 1850 | 2015-03-03 18:48 | 2015-03-04 06:30 | 353 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 11.7 | 1.9362 | 760.9149 | 65.0355 | 65
MC3 | D1 | 17 | 360 | 2015-03-07 07:00 | 2015-03-07 08:00 | 340 | 423 | 393 | Burners | F7803D Coal Mill - High Burner Temp | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 1 | 0.19622 | 77.1135 | 77.1135 | 77
MC3 | D1 | 18 | 262 | 2015-03-08 01:22 | 2015-03-08 03:06 | 325 | 423 | 393 | Primary air fan lube oil system | F5703C Mill PA Fan - Oil Change | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 1.7333 | 0.40158 | 157.8194 | 91.0496 | 91
MC3 | D1 | 19 | 360 | 2015-03-09 08:38 | 2015-03-09 08:49 | 320 | 423 | 393 | Burners | F7803D Mill - High Burner Temp | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 0.18333 | 0.044641 | 17.5441 | 95.695 | 96
MC3 | D1 | 20 | 360 | 2015-03-09 08:49 | 2015-03-09 09:42 | 320 | 423 | 393 | Burners | F7803B Mill - High Burner Temp | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 0.88333 | 0.21509 | 84.5306 | 95.695 | 96
MC3 | D1 | 21 | 1455 | 2015-03-09 19:28 | 2015-03-09 20:53 | 395 | 423 | 393 | Induced draft fans | F540ID Fan Runback | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 1.4167 | 0.093775 | 36.8534 | 26.0142 | 26
MC3 | D1 | 22 | 360 | 2015-03-11 10:22 | 2015-03-11 10:47 | 320 | 423 | 393 | Burners | F7803D Mill Burner Temps | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 0.41667 | 0.10146 | 39.8729 | 95.695 | 96
MC3 | D1 | 23 | 360 | 2015-03-11 18:44 | 2015-03-11 21:46 | 320 | 423 | 393 | Burners | F7803D Mill Burner Temps | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 3.0333 | 0.73861 | 290.2749 | 95.695 | 96
MC3 | D1 | 24 | 360 | 2015-03-16 11:28 | 2015-03-16 12:21 | 390 | 423 | 393 | Burners | F7803D Coal Mill - 3D10 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 0.88333 | 0.068913 | 27.0826 | 30.6596 | 31
MC3 | D1 | 25 | 360 | 2015-03-17 22:52 | 2015-03-17 23:39 | 330 | 423 | 393 | Burners | F7803D Coal Mill - 3D10 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 0.78333 | 0.17222 | 67.6833 | 86.4043 | 86
MC3 | D1 | 26 | 360 | 2015-03-18 08:16 | 2015-03-18 08:40 | 335 | 423 | 393 | Burners | F7803D Coal Mill - 3D10 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 0.4 | 0.083215 | 32.7035 | 81.7589 | 82
MC3 | MO | 27 | 8425 | 2015-03-20 15:14 | 2015-03-22 22:56 | 0 | 423 | 393 | Miscellaneous mechanical failures | F590Cleaned chevrons | Mill Creek | Maintenance | Coal | 3 | 2015 | 3 | 55.7 | 55.7 | 21890.1 | 393 | 393
MC3 | NC | 28 | 1850 | 2015-03-22 22:56 | 2015-03-23 11:26 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start | Mill Creek | Other | Coal | 3 | 2015 | 3 | 12.5 | 12.5 | 4912.5 | 393 | 393
MC3 | D1 | 29 | 1850 | 2015-03-23 11:26 | 2015-03-23 21:09 | 300 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 9.7167 | 2.8254 | 1110.3876 | 114.2766 | 114
MC3 | D1 | 30 | 1455 | 2015-03-26 07:28 | 2015-03-26 07:59 | 405 | 423 | 393 | Induced draft fans | F8503A ID Fan Vibration | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 0.51667 | 0.021986 | 8.6404 | 16.7234 | 17
MC3 | D1 | 31 | 1455 | 2015-03-27 06:01 | 2015-03-27 20:58 | 405 | 423 | 393 | Induced draft fans | F8503A ID Fan Vibration | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 14.95 | 0.63617 | 250.0149 | 16.7234 | 17
MC3 | D1 | 32 | 360 | 2015-03-27 20:58 | 2015-03-27 21:30 | 340 | 423 | 393 | Burners | F7803D Mill Burner Temp | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 0.53333 | 0.10465 | 41.1272 | 77.1135 | 77
MC3 | D1 | 33 | 1455 | 2015-03-27 21:30 | 2015-03-29 22:00 | 405 | 423 | 393 | Induced draft fans | F8503A ID Fan Vibration | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 48.5 | 2.0638 | 811.0851 | 16.7234 | 17
MC3 | D4 | 34 | 250 | 2015-03-29 22:00 | 2015-03-30 03:08 | 320 | 423 | 393 | Pulverizer feeders | F5903B Coal Mill Feeder hatch repair | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 5.1333 | 1.25 | 491.2345 | 95.695 | 96
MC3 | D1 | 35 | 1455 | 2015-03-30 03:08 | 2015-04-04 19:11 | 406 | 423 | 393 | Induced draft fans | F8503A ID Fan Vibration | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 136.05 | 5.4677 | 2148.8181 | 15.7943 | 16
MC3 | D1 | 36 | 360 | 2015-04-04 19:11 | 2015-04-05 11:58 | 335 | 423 | 393 | Burners | FR003C Coal Mill Burner - Coal smoldering | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 16.7833 | 3.4916 | 1372.1863 | 81.7589 | 82
MC3 | D1 | 37 | 1455 | 2015-04-05 11:58 | 2015-04-06 06:18 | 405 | 423 | 393 | Induced draft fans | F8503A ID Fan Vibration | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 18.3333 | 0.78014 | 306.5957 | 16.7234 | 17
MC3 | D1 | 38 | 1455 | 2015-04-06 06:18 | 2015-04-07 06:13 | 390 | 423 | 393 | Induced draft fans | F8503A ID Fan Vibration | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 23.9167 | 1.8658 | 733.2748 | 30.6596 | 31
MC3 | D1 | 39 | 260 | 2015-04-07 06:13 | 2015-04-07 07:23 | 320 | 423 | 393 | Primary air fan | F7803C Coal Mill PA Fan Bearing Temp | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 1.1667 | 0.28408 | 111.6442 | 95.695 | 96
MC3 | D4 | 40 | 260 | 2015-04-07 07:23 | 2015-04-07 18:22 | 340 | 423 | 393 | Primary air fan | F7803C Coal Mill Primary Air Fan Bearing Temp | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 10.9833 | 2.1551 | 846.963 | 77.1135 | 77
MC3 | D1 | 41 | 1455 | 2015-04-07 18:22 | 2015-04-08 05:52 | 405 | 423 | 393 | Induced draft fans | F8503A ID Fan Vibration | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 11.5 | 0.48936 | 192.3191 | 16.7234 | 17
MC3 | D1 | 42 | 260 | 2015-04-08 05:52 | 2015-04-08 14:02 | 320 | 423 | 393 | Primary air fan | F7803C Coal Mill PA Fan Bearing Temp | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 8.1667 | 1.9886 | 781.5095 | 95.695 | 96
MC3 | D1 | 43 | 1455 | 2015-04-08 14:02 | 2015-04-10 23:39 | 405 | 423 | 393 | Induced draft fans | F8503A ID Fan Vibration | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 57.6167 | 2.4518 | 963.5468 | 16.7234 | 17
MC3 | MO | 44 | 1455 | 2015-04-10 23:39 | 2015-04-12 08:03 | 0 | 423 | 393 | Induced draft fans | FC003A ID Fan Cleaning | Mill Creek | Maintenance | Coal | 3 | 2015 | 4 | 32.4 | 32.4 | 12733.2 | 393 | 393
MC3 | NC | 45 | 1850 | 2015-04-12 08:03 | 2015-04-12 14:31 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start | Mill Creek | Other | Coal | 3 | 2015 | 4 | 6.4667 | 6.4667 | 2541.4 | 393 | 393
MC3 | D1 | 46 | 360 | 2015-04-13 07:45 | 2015-04-13 08:07 | 350 | 423 | 393 | Burners | F7803D Mill - High Burner Temps | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 0.36667 | 0.063278 | 24.8683 | 67.8227 | 68
MC3 | D1 | 47 | 360 | 2015-04-14 05:09 | 2015-04-14 05:31 | 374 | 423 | 393 | Burners | F7803D Mill - High Burner Temps | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 0.36667 | 0.042474 | 16.6924 | 45.5248 | 46
MC3 | D1 | 48 | 360 | 2015-04-14 05:54 | 2015-04-14 07:06 | 370 | 423 | 393 | Burners | F7803D Mill - High Burner Temps | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 1.2 | 0.15035 | 59.0894 | 49.2411 | 49
MC3 | D1 | 49 | 385 | 2015-04-21 19:57 | 2015-04-21 20:29 | 360 | 423 | 393 | Igniters | F400Igniter issues | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 0.53333 | 0.079433 | 31.217 | 58.5319 | 59
MC3 | D1 | 50 | 360 | 2015-04-25 06:57 | 2015-04-25 08:45 | 325 | 423 | 393 | Burners | F7803D Mill Burner Temperature | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 1.8 | 0.41702 | 163.8894 | 91.0496 | 91
MC3 | MO | 51 | 1488 | 2015-05-01 00:22 | 2015-05-04 06:12 | 0 | 423 | 393 | Air heater (regenerative) | F320Air Pre heater wash | Mill Creek | Maintenance | Coal | 3 | 2015 | 5 | 77.8333 | 77.8333 | 30588.5 | 393 | 393
MC3 | NC | 52 | 1850 | 2015-05-04 06:12 | 2015-05-05 06:12 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica at Warm Start-up | Mill Creek | Other | Coal | 3 | 2015 | 5 | 24 | 24 | 9432 | 393 | 393
MC3 | D1 | 53 | 360 | 2015-05-07 15:12 | 2015-05-07 16:06 | 330 | 423 | 393 | Burners | F7803D Coal Mill Burner Temps | Mill Creek | Derate | Coal | 3 | 2015 | 5 | 0.9 | 0.19787 | 77.7638 | 86.4043 | 86
MC3 | D1 | 54 | 3149 | 2015-05-11 12:00 | 2015-05-11 18:22 | 400 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High backpressure | Mill Creek | Derate | Coal | 3 | 2015 | 5 | 6.3667 | 0.34618 | 136.048 | 21.3688 | 21
MC3 | D1 | 55 | 1710 | 2015-05-11 18:22 | 2015-05-11 20:34 | 415 | 423 | 393 | Combustion/steam condition controls (report local controls --- burners | F400Max steam flow | Mill Creek | Derate | Coal | 3 | 2015 | 5 | 2.2 | 0.041608 | 16.3518 | 7.4326 | 7
MC3 | D1 | 56 | 3149 | 2015-05-17 15:20 | 2015-05-17 18:38 | 410 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High backpressure | Mill Creek | Derate | Coal | 3 | 2015 | 5 | 3.3 | 0.10142 | 39.8574 | 12.078 | 12
MC3 | U1 | 57 | 3661 | 2015-05-31 15:57 | 2015-06-01 09:18 | 0 | 423 | 393 | 4160-volt circuit breakers | FR003A-2 Main Aux. breaker fire | Mill Creek | Outage | Coal | 3 | 2015 | 5 | 17.35 | 17.35 | 6818.55 | 393 | 393
MC3 | NC | 58 | 1850 | 2015-06-01 09:18 | 2015-06-01 09:19 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start | Mill Creek | Other | Coal | 3 | 2015 | 6 | 0.016667 | 0.016667 | 6.55 | 393 | 393
MC3 | U1 | 59 | 4740 | 2015-06-01 09:19 | 2015-06-01 10:22 | 0 | 423 | 393 | Emergency generator trip devices | F420Sequential trip | Mill Creek | Outage | Coal | 3 | 2015 | 6 | 1.05 | 1.05 | 412.65 | 393 | 393
MC3 | NC | 60 | 1850 | 2015-06-01 10:22 | 2015-06-01 13:00 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ hot start | Mill Creek | Other | Coal | 3 | 2015 | 6 | 2.6333 | 2.6333 | 1034.9 | 393 | 393
MC3 | D1 | 61 | 3661 | 2015-06-01 13:00 | 2015-06-03 16:12 | 210 | 423 | 393 | 4160-volt circuit breakers | F5903A - 2 Main Aux Breaker work | Mill Creek | Derate | Coal | 3 | 2015 | 6 | 51.2 | 25.7816 | 10132.1532 | 197.8936 | 198
MC3 | D1 | 62 | 3661 | 2015-06-03 16:12 | 2015-06-04 03:13 | 175 | 423 | 393 | 4160-volt circuit breakers | F5903A-2 Main Aux Breaker work | Mill Creek | Derate | Coal | 3 | 2015 | 6 | 11.0167 | 6.4589 | 2538.365 | 230.4113 | 230
MC3 | D1 | 63 | 3210 | 2015-06-04 03:13 | 2015-06-04 04:02 | 330 | 423 | 393 | Circulating water pumps | F5903A Cooling Tower pump | Mill Creek | Derate | Coal | 3 | 2015 | 6 | 0.81667 | 0.17955 | 70.5635 | 86.4043 | 86
MC3 | D1 | 64 | 8580 | 2015-06-08 06:55 | 2015-06-08 20:20 | 290 | 423 | 393 | Mechanical precipitator problems | F590"A" Side precipitator hopper full | Mill Creek | Derate | Coal | 3 | 2015 | 6 | 13.4167 | 4.2185 | 1657.8623 | 123.5674 | 124
MC3 | MO | 65 | 8550 | 2015-06-12 22:19 | 2015-06-15 06:27 | 0 | 423 | 393 | Electrostatic precipitator fouling | F3203A Precipitator - Clean Hopper | Mill Creek | Maintenance | Coal | 3 | 2015 | 6 | 56.1333 | 56.1333 | 22060.4 | 393 | 393
MC3 | NC | 66 | 1850 | 2015-06-15 06:27 | 2015-06-15 18:37 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2015 | 6 | 12.1667 | 12.1667 | 4781.5 | 393 | 393
MC3 | D1 | 67 | 1455 | 2015-06-15 22:58 | 2015-06-16 10:39 | 400 | 423 | 393 | Induced draft fans | F400Induced Draft Fans - Maxed Out | Mill Creek | Derate | Coal | 3 | 2015 | 6 | 11.6833 | 0.63526 | 249.6587 | 21.3688 | 21
MC3 | MO | 68 | 8550 | 2015-06-17 09:41 | 2015-06-21 20:12 | 0 | 423 | 393 | Electrostatic precipitator fouling | F320Precipitator Hoppers - Clean Out | Mill Creek | Maintenance | Coal | 3 | 2015 | 6 | 106.5167 | 106.5167 | 41861.05 | 393 | 393
MC3 | NC | 69 | 1850 | 2015-06-21 20:12 | 2015-06-22 12:05 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start | Mill Creek | Other | Coal | 3 | 2015 | 6 | 15.8833 | 15.8833 | 6242.15 | 393 | 393
MC3 | U1 | 70 | 3220 | 2015-06-22 12:05 | 2015-06-22 14:32 | 0 | 423 | 393 | Circulating water piping | F820Cooling tower pump trip | Mill Creek | Outage | Coal | 3 | 2015 | 6 | 2.45 | 2.45 | 962.85 | 393 | 393
MC3 | NC | 71 | 1850 | 2015-06-22 14:32 | 2015-06-22 20:43 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica @ Cold start | Mill Creek | Other | Coal | 3 | 2015 | 6 | 6.1833 | 6.1833 | 2430.05 | 393 | 393
MC3 | NC | 72 | 8548 | 2015-06-23 11:08 | 2015-06-23 17:46 | 0 | 423 | 393 | Testing B | F790Full Load testing | Mill Creek | Other | Coal | 3 | 2015 | 6 | 6.6333 | 6.6333 | 2606.9 | 393 | 393
MC3 | NC | 73 | 1160 | 2015-06-23 23:30 | 2015-06-24 05:13 | 0 | 423 | 393 | First reheater B | F320Boiler deslag - Load available if needed | Mill Creek | Other | Coal | 3 | 2015 | 6 | 5.7167 | 5.7167 | 2246.65 | 393 | 393
MC3 | NC | 74 | 8817 | 2015-06-24 10:00 | 2015-06-24 17:24 | 0 | 423 | 393 | SCR NOx Control system | F790Full load SCR testing | Mill Creek | Other | Coal | 3 | 2015 | 6 | 7.4 | 7.4 | 2908.2 | 393 | 393
MC3 | NC | 75 | 8817 | 2015-06-24 17:43 | 2015-06-24 18:30 | 0 | 423 | 393 | SCR NOx Control system | F790Full load SCR Testing | Mill Creek | Other | Coal | 3 | 2015 | 6 | 0.78333 | 0.78333 | 307.85 | 393 | 393
MC3 | D4 | 76 | 1999 | 2015-06-24 22:00 | 2015-06-25 04:47 | 200 | 423 | 393 | Boiler | F5903A Superheater reg. valve flange replacement | Mill Creek | Derate | Coal | 3 | 2015 | 6 | 6.7833 | 3.5761 | 1405.4008 | 207.1844 | 207
MC3 | D1 | 77 | 8426 | 2015-06-26 10:41 | 2015-06-26 11:02 | 300 | 423 | 393 | Miscellaneous electrical failures | F820Oxidation air compressor trip - bad contact | Mill Creek | Derate | Coal | 3 | 2015 | 6 | 0.35 | 0.10177 | 39.9968 | 114.2766 | 114
MC3 | D1 | 78 | 8426 | 2015-06-26 11:02 | 2015-06-26 13:02 | 200 | 423 | 393 | Miscellaneous electrical failures | F820Oxidation air compressor trip - bad contact | Mill Creek | Derate | Coal | 3 | 2015 | 6 | 2 | 1.0544 | 414.3688 | 207.1844 | 207
MC3 | MO | 79 | 8550 | 2015-06-30 22:16 | 2015-07-06 05:52 | 0 | 423 | 393 | Electrostatic precipitator fouling | F320Precipitator hoppers - clean out | Mill Creek | Maintenance | Coal | 3 | 2015 | 6 | 127.6 | 127.6 | 50146.8 | 393 | 393
MC3 | NC | 80 | 1850 | 2015-07-06 05:52 | 2015-07-06 22:20 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica @ cold start | Mill Creek | Other | Coal | 3 | 2015 | 7 | 16.4667 | 16.4667 | 6471.4 | 393 | 393
MC3 | D1 | 81 | 260 | 2015-07-06 22:20 | 2015-07-08 01:23 | 350 | 423 | 393 | Primary air fan | F7803C PA Fan inboard bearing temp - bad bearing | Mill Creek | Derate | Coal | 3 | 2015 | 7 | 27.05 | 4.6682 | 1834.6039 | 67.8227 | 68
MC3 | D1 | 82 | 8040 | 2015-07-13 09:15 | 2015-07-13 10:48 | 350 | 423 | 393 | Slurry transfer pumps and motors B | F120Reatant Feed Line - Pluggage on Regulator | Mill Creek | Derate | Coal | 3 | 2015 | 7 | 1.55 | 0.26749 | 105.1252 | 67.8227 | 68
MC3 | D1 | 83 | 1450 | 2015-07-13 10:48 | 2015-07-13 14:30 | 400 | 423 | 393 | Other air supply problems | F400Boiler Air Flow Issues - Controls | Mill Creek | Derate | Coal | 3 | 2015 | 7 | 3.7 | 0.20118 | 79.0645 | 21.3688 | 21
MC3 | NC | 84 | 9999 | 2015-07-16 08:30 | 2015-07-16 15:57 | 0 | 423 | 393 | Total unit performance testing (use appropriate codes for individual component testing) | F790Summer Full Load Capability Test | Mill Creek | Other | Coal | 3 | 2015 | 7 | 7.45 | 7.45 | 2927.85 | 393 | 393
MC3 | D1 | 85 | 380 | 2015-07-19 09:08 | 2015-07-19 09:19 | 230 | 423 | 393 | Light-off (igniter) systems (including fuel supply) | F4003D5 Igniter would not go in | Mill Creek | Derate | Coal | 3 | 2015 | 7 | 0.18333 | 0.083649 | 32.8739 | 179.3121 | 179
MC3 | D1 | 86 | 380 | 2015-07-19 10:00 | 2015-07-19 12:26 | 360 | 423 | 393 | Light-off (igniter) systems (including fuel supply) | F4003D5 igniter work | Mill Creek | Derate | Coal | 3 | 2015 | 7 | 2.4333 | 0.36241 | 142.4277 | 58.5319 | 59
MC3 | D1 | 87 | 250 | 2015-07-25 08:53 | 2015-07-25 09:06 | 365 | 423 | 393 | Pulverizer feeders | F1203D Coal Feeder - No coal flow at feeder intlet, coal flow issue | Mill Creek | Derate | Coal | 3 | 2015 | 7 | 0.21667 | 0.029708 | 11.6754 | 53.8865 | 54
MC3 | D1 | 88 | 3149 | 2015-07-26 17:32 | 2015-07-26 19:15 | 410 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Backpressure | Mill Creek | Derate | Coal | 3 | 2015 | 7 | 1.7167 | 0.052758 | 20.7339 | 12.078 | 12
MC3 | D1 | 89 | 3240 | 2015-08-06 07:19 | 2015-08-06 08:07 | 200 | 423 | 393 | Cooling tower fans | F820Cooling Tower Fan Bus Trip | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 0.8 | 0.42175 | 165.7475 | 207.1844 | 207
MC3 | D1 | 90 | 3240 | 2015-08-06 08:07 | 2015-08-06 09:25 | 300 | 423 | 393 | Cooling tower fans | F820Cooling Tower Fan Bus Trip | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 1.3 | 0.37801 | 148.5596 | 114.2766 | 114
MC3 | D1 | 91 | 3240 | 2015-08-06 09:25 | 2015-08-06 14:45 | 360 | 423 | 393 | Cooling tower fans | F820Cooling Tower Fan Bus Trip | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 5.3333 | 0.79433 | 312.1702 | 58.5319 | 59
MC3 | D1 | 92 | 3240 | 2015-08-06 14:45 | 2015-08-07 18:58 | 350 | 423 | 393 | Cooling tower fans | F590Cooling Tower Fans D,F & H Out of Service - Electrical Issues | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 28.2167 | 4.8695 | 1913.7304 | 67.8227 | 68
MC3 | D1 | 93 | 3149 | 2015-08-10 19:39 | 2015-08-10 23:58 | 396 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure - Cooling Tower H Fan VFD Fault | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 4.3167 | 0.27553 | 108.284 | 25.0851 | 25
MC3 | D1 | 94 | 3149 | 2015-08-11 12:06 | 2015-08-11 13:44 | 390 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure - Cooling Tower H Fan Out of Service | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 1.6333 | 0.12742 | 50.0773 | 30.6596 | 31
MC3 | NC | 95 | 3623 | 2015-08-12 12:00 | 2015-08-12 14:12 | 0 | 423 | 393 | Auxiliary generators | F790VAR Testing | Mill Creek | Other | Coal | 3 | 2015 | 8 | 2.2 | 2.2 | 864.6 | 393 | 393
MC3 | D4 | 96 | 3240 | 2015-08-13 21:00 | 2015-08-14 05:11 | 180 | 423 | 393 | Cooling tower fans | F590Cooling Tower Fan H - Breaker Issue | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 8.1833 | 4.7011 | 1847.5181 | 225.766 | 226
MC3 | D1 | 97 | 3149 | 2015-08-19 14:11 | 2015-08-19 15:53 | 400 | 423 | 393 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure - Cooling Tower H Fan Out of Service | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 1.7 | 0.092435 | 36.327 | 21.3688 | 21
MC3 | D4 | 98 | 310 | 2015-08-19 23:00 | 2015-08-20 06:01 | 350 | 423 | 393 | Pulverizer mills | F5903C Coal Mill - Inspection & Roller Repair | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 7.0167 | 1.2109 | 475.8892 | 67.8227 | 68
MC3 | D4 | 99 | 3240 | 2015-08-22 | 2015-08-22 05:11 | 200 | 423 | 393 | Cooling tower fans | F590Cooling Tower Fan H - Breaker Maintenance | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 5.1833 | 2.7326 | 1073.9058 | 207.1844 | 207
MC3 | D4 | 100 | 250 | 2015-08-24 22:00 | 2015-08-25 04:30 | 325 | 423 | 393 | Pulverizer feeders | F5903B Coal Feeder - Repair Discharge Flood Flapper | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 6.5 | 1.5059 | 591.8227 | 91.0496 | 91
MC3 | D4 | 101 | 3240 | 2015-08-25 20:00 | 2015-08-26 03:25 | 300 | 423 | 393 | Cooling tower fans | F590Cooling Tower H Fan - Switchgear Repair | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 7.4167 | 2.1566 | 847.5514 | 114.2766 | 114
MC3 | D1 | 102 | 360 | 2015-08-28 11:49 | 2015-08-28 13:42 | 325 | 423 | 393 | Burners | F7803D10 Coal Mill Burner - High Temperature | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 1.8833 | 0.43633 | 171.4768 | 91.0496 | 91
MC3 | U1 | 103 | 3412 | 2015-08-31 04:23 | 2015-08-31 05:46 | 0 | 423 | 393 | Feedwater pump drive - steam turbine | F820Boiler Feed Pump Turbine Driven - Tripped, HMI Failure | Mill Creek | Outage | Coal | 3 | 2015 | 8 | 1.3833 | 1.3833 | 543.65 | 393 | 393
MC3 | NC | 104 | 1850 | 2015-08-31 05:46 | 2015-08-31 14:09 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2015 | 8 | 8.3833 | 8.3833 | 3294.65 | 393 | 393
MC3 | D1 | 105 | 310 | 2015-09-16 16:23 | 2015-09-17 16:52 | 340 | 423 | 393 | Pulverizer mills | F5903C Coal Mill Primary Air Fan - Replace Inboard Bearing | Mill Creek | Derate | Coal | 3 | 2015 | 9 | 24.4833 | 4.8041 | 1887.9949 | 77.1135 | 77
MC3 | MO | 106 | 1050 | 2015-09-18 18:54 | 2015-09-23 08:10 | 0 | 423 | 393 | Second superheater B | F540Boiler Tube Leak - Secondary Superheat | Mill Creek | Maintenance | Coal | 3 | 2015 | 9 | 109.2667 | 109.2667 | 42941.8 | 393 | 393
MC3 | NC | 107 | 1850 | 2015-09-23 08:10 | 2015-09-24 01:31 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 3 | 2015 | 9 | 17.35 | 17.35 | 6818.55 | 393 | 393
MC3 | NC | 108 | 8700 | 2015-09-29 04:00 | 2015-09-29 07:40 | 0 | 423 | 393 | CEMS Certification and Recertification | F790RATA Test @ 300 MW | Mill Creek | Other | Coal | 3 | 2015 | 9 | 3.6667 | 3.6667 | 1441 | 393 | 393
MC3 | NC | 109 | 8700 | 2015-09-29 07:40 | 2015-09-29 14:10 | 0 | 423 | 393 | CEMS Certification and Recertification | F790RATA Test @ Full Load | Mill Creek | Other | Coal | 3 | 2015 | 9 | 6.5 | 6.5 | 2554.5 | 393 | 393
MC3 | NC | 110 | 8700 | 2015-09-30 07:03 | 2015-09-30 12:39 | 0 | 423 | 393 | CEMS Certification and Recertification | F790RATA Test @ Full Load | Mill Creek | Other | Coal | 3 | 2015 | 9 | 5.6 | 5.6 | 2200.8 | 393 | 393
MC3 | D1 | 111 | 250 | 2015-10-05 07:06 | 2015-10-05 08:58 | 330 | 423 | 393 | Pulverizer feeders | F8203D Coal Feeder -Trouble Alarm In, Would Not Start | Mill Creek | Derate | Coal | 3 | 2015 | 10 | 1.8667 | 0.4104 | 161.2879 | 86.4043 | 86
MC3 | D4 | 112 | 100 | 2015-10-05 22:00 | 2015-10-06 02:06 | 325 | 423 | 393 | Bunker gates | F1203C Bunker Valve - Cleaned Out | Mill Creek | Derate | Coal | 3 | 2015 | 10 | 4.1 | 0.94988 | 373.3035 | 91.0496 | 91
MC3 | D4 | 113 | 250 | 2015-10-07 11:40 | 2015-10-07 17:11 | 340 | 423 | 393 | Pulverizer feeders | F5903A Coal Feeder - Cleanout Conveyor Gearbox Broke | Mill Creek | Derate | Coal | 3 | 2015 | 10 | 5.5167 | 1.0825 | 425.4093 | 77.1135 | 77
MC3 | D4 | 114 | 250 | 2015-10-07 23:30 | 2015-10-08 06:41 | 340 | 423 | 393 | Pulverizer feeders | F5903A Coal Feeder - Replace Cleanout Conveyor Gearbox | Mill Creek | Derate | Coal | 3 | 2015 | 10 | 7.1833 | 1.4095 | 553.9318 | 77.1135 | 77
MC3 | D1 | 115 | 260 | 2015-10-08 11:12 | 2015-10-08 13:15 | 330 | 423 | 393 | Primary air fan | F5903A Coal Mill Primary Air Fan - Breaker Issues | Mill Creek | Derate | Coal | 3 | 2015 | 10 | 2.05 | 0.45071 | 177.1287 | 86.4043 | 86
MC3 | NC | 116 | 8670 | 2015-10-12 16:22 | 2015-10-13 | 0 | 423 | 393 | Emission monitors (other than CEMS) A | F790CEM Testing | Mill Creek | Other | Coal | 3 | 2015 | 10 | 7.6333 | 7.6333 | 2999.9 | 393 | 393
MC3 | U1 | 117 | 3412 | 2015-10-18 15:09 | 2015-10-18 17:58 | 0 | 423 | 393 | Feedwater pump drive - steam turbine | F820Turbine Driven Boiler Feed Pump - Trip, Unexpected Reboot | Mill Creek | Outage | Coal | 3 | 2015 | 10 | 2.8167 | 2.8167 | 1106.95 | 393 | 393
MC3 | NC | 118 | 1850 | 2015-10-18 17:58 | 2015-10-18 23:52 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2015 | 10 | 5.9 | 5.9 | 2318.7 | 393 | 393
MC3 | PO | 119 | 1310 | 2015-10-23 23:15 | 2015-11-09 11:17 | 0 | 423 | 393 | Water side cleaning (acid cleaning) | F590Planned Outage | Mill Creek | Other | Coal | 3 | 2015 | 10 | 396.0333 | 396.0333 | 155641.1 | 393 | 393
MC3 | D4 | 120 | 345 | 2015-11-09 11:17 | 2015-11-10 09:51 | 330 | 423 | 393 | Pulverizer overhaul | F5903D Coal Mill Overahaul | Mill Creek | Derate | Coal | 3 | 2015 | 11 | 22.5667 | 4.9615 | 1949.856 | 86.4043 | 86
MC3 | D1 | 121 | 1700 | 2015-11-10 03:44 | 2015-11-10 05:17 | 200 | 423 | 393 | Feedwater controls (report local controls --- feedwater pump | F720TDBFP Recirc valve stuck | Mill Creek | Derate | Coal | 3 | 2015 | 11 | 1.55 | 0.81714 | 321.1358 | 207.1844 | 207
MC3 | D1 | 122 | 1700 | 2015-11-10 05:17 | 2015-11-10 09:51 | 243 | 423 | 393 | Feedwater controls (report local controls --- feedwater pump | F720TDBFP recirc valve stuck | Mill Creek | Derate | Coal | 3 | 2015 | 11 | 4.5667 | 1.9433 | 763.7021 | 167.234 | 167
MC3 | D4 | 123 | 345 | 2015-11-10 09:51 | 2015-11-10 19:30 | 366 | 423 | 393 | Pulverizer overhaul | F5903D Coal Mill - Overhaul | Mill Creek | Derate | Coal | 3 | 2015 | 11 | 9.65 | 1.3004 | 511.0394 | 52.9574 | 53
MC3 | D4 | 124 | 260 | 2015-11-11 22:10 | 2015-11-12 07:09 | 330 | 423 | 393 | Primary air fan | F0403D PA Fan Balance | Mill Creek | Derate | Coal | 3 | 2015 | 11 | 8.9833 | 1.9751 | 776.1982 | 86.4043 | 86
MC3 | D1 | 125 | 360 | 2015-11-19 20:12 | 2015-11-19 20:54 | 335 | 423 | 393 | Burners | F7803C2 Burner temps | Mill Creek | Derate | Coal | 3 | 2015 | 11 | 0.7 | 0.14563 | 57.2312 | 81.7589 | 82
MC3 | U1 | 126 | 1080 | 2015-11-20 17:33 | 2015-11-23 06:40 | 0 | 423 | 393 | Economizer B | F540Boiler tube leak - economizer | Mill Creek | Outage | Coal | 3 | 2015 | 11 | 61.1167 | 61.1167 | 24018.85 | 393 | 393
MC3 | NC | 127 | 1850 | 2015-11-23 06:40 | 2015-11-23 18:55 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica @ Warm Start | Mill Creek | Other | Coal | 3 | 2015 | 11 | 12.25 | 12.25 | 4814.25 | 393 | 393
MC3 | D1 | 128 | 1850 | 2015-11-23 18:55 | 2015-11-24 04:05 | 330 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2015 | 11 | 9.1667 | 2.0154 | 792.039 | 86.4043 | 86
MC3 | D1 | 129 | 1850 | 2015-11-24 04:05 | 2015-11-24 08:31 | 400 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2015 | 11 | 4.4333 | 0.24106 | 94.735 | 21.3688 | 21
MC3 | NC | 130 | 8460 | 2015-11-24 08:31 | 2015-11-24 16:34 | 0 | 423 | 393 | Testing A | F790SCR Flue gas testing | Mill Creek | Other | Coal | 3 | 2015 | 11 | 8.05 | 8.05 | 3163.65 | 393 | 393
MC3 | D1 | 131 | 385 | 2015-11-25 16:36 | 2015-11-25 18:27 | 350 | 423 | 393 | Igniters | F3403D1 ignitor would not go in | Mill Creek | Derate | Coal | 3 | 2015 | 11 | 1.85 | 0.31927 | 125.472 | 67.8227 | 68
MC3 | D1 | 132 | 260 | 2015-12-02 13:34 | 2015-12-02 16:22 | 320 | 423 | 393 | Primary air fan | F8503C Mill PA fan vibration | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 2.8 | 0.6818 | 267.9461 | 95.695 | 96
MC3 | D4 | 133 | 262 | 2015-12-15 23:00 | 2015-12-16 06:17 | 320 | 423 | 393 | Primary air fan lube oil system | F540PA Fan oil leak | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 7.2833 | 1.7735 | 696.9788 | 95.695 | 96
MC3 | NC | 134 | 310 | 2015-12-16 08:28 | 2015-12-16 12:10 | 0 | 423 | 393 | Pulverizer mills | F790Coal fineness test | Mill Creek | Other | Coal | 3 | 2015 | 12 | 3.7 | 3.7 | 1454.1 | 393 | 393
MC3 | D1 | 135 | 8790 | 2015-12-18 10:26 | 2015-12-18 10:53 | 375 | 423 | 393 | Miscellaneous CEMS problems | F400Blower trip in CEMS | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 0.45 | 0.051064 | 20.0681 | 44.5957 | 45
MC3 | D1 | 136 | 260 | 2015-12-18 10:53 | 2015-12-18 12:36 | 325 | 423 | 393 | Primary air fan | F0603C PA fan shaft broke | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 1.7167 | 0.39771 | 156.3019 | 91.0496 | 91
MC3 | D1 | 137 | 260 | 2015-12-18 12:36 | 2015-12-18 12:44 | 330 | 423 | 393 | Primary air fan | F0603C PA fan shaft broke | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 0.13333 | 0.029314 | 11.5206 | 86.4043 | 86
MC3 | D1 | 138 | 260 | 2015-12-18 12:44 | 2015-12-23 08:32 | 350 | 423 | 393 | Primary air fan | F0603C PA fan shaft broke | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 115.8 | 19.9844 | 7853.8681 | 67.8227 | 68
MC3 | D1 | 139 | 480 | 2015-12-23 08:32 | 2015-12-23 08:40 | 235 | 423 | 393 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | F1203D-1 Gas Gun/Gas Flow Valve Issues | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 0.13333 | 0.059259 | 23.2889 | 174.6667 | 175
MC3 | D1 | 140 | 260 | 2015-12-23 08:40 | 2015-12-25 05:07 | 350 | 423 | 393 | Primary air fan | F0603C PA Fan shaft broke | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 44.45 | 7.671 | 3014.7188 | 67.8227 | 68
MC3 | D1 | 142 | 260 | 2015-12-27 21:37 | 2015-12-28 05:24 | 350 | 423 | 393 | Primary air fan | F0603C PA Fan shaft broke | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 7.7833 | 1.3432 | 527.8866 | 67.8227 | 68
MC3 | D1 | 143 | 1850 | 2015-12-28 08:00 | 2015-12-28 14:40 | 410 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 6.6667 | 0.20489 | 80.5201 | 12.078 | 12
MC3 | D1 | 144 | 250 | 2015-12-28 20:33 | 2015-12-28 21:48 | 340 | 423 | 393 | Pulverizer feeders | FW00Wet coal | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 1.25 | 0.24527 | 96.3918 | 77.1135 | 77
MC3 | D4 | 145 | 262 | 2015-12-28 23:00 | 2015-12-29 01:58 | 330 | 423 | 393 | Primary air fan lube oil system | F5903C PA Fan oil change | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 2.9667 | 0.65225 | 256.3326 | 86.4043 | 86
MC3 | D4 | 146 | 260 | 2015-12-30 21:32 | 2015-12-31 01:58 | 330 | 423 | 393 | Primary air fan | F5303A PA fan inspection | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 4.4333 | 0.9747 | 383.0589 | 86.4043 | 86
MC3 | D4 | 1 | 260 | 2016-01-03 22:00 | 2016-01-04 05:00 | 330 | 423 | 393 | Primary air fan | F5303D PA Fan inspection | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 7 | 1.539 | 604.8298 | 86.4043 | 86
MC3 | D1 | 2 | 260 | 2016-01-05 03:51 | 2016-01-05 07:37 | 320 | 423 | 393 | Primary air fan | FR003C PA Fan insulation fire | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 3.7667 | 0.91718 | 360.4513 | 95.695 | 96
MC3 | D4 | 3 | 270 | 2016-01-07 23:00 | 2016-01-08 04:28 | 320 | 423 | 393 | Primary air duct and dampers | F5303D PA fan damper inspection | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 5.4667 | 1.3311 | 523.1329 | 95.695 | 96
MC3 | D4 | 4 | 260 | 2016-01-08 08:15 | 2016-01-08 12:12 | 320 | 423 | 393 | Primary air fan | F5903C PA Fan maintenance | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 3.95 | 0.96182 | 377.9954 | 95.695 | 96
MC3 | MO | 5 | 1000 | 2016-01-13 22:26 | 2016-01-16 03:32 | 0 | 423 | 393 | Waterwall (Furnace wall) A | F540Boiler tube leak | Mill Creek | Maintenance | Coal | 3 | 2016 | 1 | 53.1 | 53.1 | 20868.3 | 393 | 393
MC3 | NC | 6 | 1850 | 2016-01-16 03:32 | 2016-01-16 15:32 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2016 | 1 | 12 | 12 | 4716 | 393 | 393
MC3 | D1 | 7 | 1850 | 2016-01-16 15:32 | 2016-01-17 04:36 | 360 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 13.0667 | 1.9461 | 764.817 | 58.5319 | 59
MC3 | D1 | 8 | 1850 | 2016-01-17 04:36 | 2016-01-17 16:33 | 370 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 11.95 | 1.4973 | 588.4316 | 49.2411 | 49
MC3 | D1 | 9 | 1850 | 2016-01-17 16:33 | 2016-01-17 19:57 | 387 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 3.4 | 0.28936 | 113.7191 | 33.4468 | 33
MC3 | D1 | 10 | 385 | 2016-01-27 17:30 | 2016-01-27 18:33 | 350 | 423 | 393 | Igniters | F3403B Mill ignitor would not light | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 1.05 | 0.18121 | 71.2138 | 67.8227 | 68
MC3 | D4 | 11 | 350 | 2016-01-27 23:00 | 2016-01-28 00:22 | 335 | 423 | 393 | Pulverized fuel and air piping (from pulverizer to wind box) | F520Replace A6 swing valve proximity switch. | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 1.3667 | 0.28432 | 111.7371 | 81.7589 | 82
MC3 | D4 | 12 | 350 | 2016-01-28 00:22 | 2016-01-28 01:24 | 320 | 423 | 393 | Pulverized fuel and air piping (from pulverizer to wind box) | F520Replace A6 swing valve proximity switch. | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 1.0333 | 0.25162 | 98.8849 | 95.695 | 96
MC3 | NC | 13 | 9999 | 2016-02-05 08:13 | 2016-02-05 13:23 | 0 | 423 | 393 | Total unit performance testing (use appropriate codes for individual component testing) | F790Full load winter capability test | Mill Creek | Other | Coal | 3 | 2016 | 2 | 5.1667 | 5.1667 | 2030.5 | 393 | 393
MC3 | D1 | 14 | 1850 | 2016-02-09 12:33 | 2016-02-10 08:10 | 404 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2016 | 2 | 19.6167 | 0.88113 | 346.2829 | 17.6525 | 18
MC3 | D1 | 15 | 3869 | 2016-02-13 14:13 | 2016-02-14 09:05 | 340 | 423 | 393 | Other fire protection system problems | F060Sprinlker head broke, water leaked into 3B Mill cabinet | Mill Creek | Derate | Coal | 3 | 2016 | 2 | 18.8667 | 3.702 | 1454.8742 | 77.1135 | 77
MC3 | D1 | 16 | 360 | 2016-02-22 10:12 | 2016-02-22 14:59 | 325 | 423 | 393 | Burners | F7803A Mill burner temps | Mill Creek | Derate | Coal | 3 | 2016 | 2 | 4.7833 | 1.1082 | 435.5208 | 91.0496 | 91
MC3 | D4 | 17 | 260 | 2016-02-29 22:00 | 2016-03-01 05:21 | 330 | 423 | 393 | Primary air fan | F8503C Mill PA fan maintenance for vibration | Mill Creek | Derate | Coal | 3 | 2016 | 2 | 7.35 | 1.616 | 635.0713 | 86.4043 | 86
MC3 | D4 | 18 | 260 | 2016-03-02 23:00 | 2016-03-03 06:55 | 330 | 423 | 393 | Primary air fan | F850Balanced 3C PA Fan | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 7.9167 | 1.7405 | 684.0337 | 86.4043 | 86
MC3 | D1 | 19 | 1850 | 2016-03-06 18:40 | 2016-03-07 03:49 | 350 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 9.15 | 1.5791 | 620.5777 | 67.8227 | 68
MC3 | D1 | 20 | 1850 | 2016-03-07 03:49 | 2016-03-08 11:28 | 300 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 31.65 | 9.2032 | 3616.8543 | 114.2766 | 114
MC3 | MO | 21 | 3110 | 2016-03-08 11:28 | 2016-03-10 06:33 | 0 | 423 | 393 | Condenser tube leaks | F540Condenser tube leak | Mill Creek | Maintenance | Coal | 3 | 2016 | 3 | 43.0833 | 43.0833 | 16931.75 | 393 | 393
MC3 | MO | 22 | 1060 | 2016-03-10 18:13 | 2016-03-12 00:02 | 0 | 423 | 393 | First reheater A | F540Boiler Tube Leak - Front SCW Hanger Tube | Mill Creek | Maintenance | Coal | 3 | 2016 | 3 | 29.8167 | 29.8167 | 11717.95 | 393 | 393
MC3 | NC | 28 | 1850 | 2016-03-12 00:02 | 2016-03-12 01:15 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica @ warm start-up | Mill Creek | Other | Coal | 3 | 2016 | 3 | 1.2167 | 1.2167 | 478.15 | 393 | 393
MC3 | D1 | 23 | 3412 | 2016-03-12 01:15 | 2016-03-12 18:04 | 125 | 423 | 393 | Feedwater pump drive - steam turbine | F540EHC Leak on TDBFP valve | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 16.8167 | 11.8472 | 4655.9506 | 276.8652 | 277
MC3 | D1 | 24 | 3412 | 2016-03-12 18:04 | 2016-03-14 13:24 | 160 | 423 | 393 | Feedwater pump drive - steam turbine | F540EHC Leak on TDBFP valve | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 43.3333 | 26.9425 | 10588.3924 | 244.3475 | 244
MC3 | D1 | 25 | 1850 | 2016-03-14 13:24 | 2016-03-15 05:00 | 328 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 15.6 | 3.5035 | 1376.8936 | 88.2624 | 88
MC3 | D1 | 26 | 1850 | 2016-03-15 05:00 | 2016-03-15 11:51 | 385 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 6.85 | 0.61537 | 241.839 | 35.305 | 35
MC3 | D1 | 29 | 1850 | 2016-03-15 11:51 | 2016-03-15 12:04 | 405 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 0.21667 | 0.0092199 | 3.6234 | 16.7234 | 17
MC3 | U1 | 30 | 3620 | 2016-03-15 18:07 | 2016-03-25 02:11 | 0 | 423 | 393 | Main transformer | FR00"A" Phase main transformer fire | Mill Creek | Outage | Coal | 3 | 2016 | 3 | 224.0667 | 224.0667 | 88058.2 | 393 | 393
MC3 | NC | 31 | 1850 | 2016-03-25 02:11 | 2016-03-26 02:30 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica @ cold start | Mill Creek | Other | Coal | 3 | 2016 | 3 | 24.3167 | 24.3167 | 9556.45 | 393 | 393
MC3 | D1 | 32 | 1850 | 2016-03-26 02:30 | 2016-03-27 18:45 | 280 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 40.25 | 13.607 | 5347.5408 | 132.8582 | 133
MC3 | D1 | 33 | 1488 | 2016-03-27 18:45 | 2016-03-27 19:30 | 265 | 423 | 393 | Air heater (regenerative) | F7603A air heater guide bearing lube oil pump motor tripped | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 0.75 | 0.28014 | 110.0957 | 146.7943 | 147
MC3 | D1 | 34 | 1488 | 2016-03-27 19:30 | 2016-03-27 21:49 | 200 | 423 | 393 | Air heater (regenerative) | F760Replaced 3A air heater guide bearing LOP motor | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 2.3167 | 1.2213 | 479.9772 | 207.1844 | 207
MC3 | D1 | 35 | 1850 | 2016-03-27 21:49 | 2016-03-28 08:55 | 280 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 11.1 | 3.7525 | 1474.7255 | 132.8582 | 133
MC3 | D1 | 36 | 1850 | 2016-03-28 08:55 | 2016-03-29 11:43 | 250 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 26.8 | 10.9608 | 4307.5773 | 160.7305 | 161
MC3 | D1 | 37 | 1850 | 2016-03-29 11:43 | 2016-03-29 20:18 | 270 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 8.5833 | 3.1046 | 1220.1117 | 142.1489 | 142
MC3 | D1 | 38 | 1850 | 2016-03-29 20:18 | 2016-04-01 00:06 | 320 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2016 | 3 | 51.8 | 12.6132 | 4957.0028 | 95.695 | 96
MC3 | MO | 39 | 3110 | 2016-04-01 00:06 | 2016-04-02 15:21 | 0 | 423 | 393 | Condenser tube leaks | F540Condenser tube leak | Mill Creek | Maintenance | Coal | 3 | 2016 | 4 | 39.25 | 39.25 | 15425.25 | 393 | 393
MC3 | NC | 40 | 1850 | 2016-04-02 15:21 | 2016-04-02 23:21 | 0 | 423 | 393 | Boiler water condition (not feedwater water quality) | FA00High silica @ Hot Start | Mill Creek | Other | Coal | 3 | 2016 | 4 | 8 | 8 | 3144 | 393 | 393
MC3 | D1 | 41 | 1850 | 2016-04-02 23:21 | 2016-04-03 11:00 | 295 | 423 | 393 | Boiler water condition (not feedwater water quality) | FA00High silica | Mill Creek | Derate | Coal | 3 | 2016 | 4 | 11.65 | 3.5253 | 1385.4411 | 118.922 | 119
MC3 | D1 | 42 | 1850 | 2016-04-03 11:00 | 2016-04-04 11:34 | 325 | 423 | 393 | Boiler water condition (not feedwater water quality) | FA00High silica | Mill Creek | Derate | Coal | 3 | 2016 | 4 | 24.5667 | 5.6916 | 2236.7863 | 91.0496 | 91
MC3 | D1 | 43 | 1850 | 2016-04-04 11:34 | 2016-04-04 12:41 | 395 | 423 | 393 | Boiler water condition (not feedwater water quality) | FA00High silica | Mill Creek | Derate | Coal | 3 | 2016 | 4 | 1.1167 | 0.073916 | 29.0492 | 26.0142 | 26
MC3 | D1 | 44 | 1850 | 2016-04-04 12:41 | 2016-04-04 15:26 | 410 | 423 | 393 | Boiler water condition (not feedwater water quality) | FA00High silica | Mill Creek | Derate | Coal | 3 | 2016 | 4 | 2.75 | 0.084515 | 33.2145 | 12.078 | 12
MC3 | D1 | 45 | 1850 | 2016-04-04 15:26 | 2016-04-05 01:20 | 390 | 423 | 393 | Boiler water condition (not feedwater water quality) | FA00High silica | Mill Creek | Derate | Coal | 3 | 2016 | 4 | 9.9 | 0.77234 | 303.5298 | 30.6596 | 31
MC3 | D1 | 46 | 1850 | 2016-04-05 10:02 | 2016-04-06 00:45 | 382 | 423 | 393 | Boiler water condition (not feedwater water quality) | FA00High silica | Mill Creek | Derate | Coal | 3 | 2016 | 4 | 14.7167 | 1.4264 | 560.5902 | 38.0922 | 38
MC3 | D1 | 47 | 1850 | 2016-04-06 00:45 | 2016-04-06 06:58 | 400 | 423 | 393 | Boiler water condition (not feedwater water quality) | FA00High silica | Mill Creek | Derate | Coal | 3 | 2016 | 4 | 6.2167 | 0.33802 | 132.8427 | 21.3688 | 21
MC3 | NC | 48 | 8460 | 2016-04-06 10:00 | 2016-04-06 11:21 | 0 | 423 | 393 | Testing A | F790Pre outage full load MATS testing | Mill Creek | Other | Coal | 3 | 2016 | 4 | 1.35 | 1.35 | 530.55 | 393 | 393
MC3 | PO | 49 | 8440 | 2016-04-09 14:58 | 2016-06-03 20:08 | 0 | 423 | 393 | Major overhaul C | F590Planned 8 week outage Install new WFGD | Mill Creek | Other | Coal | 3 | 2016 | 4 | 1325.1667 | 1325.1667 | 520790.5 | 393 | 393
MC3 | SF | 50 | 1475 | 2016-06-03 20:08 | 2016-06-04 16:04 | 0 | 423 | 393 | Induced draft fan controls | F430Relay on breaker took out ID fans | Mill Creek | Outage | Coal | 3 | 2016 | 6 | 19.9333 | 19.9333 | 7833.8 | 393 | 393
MC3 | U1 | 51 | 1475 | 2016-06-06 11:30 | 2016-06-06 12:44 | 0 | 423 | 393 | Induced draft fan controls | F660ID Fan Index Trip | Mill Creek | Outage | Coal | 3 | 2016 | 6 | 1.2333 | 1.2333 | 484.7 | 393 | 393
MC3 | D1 | 52 | 380 | 2016-06-08 04:14 | 2016-06-08 04:58 | 330 | 423 | 393 | Light-off (igniter) systems (including fuel supply) | F4303-D mill gas guns (3D7) | Mill Creek | Derate | Coal | 3 | 2016 | 6 | 0.73333 | 0.16123 | 63.3631 | 86.4043 | 86
MC3 | NC | 53 | 8010 | 2016-06-15 00:50 | 2016-06-15 04:42 | 0 | 423 | 393 | Crushers/mills | F430Lost feed to limestone crusher, cant make slurry | Mill Creek | Other | Coal | 3 | 2016 | 6 | 3.8667 | 3.8667 | 1519.6 | 393 | 393
MC3 | MO | 54 | 1512 | 2016-06-17 00:51 | 2016-06-18 05:52 | 0 | 423 | 393 | Flue gas expansion joints | F8103B ID Fan Expansion Joint Replacment | Mill Creek | Maintenance | Coal | 3 | 2016 | 6 | 29.0167 | 29.0167 | 11403.55 | 393 | 393
MC3 | U1 | 55 | 1470 | 2016-06-25 14:58 | 2016-06-25 20:55 | 0 | 423 | 393 | Induced draft fan motors and drives | F8503A ID Fan trip - high vibration | Mill Creek | Outage | Coal | 3 | 2016 | 6 | 5.95 | 5.95 | 2338.35 | 393 | 393
MC3 | D4 | 70 | 310 | 2016-07-01 | 2016-07-01 04:22 | 330 | 423 | 393 | Pulverizer mills | F590B Mill Maint. | Mill Creek | Derate | Coal | 3 | 2016 | 7 | 4.3667 | 0.96005 | 377.2986 | 86.4043 | 86
MC3 | D4 | 57 | 260 | 2016-07-05 23:37 | 2016-07-06 00:33 | 350 | 423 | 393 | Primary air fan | F5903D PA Fan Oil Change | Mill Creek | Derate | Coal | 3 | 2016 | 7 | 0.93333 | 0.16107 | 63.3012 | 67.8227 | 68
MC3 | NC | 58 | 9999 | 2016-07-06 00:33 | 2016-07-06 02:02 | 0 | 423 | 393 | Total unit performance testing (use appropriate codes for individual component testing) | F790IHR Testing | Mill Creek | Other | Coal | 3 | 2016 | 7 | 1.4833 | 1.4833 | 582.95 | 393 | 393
MC3 | NC | 59 | 9999 | 2016-07-06 02:02 | 2016-07-06 04:00 | 0 | 423 | 393 | Total unit performance testing (use appropriate codes for individual component testing) | F790IHR Testing | Mill Creek | Other | Coal | 3 | 2016 | 7 | 1.9667 | 1.9667 | 772.9 | 393 | 393
MC3 | NC | 60 | 9999 | 2016-07-06 04:00 | 2016-07-06 06:05 | 0 | 423 | 393 | Total unit performance testing (use appropriate codes for individual component testing) | F790IHR Testing | Mill Creek | Other | Coal | 3 | 2016 | 7 | 2.0833 | 2.0833 | 818.75 | 393 | 393
MC3 | D1 | 61 | 380 | 2016-07-06 14:30 | 2016-07-06 14:41 | 345 | 423 | 393 | Light-off (igniter) systems (including fuel supply) | F700D mill gas gun | Mill Creek | Derate | Coal | 3 | 2016 | 7 | 0.18333 | 0.033806 | 13.2858 | 72.4681 | 72
MC3 | NC | 62 | 9656 | 2016-07-07 03:10 | 2016-07-07 03:31 | 0 | 423 | 393 | Other stack or exhaust emissions testing - fossil | F790Unit Testing | Mill Creek | Other | Coal | 3 | 2016 | 7 | 0.35 | 0.35 | 137.55 | 393 | 393
MC3 | NC | 63 | 9656 | 2016-07-07 04:00 | 2016-07-07 05:30 | 0 | 423 | 393 | Other stack or exhaust emissions testing - fossil | F790Unit Testing | Mill Creek | Other | Coal | 3 | 2016 | 7 | 1.5 | 1.5 | 589.5 | 393 | 393
MC3 | D4 | 64 | 260 | 2016-07-07 21:55 | 2016-07-07 23:30 | 330 | 423 | 393 | Primary air fan | F5903A PA Fan Maintenance | Mill Creek | Derate | Coal | 3 | 2016 | 7 | 1.5833 | 0.34811 | 136.8067 | 86.4043 | 86
MC3 | NC | 65 | 9620 | 2016-07-07 23:30 | 2016-07-08 02:33 | 0 | 423 | 393 | Particulate stack emissions (fossil) | F790Mid Load RATA Testing | Mill Creek | Other | Coal | 3 | 2016 | 7 | 3.05 | 3.05 | 1198.65 | 393 | 393
MC3 | NC | 66 | 9620 | 2016-07-08 03:21 | 2016-07-08 06:15 | 0 | 423 | 393 | Particulate stack emissions (fossil) | F790Low Load RATA Testing | Mill Creek | Other | Coal | 3 | 2016 | 7 | 2.9 | 2.9 | 1139.7 | 393 | 393
MC3 | D1 | 67 | 300 | 2016-07-10 08:53 | 2016-07-10 09:53 | 325 | 423 | 393 | Pulverizer motors and drives | F7803B Mill motor stator temperature indication | Mill Creek | Derate | Coal | 3 | 2016 | 7 | 1 | 0.23168 | 91.0496 | 91.0496 | 91
MC3 | D4 | 68 | 262 | 2016-07-10 23:00 | 2016-07-11 02:05 | 340 | 423 | 393 | Primary air fan lube oil system | F5903C Mill Maintenance - Change oil in PA fan and inspect feeder | Mill Creek | Derate | Coal | 3 | 2016 | 7 | 3.0833 | 0.605 | 237.7665 | 77.1135 | 77
MC3 | U1 | 69 | 9900 | 2016-07-15 02:40 | 2016-07-15 06:07 | 0 | 423 | 393 | Operator error | FP00Furnace Pressure Trip | Mill Creek | Outage | Coal | 3 | 2016 | 7 | 3.45 | 3.45 | 1355.85 | 393 | 393
MC3 | D1 | 71 | 385 | 2016-07-21 05:13 | 2016-07-21 06:44 | 122 | 423 | 393 | Igniters | F520Could not get D6 igniter in & Lost A Mill | Mill Creek | Derate | Coal | 3 | 2016 | 7 | 1.5167 | 1.0792 | 424.1396 | 279.6525 | 280
MC3 | NC | 72 | 1999 | 2016-07-26 23:00 | 2016-07-27 01:40 | 0 | 423 | 393 | Boiler | F790Boiler Tuning | Mill Creek | Other | Coal | 3 | 2016 | 7 | 2.6667 | 2.6667 | 1048 | 393 | 393
MC3 | D1 | 73 | 260 | 2016-07-27 06:27 | 2016-07-27 07:28 | 370 | 423 | 393 | Primary air fan | F820'3C Primary Air Fan Breaker | Mill Creek | Derate | Coal | 3 | 2016 | 7 | 1.0167 | 0.12738 | 50.0618 | 49.2411 | 49
MC3 | NC | 74 | 1999 | 2016-07-28 00:01 | 2016-07-28 02:20 | 0 | 423 | 393 | Boiler | F790Boiler Tuning | Mill Creek | Other | Coal | 3 | 2016 | 7 | 2.3167 | 2.3167 | 910.45 | 393 | 393
MC3 | U1 | 75 | 8656 | 2016-08-04 12:18 | 2016-08-05 02:56 | 0 | 423 | 393 | Controls and instrumentation B | F410'Loss of UPS & Fire on 3A oxidation air compressor | Mill Creek | Outage | Coal | 3 | 2016 | 8 | 14.6333 | 14.6333 | 5750.9 | 393 | 393
MC3 | D1 | 76 | 1530 | 2016-08-05 11:30 | 2016-08-05 11:50 | 362 | 423 | 393 | Other flue gas problems | F0903B1 & 3B2 O2 Prob Issues | Mill Creek | Derate | Coal | 3 | 2016 | 8 | 0.33333 | 0.048069 | 18.8913 | 56.6738 | 57
MC3 | NC | 77 | 4490 | 2016-08-17 19:30 | 2016-08-17 22:00 | 0 | 423 | 393 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Heat Rate Testing | Mill Creek | Other | Coal | 3 | 2016 | 8 | 2.5 | 2.5 | 982.5 | 393 | 393
MC3 | NC | 78 | 4490 | 2016-08-17 22:00 | 2016-08-17 23:00 | 0 | 423 | 393 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Heat Rate Testing | Mill Creek | Other | Coal | 3 | 2016 | 8 | 1 | 1 | 393 | 393 | 393
MC3 | D4 | 79 | 310 | 2016-08-17 23:00 | 2016-08-18 00:30 | 320 | 423 | 393 | Pulverizer mills | F590D Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2016 | 8 | 1.5 | 0.36525 | 143.5426 | 95.695 | 96
MC3 | NC | 80 | 4490 | 2016-08-18 00:30 | 2016-08-18 02:30 | 0 | 423 | 393 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Heat Rate Testing | Mill Creek | Other | Coal | 3 | 2016 | 8 | 2 | 2 | 786 | 393 | 393
MC3 | D1 | 81 | 260 | 2016-08-19 07:01 | 2016-08-19 12:02 | 330 | 423 | 393 | Primary air fan | F5903B Mill PA fan air flow | Mill Creek | Derate | Coal | 3 | 2016 | 8 | 5.0167 | 1.103 | 433.4613 | 86.4043 | 86
MC3 | D1 | 82 | 250 | 2016-08-24 14:21 | 2016-08-24 15:09 | 350 | 423 | 393 | Pulverizer feeders | F8203A Mill and Feeder Trip | Mill Creek | Derate | Coal | 3 | 2016 | 8 | 0.8 | 0.13806 | 54.2582 | 67.8227 | 68
MC3 | D1 | 83 | 250 | 2016-08-24 15:09 | 2016-08-24 17:32 | 400 | 423 | 393 | Pulverizer feeders | F8203A Mill and Feeder Trip | Mill Creek | Derate | Coal | 3 | 2016 | 8 | 2.3833 | 0.12959 | 50.929 | 21.3688 | 21
MC3 | D4 | 84 | 310 | 2016-08-25 23:00 | 2016-08-26 11:52 | 330 | 423 | 393 | Pulverizer mills | F5903A Coal Mill Maintenance - Repaired Floor | Mill Creek | Derate | Coal | 3 | 2016 | 8 | 12.8667 | 2.8288 | 1111.7348 | 86.4043 | 86
MC3 | D1 | 85 | 3979 | 2016-08-27 12:45 | 2016-08-27 14:22 | 395 | 423 | 393 | Other DCS problems | F490125v DC Issue - DCS Ground - Gave false HTR Flooding Indication, causing the HTRs | Mill Creek | Derate | Coal | 3 | 2016 | 8 | 1.6167 | 0.10701 | 42.0563 | 26.0142 | 26
MC3 | D4 | 86 | 310 | 2016-09-20 23:00 | 2016-09-21 05:51 | 330 | 423 | 393 | Pulverizer mills | F5903A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2016 | 9 | 6.85 | 1.506 | 591.8691 | 86.4043 | 86
MC3 | D4 | 87 | 310 | 2016-09-21 23:00 | 2016-09-22 04:32 | 330 | 423 | 393 | Pulverizer mills | F5903A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2016 | 9 | 5.5333 | 1.2165 | 478.1035 | 86.4043 | 86
MC3 | D4 | 88 | 3410 | 2016-09-24 22:00 | 2016-09-25 05:52 | 130 | 423 | 393 | Feedwater pump | F540TDFP Maintenance (Small steam leak at valve) | Mill Creek | Derate | Coal | 3 | 2016 | 9 | 7.8667 | 5.449 | 2141.4629 | 272.2199 | 272
MC3 | D4 | 89 | 310 | 2016-09-26 23:00 | 2016-09-27 05:13 | 330 | 423 | 393 | Pulverizer mills | F5903B Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2016 | 9 | 6.2167 | 1.3668 | 537.1465 | 86.4043 | 86
MC3 | D4 | 90 | 250 | 2016-09-27 23:00 | 2016-09-28 05:41 | 330 | 423 | 393 | Pulverizer feeders | F0903C Coal Feeder Calibration | Mill Creek | Derate | Coal | 3 | 2016 | 9 | 6.6833 | 1.4694 | 577.4684 | 86.4043 | 86
MC3 | D4 | 91 | 310 | 2016-09-28 23:00 | 2016-09-29 05:41 | 330 | 423 | 393 | Pulverizer mills | F5903D Mill Inspection | Mill Creek | Derate | Coal | 3 | 2016 | 9 | 6.6833 | 1.4694 | 577.4684 | 86.4043 | 86
MC3 | D1 | 92 | 360 | 2016-10-10 07:04 | 2016-10-10 08:22 | 330 | 423 | 393 | Burners | F7803A Mill Burner Temps | Mill Creek | Derate | Coal | 3 | 2016 | 10 | 1.3 | 0.28582 | 112.3255 | 86.4043 | 86
MC3 | PO | 93 | 8450 | 2016-10-21 22:16 | 2016-10-30 11:18 | 0 | 423 | 393 | Inspection B | F590Planned Outage | Mill Creek | Other | Coal | 3 | 2016 | 10 | 205.0333 | 205.0333 | 80578.1 | 393 | 393
MC3 | U1 | 94 | 1480 | 2016-10-30 16:22 | 2016-10-30 23:30 | 0 | 423 | 393 | Other induced draft fan problems | F1903A ID Fan Coolant | Mill Creek | Outage | Coal | 3 | 2016 | 10 | 7.1333 | 7.1333 | 2803.4 | 393 | 393
MC3 | D4 | 95 | 310 | 2016-11-07 22:30 | 2016-11-08 05:29 | 330 | 423 | 393 | Pulverizer mills | F5903B Coal Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2016 | 11 | 6.9833 | 1.5353 | 603.3897 | 86.4043 | 86
MC3 | D1 | 96 | 270 | 2016-11-12 07:39 | 2016-11-12 09:40 | 370 | 423 | 393 | Primary air duct and dampers | F4003A Mill PA fan dampers will not operate | Mill Creek | Derate | Coal | 3 | 2016 | 11 | 2.0167 | 0.25268 | 99.303 | 49.2411 | 49
MC3 | D1 | 97 | 360 | 2016-11-12 13:20 | 2016-11-12 14:00 | 370 | 423 | 393 | Burners | F7803A Mill burner temps too high, caused dampers to close | Mill Creek | Derate | Coal | 3 | 2016 | 11 | 0.66667 | 0.08353 | 32.8274 | 49.2411 | 49
MC3 | U1 | 98 | 9300 | 2016-11-14 08:45 | 2016-11-14 11:07 | 0 | 423 | 393 | Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | F820Power Circuit Breaker Trip | Mill Creek | Outage | Coal | 3 | 2016 | 11 | 2.3667 | 2.3667 | 930.1 | 393 | 393
MC3 | D4 | 99 | 250 | 2016-11-17 23:00 | 2016-11-18 05:10 | 340 | 423 | 393 | Pulverizer feeders | F5903B Coal Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2016 | 11 | 6.1667 | 1.21 | 475.5331 | 77.1135 | 77
MC3 | D1 | 100 | 264 | 2016-11-21 05:07 | 2016-11-21 07:33 | 330 | 423 | 393 | Other primary air fan problems | F1203A PA Fan Would Not Start (clogged sensing line) | Mill Creek | Derate | Coal | 3 | 2016 | 11 | 2.4333 | 0.53499 | 210.2504 | 86.4043 | 86
MC3 | D4 | 101 | 250 | 2016-12-07 23:00 | 2016-12-08 03:26 | 330 | 423 | 393 | Pulverizer feeders | F5903A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2016 | 12 | 4.4333 | 0.9747 | 383.0589 | 86.4043 | 86
MC3 | D4 | 102 | 310 | 2016-12-13 23:00 | 2016-12-14 05:10 | 330 | 423 | 393 | Pulverizer mills | F5903A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2016 | 12 | 6.1667 | 1.3558 | 532.8262 | 86.4043 | 86
MC3 | U1 | 103 | 3416 | 2016-12-18 18:40 | 2016-12-18 21:19 | 0 | 423 | 393 | Other feedwater pump problems | F820Feedwater Flow (Tripped during TDBFP Testing) | Mill Creek | Outage | Coal | 3 | 2016 | 12 | 2.65 | 2.65 | 1041.45 | 393 | 393
MC3 | D4 | 104 | 310 | 2016-12-20 23:02 | 2016-12-21 03:29 | 330 | 423 | 393 | Pulverizer mills | F5903B Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2016 | 12 | 4.45 | 0.97837 | 384.4989 | 86.4043 | 86
MC3 | D4 | 1 | 310 | 2017-01-23 23:00 | 2017-01-24 08:36 | 325 | 423 | 393 | Pulverizer mills | F5903A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 1 | 9.6 | 2.2241 | 874.0766 | 91.0496 | 91
MC3 | D4 | 2 | 310 | 2017-02-01 23:00 | 2017-02-02 05:20 | 330 | 423 | 393 | Pulverizer mills | F5903D Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 2 | 6.3333 | 1.3924 | 547.227 | 86.4043 | 86
MC3 | D4 | 3 | 310 | 2017-02-02 23:00 | 2017-02-03 06:40 | 330 | 423 | 393 | Pulverizer mills | F5903C Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 2 | 7.6667 | 1.6856 | 662.4326 | 86.4043 | 86
MC3 | NC | 4 | 4490 | 2017-02-03 08:00 | 2017-02-03 09:23 | 0 | 423 | 393 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Full Load Capability Testing | Mill Creek | Other | Coal | 3 | 2017 | 2 | 1.3833 | 1.3833 | 543.65 | 393 | 393
MC3 | D4 | 5 | 310 | 2017-02-05 23:00 | 2017-02-06 05:18 | 330 | 423 | 393 | Pulverizer mills | F7903B Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 2 | 6.3 | 1.3851 | 544.3468 | 86.4043 | 86
MC3 | NC | 6 | 9999 | 2017-02-09 07:30 | 2017-02-09 14:31 | 0 | 423 | 393 | Total unit performance testing (use appropriate codes for individual component testing) | F790Full Load Capability Testing | Mill Creek | Other | Coal | 3 | 2017 | 2 | 7.0167 | 7.0167 | 2757.55 | 393 | 393
MC3 | U1 | 7 | 370 | 2017-02-26 22:49 | 2017-02-27 03:01 | 0 | 423 | 393 | Burner instruments and controls (except light-off) | F820Master Fuel Trip (Lost Flame Scanner) | Mill Creek | Outage | Coal | 3 | 2017 | 2 | 4.2 | 4.2 | 1650.6 | 393 | 393
MC3 | D4 | 8 | 310 | 2017-03-05 23:37 | 2017-03-06 01:39 | 330 | 423 | 393 | Pulverizer mills | F5903A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 3 | 2.0333 | 0.44704 | 175.6887 | 86.4043 | 86
MC3 | NC | 9 | 370 | 2017-03-10 22:53 | 2017-03-11 05:58 | 0 | 423 | 393 | Burner instruments and controls (except light-off) | F590Scanner Tuning - Various Loads | Mill Creek | Other | Coal | 3 | 2017 | 3 | 7.0833 | 7.0833 | 2783.75 | 393 | 393
MC3 | NC | 10 | 370 | 2017-03-11 22:32 | 2017-03-12 01:08 | 0 | 423 | 393 | Burner instruments and controls (except light-off) | F590Scanner Tuning - Various Loads | Mill Creek | Other | Coal | 3 | 2017 | 3 | 2.6 | 2.6 | 1021.8 | 393 | 393
MC3 | PO | 11 | 520 | 2017-03-17 22:03 | 2017-03-25 03:08 | 0 | 423 | 393 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | F530Planned Outage | Mill Creek | Other | Coal | 3 | 2017 | 3 | 173.0833 | 173.0833 | 68021.75 | 393 | 393
MC3 | D1 | 12 | 280 | 2017-03-25 20:15 | 2017-03-26 01:41 | 360 | 423 | 393 | Pulverizer fires | F7803A Coal Mill Fire | Mill Creek | Derate | Coal | 3 | 2017 | 3 | 5.4333 | 0.80922 | 318.0234 | 58.5319 | 59
MC3 | NC | 13 | 1990 | 2017-04-17 23:09 | 2017-04-18 04:37 | 0 | 423 | 393 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Boiler Tuning - Various Loads | Mill Creek | Other | Coal | 3 | 2017 | 4 | 5.4667 | 5.4667 | 2148.4 | 393 | 393
MC3 | NC | 14 | 1990 | 2017-04-18 23:00 | 2017-04-19 04:45 | 0 | 423 | 393 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Boiler Tuning - Various Loads | Mill Creek | Other | Coal | 3 | 2017 | 4 | 5.75 | 5.75 | 2259.75 | 393 | 393
MC3 | D4 | 15 | 310 | 2017-04-20 23:00 | 2017-04-21 03:48 | 330 | 423 | 393 | Pulverizer mills | F5903A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 4 | 4.8 | 1.0553 | 414.7404 | 86.4043 | 86
MC3 | D4 | 16 | 310 | 2017-04-23 23:00 | 2017-04-24 03:27 | 330 | 423 | 393 | Pulverizer mills | F5903A Mill & Feeder Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 4 | 4.45 | 0.97837 | 384.4989 | 86.4043 | 86
MC3 | D4 | 17 | 310 | 2017-04-30 23:00 | 2017-05-01 05:00 | 340 | 423 | 393 | Pulverizer mills | F5903D Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 4 | 6 | 1.1773 | 462.6809 | 77.1135 | 77
MC3 | D4 | 19 | 310 | 2017-05-01 22:00 | 2017-05-02 02:38 | 340 | 423 | 393 | Pulverizer mills | F5903D Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 5 | 4.6333 | 0.90914 | 357.2924 | 77.1135 | 77
MC3 | D4 | 20 | 312 | 2017-05-02 22:00 | 2017-05-03 04:00 | 340 | 423 | 393 | Pulverizer mill classifiers | F5903D Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 5 | 6 | 1.1773 | 462.6809 | 77.1135 | 77
MC3 | D4 | 22 | 310 | 2017-05-03 22:00 | 2017-05-04 03:52 | 340 | 423 | 393 | Pulverizer mills | F5903B Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 5 | 5.8667 | 1.1511 | 452.3991 | 77.1135 | 77
MC3 | D4 | 23 | 310 | 2017-05-04 22:00 | 2017-05-05 03:47 | 340 | 423 | 393 | Pulverizer mills | F5903C Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 5 | 5.7833 | 1.1348 | 445.9729 | 77.1135 | 77
MC3 | D4 | 24 | 310 | 2017-05-09 22:00 | 2017-05-10 03:20 | 340 | 423 | 393 | Pulverizer mills | F5903C Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 5 | 5.3333 | 1.0465 | 411.2719 | 77.1135 | 77
MC3 | D4 | 25 | 310 | 2017-05-11 22:25 | 2017-05-12 04:20 | 340 | 423 | 393 | Pulverizer mills | F5903A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 5 | 5.9167 | 1.161 | 456.2547 | 77.1135 | 77
MC3 | U1 | 26 | 520 | 2017-05-20 01:17 | 2017-05-20 16:41 | 0 | 423 | 393 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | F830Main Steam Non-Return Valve Packing Leak | Mill Creek | Outage | Coal | 3 | 2017 | 5 | 15.4 | 15.4 | 6052.2 | 393 | 393
MC3 | MO | 27 | 1487 | 2017-05-20 16:41 | 2017-05-23 00:01 | 0 | 423 | 393 | Air heater (tubular) | FF00Clean Water Coils & Boiler Deslag | Mill Creek | Maintenance | Coal | 3 | 2017 | 5 | 55.3333 | 55.3333 | 21746 | 393 | 393
MC3 | U1 | 28 | 800 | 2017-05-25 06:02 | 2017-05-25 07:15 | 0 | 423 | 393 | Drums and drum internals (single drum only) | F820High Drum Level (Lost B Mill) | Mill Creek | Outage | Coal | 3 | 2017 | 5 | 1.2167 | 1.2167 | 478.15 | 393 | 393
MC3 | U1 | 29 | 1475 | 2017-06-08 09:09 | 2017-06-08 12:53 | 0 | 423 | 393 | Induced draft fan controls | F820ID Fan Trip | Mill Creek | Outage | Coal | 3 | 2017 | 6 | 3.7333 | 3.7333 | 1467.2 | 393 | 393
MC3 | D1 | 30 | 1850 | 2017-06-08 18:53 | 2017-06-08 23:27 | 355 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica - Startup | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 4.5667 | 0.73412 | 288.5097 | 63.1773 | 63
MC3 | D1 | 31 | 310 | 2017-06-11 06:34 | 2017-06-11 07:20 | 370 | 423 | 393 | Pulverizer mills | F7803C Mill Bearing Temperature Indication | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 0.76667 | 0.09606 | 37.7515 | 49.2411 | 49
MC3 | D1 | 32 | 1456 | 2017-06-16 14:03 | 2017-06-16 22:00 | 405 | 423 | 393 | Induced draft fan dampers | F0603A ID Fan Beck Drive Linkage | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 7.95 | 0.3383 | 132.9511 | 16.7234 | 17
MC3 | D4 | 33 | 1456 | 2017-06-16 22:00 | 2017-06-16 23:45 | 200 | 423 | 393 | Induced draft fan dampers | F0603A ID Fan Beck Drive Linkage | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 1.75 | 0.92258 | 362.5727 | 207.1844 | 207
MC3 | D1 | 34 | 380 | 2017-06-21 03:02 | 2017-06-21 03:33 | 230 | 423 | 393 | Light-off (igniter) systems (including fuel supply) | F520Gas Gun Unavailable - Vent Line Issue | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 0.51667 | 0.23574 | 92.6446 | 179.3121 | 179
MC3 | D1 | 35 | 310 | 2017-06-24 13:07 | 2017-06-24 18:00 | 365 | 423 | 393 | Pulverizer mills | F0603C Coal Mill | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 4.8833 | 0.66958 | 263.1459 | 53.8865 | 54
MC3 | D1 | 36 | 250 | 2017-06-25 20:50 | 2017-06-26 04:47 | 340 | 423 | 393 | Pulverizer feeders | F0603C Feeder Belt | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 7.95 | 1.5599 | 613.0521 | 77.1135 | 77
MC3 | D4 | 37 | 310 | 2017-07-06 23:00 | 2017-07-07 04:56 | 340 | 423 | 393 | Pulverizer mills | F5903A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 7 | 5.9333 | 1.1642 | 457.54 | 77.1135 | 77
MC3 | D4 | 38 | 310 | 2017-07-11 23:00 | 2017-07-12 04:00 | 330 | 423 | 393 | Pulverizer mills | F5903B Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 7 | 5 | 1.0993 | 432.0213 | 86.4043 | 86
MC3 | D4 | 39 | 310 | 2017-07-12 04:00 | 2017-07-12 04:53 | 330 | 423 | 393 | Pulverizer mills | F5903B Mill Maintenance (Extension) | Mill Creek | Derate | Coal | 3 | 2017 | 7 | 0.88333 | 0.19421 | 76.3238 | 86.4043 | 86
MC3 | D1 | 40 | 250 | 2017-07-12 05:42 | 2017-07-12 06:28 | 320 | 423 | 393 | Pulverizer feeders | F5203B Mill - Feeder Plugged Alarm | Mill Creek | Derate | Coal | 3 | 2017 | 7 | 0.76667 | 0.18668 | 73.3662 | 95.695 | 96
MC3 | D4 | 41 | 310 | 2017-07-12 23:00 | 2017-07-13 02:51 | 320 | 423 | 393 | Pulverizer mills | F5903D Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 7 | 3.85 | 0.93747 | 368.4259 | 95.695 | 96
MC3 | D1 | 42 | 340 | 2017-07-13 02:51 | 2017-07-13 16:40 | 320 | 423 | 393 | Other pulverizer problems | F0603D Mill Maintenance - Tension Cable Broken | Mill Creek | Derate | Coal | 3 | 2017 | 7 | 13.8167 | 3.3643 | 1322.1864 | 95.695 | 96
MC3 | D4 | 43 | 310 | 2017-07-16 23:00 | 2017-07-17 04:00 | 350 | 423 | 393 | Pulverizer mills | F5903C Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 7 | 5 | 0.86288 | 339.1135 | 67.8227 | 68
MC3 | D4 | 45 | 310 | 2017-07-17 22:00 | 2017-07-18 04:09 | 350 | 423 | 393 | Pulverizer mills | F5903D Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 7 | 6.15 | 1.0613 | 417.1096 | 67.8227 | 68
MC3 | D1 | 46 | 250 | 2017-07-27 16:12 | 2017-07-27 17:00 | 380 | 423 | 393 | Pulverizer feeders | F7003C Coal Feeder Won't Start - Water In Control Box | Mill Creek | Derate | Coal | 3 | 2017 | 7 | 0.8 | 0.081324 | 31.9603 | 39.9504 | 40
MC3 | D4 | 47 | 590 | 2017-08-04 21:30 | 2017-08-05 10:00 | 116 | 423 | 393 | Desuperheater/attemperator valves | F540Repair Packing On SH Spray Block Valve | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 12.5 | 9.0721 | 3565.3369 | 285.227 | 285
MC3 | D4 | 48 | 310 | 2017-08-07 23:37 | 2017-08-08 04:24 | 320 | 423 | 393 | Pulverizer mills | F5903A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 4.7833 | 1.1647 | 457.7413 | 95.695 | 96
MC3 | D4 | 49 | 310 | 2017-08-08 21:46 | 2017-08-09 00:53 | 320 | 423 | 393 | Pulverizer mills | F5903C Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 3.1167 | 0.7589 | 298.2495 | 95.695 | 96
MC3 | D1 | 50 | 310 | 2017-08-09 00:53 | 2017-08-09 05:16 | 225 | 423 | 393 | Pulverizer mills | F6203C Mill Maint. & 3A Coal Mill Inspection For Suspected Light Off During Purge | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 4.3833 | 2.0518 | 806.3468 | 183.9574 | 184
MC3 | D1 | 51 | 310 | 2017-08-09 05:16 | 2017-08-09 06:25 | 330 | 423 | 393 | Pulverizer mills | F5303A Coal Mill Inspection For Suspected Light Off During Purge (Debris Found) | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 1.15 | 0.25284 | 99.3649 | 86.4043 | 86
MC3 | D4 | 52 | 310 | 2017-08-09 22:00 | 2017-08-10 01:47 | 330 | 423 | 393 | Pulverizer mills | F5903D Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 3.7833 | 0.8318 | 326.8961 | 86.4043 | 86
MC3 | D4 | 53 | 310 | 2017-08-13 23:00 | 2017-08-14 01:20 | 320 | 423 | 393 | Pulverizer mills | F5903D Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 2.3333 | 0.56816 | 223.2884 | 95.695 | 96
MC3 | D4 | 54 | 310 | 2017-08-15 22:00 | 2017-08-16 04:30 | 330 | 423 | 393 | Pulverizer mills | F5903D Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 6.5 | 1.4291 | 561.6277 | 86.4043 | 86
MC3 | D4 | 56 | 260 | 2017-08-17 22:00 | 2017-08-18 01:18 | 330 | 423 | 393 | Primary air fan | F5903A Mill PA Fan Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 3.3 | 0.72553 | 285.134 | 86.4043 | 86
MC3 | D1 | 57 | 3210 | 2017-08-20 13:43 | 2017-08-20 17:55 | 400 | 423 | 393 | Circulating water pumps | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 4.2 | 0.22837 | 89.7489 | 21.3688 | 21
MC3 | D1 | 58 | 3210 | 2017-08-21 12:40 | 2017-08-21 15:00 | 406 | 423 | 393 | Circulating water pumps | F660High Back Pressure - Low Circulating Water Flow | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 2.3333 | 0.093775 | 36.8534 | 15.7943 | 16
MC3 | D1 | 59 | 3210 | 2017-08-21 15:00 | 2017-08-22 05:30 | 400 | 423 | 393 | Circulating water pumps | F660High Back Pressure - Low Circulating Water Flow | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 14.5 | 0.78842 | 309.8475 | 21.3688 | 21
MC3 | D1 | 60 | 3210 | 2017-08-22 08:15 | 2017-08-22 14:19 | 400 | 423 | 393 | Circulating water pumps | F660High Back Pressure - Low Circulating Water Flow | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 6.0667 | 0.32987 | 129.6374 | 21.3688 | 21
MC3 | D4 | 61 | 3210 | 2017-08-22 23:00 | 2017-08-22 23:35 | 200 | 423 | 393 | Circulating water pumps | F6603A CTP Removed From Service | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 0.58333 | 0.30753 | 120.8576 | 207.1844 | 207
MC3 | D4 | 62 | 3210 | 2017-08-23 23:00 | 2017-08-24 02:00 | 200 | 423 | 393 | Circulating water pumps | F6603A CTP Removed From Service | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 3 | 1.5816 | 621.5532 | 207.1844 | 207
MC3 | D4 | 63 | 310 | 2017-08-29 01:32 | 2017-08-29 03:04 | 350 | 423 | 393 | Pulverizer mills | F5903A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 1.5333 | 0.26462 | 103.9948 | 67.8227 | 68
MC3 | D4 | 64 | 310 | 2017-08-31 22:43 | 2017-09-01 03:19 | 325 | 423 | 393 | Pulverizer mills | F5903A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 8 | 4.6 | 1.0657 | 418.8284 | 91.0496 | 91
MC3 | D1 | 65 | 3210 | 2017-09-20 12:52 | 2017-09-20 20:47 | 399 | 423 | 393 | Circulating water pumps | F660High Back Pressure - Low Circulating Water Flow | Mill Creek | Derate | Coal | 3 | 2017 | 9 | 7.9167 | 0.44917 | 176.5248 | 22.2979 | 22
MC3 | D1 | 66 | 3210 | 2017-09-21 13:00 | 2017-09-21 20:37 | 403 | 423 | 393 | Circulating water pumps | F660High Back Pressure - Low Circulating Water Flow | Mill Creek | Derate | Coal | 3 | 2017 | 9 | 7.6167 | 0.36013 | 141.5296 | 18.5816 | 19
MC3 | D1 | 67 | 3210 | 2017-09-22 12:00 | 2017-09-22 21:18 | 404 | 423 | 393 | Circulating water pumps | F660High Back Pressure - Low Circulating Water Flow | Mill Creek | Derate | Coal | 3 | 2017 | 9 | 9.3 | 0.41773 | 164.1681 | 17.6525 | 18
MC3 | D4 | 68 | 250 | 2017-09-24 22:00 | 2017-09-25 03:35 | 325 | 423 | 393 | Pulverizer feeders | F5903B Feeder Belt Replacment | Mill Creek | Derate | Coal | 3 | 2017 | 9 | 5.5833 | 1.2935 | 508.3605 | 91.0496 | 91
MC3 | D1 | 69 | 3210 | 2017-09-25 12:26 | 2017-09-25 18:52 | 407 | 423 | 393 | Circulating water pumps | F660High Back Pressure - Low Circulating Water Flow | Mill Creek | Derate | Coal | 3 | 2017 | 9 | 6.4333 | 0.24334 | 95.6331 | 14.8652 | 15
MC3 | D1 | 70 | 3210 | 2017-09-27 11:22 | 2017-09-27 22:33 | 410 | 423 | 393 | Circulating water pumps | F660High Back Pressure - Low Circulating Water Flow | Mill Creek | Derate | Coal | 3 | 2017 | 9 | 11.1833 | 0.3437 | 135.0725 | 12.078 | 12
MC3 | D4 | 71 | 335 | 2017-09-29 22:00 | 2017-09-30 07:12 | 330 | 423 | 393 | Pulverizer lube oil system | F5903B Mill Maintenance - Change oil in rollers | Mill Creek | Derate | Coal | 3 | 2017 | 9 | 9.2 | 2.0227 | 794.9191 | 86.4043 | 86
MC3 | D4 | 72 | 335 | 2017-09-30 22:00 | 2017-10-01 05:15 | 330 | 423 | 393 | Pulverizer lube oil system | F5903D Mill Maintenance - Change oil in rollers | Mill Creek | Derate | Coal | 3 | 2017 | 9 | 7.25 | 1.594 | 626.4309 | 86.4043 | 86
MC3 | D1 | 73 | 385 | 2017-10-01 05:50 | 2017-10-01 06:08 | 350 | 423 | 393 | Igniters | F5203B Mill Gas Guns | Mill Creek | Derate | Coal | 3 | 2017 | 10 | 0.3 | 0.051773 | 20.3468 | 67.8227 | 68
MC3 | D1 | 74 | 310 | 2017-10-09 04:48 | 2017-10-09 05:42 | 330 | 423 | 393 | Pulverizer mills | F5903D Coal Mill Unavailable (No call to dispatch) | Mill Creek | Derate | Coal | 3 | 2017 | 10 | 0.9 | 0.19787 | 77.7638 | 86.4043 | 86
MC3 | D4 | 75 | 310 | 2017-10-09 23:00 | 2017-10-10 04:01 | 330 | 423 | 393 | Pulverizer mills | F5903C Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 10 | 5.0167 | 1.103 | 433.4613 | 86.4043 | 86
MC3 | D4 | 77 | 310 | 2017-10-10 22:30 | 2017-10-11 03:31 | 330 | 423 | 393 | Pulverizer mills | F5903B Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 10 | 5.0167 | 1.103 | 433.4613 | 86.4043 | 86
MC3 | D1 | 78 | 335 | 2017-10-11 05:09 | 2017-10-11 05:40 | 340 | 423 | 393 | Pulverizer lube oil system | F6603B Mill Maintenance - Lube Oil Pump | Mill Creek | Derate | Coal | 3 | 2017 | 10 | 0.51667 | 0.10138 | 39.842 | 77.1135 | 77
MC3 | D4 | 79 | 310 | 2017-10-11 21:45 | 2017-10-12 03:17 | 340 | 423 | 393 | Pulverizer mills | F5903A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 10 | 5.5333 | 1.0857 | 426.6946 | 77.1135 | 77
MC3 | D1 | 80 | 250 | 2017-11-01 12:06 | 2017-11-01 12:57 | 340 | 423 | 393 | Pulverizer feeders | F1203C Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 3 | 2017 | 11 | 0.85 | 0.16678 | 65.5465 | 77.1135 | 77
MC3 | D1 | 81 | 3210 | 2017-11-05 23:35 | 2017-11-06 02:40 | 375 | 423 | 393 | Circulating water pumps | F660High Back Pressure - Low Circulating Water Flow | Mill Creek | Derate | Coal | 3 | 2017 | 11 | 3.0833 | 0.34988 | 137.5035 | 44.5957 | 45
MC3 | NC | 82 | 3690 | 2017-11-12 12:00 | 2017-11-12 13:51 | 0 | 423 | 393 | Station Service Power Distribution System - General | F610MC4 Controls Work | Mill Creek | Other | Coal | 3 | 2017 | 11 | 1.85 | 1.85 | 727.05 | 393 | 393
MC3 | D4 | 83 | 260 | 2017-11-21 23:00 | 2017-11-22 04:00 | 325 | 423 | 393 | Primary air fan | F5903B PA Fan Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 11 | 5 | 1.1584 | 455.2482 | 91.0496 | 91
MC3 | NC | 85 | 3650 | 2017-11-24 09:00 | 2017-11-24 14:25 | 0 | 423 | 393 | DC instrument power battery chargers | F790Placing New Batteries in Service (Unit 4) | Mill Creek | Other | Coal | 3 | 2017 | 11 | 5.4167 | 5.4167 | 2128.75 | 393 | 393
MC3 | U1 | 86 | 110 | 2017-11-25 02:32 | 2017-11-25 16:52 | 0 | 423 | 393 | Other coal fuel supply problems up through bunkers | F490Coal Supply To Bunker Issues - Conveyor | Mill Creek | Outage | Coal | 3 | 2017 | 11 | 14.3333 | 14.3333 | 5633 | 393 | 393
MC3 | D1 | 87 | 1850 | 2017-11-26 01:20 | 2017-11-26 03:05 | 385 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica - Startup | Mill Creek | Derate | Coal | 3 | 2017 | 11 | 1.75 | 0.15721 | 61.7837 | 35.305 | 35
MC3 | NC | 88 | 4842 | 2017-12-05 13:58 | 2017-12-05 15:49 | 0 | 423 | 393 | Reactive and capability testing | F790MOD 36 Testing - Out of AGC | Mill Creek | Other | Coal | 3 | 2017 | 12 | 1.85 | 1.85 | 727.05 | 393 | 393
MC3 | D1 | 89 | 385 | 2017-12-13 03:58 | 2017-12-13 04:28 | 365 | 423 | 393 | Igniters | F690Igniter Issues | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 0.5 | 0.068558 | 26.9433 | 53.8865 | 54
MC3 | D4 | 90 | 260 | 2017-12-15 22:48 | 2017-12-16 12:00 | 330 | 423 | 393 | Primary air fan | F5903B PA Fan Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 13.2 | 2.9021 | 1140.5362 | 86.4043 | 86
MC3 | D4 | 92 | 260 | 2017-12-18 22:00 | 2017-12-19 01:07 | 330 | 423 | 393 | Primary air fan | F5903B Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 3.1167 | 0.68522 | 269.2933 | 86.4043 | 86
MC3 | D4 | 93 | 260 | 2017-12-19 23:00 | 2017-12-20 03:34 | 340 | 423 | 393 | Primary air fan | F5903B PA Fan Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 4.5667 | 0.89606 | 352.1515 | 77.1135 | 77
MC3 | D4 | 94 | 260 | 2017-12-20 23:00 | 2017-12-21 00:47 | 340 | 423 | 393 | Primary air fan | F8503B PA Fan Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 1.7833 | 0.34992 | 137.519 | 77.1135 | 77
MC3 | D4 | 95 | 260 | 2017-12-21 21:38 | 2017-12-22 18:05 | 340 | 423 | 393 | Primary air fan | F8503B PA Fan Coupling Replacement | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 20.45 | 4.0126 | 1576.9706 | 77.1135 | 77
MC3 | D1 | 96 | 250 | 2017-12-25 10:37 | 2017-12-25 13:30 | 340 | 423 | 393 | Pulverizer feeders | F8103A Coal Feeder Belt Torn | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 2.8833 | 0.56576 | 222.3439 | 77.1135 | 77
MC3 | D1 | 97 | 250 | 2017-12-25 13:30 | 2017-12-25 19:10 | 230 | 423 | 393 | Pulverizer feeders | F8103A and 3C Coal Feeders Unavailable | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 5.6667 | 2.5855 | 1016.1017 | 179.3121 | 179
MC3 | D1 | 98 | 250 | 2017-12-25 19:10 | 2017-12-25 22:15 | 340 | 423 | 393 | Pulverizer feeders | F7203C Coal Feeder Unavailable - Lower Bunker Valve | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 3.0833 | 0.605 | 237.7665 | 77.1135 | 77
MC3 | D4 | 1 | 250 | 2018-01-03 23:00 | 2018-01-04 02:38 | 330 | 423 | 393 | Pulverizer feeders | F5903A Coal Feeder Bearing Replacement | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 3.6333 | 0.79882 | 313.9355 | 86.4043 | 86
MC3 | D4 | 2 | 253 | 2018-01-07 22:00 | 2018-01-08 02:40 | 330 | 423 | 393 | Pulverizer feeder motor | F5903A Coal Feeder Maintenance | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 4.6667 | 1.026 | 403.2199 | 86.4043 | 86
MC3 | D1 | 3 | 350 | 2018-01-09 05:48 | 2018-01-09 06:48 | 330 | 423 | 393 | Pulverized fuel and air piping (from pulverizer to wind box) | F5203B Coal Mill Swing Valve Indication | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 1 | 0.21986 | 86.4043 | 86.4043 | 86
MC3 | D4 | 4 | 310 | 2018-01-09 23:00 | 2018-01-10 04:00 | 330 | 423 | 393 | Pulverizer mills | F5903A Coal Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 5 | 1.0993 | 432.0213 | 86.4043 | 86
MC3 | D4 | 6 | 310 | 2018-01-10 23:00 | 2018-01-11 04:00 | 330 | 423 | 393 | Pulverizer mills | F5903B Coal Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 5 | 1.0993 | 432.0213 | 86.4043 | 86
MC3 | D4 | 8 | 310 | 2018-01-11 22:00 | 2018-01-12 04:00 | 330 | 423 | 393 | Pulverizer mills | F5903C Coal Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 6 | 1.3191 | 518.4255 | 86.4043 | 86
MC3 | D4 | 10 | 310 | 2018-01-21 22:00 | 2018-01-22 04:00 | 330 | 423 | 393 | Pulverizer mills | F5903D Coal Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 6 | 1.3191 | 518.4255 | 86.4043 | 86
MC3 | D4 | 12 | 260 | 2018-01-25 21:00 | 2018-01-26 05:00 | 330 | 423 | 393 | Primary air fan | F5903B PA Fan Maintenance | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 8 | 1.7589 | 691.234 | 86.4043 | 86
MC3 | D4 | 14 | 255 | 2018-01-28 22:30 | 2018-01-29 03:52 | 330 | 423 | 393 | Pulverizer feeder coal scales | F0903D Coal Feeder Calibration | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 5.3667 | 1.1799 | 463.7028 | 86.4043 | 86
MC3 | D1 | 15 | 250 | 2018-01-29 06:42 | 2018-01-29 13:10 | 340 | 423 | 393 | Pulverizer feeders | F8103A Coal Feeder Belt Torn | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 6.4667 | 1.2689 | 498.6671 | 77.1135 | 77
MC3 | D1 | 16 | 3110 | 2018-02-05 09:02 | 2018-02-05 10:20 | 375 | 423 | 393 | Condenser tube leaks | F540High Silica - Condenser Tube Leak | Mill Creek | Derate | Coal | 3 | 2018 | 2 | 1.3 | 0.14752 | 57.9745 | 44.5957 | 45
MC3 | MO | 17 | 3110 | 2018-02-05 22:36 | 2018-02-06 21:23 | 0 | 423 | 393 | Condenser tube leaks | F540Condenser Tube Leak Repairs | Mill Creek | Maintenance | Coal | 3 | 2018 | 2 | 22.7833 | 22.7833 | 8953.85 | 393 | 393
MC3 | D1 | 18 | 3110 | 2018-02-07 05:23 | 2018-02-08 05:16 | 298 | 423 | 393 | Condenser tube leaks | F540High Silica - Return From Condenser Leak (Variable Derate: Avg Load 298 MW) | Mill Creek | Derate | Coal | 3 | 2018 | 2 | 23.8833 | 7.0577 | 2773.685 | 116.1348 | 116
MC3 | D1 | 19 | 3112 | 2018-02-19 14:10 | 2018-02-19 22:37 | 385 | 423 | 393 | Condenser tube fouling tube side | F660High Condenser Backpressure | Mill Creek | Derate | Coal | 3 | 2018 | 2 | 8.45 | 0.7591 | 298.327 | 35.305 | 35
MC3 | U1 | 20 | 1050 | 2018-02-19 22:37 | 2018-02-22 09:16 | 0 | 423 | 393 | Second superheater B | F830Boiler Tube Leak - Secondary Superheat | Mill Creek | Outage | Coal | 3 | 2018 | 2 | 58.65 | 58.65 | 23049.45 | 393 | 393
MC3 | D1 | 21 | 1850 | 2018-02-22 21:16 | 2018-02-23 04:10 | 350 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica - Startup | Mill Creek | Derate | Coal | 3 | 2018 | 2 | 6.9 | 1.1908 | 467.9766 | 67.8227 | 68
MC3 | D1 | 22 | 1850 | 2018-02-24 17:53 | 2018-02-24 18:55 | 401 | 423 | 393 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2018 | 2 | 1.0333 | 0.053743 | 21.121 | 20.4397 | 20
MC3 | D4 | 23 | 1455 | 2018-03-01 23:00 | 2018-03-01 23:29 | 240 | 423 | 393 | Induced draft fans | F5203A ID Fan Indication Issue | Mill Creek | Derate | Coal | 3 | 2018 | 3 | 0.48333 | 0.2091 | 82.177 | 170.0213 | 170
MC3 | D1 | 24 | 262 | 2018-03-13 07:02 | 2018-03-13 17:24 | 340 | 423 | 393 | Primary air fan lube oil system | F7603D PA Fan Bearing Oil Temperature High | Mill Creek | Derate | Coal | 3 | 2018 | 3 | 10.3667 | 2.0341 | 799.4097 | 77.1135 | 77
MC3 | PO | 25 | 1801 | 2018-03-30 21:59 | 2018-04-30 |  | 423 | 393 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Planned Outage - 4 Weeks - Spring 2018 | Mill Creek | Other | Coal | 3 | 2018 | 3 | 722.0167 | 722.0167 | 283752.55 | 393 | 393
MC4 | U1 | 1 | 1060 | 2013-01-01 | 2013-01-02 03:15 | 0 | 521 | 482 | First reheater A | F540Boiler Tube Leak - First Reheater | Mill Creek | Outage | Coal | 3 | 2013 | 1 | 27.25 | 27.25 | 13134.5 | 482 | 482
MC4 | NC | 2 | 1850 | 2013-01-02 03:15 | 2013-01-02 15:12 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2013 | 1 | 11.95 | 11.95 | 5759.9 | 482 | 482
MC4 | D1 | 3 | 1850 | 2013-01-02 15:12 | 2013-01-02 22:00 | 365 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 6.8 | 2.0361 | 981.3927 | 144.3225 | 144
MC4 | D1 | 4 | 1850 | 2013-01-02 22:00 | 2013-01-02 23:59 | 385 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 1.9833 | 0.51772 | 249.5422 | 125.8196 | 126
MC4 | D1 | 5 | 1850 | 2013-01-02 23:59 | 2013-01-03 01:20 | 460 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 1.35 | 0.15806 | 76.1856 | 56.4338 | 56
MC4 | D1 | 6 | 1850 | 2013-01-03 01:20 | 2013-01-03 05:10 | 485 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 3.8333 | 0.26488 | 127.6699 | 33.3052 | 33
MC4 | D1 | 7 | 310 | 2013-01-03 05:17 | 2013-01-03 08:01 | 425 | 521 | 482 | Pulverizer mills | F5904C Coal Mill - Primary Air Fan Discharge Damper Repair | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 2.7333 | 0.50365 | 242.7578 | 88.8138 | 89
MC4 | D1 | 8 | 9270 | 2013-01-14 00:19 | 2013-01-14 03:54 | 425 | 521 | 482 | Wet coal | FW004D Coal Mill - Wet Coal Issues | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 3.5833 | 0.66027 | 318.2495 | 88.8138 | 89
MC4 | D1 | 9 | 9270 | 2013-01-14 07:05 | 2013-01-14 08:47 | 425 | 521 | 482 | Wet coal | FW004D Coal Feeder - Plugged, Wet Coal | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 1.7 | 0.31324 | 150.9835 | 88.8138 | 89
MC4 | D1 | 10 | 9270 | 2013-01-14 08:47 | 2013-01-15 01:59 | 420 | 521 | 482 | Wet coal | FW004D Coal Feeder - Plugged, Wet Coal | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 17.2 | 3.3344 | 1607.1601 | 93.4395 | 93
MC4 | U1 | 11 | 4267 | 2013-01-15 01:59 | 2013-01-15 05:03 | 0 | 521 | 482 | Control valve testing | F820Turbine Control Valve Test - Trip | Mill Creek | Outage | Coal | 3 | 2013 | 1 | 3.0667 | 3.0667 | 1478.1333 | 482 | 482
MC4 | NC | 12 | 1850 | 2013-01-15 05:03 | 2013-01-15 05:19 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 1 | 0.26667 | 0.26667 | 128.5333 | 482 | 482
MC4 | U1 | 13 | 800 | 2013-01-15 05:19 | 2013-01-15 06:58 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820Low Drum Level Trip | Mill Creek | Outage | Coal | 3 | 2013 | 1 | 1.65 | 1.65 | 795.3 | 482 | 482
MC4 | NC | 14 | 1850 | 2013-01-15 06:58 | 2013-01-15 13:10 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 1 | 6.2 | 6.2 | 2988.4 | 482 | 482
MC4 | D1 | 15 | 310 | 2013-01-15 13:10 | 2013-01-16 07:02 | 400 | 521 | 482 | Pulverizer mills | F5904B Coal Mill Primary Air Fan - Replace Inboard Bearing | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 17.8667 | 4.1495 | 2000.0379 | 111.9424 | 112
MC4 | D1 | 16 | 310 | 2013-01-16 07:02 | 2013-01-16 14:37 | 410 | 521 | 482 | Pulverizer mills | F5904B Coal Mill Primary Air Fan - Replace Inboard Bearing | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 7.5833 | 1.6156 | 778.7399 | 102.691 | 103
MC4 | D1 | 17 | 9270 | 2013-01-16 10:25 | 2013-01-16 13:20 | 340 | 521 | 482 | Wet coal | FW004E Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 2.9167 | 1.0133 | 488.3989 | 167.4511 | 167
MC4 | D1 | 18 | 9270 | 2013-01-16 13:20 | 2013-01-16 14:37 | 305 | 521 | 482 | Wet coal | FW004E Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 1.2833 | 0.53205 | 256.4499 | 199.8311 | 200
MC4 | D1 | 19 | 310 | 2013-01-16 14:37 | 2013-01-16 16:00 | 405 | 521 | 482 | Pulverizer mills | F5904B Coal Mill Primary Air Fan - Replace Inboard Bearing | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 1.3833 | 0.308 | 148.4548 | 107.3167 | 107
MC4 | D1 | 20 | 1710 | 2013-01-16 16:00 | 2013-01-17 11:04 | 523 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 19.0667 | -0.073193 | -35.2788 | 0 | 0
MC4 | D1 | 21 | 4609 | 2013-01-18 14:03 | 2013-01-18 14:25 | 420 | 521 | 482 | Other exciter problems | F540Rectifier - Repair Cooling Water Leak | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 0.36667 | 0.071081 | 34.2612 | 93.4395 | 93
MC4 | D4 | 22 | 310 | 2013-01-21 21:00 | 2013-01-22 00:01 | 410 | 521 | 482 | Pulverizer mills | F5904B Coal Mill Primary Air Fan - Damper Repair | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 3.0167 | 0.64271 | 309.7845 | 102.691 | 103
MC4 | D1 | 23 | 1710 | 2013-01-25 09:20 | 2013-01-26 21:34 | 520 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 36.2333 | 0.069546 | 33.521 | 0.92514 | 1
MC4 | U1 | 24 | 1040 | 2013-01-26 21:34 | 2013-01-29 05:05 | 0 | 521 | 482 | First superheater B | F540Boiler Tube Leak - First Superheater | Mill Creek | Outage | Coal | 3 | 2013 | 1 | 55.5167 | 55.5167 | 26759.0333 | 482 | 482
MC4 | NC | 25 | 1850 | 2013-01-29 05:05 | 2013-01-29 06:08 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2013 | 1 | 1.05 | 1.05 | 506.1 | 482 | 482
MC4 | U1 | 26 | 4650 | 2013-01-29 06:08 | 2013-01-29 12:07 | 0 | 521 | 482 | Other cooling system problems | F820Generator - Stator Coolant System Low Flow Trip | Mill Creek | Outage | Coal | 3 | 2013 | 1 | 5.9833 | 5.9833 | 2883.9667 | 482 | 482
MC4 | NC | 27 | 1850 | 2013-01-29 12:07 | 2013-01-29 23:00 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2013 | 1 | 10.8833 | 10.8833 | 5245.7667 | 482 | 482
MC4 | D1 | 28 | 1850 | 2013-01-29 23:00 | 2013-01-30 04:40 | 435 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 1 | 5.6667 | 0.93538 | 450.8535 | 79.5624 | 80
MC4 | D4 | 29 | 360 | 2013-02-06 22:53 | 2013-02-07 00:55 | 420 | 521 | 482 | Burners | F5904A2 Coal Burner - Blanked Burner | Mill Creek | Derate | Coal | 3 | 2013 | 2 | 2.0333 | 0.39418 | 189.9937 | 93.4395 | 93
MC4 | D1 | 30 | 360 | 2013-02-07 00:55 | 2013-02-07 04:25 | 420 | 521 | 482 | Burners | F5904C7 Coal Burner - Blanked Burner | Mill Creek | Derate | Coal | 3 | 2013 | 2 | 3.5 | 0.6785 | 327.0384 | 93.4395 | 93
MC4 | D4 | 31 | 250 | 2013-02-17 22:15 | 2013-02-18 01:30 | 425 | 521 | 482 | Pulverizer feeders | F5904A Coal Feeder - Adjust Belt | Mill Creek | Derate | Coal | 3 | 2013 | 2 | 3.25 | 0.59885 | 288.6449 | 88.8138 | 89
MC4 | U1 | 32 | 1050 | 2013-02-18 21:34 | 2013-02-20 20:24 | 0 | 521 | 482 | Second superheater B | F540Boiler Tube Leak - Second Superheater | Mill Creek | Outage | Coal | 3 | 2013 | 2 | 46.8333 | 46.8333 | 22573.6667 | 482 | 482
MC4 | NC | 33 | 1850 | 2013-02-20 20:24 | 2013-02-21 08:45 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2013 | 2 | 12.35 | 12.35 | 5952.7 | 482 | 482
MC4 | D1 | 34 | 1850 | 2013-02-21 08:45 | 2013-02-21 15:10 | 390 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 2 | 6.4167 | 1.6134 | 777.6606 | 121.1939 | 121
MC4 | D1 | 35 | 1850 | 2013-02-21 15:10 | 2013-02-21 17:02 | 506 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 2 | 1.8667 | 0.053743 | 25.904 | 13.8772 | 14
MC4 | U1 | 36 | 1480 | 2013-02-27 13:12 | 2013-02-27 16:56 | 0 | 521 | 482 | Other induced draft fan problems | F820Loss of all FD & ID Fans; 4B2 breaker trip | Mill Creek | Outage | Coal | 3 | 2013 | 2 | 3.7333 | 3.7333 | 1799.4667 | 482 | 482
MC4 | SF | 37 | 800 | 2013-02-27 16:56 | 2013-02-27 21:22 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F460Low Drum Level | Mill Creek | Outage | Coal | 3 | 2013 | 2 | 4.4333 | 4.4333 | 2136.8667 | 482 | 482
MC4 | D1 | 38 | 8560 | 2013-02-28 05:10 | 2013-02-28 05:48 | 440 | 521 | 482 | Electrostatic precipitator problems | F820Particulate Matter Exceedance Alarm | Mill Creek | Derate | Coal | 3 | 2013 | 2 | 0.63333 | 0.098464 | 47.4599 | 74.9367 | 75
MC4 | D1 | 39 | 8560 | 2013-02-28 05:48 | 2013-02-28 08:06 | 425 | 521 | 482 | Electrostatic precipitator problems | F820Particulate Matter Exceedance | Mill Creek | Derate | Coal | 3 | 2013 | 2 | 2.3 | 0.4238 | 204.2718 | 88.8138 | 89
MC4 | D1 | 40 | 1710 | 2013-02-28 10:00 | 2013-03-01 12:56 | 521 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow | Mill Creek | Derate | Coal | 3 | 2013 | 2 | 26.9333 | 0 | 0 | 0 | 0
MC4 | PO | 41 | 1801 | 2013-03-01 12:56 | 2013-03-17 20:36 | 0 | 521 | 482 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Planned Outage | Mill Creek | Other | Coal | 3 | 2013 | 3 | 391.6667 | 391.6667 | 188783.3333 | 482 | 482
MC4 | NC | 42 | 1850 | 2013-03-17 20:36 | 2013-03-18 12:44 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 3 | 2013 | 3 | 16.1333 | 16.1333 | 7776.2667 | 482 | 482
MC4 | U1 | 43 | 8125 | 2013-03-18 12:44 | 2013-03-18 16:19 | 0 | 521 | 482 | Scrubber recycle (liquid) pumps | F520FGD Recycle Pumps - False Trip Indication | Mill Creek | Outage | Coal | 3 | 2013 | 3 | 3.5833 | 3.5833 | 1727.1667 | 482 | 482
MC4 | NC | 44 | 1850 | 2013-03-18 16:19 | 2013-03-18 23:45 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 3 | 7.4333 | 7.4333 | 3582.8667 | 482 | 482
MC4 | D1 | 45 | 310 | 2013-03-18 23:45 | 2013-03-19 02:46 | 430 | 521 | 482 | Pulverizer mills | F5904A Coal Mill - Breaker Issue | Mill Creek | Derate | Coal | 3 | 2013 | 3 | 3.0167 | 0.5269 | 253.9674 | 84.1881 | 84
MC4 | D1 | 46 | 9270 | 2013-03-19 04:02 | 2013-03-19 12:25 | 430 | 521 | 482 | Wet coal | FW004D Coal Feeder - Wet Coal | Mill Creek | Derate | Coal | 3 | 2013 | 3 | 8.3833 | 1.4643 | 705.7769 | 84.1881 | 84
MC4 | D4 | 47 | 3412 | 2013-03-23 22:00 | 2013-03-24 08:26 | 100 | 521 | 482 | Feedwater pump drive - steam turbine | F590Turbine Driven Boiler Feed Pump - Replace Suction Flow Transmitter | Mill Creek | Derate | Coal | 3 | 2013 | 3 | 10.4333 | 8.4308 | 4063.6331 | 389.4856 | 389
MC4 | U1 | 48 | 800 | 2013-03-24 08:26 | 2013-03-24 10:35 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820Low Drum Level Trip | Mill Creek | Outage | Coal | 3 | 2013 | 3 | 2.15 | 2.15 | 1036.3 | 482 | 482
MC4 | NC | 49 | 1850 | 2013-03-24 10:35 | 2013-03-24 16:35 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 3 | 6 | 6 | 2892 | 482 | 482
MC4 | D1 | 50 | 1850 | 2013-03-24 16:35 | 2013-03-24 19:55 | 410 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 3 | 3.3333 | 0.71017 | 342.3033 | 102.691 | 103
MC4 | D1 | 51 | 8551 | 2013-03-24 19:55 | 2013-03-24 22:03 | 390 | 521 | 482 | Electrostatic precipitator field out of service | F400Particulate Matter Issue | Mill Creek | Derate | Coal | 3 | 2013 | 3 | 2.1333 | 0.5364 | 258.5469 | 121.1939 | 121
MC4 | U1 | 52 | 4730 | 2013-03-24 22:03 | 2013-03-25 08:54 | 0 | 521 | 482 | Generator current and potential transformers | F430Generator Lock-Out: Broken Wire on Current Transformer | Mill Creek | Outage | Coal | 3 | 2013 | 3 | 10.85 | 10.85 | 5229.7 | 482 | 482
MC4 | NC | 53 | 1850 | 2013-03-25 08:54 | 2013-03-25 17:00 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 3 | 8.1 | 8.1 | 3904.2 | 482 | 482
MC4 | D1 | 54 | 1850 | 2013-03-25 17:00 | 2013-03-26 03:20 | 379 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 3 | 10.3333 | 2.8164 | 1357.4946 | 131.3704 | 131
MC4 | D1 | 55 | 4499 | 2013-04-06 05:30 | 2013-04-06 12:51 | 200 | 521 | 482 | Other miscellaneous steam turbine problems | F780Turbine - Force Cool | Mill Creek | Derate | Coal | 3 | 2013 | 4 | 7.35 | 4.5285 | 2182.7384 | 296.9712 | 297
MC4 | MO | 56 | 4550 | 2013-04-06 12:51 | 2013-04-12 07:21 | 0 | 521 | 482 | Generator bearings and lube oil system (including thrust bearings on hydro units) | F920Generator - #8 Bearing Wiped | Mill Creek | Maintenance | Coal | 3 | 2013 | 4 | 138.5 | 138.5 | 66757 | 482 | 482
MC4 | NC | 57 | 1850 | 2013-04-12 07:21 | 2013-04-13 01:40 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 3 | 2013 | 4 | 18.3167 | 18.3167 | 8828.6333 | 482 | 482
MC4 | D1 | 58 | 4613 | 2013-04-13 01:40 | 2013-04-13 03:57 | 441 | 521 | 482 | Hydrogen seals | F540Generator - Hydrogen Seal Leak | Mill Creek | Derate | Coal | 3 | 2013 | 4 | 2.2833 | 0.35061 | 168.993 | 74.0115 | 74
MC4 | U2 | 59 | 4613 | 2013-04-13 03:57 | 2013-04-17 19:12 | 0 | 521 | 482 | Hydrogen seals | F540Generator - Hydrogen Seal Leak | Mill Creek | Outage | Coal | 3 | 2013 | 4 | 111.25 | 111.25 | 53622.5 | 482 | 482
MC4 | SF | 60 | 4550 | 2013-04-17 19:12 | 2013-04-23 07:20 | 0 | 521 | 482 | Generator bearings and lube oil system (including thrust bearings on hydro units) | F920Generator - #8 Bearing Wiped | Mill Creek | Outage | Coal | 3 | 2013 | 4 | 132.1333 | 132.1333 | 63688.2667 | 482 | 482
MC4 | NC | 61 | 1850 | 2013-04-23 07:20 | 2013-04-23 21:19 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 3 | 2013 | 4 | 13.9833 | 13.9833 | 6739.9667 | 482 | 482
MC4 | U1 | 62 | 4730 | 2013-04-23 21:19 | 2013-04-24 11:23 | 0 | 521 | 482 | Generator current and potential transformers | F430Generator C Phase Current Transformer - Wiring Issue | Mill Creek | Outage | Coal | 3 | 2013 | 4 | 14.0667 | 14.0667 | 6780.1333 | 482 | 482
MC4 | NC | 63 | 1850 | 2013-04-24 11:23 | 2013-04-24 20:00 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 4 | 8.6167 | 8.6167 | 4153.2333 | 482 | 482
MC4 | D1 | 64 | 1850 | 2013-04-24 20:00 | 2013-04-25 00:31 | 400 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 4 | 4.5167 | 1.049 | 505.6066 | 111.9424 | 112
MC4 | D1 | 65 | 1850 | 2013-04-30 19:45 | 2013-04-30 20:40 | 511 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 4 | 0.91667 | 0.017594 | 8.4805 | 9.2514 | 9
MC4 | D1 | 66 | 1850 | 2013-04-30 20:40 | 2013-05-01 05:40 | 450 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 4 | 9 | 1.2265 | 591.167 | 65.6852 | 66
MC4 | D1 | 67 | 1850 | 2013-05-01 05:40 | 2013-05-01 10:06 | 400 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 4.4333 | 1.0296 | 496.2781 | 111.9424 | 112
MC4 | U1 | 68 | 3110 | 2013-05-01 10:06 | 2013-05-02 22:13 | 0 | 521 | 482 | Condenser tube leaks | F540Condenser Tube Leaks | Mill Creek | Outage | Coal | 3 | 2013 | 5 | 36.1167 | 36.1167 | 17408.2333 | 482 | 482
MC4 | NC | 69 | 1850 | 2013-05-02 22:13 | 2013-05-03 07:41 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 5 | 9.4667 | 9.4667 | 4562.9333 | 482 | 482
MC4 | D1 | 70 | 1850 | 2013-05-03 07:41 | 2013-05-03 22:21 | 447 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 14.6667 | 2.0832 | 1004.0896 | 68.4607 | 68
MC4 | D1 | 71 | 1710 | 2013-05-14 18:27 | 2013-05-14 19:11 | 510 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 0.73333 | 0.015483 | 7.4628 | 10.1766 | 10
MC4 | NC | 72 | 1160 | 2013-05-20 | 2013-05-20 04:00 | 0 | 521 | 482 | First reheater B | F320Boiler Deslag - First Reheater | Mill Creek | Other | Coal | 3 | 2013 | 5 | 4 | 4 | 1928 | 482 | 482
MC4 | D4 | 73 | 1160 | 2013-05-20 22:30 | 2013-05-21 03:57 | 300 | 521 | 482 | First reheater B | F320Boiler Deslag - First Reheater4C Coal Mill - Clean Bowl Differential Reference L | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 5.45 | 2.3118 | 1114.2896 | 204.4568 | 204
MC4 | U1 | 74 | 4619 | 2013-05-21 12:17 | 2013-05-23 06:00 | 0 | 521 | 482 | Other hydrogen system problems | F540Generator Hydrogen Leak | Mill Creek | Outage | Coal | 3 | 2013 | 5 | 41.7167 | 41.7167 | 20107.4333 | 482 | 482
MC4 | MO | 75 | 8100 | 2013-05-23 06:00 | 2013-05-23 21:10 | 0 | 521 | 482 | Scrubber/absorber tower or module | F590FGD Module - Cleaning | Mill Creek | Maintenance | Coal | 3 | 2013 | 5 | 15.1667 | 15.1667 | 7310.3333 | 482 | 482
MC4 | NC | 76 | 1850 | 2013-05-23 21:10 | 2013-05-24 04:55 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2013 | 5 | 7.75 | 7.75 | 3735.5 | 482 | 482
MC4 | D1 | 77 | 4619 | 2013-05-24 04:55 | 2013-05-24 08:07 | 400 | 521 | 482 | Other hydrogen system problems | F540Generator Hydrogen Leak - Bushing Box Drain | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 3.2 | 0.74319 | 358.2157 | 111.9424 | 112
MC4 | U2 | 78 | 4619 | 2013-05-24 08:07 | 2013-05-25 05:28 | 0 | 521 | 482 | Other hydrogen system problems | F540Generator Hydrogen Leak - Bushing Box Drain | Mill Creek | Outage | Coal | 3 | 2013 | 5 | 21.35 | 21.35 | 10290.7 | 482 | 482
MC4 | NC | 79 | 1850 | 2013-05-25 05:28 | 2013-05-25 11:23 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 5 | 5.9167 | 5.9167 | 2851.8333 | 482 | 482
MC4 | U1 | 80 | 800 | 2013-05-25 12:07 | 2013-05-25 14:34 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F420Low Drum Level Trip - Operator Error | Mill Creek | Outage | Coal | 3 | 2013 | 5 | 2.45 | 2.45 | 1180.9 | 482 | 482
MC4 | NC | 81 | 1850 | 2013-05-25 14:34 | 2013-05-25 20:34 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 5 | 6 | 6 | 2892 | 482 | 482
MC4 | D1 | 82 | 1850 | 2013-05-25 20:34 | 2013-05-25 21:50 | 400 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 5 | 1.2667 | 0.29418 | 141.7937 | 111.9424 | 112
MC4 | D1 | 83 | 3499 | 2013-06-06 13:42 | 2013-06-07 13:35 | 511 | 521 | 482 | Other feedwater system problems | F520Feedwater Flow - ExcessiveBlowdown Valve - Not Completely Closed | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 23.8833 | 0.45841 | 220.9552 | 9.2514 | 9
MC4 | D1 | 84 | 3499 | 2013-06-07 13:35 | 2013-06-07 14:30 | 500 | 521 | 482 | Other feedwater system problems | F520Feedwater Flow - ExcessiveBlowdown Valve - Not Completely Closed | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 0.91667 | 0.036948 | 17.809 | 19.428 | 19
MC4 | D1 | 85 | 3499 | 2013-06-07 14:30 | 2013-06-11 12:20 | 513 | 521 | 482 | Other feedwater system problems | F520Feedwater Flow - ExcessiveBlowdown Valve - Not Completely Closed | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 93.8333 | 1.4408 | 694.4747 | 7.4012 | 7
MC4 | D4 | 86 | 3412 | 2013-06-14 20:00 | 2013-06-14 20:12 | 170 | 521 | 482 | Feedwater pump drive - steam turbine | F590Turbine Driven Boiler Feed Pump - Replace Suction Relief Valve | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 0.2 | 0.13474 | 64.9451 | 324.7255 | 325
MC4 | U1 | 87 | 800 | 2013-06-14 20:12 | 2013-06-14 22:18 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F420High Drum Level Trip - Operator Error | Mill Creek | Outage | Coal | 3 | 2013 | 6 | 2.1 | 2.1 | 1012.2 | 482 | 482
MC4 | NC | 88 | 1850 | 2013-06-14 22:18 | 2013-06-15 01:00 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 6 | 2.7 | 2.7 | 1301.4 | 482 | 482
MC4 | D4 | 89 | 3412 | 2013-06-15 01:00 | 2013-06-15 07:56 | 125 | 521 | 482 | Feedwater pump drive - steam turbine | F590Turbine Driven Boiler Feed Pump - Replace Suction Relief Valve | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 6.9333 | 5.2699 | 2540.0752 | 366.357 | 366
MC4 | D1 | 90 | 3123 | 2013-06-16 11:09 | 2013-06-16 12:29 | 420 | 521 | 482 | Hot well | F5904C Hotwell Pump Motor - Replace Outboard Bearing Sightglass | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 1.3333 | 0.25848 | 124.5861 | 93.4395 | 93
MC4 | U1 | 91 | 3662 | 2013-06-19 16:06 | 2013-06-19 17:43 | 0 | 521 | 482 | 4160-volt conductors and buses | F8204KV Bus Under Voltage Trip | Mill Creek | Outage | Coal | 3 | 2013 | 6 | 1.6167 | 1.6167 | 779.2333 | 482 | 482
MC4 | NC | 92 | 1850 | 2013-06-19 17:43 | 2013-06-19 20:27 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 6 | 2.7333 | 2.7333 | 1317.4667 | 482 | 482
MC4 | D1 | 93 | 3149 | 2013-06-25 13:32 | 2013-06-25 17:57 | 507 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 4.4167 | 0.11868 | 57.2047 | 12.952 | 13
MC4 | D1 | 94 | 1710 | 2013-06-25 17:57 | 2013-06-27 13:25 | 511 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 43.4667 | 0.83429 | 402.1292 | 9.2514 | 9
MC4 | D1 | 95 | 1710 | 2013-06-27 13:25 | 2013-06-28 22:44 | 504 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 33.3167 | 1.0871 | 523.9861 | 15.7274 | 16
MC4 | D1 | 96 | 260 | 2013-06-28 07:50 | 2013-06-28 08:13 | 325 | 521 | 482 | Primary air fan | F4004B & 4C Coal Feeders Trip - Low PA Flow | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 0.38333 | 0.14421 | 69.5091 | 181.3282 | 181
MC4 | MO | 97 | 1000 | 2013-06-28 22:44 | 2013-06-30 13:49 | 0 | 521 | 482 | Waterwall (Furnace wall) A | F540Boiler Tube Leak - Waterwall | Mill Creek | Maintenance | Coal | 3 | 2013 | 6 | 39.0833 | 39.0833 | 18838.1667 | 482 | 482
MC4 | NC | 98 | 1850 | 2013-06-30 13:49 | 2013-06-30 22:30 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 6 | 8.6833 | 8.6833 | 4185.3667 | 482 | 482
MC4 | D1 | 99 | 250 | 2013-06-30 22:30 | 2013-07-01 08:09 | 425 | 521 | 482 | Pulverizer feeders | F5904E Coal Feeder - Replace Load Cell | Mill Creek | Derate | Coal | 3 | 2013 | 6 | 9.65 | 1.7781 | 857.0534 | 88.8138 | 89
MC4 | D1 | 100 | 385 | 2013-07-01 07:20 | 2013-07-01 08:09 | 305 | 521 | 482 | Igniters | F5904D Igniters - Replace Solenoid | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 0.81667 | 0.33858 | 163.1954 | 199.8311 | 200
MC4 | D1 | 101 | 250 | 2013-07-01 08:09 | 2013-07-01 08:33 | 430 | 521 | 482 | Pulverizer feeders | F5904E Coal Feeder - Replace Load Cell | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 0.4 | 0.069866 | 33.6752 | 84.1881 | 84
MC4 | D1 | 102 | 1710 | 2013-07-01 13:59 | 2013-07-02 01:34 | 509 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 11.5833 | 0.26679 | 128.595 | 11.1017 | 11
MC4 | U1 | 103 | 4268 | 2013-07-02 01:34 | 2013-07-02 03:15 | 0 | 521 | 482 | Reheat/intercept valve testing | F790Sudden Load Rejection during Turbine Reheat/Intercept Valve Test | Mill Creek | Outage | Coal | 3 | 2013 | 7 | 1.6833 | 1.6833 | 811.3667 | 482 | 482
MC4 | NC | 104 | 1850 | 2013-07-02 03:15 | 2013-07-02 09:17 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 7 | 6.0333 | 6.0333 | 2908.0667 | 482 | 482
MC4 | D1 | 105 | 1850 | 2013-07-02 09:17 | 2013-07-02 09:33 | 483 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 0.26667 | 0.01945 | 9.3748 | 35.1555 | 35
MC4 | D1 | 106 | 1710 | 2013-07-02 10:06 | 2013-07-02 11:37 | 485 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Feedwater Flow | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 1.5167 | 0.1048 | 50.5129 | 33.3052 | 33
MC4 | D1 | 107 | 1710 | 2013-07-02 11:37 | 2013-07-03 16:06 | 510 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 28.4833 | 0.60138 | 289.863 | 10.1766 | 10
MC4 | U1 | 108 | 4730 | 2013-07-03 16:06 | 2013-07-03 19:56 | 0 | 521 | 482 | Generator current and potential transformers | F430Current Transformer - Wiring Issues | Mill Creek | Outage | Coal | 3 | 2013 | 7 | 3.8333 | 3.8333 | 1847.6667 | 482 | 482
MC4 | NC | 109 | 1850 | 2013-07-03 19:56 | 2013-07-04 00:54 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 7 | 4.9667 | 4.9667 | 2393.9333 | 482 | 482
MC4 | D1 | 110 | 310 | 2013-07-06 07:50 | 2013-07-06 10:57 | 425 | 521 | 482 | Pulverizer mills | F5304C Coal Mill - Inspection, Bowl Seal Leak | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 3.1167 | 0.57428 | 276.8031 | 88.8138 | 89
MC4 | D4 | 111 | 250 | 2013-07-07 22:00 | 2013-07-08 05:27 | 425 | 521 | 482 | Pulverizer feeders | F0904D Coal Feeder - Calibration | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 7.45 | 1.3727 | 661.663 | 88.8138 | 89
MC4 | D1 | 112 | 1710 | 2013-07-08 10:35 | 2013-07-08 22:30 | 509 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 11.9167 | 0.27447 | 132.2956 | 11.1017 | 11
MC4 | D4 | 113 | 250 | 2013-07-08 22:30 | 2013-07-09 03:05 | 425 | 521 | 482 | Pulverizer feeders | F0904A Coal Feeder - Calibration | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 4.5833 | 0.84453 | 407.0633 | 88.8138 | 89
MC4 | D1 | 114 | 1710 | 2013-07-09 09:48 | 2013-07-09 12:12 | 511 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 2.4 | 0.046065 | 22.2035 | 9.2514 | 9
MC4 | D1 | 115 | 3149 | 2013-07-09 12:12 | 2013-07-09 23:00 | 500 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 10.8 | 0.43532 | 209.8226 | 19.428 | 19
MC4 | D4 | 116 | 250 | 2013-07-09 23:00 | 2013-07-10 04:11 | 425 | 521 | 482 | Pulverizer feeders | F0904B Coal Feeder - Calibration | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 5.1833 | 0.95509 | 460.3516 | 88.8138 | 89
MC4 | D1 | 117 | 310 | 2013-07-10 04:11 | 2013-07-10 23:30 | 425 | 521 | 482 | Pulverizer mills | F5904B Coal Mill - Breaker Issue, Racking Mechanism | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 19.3167 | 3.5593 | 1715.5869 | 88.8138 | 89
MC4 | D4 | 118 | 3662 | 2013-07-10 23:30 | 2013-07-11 07:37 | 180 | 521 | 482 | 4160-volt conductors and buses | F5904KV Bus - Section 4B1 Repair | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 8.1167 | 5.3124 | 2560.598 | 315.4741 | 315
MC4 | D1 | 119 | 1710 | 2013-07-11 13:20 | 2013-07-13 16:58 | 505 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 51.6333 | 1.5857 | 764.2923 | 14.8023 | 15
MC4 | D1 | 120 | 1710 | 2013-07-13 16:58 | 2013-07-14 20:40 | 515 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 27.7 | 0.319 | 153.7589 | 5.5509 | 6
MC4 | D1 | 121 | 1710 | 2013-07-14 20:40 | 2013-07-16 11:03 | 510 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 38.3833 | 0.8104 | 390.6112 | 10.1766 | 10
MC4 | D4 | 122 | 250 | 2013-07-15 23:00 | 2013-07-16 03:54 | 425 | 521 | 482 | Pulverizer feeders | F0904C Coal Feeder - Calibration | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 4.9 | 0.90288 | 435.1877 | 88.8138 | 89
MC4 | D1 | 123 | 1710 | 2013-07-16 11:03 | 2013-07-18 06:00 | 504 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 42.95 | 1.4014 | 675.4939 | 15.7274 | 16
MC4 | D1 | 124 | 1710 | 2013-07-18 06:00 | 2013-07-18 09:54 | 510 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 3.9 | 0.082342 | 39.6887 | 10.1766 | 10
MC4 | D1 | 125 | 1710 | 2013-07-18 09:54 | 2013-07-19 08:49 | 506 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 22.9167 | 0.65979 | 318.0182 | 13.8772 | 14
MC4 | D1 | 126 | 1710 | 2013-07-19 10:46 | 2013-07-22 20:15 | 512 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 81.4833 | 1.4076 | 678.4543 | 8.3263 | 8
MC4 | D4 | 127 | 260 | 2013-07-22 22:00 | 2013-07-23 03:20 | 425 | 521 | 482 | Primary air fan | F5904E Coal Mill PA Fan - Repair Discharge Damper Linkage | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 5.3333 | 0.98273 | 473.6737 | 88.8138 | 89
MC4 | D1 | 128 | 385 | 2013-07-23 10:15 | 2013-07-23 10:32 | 440 | 521 | 482 | Igniters | F4004E Coal Mill - 4E6 Igniter Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 0.28333 | 0.04405 | 21.2321 | 74.9367 | 75
MC4 | D1 | 129 | 1710 | 2013-07-23 12:40 | 2013-07-28 17:18 | 514 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 7 | 124.6333 | 1.6745 | 807.1264 | 6.476 | 6
MC4 | NC | 130 | 9999 | 2013-08-01 08:35 | 2013-08-01 13:10 | 0 | 521 | 482 | Total unit performance testing (use appropriate codes for individual component testing) | F790Full Load Capability Test | Mill Creek | Other | Coal | 3 | 2013 | 8 | 4.5833 | 4.5833 | 2209.1667 | 482 | 482
MC4 | D1 | 131 | 310 | 2013-08-01 17:05 | 2013-08-02 10:50 | 430 | 521 | 482 | Pulverizer mills | F5904A Coal Mill - Seal Air Line Plugged | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 17.75 | 3.1003 | 1494.3388 | 84.1881 | 84
MC4 | D4 | 132 | 260 | 2013-08-04 19:30 | 2013-08-05 02:48 | 420 | 521 | 482 | Primary air fan | F3204B, D & E Coal Mill Primary Air Fans - Clean Pitot Tubes | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 7.3 | 1.4152 | 682.1086 | 93.4395 | 93
MC4 | D1 | 133 | 260 | 2013-08-05 05:36 | 2013-08-05 14:07 | 430 | 521 | 482 | Primary air fan | F4004A Coal Mill Primary Air Fan - Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 8.5167 | 1.4876 | 717.002 | 84.1881 | 84
MC4 | D1 | 134 | 310 | 2013-08-05 17:34 | 2013-08-08 03:42 | 455 | 521 | 482 | Pulverizer mills | F5904A Coal Mill - Replace Rollers | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 58.1333 | 7.3643 | 3549.5923 | 61.0595 | 61
MC4 | D1 | 135 | 3149 | 2013-08-08 14:44 | 2013-08-08 17:16 | 485 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 2.5333 | 0.17505 | 84.3731 | 33.3052 | 33
MC4 | D1 | 136 | 3149 | 2013-08-08 17:16 | 2013-08-08 20:20 | 505 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 3.0667 | 0.094178 | 45.3937 | 14.8023 | 15
MC4 | D1 | 137 | 1710 | 2013-08-08 20:20 | 2013-08-11 10:56 | 514 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 62.6 | 0.84107 | 405.3981 | 6.476 | 6
MC4 | D1 | 138 | 335 | 2013-08-11 10:56 | 2013-08-11 16:00 | 235 | 521 | 482 | Pulverizer lube oil system | F4904B, D & E Coal Mills - Loss Lube Oil Pumps, 480V Feed to MCC (Motor Control Center | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 5.0667 | 2.7813 | 1340.5953 | 264.5912 | 265
MC4 | D1 | 139 | 1710 | 2013-08-11 16:00 | 2013-08-12 10:23 | 500 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 18.3833 | 0.74098 | 357.1518 | 19.428 | 19
MC4 | D1 | 140 | 1710 | 2013-08-12 10:23 | 2013-08-12 11:33 | 503 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 1.1667 | 0.040307 | 19.428 | 16.6526 | 17
MC4 | D1 | 141 | 3149 | 2013-08-12 11:33 | 2013-08-12 12:23 | 496 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 0.83333 | 0.039987 | 19.2738 | 23.1286 | 23
MC4 | D1 | 142 | 3149 | 2013-08-12 12:23 | 2013-08-12 12:45 | 485 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 0.36667 | 0.025336 | 12.2119 | 33.3052 | 33
MC4 | D1 | 143 | 3149 | 2013-08-12 12:45 | 2013-08-12 17:30 | 482 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 4.75 | 0.35557 | 171.3829 | 36.0806 | 36
MC4 | D1 | 144 | 1710 | 2013-08-12 17:30 | 2013-08-13 12:32 | 502 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 19.0333 | 0.69411 | 334.5629 | 17.5777 | 18
MC4 | D1 | 145 | 1710 | 2013-08-13 12:32 | 2013-08-16 21:12 | 510 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 80.6667 | 1.7031 | 820.9111 | 10.1766 | 10
MC4 | MO | 146 | 8230 | 2013-08-16 21:12 | 2013-08-19 01:45 | 0 | 521 | 482 | Ducting A | F5904B1 FGD Wet-Dry Interface Ductwork Repair | Mill Creek | Maintenance | Coal | 3 | 2013 | 8 | 52.55 | 52.55 | 25329.1 | 482 | 482
MC4 | NC | 147 | 1850 | 2013-08-19 01:45 | 2013-08-19 13:50 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2013 | 8 | 12.0833 | 12.0833 | 5824.1667 | 482 | 482
MC4 | D1 | 148 | 1710 | 2013-08-19 13:50 | 2013-08-19 16:50 | 513 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 3 | 0.046065 | 22.2035 | 7.4012 | 7
MC4 | U1 | 149 | 4609 | 2013-08-20 10:40 | 2013-08-20 13:50 | 0 | 521 | 482 | Other exciter problems | F540Exciter Rectifier - Cooling Water Line Leak | Mill Creek | Outage | Coal | 3 | 2013 | 8 | 3.1667 | 3.1667 | 1526.3333 | 482 | 482
MC4 | NC | 150 | 1850 | 2013-08-20 13:50 | 2013-08-20 19:23 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 8 | 5.55 | 5.55 | 2675.1 | 482 | 482
MC4 | D1 | 151 | 3149 | 2013-08-23 13:50 | 2013-08-23 18:20 | 512 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 4.5 | 0.077735 | 37.4683 | 8.3263 | 8
MC4 | D1 | 152 | 1710 | 2013-08-26 15:50 | 2013-08-26 21:05 | 511 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 5.25 | 0.10077 | 48.5701 | 9.2514 | 9
MC4 | D1 | 153 | 1710 | 2013-08-27 13:46 | 2013-08-29 23:00 | 510 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 57.2333 | 1.2084 | 582.4398 | 10.1766 | 10
MC4 | D4 | 154 | 250 | 2013-08-29 23:00 | 2013-08-30 04:00 | 425 | 521 | 482 | Pulverizer feeders | F5904B Coal Feeder - Replace Cabinet Display Panel | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 5 | 0.92131 | 444.0691 | 88.8138 | 89
MC4 | D1 | 155 | 8590 | 2013-08-30 21:30 | 2013-08-30 22:30 | 425 | 521 | 482 | Other precipitator problems | F4104A Precipitator Power Supply - Lost Feed Breaker | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 1 | 0.18426 | 88.8138 | 88.8138 | 89
MC4 | D1 | 156 | 8590 | 2013-08-30 22:30 | 2013-08-31 06:14 | 330 | 521 | 482 | Other precipitator problems | F4104A Precipitator Power Supply - Lost Feed Breaker | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 7.7333 | 2.8351 | 1366.4993 | 176.7025 | 177
MC4 | D1 | 157 | 8590 | 2013-08-31 06:14 | 2013-08-31 07:20 | 410 | 521 | 482 | Other precipitator problems | F4104A Precipitator Power Supply - Lost Feed Breaker | Mill Creek | Derate | Coal | 3 | 2013 | 8 | 1.1 | 0.23436 | 112.9601 | 102.691 | 103
MC4 | U1 | 158 | 1415 | 2013-09-06 06:28 | 2013-09-06 08:37 | 0 | 521 | 482 | Forced draft fan controls | F820Forced Draft Fans Trip due to Induced Draft Fan Speed Signal Loss | Mill Creek | Outage | Coal | 3 | 2013 | 9 | 2.15 | 2.15 | 1036.3 | 482 | 482
MC4 | NC | 159 | 1850 | 2013-09-06 08:37 | 2013-09-06 17:50 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 9 | 9.2167 | 9.2167 | 4442.4333 | 482 | 482
MC4 | D1 | 160 | 1710 | 2013-09-09 12:08 | 2013-09-10 09:07 | 511 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 20.9833 | 0.40275 | 194.126 | 9.2514 | 9
MC4 | D1 | 161 | 1710 | 2013-09-10 09:07 | 2013-09-10 11:15 | 515 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 2.1333 | 0.024568 | 11.8418 | 5.5509 | 6
MC4 | D1 | 162 | 1710 | 2013-09-10 11:15 | 2013-09-12 13:01 | 508 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 49.7667 | 1.2418 | 598.5373 | 12.0269 | 12
MC4 | D4 | 163 | 310 | 2013-09-17 22:00 | 2013-09-18 02:15 | 425 | 521 | 482 | Pulverizer mills | F5304A Coal Mill - Inspect Wear Plates | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 4.25 | 0.78311 | 377.4587 | 88.8138 | 89
MC4 | D4 | 164 | 310 | 2013-09-18 22:00 | 2013-09-19 03:16 | 435 | 521 | 482 | Pulverizer mills | F5904C Coal Mill - Replace Scraper | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 5.2667 | 0.86935 | 419.0285 | 79.5624 | 80
MC4 | D1 | 165 | 385 | 2013-09-29 06:43 | 2013-09-29 08:32 | 425 | 521 | 482 | Igniters | F5904D Coal Mill - 4D9 Gas Igniter Maintenance | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 1.8167 | 0.33474 | 161.3451 | 88.8138 | 89
MC4 | D1 | 166 | 1488 | 2013-09-30 11:13 | 2013-10-01 | 500 | 521 | 482 | Air heater (regenerative) | F3204B Air Heater - High Differential, Dirty | Mill Creek | Derate | Coal | 3 | 2013 | 9 | 12.7833 | 0.51526 | 248.3549 | 19.428 | 19
MC4 | D1 | 167 | 1488 | 2013-10-01 | 2013-10-07 21:47 | 500 | 521 | 482 | Air heater (regenerative) | F3204B Air Heater - High Differential, Dirty | Mill Creek | Derate | Coal | 3 | 2013 | 10 | 165.7833 | 6.6822 | 3220.8424 | 19.428 | 19
MC4 | MO | 168 | 1488 | 2013-10-07 21:47 | 2013-10-12 00:13 | 0 | 521 | 482 | Air heater (regenerative) | F320Air Heaters - Wash | Mill Creek | Maintenance | Coal | 3 | 2013 | 10 | 98.4333 | 98.4333 | 47444.8667 | 482 | 482
MC4 | NC | 169 | 1850 | 2013-10-12 00:13 | 2013-10-12 19:22 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 3 | 2013 | 10 | 19.15 | 19.15 | 9230.3 | 482 | 482
MC4 | D1 | 170 | 4609 | 2013-10-13 15:58 | 2013-10-13 18:29 | 420 | 521 | 482 | Other exciter problems | F850Turbine Exciter #9 Bearing - Vibration | Mill Creek | Derate | Coal | 3 | 2013 | 10 | 2.5167 | 0.48788 | 235.1562 | 93.4395 | 93
MC4 | D1 | 171 | 4609 | 2013-10-13 18:29 | 2013-10-14 06:00 | 430 | 521 | 482 | Other exciter problems | F850Turbine Exciter #9 Bearing - Vibration | Mill Creek | Derate | Coal | 3 | 2013 | 10 | 11.5167 | 2.0115 | 969.5663 | 84.1881 | 84
MC4 | D1 | 172 | 4609 | 2013-10-14 06:00 | 2013-10-14 08:00 | 300 | 521 | 482 | Other exciter problems | F850Turbine Exciter #9 Bearing - Vibration | Mill Creek | Derate | Coal | 3 | 2013 | 10 | 2 | 0.84837 | 408.9136 | 204.4568 | 204
MC4 | D1 | 173 | 4609 | 2013-10-14 08:00 | 2013-10-14 10:00 | 480 | 521 | 482 | Other exciter problems | F850Turbine Exciter #9 Bearing - Vibration | Mill Creek | Derate | Coal | 3 | 2013 | 10 | 2 | 0.15739 | 75.8618 | 37.9309 | 38
MC4 | D1 | 174 | 1710 | 2013-10-14 10:00 | 2013-10-17 22:16 | 520 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 10 | 84.2667 | 0.16174 | 77.9588 | 0.92514 | 1
MC4 | MO | 175 | 4609 | 2013-10-17 22:16 | 2013-10-18 23:12 | 0 | 521 | 482 | Other exciter problems | F850Turbine Exciter Bearing #9 Vibration - Balance ShotClosed Cooling Water System L | Mill Creek | Maintenance | Coal | 3 | 2013 | 10 | 24.9333 | 24.9333 | 12017.8667 | 482 | 482
MC4 | NC | 176 | 1850 | 2013-10-18 23:12 | 2013-10-19 16:09 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2013 | 10 | 16.95 | 16.95 | 8169.9 | 482 | 482
MC4 | U1 | 177 | 1060 | 2013-11-04 15:59 | 2013-11-09 03:52 | 0 | 521 | 482 | First reheater A | F540Boiler Tube Leak - First Reheater and Main Steam Safety Repairs | Mill Creek | Outage | Coal | 3 | 2013 | 11 | 107.8833 | 107.8833 | 51999.7667 | 482 | 482
MC4 | D1 | 178 | 300 | 2013-11-09 18:00 | 2013-11-09 19:45 | 465 | 521 | 482 | Pulverizer motors and drives | F4904A Coal Mill - Breaker Issues | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 1.75 | 0.1881 | 90.6641 | 51.8081 | 52
MC4 | D1 | 179 | 9620 | 2013-11-11 12:52 | 2013-11-11 17:55 | 410 | 521 | 482 | Particulate stack emissions (fossil) | F320Particulate Matter Alarm | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 5.05 | 1.0759 | 518.5894 | 102.691 | 103
MC4 | D1 | 180 | 9620 | 2013-11-11 17:55 | 2013-11-11 22:25 | 320 | 521 | 482 | Particulate stack emissions (fossil) | F320Particulate Matter Alarm | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 4.5 | 1.7361 | 836.7927 | 185.9539 | 186
MC4 | D1 | 181 | 9620 | 2013-11-11 22:25 | 2013-11-11 22:40 | 420 | 521 | 482 | Particulate stack emissions (fossil) | F320Particulate Matter Alarm | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 0.25 | 0.048464 | 23.3599 | 93.4395 | 93
MC4 | D1 | 182 | 270 | 2013-11-12 01:40 | 2013-11-12 06:49 | 440 | 521 | 482 | Primary air duct and dampers | F5504C Coal Mill PA Fan Damper Loose | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 5.15 | 0.80067 | 385.9238 | 74.9367 | 75
MC4 | D1 | 183 | 380 | 2013-11-12 07:25 | 2013-11-12 08:35 | 440 | 521 | 482 | Light-off (igniter) systems (including fuel supply) | F4004C1 Scanner Issues, not reading | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 1.1667 | 0.18138 | 87.4261 | 74.9367 | 75
MC4 | D1 | 184 | 1710 | 2013-11-13 08:00 | 2013-11-13 09:34 | 517 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Maximum Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 1.5667 | 0.012028 | 5.7976 | 3.7006 | 4
MC4 | D1 | 185 | 385 | 2013-11-15 13:40 | 2013-11-15 13:55 | 420 | 521 | 482 | Igniters | F4004E Coal Mill - Igniter Issue | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 0.25 | 0.048464 | 23.3599 | 93.4395 | 93
MC4 | NC | 186 | 8460 | 2013-11-18 12:00 | 2013-11-18 12:42 | 0 | 521 | 482 | Testing A | F790RATA Testing Full Load | Mill Creek | Other | Coal | 3 | 2013 | 11 | 0.7 | 0.7 | 337.4 | 482 | 482
MC4 | D1 | 187 | 1710 | 2013-11-18 12:42 | 2013-11-19 12:00 | 517 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 23.3 | 0.17889 | 86.2234 | 3.7006 | 4
MC4 | D1 | 188 | 360 | 2013-11-18 20:04 | 2013-11-18 21:05 | 430 | 521 | 482 | Burners | F7804C7 Coal Burner - High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 1.0167 | 0.17758 | 85.5912 | 84.1881 | 84
MC4 | NC | 189 | 8460 | 2013-11-19 07:45 | 2013-11-19 15:40 | 0 | 521 | 482 | Testing A | F790RATA Testing Full Load | Mill Creek | Other | Coal | 3 | 2013 | 11 | 7.9167 | 7.9167 | 3815.8333 | 482 | 482
MC4 | D1 | 190 | 1710 | 2013-11-19 12:00 | 2013-11-19 18:00 | 520 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 6 | 0.011516 | 5.5509 | 0.92514 | 1
MC4 | NC | 191 | 8460 | 2013-11-20 01:00 | 2013-11-20 04:48 | 0 | 521 | 482 | Testing A | F790RATA Testing Mid Load | Mill Creek | Other | Coal | 3 | 2013 | 11 | 3.8 | 3.8 | 1831.6 | 482 | 482
MC4 | NC | 192 | 8460 | 2013-11-20 08:35 | 2013-11-20 15:00 | 0 | 521 | 482 | Testing A | F790RATA Testing - Full Load | Mill Creek | Other | Coal | 3 | 2013 | 11 | 6.4167 | 6.4167 | 3092.8333 | 482 | 482
MC4 | D1 | 193 | 310 | 2013-11-21 18:00 | 2013-11-21 20:00 | 465 | 521 | 482 | Pulverizer mills | F5904A Coal Mill Primary Air Fan - Motor Bearing Low Oil | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 2 | 0.21497 | 103.6161 | 51.8081 | 52
MC4 | D1 | 194 | 1710 | 2013-11-27 08:20 | 2013-11-29 03:50 | 520 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 43.5 | 0.083493 | 40.2438 | 0.92514 | 1
MC4 | D1 | 195 | 1710 | 2013-11-29 03:50 | 2013-12-06 18:48 | 523 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 11 | 182.9667 | -0.70237 | -338.541 | 0 | 0
MC4 | D1 | 196 | 1710 | 2013-12-06 19:25 | 2013-12-07 11:07 | 516 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 15.7 | 0.15067 | 72.6238 | 4.6257 | 5
MC4 | D1 | 197 | 3341 | 2013-12-07 01:52 | 2013-12-07 04:20 | 450 | 521 | 482 | Other LP heater - general | F400Heater 2B Low Pressure Feedwater Heater - High Level | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 2.4667 | 0.33615 | 162.0235 | 65.6852 | 66
MC4 | D1 | 198 | 385 | 2013-12-10 06:07 | 2013-12-10 06:33 | 420 | 521 | 482 | Igniters | F4004A Mill - 4A2 Igniter Issue | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.43333 | 0.084005 | 40.4905 | 93.4395 | 93
MC4 | D1 | 199 | 385 | 2013-12-10 06:33 | 2013-12-10 07:04 | 430 | 521 | 482 | Igniters | F4004A Mill - 4A2 Igniter Issue | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.51667 | 0.090243 | 43.4972 | 84.1881 | 84
MC4 | D4 | 200 | 385 | 2013-12-10 14:05 | 2013-12-10 16:10 | 430 | 521 | 482 | Igniters | F5904A Mill - 4A2 Igniter Replaced Actuator | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 2.0833 | 0.36388 | 175.3919 | 84.1881 | 84
MC4 | D4 | 201 | 3235 | 2013-12-13 22:00 | 2013-12-13 22:40 | 330 | 521 | 482 | Cooling tower booster pump | F3204A Cooling Tower Pump - Backflush | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.66667 | 0.2444 | 117.8017 | 176.7025 | 177
MC4 | D1 | 202 | 3149 | 2013-12-14 10:30 | 2013-12-16 06:43 | 518 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 44.2167 | 0.25461 | 122.7203 | 2.7754 | 3
MC4 | NC | 203 | 1160 | 2013-12-17 00:30 | 2013-12-17 05:22 | 0 | 521 | 482 | First reheater B | F320Boiler Deslag - First Reheater, Overheating Prevention | Mill Creek | Other | Coal | 3 | 2013 | 12 | 4.8667 | 4.8667 | 2345.7333 | 482 | 482
MC4 | D1 | 204 | 3340 | 2013-12-18 17:30 | 2013-12-18 18:15 | 493 | 521 | 482 | LP heater tube leaks | F5402B Low Pressure Feedwater Heater - Leak | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.75 | 0.040307 | 19.428 | 25.904 | 26
MC4 | D1 | 205 | 3340 | 2013-12-18 18:15 | 2013-12-18 20:10 | 340 | 521 | 482 | LP heater tube leaks | F5402B Low Pressure Feedwater Heater - LeakBypassed Heaters 1A,1B, 2A & 2B | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 1.9167 | 0.66587 | 320.9479 | 167.4511 | 167
MC4 | D1 | 206 | 3340 | 2013-12-18 20:10 | 2013-12-19 22:42 | 330 | 521 | 482 | LP heater tube leaks | F540#2B Low Pressure Feedwater Heater - LeakBypassed Heaters 1A,1B, 2A & 2B | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 26.5333 | 9.7272 | 4688.5062 | 176.7025 | 177
MC4 | MO | 207 | 3340 | 2013-12-19 22:42 | 2013-12-23 08:21 | 0 | 521 | 482 | LP heater tube leaks | F590#2B Low Pressure Feedwater Heater - Leak Repairs | Mill Creek | Maintenance | Coal | 3 | 2013 | 12 | 81.65 | 81.65 | 39355.3 | 482 | 482
MC4 | D1 | 208 | 1850 | 2013-12-23 20:30 | 2013-12-23 23:30 | 330 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 3 | 1.0998 | 530.1075 | 176.7025 | 177
MC4 | D1 | 209 | 1850 | 2013-12-23 23:30 | 2013-12-24 09:45 | 460 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 10.25 | 1.2001 | 578.4463 | 56.4338 | 56
MC4 | D1 | 210 | 1710 | 2013-12-24 09:45 | 2013-12-26 10:27 | 522 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issues | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 48.7 | -0.093474 | -45.0545 | 0 | 0
MC4 | D1 | 211 | 3149 | 2013-12-26 10:27 | 2013-12-26 11:03 | 484 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure/Max Steam Flow Issues | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.6 | 0.04261 | 20.5382 | 34.2303 | 34
MC4 | D1 | 212 | 3149 | 2013-12-26 11:03 | 2013-12-26 18:28 | 480 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure/Max Steam Flow Issues | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 7.4167 | 0.58365 | 281.3209 | 37.9309 | 38
MC4 | D1 | 213 | 3235 | 2013-12-26 18:28 | 2013-12-27 23:20 | 425 | 521 | 482 | Cooling tower booster pump | F8504B Cooling Tower Pump Vibrations/High Back Pressure | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 28.8667 | 5.319 | 2563.7589 | 88.8138 | 89
MC4 | D4 | 214 | 3235 | 2013-12-27 23:20 | 2013-12-28 00:57 | 335 | 521 | 482 | Cooling tower booster pump | F5904B Cooling Tower Pump | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 1.6167 | 0.57716 | 278.1908 | 172.0768 | 172
MC4 | D1 | 215 | 1710 | 2013-12-28 00:57 | 2013-12-28 01:03 | 522 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issues | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.1 | -0.00019194 | -0.092514 | 0 | 0
MC4 | U1 | 216 | 4730 | 2013-12-28 01:03 | 2013-12-30 20:50 | 0 | 521 | 482 | Generator current and potential transformers | F430Generator Lock out - Broken Wire on Current Transformer | Mill Creek | Outage | Coal | 3 | 2013 | 12 | 67.7833 | 67.7833 | 32671.5667 | 482 | 482
MC4 | NC | 217 | 1850 | 2013-12-30 20:50 | 2013-12-31 08:55 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2013 | 12 | 12.0833 | 12.0833 | 5824.1667 | 482 | 482
MC4 | D1 | 218 | 95 | 2013-12-31 08:55 | 2013-12-31 15:44 | 430 | 521 | 482 | Bunker flow problems | FW004B Coal Silo - Plugged, Wet Coal | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 6.8167 | 1.1906 | 573.8822 | 84.1881 | 84
MC4 | D1 | 219 | 360 | 2013-12-31 23:30 | 2014-01-01 | 420 | 521 | 482 | Burners | F7804C Mill - 4C7 & 4C9 Burners High Temperature | Mill Creek | Derate | Coal | 3 | 2013 | 12 | 0.5 | 0.096929 | 46.7198 | 93.4395 | 93
MC4 | D1 | 1 | 360 | 2014-01-01 | 2014-01-01 03:30 | 420 | 521 | 482 | Burners | F7804C Mill - 4C7 & 4C9 Burners High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 3.5 | 0.6785 | 327.0384 | 93.4395 | 93
MC4 | D1 | 2 | 4261 | 2014-01-02 11:34 | 2014-01-02 12:11 | 500 | 521 | 482 | Control valves | F400Turbine Control Valves - EHC Issue | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 0.61667 | 0.024856 | 11.9806 | 19.428 | 19
MC4 | D1 | 3 | 380 | 2014-01-06 05:40 | 2014-01-06 05:48 | 255 | 521 | 482 | Light-off (igniter) systems (including fuel supply) | F4004C Mill - Gas Igniter Issue | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 0.13333 | 0.068074 | 32.8118 | 246.0883 | 246
MC4 | D1 | 4 | 380 | 2014-01-06 06:40 | 2014-01-06 08:55 | 340 | 521 | 482 | Light-off (igniter) systems (including fuel supply) | F4004B & 4C Mills - Gas Igniter Issues | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 2.25 | 0.78167 | 376.7649 | 167.4511 | 167
MC4 | D1 | 5 | 380 | 2014-01-06 08:55 | 2014-01-06 12:30 | 420 | 521 | 482 | Light-off (igniter) systems (including fuel supply) | F7204C Mill - Gas Vent Valve Stuck Open | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 3.5833 | 0.69466 | 334.825 | 93.4395 | 93
MC4 | D4 | 6 | 360 | 2014-01-08 21:00 | 2014-01-08 21:55 | 410 | 521 | 482 | Burners | F5304B Mill - Coal Burners Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 0.91667 | 0.1953 | 94.1334 | 102.691 | 103
MC4 | D1 | 7 | 250 | 2014-01-08 21:55 | 2014-01-09 05:00 | 410 | 521 | 482 | Pulverizer feeders | F5904A Coal Feeder - VFD Beck Drive Bad Card | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 7.0833 | 1.5091 | 727.3944 | 102.691 | 103
MC4 | D1 | 8 | 310 | 2014-01-09 07:00 | 2014-01-09 08:38 | 475 | 521 | 482 | Pulverizer mills | F5904A Coal Mill - Breaker Issue | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 1.6333 | 0.14421 | 69.5091 | 42.5566 | 43
MC4 | D1 | 9 | 360 | 2014-01-12 02:48 | 2014-01-12 09:33 | 430 | 521 | 482 | Burners | F0704B Mill - Fire, 4B1 Burner Blanked Off | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 6.75 | 1.179 | 568.2697 | 84.1881 | 84
MC4 | NC | 10 | 1160 | 2014-01-18 21:00 | 2014-01-19 07:41 | 0 | 521 | 482 | First reheater B | F320Boiler Deslag - First Reheater. Full load available if needed. | Mill Creek | Other | Coal | 3 | 2014 | 1 | 10.6833 | 10.6833 | 5149.3667 | 482 | 482
MC4 | NC | 11 | 8825 | 2014-01-22 10:35 | 2014-01-22 20:00 | 0 | 521 | 482 | Other SCR NOx problems | F790SCR Flow Test @ Full Load | Mill Creek | Other | Coal | 3 | 2014 | 1 | 9.4167 | 9.4167 | 4538.8333 | 482 | 482
MC4 | NC | 12 | 8825 | 2014-01-23 08:47 | 2014-01-23 15:10 | 0 | 521 | 482 | Other SCR NOx problems | F790SCR Flow Test @ Full Load | Mill Creek | Other | Coal | 3 | 2014 | 1 | 6.3833 | 6.3833 | 3076.7667 | 482 | 482
MC4 | NC | 13 | 8825 | 2014-01-24 12:20 | 2014-01-24 18:02 | 0 | 521 | 482 | Other SCR NOx problems | F790SCR Flow Test - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 1 | 5.7 | 5.7 | 2747.4 | 482 | 482
MC4 | NC | 14 | 1160 | 2014-01-26 11:35 | 2014-01-27 05:50 | 0 | 521 | 482 | First reheater B | F320Boiler Deslag - First Reheater. Full load available if needed. | Mill Creek | Other | Coal | 3 | 2014 | 1 | 18.25 | 18.25 | 8796.5 | 482 | 482
MC4 | D1 | 15 | 310 | 2014-01-30 02:30 | 2014-01-30 06:55 | 420 | 521 | 482 | Pulverizer mills | F5904E Coal Mill - Primary Air Fan Flow Issues | Mill Creek | Derate | Coal | 3 | 2014 | 1 | 4.4167 | 0.85621 | 412.6913 | 93.4395 | 93
MC4 | D4 | 16 | 310 | 2014-02-02 23:00 | 2014-02-03 03:55 | 420 | 521 | 482 | Pulverizer mills | F5304C Coal Mill - Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 4.9167 | 0.95313 | 459.4111 | 93.4395 | 93
MC4 | D1 | 17 | 360 | 2014-02-03 03:55 | 2014-02-03 06:08 | 330 | 521 | 482 | Burners | F7804B Mill - 4B3 Coal Burner High Temperature4C Coal Mill - Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 2.2167 | 0.81264 | 391.6905 | 176.7025 | 177
MC4 | D1 | 18 | 1710 | 2014-02-04 14:30 | 2014-02-19 06:00 | 518 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issues | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 351.5 | 2.024 | 975.5643 | 2.7754 | 3
MC4 | D1 | 19 | 310 | 2014-02-07 06:50 | 2014-02-07 07:05 | 460 | 521 | 482 | Pulverizer mills | F5904B Coal Mill - Swing Valve & Ignitor Gas Valve Issues | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 0.25 | 0.029271 | 14.1084 | 56.4338 | 56
MC4 | D1 | 20 | 250 | 2014-02-11 09:10 | 2014-02-11 09:20 | 430 | 521 | 482 | Pulverizer feeders | F4004C Coal Feeder - Microprocessor Issue | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 0.16667 | 0.029111 | 14.0313 | 84.1881 | 84
MC4 | NC | 21 | 1160 | 2014-02-12 23:59 | 2014-02-13 04:20 | 0 | 521 | 482 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 3 | 2014 | 2 | 4.35 | 4.35 | 2096.7 | 482 | 482
MC4 | D4 | 22 | 8160 | 2014-02-17 20:00 | 2014-02-18 00:24 | 330 | 521 | 482 | Mist eliminators/demisters and washdown | F590FGD Demister Wash Line - Relocation | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 4.4 | 1.6131 | 777.491 | 176.7025 | 177
MC4 | NC | 23 | 4490 | 2014-02-19 06:00 | 2014-02-19 12:30 | 0 | 521 | 482 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Full Load Capability Test | Mill Creek | Other | Coal | 3 | 2014 | 2 | 6.5 | 6.5 | 3133 | 482 | 482
MC4 | D1 | 24 | 1710 | 2014-02-19 17:42 | 2014-02-21 10:13 | 518 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 40.5167 | 0.2333 | 112.4512 | 2.7754 | 3
MC4 | NC | 25 | 1160 | 2014-02-20 23:00 | 2014-02-21 04:00 | 0 | 521 | 482 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 3 | 2014 | 2 | 5 | 5 | 2410 | 482 | 482
MC4 | D1 | 26 | 1710 | 2014-02-21 10:13 | 2014-03-04 06:41 | 522 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 260.4667 | -0.49994 | -240.9692 | 0 | 0
MC4 | D1 | 27 | 4460 | 2014-02-23 04:00 | 2014-02-23 04:33 | 220 | 521 | 482 | Turbine overspeed trip test | F720Turbine Overspeed Test - Linkage Stuck | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 0.55 | 0.31775 | 153.1576 | 278.4683 | 278
MC4 | D1 | 28 | 1520 | 2014-02-25 08:16 | 2014-02-25 09:00 | 475 | 521 | 482 | Flue gas dampers (except recirculation) | F3404A Economizer Outlet Damper - Failed to Open Completely | Mill Creek | Derate | Coal | 3 | 2014 | 2 | 0.73333 | 0.064747 | 31.2082 | 42.5566 | 43
MC4 | D1 | 29 | 250 | 2014-03-01 19:00 | 2014-03-01 22:35 | 430 | 521 | 482 | Pulverizer feeders | F4304C Coal Feeder - Loose Connection @ Control Board | Mill Creek | Derate | Coal | 3 | 2014 | 3 | 3.5833 | 0.62588 | 301.674 | 84.1881 | 84
MC4 | D1 | 30 | 360 | 2014-03-02 11:41 | 2014-03-02 12:14 | 445 | 521 | 482 | Burners | F7804B Mill - 4B7 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 3 | 0.55 | 0.08023 | 38.671 | 70.3109 | 70
MC4 | D1 | 31 | 1710 | 2014-03-04 08:45 | 2014-03-12 18:14 | 522 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 3 | 201.4833 | -0.38672 | -186.4011 | 0 | 0
MC4 | D1 | 32 | 876 | 2014-03-07 23:20 | 2014-03-08 03:55 | 320 | 521 | 482 | Soot blower controls | F590Sootblower Regulator - Repair Positioner | Mill Creek | Derate | Coal | 3 | 2014 | 3 | 4.5833 | 1.7682 | 852.2889 | 185.9539 | 186
MC4 | D4 | 33 | 8160 | 2014-03-08 23:30 | 2014-03-09 06:36 | 340 | 521 | 482 | Mist eliminators/demisters and washdown | F590FGD Mist Eliminator - Wash Line Tie In | Mill Creek | Derate | Coal | 3 | 2014 | 3 | 7.1 | 2.4666 | 1188.9025 | 167.4511 | 167
MC4 | D1 | 34 | 1710 | 2014-03-13 06:15 | 2014-03-14 23:47 | 522 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 3 | 41.5333 | -0.079718 | -38.4243 | 0 | 0
MC4 | PO | 35 | 1801 | 2014-03-14 23:47 | 2014-03-30 19:15 | 0 | 521 | 482 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Planned 2 Week Outage | Mill Creek | Other | Coal | 3 | 2014 | 3 | 379.4667 | 379.4667 | 182902.9333 | 482 | 482
MC4 | NC | 36 | 1850 | 2014-03-30 19:15 | 2014-03-31 19:30 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 3 | 2014 | 3 | 24.25 | 24.25 | 11688.5 | 482 | 482
MC4 | D1 | 37 | 1850 | 2014-03-31 19:30 | 2014-04-01 03:35 | 335 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 3 | 8.0833 | 2.8858 | 1390.9539 | 172.0768 | 172
MC4 | D1 | 38 | 1850 | 2014-04-01 03:35 | 2014-04-01 12:00 | 392 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 8.4167 | 2.084 | 1004.475 | 119.3436 | 119
MC4 | D1 | 39 | 1850 | 2014-04-01 12:00 | 2014-04-01 19:53 | 472 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 7.8833 | 0.74143 | 357.3677 | 45.3321 | 45
MC4 | D1 | 40 | 1710 | 2014-04-01 19:53 | 2014-04-02 06:10 | 499 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 10.2833 | 0.43423 | 209.2984 | 20.3532 | 20
MC4 | D1 | 41 | 800 | 2014-04-02 08:30 | 2014-04-02 18:11 | 492 | 521 | 482 | Drums and drum internals (single drum only) | F400Low Drum Level | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 9.6833 | 0.539 | 259.7958 | 26.8292 | 27
MC4 | D1 | 42 | 1710 | 2014-04-02 18:11 | 2014-04-02 19:55 | 507 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 1.7333 | 0.046577 | 22.4502 | 12.952 | 13
MC4 | D4 | 43 | 310 | 2014-04-03 21:30 | 2014-04-04 02:54 | 407 | 521 | 482 | Pulverizer mills | F5904E Coal Mill - Pitot Tube Cleaning4C Coal Mill - Air Tap Cleaninng | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 5.4 | 1.1816 | 569.5186 | 105.4664 | 105
MC4 | D1 | 44 | 310 | 2014-04-04 06:00 | 2014-04-04 09:12 | 430 | 521 | 482 | Pulverizer mills | F1204E Coal Mill - Excessive PyritesCooling Tower Chemistry - Brominate | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 3.2 | 0.55893 | 269.4019 | 84.1881 | 84
MC4 | D4 | 45 | 310 | 2014-04-06 21:00 | 2014-04-07 05:34 | 430 | 521 | 482 | Pulverizer mills | F5904E Coal Mill - Clean Pitot Tubes | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 8.5667 | 1.4963 | 721.2114 | 84.1881 | 84
MC4 | D4 | 46 | 310 | 2014-04-07 22:20 | 2014-04-08 04:00 | 430 | 521 | 482 | Pulverizer mills | F5304B Coal Mill - Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 5.6667 | 0.98976 | 477.0659 | 84.1881 | 84
MC4 | D1 | 47 | 310 | 2014-04-08 04:00 | 2014-04-08 05:45 | 430 | 521 | 482 | Pulverizer mills | F5904B Coal Mill - Replace Pyrite Scrapper | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 1.75 | 0.30566 | 147.3292 | 84.1881 | 84
MC4 | D1 | 48 | 310 | 2014-04-08 05:45 | 2014-04-08 07:15 | 485 | 521 | 482 | Pulverizer mills | F5904B Coal Mill - Replace Pyrite Scrapper (Gas Guns In) | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 1.5 | 0.10365 | 49.9578 | 33.3052 | 33
MC4 | NC | 49 | 9620 | 2014-04-08 08:30 | 2014-04-08 13:31 | 0 | 521 | 482 | Particulate stack emissions (fossil) | F790Particulate Matter Testing - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 4 | 5.0167 | 5.0167 | 2418.0333 | 482 | 482
MC4 | NC | 50 | 9620 | 2014-04-09 07:20 | 2014-04-09 10:53 | 0 | 521 | 482 | Particulate stack emissions (fossil) | F790Particulate Matter Testing - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 4 | 3.55 | 3.55 | 1711.1 | 482 | 482
MC4 | D4 | 51 | 1160 | 2014-04-09 21:47 | 2014-04-10 03:51 | 300 | 521 | 482 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 6.0667 | 2.5734 | 1240.3713 | 204.4568 | 204
MC4 | NC | 52 | 9620 | 2014-04-10 06:30 | 2014-04-10 06:58 | 0 | 521 | 482 | Particulate stack emissions (fossil) | F790Particulate Matter Testing - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 4 | 0.46667 | 0.46667 | 224.9333 | 482 | 482
MC4 | D4 | 53 | 1160 | 2014-04-10 22:00 | 2014-04-11 03:30 | 300 | 521 | 482 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 5.5 | 2.333 | 1124.5125 | 204.4568 | 204
MC4 | NC | 54 | 9620 | 2014-04-11 07:00 | 2014-04-11 12:39 | 0 | 521 | 482 | Particulate stack emissions (fossil) | F790Particulate Matter Testing - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 4 | 5.65 | 5.65 | 2723.3 | 482 | 482
MC4 | D1 | 55 | 310 | 2014-04-11 12:39 | 2014-04-11 15:52 | 450 | 521 | 482 | Pulverizer mills | F5904A Coal Mill - Repair A5 Conduit Coal Sample Port | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 3.2167 | 0.43836 | 211.2875 | 65.6852 | 66
MC4 | NC | 56 | 9620 | 2014-04-11 15:52 | 2014-04-11 16:14 | 0 | 521 | 482 | Particulate stack emissions (fossil) | F790Particulate Matter Testing - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 4 | 0.36667 | 0.36667 | 176.7333 | 482 | 482
MC4 | D4 | 57 | 1160 | 2014-04-11 22:25 | 2014-04-12 04:15 | 300 | 521 | 482 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 5.8333 | 2.4744 | 1192.6647 | 204.4568 | 204
MC4 | D1 | 58 | 4309 | 2014-04-12 15:36 | 2014-04-12 17:30 | 365 | 521 | 482 | Other turbine instrument and control problems | F400Turbine EHC Control Issue - Primary Air Fan Flow | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 1.9 | 0.56891 | 274.2127 | 144.3225 | 144
MC4 | D4 | 59 | 1160 | 2014-04-12 21:15 | 2014-04-13 04:00 | 325 | 521 | 482 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 6.75 | 2.5393 | 1223.9655 | 181.3282 | 181
MC4 | U1 | 60 | 4309 | 2014-04-13 16:27 | 2014-04-13 18:03 | 0 | 521 | 482 | Other turbine instrument and control problems | F400Turbine EHC Control Issue - Lost All Feeders | Mill Creek | Outage | Coal | 3 | 2014 | 4 | 1.6 | 1.6 | 771.2 | 482 | 482
MC4 | NC | 61 | 1850 | 2014-04-13 18:03 | 2014-04-14 02:20 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2014 | 4 | 8.2833 | 8.2833 | 3992.5667 | 482 | 482
MC4 | D1 | 62 | 1850 | 2014-04-14 02:20 | 2014-04-14 05:19 | 400 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 2.9833 | 0.69287 | 333.9615 | 111.9424 | 112
MC4 | D1 | 63 | 3412 | 2014-04-14 07:30 | 2014-04-14 09:41 | 500 | 521 | 482 | Feedwater pump drive - steam turbine | F400Turbine Driven Boiler Feed Pump - Feed Water Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 2.1833 | 0.088004 | 42.4179 | 19.428 | 19
MC4 | D4 | 64 | 310 | 2014-04-17 22:00 | 2014-04-18 03:25 | 430 | 521 | 482 | Pulverizer mills | F5304C Coal Mill - Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 5.4167 | 0.9461 | 456.0189 | 84.1881 | 84
MC4 | D1 | 65 | 250 | 2014-04-18 09:20 | 2014-04-18 21:30 | 420 | 521 | 482 | Pulverizer feeders | F0904C Coal Feeder - Calibration4C Coal Mill - Classifiers Blade Brackets Correction | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 12.1667 | 2.3586 | 1136.8477 | 93.4395 | 93
MC4 | NC | 66 | 1160 | 2014-04-20 21:25 | 2014-04-21 03:00 | 0 | 521 | 482 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 3 | 2014 | 4 | 5.5833 | 5.5833 | 2691.1667 | 482 | 482
MC4 | D4 | 67 | 350 | 2014-04-21 23:00 | 2014-04-22 00:23 | 420 | 521 | 482 | Pulverized fuel and air piping (from pulverizer to wind box) | F5304C Raw Coal Conduit to Mill - Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 1.3833 | 0.26817 | 129.258 | 93.4395 | 93
MC4 | D4 | 68 | 310 | 2014-04-22 22:00 | 2014-04-23 04:00 | 430 | 521 | 482 | Pulverizer mills | F5304C Coal Mill - Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 6 | 1.048 | 505.1286 | 84.1881 | 84
MC4 | D1 | 69 | 310 | 2014-04-23 04:00 | 2014-04-23 10:15 | 430 | 521 | 482 | Pulverizer mills | F1204C Coal Mill - Classifier Plugged | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 6.25 | 1.0917 | 526.1756 | 84.1881 | 84
MC4 | D1 | 70 | 310 | 2014-04-23 10:15 | 2014-04-23 12:20 | 512 | 521 | 482 | Pulverizer mills | F1204C Coal Mill - Classifier Plugged ( Gas In) | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 2.0833 | 0.035988 | 17.3464 | 8.3263 | 8
MC4 | NC | 71 | 1160 | 2014-04-26 22:00 | 2014-04-27 07:30 | 0 | 521 | 482 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 3 | 2014 | 4 | 9.5 | 9.5 | 4579 | 482 | 482
MC4 | D1 | 72 | 3149 | 2014-04-27 14:00 | 2014-04-27 16:00 | 475 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure - Cooling Tower Fan Issues | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 2 | 0.17658 | 85.1132 | 42.5566 | 43
MC4 | D1 | 73 | 3149 | 2014-04-27 16:00 | 2014-04-28 05:53 | 500 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure - Cooling Tower Fan Issues | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 13.8833 | 0.5596 | 269.7257 | 19.428 | 19
MC4 | D1 | 74 | 3149 | 2014-04-28 05:53 | 2014-04-28 08:31 | 510 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure - Cooling Tower Fan Issues | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 2.6333 | 0.055598 | 26.7983 | 10.1766 | 10
MC4 | D1 | 75 | 3149 | 2014-04-28 09:50 | 2014-04-28 13:34 | 495 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure - Cooling Tower Fan Issues | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 3.7333 | 0.18631 | 89.8006 | 24.0537 | 24
MC4 | D4 | 76 | 1160 | 2014-04-28 23:00 | 2014-04-29 05:00 | 330 | 521 | 482 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 6 | 2.1996 | 1060.215 | 176.7025 | 177
MC4 | D4 | 77 | 1160 | 2014-04-29 23:00 | 2014-04-30 01:13 | 325 | 521 | 482 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Derate | Coal | 3 | 2014 | 4 | 2.2167 | 0.83391 | 401.9442 | 181.3282 | 181
MC4 | NC | 78 | 1160 | 2014-04-30 23:00 | 2014-05-01 05:00 | 0 | 521 | 482 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 3 | 2014 | 4 | 6 | 6 | 2892 | 482 | 482
MC4 | NC | 79 | 1160 | 2014-05-01 22:15 | 2014-05-02 04:00 | 0 | 521 | 482 | First reheater B | F320Boiler Deslag - First ReheaterFull Load Available as Needed | Mill Creek | Other | Coal | 3 | 2014 | 5 | 5.75 | 5.75 | 2771.5 | 482 | 482
MC4 | NC | 80 | 1160 | 2014-05-02 22:45 | 2014-05-03 02:39 | 0 | 521 | 482 | First reheater B | F320Boiler Deslag - First Reheater Full Load Available as Needed | Mill Creek | Other | Coal | 3 | 2014 | 5 | 3.9 | 3.9 | 1879.8 | 482 | 482
MC4 | D1 | 81 | 360 | 2014-05-06 14:55 | 2014-05-06 22:00 | 420 | 521 | 482 | Burners | F7804B Mill - 4B6 Coal Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 7.0833 | 1.3732 | 661.8634 | 93.4395 | 93
MC4 | D1 | 82 | 360 | 2014-05-07 06:40 | 2014-05-07 11:10 | 420 | 521 | 482 | Burners | F5904B Mill - 4B6 Coal Burner Install Blank | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 4.5 | 0.87236 | 420.4779 | 93.4395 | 93
MC4 | D1 | 83 | 3149 | 2014-05-12 09:10 | 2014-05-12 17:40 | 500 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 8.5 | 0.34261 | 165.1382 | 19.428 | 19
MC4 | D1 | 84 | 3149 | 2014-05-12 17:40 | 2014-05-12 20:49 | 512 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 3.15 | 0.054415 | 26.2278 | 8.3263 | 8
MC4 | D4 | 85 | 310 | 2014-05-12 22:28 | 2014-05-13 03:58 | 420 | 521 | 482 | Pulverizer mills | F5904A Coal Mill - Clean Pitot Tubes & Repair Swing Valves | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 5.5 | 1.0662 | 513.9175 | 93.4395 | 93
MC4 | D1 | 86 | 3149 | 2014-05-13 12:30 | 2014-05-14 06:15 | 510 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 17.75 | 0.37476 | 180.6344 | 10.1766 | 10
MC4 | D4 | 87 | 300 | 2014-05-13 22:11 | 2014-05-14 00:01 | 425 | 521 | 482 | Pulverizer motors and drives | F5904B Coal Mill Motor Stator Temperature - RTD Change Out | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 1.8333 | 0.33781 | 162.8253 | 88.8138 | 89
MC4 | D4 | 88 | 3412 | 2014-05-14 23:38 | 2014-05-15 08:18 | 140 | 521 | 482 | Feedwater pump drive - steam turbine | F590Turbine Driven Boiler Feed Pump - Replace Suction Safety | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 8.6667 | 6.3378 | 3054.8253 | 352.4798 | 352
MC4 | D1 | 89 | 1710 | 2014-05-20 14:25 | 2014-05-22 08:21 | 510 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 41.9333 | 0.88535 | 426.7381 | 10.1766 | 10
MC4 | D1 | 90 | 3149 | 2014-05-21 13:33 | 2014-05-21 21:18 | 495 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 7.75 | 0.38676 | 186.4165 | 24.0537 | 24
MC4 | D1 | 91 | 1710 | 2014-05-22 08:21 | 2014-05-22 08:43 | 513 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 0.36667 | 0.0056302 | 2.7138 | 7.4012 | 7
MC4 | D1 | 92 | 3149 | 2014-05-22 13:34 | 2014-05-23 05:56 | 508 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 16.3667 | 0.40838 | 196.8398 | 12.0269 | 12
MC4 | D1 | 93 | 250 | 2014-05-23 05:56 | 2014-05-23 06:20 | 460 | 521 | 482 | Pulverizer feeders | F1204B Coal Feeder - Plugged Foreign Material | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 0.4 | 0.046833 | 22.5735 | 56.4338 | 56
MC4 | D1 | 94 | 250 | 2014-05-23 06:20 | 2014-05-23 07:52 | 440 | 521 | 482 | Pulverizer feeders | F1204B Coal Feeder - Plugged Foreign Material | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 1.5333 | 0.23839 | 114.9029 | 74.9367 | 75
MC4 | D1 | 95 | 3149 | 2014-05-26 16:45 | 2014-05-27 22:30 | 495 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 29.75 | 1.4846 | 715.5988 | 24.0537 | 24
MC4 | D1 | 96 | 1710 | 2014-05-27 08:35 | 2014-05-27 12:07 | 510 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issues | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 3.5333 | 0.0746 | 35.9573 | 10.1766 | 10
MC4 | D1 | 97 | 3149 | 2014-05-27 12:07 | 2014-05-27 17:09 | 495 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 5.0333 | 0.25118 | 121.0705 | 24.0537 | 24
MC4 | D1 | 98 | 3149 | 2014-05-27 17:09 | 2014-05-27 18:21 | 510 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 1.2 | 0.025336 | 12.2119 | 10.1766 | 10
MC4 | D1 | 99 | 3149 | 2014-05-27 18:21 | 2014-05-27 21:26 | 495 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 3.0833 | 0.15387 | 74.1657 | 24.0537 | 24
MC4 | D1 | 100 | 1710 | 2014-05-27 21:26 | 2014-05-28 11:39 | 510 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issues | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 14.2167 | 0.30016 | 144.6771 | 10.1766 | 10
MC4 | D1 | 101 | 3149 | 2014-05-28 11:39 | 2014-05-28 15:03 | 495 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 3.4 | 0.16967 | 81.7827 | 24.0537 | 24
MC4 | D1 | 102 | 3149 | 2014-05-28 15:03 | 2014-05-28 15:53 | 502 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 0.83333 | 0.03039 | 14.6481 | 17.5777 | 18
MC4 | D1 | 103 | 3149 | 2014-05-28 15:53 | 2014-05-28 17:01 | 492 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 1.1333 | 0.063084 | 30.4064 | 26.8292 | 27
MC4 | D1 | 104 | 3149 | 2014-05-28 17:01 | 2014-05-29 07:29 | 473 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 14.4667 | 1.3328 | 642.42 | 44.4069 | 44
MC4 | D1 | 105 | 1710 | 2014-05-29 07:29 | 2014-05-29 13:18 | 515 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 5.8167 | 0.066987 | 32.2875 | 5.5509 | 6
MC4 | D1 | 106 | 3149 | 2014-05-29 13:18 | 2014-05-29 15:54 | 505 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 2.6 | 0.079846 | 38.486 | 14.8023 | 15
MC4 | D1 | 107 | 3149 | 2014-05-29 15:54 | 2014-05-30 08:27 | 492 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 16.55 | 0.92121 | 444.0228 | 26.8292 | 27
MC4 | D1 | 108 | 1710 | 2014-05-30 08:27 | 2014-05-30 09:39 | 506 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 1.2 | 0.034549 | 16.6526 | 13.8772 | 14
MC4 | D1 | 109 | 3149 | 2014-05-30 09:39 | 2014-05-30 14:50 | 495 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 5.1833 | 0.25867 | 124.6786 | 24.0537 | 24
MC4 | D1 | 110 | 3149 | 2014-05-30 14:50 | 2014-05-30 15:09 | 490 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 0.31667 | 0.018842 | 9.0818 | 28.6795 | 29
MC4 | D1 | 111 | 310 | 2014-05-30 15:09 | 2014-05-30 17:40 | 420 | 521 | 482 | Pulverizer mills | F5904A Coal Mill - Bowl Differential Transmitter Repair | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 2.5167 | 0.48788 | 235.1562 | 93.4395 | 93
MC4 | D1 | 112 | 3149 | 2014-05-30 17:40 | 2014-05-30 22:56 | 495 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 5 | 5.2667 | 0.26283 | 126.683 | 24.0537 | 24
MC4 | MO | 113 | 3113 | 2014-05-30 22:56 | 2014-06-01 12:39 | 0 | 521 | 482 | Condenser tube and water box cleaning (including circulating water flow reversal) | F320Condenser - Clean Water Box Tubesheets | Mill Creek | Maintenance | Coal | 3 | 2014 | 5 | 37.7167 | 37.7167 | 18179.4333 | 482 | 482
MC4 | ME | 114 | 1040 | 2014-06-01 12:39 | 2014-06-02 08:03 | 0 | 521 | 482 | First superheater B | F540Boiler Tube Leak - First Superheater | Mill Creek | Maintenance | Coal | 3 | 2014 | 6 | 19.4 | 19.4 | 9350.8 | 482 | 482
MC4 | NC | 115 | 1850 | 2014-06-02 08:03 | 2014-06-02 20:10 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2014 | 6 | 12.1167 | 12.1167 | 5840.2333 | 482 | 482
MC4 | D1 | 116 | 1850 | 2014-06-02 20:10 | 2014-06-03 01:49 | 455 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 5.65 | 0.71574 | 344.9862 | 61.0595 | 61
MC4 | D1 | 117 | 1850 | 2014-06-03 01:49 | 2014-06-03 02:31 | 485 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 0.7 | 0.048369 | 23.3136 | 33.3052 | 33
MC4 | D1 | 118 | 1710 | 2014-06-03 12:46 | 2014-06-05 13:16 | 501 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 48.5 | 1.8618 | 897.3896 | 18.5029 | 19
MC4 | D1 | 119 | 1710 | 2014-06-05 13:16 | 2014-06-08 03:25 | 510 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 62.15 | 1.3122 | 632.4747 | 10.1766 | 10
MC4 | U1 | 120 | 1060 | 2014-06-08 03:25 | 2014-06-09 16:15 | 0 | 521 | 482 | First reheater A | F540Boiler Tube Leak - First Reheater | Mill Creek | Outage | Coal | 3 | 2014 | 6 | 36.8333 | 36.8333 | 17753.6667 | 482 | 482
MC4 | MO | 121 | 360 | 2014-06-09 16:15 | 2014-06-10 18:26 | 0 | 521 | 482 | Burners | F530Burner Inspection/Maintenance | Mill Creek | Maintenance | Coal | 3 | 2014 | 6 | 26.1833 | 26.1833 | 12620.3667 | 482 | 482
MC4 | D1 | 122 | 1850 | 2014-06-11 06:35 | 2014-06-11 07:09 | 482 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 0.56667 | 0.042418 | 20.4457 | 36.0806 | 36
MC4 | D4 | 123 | 8125 | 2014-06-11 22:00 | 2014-06-11 23:41 | 380 | 521 | 482 | Scrubber recycle (liquid) pumps | F590FGD Maintenance - Attempt to Install blank in 4A1 Recycle Pump | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 1.6833 | 0.45557 | 219.5829 | 130.4453 | 130
MC4 | D4 | 124 | 1710 | 2014-06-12 11:00 | 2014-06-12 12:20 | 500 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issues | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 1.3333 | 0.053743 | 25.904 | 19.428 | 19
MC4 | D1 | 125 | 800 | 2014-06-12 12:20 | 2014-06-12 13:07 | 415 | 521 | 482 | Drums and drum internals (single drum only) | F660Boiler Pressure Swing | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 0.78333 | 0.15937 | 76.8178 | 98.0653 | 98
MC4 | D1 | 126 | 800 | 2014-06-12 13:07 | 2014-06-12 15:22 | 465 | 521 | 482 | Drums and drum internals (single drum only) | F660Boiler Pressure Swing | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 2.25 | 0.24184 | 116.5681 | 51.8081 | 52
MC4 | D1 | 127 | 800 | 2014-06-12 15:22 | 2014-06-12 17:30 | 490 | 521 | 482 | Drums and drum internals (single drum only) | F660Boiler Pressure Swing | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 2.1333 | 0.12694 | 61.1829 | 28.6795 | 29
MC4 | D1 | 128 | 1710 | 2014-06-12 17:30 | 2014-06-12 22:23 | 500 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issues | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 4.8833 | 0.19683 | 94.8735 | 19.428 | 19
MC4 | D4 | 129 | 260 | 2014-06-12 22:23 | 2014-06-13 04:15 | 430 | 521 | 482 | Primary air fan | F5304E Coal Mill - PA Fan Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 5.8667 | 1.0247 | 493.9035 | 84.1881 | 84
MC4 | D1 | 130 | 1710 | 2014-06-13 04:15 | 2014-06-19 11:00 | 500 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 150.75 | 6.0763 | 2928.7745 | 19.428 | 19
MC4 | D4 | 131 | 8125 | 2014-06-15 22:00 | 2014-06-16 03:08 | 380 | 521 | 482 | Scrubber recycle (liquid) pumps | F130FGD 4A1 Recycle Pump - Installed Blank | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 5.1333 | 1.3893 | 669.6192 | 130.4453 | 130
MC4 | D4 | 132 | 8125 | 2014-06-17 23:00 | 2014-06-18 03:05 | 380 | 521 | 482 | Scrubber recycle (liquid) pumps | F130FGD 4A1 Recycle Pump - Adjusted Blank | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 4.0833 | 1.1051 | 532.6516 | 130.4453 | 130
MC4 | D4 | 133 | 8125 | 2014-06-18 23:00 | 2014-06-19 05:29 | 380 | 521 | 482 | Scrubber recycle (liquid) pumps | F130FGD 4A1 Recycle Pump - Relocated Blank | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 6.4833 | 1.7546 | 845.7203 | 130.4453 | 130
MC4 | D1 | 134 | 1710 | 2014-06-19 11:00 | 2014-06-22 22:00 | 505 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 83 | 2.5489 | 1228.5912 | 14.8023 | 15
MC4 | D4 | 135 | 310 | 2014-06-22 22:00 | 2014-06-23 04:35 | 472 | 521 | 482 | Pulverizer mills | F5304A Coal Mill - Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 6.5833 | 0.61916 | 298.436 | 45.3321 | 45
MC4 | D1 | 136 | 1710 | 2014-06-23 04:35 | 2014-06-30 13:09 | 505 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 176.5667 | 5.4224 | 2613.5933 | 14.8023 | 15
MC4 | D1 | 137 | 310 | 2014-06-23 08:40 | 2014-06-23 09:07 | 420 | 521 | 482 | Pulverizer mills | F5904A Coal Mill - Swing Valve Issue | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 0.45 | 0.087236 | 42.0478 | 93.4395 | 93
MC4 | D1 | 138 | 3341 | 2014-06-26 15:10 | 2014-06-26 16:44 | 480 | 521 | 482 | Other LP heater - general | F130Feedwater Heaters #1 thru #4 - Bypassed | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 1.5667 | 0.12329 | 59.4251 | 37.9309 | 38
MC4 | D1 | 139 | 3341 | 2014-06-27 10:10 | 2014-06-27 11:46 | 480 | 521 | 482 | Other LP heater - general | F130Feedwater Heaters #1 thru 4 - Bypassed | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 1.6 | 0.12591 | 60.6894 | 37.9309 | 38
MC4 | D1 | 140 | 3149 | 2014-06-30 13:09 | 2014-07-01 07:21 | 500 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 6 | 18.2 | 0.73359 | 353.59 | 19.428 | 19
MC4 | D1 | 141 | 1710 | 2014-07-01 07:21 | 2014-07-01 08:11 | 510 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 0.83333 | 0.017594 | 8.4805 | 10.1766 | 10
MC4 | D1 | 142 | 3149 | 2014-07-01 08:11 | 2014-07-01 13:43 | 505 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 5.5333 | 0.16993 | 81.9061 | 14.8023 | 15
MC4 | D1 | 143 | 3149 | 2014-07-01 13:43 | 2014-07-01 22:00 | 495 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 8.2833 | 0.41337 | 199.2452 | 24.0537 | 24
MC4 | D4 | 144 | 250 | 2014-07-01 22:00 | 2014-07-02 05:00 | 430 | 521 | 482 | Pulverizer feeders | F0904E Coal Feeder - Calibration & Primary Air Fan Damper Repair | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 7 | 1.2226 | 589.3167 | 84.1881 | 84
MC4 | D1 | 145 | 1710 | 2014-07-02 05:00 | 2014-07-02 10:30 | 500 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 5.5 | 0.22169 | 106.8541 | 19.428 | 19
MC4 | D1 | 146 | 1710 | 2014-07-02 10:30 | 2014-07-06 12:28 | 505 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 97.9667 | 3.0086 | 1450.1323 | 14.8023 | 15
MC4 | D1 | 147 | 360 | 2014-07-06 12:28 | 2014-07-06 13:17 | 420 | 521 | 482 | Burners | F7804B4 Burner Tip - High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 0.81667 | 0.15832 | 76.309 | 93.4395 | 93
MC4 | D1 | 148 | 1710 | 2014-07-06 13:17 | 2014-07-10 08:30 | 505 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 91.2167 | 2.8013 | 1350.2168 | 14.8023 | 15
MC4 | D1 | 149 | 270 | 2014-07-10 08:30 | 2014-07-10 11:16 | 420 | 521 | 482 | Primary air duct and dampers | F7204C PA Fan - Hot Air Damper not operating | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 2.7667 | 0.53634 | 258.5161 | 93.4395 | 93
MC4 | D1 | 150 | 1710 | 2014-07-10 11:16 | 2014-07-10 18:27 | 505 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issues | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 7.1833 | 0.2206 | 106.3299 | 14.8023 | 15
MC4 | D1 | 151 | 3341 | 2014-07-10 18:27 | 2014-07-10 23:57 | 300 | 521 | 482 | Other LP heater - general | F660LP Heater 1&2A and 1&2B Bypassed - High Level | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 5.5 | 2.333 | 1124.5125 | 204.4568 | 204
MC4 | D1 | 152 | 3341 | 2014-07-10 23:57 | 2014-07-11 04:13 | 390 | 521 | 482 | Other LP heater - general | F660LP Heater 1&2A and 1&2B Bypassed - High Level | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 4.2667 | 1.0728 | 517.0938 | 121.1939 | 121
MC4 | D1 | 153 | 3341 | 2014-07-11 04:13 | 2014-07-11 07:00 | 360 | 521 | 482 | Other LP heater - general | F660LP Heater 1&2A and 1&2B Bypassed - High Level | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 2.7833 | 0.86011 | 414.5724 | 148.9482 | 149
MC4 | D1 | 154 | 3341 | 2014-07-11 07:00 | 2014-07-11 08:54 | 375 | 521 | 482 | Other LP heater - general | F660LP Heater 1&2A and 1&2B Bypassed - High Level | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 1.9 | 0.53244 | 256.6349 | 135.071 | 135
MC4 | D1 | 155 | 3341 | 2014-07-11 08:54 | 2014-07-11 09:25 | 495 | 521 | 482 | Other LP heater - general | F660LP Heater 1&2A and 1&2B Bypassed - High Level | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 0.51667 | 0.025784 | 12.4278 | 24.0537 | 24
MC4 | D1 | 156 | 1710 | 2014-07-12 09:25 | 2014-07-12 11:27 | 505 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issues | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 2.0333 | 0.062444 | 30.098 | 14.8023 | 15
MC4 | D1 | 157 | 1710 | 2014-07-12 11:27 | 2014-07-12 18:08 | 500 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issues | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 6.6833 | 0.26939 | 129.844 | 19.428 | 19
MC4 | D1 | 158 | 3149 | 2014-07-12 18:08 | 2014-07-12 20:10 | 490 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 2.0333 | 0.12099 | 58.3149 | 28.6795 | 29
MC4 | D1 | 159 | 3149 | 2014-07-12 20:10 | 2014-07-12 22:50 | 480 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 2.6667 | 0.20985 | 101.1491 | 37.9309 | 38
MC4 | D1 | 160 | 3149 | 2014-07-12 22:50 | 2014-07-13 09:03 | 495 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 10.2167 | 0.50985 | 245.7491 | 24.0537 | 24
MC4 | D1 | 161 | 3149 | 2014-07-13 09:03 | 2014-07-13 10:20 | 490 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 1.2833 | 0.07636 | 36.8053 | 28.6795 | 29
MC4 | D1 | 162 | 3149 | 2014-07-13 10:20 | 2014-07-13 10:54 | 480 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 0.56667 | 0.044594 | 21.4942 | 37.9309 | 38
MC4 | D1 | 163 | 3149 | 2014-07-13 10:54 | 2014-07-14 11:43 | 470 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 24.8167 | 2.4293 | 1170.9084 | 47.1823 | 47
MC4 | D1 | 164 | 3149 | 2014-07-14 11:43 | 2014-07-14 13:42 | 490 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 1.9833 | 0.11801 | 56.8809 | 28.6795 | 29
MC4 | D1 | 165 | 3149 | 2014-07-14 13:42 | 2014-07-14 23:25 | 480 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 9.7167 | 0.76465 | 368.5619 | 37.9309 | 38
MC4 | MO | 166 | 3340 | 2014-07-14 23:25 | 2014-07-17 20:55 | 0 | 521 | 482 | LP heater tube leaks | F540LP Heater 2A Leak Repair | Mill Creek | Maintenance | Coal | 3 | 2014 | 7 | 69.5 | 69.5 | 33499 | 482 | 482
MC4 | U1 | 167 | 800 | 2014-07-17 21:56 | 2014-07-17 23:26 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F420Low Drum Level | Mill Creek | Outage | Coal | 3 | 2014 | 7 | 1.5 | 1.5 | 723 | 482 | 482
MC4 | D1 | 168 | 4261 | 2014-07-18 05:48 | 2014-07-18 06:11 | 155 | 521 | 482 | Control valves | F400#2 Turbine Control Valve - Turbine EHC system | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 0.38333 | 0.26929 | 129.7977 | 338.6027 | 339
MC4 | D1 | 169 | 1850 | 2014-07-18 10:26 | 2014-07-18 14:10 | 382 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 3.7333 | 0.99603 | 480.088 | 128.595 | 129
MC4 | D1 | 170 | 1850 | 2014-07-18 14:10 | 2014-07-18 16:05 | 490 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 1.9167 | 0.11404 | 54.969 | 28.6795 | 29
MC4 | D1 | 171 | 1710 | 2014-07-18 16:05 | 2014-07-19 13:34 | 498 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 21.4833 | 0.9484 | 457.129 | 21.2783 | 21
MC4 | D1 | 172 | 1710 | 2014-07-19 13:34 | 2014-07-25 01:43 | 502 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 132.15 | 4.8193 | 2322.8977 | 17.5777 | 18
MC4 | D1 | 173 | 3149 | 2014-07-22 19:09 | 2014-07-22 22:15 | 490 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 3.1 | 0.18445 | 88.9063 | 28.6795 | 29
MC4 | D4 | 174 | 310 | 2014-07-22 23:53 | 2014-07-23 03:09 | 425 | 521 | 482 | Pulverizer mills | F5904E Coal Mill - Clean Pitot Tubes | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 3.2667 | 0.60192 | 290.1251 | 88.8138 | 89
MC4 | U1 | 175 | 1000 | 2014-07-25 01:43 | 2014-07-27 17:10 | 0 | 521 | 482 | Waterwall (Furnace wall) A | F540Boiler Tube Leak - Lower Slope Waterwall | Mill Creek | Outage | Coal | 3 | 2014 | 7 | 63.45 | 63.45 | 30582.9 | 482 | 482
MC4 | NC | 176 | 1850 | 2014-07-27 17:10 | 2014-07-27 17:30 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2014 | 7 | 0.33333 | 0.33333 | 160.6667 | 482 | 482
MC4 | U1 | 177 | 800 | 2014-07-27 17:30 | 2014-07-27 19:10 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820Low Drum Level Trip - Boiler Feed Pump Low Pressure Steam Supply Check Valve Stuck | Mill Creek | Outage | Coal | 3 | 2014 | 7 | 1.6667 | 1.6667 | 803.3333 | 482 | 482
MC4 | NC | 178 | 1850 | 2014-07-27 19:10 | 2014-07-28 03:04 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2014 | 7 | 7.9 | 7.9 | 3807.8 | 482 | 482
MC4 | U1 | 179 | 800 | 2014-07-28 03:04 | 2014-07-28 05:13 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F400Low Drum Level Trip | Mill Creek | Outage | Coal | 3 | 2014 | 7 | 2.15 | 2.15 | 1036.3 | 482 | 482
MC4 | NC | 180 | 1850 | 2014-07-28 05:13 | 2014-07-28 11:13 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2014 | 7 | 6 | 6 | 2892 | 482 | 482
MC4 | D1 | 181 | 1850 | 2014-07-28 11:13 | 2014-07-28 15:15 | 370 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 4.0333 | 1.169 | 563.4435 | 139.6967 | 140
MC4 | D1 | 182 | 1850 | 2014-07-28 15:15 | 2014-07-28 20:38 | 485 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 5.3833 | 0.37198 | 179.2929 | 33.3052 | 33
MC4 | D1 | 183 | 1710 | 2014-07-28 20:38 | 2014-07-29 02:24 | 498 | 521 | 482 | Combustion/steam condition controls (report local controls --- burners | F400Max Steam Flow Issue | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 5.7667 | 0.25457 | 122.7049 | 21.2783 | 21
MC4 | U1 | 184 | 1060 | 2014-07-29 02:24 | 2014-07-31 09:57 | 0 | 521 | 482 | First reheater A | F540Boiler Tube Leak - First Reheater | Mill Creek | Outage | Coal | 3 | 2014 | 7 | 55.55 | 55.55 | 26775.1 | 482 | 482
MC4 | NC | 185 | 1850 | 2014-07-31 09:57 | 2014-07-31 10:13 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2014 | 7 | 0.26667 | 0.26667 | 128.5333 | 482 | 482
MC4 | U1 | 186 | 800 | 2014-07-31 10:13 | 2014-07-31 11:37 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820Low Drum Level Trip - Turbine Driven Boiler Feed Pump Issues | Mill Creek | Outage | Coal | 3 | 2014 | 7 | 1.4 | 1.4 | 674.8 | 482 | 482
MC4 | NC | 187 | 1850 | 2014-07-31 11:37 | 2014-07-31 20:45 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2014 | 7 | 9.1333 | 9.1333 | 4402.2667 | 482 | 482
MC4 | D1 | 188 | 250 | 2014-07-31 20:45 | 2014-08-01 01:00 | 420 | 521 | 482 | Pulverizer feeders | F1204B Coal Feeder - Coal Under Belt | Mill Creek | Derate | Coal | 3 | 2014 | 7 | 4.25 | 0.8239 | 397.118 | 93.4395 | 93
MC4 | D1 | 189 | 8125 | 2014-08-01 09:48 | 2014-08-01 22:04 | 495 | 521 | 482 | Scrubber recycle (liquid) pumps | F590SO2 Compliance - 4A1 & 4B2 Recycle Pumps Out of Service | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 12.2667 | 0.61216 | 295.0592 | 24.0537 | 24
MC4 | U1 | 190 | 1060 | 2014-08-01 22:04 | 2014-08-03 07:43 | 0 | 521 | 482 | First reheater A | F540Boiler Tube Leak - First Reheater | Mill Creek | Outage | Coal | 3 | 2014 | 8 | 33.65 | 33.65 | 16219.3 | 482 | 482
MC4 | NC | 191 | 1850 | 2014-08-03 07:43 | 2014-08-03 19:39 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2014 | 8 | 11.9333 | 11.9333 | 5751.8667 | 482 | 482
MC4 | D1 | 192 | 3499 | 2014-08-03 19:39 | 2014-08-03 22:53 | 485 | 521 | 482 | Other feedwater system problems | F150Feedwater Flow Maxed Out | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 3.2333 | 0.22342 | 107.6868 | 33.3052 | 33
MC4 | D1 | 193 | 3499 | 2014-08-03 22:53 | 2014-09-04 10:03 | 496 | 521 | 482 | Other feedwater system problems | F150Feedwater Flow Maxed Out | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 755.1667 | 36.2364 | 17465.9469 | 23.1286 | 23
MC4 | D1 | 194 | 360 | 2014-08-07 16:40 | 2014-08-07 17:35 | 430 | 521 | 482 | Burners | F7804B Coal Mill - 4B4 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 0.91667 | 0.16011 | 77.1724 | 84.1881 | 84
MC4 | D1 | 195 | 310 | 2014-08-08 06:56 | 2014-08-08 09:57 | 430 | 521 | 482 | Pulverizer mills | F5904D Coal Mill - Replace Breaker Housing Switch | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 3.0167 | 0.5269 | 253.9674 | 84.1881 | 84
MC4 | D1 | 196 | 8670 | 2014-08-10 16:58 | 2014-08-10 18:04 | 430 | 521 | 482 | Emission monitors (other than CEMS) A | F320Particulate Matter Limitation - Cleaned Probes | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 1.1 | 0.19213 | 92.6069 | 84.1881 | 84
MC4 | D4 | 197 | 1470 | 2014-08-18 22:00 | 2014-08-19 02:35 | 290 | 521 | 482 | Induced draft fan motors and drives | F5904B Induced Draft Fan - Replace Beck Drive Motor | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 4.5833 | 2.0321 | 979.4962 | 213.7083 | 214
MC4 | D1 | 198 | 3149 | 2014-08-20 14:20 | 2014-08-20 16:58 | 485 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 2.6333 | 0.18196 | 87.7036 | 33.3052 | 33
MC4 | D1 | 199 | 250 | 2014-08-22 08:20 | 2014-08-22 09:55 | 450 | 521 | 482 | Pulverizer feeders | F8204B Coal Feeder - Trip | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 1.5833 | 0.21577 | 104.0016 | 65.6852 | 66
MC4 | D1 | 200 | 3149 | 2014-08-22 15:18 | 2014-08-24 12:34 | 485 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 45.2667 | 3.1278 | 1507.6146 | 33.3052 | 33
MC4 | D1 | 201 | 3149 | 2014-08-24 12:34 | 2014-08-24 19:07 | 475 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 6.55 | 0.57831 | 278.7459 | 42.5566 | 43
MC4 | D1 | 202 | 3149 | 2014-08-24 19:07 | 2014-08-25 09:54 | 465 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 14.7833 | 1.589 | 765.8958 | 51.8081 | 52
MC4 | D1 | 203 | 3149 | 2014-08-25 09:54 | 2014-08-25 10:36 | 490 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 0.7 | 0.041651 | 20.0756 | 28.6795 | 29
MC4 | D1 | 204 | 3149 | 2014-08-25 10:36 | 2014-08-25 11:36 | 480 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 1 | 0.078695 | 37.9309 | 37.9309 | 38
MC4 | D1 | 205 | 3149 | 2014-08-25 11:36 | 2014-08-26 07:45 | 465 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 20.15 | 2.1658 | 1043.9324 | 51.8081 | 52
MC4 | D1 | 206 | 3149 | 2014-08-26 07:45 | 2014-08-26 10:47 | 490 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 3.0333 | 0.18049 | 86.9944 | 28.6795 | 29
MC4 | D1 | 207 | 3149 | 2014-08-26 10:47 | 2014-08-26 13:50 | 480 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 3.05 | 0.24002 | 115.6893 | 37.9309 | 38
MC4 | D1 | 208 | 3149 | 2014-08-26 13:50 | 2014-08-26 19:25 | 470 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 5.5833 | 0.54655 | 263.4347 | 47.1823 | 47
MC4 | D1 | 209 | 3149 | 2014-08-26 19:25 | 2014-08-26 22:00 | 480 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 2.5833 | 0.20329 | 97.9882 | 37.9309 | 38
MC4 | D4 | 210 | 3240 | 2014-08-26 22:00 | 2014-08-27 02:26 | 280 | 521 | 482 | Cooling tower fans | F5904D Cooling Tower Fan - Maintenance4A Coal Mill PA Fan - Repair Discharge Duct | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 4.4333 | 2.0507 | 988.4546 | 222.9597 | 223
MC4 | D1 | 211 | 3149 | 2014-08-27 02:26 | 2014-08-27 11:18 | 480 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 8.8667 | 0.69776 | 336.3207 | 37.9309 | 38
MC4 | D1 | 212 | 3133 | 2014-08-27 11:18 | 2014-08-27 11:59 | 470 | 521 | 482 | Vacuum pumps | F8204A Condenser Vacuum Pump - Trip, Breaker Overheated | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 0.68333 | 0.066891 | 32.2413 | 47.1823 | 47
MC4 | D1 | 213 | 3149 | 2014-08-27 11:59 | 2014-08-27 13:54 | 480 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 1.9167 | 0.15083 | 72.7009 | 37.9309 | 38
MC4 | D1 | 214 | 3149 | 2014-08-27 13:54 | 2014-08-27 17:30 | 465 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 3.6 | 0.38695 | 186.509 | 51.8081 | 52
MC4 | D1 | 215 | 3149 | 2014-08-27 17:30 | 2014-08-28 10:40 | 485 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 17.1667 | 1.1862 | 571.739 | 33.3052 | 33
MC4 | D1 | 216 | 3149 | 2014-08-28 10:40 | 2014-08-28 23:19 | 475 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 12.65 | 1.1169 | 538.3413 | 42.5566 | 43
MC4 | D1 | 217 | 3149 | 2014-08-28 23:19 | 2014-08-29 12:16 | 485 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 12.95 | 0.89482 | 431.3021 | 33.3052 | 33
MC4 | D1 | 218 | 360 | 2014-08-29 05:36 | 2014-08-29 06:38 | 420 | 521 | 482 | Burners | F7804C Coal Mill - 4C2 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 1.0333 | 0.20032 | 96.5542 | 93.4395 | 93
MC4 | D1 | 219 | 3149 | 2014-08-29 12:16 | 2014-08-29 18:55 | 470 | 521 | 482 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or | F660High Back Pressure | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 6.65 | 0.65096 | 313.7626 | 47.1823 | 47
MC4 | D1 | 220 | 360 | 2014-08-31 12:45 | 2014-08-31 13:33 | 420 | 521 | 482 | Burners | F7804A Coal Mill - 4A2 Burner High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 8 | 0.8 | 0.15509 | 74.7516 | 93.4395 | 93
MC4 | D4 | 221 | 310 | 2014-09-02 22:00 | 2014-09-03 00:47 | 420 | 521 | 482 | Pulverizer mills | F7904E Coal Mill - Clean Air Test | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 2.7833 | 0.53957 | 260.0734 | 93.4395 | 93
MC4 | D1 | 222 | 1488 | 2014-09-03 10:20 | 2014-09-03 12:00 | 485 | 521 | 482 | Air heater (regenerative) | F6604A Air Heater - High Differential | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 1.6667 | 0.11516 | 55.5086 | 33.3052 | 33
MC4 | D1 | 223 | 3499 | 2014-09-04 10:03 | 2014-09-04 14:50 | 480 | 521 | 482 | Other feedwater system problems | F150Feedwater Flow Maxed Out | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 4.7833 | 0.37642 | 181.4361 | 37.9309 | 38
MC4 | D1 | 224 | 3499 | 2014-09-04 14:50 | 2014-09-05 12:18 | 495 | 521 | 482 | Other feedwater system problems | F150Feedwater Flow Maxed Out | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 21.4667 | 1.0713 | 516.3537 | 24.0537 | 24
MC4 | D1 | 225 | 3499 | 2014-09-05 12:18 | 2014-09-05 14:33 | 490 | 521 | 482 | Other feedwater system problems | F150Feedwater Flow Maxed Out | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 2.25 | 0.13388 | 64.5288 | 28.6795 | 29
MC4 | D1 | 226 | 3499 | 2014-09-05 14:33 | 2014-09-10 02:54 | 496 | 521 | 482 | Other feedwater system problems | F150Feedwater Flow Maxed Out | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 108.35 | 5.1991 | 2505.9837 | 23.1286 | 23
MC4 | U1 | 227 | 800 | 2014-09-10 02:54 | 2014-09-10 05:39 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F420Low Drum Level Trip - Operator Error | Mill Creek | Outage | Coal | 3 | 2014 | 9 | 2.75 | 2.75 | 1325.5 | 482 | 482
MC4 | D1 | 228 | 3499 | 2014-09-10 05:39 | 2014-09-18 13:10 | 496 | 521 | 482 | Other feedwater system problems | F150Feedwater Flow Maxed Out | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 199.5167 | 9.5737 | 4614.5409 | 23.1286 | 23
MC4 | D1 | 229 | 1850 | 2014-09-10 11:39 | 2014-09-10 20:00 | 370 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 8.35 | 2.4201 | 1166.4678 | 139.6967 | 140
MC4 | NC | 230 | 9690 | 2014-09-11 10:00 | 2014-09-11 12:00 | 0 | 521 | 482 | Other miscellaneous operational environmental limits (fossil and nuclear) | F790MAT Testing - Full Load | Mill Creek | Other | Coal | 3 | 2014 | 9 | 2 | 2 | 964 | 482 | 482
MC4 | D1 | 231 | 1470 | 2014-09-16 05:15 | 2014-09-16 05:56 | 395 | 521 | 482 | Induced draft fan motors and drives | F5904B Induced Draft Fan - Beck Drive Issue | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 0.68333 | 0.16526 | 79.6549 | 116.5681 | 117
MC4 | D1 | 232 | 570 | 2014-09-16 15:53 | 2014-09-17 10:15 | 485 | 521 | 482 | Other reheat steam problems | F780Reheat Spray Issue - High Temperature | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 18.3667 | 1.2691 | 611.7052 | 33.3052 | 33
MC4 | D1 | 233 | 560 | 2014-09-18 13:10 | 2014-09-18 14:35 | 220 | 521 | 482 | Other hot reheat steam valves (not including turbine stop or intercept valves) | F780Reheat Spray Issue - High Temperature, Block Valve Closed | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 1.4167 | 0.81846 | 394.4968 | 278.4683 | 278
MC4 | U1 | 234 | 3649 | 2014-09-18 14:35 | 2014-09-23 14:46 | 0 | 521 | 482 | Other AC instrument power problems | F430Electrical Wiring - Burnt Wiring in Cable Tray | Mill Creek | Outage | Coal | 3 | 2014 | 9 | 120.1833 | 120.1833 | 57928.3667 | 482 | 482
MC4 | NC | 235 | 1850 | 2014-09-23 14:46 | 2014-09-24 05:05 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 3 | 2014 | 9 | 14.3167 | 14.3167 | 6900.6333 | 482 | 482
MC4 | D1 | 236 | 3499 | 2014-09-24 05:05 | 2014-09-24 06:54 | 496 | 521 | 482 | Other feedwater system problems | F150Feedwater Flow Maxed Out | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 1.8167 | 0.087172 | 42.017 | 23.1286 | 23
MC4 | U1 | 237 | 800 | 2014-09-24 06:54 | 2014-09-24 08:05 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820Low Drum Level Trip - Boiler Pressure Swing | Mill Creek | Outage | Coal | 3 | 2014 | 9 | 1.1833 | 1.1833 | 570.3667 | 482 | 482
MC4 | NC | 238 | 1850 | 2014-09-24 08:05 | 2014-09-24 09:45 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2014 | 9 | 1.6667 | 1.6667 | 803.3333 | 482 | 482
MC4 | U1 | 239 | 800 | 2014-09-24 09:45 | 2014-09-24 11:02 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820Low Drum Level Trip | Mill Creek | Outage | Coal | 3 | 2014 | 9 | 1.2833 | 1.2833 | 618.5667 | 482 | 482
MC4 | D1 | 240 | 3499 | 2014-09-24 11:03 | 2014-09-24 23:47 | 496 | 521 | 482 | Other feedwater system problems | F150Feedwater Flow Maxed Out | Mill Creek | Derate | Coal | 3 | 2014 | 9 | 12.7333 | 0.611 | 294.5042 | 23.1286 | 23
MC4 | PO | 241 | 4400 | 2014-09-24 23:47 | 2014-12-02 18:05 | 0 | 521 | 482 | Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | F590Planned 10 Week Outage | Mill Creek | Other | Coal | 3 | 2014 | 9 | 1650.3 | 1650.3 | 795444.6 | 482 | 482
MC4 | PO | 242 | 8460 | 2014-12-02 18:15 | 2014-12-03 10:13 | 0 | 521 | 482 | Testing A | F790FGD Testing | Mill Creek | Other | Coal | 3 | 2014 | 12 | 15.9667 | 15.9667 | 7695.9333 | 482 | 482
MC4 | U1 | 243 | 800 | 2014-12-03 10:19 | 2014-12-03 11:00 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820Low Drum Level Trip | Mill Creek | Outage | Coal | 3 | 2014 | 12 | 0.68333 | 0.68333 | 329.3667 | 482 | 482
MC4 | MO | 244 | 4240 | 2014-12-03 17:46 | 2014-12-04 09:42 | 0 | 521 | 482 | Bearings E | F850Turbine #3 Bearing - High Vibration | Mill Creek | Maintenance | Coal | 3 | 2014 | 12 | 15.9333 | 15.9333 | 7679.8667 | 482 | 482
MC4 | MO | 245 | 4560 | 2014-12-04 17:07 | 2014-12-06 11:53 | 0 | 521 | 482 | Generator vibration (excluding vibration due to failed bearing and other components) | F850Generator - Balance Shot | Mill Creek | Maintenance | Coal | 3 | 2014 | 12 | 42.7667 | 42.7667 | 20613.5333 | 482 | 482
MC4 | NC | 246 | 1850 | 2014-12-06 11:53 | 2014-12-06 11:58 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2014 | 12 | 0.083333 | 0.083333 | 40.1667 | 482 | 482
MC4 | U1 | 247 | 800 | 2014-12-06 11:58 | 2014-12-06 12:35 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F420Low Drum Level Trip - Operator Error | Mill Creek | Outage | Coal | 3 | 2014 | 12 | 0.61667 | 0.61667 | 297.2333 | 482 | 482
MC4 | NC | 248 | 1850 | 2014-12-06 12:35 | 2014-12-07 12:35 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 3 | 2014 | 12 | 24 | 24 | 11568 | 482 | 482
MC4 | D1 | 249 | 1850 | 2014-12-07 12:35 | 2014-12-08 06:00 | 360 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 17.4167 | 5.3821 | 2594.1807 | 148.9482 | 149
MC4 | D1 | 250 | 1850 | 2014-12-08 06:00 | 2014-12-08 15:20 | 370 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 9.3333 | 2.7051 | 1303.8362 | 139.6967 | 140
MC4 | D1 | 251 | 1850 | 2014-12-08 15:20 | 2014-12-08 22:30 | 340 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 7.1667 | 2.4898 | 1200.0659 | 167.4511 | 167
MC4 | D1 | 252 | 1850 | 2014-12-08 22:30 | 2014-12-09 16:40 | 365 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 18.1667 | 5.4395 | 2621.858 | 144.3225 | 144
MC4 | D1 | 253 | 1850 | 2014-12-09 16:40 | 2014-12-09 20:50 | 445 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 4.1667 | 0.60781 | 292.9623 | 70.3109 | 70
MC4 | D1 | 254 | 3412 | 2014-12-09 20:50 | 2014-12-09 22:10 | 390 | 521 | 482 | Feedwater pump drive - steam turbine | F400Turbine Driven Boiler Feed Pump - Control Issue | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 1.3333 | 0.33525 | 161.5918 | 121.1939 | 121
MC4 | D1 | 255 | 3412 | 2014-12-09 22:10 | 2014-12-09 22:15 | 330 | 521 | 482 | Feedwater pump drive - steam turbine | F400Turbine Driven Boiler Feed Pump - Control Issue | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 0.083333 | 0.03055 | 14.7252 | 176.7025 | 177
MC4 | U1 | 256 | 1455 | 2014-12-09 22:15 | 2014-12-10 02:09 | 0 | 521 | 482 | Induced draft fans | F8204A Induced Draft Fan - Trip | Mill Creek | Outage | Coal | 3 | 2014 | 12 | 3.9 | 3.9 | 1879.8 | 482 | 482
MC4 | NC | 257 | 1850 | 2014-12-10 02:09 | 2014-12-10 03:20 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2014 | 12 | 1.1833 | 1.1833 | 570.3667 | 482 | 482
MC4 | D1 | 258 | 3412 | 2014-12-10 03:20 | 2014-12-10 04:12 | 130 | 521 | 482 | Feedwater pump drive - steam turbine | F400Turbine Driven Boiler Feed Pump - Control Issue | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 0.86667 | 0.65042 | 313.5004 | 361.7313 | 362
MC4 | D1 | 259 | 3412 | 2014-12-10 04:12 | 2014-12-10 06:39 | 156 | 521 | 482 | Feedwater pump drive - steam turbine | F400Turbine Driven Boiler Feed Pump - Control Issue | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 2.45 | 1.7164 | 827.31 | 337.6775 | 338
MC4 | U1 | 260 | 800 | 2014-12-10 06:39 | 2014-12-10 08:39 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F420Low Drum Level Trip - Operator Error | Mill Creek | Outage | Coal | 3 | 2014 | 12 | 2 | 2 | 964 | 482 | 482
MC4 | NC | 261 | 1850 | 2014-12-10 08:39 | 2014-12-10 19:25 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2014 | 12 | 10.7667 | 10.7667 | 5189.5333 | 482 | 482
MC4 | U1 | 262 | 3110 | 2014-12-10 19:25 | 2014-12-13 22:03 | 0 | 521 | 482 | Condenser tube leaks | F540Condenser Tube Leaks | Mill Creek | Outage | Coal | 3 | 2014 | 12 | 74.6333 | 74.6333 | 35973.2667 | 482 | 482
MC4 | NC | 263 | 1850 | 2014-12-13 22:03 | 2014-12-14 13:30 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2014 | 12 | 15.45 | 15.45 | 7446.9 | 482 | 482
MC4 | D1 | 264 | 1850 | 2014-12-14 13:30 | 2014-12-14 16:30 | 240 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 3 | 1.618 | 779.8964 | 259.9655 | 260
MC4 | D1 | 265 | 1850 | 2014-12-14 16:30 | 2014-12-14 17:05 | 320 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 0.58333 | 0.22505 | 108.4731 | 185.9539 | 186
MC4 | D1 | 266 | 1850 | 2014-12-14 17:05 | 2014-12-14 21:45 | 200 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica/ Condensate Valve Sticking | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 4.6667 | 2.8752 | 1385.8656 | 296.9712 | 297
MC4 | D1 | 267 | 1850 | 2014-12-14 21:45 | 2014-12-15 00:57 | 310 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 3.2 | 1.296 | 624.6572 | 195.2054 | 195
MC4 | D1 | 268 | 1850 | 2014-12-15 00:57 | 2014-12-15 05:36 | 345 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 4.65 | 1.5708 | 757.1378 | 162.8253 | 163
MC4 | D1 | 269 | 1850 | 2014-12-15 05:36 | 2014-12-15 16:39 | 390 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 11.05 | 2.7784 | 1339.1921 | 121.1939 | 121
MC4 | D1 | 270 | 1850 | 2014-12-15 16:39 | 2014-12-16 06:50 | 430 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 14.1833 | 2.4773 | 1194.0679 | 84.1881 | 84
MC4 | D1 | 271 | 1850 | 2014-12-16 06:50 | 2014-12-16 09:12 | 275 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 2.3667 | 1.1175 | 538.6188 | 227.5854 | 228
MC4 | U1 | 272 | 3110 | 2014-12-16 09:12 | 2014-12-18 11:49 | 0 | 521 | 482 | Condenser tube leaks | F540Condenser Tube Leaks | Mill Creek | Outage | Coal | 3 | 2014 | 12 | 50.6167 | 50.6167 | 24397.2333 | 482 | 482
MC4 | NC | 273 | 1850 | 2014-12-18 11:49 | 2014-12-19 01:23 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2014 | 12 | 13.5667 | 13.5667 | 6539.1333 | 482 | 482
MC4 | D1 | 274 | 1850 | 2014-12-19 01:23 | 2014-12-19 12:50 | 275 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 11.45 | 5.4063 | 2605.853 | 227.5854 | 228
MC4 | D1 | 275 | 1850 | 2014-12-19 12:50 | 2014-12-20 03:10 | 332 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 14.3333 | 5.1996 | 2506.215 | 174.8522 | 175
MC4 | D1 | 276 | 1850 | 2014-12-20 03:10 | 2014-12-20 11:17 | 350 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 8.1167 | 2.664 | 1284.0536 | 158.1996 | 158
MC4 | D1 | 277 | 1850 | 2014-12-20 11:17 | 2014-12-20 16:25 | 400 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 5.1333 | 1.1922 | 574.6377 | 111.9424 | 112
MC4 | D1 | 278 | 1850 | 2014-12-20 16:25 | 2014-12-20 21:30 | 430 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 5.0833 | 0.88788 | 427.9562 | 84.1881 | 84
MC4 | D1 | 279 | 1850 | 2014-12-20 21:30 | 2014-12-21 06:28 | 405 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 8.9667 | 1.9964 | 962.2731 | 107.3167 | 107
MC4 | D1 | 280 | 1850 | 2014-12-21 06:28 | 2014-12-21 16:06 | 420 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 9.6333 | 1.8675 | 900.1342 | 93.4395 | 93
MC4 | D1 | 281 | 1850 | 2014-12-21 16:06 | 2014-12-22 07:00 | 440 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 14.9 | 2.3165 | 1116.5562 | 74.9367 | 75
MC4 | D1 | 282 | 1850 | 2014-12-22 07:00 | 2014-12-22 12:36 | 463 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 5.6 | 0.62342 | 300.4868 | 53.6583 | 54
MC4 | D4 | 283 | 331 | 2014-12-22 21:00 | 2014-12-23 04:40 | 420 | 521 | 482 | Pulverizer system coal leaks (other than pulverizers | F5404A Coal Mill Maintenance - Coal Conduit Leaks | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 7.6667 | 1.4862 | 716.3698 | 93.4395 | 93
MC4 | D1 | 284 | 260 | 2014-12-23 04:40 | 2014-12-23 08:47 | 420 | 521 | 482 | Primary air fan | F4004A PA Fan 4kV Breaker issues | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 4.1167 | 0.79805 | 384.6594 | 93.4395 | 93
MC4 | D1 | 285 | 310 | 2014-12-23 10:13 | 2014-12-23 13:21 | 490 | 521 | 482 | Pulverizer mills | F7804B Coal Mill Fire | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 3.1333 | 0.18644 | 89.8623 | 28.6795 | 29
MC4 | D1 | 286 | 250 | 2014-12-23 16:22 | 2014-12-23 19:12 | 450 | 521 | 482 | Pulverizer feeders | F8204B Coal Mill Feeder Trip | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 2.8333 | 0.38612 | 186.1081 | 65.6852 | 66
MC4 | D1 | 287 | 270 | 2014-12-23 21:08 | 2014-12-23 23:37 | 500 | 521 | 482 | Primary air duct and dampers | F7804B Coal Mill PA Duct - Hot Spot | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 2.4833 | 0.1001 | 48.2463 | 19.428 | 19
MC4 | D1 | 288 | 310 | 2014-12-24 01:00 | 2014-12-24 06:20 | 450 | 521 | 482 | Pulverizer mills | F5304B Coal Mill Inspection | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 5.3333 | 0.72681 | 350.3212 | 65.6852 | 66
MC4 | D1 | 289 | 331 | 2014-12-25 16:56 | 2014-12-25 22:11 | 430 | 521 | 482 | Pulverizer system coal leaks (other than pulverizers | F5404A Coal Mill - 4A3 Coal Conduit Leak | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 5.25 | 0.91699 | 441.9875 | 84.1881 | 84
MC4 | D1 | 290 | 250 | 2014-12-26 14:20 | 2014-12-26 15:00 | 420 | 521 | 482 | Pulverizer feeders | F4004C Feeder - Fuse block issue | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 0.66667 | 0.12924 | 62.293 | 93.4395 | 93
MC4 | D1 | 291 | 260 | 2014-12-26 22:14 | 2014-12-27 02:08 | 500 | 521 | 482 | Primary air fan | F0604A PA Fan 4kV breaker racking mechanism | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 3.9 | 0.1572 | 75.7693 | 19.428 | 19
MC4 | D1 | 292 | 330 | 2014-12-28 16:48 | 2014-12-28 18:11 | 440 | 521 | 482 | Pulverizer coal leak (pulverizers only) | F5404A Coal Mill Leak | Mill Creek | Derate | Coal | 3 | 2014 | 12 | 1.3833 | 0.21507 | 103.6624 | 74.9367 | 75
MC4 | D4 | 1 | 250 | 2015-01-04 23:00 | 2015-01-05 03:20 | 420 | 521 | 482 | Pulverizer feeders | F5904A Coal Feeder - Replaced Power Supply Board | Mill Creek | Derate | Coal | 3 | 2015 | 1 | 4.3333 | 0.84005 | 404.9047 | 93.4395 | 93
MC4 | NC | 2 | 1990 | 2015-01-07 08:00 | 2015-01-07 16:18 | 0 | 521 | 482 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Combustion Tuning - Full Load Test | Mill Creek | Other | Coal | 3 | 2015 | 1 | 8.3 | 8.3 | 4000.6 | 482 | 482
MC4 | D1 | 3 | 1599 | 2015-01-10 18:33 | 2015-01-10 19:05 | 355 | 521 | 482 | Other miscellaneous boiler air and gas system problems | F400Air Flow Issues | Mill Creek | Derate | Coal | 3 | 2015 | 1 | 0.53333 | 0.16993 | 81.9061 | 153.5739 | 154
MC4 | NC | 4 | 8460 | 2015-01-12 08:30 | 2015-01-12 18:20 | 0 | 521 | 482 | Testing A | F790FGD Performance Testing - Full Load | Mill Creek | Other | Coal | 3 | 2015 | 1 | 9.8333 | 9.8333 | 4739.6667 | 482 | 482
MC4 | NC | 5 | 8460 | 2015-01-13 07:00 | 2015-01-13 18:00 | 0 | 521 | 482 | Testing A | F790FGD Performance Testing - Full Load | Mill Creek | Other | Coal | 3 | 2015 | 1 | 11 | 11 | 5302 | 482 | 482
MC4 | NC | 6 | 8460 | 2015-01-14 07:00 | 2015-01-15 02:34 | 0 | 521 | 482 | Testing A | F790FGD Performance Testing - Full Load | Mill Creek | Other | Coal | 3 | 2015 | 1 | 19.5667 | 19.5667 | 9431.1333 | 482 | 482
MC4 | U1 | 7 | 1480 | 2015-01-15 02:34 | 2015-01-15 07:18 | 0 | 521 | 482 | Other induced draft fan problems | F820Induced Draft Fan Suction Pressure Trip | Mill Creek | Outage | Coal | 3 | 2015 | 1 | 4.7333 | 4.7333 | 2281.4667 | 482 | 482
MC4 | NC | 8 | 1850 | 2015-01-15 07:18 | 2015-01-15 13:20 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2015 | 1 | 6.0333 | 6.0333 | 2908.0667 | 482 | 482
MC4 | D1 | 9 | 1850 | 2015-01-15 13:20 | 2015-01-15 15:15 | 408 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 1 | 1.9167 | 0.41571 | 200.3708 | 104.5413 | 105
MC4 | D1 | 10 | 1850 | 2015-01-15 15:15 | 2015-01-15 16:45 | 500 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 1 | 1.5 | 0.060461 | 29.142 | 19.428 | 19
MC4 | U1 | 11 | 4299 | 2015-01-16 20:40 | 2015-01-17 03:02 | 0 | 521 | 482 | Other hydraulic system problems | F540Turbine Left Intercept Valve - EHC Leak | Mill Creek | Outage | Coal | 3 | 2015 | 1 | 6.3667 | 6.3667 | 3068.7333 | 482 | 482
MC4 | NC | 12 | 1850 | 2015-01-17 03:02 | 2015-01-17 11:58 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2015 | 1 | 8.9333 | 8.9333 | 4305.8667 | 482 | 482
MC4 | D4 | 13 | 8460 | 2015-01-18 03:00 | 2015-01-18 18:05 | 300 | 521 | 482 | Testing A | F790FGD Performance Testing | Mill Creek | Derate | Coal | 3 | 2015 | 1 | 15.0833 | 6.3981 | 3083.8903 | 204.4568 | 204
MC4 | U1 | 14 | 4268 | 2015-01-18 22:43 | 2015-01-19 01:41 | 0 | 521 | 482 | Reheat/intercept valve testing | F820Turbine Reheat/Intercept Valve Check - Trip | Mill Creek | Outage | Coal | 3 | 2015 | 1 | 2.9667 | 2.9667 | 1429.9333 | 482 | 482
MC4 | NC | 15 | 1850 | 2015-01-19 01:41 | 2015-01-19 10:00 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2015 | 1 | 8.3167 | 8.3167 | 4008.6333 | 482 | 482
MC4 | D1 | 16 | 1850 | 2015-01-19 10:00 | 2015-01-19 11:54 | 400 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 1 | 1.9 | 0.44127 | 212.6906 | 111.9424 | 112
MC4 | NC | 17 | 8460 | 2015-01-20 04:00 | 2015-01-20 17:15 | 0 | 521 | 482 | Testing A | F790FGD Performance Testing - Full Load | Mill Creek | Other | Coal | 3 | 2015 | 1 | 13.25 | 13.25 | 6386.5 | 482 | 482
MC4 | NC | 18 | 8650 | 2015-01-21 14:00 | 2015-01-21 17:15 | 0 | 521 | 482 | Baghouse systems | F790FGD Pulse Jet Fabric Filter (PJFF) - Control Efficiency Test at Full Load | Mill Creek | Other | Coal | 3 | 2015 | 1 | 3.25 | 3.25 | 1566.5 | 482 | 482
MC4 | NC | 19 | 510 | 2015-01-21 20:26 | 2015-01-22 03:55 | 0 | 521 | 482 | Main steam relief/safety valves off superheater | F590Main Steam, Reheat & Superheat Safeties - Set | Mill Creek | Other | Coal | 3 | 2015 | 1 | 7.4833 | 7.4833 | 3606.9667 | 482 | 482
MC4 | NC | 20 | 8650 | 2015-01-22 08:00 | 2015-01-22 15:30 | 0 | 521 | 482 | Baghouse systems | F790FGD PJFF - Control Efficiency Test at Full Load | Mill Creek | Other | Coal | 3 | 2015 | 1 | 7.5 | 7.5 | 3615 | 482 | 482
MC4 | NC | 21 | 8650 | 2015-01-22 15:30 | 2015-01-22 19:06 | 0 | 521 | 482 | Baghouse systems | F790FGD PJFF - Pressure Drop Test at Full Load | Mill Creek | Other | Coal | 3 | 2015 | 1 | 3.6 | 3.6 | 1735.2 | 482 | 482
MC4 | NC | 22 | 8460 | 2015-01-27 06:00 | 2015-01-27 14:38 | 0 | 521 | 482 | Testing A | F790RATA Testing - Full Load | Mill Creek | Other | Coal | 3 | 2015 | 1 | 8.6333 | 8.6333 | 4161.2667 | 482 | 482
MC4 | NC | 23 | 8460 | 2015-01-27 22:30 | 2015-01-28 03:00 | 0 | 521 | 482 | Testing A | F790RATA Testing - Low Load @ 290 MW | Mill Creek | Other | Coal | 3 | 2015 | 1 | 4.5 | 4.5 | 2169 | 482 | 482
MC4 | NC | 24 | 8460 | 2015-01-28 03:00 | 2015-01-28 06:32 | 0 | 521 | 482 | Testing A | F790RATA Testing - Mid Load @ 390 MW | Mill Creek | Other | Coal | 3 | 2015 | 1 | 3.5333 | 3.5333 | 1703.0667 | 482 | 482
MC4 | MO | 25 | 8650 | 2015-01-28 11:26 | 2015-01-31 14:55 | 0 | 521 | 482 | Baghouse systems | F530Baghouse inspection | Mill Creek | Maintenance | Coal | 3 | 2015 | 1 | 75.4833 | 75.4833 | 36382.9667 | 482 | 482
MC4 | NC | 26 | 1850 | 2015-01-31 14:55 | 2015-02-01 03:20 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica at warm start-up | Mill Creek | Other | Coal | 3 | 2015 | 1 | 12.4167 | 12.4167 | 5984.8333 | 482 | 482
MC4 | D1 | 27 | 1850 | 2015-02-01 03:20 | 2015-02-01 07:52 | 465 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2015 | 2 | 4.5333 | 0.48727 | 234.8632 | 51.8081 | 52
MC4 | NC | 28 | 8650 | 2015-02-04 04:00 | 2015-02-04 18:00 | 0 | 521 | 482 | Baghouse systems | F790Baghouse testing at Full Load | Mill Creek | Other | Coal | 3 | 2015 | 2 | 14 | 14 | 6748 | 482 | 482
MC4 | NC | 29 | 8650 | 2015-02-05 04:00 | 2015-02-06 19:00 | 0 | 521 | 482 | Baghouse systems | F790Baghouse - Testing at Full Load | Mill Creek | Other | Coal | 3 | 2015 | 2 | 39 | 39 | 18798 | 482 | 482
MC4 | NC | 30 | 1990 | 2015-02-06 22:00 | 2015-02-07 05:19 | 0 | 521 | 482 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Boiler tuning - Full load available if needed. | Mill Creek | Other | Coal | 3 | 2015 | 2 | 7.3167 | 7.3167 | 3526.6333 | 482 | 482
MC4 | D1 | 31 | 3504 | 2015-02-09 09:38 | 2015-02-09 11:27 | 430 | 521 | 482 | Heater drain valves | F590Heater 5 Drain valve regulator issue | Mill Creek | Derate | Coal | 3 | 2015 | 2 | 1.8167 | 0.31731 | 152.9417 | 84.1881 | 84
MC4 | NC | 32 | 360 | 2015-02-09 11:27 | 2015-02-09 17:22 | 0 | 521 | 482 | Burners | F790Burner testing | Mill Creek | Other | Coal | 3 | 2015 | 2 | 5.9167 | 5.9167 | 2851.8333 | 482 | 482
MC4 | NC | 33 | 8460 | 2015-02-11 08:00 | 2015-02-11 17:00 | 0 | 521 | 482 | Testing A | F790FGD Power Consumption Test @ Full Load | Mill Creek | Other | Coal | 3 | 2015 | 2 | 9 | 9 | 4338 | 482 | 482
MC4 | D1 | 34 | 260 | 2015-02-11 23:00 | 2015-02-12 05:00 | 430 | 521 | 482 | Primary air fan | F5904D Coal Mill Primary Air Fan Inboard Bearing - Replaced Shaft Seal | Mill Creek | Derate | Coal | 3 | 2015 | 2 | 6 | 1.048 | 505.1286 | 84.1881 | 84
MC4 | D1 | 35 | 260 | 2015-02-13 07:31 | 2015-02-13 08:20 | 430 | 521 | 482 | Primary air fan | F5904A Coal Mill Primary Air Fan - Breaker Issue | Mill Creek | Derate | Coal | 3 | 2015 | 2 | 0.81667 | 0.14264 | 68.7536 | 84.1881 | 84
MC4 | NC | 36 | 360 | 2015-02-13 09:30 | 2015-02-13 15:50 | 0 | 521 | 482 | Burners | F790Burner Tuning @ Full Load | Mill Creek | Other | Coal | 3 | 2015 | 2 | 6.3333 | 6.3333 | 3052.6667 | 482 | 482
MC4 | NC | 37 | 8700 | 2015-02-24 08:00 | 2015-02-24 16:00 | 0 | 521 | 482 | CEMS Certification and Recertification | F790PM and RATA - Full Load Test | Mill Creek | Other | Coal | 3 | 2015 | 2 | 8 | 8 | 3856 | 482 | 482
MC4 | NC | 38 | 8460 | 2015-02-25 08:00 | 2015-02-25 17:00 | 0 | 521 | 482 | Testing A | F790RATA Testing | Mill Creek | Other | Coal | 3 | 2015 | 2 | 9 | 9 | 4338 | 482 | 482
MC4 | NC | 39 | 8460 | 2015-02-26 08:00 | 2015-02-26 15:54 | 0 | 521 | 482 | Testing A | F790RATA Testing - Full Load | Mill Creek | Other | Coal | 3 | 2015 | 2 | 7.9 | 7.9 | 3807.8 | 482 | 482
MC4 | NC | 40 | 9999 | 2015-03-02 08:00 | 2015-03-02 13:00 | 0 | 521 | 482 | Total unit performance testing (use appropriate codes for individual component testing) | F790Winter Capability Test - Full Load | Mill Creek | Other | Coal | 3 | 2015 | 3 | 5 | 5 | 2410 | 482 | 482
MC4 | D1 | 41 | 1488 | 2015-03-06 04:55 | 2015-03-12 08:54 | 512 | 521 | 482 | Air heater (regenerative) | F6604B Air Heater Differential Pressure | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 147.9833 | 2.5563 | 1232.153 | 8.3263 | 8
MC4 | D1 | 42 | 1488 | 2015-03-12 08:54 | 2015-03-13 00:16 | 500 | 521 | 482 | Air heater (regenerative) | F660Air heater high differential pressure - B side | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 15.3667 | 0.61939 | 298.544 | 19.428 | 19
MC4 | MO | 43 | 1488 | 2015-03-13 00:16 | 2015-03-16 15:44 | 0 | 521 | 482 | Air heater (regenerative) | F320Air Heaters - Wash | Mill Creek | Maintenance | Coal | 3 | 2015 | 3 | 87.4667 | 87.4667 | 42158.9333 | 482 | 482
MC4 | NC | 44 | 1850 | 2015-03-16 15:44 | 2015-03-17 03:45 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Warm Start Up | Mill Creek | Other | Coal | 3 | 2015 | 3 | 12.0167 | 12.0167 | 5792.0333 | 482 | 482
MC4 | D1 | 45 | 1850 | 2015-03-17 03:45 | 2015-03-17 21:22 | 459 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 17.6167 | 2.0964 | 1010.4731 | 57.3589 | 57
MC4 | U1 | 46 | 800 | 2015-03-25 15:24 | 2015-03-25 19:31 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820Low Drum Level Trip | Mill Creek | Outage | Coal | 3 | 2015 | 3 | 4.1167 | 4.1167 | 1984.2333 | 482 | 482
MC4 | NC | 47 | 1850 | 2015-03-25 19:31 | 2015-03-26 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start | Mill Creek | Other | Coal | 3 | 2015 | 3 | 4.4833 | 4.4833 | 2160.9667 | 482 | 482
MC4 | D1 | 56 | 1850 | 2015-03-26 | 2015-03-26 01:31 | 450 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 1.5167 | 0.20669 | 99.6226 | 65.6852 | 66
MC4 | D1 | 48 | 1850 | 2015-03-26 01:31 | 2015-03-26 03:00 | 350 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 1.4833 | 0.48685 | 234.6628 | 158.1996 | 158
MC4 | D1 | 49 | 1850 | 2015-03-26 03:00 | 2015-03-26 06:21 | 370 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 3.35 | 0.97092 | 467.9841 | 139.6967 | 140
MC4 | D1 | 50 | 1850 | 2015-03-26 06:21 | 2015-03-26 07:24 | 437 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 1.05 | 0.16929 | 81.5977 | 77.7121 | 78
MC4 | D1 | 51 | 1850 | 2015-03-26 07:24 | 2015-03-26 10:10 | 450 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 2.7667 | 0.37703 | 181.7291 | 65.6852 | 66
MC4 | D1 | 52 | 360 | 2015-03-27 23:36 | 2015-03-28 00:56 | 380 | 521 | 482 | Burners | F7804A Mill Burner Temp | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 1.3333 | 0.36084 | 173.9271 | 130.4453 | 130
MC4 | D1 | 53 | 360 | 2015-03-28 02:00 | 2015-03-28 02:27 | 430 | 521 | 482 | Burners | F7804D Mill Burner Temp | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 0.45 | 0.078599 | 37.8846 | 84.1881 | 84
MC4 | D4 | 54 | 310 | 2015-03-30 22:00 | 2015-03-31 04:17 | 390 | 521 | 482 | Pulverizer mills | F790Coal Mill Air Flow Testing | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 6.2833 | 1.5799 | 761.5014 | 121.1939 | 121
MC4 | D4 | 55 | 310 | 2015-03-31 23:00 | 2015-04-01 02:23 | 350 | 521 | 482 | Pulverizer mills | F790Coal Mill Air Flow Testing | Mill Creek | Derate | Coal | 3 | 2015 | 3 | 3.3833 | 1.1105 | 535.242 | 158.1996 | 158
MC4 | U1 | 57 | 1455 | 2015-04-01 18:22 | 2015-04-01 20:30 | 0 | 521 | 482 | Induced draft fans | F8204A Induced Draft Fan - Tripped | Mill Creek | Outage | Coal | 3 | 2015 | 4 | 2.1333 | 2.1333 | 1028.2667 | 482 | 482
MC4 | NC | 58 | 1850 | 2015-04-01 20:30 | 2015-04-01 23:22 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2015 | 4 | 2.8667 | 2.8667 | 1381.7333 | 482 | 482
MC4 | D4 | 59 | 1471 | 2015-04-03 | 2015-04-03 00:08 | 300 | 521 | 482 | Induced draft fan motors - variable speed | F590ID Fan VFD Cooling Water - Changed filters | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 0.13333 | 0.056558 | 27.2609 | 204.4568 | 204
MC4 | D1 | 60 | 250 | 2015-04-06 11:00 | 2015-04-06 15:00 | 510 | 521 | 482 | Pulverizer feeders | FW00Wet coal | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 4 | 0.084453 | 40.7063 | 10.1766 | 10
MC4 | D4 | 61 | 250 | 2015-04-07 22:50 | 2015-04-08 04:30 | 425 | 521 | 482 | Pulverizer feeders | F0904E Coal Mill Feeder Calibration | Mill Creek | Derate | Coal | 3 | 2015 | 4 | 5.6667 | 1.0441 | 503.2783 | 88.8138 | 89
MC4 | D1 | 62 | 1488 | 2015-05-11 12:00 | 2015-05-14 10:40 | 500 | 521 | 482 | Air heater (regenerative) | F6604A air heater pressure differential | Mill Creek | Derate | Coal | 3 | 2015 | 5 | 70.6667 | 2.8484 | 1372.9136 | 19.428 | 19
MC4 | U1 | 63 | 1455 | 2015-05-14 10:40 | 2015-05-14 12:39 | 0 | 521 | 482 | Induced draft fans | F820ID fan sunction pressure trip | Mill Creek | Outage | Coal | 3 | 2015 | 5 | 1.9833 | 1.9833 | 955.9667 | 482 | 482
MC4 | NC | 64 | 1850 | 2015-05-14 12:39 | 2015-05-14 13:42 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica @ very hot start | Mill Creek | Other | Coal | 3 | 2015 | 5 | 1.05 | 1.05 | 506.1 | 482 | 482
MC4 | U1 | 65 | 800 | 2015-05-14 13:42 | 2015-05-14 14:10 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820High drum level trip | Mill Creek | Outage | Coal | 3 | 2015 | 5 | 0.46667 | 0.46667 | 224.9333 | 482 | 482
MC4 | NC | 66 | 1850 | 2015-05-14 14:10 | 2015-05-14 20:10 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica @ very hot start | Mill Creek | Other | Coal | 3 | 2015 | 5 | 6 | 6 | 2892 | 482 | 482
MC4 | D1 | 67 | 1850 | 2015-05-14 20:10 | 2015-05-15 03:00 | 350 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2015 | 5 | 6.8333 | 2.2428 | 1081.0307 | 158.1996 | 158
MC4 | D1 | 68 | 1850 | 2015-05-15 03:00 | 2015-05-15 06:50 | 400 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2015 | 5 | 3.8333 | 0.89028 | 429.1126 | 111.9424 | 112
MC4 | D1 | 69 | 1850 | 2015-05-15 06:50 | 2015-05-15 09:44 | 460 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 5 | 2.9 | 0.33954 | 163.658 | 56.4338 | 56
MC4 | D1 | 70 | 1488 | 2015-05-15 09:44 | 2015-05-21 13:14 | 500 | 521 | 482 | Air heater (regenerative) | F6604A Air heater pressure differential | Mill Creek | Derate | Coal | 3 | 2015 | 5 | 147.5 | 5.9453 | 2865.6334 | 19.428 | 19
MC4 | MO | 71 | 1488 | 2015-05-21 13:14 | 2015-05-23 20:30 | 0 | 521 | 482 | Air heater (regenerative) | F320Air heater wash | Mill Creek | Maintenance | Coal | 3 | 2015 | 5 | 55.2667 | 55.2667 | 26638.5333 | 482 | 482
MC4 | NC | 73 | 1850 | 2015-05-25 09:19 | 2015-05-26 05:10 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica at Cold Start | Mill Creek | Other | Coal | 3 | 2015 | 5 | 19.85 | 19.85 | 9567.7 | 482 | 482
MC4 | NC | 74 | 8460 | 2015-06-10 09:20 | 2015-06-10 19:41 | 0 | 521 | 482 | Testing A | F790Full Load Testing | Mill Creek | Other | Coal | 3 | 2015 | 6 | 10.35 | 10.35 | 4988.7 | 482 | 482
MC4 | NC | 75 | 8460 | 2015-06-11 09:15 | 2015-06-11 16:27 | 0 | 521 | 482 | Testing A | F790Full Load Testing | Mill Creek | Other | Coal | 3 | 2015 | 6 | 7.2 | 7.2 | 3470.4 | 482 | 482
MC4 | NC | 76 | 9999 | 2015-07-08 10:16 | 2015-07-08 11:32 | 0 | 521 | 482 | Total unit performance testing (use appropriate codes for individual component testing) | F790Summer capability test | Mill Creek | Other | Coal | 3 | 2015 | 7 | 1.2667 | 1.2667 | 610.5333 | 482 | 482
MC4 | NC | 77 | 3240 | 2015-07-09 09:27 | 2015-07-09 19:55 | 0 | 521 | 482 | Cooling tower fans | F790Cooling Tower Test | Mill Creek | Other | Coal | 3 | 2015 | 7 | 10.4667 | 10.4667 | 5044.9333 | 482 | 482
MC4 | NC | 78 | 3240 | 2015-07-10 09:00 | 2015-07-10 22:54 | 0 | 521 | 482 | Cooling tower fans | F790Cooling Tower Test | Mill Creek | Other | Coal | 3 | 2015 | 7 | 13.9 | 13.9 | 6699.8 | 482 | 482
MC4 | D1 | 79 | 310 | 2015-07-15 15:28 | 2015-07-15 18:27 | 402 | 521 | 482 | Pulverizer mills | F5904A Coal Mill - Breaker Issue | Mill Creek | Derate | Coal | 3 | 2015 | 7 | 2.9833 | 0.68141 | 328.4415 | 110.0921 | 110
MC4 | NC | 80 | 9999 | 2015-07-17 08:42 | 2015-07-17 14:27 | 0 | 521 | 482 | Total unit performance testing (use appropriate codes for individual component testing) | F790Summer capability test | Mill Creek | Other | Coal | 3 | 2015 | 7 | 5.75 | 5.75 | 2771.5 | 482 | 482
MC4 | D1 | 81 | 95 | 2015-07-18 23:17 | 2015-07-19 01:53 | 375 | 521 | 482 | Bunker flow problems | F1204A Conduit pluggage | Mill Creek | Derate | Coal | 3 | 2015 | 7 | 2.6 | 0.7286 | 351.1846 | 135.071 | 135
MC4 | NC | 82 | 8460 | 2015-07-22 09:10 | 2015-07-22 13:49 | 0 | 521 | 482 | Testing A | F790Sulfuric Acid Mist (SAM's) Testing | Mill Creek | Other | Coal | 3 | 2015 | 7 | 4.65 | 4.65 | 2241.3 | 482 | 482
MC4 | D4 | 83 | 1407 | 2015-07-22 22:00 | 2015-07-22 22:26 | 200 | 521 | 482 | Forced draft fan lubrication system | F5904A Forced Draft Fan Lube Oil System - Alternate Filter | Mill Creek | Derate | Coal | 3 | 2015 | 7 | 0.43333 | 0.26699 | 128.6875 | 296.9712 | 297
MC4 | U1 | 84 | 4264 | 2015-08-02 02:27 | 2015-08-02 09:10 | 0 | 521 | 482 | Combined intercept valves | F540Turbine #2 Reheat/Intercept Valve - EHC Leak | Mill Creek | Outage | Coal | 3 | 2015 | 8 | 6.7167 | 6.7167 | 3237.4333 | 482 | 482
MC4 | NC | 85 | 1850 | 2015-08-02 09:10 | 2015-08-02 17:26 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2015 | 8 | 8.2667 | 8.2667 | 3984.5333 | 482 | 482
MC4 | U1 | 86 | 800 | 2015-08-02 17:26 | 2015-08-02 20:09 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820High Drum Level Trip | Mill Creek | Outage | Coal | 3 | 2015 | 8 | 2.7167 | 2.7167 | 1309.4333 | 482 | 482
MC4 | NC | 87 | 1850 | 2015-08-02 20:09 | 2015-08-03 02:21 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2015 | 8 | 6.2 | 6.2 | 2988.4 | 482 | 482
MC4 | D1 | 88 | 1850 | 2015-08-03 02:21 | 2015-08-03 06:52 | 495 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 4.5167 | 0.2254 | 108.6427 | 24.0537 | 24
MC4 | U1 | 89 | 800 | 2015-08-04 02:33 | 2015-08-04 04:58 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820High Drum Level Trip - Feedwater Heater Bypass | Mill Creek | Outage | Coal | 3 | 2015 | 8 | 2.4167 | 2.4167 | 1164.8333 | 482 | 482
MC4 | NC | 90 | 1850 | 2015-08-04 04:58 | 2015-08-04 11:50 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Very Hot Start Up | Mill Creek | Other | Coal | 3 | 2015 | 8 | 6.8667 | 6.8667 | 3309.7333 | 482 | 482
MC4 | D1 | 91 | 1850 | 2015-08-04 11:50 | 2015-08-04 16:08 | 355 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 4.3 | 1.3701 | 660.3678 | 153.5739 | 154
MC4 | NC | 92 | 3623 | 2015-08-13 12:00 | 2015-08-13 13:54 | 0 | 521 | 482 | Auxiliary generators | F790VAR Testing | Mill Creek | Other | Coal | 3 | 2015 | 8 | 1.9 | 1.9 | 915.8 | 482 | 482
MC4 | D4 | 93 | 876 | 2015-08-26 23:00 | 2015-08-27 05:02 | 280 | 521 | 482 | Soot blower controls | F590Sootblower Regulator Repair | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 6.0333 | 2.7909 | 1345.1901 | 222.9597 | 223
MC4 | D1 | 94 | 380 | 2015-08-30 12:00 | 2015-08-30 12:22 | 370 | 521 | 482 | Light-off (igniter) systems (including fuel supply) | F5904C & 4E Coal Mills - Lighter Issues | Mill Creek | Derate | Coal | 3 | 2015 | 8 | 0.36667 | 0.10627 | 51.2221 | 139.6967 | 140
MC4 | MO | 95 | 3110 | 2015-09-05 19:57 | 2015-09-07 18:53 | 0 | 521 | 482 | Condenser tube leaks | F540Condenser Tube Leak Repair | Mill Creek | Maintenance | Coal | 3 | 2015 | 9 | 46.9333 | 46.9333 | 22621.8667 | 482 | 482
MC4 | NC | 96 | 1850 | 2015-09-07 18:53 | 2015-09-08 05:00 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2015 | 9 | 10.1167 | 10.1167 | 4876.2333 | 482 | 482
MC4 | D1 | 97 | 1850 | 2015-09-08 05:00 | 2015-09-08 06:32 | 350 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica | Mill Creek | Derate | Coal | 3 | 2015 | 9 | 1.5333 | 0.50326 | 242.5727 | 158.1996 | 158
MC4 | NC | 98 | 3623 | 2015-09-09 12:41 | 2015-09-09 14:10 | 0 | 521 | 482 | Auxiliary generators | F790VAR Testing | Mill Creek | Other | Coal | 3 | 2015 | 9 | 1.4833 | 1.4833 | 714.9667 | 482 | 482
MC4 | PO | 99 | 1801 | 2015-09-24 21:27 | 2015-10-08 01:27 | 0 | 521 | 482 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Planned Outage | Mill Creek | Other | Coal | 3 | 2015 | 9 | 316 | 316 | 152312 | 482 | 482
MC4 | NC | 100 | 1850 | 2015-10-08 01:27 | 2015-10-09 01:30 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Cold Start Up | Mill Creek | Other | Coal | 3 | 2015 | 10 | 24.05 | 24.05 | 11592.1 | 482 | 482
MC4 | D1 | 101 | 310 | 2015-10-14 11:05 | 2015-10-14 11:26 | 400 | 521 | 482 | Pulverizer mills | F8204D Coal Mill - Trip, Breaker Issue | Mill Creek | Derate | Coal | 3 | 2015 | 10 | 0.35 | 0.081286 | 39.1798 | 111.9424 | 112
MC4 | U1 | 102 | 1000 | 2015-10-18 00:22 | 2015-10-19 14:53 | 0 | 521 | 482 | Waterwall (Furnace wall) A | F540Boiler Tube Leak - Waterwall | Mill Creek | Outage | Coal | 3 | 2015 | 10 | 38.5167 | 38.5167 | 18565.0333 | 482 | 482
MC4 | NC | 103 | 1850 | 2015-10-19 14:53 | 2015-10-19 22:55 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica @ Hot Start Up | Mill Creek | Other | Coal | 3 | 2015 | 10 | 8.0333 | 8.0333 | 3872.0667 | 482 | 482
MC4 | MO | 104 | 1000 | 2015-10-30 21:53 | 2015-10-31 18:45 | 0 | 521 | 482 | Waterwall (Furnace wall) A | F540Boiler tube leak - waterwall | Mill Creek | Maintenance | Coal | 3 | 2015 | 10 | 20.8667 | 20.8667 | 10057.7333 | 482 | 482
MC4 | NC | 105 | 1850 | 2015-10-31 18:45 | 2015-11-01 01:54 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica @ hot start | Mill Creek | Other | Coal | 3 | 2015 | 10 | 7.15 | 7.15 | 3446.3 | 482 | 482
MC4 | D1 | 106 | 95 | 2015-11-18 04:18 | 2015-11-18 07:03 | 390 | 521 | 482 | Bunker flow problems | F1204B Coal bunker valve stuck | Mill Creek | Derate | Coal | 3 | 2015 | 11 | 2.75 | 0.69146 | 333.2831 | 121.1939 | 121
MC4 | NC | 107 | 8460 | 2015-11-23 09:45 | 2015-11-23 16:35 | 0 | 521 | 482 | Testing A | F790SCR Flue gas testing | Mill Creek | Other | Coal | 3 | 2015 | 11 | 6.8333 | 6.8333 | 3293.6667 | 482 | 482
MC4 | NC | 108 | 8460 | 2015-11-24 09:00 | 2015-11-24 16:34 | 0 | 521 | 482 | Testing A | F790WFGD testing for Babcock Power | Mill Creek | Other | Coal | 3 | 2015 | 11 | 7.5667 | 7.5667 | 3647.1333 | 482 | 482
MC4 | MO | 109 | 1310 | 2015-11-27 06:48 | 2015-12-05 22:15 | 0 | 521 | 482 | Water side cleaning (acid cleaning) | FC00Boiler chemical clean | Mill Creek | Maintenance | Coal | 3 | 2015 | 11 | 207.45 | 207.45 | 99990.9 | 482 | 482
MC4 | NC | 110 | 1850 | 2015-12-05 22:15 | 2015-12-06 20:40 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica @ Cold Start | Mill Creek | Other | Coal | 3 | 2015 | 12 | 22.4167 | 22.4167 | 10804.8333 | 482 | 482
MC4 | NC | 111 | 8460 | 2015-12-08 22:00 | 2015-12-09 05:15 | 0 | 521 | 482 | Testing A | F790FGD Low Load Testing | Mill Creek | Other | Coal | 3 | 2015 | 12 | 7.25 | 7.25 | 3494.5 | 482 | 482
MC4 | D1 | 112 | 310 | 2015-12-23 08:17 | 2015-12-23 08:38 | 190 | 521 | 482 | Pulverizer mills | F400Lost 4A and 4D Coal Mills - Electrical Trips | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 0.35 | 0.22236 | 107.1779 | 306.2226 | 306
MC4 | D1 | 113 | 310 | 2015-12-23 08:38 | 2015-12-23 09:28 | 205 | 521 | 482 | Pulverizer mills | F400Lost 4A and 4D Coal Mills - Electrical Trips | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 0.83333 | 0.50544 | 243.6212 | 292.3455 | 292
MC4 | D1 | 114 | 4269 | 2015-12-23 09:28 | 2015-12-23 10:42 | 100 | 521 | 482 | Other turbine valves | F660Transfer Turbine Valves from Full Arc to Partial Arc | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 1.2333 | 0.99661 | 480.3656 | 389.4856 | 389
MC4 | D1 | 115 | 310 | 2015-12-24 00:19 | 2015-12-24 01:10 | 125 | 521 | 482 | Pulverizer mills | F400Lost 4A and 4D Coal Mills - Electrical Trips | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 0.85 | 0.64607 | 311.4035 | 366.357 | 366
MC4 | D1 | 116 | 310 | 2015-12-24 15:01 | 2015-12-24 17:40 | 140 | 521 | 482 | Pulverizer mills | F400Lost 4A and 4C Coal Mills - Electrical Trips | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 2.65 | 1.9379 | 934.0716 | 352.4798 | 352
MC4 | D4 | 117 | 360 | 2015-12-30 21:32 | 2015-12-30 21:54 | 380 | 521 | 482 | Burners | F5304A Mill burner inspection | Mill Creek | Derate | Coal | 3 | 2015 | 12 | 0.36667 | 0.099232 | 47.8299 | 130.4453 | 130
MC4 | D1 | 1 | 250 | 2016-01-04 00:30 | 2016-01-04 03:00 | 420 | 521 | 482 | Pulverizer feeders | F120E Mill feeder plugged | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 2.5 | 0.48464 | 233.5988 | 93.4395 | 93
MC4 | D1 | 2 | 310 | 2016-01-06 05:16 | 2016-01-06 10:50 | 390 | 521 | 482 | Pulverizer mills | F8204E Mill tripped with instantaneous targets on the A & B Phases. | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 5.5667 | 1.3997 | 674.6458 | 121.1939 | 121
MC4 | D1 | 3 | 270 | 2016-01-07 06:15 | 2016-01-07 06:45 | 440 | 521 | 482 | Primary air duct and dampers | F3404E mill hot air damper switch | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 0.5 | 0.077735 | 37.4683 | 74.9367 | 75
MC4 | D1 | 4 | 360 | 2016-01-10 07:52 | 2016-01-10 09:20 | 270 | 521 | 482 | Burners | F780A Mill high burner temps | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 1.4667 | 0.70659 | 340.5763 | 232.2111 | 232
MC4 | D1 | 5 | 260 | 2016-01-10 11:33 | 2016-01-10 13:50 | 360 | 521 | 482 | Primary air fan | F4004D PA Fan tripping out | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 2.2833 | 0.7056 | 340.0983 | 148.9482 | 149
MC4 | NC | 6 | 8700 | 2016-01-12 08:00 | 2016-01-12 18:18 | 0 | 521 | 482 | CEMS Certification and Recertification | F790Full load RATA testing | Mill Creek | Other | Coal | 3 | 2016 | 1 | 10.3 | 10.3 | 4964.6 | 482 | 482
MC4 | NC | 7 | 8700 | 2016-01-13 10:23 | 2016-01-13 13:56 | 0 | 521 | 482 | CEMS Certification and Recertification | F790Full load RATA testing | Mill Creek | Other | Coal | 3 | 2016 | 1 | 3.55 | 3.55 | 1711.1 | 482 | 482
MC4 | NC | 8 | 8700 | 2016-01-13 22:00 | 2016-01-14 00:59 | 0 | 521 | 482 | CEMS Certification and Recertification | F790Mid load RATA testing | Mill Creek | Other | Coal | 3 | 2016 | 1 | 2.9833 | 2.9833 | 1437.9667 | 482 | 482
MC4 | D1 | 9 | 335 | 2016-01-27 11:16 | 2016-01-27 20:09 | 395 | 521 | 482 | Pulverizer lube oil system | F820A mill lube oil pump motor trip | Mill Creek | Derate | Coal | 3 | 2016 | 1 | 8.8833 | 2.1484 | 1035.5136 | 116.5681 | 117
MC4 | NC | 10 | 9999 | 2016-02-02 09:00 | 2016-02-02 13:01 | 0 | 521 | 482 | Total unit performance testing (use appropriate codes for individual component testing) | F790Full Load winter capability test | Mill Creek | Other | Coal | 3 | 2016 | 2 | 4.0167 | 4.0167 | 1936.0333 | 482 | 482
MC4 | U1 | 11 | 1470 | 2016-02-02 13:01 | 2016-02-02 16:34 | 0 | 521 | 482 | Induced draft fan motors and drives | F8204B ID fan trip on high stator temp. | Mill Creek | Outage | Coal | 3 | 2016 | 2 | 3.55 | 3.55 | 1711.1 | 482 | 482
MC4 | NC | 12 | 1850 | 2016-02-02 16:34 | 2016-02-02 20:34 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica at very hot start | Mill Creek | Other | Coal | 3 | 2016 | 2 | 4 | 4 | 1928 | 482 | 482
MC4 | D4 | 13 | 360 | 2016-02-02 22:00 | 2016-02-03 03:08 | 360 | 521 | 482 | Burners | F5904D mill burner maintenance | Mill Creek | Derate | Coal | 3 | 2016 | 2 | 5.1333 | 1.5863 | 764.6006 | 148.9482 | 149
MC4 | D1 | 14 | 360 | 2016-02-09 11:45 | 2016-02-09 12:46 | 415 | 521 | 482 | Burners | F7804C mill high burner temps | Mill Creek | Derate | Coal | 3 | 2016 | 2 | 1.0167 | 0.20685 | 99.6997 | 98.0653 | 98
MC4 | NC | 15 | 8700 | 2016-02-10 08:00 | 2016-02-10 15:50 | 0 | 521 | 482 | CEMS Certification and Recertification | F790Full load PM/RRA Testing | Mill Creek | Other | Coal | 3 | 2016 | 2 | 7.8333 | 7.8333 | 3775.6667 | 482 | 482
MC4 | U1 | 16 | 250 | 2016-02-27 14:37 | 2016-02-27 16:18 | 0 | 521 | 482 | Pulverizer feeders | F8204A and 4B Mill feeders tripped. | Mill Creek | Outage | Coal | 3 | 2016 | 2 | 1.6833 | 1.6833 | 811.3667 | 482 | 482
MC4 | NC | 17 | 1850 | 2016-02-27 16:18 | 2016-02-27 21:44 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica @ very hot start | Mill Creek | Other | Coal | 3 | 2016 | 2 | 5.4333 | 5.4333 | 2618.8667 | 482 | 482
MC4 | U1 | 18 | 1470 | 2016-02-27 21:44 | 2016-02-28 00:57 | 0 | 521 | 482 | Induced draft fan motors and drives | F8204A ID fan inlet load index trip | Mill Creek | Outage | Coal | 3 | 2016 | 2 | 3.2167 | 3.2167 | 1550.4333 | 482 | 482
MC4 | NC | 19 | 1850 | 2016-02-28 00:57 | 2016-02-28 06:57 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica @ very hot start | Mill Creek | Other | Coal | 3 | 2016 | 2 | 6 | 6 | 2892 | 482 | 482
MC4 | D1 | 20 | 1850 | 2016-02-28 06:57 | 2016-02-28 08:15 | 490 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica | Mill Creek | Derate | Coal | 3 | 2016 | 2 | 1.3 | 0.077351 | 37.2833 | 28.6795 | 29
MC4 | NC | 21 | 1999 | 2016-03-01 09:30 | 2016-03-01 12:00 | 0 | 521 | 482 | Boiler | F790Full load windbox testing | Mill Creek | Other | Coal | 3 | 2016 | 3 | 2.5 | 2.5 | 1205 | 482 | 482
MC4 | NC | 22 | 8460 | 2016-04-16 15:00 | 2016-04-16 18:00 | 0 | 521 | 482 | Testing A | F790Hg compliance testing | Mill Creek | Other | Coal | 3 | 2016 | 4 | 3 | 3 | 1446 | 482 | 482
MC4 | U1 | 23 | 1040 | 2016-04-28 10:34 | 2016-05-01 23:27 | 0 | 521 | 482 | First superheater B | F540Boiler tube leak - superheat | Mill Creek | Outage | Coal | 3 | 2016 | 4 | 84.8833 | 84.8833 | 40913.7667 | 482 | 482
MC4 | NC | 24 | 1850 | 2016-05-01 23:27 | 2016-05-02 14:06 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica @ warm start | Mill Creek | Other | Coal | 3 | 2016 | 5 | 14.65 | 14.65 | 7061.3 | 482 | 482
MC4 | D1 | 25 | 3150 | 2016-06-04 09:07 | 2016-06-04 09:21 | 307 | 521 | 482 | Hot well level controls | F690Make up to hotwell not operating | Mill Creek | Derate | Coal | 3 | 2016 | 6 | 0.23333 | 0.095841 | 46.1955 | 197.9808 | 198
MC4 | D1 | 26 | 260 | 2016-06-14 08:14 | 2016-06-14 08:25 | 430 | 521 | 482 | Primary air fan | F5904A mill not available, 4C PA fan not available | Mill Creek | Derate | Coal | 3 | 2016 | 6 | 0.18333 | 0.032022 | 15.4345 | 84.1881 | 84
MC4 | NC | 27 | 8010 | 2016-06-15 00:50 | 2016-06-15 04:42 | 0 | 521 | 482 | Crushers/mills | F430Lost feed to limestone crusher, cant make slurry | Mill Creek | Other | Coal | 3 | 2016 | 6 | 3.8667 | 3.8667 | 1863.7333 | 482 | 482
MC4 | D1 | 28 | 335 | 2016-07-30 23:09 | 2016-07-31 00:06 | 220 | 521 | 482 | Pulverizer lube oil system | F490Lost two mills (A&C) - Power to lube oil lost(Grounded 480V Transformer 4A1) | Mill Creek | Derate | Coal | 3 | 2016 | 7 | 0.95 | 0.54885 | 264.5449 | 278.4683 | 278
MC4 | NC | 29 | 4490 | 2016-08-10 20:00 | 2016-08-11 01:03 | 0 | 521 | 482 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Heat Rate Testing (various loads) | Mill Creek | Other | Coal | 3 | 2016 | 8 | 5.05 | 5.05 | 2434.1 | 482 | 482
MC4 | NC | 30 | 1190 | 2016-08-31 20:55 | 2016-09-01 03:02 | 0 | 521 | 482 | Other tube slagging or fouling | FS00Boiler Deslag | Mill Creek | Other | Coal | 3 | 2016 | 8 | 6.1167 | 6.1167 | 2948.2333 | 482 | 482
MC4 | U1 | 31 | 1040 | 2016-09-20 09:36 | 2016-09-24 10:55 | 0 | 521 | 482 | First superheater B | F830Boiler tube leak - superheater | Mill Creek | Outage | Coal | 3 | 2016 | 9 | 97.3167 | 97.3167 | 46906.6333 | 482 | 482
MC4 | U1 | 32 | 380 | 2016-09-24 12:09 | 2016-09-24 12:39 | 0 | 521 | 482 | Light-off (igniter) systems (including fuel supply) | F820'Trip - Loss of Fuel | Mill Creek | Outage | Coal | 3 | 2016 | 9 | 0.5 | 0.5 | 241 | 482 | 482
MC4 | D1 | 33 | 3431 | 2016-09-27 15:10 | 2016-09-27 18:25 | 420 | 521 | 482 | Other feedwater valves | F630'TDBFP Recirc Valve Stuck Open | Mill Creek | Derate | Coal | 3 | 2016 | 9 | 3.25 | 0.63004 | 303.6785 | 93.4395 | 93
MC4 | PO | 34 | 1800 | 2016-09-30 01:23 | 2016-11-07 | 0 | 521 | 482 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | F590Planned Outage | Mill Creek | Other | Coal | 3 | 2016 | 9 | 910.6167 | 910.6167 | 438917.2333 | 482 | 482
MC4 | PE | 35 | 1800 | 2016-11-07 | 2016-11-21 07:48 | 0 | 521 | 482 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | F590Planned Outage Extension | Mill Creek | Other | Coal | 3 | 2016 | 11 | 343.8 | 343.8 | 165711.6 | 482 | 482
MC4 | NC | 36 | 1850 | 2016-11-21 07:48 | 2016-11-23 05:06 | 0 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High silica at cold start-up | Mill Creek | Other | Coal | 3 | 2016 | 11 | 45.3 | 45.3 | 21834.6 | 482 | 482
MC4 | D1 | 37 | 300 | 2016-12-02 17:04 | 2016-12-02 17:50 | 430 | 521 | 482 | Pulverizer motors and drives | F410A Mill Breaker | Mill Creek | Derate | Coal | 3 | 2016 | 12 | 0.76667 | 0.13391 | 64.5442 | 84.1881 | 84
MC4 | D1 | 38 | 260 | 2016-12-10 04:58 | 2016-12-10 05:30 | 385 | 521 | 482 | Primary air fan | F780C Mill PA Fan Bearing Temperature Spiked | Mill Creek | Derate | Coal | 3 | 2016 | 12 | 0.53333 | 0.13922 | 67.1038 | 125.8196 | 126
MC4 | D1 | 39 | 267 | 2016-12-10 07:55 | 2016-12-11 04:29 | 500 | 521 | 482 | Primary air flow instrumentation | F120Air Fuel Flow Issues | Mill Creek | Derate | Coal | 3 | 2016 | 12 | 20.5667 | 0.82898 | 399.5697 | 19.428 | 19
MC4 | D4 | 40 | 510 | 2016-12-11 22:38 | 2016-12-12 00:17 | 400 | 521 | 482 | Main steam relief/safety valves off superheater | F790Set Safeties | Mill Creek | Derate | Coal | 3 | 2016 | 12 | 1.65 | 0.38321 | 184.705 | 111.9424 | 112
MC4 | D1 | 41 | 3344 | 2016-12-21 05:50 | 2016-12-21 09:31 | 450 | 521 | 482 | Deaerator (including level control) | F430Dearator Level Transmitter | Mill Creek | Derate | Coal | 3 | 2016 | 12 | 3.6833 | 0.50195 | 241.9406 | 65.6852 | 66
MC4 | D1 | 42 | 250 | 2016-12-29 11:27 | 2016-12-29 13:35 | 150 | 521 | 482 | Pulverizer feeders | F820Lost 4A/4B Mill feeders | Mill Creek | Derate | Coal | 3 | 2016 | 12 | 2.1333 | 1.5191 | 732.2206 | 343.2284 | 343
MC4 | D1 | 43 | 264 | 2016-12-29 18:30 | 2016-12-29 19:34 | 450 | 521 | 482 | Other primary air fan problems | F720Air flow issues | Mill Creek | Derate | Coal | 3 | 2016 | 12 | 1.0667 | 0.14536 | 70.0642 | 65.6852 | 66
MC4 | D1 | 44 | 250 | 2016-12-29 19:34 | 2016-12-30 07:54 | 510 | 521 | 482 | Pulverizer feeders | F5504E Feeder belt slipping | Mill Creek | Derate | Coal | 3 | 2016 | 12 | 12.3333 | 0.2604 | 125.5112 | 10.1766 | 10
MC4 | D1 | 1 | 250 | 2017-01-05 19:02 | 2017-01-05 19:40 | 406 | 521 | 482 | Pulverizer feeders | F8204C Feeder Tripped | Mill Creek | Derate | Coal | 3 | 2017 | 1 | 0.63333 | 0.1398 | 67.3813 | 106.3916 | 106
MC4 | MO | 2 | 3110 | 2017-01-09 14:25 | 2017-01-10 13:47 | 0 | 521 | 482 | Condenser tube leaks | F540Condenser Tube Leak | Mill Creek | Maintenance | Coal | 3 | 2017 | 1 | 23.3667 | 23.3667 | 11262.7333 | 482 | 482
MC4 | D1 | 3 | 1850 | 2017-01-10 22:20 | 2017-01-11 06:55 | 437 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica From Statup | Mill Creek | Derate | Coal | 3 | 2017 | 1 | 8.5833 | 1.3839 | 667.0288 | 77.7121 | 78
MC4 | D1 | 4 | 1850 | 2017-01-11 06:55 | 2017-01-11 09:18 | 475 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica From Startup | Mill Creek | Derate | Coal | 3 | 2017 | 1 | 2.3833 | 0.21043 | 101.4266 | 42.5566 | 43
MC4 | NC | 5 | 8460 | 2017-01-11 21:22 | 2017-01-12 02:03 | 0 | 521 | 482 | Testing A | F790Low Load RATA Testing | Mill Creek | Other | Coal | 3 | 2017 | 1 | 4.6833 | 4.6833 | 2257.3667 | 482 | 482
MC4 | NC | 6 | 1990 | 2017-01-23 22:30 | 2017-01-24 00:30 | 0 | 521 | 482 | Boiler performance testing (use code 9999 for total unit performance testing) | F7903 Mill Testing - Boiler Tuning | Mill Creek | Other | Coal | 3 | 2017 | 1 | 2 | 2 | 964 | 482 | 482
MC4 | NC | 7 | 1990 | 2017-01-24 00:30 | 2017-01-24 02:30 | 0 | 521 | 482 | Boiler performance testing (use code 9999 for total unit performance testing) | F7903 Mill Testing - Boiler Tuning | Mill Creek | Other | Coal | 3 | 2017 | 1 | 2 | 2 | 964 | 482 | 482
MC4 | NC | 8 | 1990 | 2017-01-24 02:30 | 2017-01-24 04:16 | 0 | 521 | 482 | Boiler performance testing (use code 9999 for total unit performance testing) | F7903 Mill Testing - Boiler Tuning | Mill Creek | Other | Coal | 3 | 2017 | 1 | 1.7667 | 1.7667 | 851.5333 | 482 | 482
MC4 | NC | 9 | 1990 | 2017-01-24 22:00 | 2017-01-25 03:36 | 0 | 521 | 482 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Mill Testing - Boiler Tuning | Mill Creek | Other | Coal | 3 | 2017 | 1 | 5.6 | 5.6 | 2699.2 | 482 | 482
MC4 | NC | 10 | 9999 | 2017-02-06 08:00 | 2017-02-06 13:00 | 0 | 521 | 482 | Total unit performance testing (use appropriate codes for individual component testing) | F790Full Load Capability Testing | Mill Creek | Other | Coal | 3 | 2017 | 2 | 5 | 5 | 2410 | 482 | 482
MC4 | NC | 11 | 1990 | 2017-02-09 10:09 | 2017-02-09 11:20 | 0 | 521 | 482 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Full Load Boiler Tuning | Mill Creek | Other | Coal | 3 | 2017 | 2 | 1.1833 | 1.1833 | 570.3667 | 482 | 482
MC4 | NC | 12 | 1999 | 2017-02-13 08:00 | 2017-02-13 15:33 | 0 | 521 | 482 | Boiler | F790Full Load Boiler Tuning | Mill Creek | Other | Coal | 3 | 2017 | 2 | 7.55 | 7.55 | 3639.1 | 482 | 482
MC4 | U1 | 13 | 4268 | 2017-02-14 02:13 | 2017-02-14 04:11 | 0 | 521 | 482 | Reheat/intercept valve testing | F820Trip During Valve Testing (Under Investigation) | Mill Creek | Outage | Coal | 3 | 2017 | 2 | 1.9667 | 1.9667 | 947.9333 | 482 | 482
MC4 | D1 | 14 | 1850 | 2017-02-14 10:15 | 2017-02-14 12:04 | 420 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170Boiler Chemistry - High Silica After Startup | Mill Creek | Derate | Coal | 3 | 2017 | 2 | 1.8167 | 0.35218 | 169.7485 | 93.4395 | 93
MC4 | D1 | 15 | 260 | 2017-02-20 06:46 | 2017-02-20 07:03 | 380 | 521 | 482 | Primary air fan | F4104C PA Fan breaker issue & 4D-10 igniter malfunctioning | Mill Creek | Derate | Coal | 3 | 2017 | 2 | 0.28333 | 0.076679 | 36.9595 | 130.4453 | 130
MC4 | U1 | 16 | 370 | 2017-02-25 18:00 | 2017-02-26 20:49 | 0 | 521 | 482 | Burner instruments and controls (except light-off) | F820Master Fuel Trip (Lost Flame Scanner) | Mill Creek | Outage | Coal | 3 | 2017 | 2 | 26.8167 | 26.8167 | 12925.6333 | 482 | 482
MC4 | D1 | 17 | 1850 | 2017-02-27 04:52 | 2017-02-27 07:38 | 382 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica From Startup and Scanner Issues | Mill Creek | Derate | Coal | 3 | 2017 | 2 | 2.7667 | 0.73813 | 355.7795 | 128.595 | 129
MC4 | NC | 18 | 9999 | 2017-02-28 08:00 | 2017-02-28 13:26 | 0 | 521 | 482 | Total unit performance testing (use appropriate codes for individual component testing) | F790MATS Testing - Full Load | Mill Creek | Other | Coal | 3 | 2017 | 2 | 5.4333 | 5.4333 | 2618.8667 | 482 | 482
MC4 | NC | 19 | 370 | 2017-03-12 00:58 | 2017-03-12 06:13 | 0 | 521 | 482 | Burner instruments and controls (except light-off) | F590Scanner Tuning - Various Loads | Mill Creek | Other | Coal | 3 | 2017 | 3 | 5.25 | 5.25 | 2530.5 | 482 | 482
MC4 | U1 | 20 | 4268 | 2017-03-25 08:50 | 2017-03-25 08:55 | 0 | 521 | 482 | Reheat/intercept valve testing | F820Trip During Valve Testing (Under Investigation) | Mill Creek | Outage | Coal | 3 | 2017 | 3 | 0.083333 | 0.083333 | 40.1667 | 482 | 482
MC4 | MO | 21 | 1493 | 2017-03-25 08:55 | 2017-03-28 19:48 | 0 | 521 | 482 | Air heater fouling (regenerative) | F660Air Heater Wash | Mill Creek | Maintenance | Coal | 3 | 2017 | 3 | 82.8833 | 82.8833 | 39949.7667 | 482 | 482
MC4 | D1 | 22 | 1850 | 2017-03-29 08:27 | 2017-03-29 09:42 | 473 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica From Startup | Mill Creek | Derate | Coal | 3 | 2017 | 3 | 1.25 | 0.11516 | 55.5086 | 44.4069 | 44
MC4 | D1 | 23 | 1850 | 2017-03-29 09:42 | 2017-03-29 12:10 | 490 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica From Startup | Mill Creek | Derate | Coal | 3 | 2017 | 3 | 2.4667 | 0.14677 | 70.7427 | 28.6795 | 29
MC4 | U1 | 24 | 4810 | 2017-03-30 14:49 | 2017-04-02 08:34 | 0 | 521 | 482 | Generator output breaker | F820Generator Lockout Trip (Electrical Ground Indication) | Mill Creek | Outage | Coal | 3 | 2017 | 3 | 65.75 | 65.75 | 31691.5 | 482 | 482
MC4 | U1 | 25 | 800 | 2017-04-02 09:22 | 2017-04-02 11:06 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820Drum Level Trip | Mill Creek | Outage | Coal | 3 | 2017 | 4 | 1.7333 | 1.7333 | 835.4667 | 482 | 482
MC4 | D1 | 26 | 1850 | 2017-04-02 19:06 | 2017-04-02 19:50 | 450 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica From Startup | Mill Creek | Derate | Coal | 3 | 2017 | 4 | 0.73333 | 0.099936 | 48.1692 | 65.6852 | 66
MC4 | D1 | 27 | 1850 | 2017-04-02 19:50 | 2017-04-02 22:18 | 470 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica From Startup | Mill Creek | Derate | Coal | 3 | 2017 | 4 | 2.4667 | 0.24146 | 116.3831 | 47.1823 | 47
MC4 | D4 | 28 | 4268 | 2017-04-03 20:00 | 2017-04-03 21:20 | 200 | 521 | 482 | Reheat/intercept valve testing | F790Turbine Valve Testing | Mill Creek | Derate | Coal | 3 | 2017 | 4 | 1.3333 | 0.8215 | 395.9616 | 296.9712 | 297
MC4 | U1 | 29 | 4268 | 2017-04-07 00:50 | 2017-04-07 03:41 | 0 | 521 | 482 | Reheat/intercept valve testing | F820Trip During Valve Testing | Mill Creek | Outage | Coal | 3 | 2017 | 4 | 2.85 | 2.85 | 1373.7 | 482 | 482
MC4 | D1 | 30 | 1850 | 2017-04-07 09:41 | 2017-04-07 14:26 | 390 | 521 | 482 | Boiler water condition (not feedwater water quality) | F170High Silica From Startup | Mill Creek | Derate | Coal | 3 | 2017 | 4 | 4.75 | 1.1943 | 575.6708 | 121.1939 | 121
MC4 | NC | 31 | 1990 | 2017-04-20 01:04 | 2017-04-20 03:41 | 0 | 521 | 482 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Boiler Tuning - Various Loads | Mill Creek | Other | Coal | 3 | 2017 | 4 | 2.6167 | 2.6167 | 1261.2333 | 482 | 482
MC4 | U1 | 32 | 4266 | 2017-05-08 01:46 | 2017-05-08 03:03 | 0 | 521 | 482 | Main stop valve testing | F820Drum Level Trip (During Main Stop Valve Testing) | Mill Creek | Outage | Coal | 3 | 2017 | 5 | 1.2833 | 1.2833 | 618.5667 | 482 | 482
MC4 | U1 | 33 | 4268 | 2017-05-12 21:07 | 2017-05-12 21:22 | 0 | 521 | 482 | Reheat/intercept valve testing | F820Trip During Valve Testing | Mill Creek | Outage | Coal | 3 | 2017 | 5 | 0.25 | 0.25 | 120.5 | 482 | 482
MC4 | MO | 34 | 4263 | 2017-05-12 21:22 | 2017-05-13 16:41 | 0 | 521 | 482 | Reheat stop valves | F610Reheat and Stop Valve Maintenance | Mill Creek | Maintenance | Coal | 3 | 2017 | 5 | 19.3167 | 19.3167 | 9310.6333 | 482 | 482
MC4 | U1 | 35 | 4810 | 2017-05-19 02:11 | 2017-05-19 07:58 | 0 | 521 | 482 | Generator output breaker | F820Generator Lockout Trip | Mill Creek | Outage | Coal | 3 | 2017 | 5 | 5.7833 | 5.7833 | 2787.5667 | 482 | 482
MC4 | D1 | 36 | 3110 | 2017-05-30 21:45 | 2017-05-31 22:04 | 370 | 521 | 482 | Condenser tube leaks | F540High Silica - Suspected Condenser Leak | Mill Creek | Derate | Coal | 3 | 2017 | 5 | 24.3167 | 7.0476 | 3396.959 | 139.6967 | 140
MC4 | D1 | 37 | 3110 | 2017-05-31 22:04 | 2017-06-01 04:10 | 391 | 521 | 482 | Condenser tube leaks | F540High Silica - Suspected Condenser Leak | Mill Creek | Derate | Coal | 3 | 2017 | 5 | 6.1 | 1.5221 | 733.6392 | 120.2687 | 120
MC4 | D1 | 38 | 100 | 2017-06-21 07:24 | 2017-06-21 07:33 | 356 | 521 | 482 | Bunker gates | F520Coal Swing Valves | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 0.15 | 0.047505 | 22.8973 | 152.6488 | 153
MC4 | D1 | 39 | 3110 | 2017-06-27 07:28 | 2017-06-27 12:32 | 418 | 521 | 482 | Condenser tube leaks | F540High Silica - Condenser Leak | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 5.0667 | 1.0017 | 482.8018 | 95.2898 | 95
MC4 | U1 | 40 | 3110 | 2017-06-27 12:32 | 2017-06-28 14:01 | 0 | 521 | 482 | Condenser tube leaks | F830Condenser Leak | Mill Creek | Outage | Coal | 3 | 2017 | 6 | 25.4833 | 25.4833 | 12282.9667 | 482 | 482
MC4 | D1 | 41 | 3110 | 2017-06-28 22:18 | 2017-06-29 05:32 | 275 | 521 | 482 | Condenser tube leaks | F540High Silica - Startup After Condenser Leak | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 7.2333 | 3.4154 | 1646.2012 | 227.5854 | 228
MC4 | D1 | 42 | 3110 | 2017-06-29 05:32 | 2017-06-29 18:53 | 350 | 521 | 482 | Condenser tube leaks | F540High Silica - Startup After Condenser Leak | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 13.35 | 4.3817 | 2111.9649 | 158.1996 | 158
MC4 | D1 | 43 | 3110 | 2017-06-29 18:53 | 2017-06-29 19:32 | 250 | 521 | 482 | Condenser tube leaks | F540High Silica - Startup After Condenser Leak (A,E & D Mill Issues) | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 0.65 | 0.3381 | 162.9641 | 250.714 | 251
MC4 | D1 | 44 | 3110 | 2017-06-29 19:32 | 2017-06-30 05:30 | 385 | 521 | 482 | Condenser tube leaks | F540High Silica - Startup After Condenser Leak (A Mill Issue) | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 9.9667 | 2.6017 | 1254.0018 | 125.8196 | 126
MC4 | D1 | 45 | 3110 | 2017-06-30 05:30 | 2017-06-30 15:36 | 460 | 521 | 482 | Condenser tube leaks | F540High Silica - Startup After Condenser Leak | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 10.1 | 1.1825 | 569.9812 | 56.4338 | 56
MC4 | D1 | 46 | 3110 | 2017-06-30 15:36 | 2017-06-30 19:58 | 500 | 521 | 482 | Condenser tube leaks | F540High Silica - Startup After Condenser Leak | Mill Creek | Derate | Coal | 3 | 2017 | 6 | 4.3667 | 0.17601 | 84.8357 | 19.428 | 19
MC4 | D4 | 47 | 300 | 2017-07-23 22:00 | 2017-07-24 02:37 | 370 | 521 | 482 | Pulverizer motors and drives | F5304D Mill Motor Bearing Inspection & 4A Mill Maintenance | Mill Creek | Derate | Coal | 3 | 2017 | 7 | 4.6167 | 1.338 | 644.9333 | 139.6967 | 140
MC4 | D4 | 48 | 8620 | 2017-07-29 00:35 | 2017-07-29 04:38 | 300 | 521 | 482 | Mercury Abatement Equipment | F610FGD Controls - Nalco System Installation | Mill Creek | Derate | Coal | 3 | 2017 | 7 | 4.05 | 1.7179 | 828.0501 | 204.4568 | 204
MC4 | PO | 49 | 1801 | 2017-10-27 23:31 | 2017-11-26 | 0 | 521 | 482 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Planned Outage - Fall 2017 | Mill Creek | Other | Coal | 3 | 2017 | 10 | 696.4833 | 696.4833 | 335704.9667 | 482 | 482
MC4 | PE | 50 | 1801 | 2017-11-26 | 2017-11-29 04:13 | 0 | 521 | 482 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Planned Outage Extension - Fall 2017 | Mill Creek | Other | Coal | 3 | 2017 | 11 | 76.2167 | 76.2167 | 36736.4333 | 482 | 482
MC4 | U1 | 51 | 520 | 2017-11-29 04:47 | 2017-11-30 13:16 | 0 | 521 | 482 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | F540Steam Leaks (Blowdown Tank & Stop Valve Drain) | Mill Creek | Outage | Coal | 3 | 2017 | 11 | 32.4833 | 32.4833 | 15656.9667 | 482 | 482
MC4 | NC | 52 | 4842 | 2017-12-05 15:52 | 2017-12-05 17:36 | 0 | 521 | 482 | Reactive and capability testing | F790MOD 36 Testing - Out of AGC | Mill Creek | Other | Coal | 3 | 2017 | 12 | 1.7333 | 1.7333 | 835.4667 | 482 | 482
MC4 | U1 | 53 | 3700 | 2017-12-06 14:35 | 2017-12-06 17:01 | 0 | 521 | 482 | Powerhouse switchyard (non generating unit equipment) | F820Generator Protective Trip - Switchyard Work | Mill Creek | Outage | Coal | 3 | 2017 | 12 | 2.4333 | 2.4333 | 1172.8667 | 482 | 482
MC4 | D1 | 54 | 1850 | 2017-12-06 23:06 | 2017-12-07 00:40 | 390 | 521 | 482 | Boiler water condition (not feedwater water quality) | FA00High Silica From Startup | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 1.5667 | 0.39392 | 189.8704 | 121.1939 | 121
MC4 | D1 | 55 | 3632 | 2017-12-11 18:45 | 2017-12-12 03:00 | 500 | 521 | 482 | 480-volt conductors and buses | F490Cooling Tower Fan Bus Issue | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 8.25 | 0.33253 | 160.2812 | 19.428 | 19
MC4 | D1 | 56 | 1400 | 2017-12-12 06:52 | 2017-12-12 09:37 | 517 | 521 | 482 | Forced draft fans | F660FD Fan Maxed Out | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 2.75 | 0.021113 | 10.1766 | 3.7006 | 4
MC4 | D1 | 57 | 3415 | 2017-12-12 09:37 | 2017-12-12 12:10 | 300 | 521 | 482 | Feedwater pump/drive lube oil system | F6604A EHC Pump | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 2.55 | 1.0817 | 521.3649 | 204.4568 | 204
MC4 | D4 | 58 | 3670 | 2017-12-15 23:55 | 2017-12-16 00:04 | 300 | 521 | 482 | 12kV transformers | F4304A2 Main Aux Feed - Replaced Fuse Holder | Mill Creek | Derate | Coal | 3 | 2017 | 12 | 0.15 | 0.063628 | 30.6685 | 204.4568 | 204
MC4 | D4 | 1 | 1190 | 2018-01-05 20:30 | 2018-01-06 02:33 | 300 | 521 | 482 | Other tube slagging or fouling | FS00Boiler Deslag | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 6.05 | 2.5663 | 1236.9637 | 204.4568 | 204
MC4 | D4 | 2 | 1190 | 2018-01-06 19:40 | 2018-01-07 01:30 | 285 | 521 | 482 | Other tube slagging or fouling | FS00Boiler Deslag | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 5.8333 | 2.6424 | 1273.6148 | 218.334 | 218
MC4 | D4 | 3 | 1190 | 2018-01-07 12:30 | 2018-01-07 18:00 | 300 | 521 | 482 | Other tube slagging or fouling | FS00Boiler Deslag | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 5.5 | 2.333 | 1124.5125 | 204.4568 | 204
MC4 | D4 | 4 | 1190 | 2018-01-07 18:00 | 2018-01-08 01:00 | 285 | 521 | 482 | Other tube slagging or fouling | FS00Boiler Deslag | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 7 | 3.1708 | 1528.3378 | 218.334 | 218
MC4 | NC | 5 | 1190 | 2018-01-08 21:55 | 2018-01-09 03:50 | 0 | 521 | 482 | Other tube slagging or fouling | FS00Boiler Deslag | Mill Creek | Other | Coal | 3 | 2018 | 1 | 5.9167 | 5.9167 | 2851.8333 | 482 | 482
MC4 | NC | 6 | 1190 | 2018-01-09 23:00 | 2018-01-10 04:00 | 0 | 521 | 482 | Other tube slagging or fouling | FS00Boiler Deslag | Mill Creek | Other | Coal | 3 | 2018 | 1 | 5 | 5 | 2410 | 482 | 482
MC4 | NC | 7 | 1190 | 2018-01-10 22:00 | 2018-01-11 04:00 | 0 | 521 | 482 | Other tube slagging or fouling | FS00Boiler Deslag | Mill Creek | Other | Coal | 3 | 2018 | 1 | 6 | 6 | 2892 | 482 | 482
MC4 | NC | 8 | 1190 | 2018-01-11 06:40 | 2018-01-11 20:00 | 0 | 521 | 482 | Other tube slagging or fouling | FS00Boiler Deslag - Top Mills Off | Mill Creek | Other | Coal | 3 | 2018 | 1 | 13.3333 | 13.3333 | 6426.6667 | 482 | 482
MC4 | NC | 9 | 1190 | 2018-01-11 20:00 | 2018-01-12 05:00 | 0 | 521 | 482 | Other tube slagging or fouling | FS00Boiler Deslag | Mill Creek | Other | Coal | 3 | 2018 | 1 | 9 | 9 | 4338 | 482 | 482
MC4 | NC | 10 | 1190 | 2018-01-15 20:00 | 2018-01-16 03:49 | 0 | 521 | 482 | Other tube slagging or fouling | FS00Boiler Deslag | Mill Creek | Other | Coal | 3 | 2018 | 1 | 7.8167 | 7.8167 | 3767.6333 | 482 | 482
MC4 | D1 | 11 | 1455 | 2018-01-19 19:15 | 2018-01-20 02:08 | 510 | 521 | 482 | Induced draft fans | F660ID Fan Suction Pressure | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 6.8833 | 0.14533 | 70.0488 | 10.1766 | 10
MC4 | MO | 12 | 1493 | 2018-01-20 02:08 | 2018-01-23 | 0 | 521 | 482 | Air heater fouling (regenerative) | F660Air Pre-Heater Wash | Mill Creek | Maintenance | Coal | 3 | 2018 | 1 | 69.8667 | 69.8667 | 33675.7333 | 482 | 482
MC4 | ME | 13 | 1493 | 2018-01-23 | 2018-01-23 03:25 | 0 | 521 | 482 | Air heater fouling (regenerative) | F660Air Pre-Heater Wash (Extension) | Mill Creek | Maintenance | Coal | 3 | 2018 | 1 | 3.4167 | 3.4167 | 1646.8333 | 482 | 482
MC4 | U1 | 14 | 800 | 2018-01-23 03:45 | 2018-01-23 04:24 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820Low Drum Level Trip | Mill Creek | Outage | Coal | 3 | 2018 | 1 | 0.65 | 0.65 | 313.3 | 482 | 482
MC4 | D1 | 15 | 1400 | 2018-01-23 16:32 | 2018-01-24 07:13 | 500 | 521 | 482 | Forced draft fans | F660Air Flow (FD Fans Maxed Out) | Mill Creek | Derate | Coal | 3 | 2018 | 1 | 14.6833 | 0.59184 | 285.2681 | 19.428 | 19
MC4 | MO | 16 | 1495 | 2018-02-08 23:16 | 2018-02-11 17:02 | 0 | 521 | 482 | Other air heater fouling (heat pipe | F660Clean Plugged WCAHs | Mill Creek | Maintenance | Coal | 3 | 2018 | 2 | 65.7667 | 65.7667 | 31699.5333 | 482 | 482
MC4 | NC | 17 | 1471 | 2018-02-16 23:00 | 2018-02-17 00:43 | 0 | 521 | 482 | Induced draft fan motors - variable speed | F5304A ID Fan VFD Cooling Water Pump Check | Mill Creek | Other | Coal | 3 | 2018 | 2 | 1.7167 | 1.7167 | 827.4333 | 482 | 482
MC4 | U1 | 18 | 800 | 2018-02-25 06:50 | 2018-02-25 08:50 | 0 | 521 | 482 | Drums and drum internals (single drum only) | F820Drum Level Trip - Low Level | Mill Creek | Outage | Coal | 3 | 2018 | 2 | 2 | 2 | 964 | 482 | 482
MC4 | NC | 19 | 1471 | 2018-02-27 09:02 | 2018-02-27 09:18 | 0 | 521 | 482 | Induced draft fan motors - variable speed | F5304B ID Fan VFD Cooling Water Pump Check | Mill Creek | Other | Coal | 3 | 2018 | 2 | 0.26667 | 0.26667 | 128.5333 | 482 | 482
MC4 | MO | 20 | 1493 | 2018-03-02 23:35 | 2018-03-06 | 0 | 521 | 482 | Air heater fouling (regenerative) | F660Air Pre-Heater Wash | Mill Creek | Maintenance | Coal | 3 | 2018 | 3 | 72.4167 | 72.4167 | 34904.8333 | 482 | 482
MC4 | ME | 21 | 1493 | 2018-03-06 | 2018-03-07 02:33 | 0 | 521 | 482 | Air heater fouling (regenerative) | F660Air Pre-Heater Wash (Extension) | Mill Creek | Maintenance | Coal | 3 | 2018 | 3 | 26.55 | 26.55 | 12797.1 | 482 | 482
MC4 | SF | 22 | 8280 | 2018-03-07 02:33 | 2018-03-07 07:56 | 0 | 521 | 482 | Reagent feed piping | F120Plugged Limestone Feed (SUF) | Mill Creek | Outage | Coal | 3 | 2018 | 3 | 5.3833 | 5.3833 | 2594.7667 | 482 | 482
MC4 | D4 | 23 | 3211 | 2018-04-20 22:00 | 2018-04-21 04:00 | 290 | 521 | 482 | Circulating water pump motors | F7804A CTP Maintenance | Mill Creek | Derate | Coal | 3 | 2018 | 4 | 6 | 2.6603 | 1282.2495 | 213.7083 | 214
TC1 | U2 | 2 | 1000 | 2013-01-01 | 2013-01-01 02:42 | 0 | 530 | 493 | Waterwall (Furnace wall) A | F540The unit was removed from service to repair the lower slope boiler tube leak. The | Trimble | Outage | Coal | 3 | 2013 | 1 | 2.7 | 2.7 | 1331.1 | 493 | 493
TC1 | NC | 1 | 1850 | 2013-01-01 02:42 | 2013-01-01 08:43 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00TC-1 was on line and ramping up. The load was held down some due to silica from th | Trimble | Other | Coal | 3 | 2013 | 1 | 6.0167 | 6.0167 | 2966.2167 | 493 | 493
TC1 | NC | 3 | 4261 | 2013-01-06 01:00 | 2013-01-06 01:08 | 0 | 530 | 493 | Control valves | F790This de-rate was for testing of control valves. This is a weekly test of the contr | Trimble | Other | Coal | 3 | 2013 | 1 | 0.13333 | 0.13333 | 65.7333 | 493 | 493
TC1 | U1 | 4 | 1000 | 2013-01-09 22:27 | 2013-01-09 23:27 | 0 | 530 | 493 | Waterwall (Furnace wall) A | F540The unit tripped off when we were removing the unit from service for boiler tube r | Trimble | Outage | Coal | 3 | 2013 | 1 | 1 | 1 | 493 | 493 | 493
TC1 | MO | 5 | 1000 | 2013-01-09 23:27 | 2013-01-14 06:00 | 0 | 530 | 493 | Waterwall (Furnace wall) A | F540This outage was to replace the tube panels on the East side of the lower slope. Th | Trimble | Maintenance | Coal | 3 | 2013 | 1 | 102.55 | 102.55 | 50557.15 | 493 | 493
TC1 | ME | 6 | 1000 | 2013-01-14 06:00 | 2013-01-14 23:56 | 0 | 530 | 493 | Waterwall (Furnace wall) A | F540This outage was to replace the tube panels on the East side of the lower slope. Th | Trimble | Maintenance | Coal | 3 | 2013 | 1 | 17.9333 | 17.9333 | 8841.1333 | 493 | 493
TC1 | NC | 8 | 1850 | 2013-01-14 23:56 | 2013-01-15 14:10 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00TC-1 was on line and ramping up. The load was held down some due to silica from th | Trimble | Other | Coal | 3 | 2013 | 1 | 14.2333 | 14.2333 | 7017.0333 | 493 | 493
TC1 | D1 | 9 | 310 | 2013-01-16 05:56 | 2013-01-16 07:15 | 510 | 530 | 493 | Pulverizer mills | FR00TC1 coal mill A had a fire and D coal mill was unavailable and required a unit de- | Trimble | Derate | Coal | 3 | 2013 | 1 | 1.3167 | 0.049686 | 24.495 | 18.6038 | 19
TC1 | D1 | 10 | 250 | 2013-01-17 06:04 | 2013-01-17 06:40 | 510 | 530 | 493 | Pulverizer feeders | F820TC1 had the 1C coal feeder belt track north tripped the feeder. Maintenance repla | Trimble | Derate | Coal | 3 | 2013 | 1 | 0.6 | 0.022642 | 11.1623 | 18.6038 | 19
TC1 | D4 | 11 | 360 | 2013-01-17 07:38 | 2013-01-17 08:40 | 510 | 530 | 493 | Burners | F780The 1D burner was getting hot, removed mill and inspected for cause | Trimble | Derate | Coal | 3 | 2013 | 1 | 1.0333 | 0.038994 | 19.2239 | 18.6038 | 19
TC1 | D1 | 12 | 310 | 2013-01-19 08:18 | 2013-01-19 11:43 | 500 | 530 | 493 | Pulverizer mills | FR00A mill fire caused derate. Unable to put A mill back on after washing it out due | Trimble | Derate | Coal | 3 | 2013 | 1 | 3.4167 | 0.1934 | 95.3443 | 27.9057 | 28
TC1 | U1 | 13 | 3110 | 2013-01-20 09:59 | 2013-01-21 04:58 | 0 | 530 | 493 | Condenser tube leaks | F540Condenser tube leaks found in LP 1A1 condenser. 15 tubes plugged and unit returne | Trimble | Outage | Coal | 3 | 2013 | 1 | 18.9833 | 18.9833 | 9358.7833 | 493 | 493
TC1 | NC | 14 | 1850 | 2013-01-21 04:58 | 2013-01-21 15:08 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Unit was online and ramping. Held on silica restriction. Followed the condenser | Trimble | Other | Coal | 3 | 2013 | 1 | 10.1667 | 10.1667 | 5012.1667 | 493 | 493
TC1 | D1 | 15 | 310 | 2013-01-22 22:02 | 2013-01-22 22:32 | 480 | 530 | 493 | Pulverizer mills | FR00A coal caught fire and resulted in unit derate to 480 MW | Trimble | Derate | Coal | 3 | 2013 | 1 | 0.5 | 0.04717 | 23.2547 | 46.5094 | 47
TC1 | D1 | 16 | 250 | 2013-01-24 07:30 | 2013-01-24 08:33 | 490 | 530 | 493 | Pulverizer feeders | F820Unit 1 A coal mill feeder tripped causing the A mill to be tripped resulting in a | Trimble | Derate | Coal | 3 | 2013 | 1 | 1.05 | 0.079245 | 39.0679 | 37.2075 | 37
TC1 | D1 | 17 | 360 | 2013-01-30 22:25 | 2013-01-30 23:00 | 450 | 530 | 493 | Burners | F8201B3 coal burner had a fire which ended up tripping the B coal mill. Derate requir | Trimble | Derate | Coal | 3 | 2013 | 1 | 0.58333 | 0.08805 | 43.4088 | 74.4151 | 74
TC1 | D1 | 18 | 3710 | 2013-02-05 01:10 | 2013-02-05 01:46 | 500 | 530 | 493 | Transmission line (connected to powerhouse switchyard to 1st Substation) | F700At 0106 there was an event at the switchyard. The 4542 A-phase coupling capacitor/ | Trimble | Derate | Coal | 3 | 2013 | 2 | 0.6 | 0.033962 | 16.7434 | 27.9057 | 28
TC1 | D4 | 19 | 920 | 2013-02-16 | 2013-02-16 04:00 | 300 | 530 | 493 | Other slag and ash removal problems A | FC00Unit 1 was derated to 300MW for deslag of the boiler. This derate was also used t | Trimble | Derate | Coal | 3 | 2013 | 2 | 4 | 1.7358 | 855.7736 | 213.9434 | 214
TC1 | D1 | 20 | 310 | 2013-02-20 05:53 | 2013-02-20 06:26 | 500 | 530 | 493 | Pulverizer mills | FR00Unit 1 had the B coal mill on fire and was taken offline and load reduced to 500MW | Trimble | Derate | Coal | 3 | 2013 | 2 | 0.55 | 0.031132 | 15.3481 | 27.9057 | 28
TC1 | D1 | 21 | 310 | 2013-02-20 06:26 | 2013-02-20 09:39 | 520 | 530 | 493 | Pulverizer mills | FR00Unit 1 was increased to 520MW while the previous work was being conducted on the B | Trimble | Derate | Coal | 3 | 2013 | 2 | 3.2167 | 0.060692 | 29.9211 | 9.3019 | 9
TC1 | D1 | 22 | 4899 | 2013-02-27 07:14 | 2013-02-27 07:20 | 527 | 530 | 493 | Other miscellaneous generator problems | F780The generator field temperature indication began reading high and came into alarm | Trimble | Derate | Coal | 3 | 2013 | 2 | 0.1 | 0.00056604 | 0.27906 | 2.7906 | 3
TC1 | D1 | 23 | 4899 | 2013-02-27 07:20 | 2013-02-27 09:25 | 507 | 530 | 493 | Other miscellaneous generator problems | F780Generator field temperature remained high. Unit was reduced another 20MW bringing | Trimble | Derate | Coal | 3 | 2013 | 2 | 2.0833 | 0.090409 | 44.5715 | 21.3943 | 21
TC1 | NC | 24 | 1305 | 2013-03-02 00:01 | 2013-03-02 05:00 | 0 | 530 | 493 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | FS00U1 was reduced to 250 MW for a planned de-slag of the boiler. | Trimble | Other | Coal | 3 | 2013 | 3 | 4.9833 | 4.9833 | 2456.7833 | 493 | 493
TC1 | D1 | 25 | 760 | 2013-03-02 05:58 | 2013-03-02 08:11 | 525 | 530 | 493 | Boiler recirculation valves | F690The 1A TDBFP valve would not operate properly and was taken out of service to inve | Trimble | Derate | Coal | 3 | 2013 | 3 | 2.2167 | 0.020912 | 10.3096 | 4.6509 | 5
TC1 | D1 | 26 | 310 | 2013-03-10 11:10 | 2013-03-10 13:00 | 515 | 530 | 493 | Pulverizer mills | F180The D mill on Unit 1 lit off and required the mill to be shut down in order for th | Trimble | Derate | Coal | 3 | 2013 | 3 | 1.8333 | 0.051887 | 25.5802 | 13.9528 | 14
TC1 | D1 | 27 | 340 | 2013-03-12 04:20 | 2013-03-12 05:00 | 510 | 530 | 493 | Other pulverizer problems | F060The solenoid on the 1F coal mill broke causing the derate. The solenoid grounded | Trimble | Derate | Coal | 3 | 2013 | 3 | 0.66667 | 0.025157 | 12.4025 | 18.6038 | 19
TC1 | D1 | 28 | 340 | 2013-03-12 05:00 | 2013-03-12 07:53 | 520 | 530 | 493 | Other pulverizer problems | F060Operations was able to increase unit load by 10MW (up to 520MW) after F Mill was r | Trimble | Derate | Coal | 3 | 2013 | 3 | 2.8833 | 0.054403 | 26.8204 | 9.3019 | 9
TC1 | D1 | 29 | 340 | 2013-03-18 09:30 | 2013-03-18 12:20 | 515 | 530 | 493 | Other pulverizer problems | F540Removed the 1B Coal Mill from service and carded for inspection after water backed | Trimble | Derate | Coal | 3 | 2013 | 3 | 2.8333 | 0.080189 | 39.533 | 13.9528 | 14
TC1 | NC | 30 | 1305 | 2013-03-23 23:00 | 2013-03-24 05:00 | 0 | 530 | 493 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | FS00Unit was derated to 350MW to perform a deslag. Unit load was readily available sh | Trimble | Other | Coal | 3 | 2013 | 3 | 6 | 6 | 2958 | 493 | 493
TC1 | D1 | 31 | 1360 | 2013-03-27 22:00 | 2013-03-27 23:21 | 300 | 530 | 493 | Boiler drains system | F540Variable derate moving into forced outage due to SH-9 drain line leak | Trimble | Derate | Coal | 3 | 2013 | 3 | 1.35 | 0.58585 | 288.8236 | 213.9434 | 214
TC1 | U1 | 32 | 1360 | 2013-03-27 23:21 | 2013-03-28 16:04 | 0 | 530 | 493 | Boiler drains system | F540Forced outage due to SH-9 drain line leak, repairs were completed and changed into | Trimble | Outage | Coal | 3 | 2013 | 3 | 16.7167 | 16.7167 | 8241.3167 | 493 | 493
TC1 | MO | 33 | 1489 | 2013-03-28 16:04 | 2013-03-30 22:02 | 0 | 530 | 493 | Air heater (heat pipe | F320Maintenance outage in order to perform an air heater wash after the forced outage. | Trimble | Maintenance | Coal | 3 | 2013 | 3 | 53.9667 | 53.9667 | 26605.5667 | 493 | 493
TC1 | D1 | 34 | 3641 | 2013-04-02 08:00 | 2013-04-02 08:25 | 450 | 530 | 493 | AC Circuit breakers | F700Problems with breaker MOD 4511. One phase shorted out, switched to reserve. Lowere | Trimble | Derate | Coal | 3 | 2013 | 4 | 0.41667 | 0.062893 | 31.0063 | 74.4151 | 74
TC1 | D1 | 35 | 3431 | 2013-04-02 23:00 | 2013-04-03 04:31 | 525 | 530 | 493 | Other feedwater valves | F610The unit was derated to 525 MW to allow TDBFP swapping so I/E could make logic cha | Trimble | Derate | Coal | 3 | 2013 | 4 | 5.5167 | 0.052044 | 25.6577 | 4.6509 | 5
TC1 | D1 | 36 | 3431 | 2013-04-03 05:40 | 2013-04-03 07:35 | 525 | 530 | 493 | Other feedwater valves | F590There was an issue with the TDBFP-A recirc valve when bringing the unit to full lo | Trimble | Derate | Coal | 3 | 2013 | 4 | 1.9167 | 0.018082 | 8.9143 | 4.6509 | 5
TC1 | D1 | 37 | 310 | 2013-04-21 12:51 | 2013-04-21 13:51 | 525 | 530 | 493 | Pulverizer mills | FR001B Coal mill fire required mill swap, however the O/S mill, Mill 1A, had issues ge | Trimble | Derate | Coal | 3 | 2013 | 4 | 1 | 0.009434 | 4.6509 | 4.6509 | 5
TC1 | NC | 38 | 4269 | 2013-05-01 | 2013-05-01 01:00 | 0 | 530 | 493 | Other turbine valves | F530Planned de-rate (non-curtailing) to inspect turbine valves (490 MW) | Trimble | Other | Coal | 3 | 2013 | 5 | 1 | 1 | 493 | 493 | 493
TC1 | D4 | 39 | 3410 | 2013-05-03 20:00 | 2013-05-03 22:40 | 525 | 530 | 493 | Feedwater pump | F5401A TDBFP has had an oil leak. The derate was to attempt to repair the valve. A ne | Trimble | Derate | Coal | 3 | 2013 | 5 | 2.6667 | 0.025157 | 12.4025 | 4.6509 | 5
TC1 | U1 | 40 | 4609 | 2013-05-03 22:40 | 2013-05-04 18:21 | 0 | 530 | 493 | Other exciter problems | F820TC1 began having exciter field voltage issues going HI and LOW. Megavars were als | Trimble | Outage | Coal | 3 | 2013 | 5 | 19.6833 | 19.6833 | 9703.8833 | 493 | 493
TC1 | NC | 41 | 1850 | 2013-05-04 18:21 | 2013-05-05 04:28 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Unit was on-line and ramping and hold was placed for silica | Trimble | Other | Coal | 3 | 2013 | 5 | 10.1167 | 10.1167 | 4987.5167 | 493 | 493
TC1 | NC | 42 | 4267 | 2013-05-12 01:00 | 2013-05-12 01:15 | 0 | 530 | 493 | Control valve testing | F790Completed a valve test on unit one turbine valves to ensure working order. #3 and | Trimble | Other | Coal | 3 | 2013 | 5 | 0.25 | 0.25 | 123.25 | 493 | 493
TC1 | D1 | 43 | 310 | 2013-05-13 08:00 | 2013-05-13 08:25 | 525 | 530 | 493 | Pulverizer mills | F780Unit 1 B Coal Mill came in at high temperature. More information in following even | Trimble | Derate | Coal | 3 | 2013 | 5 | 0.41667 | 0.0039308 | 1.9379 | 4.6509 | 5
TC1 | D1 | 44 | 310 | 2013-05-13 08:25 | 2013-05-13 09:55 | 515 | 530 | 493 | Pulverizer mills | F780TC1 B Coal mill continued to increase in temperature and load was reduced further. | Trimble | Derate | Coal | 3 | 2013 | 5 | 1.5 | 0.042453 | 20.9292 | 13.9528 | 14
TC1 | D1 | 45 | 310 | 2013-05-13 09:55 | 2013-05-13 11:13 | 530 | 530 | 493 | Pulverizer mills | FR00TC1 B Coal mill caught fire as temperatures continued to rise. C Mill was brought | Trimble | Derate | Coal | 3 | 2013 | 5 | 1.3 | 0 | 0 | 0 | 0
TC1 | NC | 46 | 4267 | 2013-05-18 22:30 | 2013-05-18 23:03 | 0 | 530 | 493 | Control valve testing | F790Performed weekly valve test over the weekend. | Trimble | Other | Coal | 3 | 2013 | 5 | 0.55 | 0.55 | 271.15 | 493 | 493
TC1 | U1 | 47 | 800 | 2013-05-25 11:20 | 2013-05-25 15:41 | 0 | 530 | 493 | Drums and drum internals (single drum only) | F820When attempting to isolate the north hydrastep which was leaking and in need of re | Trimble | Outage | Coal | 3 | 2013 | 5 | 4.35 | 4.35 | 2144.55 | 493 | 493
TC1 | NC | 48 | 1850 | 2013-05-25 15:41 | 2013-05-25 23:15 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Following the MFT and before returning to full-load the unit was placed on a silic | Trimble | Other | Coal | 3 | 2013 | 5 | 7.5667 | 7.5667 | 3730.3667 | 493 | 493
TC1 | D1 | 49 | 3410 | 2013-06-13 12:15 | 2013-06-14 01:37 | 525 | 530 | 493 | Feedwater pump | F5401A TDBFP suction header annubar found leaking. Repaired with pump O/S and returne | Trimble | Derate | Coal | 3 | 2013 | 6 | 13.3667 | 0.1261 | 62.1676 | 4.6509 | 5
TC1 | NC | 50 | 4267 | 2013-06-16 01:00 | 2013-06-16 01:20 | 0 | 530 | 493 | Control valve testing | F790Weekly valve test conducted over weekend. Non-curtailing load drop to 500MW to co | Trimble | Other | Coal | 3 | 2013 | 6 | 0.33333 | 0.33333 | 164.3333 | 493 | 493
TC1 | NC | 51 | 4267 | 2013-06-22 01:00 | 2013-06-22 01:50 | 0 | 530 | 493 | Control valve testing | F790Weekly valve test for Unit 1. | Trimble | Other | Coal | 3 | 2013 | 6 | 0.83333 | 0.83333 | 410.8333 | 493 | 493
TC1 | D4 | 52 | 3410 | 2013-06-28 21:00 | 2013-06-29 09:00 | 525 | 530 | 493 | Feedwater pump | F590Planned maintenance to repair 1A TDBFP. | Trimble | Derate | Coal | 3 | 2013 | 6 | 12 | 0.11321 | 55.8113 | 4.6509 | 5
TC1 | NC | 53 | 4267 | 2013-06-29 | 2013-06-29 01:08 | 0 | 530 | 493 | Control valve testing | F790Weekly valve test for Unit 1. | Trimble | Other | Coal | 3 | 2013 | 6 | 1.1333 | 1.1333 | 558.7333 | 493 | 493
TC1 | D4 | 54 | 3110 | 2013-07-05 23:00 | 2013-07-05 23:26 | 300 | 530 | 493 | Condenser tube leaks | F530Variable de-rate to come offline for a condenser inspection due to potential tube | Trimble | Derate | Coal | 3 | 2013 | 7 | 0.43333 | 0.18805 | 92.7088 | 213.9434 | 214
TC1 | MO | 55 | 3110 | 2013-07-05 23:26 | 2013-07-07 04:22 | 0 | 530 | 493 | Condenser tube leaks | F540Outage for a condenser inspection for potential tube leak as well as meter mainten | Trimble | Maintenance | Coal | 3 | 2013 | 7 | 28.9333 | 28.9333 | 14264.1333 | 493 | 493
TC1 | NC | 56 | 1850 | 2013-07-07 04:22 | 2013-07-07 04:23 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Silica hold following outage. | Trimble | Other | Coal | 3 | 2013 | 7 | 0.016667 | 0.016667 | 8.2167 | 493 | 493
TC1 | U1 | 57 | 3624 | 2013-07-07 04:23 | 2013-07-07 08:42 | 0 | 530 | 493 | Generator Voltage Supply System | F820Generator phase angle trip | Trimble | Outage | Coal | 3 | 2013 | 7 | 4.3167 | 4.3167 | 2128.1167 | 493 | 493
TC1 | NC | 58 | 1850 | 2013-07-07 08:42 | 2013-07-07 18:50 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Silica hold following unit trip | Trimble | Other | Coal | 3 | 2013 | 7 | 10.1333 | 10.1333 | 4995.7333 | 493 | 493
TC1 | D1 | 59 | 1850 | 2013-07-07 18:50 | 2013-07-07 21:30 | 525 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Derate due to silica conditions for water chemistry. | Trimble | Derate | Coal | 3 | 2013 | 7 | 2.6667 | 0.025157 | 12.4025 | 4.6509 | 5
TC1 | D1 | 60 | 1850 | 2013-07-07 21:30 | 2013-07-08 00:20 | 535 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Derate due to silica conditions for water chemistry. | Trimble | Derate | Coal | 3 | 2013 | 7 | 2.8333 | -0.02673 | -13.1777 | 0 | 0
TC1 | D1 | 61 | 1850 | 2013-07-08 11:10 | 2013-07-10 07:15 | 520 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry has a silica issue requiring a derate to the boiler. | Trimble | Derate | Coal | 3 | 2013 | 7 | 44.0833 | 0.83176 | 410.0582 | 9.3019 | 9
TC1 | D1 | 62 | 1850 | 2013-07-10 07:15 | 2013-07-12 22:06 | 525 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler water chemistry has silica issues requiring derate. | Trimble | Derate | Coal | 3 | 2013 | 7 | 62.85 | 0.59292 | 292.3118 | 4.6509 | 5
TC1 | MO | 63 | 3110 | 2013-07-12 22:06 | 2013-07-13 23:58 | 0 | 530 | 493 | Condenser tube leaks | F540Suspected condenser tube leak from silica issues in condenser lead to this mainten | Trimble | Maintenance | Coal | 3 | 2013 | 7 | 25.8667 | 25.8667 | 12752.2667 | 493 | 493
TC1 | NC | 64 | 1850 | 2013-07-13 23:58 | 2013-07-14 11:15 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Silica-hold following outage. | Trimble | Other | Coal | 3 | 2013 | 7 | 11.2833 | 11.2833 | 5562.6833 | 493 | 493
TC1 | D1 | 65 | 310 | 2013-07-17 05:12 | 2013-07-17 06:50 | 525 | 530 | 493 | Pulverizer mills | F070U1 B coal mill had a fire. When attempting to put the A/B oil gun in service ther | Trimble | Derate | Coal | 3 | 2013 | 7 | 1.6333 | 0.015409 | 7.5965 | 4.6509 | 5
TC1 | D1 | 66 | 310 | 2013-07-27 17:32 | 2013-07-27 17:47 | 525 | 530 | 493 | Pulverizer mills | F660E coal mill began having air flow issues. | Trimble | Derate | Coal | 3 | 2013 | 7 | 0.25 | 0.0023585 | 1.1627 | 4.6509 | 5
TC1 | D1 | 67 | 310 | 2013-07-27 17:47 | 2013-07-28 03:48 | 500 | 530 | 493 | Pulverizer mills | F780E coal mill continued to have air flow issues. With mill temperature continuing t | Trimble | Derate | Coal | 3 | 2013 | 7 | 10.0167 | 0.56698 | 279.5217 | 27.9057 | 28
TC1 | D4 | 68 | 3410 | 2013-07-31 03:00 | 2013-07-31 05:42 | 525 | 530 | 493 | Feedwater pump | F590Planned derate to perform maintenance on 1A TDBFP in order to attempt possible sol | Trimble | Derate | Coal | 3 | 2013 | 7 | 2.7 | 0.025472 | 12.5575 | 4.6509 | 5
TC1 | D4 | 69 | 790 | 2013-08-28 | 2013-08-28 03:00 | 525 | 530 | 493 | Pipe hangers | F790Planned derate to perform testing on Bolier Feed Pump piping hangers with Generati | Trimble | Derate | Coal | 3 | 2013 | 8 | 3 | 0.028302 | 13.9528 | 4.6509 | 5
TC1 | D4 | 70 | 3624 | 2013-09-05 04:00 | 2013-09-05 05:00 | 450 | 530 | 493 | Generator Voltage Supply System | F790Planned derate to run required VAR testing on the generator electrical supply syst | Trimble | Derate | Coal | 3 | 2013 | 9 | 1 | 0.15094 | 74.4151 | 74.4151 | 74
TC1 | NC | 71 | 1190 | 2013-09-08 | 2013-09-08 04:19 | 0 | 530 | 493 | Other tube slagging or fouling | FS00Planned deslag of the boiler to prepare for coal test burn operation. Unit was av | Trimble | Other | Coal | 3 | 2013 | 9 | 4.3167 | 4.3167 | 2128.1167 | 493 | 493
TC1 | D4 | 72 | 1487 | 2013-09-17 | 2013-09-17 00:30 | 450 | 530 | 493 | Air heater (tubular) | F540Water coil airheater leaks were repaired and required a maintenance derate to corr | Trimble | Derate | Coal | 3 | 2013 | 9 | 0.5 | 0.075472 | 37.2075 | 74.4151 | 74
TC1 | D4 | 73 | 1487 | 2013-09-17 00:30 | 2013-09-17 04:00 | 400 | 530 | 493 | Air heater (tubular) | F540Water coil airheater leaks were repaired and required a maintenance derate to corr | Trimble | Derate | Coal | 3 | 2013 | 9 | 3.5 | 0.85849 | 423.2358 | 120.9245 | 121
TC1 | D1 | 74 | 1455 | 2013-09-20 11:15 | 2013-09-20 12:17 | 520 | 530 | 493 | Induced draft fans | F790Fuel testing being conducted is causing the unit to run with high O2 putting a lim | Trimble | Derate | Coal | 3 | 2013 | 9 | 1.0333 | 0.019497 | 9.6119 | 9.3019 | 9
TC1 | D1 | 75 | 1455 | 2013-09-20 12:17 | 2013-09-21 06:00 | 510 | 530 | 493 | Induced draft fans | F790Fuel testing being conducted is causing the unit to run with high O2 putting a lim | Trimble | Derate | Coal | 3 | 2013 | 9 | 17.7167 | 0.66855 | 329.5969 | 18.6038 | 19
TC1 | D1 | 76 | 1455 | 2013-09-21 06:00 | 2013-09-21 09:15 | 505 | 530 | 493 | Induced draft fans | F790Fuel testing being conducted is causing the unit to run with high O2 putting a lim | Trimble | Derate | Coal | 3 | 2013 | 9 | 3.25 | 0.1533 | 75.5778 | 23.2547 | 23
TC1 | D1 | 77 | 1455 | 2013-09-21 09:15 | 2013-09-23 08:15 | 515 | 530 | 493 | Induced draft fans | F790Fuel testing being conducted is causing the unit to run with high O2 putting a lim | Trimble | Derate | Coal | 3 | 2013 | 9 | 47 | 1.3302 | 655.783 | 13.9528 | 14
TC1 | D1 | 78 | 1455 | 2013-09-23 08:15 | 2013-09-23 11:00 | 525 | 530 | 493 | Induced draft fans | F790Fuel testing being conducted is causing the unit to run with high O2 putting a lim | Trimble | Derate | Coal | 3 | 2013 | 9 | 2.75 | 0.025943 | 12.7901 | 4.6509 | 5
TC1 | D1 | 79 | 1455 | 2013-09-23 17:24 | 2013-09-23 18:09 | 535 | 530 | 493 | Induced draft fans | F790Fuel testing being conducted is causing the unit to run with high O2 putting a lim | Trimble | Derate | Coal | 3 | 2013 | 9 | 0.75 | -0.0070755 | -3.4882 | 0 | 0
TC1 | D1 | 80 | 1455 | 2013-09-23 18:09 | 2013-09-25 16:30 | 540 | 530 | 493 | Induced draft fans | F790Fuel testing being conducted is causing the unit to run with high O2 putting a lim | Trimble | Derate | Coal | 3 | 2013 | 9 | 46.35 | -0.87453 | -431.1425 | 0 | 0
TC1 | D1 | 81 | 1455 | 2013-09-25 16:30 | 2013-09-25 19:45 | 535 | 530 | 493 | Induced draft fans | F790Fuel testing being conducted is causing the unit to run with high O2 putting a lim | Trimble | Derate | Coal | 3 | 2013 | 9 | 3.25 | -0.03066 | -15.1156 | 0 | 0
TC1 | D1 | 82 | 1455 | 2013-09-25 19:45 | 2013-09-26 08:35 | 515 | 530 | 493 | Induced draft fans | F790Fuel testing being conducted is causing the unit to run with high O2 putting a lim | Trimble | Derate | Coal | 3 | 2013 | 9 | 12.8333 | 0.36321 | 179.0613 | 13.9528 | 14
TC1 | D1 | 83 | 1455 | 2013-09-26 08:35 | 2013-09-26 12:55 | 525 | 530 | 493 | Induced draft fans | F790Fuel testing being conducted is causing the unit to run with high O2 putting a lim | Trimble | Derate | Coal | 3 | 2013 | 9 | 4.3333 | 0.040881 | 20.1541 | 4.6509 | 5
TC1 | D1 | 84 | 1455 | 2013-09-26 12:55 | 2013-09-27 12:14 | 520 | 530 | 493 | Induced draft fans | F790Fuel testing being conducted is causing the unit to run with high O2 putting a lim | Trimble | Derate | Coal | 3 | 2013 | 9 | 23.3167 | 0.43994 | 216.889 | 9.3019 | 9
TC1 | D1 | 85 | 1455 | 2013-09-27 12:14 | 2013-09-28 04:20 | 525 | 530 | 493 | Induced draft fans | F790Fuel testing being conducted is causing the unit to run with high O2 putting a lim | Trimble | Derate | Coal | 3 | 2013 | 9 | 16.1 | 0.15189 | 74.8802 | 4.6509 | 5
TC1 | D4 | 86 | 75 | 2013-10-04 21:00 | 2013-10-04 22:00 | 445 | 530 | 493 | Storage silos/hoppers | F590Planned derate going into the outage to purge coal silos. | Trimble | Derate | Coal | 3 | 2013 | 10 | 1 | 0.16038 | 79.066 | 79.066 | 79
TC1 | D4 | 87 | 75 | 2013-10-04 22:00 | 2013-10-05 00:15 | 340 | 530 | 493 | Storage silos/hoppers | F590Planned derate going into the outage to purge coal silos. | Trimble | Derate | Coal | 3 | 2013 | 10 | 2.25 | 0.8066 | 397.6557 | 176.7358 | 177
TC1 | PO | 88 | 1801 | 2013-10-05 00:15 | 2013-11-05 07:02 | 0 | 530 | 493 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | F590Planned outage for boiler overhaul. Details of boiler tube work and of other majo | Trimble | Other | Coal | 3 | 2013 | 10 | 750.7833 | 750.7833 | 370136.1833 | 493 | 493
TC1 | SF | 89 | 1500 | 2013-11-05 07:02 | 2013-11-05 11:25 | 0 | 530 | 493 | Air heater soot blowers | F150The power to the A and B sootblowers was tripped, potential cause was from the boi | Trimble | Outage | Coal | 3 | 2013 | 11 | 4.3833 | 4.3833 | 2160.9833 | 493 | 493
TC1 | U1 | 90 | 1000 | 2013-11-05 11:25 | 2013-11-06 16:24 | 0 | 530 | 493 | Waterwall (Furnace wall) A | F540Tube failure was found after the start up failure. Leak was at the upper arch, 8t | Trimble | Outage | Coal | 3 | 2013 | 11 | 28.9833 | 28.9833 | 14288.7833 | 493 | 493
TC1 | NC | 91 | 1850 | 2013-11-06 16:24 | 2013-11-07 05:16 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00TC1 was online and ramping. The load was held down some due to silica from the un | Trimble | Other | Coal | 3 | 2013 | 11 | 12.8667 | 12.8667 | 6343.2667 | 493 | 493
TC1 | D1 | 92 | 1850 | 2013-11-07 05:16 | 2013-11-07 08:21 | 305 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry, specifically silica, was causing start-up issues and unit derate | Trimble | Derate | Coal | 3 | 2013 | 11 | 3.0833 | 1.309 | 645.3184 | 209.2925 | 209
TC1 | NC | 93 | 1850 | 2013-11-07 08:21 | 2013-11-07 16:50 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Unit was online and ramping following a chemistry issue, and load was held down fo | Trimble | Other | Coal | 3 | 2013 | 11 | 8.4833 | 8.4833 | 4182.2833 | 493 | 493
TC1 | D1 | 94 | 1850 | 2013-11-07 16:50 | 2013-11-07 17:51 | 305 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Silica in the boiler water chemistry did not get to acceptable levels and derate r | Trimble | Derate | Coal | 3 | 2013 | 11 | 1.0167 | 0.4316 | 212.7807 | 209.2925 | 209
TC1 | U1 | 95 | 400 | 2013-11-07 17:51 | 2013-11-08 14:09 | 0 | 530 | 493 | Burner wind box fires | F830Coal fire outside of boiler, #2 corner, C-D elevation of the burner windbox. Came | Trimble | Outage | Coal | 3 | 2013 | 11 | 20.3 | 20.3 | 10007.9 | 493 | 493
TC1 | NC | 96 | 1850 | 2013-11-08 14:09 | 2013-11-09 03:40 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Unit on-line and ramping. Load held down some due to silica from the unit outage. | Trimble | Other | Coal | 3 | 2013 | 11 | 13.5167 | 13.5167 | 6663.7167 | 493 | 493
TC1 | D1 | 97 | 8140 | 2013-11-09 03:40 | 2013-11-10 09:10 | 300 | 530 | 493 | Reaction tanks including agitators | F170Scrubber chemistry, low solids due to over dilution was the main driver of the der | Trimble | Derate | Coal | 3 | 2013 | 11 | 29.5 | 12.8019 | 6311.3302 | 213.9434 | 214
TC1 | D1 | 98 | 1850 | 2013-11-10 09:10 | 2013-11-10 12:00 | 375 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 2.8333 | 0.82862 | 408.5079 | 144.1792 | 144
TC1 | D1 | 99 | 1850 | 2013-11-10 12:00 | 2013-11-10 16:10 | 390 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 4.1667 | 1.1006 | 542.6101 | 130.2264 | 130
TC1 | D1 | 100 | 1850 | 2013-11-10 16:10 | 2013-11-10 20:30 | 360 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 4.3333 | 1.3899 | 685.239 | 158.1321 | 158
TC1 | D1 | 101 | 1850 | 2013-11-10 20:30 | 2013-11-11 00:10 | 385 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 3.6667 | 1.0031 | 494.5503 | 134.8774 | 135
TC1 | D1 | 102 | 1850 | 2013-11-11 00:10 | 2013-11-11 00:35 | 355 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 0.41667 | 0.13758 | 67.8263 | 162.783 | 163
TC1 | D1 | 103 | 1850 | 2013-11-11 00:35 | 2013-11-11 05:40 | 380 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 5.0833 | 1.4387 | 709.2689 | 139.5283 | 140
TC1 | D1 | 104 | 1850 | 2013-11-11 05:40 | 2013-11-11 07:40 | 405 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 2 | 0.4717 | 232.5472 | 116.2736 | 116
TC1 | D1 | 105 | 1850 | 2013-11-11 07:40 | 2013-11-11 14:13 | 415 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 6.55 | 1.4212 | 700.6646 | 106.9717 | 107
TC1 | D1 | 106 | 1850 | 2013-11-11 14:13 | 2013-11-12 05:00 | 432 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 14.7833 | 2.7335 | 1347.6264 | 91.1585 | 91
TC1 | D1 | 107 | 1850 | 2013-11-12 05:00 | 2013-11-12 11:40 | 448 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 6.6667 | 1.0314 | 508.5031 | 76.2755 | 76
TC1 | D1 | 108 | 1850 | 2013-11-12 11:40 | 2013-11-12 13:45 | 462 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 2.0833 | 0.2673 | 131.7767 | 63.2528 | 63
TC1 | D1 | 109 | 1850 | 2013-11-12 13:45 | 2013-11-13 01:00 | 475 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 11.25 | 1.1675 | 575.5542 | 51.1604 | 51
TC1 | D1 | 110 | 1850 | 2013-11-13 01:00 | 2013-11-13 08:15 | 493 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 7.25 | 0.50613 | 249.5231 | 34.417 | 34
TC1 | D1 | 111 | 1850 | 2013-11-13 08:15 | 2013-11-13 16:15 | 510 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 8 | 0.30189 | 148.8302 | 18.6038 | 19
TC1 | D1 | 112 | 1850 | 2013-11-13 16:15 | 2013-11-14 02:54 | 520 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 10.65 | 0.20094 | 99.0651 | 9.3019 | 9
TC1 | D1 | 113 | 1850 | 2013-11-14 02:54 | 2013-11-14 09:45 | 525 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 6.85 | 0.064623 | 31.859 | 4.6509 | 5
TC1 | D1 | 114 | 1850 | 2013-11-14 09:45 | 2013-11-14 20:42 | 532 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 10.95 | -0.041321 | -20.3711 | 0 | 0
TC1 | D1 | 115 | 1850 | 2013-11-14 20:42 | 2013-11-15 03:20 | 538 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 6.6333 | -0.10013 | -49.362 | 0 | 0
TC1 | D1 | 116 | 1850 | 2013-11-15 03:20 | 2013-11-17 06:15 | 543 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Boiler chemistry issues continue. Silica in the boiler water not meeting required | Trimble | Derate | Coal | 3 | 2013 | 11 | 50.9167 | -1.2489 | -615.7074 | 0 | 0
TC1 | D1 | 117 | 3979 | 2013-11-17 06:15 | 2013-11-17 07:00 | 432 | 530 | 493 | Other DCS problems | F410A hard wired, DCS input for the coal feeders read "no coal on feeder" for 1 second | Trimble | Derate | Coal | 3 | 2013 | 11 | 0.75 | 0.13868 | 68.3689 | 91.1585 | 91
TC1 | NC | 118 | 530 | 2013-11-17 22:27 | 2013-11-18 16:51 | 0 | 530 | 493 | Other main steam system problems | F660With Unit 2 coming online following a weekend outage, TC1 is being locked into low | Trimble | Other | Coal | 3 | 2013 | 11 | 18.4 | 18.4 | 9071.2 | 493 | 493
TC1 | D1 | 119 | 1850 | 2013-11-19 07:54 | 2013-11-19 08:50 | 500 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Silica continued to run high requiring unit derate to avoid additional issues/dama | Trimble | Derate | Coal | 3 | 2013 | 11 | 0.93333 | 0.05283 | 26.0453 | 27.9057 | 28
TC1 | D1 | 120 | 3110 | 2013-11-19 08:50 | 2013-11-19 12:20 | 470 | 530 | 493 | Condenser tube leaks | F540Due to the continued high silica, a condenser tube leak was suspect. The decision | Trimble | Derate | Coal | 3 | 2013 | 11 | 3.5 | 0.39623 | 195.3396 | 55.8113 | 56
TC1 | U1 | 121 | 3110 | 2013-11-19 12:20 | 2013-11-20 13:14 | 0 | 530 | 493 | Condenser tube leaks | F830The suspected condenser tube leak from the continued high silica readings brought | Trimble | Outage | Coal | 3 | 2013 | 11 | 24.9 | 24.9 | 12275.7 | 493 | 493
TC1 | MO | 122 | 1455 | 2013-11-20 13:14 | 2013-11-21 05:30 | 0 | 530 | 493 | Induced draft fans | F040The A ID fan required balancing and was completed during this maintenance outage p | Trimble | Maintenance | Coal | 3 | 2013 | 11 | 16.2667 | 16.2667 | 8019.4667 | 493 | 493
TC1 | SF | 123 | 3624 | 2013-11-21 05:30 | 2013-11-21 09:38 | 0 | 530 | 493 | Generator Voltage Supply System | F870There were issues with the generator terminal voltage feedback. Two issues were f | Trimble | Outage | Coal | 3 | 2013 | 11 | 4.1333 | 4.1333 | 2037.7333 | 493 | 493
TC1 | D1 | 124 | 1850 | 2013-11-21 20:00 | 2013-11-22 | 475 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Following return from outage, silica remained high and required continued blow dow | Trimble | Derate | Coal | 3 | 2013 | 11 | 4 | 0.41509 | 204.6415 | 51.1604 | 51
TC1 | D1 | 125 | 1850 | 2013-11-22 | 2013-11-22 05:48 | 500 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Silica remained high, but was decreasing with blow down. | Trimble | Derate | Coal | 3 | 2013 | 11 | 5.8 | 0.3283 | 161.8528 | 27.9057 | 28
TC1 | D1 | 126 | 1850 | 2013-11-22 05:48 | 2013-11-22 06:27 | 510 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Silica nearing acceptable levels, last derated needed before full load possible. | Trimble | Derate | Coal | 3 | 2013 | 11 | 0.65 | 0.024528 | 12.0925 | 18.6038 | 19
TC1 | D1 | 127 | 3441 | 2013-11-22 17:40 | 2013-11-22 19:04 | 500 | 530 | 493 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F540During start-up, BFP's began getting taxed and couldn't keep load up. This was tr | Trimble | Derate | Coal | 3 | 2013 | 11 | 1.4 | 0.079245 | 39.0679 | 27.9057 | 28
TC1 | D1 | 128 | 280 | 2013-11-25 17:16 | 2013-11-25 17:56 | 520 | 530 | 493 | Pulverizer fires | F780Derate due to fires in the 1D and 1E coal mills. | Trimble | Derate | Coal | 3 | 2013 | 11 | 0.66667 | 0.012579 | 6.2013 | 9.3019 | 9
TC1 | D1 | 129 | 280 | 2013-11-25 17:56 | 2013-11-25 20:19 | 380 | 530 | 493 | Pulverizer fires | F780Derate due to fires in the 1B, 1D, and 1E coal mills. | Trimble | Derate | Coal | 3 | 2013 | 11 | 2.3833 | 0.67453 | 332.5425 | 139.5283 | 140
TC1 | D1 | 130 | 280 | 2013-11-25 21:00 | 2013-11-25 21:32 | 435 | 530 | 493 | Pulverizer fires | F780Derate due to fires in the 1F coal mill. | Trimble | Derate | Coal | 3 | 2013 | 11 | 0.53333 | 0.095597 | 47.1296 | 88.3679 | 88
TC1 | D1 | 131 | 280 | 2013-11-27 20:32 | 2013-11-27 21:00 | 488 | 530 | 493 | Pulverizer fires | F780Derate due to fires in the 1A and 1E coal mills. | Trimble | Derate | Coal | 3 | 2013 | 11 | 0.46667 | 0.036981 | 18.2317 | 39.0679 | 39
TC1 | D1 | 132 | 280 | 2013-12-04 13:59 | 2013-12-04 14:39 | 410 | 530 | 493 | Pulverizer fires | F780The 1D Mill caught fire and was taken out of service to investigate in the mill an | Trimble | Derate | Coal | 3 | 2013 | 12 | 0.66667 | 0.15094 | 74.4151 | 111.6226 | 112
TC1 | D1 | 133 | 280 | 2013-12-06 13:47 | 2013-12-06 15:10 | 485 | 530 | 493 | Pulverizer fires | F780The 1B mill caught fire requiring unit derate. | Trimble | Derate | Coal | 3 | 2013 | 12 | 1.3833 | 0.11745 | 57.9042 | 41.8585 | 42
TC1 | NC | 134 | 4268 | 2013-12-08 01:00 | 2013-12-08 01:35 | 0 | 530 | 493 | Reheat/intercept valve testing | F790Completed a valve test on unit one turbine valves to ensure working order. Unit a | Trimble | Other | Coal | 3 | 2013 | 12 | 0.58333 | 0.58333 | 287.5833 | 493 | 493
TC1 | D1 | 135 | 280 | 2013-12-10 09:01 | 2013-12-10 14:11 | 500 | 530 | 493 | Pulverizer fires | F780TC1 1B Coal mill fire caused derate on unit. | Trimble | Derate | Coal | 3 | 2013 | 12 | 5.1667 | 0.29245 | 144.1792 | 27.9057 | 28
TC1 | NC | 141 | 8813 | 2013-12-10 14:11 | 2013-12-10 15:26 | 0 | 530 | 493 | SCR NOx Injection grid piping/valves | F790Conducted testing on the U1 Ammonia Injection system. Clean Combustion & Energy w | Trimble | Other | Coal | 3 | 2013 | 12 | 1.25 | 1.25 | 616.25 | 493 | 493
TC1 | D1 | 136 | 280 | 2013-12-10 15:26 | 2013-12-10 15:37 | 500 | 530 | 493 | Pulverizer fires | F780TC1 1B Coal mill fire caused derate on unit. | Trimble | Derate | Coal | 3 | 2013 | 12 | 0.18333 | 0.010377 | 5.116 | 27.9057 | 28
TC1 | NC | 142 | 8813 | 2013-12-11 07:00 | 2013-12-11 14:20 | 0 | 530 | 493 | SCR NOx Injection grid piping/valves | F790Continued testing on the U1 Ammonia Injection system. Clean Combustion & Energy w | Trimble | Other | Coal | 3 | 2013 | 12 | 7.3333 | 7.3333 | 3615.3333 | 493 | 493
TC1 | D1 | 137 | 280 | 2013-12-11 14:20 | 2013-12-11 15:10 | 500 | 530 | 493 | Pulverizer fires | F780TC1 1A and 1B Coal mill fires caused derate on unit. | Trimble | Derate | Coal | 3 | 2013 | 12 | 0.83333 | 0.04717 | 23.2547 | 27.9057 | 28
TC1 | NC | 143 | 8813 | 2013-12-12 07:30 | 2013-12-12 19:27 | 0 | 530 | 493 | SCR NOx Injection grid piping/valves | F790Continued testing on the U1 Ammonia Injection system. Clean Combustion & Energy w | Trimble | Other | Coal | 3 | 2013 | 12 | 11.95 | 11.95 | 5891.35 | 493 | 493
TC1 | D1 | 138 | 385 | 2013-12-12 23:05 | 2013-12-13 02:39 | 510 | 530 | 493 | Igniters | F460Oil gun failure caused unit derate. | Trimble | Derate | Coal | 3 | 2013 | 12 | 3.5667 | 0.13459 | 66.3535 | 18.6038 | 19
TC1 | MO | 139 | 1000 | 2013-12-13 13:03 | 2013-12-16 01:05 | 0 | 530 | 493 | Waterwall (Furnace wall) A | F540Boiler tube leak was located in the penthouse at the waterwall stub that extended | Trimble | Maintenance | Coal | 3 | 2013 | 12 | 60.0333 | 60.0333 | 29596.4333 | 493 | 493
TC1 | D1 | 144 | 280 | 2013-12-20 06:06 | 2013-12-20 06:27 | 470 | 530 | 493 | Pulverizer fires | F780Derate due to fires on A and D coal mills requiring derate due to running with 4 m | Trimble | Derate | Coal | 3 | 2013 | 12 | 0.35 | 0.039623 | 19.534 | 55.8113 | 56
TC1 | D1 | 145 | 280 | 2013-12-25 08:25 | 2013-12-25 11:47 | 485 | 530 | 493 | Pulverizer fires | F780Derate due to fires in the B and D coal mills. | Trimble | Derate | Coal | 3 | 2013 | 12 | 3.3667 | 0.28585 | 140.9236 | 41.8585 | 42
TC1 | D1 | 146 | 280 | 2013-12-26 06:00 | 2013-12-26 07:25 | 475 | 530 | 493 | Pulverizer fires | F780Derate due to fires in the B and D coal mills. | Trimble | Derate | Coal | 3 | 2013 | 12 | 1.4167 | 0.14701 | 72.4772 | 51.1604 | 51
TC1 | D1 | 147 | 280 | 2013-12-26 07:25 | 2013-12-26 09:03 | 525 | 530 | 493 | Pulverizer fires | F780Derate due to fire in the D coal mill. | Trimble | Derate | Coal | 3 | 2013 | 12 | 1.6333 | 0.015409 | 7.5965 | 4.6509 | 5
TC1 | D1 | 148 | 280 | 2013-12-28 17:45 | 2013-12-28 18:09 | 505 | 530 | 493 | Pulverizer fires | F780Derate due to fires in the B and D coal mills. | Trimble | Derate | Coal | 3 | 2013 | 12 | 0.4 | 0.018868 | 9.3019 | 23.2547 | 23
TC1 | D1 | 149 | 280 | 2013-12-28 18:09 | 2013-12-28 19:32 | 510 | 530 | 493 | Pulverizer fires | F780Derate due to fires in the B and D coal mills. | Trimble | Derate | Coal | 3 | 2013 | 12 | 1.3833 | 0.052201 | 25.7352 | 18.6038 | 19
TC1 | NC | 150 | 1489 | 2013-12-30 07:00 | 2013-12-30 13:00 | 0 | 530 | 493 | Air heater (heat pipe | F790Holding load over 525 MW for air heater slip testing to be conducted. | Trimble | Other | Coal | 3 | 2013 | 12 | 6 | 6 | 2958 | 493 | 493
TC1 | NC | 151 | 1489 | 2013-12-31 06:45 | 2013-12-31 13:00 | 0 | 530 | 493 | Air heater (heat pipe | F790Holding load over 525 MW to conduct air heater slip testing. | Trimble | Other | Coal | 3 | 2013 | 12 | 6.25 | 6.25 | 3081.25 | 493 | 493
TC1 | NC | 1 | 1489 | 2014-01-02 09:00 | 2014-01-02 15:00 | 0 | 530 | 493 | Air heater (heat pipe | F790Holding the unit above 525 MW's for Air Heater Slip Testing to be conducted. Unit | Trimble | Other | Coal | 3 | 2014 | 1 | 6 | 6 | 2958 | 493 | 493
TC1 | NC | 2 | 1489 | 2014-01-03 05:00 | 2014-01-03 09:40 | 0 | 530 | 493 | Air heater (heat pipe | F790Holding load above 525 MW's for ammonia slip testing for the air heaters. Unit av | Trimble | Other | Coal | 3 | 2014 | 1 | 4.6667 | 4.6667 | 2300.6667 | 493 | 493
TC1 | D1 | 3 | 280 | 2014-01-03 09:40 | 2014-01-03 11:31 | 505 | 530 | 493 | Pulverizer fires | F780Derate due to fires in the B and D coal mills. | Trimble | Derate | Coal | 3 | 2014 | 1 | 1.85 | 0.087264 | 43.0212 | 23.2547 | 23
TC1 | D1 | 4 | 280 | 2014-01-04 02:47 | 2014-01-04 03:56 | 500 | 530 | 493 | Pulverizer fires | F780Derate due to fire in the D coal mill. | Trimble | Derate | Coal | 3 | 2014 | 1 | 1.15 | 0.065094 | 32.0915 | 27.9057 | 28
TC1 | D1 | 5 | 280 | 2014-01-04 05:09 | 2014-01-04 08:18 | 489 | 530 | 493 | Pulverizer fires | F780Derate due to fires in the D coal mill and the E coal mill was unavailable for a m | Trimble | Derate | Coal | 3 | 2014 | 1 | 3.15 | 0.24368 | 120.1339 | 38.1377 | 38
TC1 | D1 | 6 | 280 | 2014-01-07 17:25 | 2014-01-07 21:08 | 490 | 530 | 493 | Pulverizer fires | F780Derate required due to A & B coal mill fires. | Trimble | Derate | Coal | 3 | 2014 | 1 | 3.7167 | 0.2805 | 138.2881 | 37.2075 | 37
TC1 | D1 | 7 | 590 | 2014-01-08 12:00 | 2014-01-08 17:26 | 500 | 530 | 493 | Desuperheater/attemperator valves | F540The SH Spray control valve was leaking and required a unit derate to accomplish th | Trimble | Derate | Coal | 3 | 2014 | 1 | 5.4333 | 0.30755 | 151.6208 | 27.9057 | 28
TC1 | NC | 8 | 1489 | 2014-01-09 07:00 | 2014-01-09 13:00 | 0 | 530 | 493 | Air heater (heat pipe | F790A 525 MW minimum limit was set on the unit to accomplish air heater slip testing. | Trimble | Other | Coal | 3 | 2014 | 1 | 6 | 6 | 2958 | 493 | 493
TC1 | NC | 9 | 1489 | 2014-01-10 06:30 | 2014-01-10 15:00 | 0 | 530 | 493 | Air heater (heat pipe | F790A 525 MW minimum limit was set on the unit to accomplish air heater slip testing. | Trimble | Other | Coal | 3 | 2014 | 1 | 8.5 | 8.5 | 4190.5 | 493 | 493
TC1 | D1 | 10 | 8000 | 2014-01-11 05:23 | 2014-01-11 19:09 | 450 | 530 | 493 | Chemical feed storage | F060Reactant supply C Limestone conveyor belt broke and issues with running backup con | Trimble | Derate | Coal | 3 | 2014 | 1 | 13.7667 | 2.078 | 1024.4478 | 74.4151 | 74
TC1 | D1 | 11 | 8000 | 2014-01-11 19:09 | 2014-01-11 21:03 | 275 | 530 | 493 | Chemical feed storage | F060Reactant supply C Limestone conveyor belt broke and issues with running backup con | Trimble | Derate | Coal | 3 | 2014 | 1 | 1.9 | 0.91415 | 450.6764 | 237.1981 | 237
TC1 | U1 | 12 | 9900 | 2014-01-11 21:03 | 2014-01-12 07:57 | 0 | 530 | 493 | Operator error | F820During load drop, operator error in valve closing caused the TDBFP main extraction | Trimble | Outage | Coal | 3 | 2014 | 1 | 10.9 | 10.9 | 5373.7 | 493 | 493
TC1 | D1 | 13 | 280 | 2014-01-13 06:39 | 2014-01-13 10:33 | 500 | 530 | 493 | Pulverizer fires | F780Unit derate due to two coal mill issues: 1E mill had a fire that needed to be put | Trimble | Derate | Coal | 3 | 2014 | 1 | 3.9 | 0.22075 | 108.8321 | 27.9057 | 28
TC1 | D1 | 14 | 280 | 2014-01-14 08:36 | 2014-01-14 10:39 | 500 | 530 | 493 | Pulverizer fires | F780Derate due to fire in the 1B Coal Mill. | Trimble | Derate | Coal | 3 | 2014 | 1 | 2.05 | 0.11604 | 57.2066 | 27.9057 | 28
TC1 | U1 | 15 | 3344 | 2014-01-14 10:39 | 2014-01-16 22:16 | 0 | 530 | 493 | Deaerator (including level control) | F540Leak in the deaerator heater head was discovered. Unit was taken offline to repai | Trimble | Outage | Coal | 3 | 2014 | 1 | 59.6167 | 59.6167 | 29391.0167 | 493 | 493
TC1 | D1 | 16 | 280 | 2014-01-17 15:20 | 2014-01-17 16:00 | 510 | 530 | 493 | Pulverizer fires | F780Fires in the 1A and 1B coal mills required unit derate. | Trimble | Derate | Coal | 3 | 2014 | 1 | 0.66667 | 0.025157 | 12.4025 | 18.6038 | 19
TC1 | D1 | 17 | 280 | 2014-01-17 16:00 | 2014-01-17 16:45 | 380 | 530 | 493 | Pulverizer fires | F780Additional fire in the 1C mill following 1A and 1B mill fires required further der | Trimble | Derate | Coal | 3 | 2014 | 1 | 0.75 | 0.21226 | 104.6462 | 139.5283 | 140
TC1 | D1 | 18 | 280 | 2014-01-17 16:45 | 2014-01-17 19:40 | 250 | 530 | 493 | Pulverizer fires | F780Additional fire in the 1D mill after fires in the 1A, 1B, and 1C mills required ad | Trimble | Derate | Coal | 3 | 2014 | 1 | 2.9167 | 1.5409 | 759.6541 | 260.4528 | 260
TC1 | D1 | 19 | 280 | 2014-01-17 19:40 | 2014-01-17 20:08 | 480 | 530 | 493 | Pulverizer fires | F780Some of the mills were returned to service. However, unit derate was still necess | Trimble | Derate | Coal | 3 | 2014 | 1 | 0.46667 | 0.044025 | 21.7044 | 46.5094 | 47
TC1 | NC | 20 | 4267 | 2014-01-19 01:00 | 2014-01-19 01:30 | 0 | 530 | 493 | Control valve testing | F790Weekly valve check on the unit, Unit available to return to full load if required | Trimble | Other | Coal | 3 | 2014 | 1 | 0.5 | 0.5 | 246.5 | 493 | 493
TC1 | NC | 21 | 1489 | 2014-01-21 18:00 | 2014-01-21 23:59 | 0 | 530 | 493 | Air heater (heat pipe | FF00Unit was running and good for full load but with a 525 MW limit set for ammonia sl | Trimble | Other | Coal | 3 | 2014 | 1 | 5.9833 | 5.9833 | 2949.7833 | 493 | 493
TC1 | NC | 22 | 1489 | 2014-01-29 06:00 | 2014-01-29 08:00 | 0 | 530 | 493 | Air heater (heat pipe | FF00Unit was running and good for full load but with a 525 MW limit set for ammonia sl | Trimble | Other | Coal | 3 | 2014 | 1 | 2 | 2 | 986 | 493 | 493
TC1 | NC | 23 | 9999 | 2014-01-29 08:00 | 2014-01-29 10:00 | 0 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Unit was running and requested full load production to allow for the full-load tes | Trimble | Other | Coal | 3 | 2014 | 1 | 2 | 2 | 986 | 493 | 493
TC1 | NC | 24 | 1489 | 2014-01-29 10:00 | 2014-01-29 14:37 | 0 | 530 | 493 | Air heater (heat pipe | FF00Unit was running and good for full load but with a 525 MW limit set for ammonia sl | Trimble | Other | Coal | 3 | 2014 | 1 | 4.6167 | 4.6167 | 2276.0167 | 493 | 493
TC1 | NC | 25 | 1489 | 2014-01-31 13:00 | 2014-01-31 20:00 | 0 | 530 | 493 | Air heater (heat pipe | FF00Unit was running & good for full load with a 525 MW limit set for ammonia slip mit | Trimble | Other | Coal | 3 | 2014 | 1 | 7 | 7 | 3451 | 493 | 493
TC1 | NC | 147 | 1489 | 2014-01-31 13:00 | 2014-01-31 20:00 | 0 | 530 | 493 | Air heater (heat pipe | FF00Unit was running and good for full load with a 525 MW limit set for ammonia slip m | Trimble | Other | Coal | 3 | 2014 | 1 | 7 | 7 | 3451 | 493 | 493
TC1 | NC | 26 | 9999 | 2014-02-05 10:45 | 2014-02-05 16:26 | 0 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Unit running and good for full load, this non-curtailing event was for the complet | Trimble | Other | Coal | 3 | 2014 | 2 | 5.6833 | 5.6833 | 2801.8833 | 493 | 493
TC1 | D1 | 27 | 310 | 2014-02-10 07:22 | 2014-02-10 07:45 | 500 | 530 | 493 | Pulverizer mills | F780Derate on TC1 to 500 MW's due to D coal mill fire. Additional issue with the E co | Trimble | Derate | Coal | 3 | 2014 | 2 | 0.38333 | 0.021698 | 10.6972 | 27.9057 | 28
TC1 | D1 | 28 | 310 | 2014-02-10 10:00 | 2014-02-10 13:58 | 500 | 530 | 493 | Pulverizer mills | F780Derate required due to fire on the 1D coal mill. | Trimble | Derate | Coal | 3 | 2014 | 2 | 3.9667 | 0.22453 | 110.6925 | 27.9057 | 28
TC1 | D1 | 29 | 310 | 2014-02-11 22:17 | 2014-02-11 23:30 | 500 | 530 | 493 | Pulverizer mills | F780Derate required due to high temperature on the 1B coal mill. | Trimble | Derate | Coal | 3 | 2014 | 2 | 1.2167 | 0.068868 | 33.9519 | 27.9057 | 28
TC1 | NC | 30 | 9999 | 2014-02-19 08:00 | 2014-02-19 14:00 | 0 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Test run at full load to maintain high temperatures for unit testing. | Trimble | Other | Coal | 3 | 2014 | 2 | 6 | 6 | 2958 | 493 | 493
TC1 | NC | 31 | 510 | 2014-03-02 01:00 | 2014-03-02 01:20 | 0 | 530 | 493 | Main steam relief/safety valves off superheater | F790Non-curtailing derate for a planned, weekly valve check. Unit was available to re | Trimble | Other | Coal | 3 | 2014 | 3 | 0.33333 | 0.33333 | 164.3333 | 493 | 493
TC1 | U1 | 32 | 1471 | 2014-03-06 01:06 | 2014-03-06 12:48 | 0 | 530 | 493 | Induced draft fan motors - variable speed | F820The VFD on the 1B ID fan sent a false alarm due to a low-low cooling supply alarm | Trimble | Outage | Coal | 3 | 2014 | 3 | 11.7 | 11.7 | 5768.1 | 493 | 493
TC1 | D1 | 33 | 280 | 2014-03-09 09:00 | 2014-03-09 10:15 | 500 | 530 | 493 | Pulverizer fires | F780TC1 D coal mill had a fire and required a derate. | Trimble | Derate | Coal | 3 | 2014 | 3 | 1.25 | 0.070755 | 34.8821 | 27.9057 | 28
TC1 | D1 | 34 | 310 | 2014-03-09 10:15 | 2014-03-09 12:45 | 500 | 530 | 493 | Pulverizer mills | F060TC1 D coal mill breaker had an issue requiring replacement. | Trimble | Derate | Coal | 3 | 2014 | 3 | 2.5 | 0.14151 | 69.7642 | 27.9057 | 28
TC1 | D1 | 35 | 340 | 2014-03-13 08:15 | 2014-03-13 10:20 | 510 | 530 | 493 | Other pulverizer problems | F400The 1D Mill discharge valve was behaving erratically affecting mill control. | Trimble | Derate | Coal | 3 | 2014 | 3 | 2.0833 | 0.078616 | 38.7579 | 18.6038 | 19
TC1 | D1 | 36 | 280 | 2014-03-13 10:20 | 2014-03-13 10:46 | 435 | 530 | 493 | Pulverizer fires | F7801B mill fire required unit derate until OOS mill could be started | Trimble | Derate | Coal | 3 | 2014 | 3 | 0.43333 | 0.077673 | 38.2928 | 88.3679 | 88
TC1 | D1 | 37 | 340 | 2014-03-13 10:46 | 2014-03-13 11:30 | 510 | 530 | 493 | Other pulverizer problems | F4001D mill discharge valve was operating erratically affecting mill control. | Trimble | Derate | Coal | 3 | 2014 | 3 | 0.73333 | 0.027673 | 13.6428 | 18.6038 | 19
TC1 | D1 | 38 | 340 | 2014-03-14 14:00 | 2014-03-14 16:15 | 510 | 530 | 493 | Other pulverizer problems | F4001D coal mill discharge valve was operating erratically affecting mill control. Ad | Trimble | Derate | Coal | 3 | 2014 | 3 | 2.25 | 0.084906 | 41.8585 | 18.6038 | 19
TC1 | D1 | 39 | 3412 | 2014-03-15 01:55 | 2014-03-15 08:50 | 525 | 530 | 493 | Feedwater pump drive - steam turbine | F820The 1A TDBFP had an emergency governor trip removing it from service. | Trimble | Derate | Coal | 3 | 2014 | 3 | 6.9167 | 0.065252 | 32.169 | 4.6509 | 5
TC1 | D1 | 40 | 3412 | 2014-03-15 11:32 | 2014-03-15 13:33 | 525 | 530 | 493 | Feedwater pump drive - steam turbine | F540The 1A TDBFP had an oil leak which required removal from service to repair. | Trimble | Derate | Coal | 3 | 2014 | 3 | 2.0167 | 0.019025 | 9.3794 | 4.6509 | 5
TC1 | D1 | 41 | 280 | 2014-03-17 18:20 | 2014-03-17 21:55 | 525 | 530 | 493 | Pulverizer fires | F780TC1 B Coal Mill had a fire and required removal from service and unit derate. | Trimble | Derate | Coal | 3 | 2014 | 3 | 3.5833 | 0.033805 | 16.6659 | 4.6509 | 5
TC1 | NC | 42 | 1100 | 2014-03-29 | 2014-03-29 05:00 | 0 | 530 | 493 | Waterwall (Furnace wall) B | FS00Non-curtailing derate was placed on the unit to complete a planned boiler deslag. | Trimble | Other | Coal | 3 | 2014 | 3 | 5 | 5 | 2465 | 493 | 493
TC1 | MO | 43 | 1000 | 2014-04-05 | 2014-04-06 16:49 | 0 | 530 | 493 | Waterwall (Furnace wall) A | F540TC1 boiler tube leak on 12th landing. The waterwall tube was located on the left | Trimble | Maintenance | Coal | 3 | 2014 | 4 | 40.8167 | 40.8167 | 20122.6167 | 493 | 493
TC1 | D1 | 44 | 1455 | 2014-04-07 10:59 | 2014-04-14 18:45 | 525 | 530 | 493 | Induced draft fans | F8501B ID Fan Bearing vibrations required unit derate to keep vibrations within limits | Trimble | Derate | Coal | 3 | 2014 | 4 | 175.7667 | 1.6582 | 817.4808 | 4.6509 | 5
TC1 | NC | 45 | 4267 | 2014-04-13 01:00 | 2014-04-13 01:24 | 0 | 530 | 493 | Control valve testing | F790TC1 had a non-curtailing event for the weekly valve test. The unit was available | Trimble | Other | Coal | 3 | 2014 | 4 | 0.4 | 0.4 | 197.2 | 493 | 493
TC1 | D1 | 46 | 895 | 2014-04-14 18:45 | 2014-04-14 20:53 | 450 | 530 | 493 | Ashpit trouble | F060Derate was required to make necessary repairs to the ash pit hopper doors after a | Trimble | Derate | Coal | 3 | 2014 | 4 | 2.1333 | 0.32201 | 158.7522 | 74.4151 | 74
TC1 | D1 | 47 | 1455 | 2014-04-14 20:53 | 2014-04-16 02:46 | 525 | 530 | 493 | Induced draft fans | F8501B ID Fan Bearing vibrations required unit derate to keep vibrations within limits | Trimble | Derate | Coal | 3 | 2014 | 4 | 29.8833 | 0.28192 | 138.9857 | 4.6509 | 5
TC1 | D1 | 48 | 385 | 2014-04-16 02:46 | 2014-04-16 03:16 | 480 | 530 | 493 | Igniters | F400Derate was required due to AB oil gun issues related to B coal mill issues. | Trimble | Derate | Coal | 3 | 2014 | 4 | 0.5 | 0.04717 | 23.2547 | 46.5094 | 47
TC1 | D1 | 49 | 1455 | 2014-04-16 03:16 | 2014-04-16 12:10 | 525 | 530 | 493 | Induced draft fans | F8501B ID Fan Bearing vibrations required unit derate to keep vibrations within limits | Trimble | Derate | Coal | 3 | 2014 | 4 | 8.9 | 0.083962 | 41.3934 | 4.6509 | 5
TC1 | D1 | 50 | 310 | 2014-04-16 12:10 | 2014-04-16 12:35 | 450 | 530 | 493 | Pulverizer mills | F780Derate required when E Coal Mill tripped after it lit off. | Trimble | Derate | Coal | 3 | 2014 | 4 | 0.41667 | 0.062893 | 31.0063 | 74.4151 | 74
TC1 | D1 | 51 | 310 | 2014-04-16 12:35 | 2014-04-16 14:30 | 479 | 530 | 493 | Pulverizer mills | F780Load raised to 479MW, but derate was still due to E Coal Mill trip. | Trimble | Derate | Coal | 3 | 2014 | 4 | 1.9167 | 0.18443 | 90.9259 | 47.4396 | 47
TC1 | D1 | 52 | 310 | 2014-04-16 14:30 | 2014-04-16 18:41 | 370 | 530 | 493 | Pulverizer mills | F820Derate to 370MW due to mill runback caused by mill issues/trips. | Trimble | Derate | Coal | 3 | 2014 | 4 | 4.1833 | 1.2629 | 622.6063 | 148.8302 | 149
TC1 | D1 | 53 | 310 | 2014-04-16 18:41 | 2014-04-16 21:31 | 480 | 530 | 493 | Pulverizer mills | F820Derate to 480MW due to mill runback caused by mill issues/trips. | Trimble | Derate | Coal | 3 | 2014 | 4 | 2.8333 | 0.2673 | 131.7767 | 46.5094 | 47
TC1 | D1 | 54 | 1455 | 2014-04-16 21:31 | 2014-04-17 07:05 | 525 | 530 | 493 | Induced draft fans | F8501B ID Fan Bearing vibrations required unit derate to keep vibrations within limits | Trimble | Derate | Coal | 3 | 2014 | 4 | 9.5667 | 0.090252 | 44.494 | 4.6509 | 5
TC1 | D1 | 55 | 310 | 2014-04-17 07:05 | 2014-04-17 07:55 | 475 | 530 | 493 | Pulverizer mills | F780Derate required due to 1B coal mill fire | Trimble | Derate | Coal | 3 | 2014 | 4 | 0.83333 | 0.086478 | 42.6336 | 51.1604 | 51
TC1 | D1 | 56 | 1455 | 2014-04-17 07:55 | 2014-04-17 08:57 | 525 | 530 | 493 | Induced draft fans | F8501B ID Fan Bearing vibrations required unit derate to keep vibrations within limits | Trimble | Derate | Coal | 3 | 2014 | 4 | 1.0333 | 0.0097484 | 4.806 | 4.6509 | 5
TC1 | D1 | 57 | 310 | 2014-04-17 08:57 | 2014-04-17 12:08 | 475 | 530 | 493 | Pulverizer mills | F780Mill fires required unit derate. | Trimble | Derate | Coal | 3 | 2014 | 4 | 3.1833 | 0.33035 | 162.8605 | 51.1604 | 51
TC1 | D1 | 58 | 1455 | 2014-04-17 12:08 | 2014-04-17 16:33 | 525 | 530 | 493 | Induced draft fans | F8501B ID Fan Bearing vibrations required unit derate to keep vibrations within limits | Trimble | Derate | Coal | 3 | 2014 | 4 | 4.4167 | 0.041667 | 20.5417 | 4.6509 | 5
TC1 | D1 | 59 | 310 | 2014-04-17 16:33 | 2014-04-17 19:08 | 450 | 530 | 493 | Pulverizer mills | F780Mill fires required unit derate to 450MW. | Trimble | Derate | Coal | 3 | 2014 | 4 | 2.5833 | 0.38994 | 192.239 | 74.4151 | 74
TC1 | D1 | 60 | 1455 | 2014-04-17 19:08 | 2014-04-23 12:52 | 525 | 530 | 493 | Induced draft fans | F8501B ID fan vibrations are high requiring unit derate to keep the vibrations within | Trimble | Derate | Coal | 3 | 2014 | 4 | 137.7333 | 1.2994 | 640.5899 | 4.6509 | 5
TC1 | D1 | 61 | 310 | 2014-04-23 12:52 | 2014-04-23 18:07 | 475 | 530 | 493 | Pulverizer mills | F780Derate was required after 1B Coal mill became unavailable due to a fire and the 1D | Trimble | Derate | Coal | 3 | 2014 | 4 | 5.25 | 0.54481 | 268.592 | 51.1604 | 51
TC1 | D1 | 62 | 1455 | 2014-04-23 18:07 | 2014-04-24 08:15 | 525 | 530 | 493 | Induced draft fans | F8501B ID fan vibrations are high requiring unit derate to keep the vibrations within | Trimble | Derate | Coal | 3 | 2014 | 4 | 14.1333 | 0.13333 | 65.7333 | 4.6509 | 5
TC1 | D1 | 63 | 3235 | 2014-04-24 08:15 | 2014-04-24 08:47 | 300 | 530 | 493 | Cooling tower booster pump | F820The "A" cooling tower pump tripped, the unit went into a runback which in turn tri | Trimble | Derate | Coal | 3 | 2014 | 4 | 0.53333 | 0.23145 | 114.1031 | 213.9434 | 214
TC1 | D1 | 64 | 3235 | 2014-04-24 08:47 | 2014-04-24 10:35 | 375 | 530 | 493 | Cooling tower booster pump | F820Following the initial run back on the unit from the cooling tower pump trip and su | Trimble | Derate | Coal | 3 | 2014 | 4 | 1.8 | 0.52642 | 259.5226 | 144.1792 | 144
TC1 | D1 | 65 | 1455 | 2014-04-24 10:35 | 2014-04-24 14:58 | 525 | 530 | 493 | Induced draft fans | F8501B ID fan vibrations are high requiring unit derate to keep the vibrations within | Trimble | Derate | Coal | 3 | 2014 | 4 | 4.3833 | 0.041352 | 20.3866 | 4.6509 | 5
TC1 | D1 | 66 | 310 | 2014-04-24 14:58 | 2014-04-24 20:01 | 475 | 530 | 493 | Pulverizer mills | F7801B coal mill caught fire and the 1A and 1D mills were unavailable requiring unit d | Trimble | Derate | Coal | 3 | 2014 | 4 | 5.05 | 0.52406 | 258.3599 | 51.1604 | 51
TC1 | D1 | 67 | 1455 | 2014-04-24 20:01 | 2014-05-09 00:24 | 525 | 530 | 493 | Induced draft fans | F8501B ID fan vibrations are high requiring unit derate to keep the vibrations within | Trimble | Derate | Coal | 3 | 2014 | 4 | 340.3833 | 3.2112 | 1583.1036 | 4.6509 | 5
TC1 | D1 | 68 | 310 | 2014-04-29 09:00 | 2014-04-29 16:33 | 500 | 530 | 493 | Pulverizer mills | F850Unit derated an additional 25 MW due to various mill issues during this period. A | Trimble | Derate | Coal | 3 | 2014 | 4 | 7.55 | 0.42736 | 210.6877 | 27.9057 | 28
TC1 | MO | 69 | 1495 | 2014-05-09 00:24 | 2014-05-12 10:31 | 0 | 530 | 493 | Other air heater fouling (heat pipe | F320TC1 required a maintenance outage to conduct an air heater wash due to increased d | Trimble | Maintenance | Coal | 3 | 2014 | 5 | 82.1167 | 82.1167 | 40483.5167 | 493 | 493
TC1 | NC | 70 | 1850 | 2014-05-12 20:04 | 2014-05-13 00:24 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00This non-curtailing derate was due to a silica hold on the unit until boiler water | Trimble | Other | Coal | 3 | 2014 | 5 | 4.3333 | 4.3333 | 2136.3333 | 493 | 493
TC1 | NC | 71 | 8813 | 2014-05-20 08:15 | 2014-05-20 18:15 | 0 | 530 | 493 | SCR NOx Injection grid piping/valves | F790Testing of the TC1 SCR was conducted to compare inlet/outlet/CEMS data for SCR NOx | Trimble | Other | Coal | 3 | 2014 | 5 | 10 | 10 | 4930 | 493 | 493
TC1 | D1 | 72 | 330 | 2014-05-21 05:29 | 2014-05-21 06:15 | 525 | 530 | 493 | Pulverizer coal leak (pulverizers only) | F540Derate was required on TC1 to 525MW due to a coal leak on the 1E mill. The 1C Mil | Trimble | Derate | Coal | 3 | 2014 | 5 | 0.76667 | 0.0072327 | 3.5657 | 4.6509 | 5
TC1 | NC | 73 | 8813 | 2014-05-21 07:17 | 2014-05-21 17:30 | 0 | 530 | 493 | SCR NOx Injection grid piping/valves | F790Testing of the TC1 SCR was conducted to compare inlet/outlet/CEMS data for SCR NOx | Trimble | Other | Coal | 3 | 2014 | 5 | 10.2167 | 10.2167 | 5036.8167 | 493 | 493
TC1 | NC | 74 | 8813 | 2014-05-22 06:25 | 2014-05-22 11:10 | 0 | 530 | 493 | SCR NOx Injection grid piping/valves | F790Testing of the TC1 SCR was conducted to compare inlet/outlet/CEMS data for SCR NOx | Trimble | Other | Coal | 3 | 2014 | 5 | 4.75 | 4.75 | 2341.75 | 493 | 493
TC1 | D1 | 75 | 1420 | 2014-05-22 13:38 | 2014-05-27 11:04 | 530 | 530 | 493 | Other forced draft fan problems | F640Derate to 530MW is required on TC1 due to high air flow on the unit from excess st | Trimble | Derate | Coal | 3 | 2014 | 5 | 117.4333 | 0 | 0 | 0 | 0
TC1 | NC | 76 | 4267 | 2014-05-25 01:00 | 2014-05-25 01:30 | 0 | 530 | 493 | Control valve testing | F790Non-curtailing derate to 485MW for a weekly valve check on the unit. Unit was rea | Trimble | Other | Coal | 3 | 2014 | 5 | 0.5 | 0.5 | 246.5 | 493 | 493
TC1 | D1 | 77 | 1470 | 2014-05-29 13:58 | 2014-05-29 15:00 | 530 | 530 | 493 | Induced draft fan motors and drives | F870Derate to 530MW due to high amps on the ID Fans. | Trimble | Derate | Coal | 3 | 2014 | 5 | 1.0333 | 0 | 0 | 0 | 0
TC1 | D4 | 78 | 1305 | 2014-06-04 23:04 | 2014-06-05 01:04 | 450 | 530 | 493 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | FS00TC1 had a planned maintenance derate to conduct a boiler deslag on the furnace. | Trimble | Derate | Coal | 3 | 2014 | 6 | 2 | 0.30189 | 148.8302 | 74.4151 | 74
TC1 | NC | 79 | 1599 | 2014-06-10 08:45 | 2014-06-10 09:38 | 0 | 530 | 493 | Other miscellaneous boiler air and gas system problems | F090Unit was not derated, but load was controlled to allow for O2 probe calibration. | Trimble | Other | Coal | 3 | 2014 | 6 | 0.88333 | 0.88333 | 435.4833 | 493 | 493
TC1 | D4 | 80 | 1160 | 2014-06-11 04:00 | 2014-06-11 05:25 | 450 | 530 | 493 | First reheater B | F410Planned maintenance derate to allow I/E to work on the valve controls for the Rehe | Trimble | Derate | Coal | 3 | 2014 | 6 | 1.4167 | 0.21384 | 105.4214 | 74.4151 | 74
TC1 | D1 | 81 | 360 | 2014-06-11 08:58 | 2014-06-12 00:32 | 525 | 530 | 493 | Burners | F130Derate to 525 required due to 1A and 1E coal mill having blanked burners. | Trimble | Derate | Coal | 3 | 2014 | 6 | 15.5667 | 0.14686 | 72.3997 | 4.6509 | 5
TC1 | U1 | 82 | 1457 | 2014-06-12 00:32 | 2014-06-12 01:21 | 0 | 530 | 493 | Induced draft fan lubrication systems | F820During a lube oil pump swap for the 1A ID Fan, the second lube oil pump failed to | Trimble | Outage | Coal | 3 | 2014 | 6 | 0.81667 | 0.81667 | 402.6167 | 493 | 493
TC1 | D1 | 83 | 360 | 2014-06-12 03:17 | 2014-06-12 08:20 | 525 | 530 | 493 | Burners | F130Derate to 525MW was required due to 1A and 1E coal mills still having burners blan | Trimble | Derate | Coal | 3 | 2014 | 6 | 5.05 | 0.047642 | 23.4873 | 4.6509 | 5
TC1 | D1 | 84 | 346 | 2014-06-12 08:20 | 2014-06-12 09:21 | 475 | 530 | 493 | Pulverizer pyrite removal system | F820While pullling pyrites on the 1E coal mill, a failed pyrite valve resulted in the | Trimble | Derate | Coal | 3 | 2014 | 6 | 1.0167 | 0.1055 | 52.0131 | 51.1604 | 51
TC1 | D1 | 85 | 360 | 2014-06-12 09:21 | 2014-06-12 22:00 | 525 | 530 | 493 | Burners | F130Derate of 525MW is required due to 1A and 1E coal mill having burners blanked off. | Trimble | Derate | Coal | 3 | 2014 | 6 | 12.65 | 0.11934 | 58.8344 | 4.6509 | 5
TC1 | D1 | 86 | 8825 | 2014-06-12 22:00 | 2014-06-13 03:00 | 375 | 530 | 493 | Other SCR NOx problems | F540Derate to 375MW required to allow maintenance to repair a leak on the SCR water co | Trimble | Derate | Coal | 3 | 2014 | 6 | 5 | 1.4623 | 720.8962 | 144.1792 | 144
TC1 | D1 | 87 | 360 | 2014-06-13 03:00 | 2014-06-16 06:41 | 525 | 530 | 493 | Burners | F130Derate of 525MW is required due to 1A and 1E coal mill having burners blanked off. | Trimble | Derate | Coal | 3 | 2014 | 6 | 75.6833 | 0.71399 | 351.9989 | 4.6509 | 5
TC1 | D1 | 88 | 310 | 2014-06-16 06:41 | 2014-06-16 06:57 | 375 | 530 | 493 | Pulverizer mills | F7801D coal mill caught fire and was removed from service causing load to drop to 375M | Trimble | Derate | Coal | 3 | 2014 | 6 | 0.26667 | 0.077987 | 38.4478 | 144.1792 | 144
TC1 | D1 | 89 | 360 | 2014-06-16 06:57 | 2014-06-17 22:12 | 525 | 530 | 493 | Burners | F130Derate of 525MW is required due to 1A and 1E coal mill having burners blanked off. | Trimble | Derate | Coal | 3 | 2014 | 6 | 39.25 | 0.37028 | 182.5495 | 4.6509 | 5
TC1 | U1 | 90 | 530 | 2014-06-17 22:12 | 2014-06-19 04:24 | 0 | 530 | 493 | Other main steam system problems | F820A thermowell on the TC1 Main Steam line failed at a weld and caused a steam leak o | Trimble | Outage | Coal | 3 | 2014 | 6 | 30.2 | 30.2 | 14888.6 | 493 | 493
TC1 | D1 | 91 | 350 | 2014-06-19 14:19 | 2014-06-19 15:40 | 500 | 530 | 493 | Pulverized fuel and air piping (from pulverizer to wind box) | F540Derate required on the unit when the 1A coal conduit began leaking. | Trimble | Derate | Coal | 3 | 2014 | 6 | 1.35 | 0.076415 | 37.6726 | 27.9057 | 28
TC1 | NC | 92 | 1190 | 2014-07-05 | 2014-07-05 05:00 | 0 | 530 | 493 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct a boiler deslag on the unit. Unit was available t | Trimble | Other | Coal | 3 | 2014 | 7 | 5 | 5 | 2465 | 493 | 493
TC1 | NC | 93 | 4267 | 2014-07-06 01:00 | 2014-07-06 01:30 | 0 | 530 | 493 | Control valve testing | F790Non-curtailing derate to conduct a valve test on the unit. Unit was available to r | Trimble | Other | Coal | 3 | 2014 | 7 | 0.5 | 0.5 | 246.5 | 493 | 493
TC1 | D1 | 94 | 4267 | 2014-07-08 | 2014-07-08 00:08 | 450 | 530 | 493 | Control valve testing | F790Derate required to conduct testing on control valves. | Trimble | Derate | Coal | 3 | 2014 | 7 | 0.13333 | 0.020126 | 9.922 | 74.4151 | 74
TC1 | U1 | 95 | 4267 | 2014-07-08 00:08 | 2014-07-08 04:12 | 0 | 530 | 493 | Control valve testing | F820During the control valve testing and while changing out a servo filter, the unit w | Trimble | Outage | Coal | 3 | 2014 | 7 | 4.0667 | 4.0667 | 2004.8667 | 493 | 493
TC1 | U1 | 96 | 3412 | 2014-07-08 05:41 | 2014-07-08 06:22 | 0 | 530 | 493 | Feedwater pump drive - steam turbine | F820While ramping the unit from the initial forced outage, one of the turbine driven b | Trimble | Outage | Coal | 3 | 2014 | 7 | 0.68333 | 0.68333 | 336.8833 | 493 | 493
TC1 | MO | 97 | 1090 | 2014-07-19 00:07 | 2014-07-20 22:24 | 0 | 530 | 493 | Other boiler tube leaks | F540Maintenance outage to inspect for an expected boiler tube leak in the penthouse. N | Trimble | Maintenance | Coal | 3 | 2014 | 7 | 46.2833 | 46.2833 | 22817.6833 | 493 | 493
TC1 | D1 | 98 | 3352 | 2014-07-21 08:24 | 2014-07-21 11:15 | 430 | 530 | 493 | Feedwater chemistry (not specific to condenser | FA00Derate at 430MW due to silica levels in the feedwater chemistry. | Trimble | Derate | Coal | 3 | 2014 | 7 | 2.85 | 0.53774 | 265.1038 | 93.0189 | 93
TC1 | D1 | 99 | 3352 | 2014-07-21 11:15 | 2014-07-21 22:30 | 530 | 530 | 493 | Feedwater chemistry (not specific to condenser | FA00Non-curtailing derate at 530MW due to silica levels in the feedwater chemistry. | Trimble | Derate | Coal | 3 | 2014 | 7 | 11.25 | 0 | 0 | 0 | 0
TC1 | NC | 100 | 4267 | 2014-07-31 07:40 | 2014-07-31 11:25 | 0 | 530 | 493 | Control valve testing | F790Non-curtailing full load test on the turbine control valves. | Trimble | Other | Coal | 3 | 2014 | 7 | 3.75 | 3.75 | 1848.75 | 493 | 493
TC1 | MO | 101 | 4261 | 2014-08-01 00:24 | 2014-08-03 23:38 | 0 | 530 | 493 | Control valves | F720During a past control valve test, the #4 CV on TC1 stuck open twice. This mainten | Trimble | Maintenance | Coal | 3 | 2014 | 8 | 71.2333 | 71.2333 | 35118.0333 | 493 | 493
TC1 | D4 | 102 | 4279 | 2014-08-08 | 2014-08-08 00:44 | 450 | 530 | 493 | Miscellaneous turbine piping | F540Maintenance derate to repair the Reheat Spray Line reference line. | Trimble | Derate | Coal | 3 | 2014 | 8 | 0.73333 | 0.11069 | 54.5711 | 74.4151 | 74
TC1 | NC | 103 | 3624 | 2014-08-14 10:15 | 2014-08-14 12:30 | 0 | 530 | 493 | Generator Voltage Supply System | F790Non-curtailing event to conduct VAR testing. Unit was at full load but removed fr | Trimble | Other | Coal | 3 | 2014 | 8 | 2.25 | 2.25 | 1109.25 | 493 | 493
TC1 | NC | 104 | 1190 | 2014-08-17 | 2014-08-17 08:24 | 0 | 530 | 493 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct planned boiler deslag. Unit was available to ret | Trimble | Other | Coal | 3 | 2014 | 8 | 8.4 | 8.4 | 4141.2 | 493 | 493
TC1 | NC | 105 | 1990 | 2014-08-20 08:45 | 2014-08-20 14:35 | 0 | 530 | 493 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Non-curtailing derate to conduct heat rate test on the unit. Unit was removed fro | Trimble | Other | Coal | 3 | 2014 | 8 | 5.8333 | 5.8333 | 2875.8333 | 493 | 493
TC1 | D1 | 106 | 346 | 2014-08-20 16:15 | 2014-08-20 18:19 | 470 | 530 | 493 | Pulverizer pyrite removal system | F400A malfunctioning pyrite disposal valve caused water to backup into the mill requir | Trimble | Derate | Coal | 3 | 2014 | 8 | 2.0667 | 0.23396 | 115.3434 | 55.8113 | 56
TC1 | D1 | 107 | 340 | 2014-08-21 13:55 | 2014-08-21 15:12 | 460 | 530 | 493 | Other pulverizer problems | F120B Mill issues requiring isolation for cleaning of duct work and I/E to clear instr | Trimble | Derate | Coal | 3 | 2014 | 8 | 1.2833 | 0.1695 | 83.5619 | 65.1132 | 65
TC1 | D1 | 108 | 340 | 2014-08-21 15:12 | 2014-08-22 04:28 | 535 | 530 | 493 | Other pulverizer problems | F120B Mill issues requiring isolation for cleaning of duct work and I/E to clear instr | Trimble | Derate | Coal | 3 | 2014 | 8 | 13.2667 | -0.12516 | -61.7025 | 0 | 0
TC1 | D1 | 109 | 280 | 2014-08-23 19:42 | 2014-08-24 01:46 | 525 | 530 | 493 | Pulverizer fires | F780B Coal mill caught fire. Removed from service to clear out mill. | Trimble | Derate | Coal | 3 | 2014 | 8 | 6.0667 | 0.057233 | 28.2157 | 4.6509 | 5
TC1 | D1 | 110 | 280 | 2014-08-24 06:00 | 2014-08-24 06:58 | 375 | 530 | 493 | Pulverizer fires | F780Fires in the A and B mills required derate for mill isolation and clear out. | Trimble | Derate | Coal | 3 | 2014 | 8 | 0.96667 | 0.2827 | 139.3733 | 144.1792 | 144
TC1 | D1 | 111 | 1455 | 2014-08-27 12:37 | 2014-08-27 12:53 | 540 | 530 | 493 | Induced draft fans | F640Derate on the unit due to ID fans experiencing high amps. Load was reduced until | Trimble | Derate | Coal | 3 | 2014 | 8 | 0.26667 | -0.0050314 | -2.4805 | 0 | 0
TC1 | D1 | 112 | 4261 | 2014-08-31 01:45 | 2014-08-31 06:10 | 460 | 530 | 493 | Control valves | F690Derate was placed on the unit due to #3 CV not operating correctly. Troubleshooti | Trimble | Derate | Coal | 3 | 2014 | 8 | 4.4167 | 0.58333 | 287.5833 | 65.1132 | 65
TC1 | D1 | 113 | 4261 | 2014-08-31 06:10 | 2014-08-31 13:20 | 438 | 530 | 493 | Control valves | F690Derate on the unit to troubleshoot #3 CV which was sticking during unit operation. | Trimble | Derate | Coal | 3 | 2014 | 8 | 7.1667 | 1.244 | 613.3044 | 85.5774 | 86
TC1 | D1 | 114 | 4261 | 2014-08-31 13:20 | 2014-08-31 15:36 | 460 | 530 | 493 | Control valves | F690Derate on the unit to troubleshoot #3 CV which was sticking during unit operation. | Trimble | Derate | Coal | 3 | 2014 | 8 | 2.2667 | 0.29937 | 147.5899 | 65.1132 | 65
TC1 | MO | 115 | 4261 | 2014-08-31 15:36 | 2014-09-01 00:35 | 0 | 530 | 493 | Control valves | F690TC1 was taken off line for maintenance and inspection of the #3 CV which would not | Trimble | Maintenance | Coal | 3 | 2014 | 8 | 8.9833 | 8.9833 | 4428.7833 | 493 | 493
TC1 | D1 | 116 | 530 | 2014-09-04 10:15 | 2014-09-04 11:00 | 450 | 530 | 493 | Other main steam system problems | F660Unit was derated due to unit pressure swings from sootblower maintenance being con | Trimble | Derate | Coal | 3 | 2014 | 9 | 0.75 | 0.11321 | 55.8113 | 74.4151 | 74
TC1 | D1 | 117 | 410 | 2014-09-23 23:00 | 2014-09-24 03:07 | 400 | 530 | 493 | Other burner problems | F780Unit derate was due to a C Coal Mill burner fire. Took mill out of service then p | Trimble | Derate | Coal | 3 | 2014 | 9 | 4.1167 | 1.0097 | 497.806 | 120.9245 | 121
TC1 | D1 | 118 | 310 | 2014-09-25 08:37 | 2014-09-25 15:44 | 515 | 530 | 493 | Pulverizer mills | F780Unit derated due to two mills unavailable and limit on third mill: 1E mill out of | Trimble | Derate | Coal | 3 | 2014 | 9 | 7.1167 | 0.20142 | 99.2976 | 13.9528 | 14
TC1 | NC | 119 | 1190 | 2014-09-27 | 2014-09-27 05:00 | 0 | 530 | 493 | Other tube slagging or fouling | FS00Non-curtailing derate on the unit to conduct a planned unit deslag. The unit was | Trimble | Other | Coal | 3 | 2014 | 9 | 5 | 5 | 2465 | 493 | 493
TC1 | NC | 120 | 4267 | 2014-09-28 | 2014-09-28 00:24 | 0 | 530 | 493 | Control valve testing | F790Non-curtailing derate to conduct the planned, weekly valve test on the unit. The | Trimble | Other | Coal | 3 | 2014 | 9 | 0.4 | 0.4 | 197.2 | 493 | 493
TC1 | D1 | 121 | 310 | 2014-10-07 17:17 | 2014-10-07 17:54 | 517 | 530 | 493 | Pulverizer mills | F400Derate placed on unit to 517MW due to air flow issues on the A, C, and D coal mill | Trimble | Derate | Coal | 3 | 2014 | 10 | 0.61667 | 0.015126 | 7.457 | 12.0925 | 12
TC1 | U1 | 122 | 400 | 2014-10-07 18:30 | 2014-10-10 13:24 | 0 | 530 | 493 | Burner wind box fires | FR00TC1 was taken offline due to a fire at the A3 burner windbox area. Severe damager | Trimble | Outage | Coal | 3 | 2014 | 10 | 66.9 | 66.9 | 32981.7 | 493 | 493
TC1 | D1 | 123 | 360 | 2014-10-10 20:50 | 2014-10-10 23:00 | 380 | 530 | 493 | Burners | FR00Unit was derated when the C mill had a fire in the C2 burner in the insulation and | Trimble | Derate | Coal | 3 | 2014 | 10 | 2.1667 | 0.61321 | 302.3113 | 139.5283 | 140
TC1 | D1 | 124 | 360 | 2014-10-10 23:00 | 2014-10-11 03:10 | 460 | 530 | 493 | Burners | FR00Following the return from the derate due to the C mill burner fire, the unit was a | Trimble | Derate | Coal | 3 | 2014 | 10 | 4.1667 | 0.55031 | 271.305 | 65.1132 | 65
TC1 | U1 | 125 | 3410 | 2014-10-30 06:00 | 2014-10-30 07:49 | 0 | 530 | 493 | Feedwater pump | F820TC1 tripped due to a feedwater and steam flow mismatch which resulted because of a | Trimble | Outage | Coal | 3 | 2014 | 10 | 1.8167 | 1.8167 | 895.6167 | 493 | 493
TC1 | D1 | 126 | 4261 | 2014-10-31 21:51 | 2014-11-01 06:00 | 390 | 530 | 493 | Control valves | F400The #3 control valve was drifting closed requiring a unit derate. | Trimble | Derate | Coal | 3 | 2014 | 10 | 8.15 | 2.1528 | 1061.3453 | 130.2264 | 130
TC1 | D1 | 127 | 4261 | 2014-11-01 06:00 | 2014-11-01 22:45 | 380 | 530 | 493 | Control valves | F400The #3 control valve continued drifting closed and required a slightly further der | Trimble | Derate | Coal | 3 | 2014 | 11 | 16.75 | 4.7406 | 2337.0991 | 139.5283 | 140
TC1 | U1 | 128 | 4261 | 2014-11-01 22:45 | 2014-11-02 12:03 | 0 | 530 | 493 | Control valves | F400The unit was taken offline to work on the #3 control valve which was found to have | Trimble | Outage | Coal | 3 | 2014 | 11 | 13.3 | 13.3 | 6556.9 | 493 | 493
TC1 | D1 | 129 | 3431 | 2014-11-02 22:00 | 2014-11-03 01:10 | 485 | 530 | 493 | Other feedwater valves | F130The 1A TDBFP discharge valve won't open requiring a unit derate. | Trimble | Derate | Coal | 3 | 2014 | 11 | 3.1667 | 0.26887 | 132.5519 | 41.8585 | 42
TC1 | D1 | 130 | 3431 | 2014-11-03 01:10 | 2014-11-03 13:10 | 515 | 530 | 493 | Other feedwater valves | F130The 1A TDBFP discharge valve won't open requiring a unit derate. | Trimble | Derate | Coal | 3 | 2014 | 11 | 12 | 0.33962 | 167.434 | 13.9528 | 14
TC1 | U1 | 131 | 3412 | 2014-11-08 02:00 | 2014-11-08 04:54 | 0 | 530 | 493 | Feedwater pump drive - steam turbine | F820The 1B TDBFP malfunctioned during the emergency governor test. | Trimble | Outage | Coal | 3 | 2014 | 11 | 2.9 | 2.9 | 1429.7 | 493 | 493
TC1 | D1 | 132 | 340 | 2014-11-13 09:47 | 2014-11-13 11:36 | 520 | 530 | 493 | Other pulverizer problems | F540Leak on the 1D coal mill hydraulic system caused a unit derate to 520MW. | Trimble | Derate | Coal | 3 | 2014 | 11 | 1.8167 | 0.034277 | 16.8984 | 9.3019 | 9
TC1 | D1 | 133 | 3410 | 2014-11-16 06:30 | 2014-11-16 23:14 | 525 | 530 | 493 | Feedwater pump | F540A leak on the 1B turbine driven boiler feed pump suction line caused a unit derate | Trimble | Derate | Coal | 3 | 2014 | 11 | 16.7333 | 0.15786 | 77.8258 | 4.6509 | 5
TC1 | U1 | 134 | 1455 | 2014-11-17 01:40 | 2014-11-17 15:28 | 0 | 530 | 493 | Induced draft fans | F820Unit 1 went on a forced outage after the 1B ID fan tripped. The trip on the ID fa | Trimble | Outage | Coal | 3 | 2014 | 11 | 13.8 | 13.8 | 6803.4 | 493 | 493
TC1 | U1 | 135 | 1400 | 2014-11-18 01:07 | 2014-11-18 03:03 | 0 | 530 | 493 | Forced draft fans | F870TC1 is believe to have tripped due to the 1B FD fan having a power supply issue to | Trimble | Outage | Coal | 3 | 2014 | 11 | 1.9333 | 1.9333 | 953.1333 | 493 | 493
TC1 | NC | 136 | 9620 | 2014-11-18 14:00 | 2014-11-18 20:45 | 0 | 530 | 493 | Particulate stack emissions (fossil) | F790Non-curtailing event on the unit to conduct PM testing, requirements for the test | Trimble | Other | Coal | 3 | 2014 | 11 | 6.75 | 6.75 | 3327.75 | 493 | 493
TC1 | U1 | 137 | 740 | 2014-11-22 05:09 | 2014-11-22 21:51 | 0 | 530 | 493 | Boiler recirculation pumps | F820TC1 MFT due to the BCP suction valves showing closed which was due to a DCS proces | Trimble | Outage | Coal | 3 | 2014 | 11 | 16.7 | 16.7 | 8233.1 | 493 | 493
TC1 | D1 | 138 | 310 | 2014-11-23 03:30 | 2014-11-23 04:19 | 400 | 530 | 493 | Pulverizer mills | FR00Derate due to removal of the A coal mill from service as a result of the corner fi | Trimble | Derate | Coal | 3 | 2014 | 11 | 0.81667 | 0.20031 | 98.755 | 120.9245 | 121
TC1 | U1 | 139 | 400 | 2014-11-23 04:19 | 2014-11-24 12:03 | 0 | 530 | 493 | Burner wind box fires | FR00Following the burner fire the decision was made to remove the unit from service wh | Trimble | Outage | Coal | 3 | 2014 | 11 | 31.7333 | 31.7333 | 15644.5333 | 493 | 493
TC1 | D1 | 140 | 530 | 2014-12-07 09:41 | 2014-12-07 16:15 | 535 | 530 | 493 | Other main steam system problems | F660Unit 2 using Unit 1 steam during Unit 2 start-up. | Trimble | Derate | Coal | 3 | 2014 | 12 | 6.5667 | -0.06195 | -30.5412 | 0 | 0
TC1 | D1 | 141 | 300 | 2014-12-17 18:44 | 2014-12-18 05:30 | 530 | 530 | 493 | Pulverizer motors and drives | F870Coal Pulverizer motor current increased above the high limit, forcing a derate. | Trimble | Derate | Coal | 3 | 2014 | 12 | 10.7667 | 0 | 0 | 0 | 0
TC1 | D1 | 142 | 300 | 2014-12-18 10:50 | 2014-12-18 23:49 | 540 | 530 | 493 | Pulverizer motors and drives | F870Coal pulverizer motor current increased above the high limit, forcing a derate. | Trimble | Derate | Coal | 3 | 2014 | 12 | 12.9833 | -0.24497 | -120.7695 | 0 | 0
TC1 | D1 | 143 | 300 | 2014-12-19 06:33 | 2014-12-21 00:40 | 530 | 530 | 493 | Pulverizer motors and drives | F870Coal pulverizer motor current increased above the high limit, forcing a derate. | Trimble | Derate | Coal | 3 | 2014 | 12 | 42.1167 | 0 | 0 | 0 | 0
TC1 | D4 | 144 | 4267 | 2014-12-21 00:40 | 2014-12-21 01:09 | 485 | 530 | 493 | Control valve testing | F790Derate to conduct turbine bypass control valve testing. Unit was available for fu | Trimble | Derate | Coal | 3 | 2014 | 12 | 0.48333 | 0.041038 | 20.2316 | 41.8585 | 42
TC1 | D1 | 145 | 300 | 2014-12-21 01:09 | 2014-12-21 08:30 | 530 | 530 | 493 | Pulverizer motors and drives | F870Coal pulverizer motor current increased above the high limit, forcing a derate. | Trimble | Derate | Coal | 3 | 2014 | 12 | 7.35 | 0 | 0 | 0 | 0
TC1 | D1 | 146 | 300 | 2014-12-22 18:25 | 2014-12-23 07:53 | 530 | 530 | 493 | Pulverizer motors and drives | F870Coal pulverizer motor current increased above the high limit, forcing a derate. | Trimble | Derate | Coal | 3 | 2014 | 12 | 13.4667 | 0 | 0 | 0 | 0
TC1 | D1 | 1 | 300 | 2015-01-05 18:00 | 2015-01-06 06:37 | 525 | 530 | 493 | Pulverizer motors and drives | F870Coal Pulverizer motor current increased above the high limit, forcing a derate. | Trimble | Derate | Coal | 3 | 2015 | 1 | 12.6167 | 0.11903 | 58.6794 | 4.6509 | 5
TC1 | D1 | 2 | 280 | 2015-01-14 10:18 | 2015-01-14 17:45 | 525 | 530 | 493 | Pulverizer fires | FW00Derate due to 1A mill fire. Mill was taken out of service, cleaned out, and inspe | Trimble | Derate | Coal | 3 | 2015 | 1 | 7.45 | 0.070283 | 34.6495 | 4.6509 | 5
TC1 | D1 | 3 | 300 | 2015-01-14 17:45 | 2015-01-14 21:40 | 510 | 530 | 493 | Pulverizer motors and drives | F400During mill swaps the mills experienced some high mill amps requiring a unit derat | Trimble | Derate | Coal | 3 | 2015 | 1 | 3.9167 | 0.1478 | 72.8648 | 18.6038 | 19
TC1 | D1 | 4 | 280 | 2015-01-18 23:30 | 2015-01-19 00:10 | 375 | 530 | 493 | Pulverizer fires | FR00The 1D coal mill had a temperature spike which brought the mill offline. Inspecti | Trimble | Derate | Coal | 3 | 2015 | 1 | 0.66667 | 0.19497 | 96.1195 | 144.1792 | 144
TC1 | D1 | 5 | 280 | 2015-01-19 00:10 | 2015-01-19 02:03 | 400 | 530 | 493 | Pulverizer fires | FR00The 1D coal mill had a temperature spike which brought the mill offline. Inspecti | Trimble | Derate | Coal | 3 | 2015 | 1 | 1.8833 | 0.46195 | 227.7412 | 120.9245 | 121
TC1 | NC | 6 | 9656 | 2015-01-20 08:00 | 2015-01-20 16:50 | 0 | 530 | 493 | Other stack or exhaust emissions testing - fossil | F790Non-curtailing event holding unit at full load to conduct RATA testing. | Trimble | Other | Coal | 3 | 2015 | 1 | 8.8333 | 8.8333 | 4354.8333 | 493 | 493
TC1 | NC | 7 | 9656 | 2015-01-21 09:00 | 2015-01-21 16:12 | 0 | 530 | 493 | Other stack or exhaust emissions testing - fossil | F790Non-curtailing event holding unit at full load to conduct RATA testing. | Trimble | Other | Coal | 3 | 2015 | 1 | 7.2 | 7.2 | 3549.6 | 493 | 493
TC1 | D4 | 8 | 4261 | 2015-01-23 22:00 | 2015-01-24 08:00 | 380 | 530 | 493 | Control valves | F790Variable load planned derate to conduct control valve testing and tuning on the un | Trimble | Derate | Coal | 3 | 2015 | 1 | 10 | 2.8302 | 1395.283 | 139.5283 | 140
TC1 | D4 | 9 | 3431 | 2015-01-24 08:00 | 2015-01-24 14:34 | 525 | 530 | 493 | Other feedwater valves | F790Derate to conduct governor trip test on the TDBFP's for TC1. All tests completed | Trimble | Derate | Coal | 3 | 2015 | 1 | 6.5667 | 0.06195 | 30.5412 | 4.6509 | 5
TC1 | D1 | 10 | 9999 | 2015-01-30 22:00 | 2015-01-30 23:00 | 362 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 1 | 0.31698 | 156.2717 | 156.2717 | 156
TC1 | D1 | 11 | 9999 | 2015-01-30 23:00 | 2015-01-31 | 312 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 1 | 0.41132 | 202.7811 | 202.7811 | 203
TC1 | D4 | 12 | 9999 | 2015-01-31 | 2015-01-31 01:00 | 305 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 1 | 0.42453 | 209.2925 | 209.2925 | 209
TC1 | D4 | 13 | 9999 | 2015-01-31 01:00 | 2015-01-31 02:00 | 215 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 1 | 0.59434 | 293.0094 | 293.0094 | 293
TC1 | D4 | 14 | 9999 | 2015-01-31 02:00 | 2015-01-31 03:00 | 205 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 1 | 0.61321 | 302.3113 | 302.3113 | 302
TC1 | D4 | 15 | 9999 | 2015-01-31 03:00 | 2015-01-31 04:00 | 207 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 1 | 0.60943 | 300.4509 | 300.4509 | 300
TC1 | D4 | 16 | 9999 | 2015-01-31 04:00 | 2015-01-31 05:00 | 248 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 1 | 0.53208 | 262.3132 | 262.3132 | 262
TC1 | D4 | 17 | 9999 | 2015-01-31 05:00 | 2015-01-31 06:00 | 317 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 1 | 0.40189 | 198.1302 | 198.1302 | 198
TC1 | D4 | 18 | 9999 | 2015-01-31 06:00 | 2015-01-31 07:00 | 347 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 1 | 0.34528 | 170.2245 | 170.2245 | 170
TC1 | D4 | 19 | 9999 | 2015-01-31 07:00 | 2015-01-31 08:00 | 362 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 1 | 0.31698 | 156.2717 | 156.2717 | 156
TC1 | D4 | 20 | 9999 | 2015-01-31 08:00 | 2015-01-31 09:00 | 466 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 1 | 0.12075 | 59.5321 | 59.5321 | 60
TC1 | D4 | 21 | 9999 | 2015-01-31 09:00 | 2015-01-31 10:00 | 503 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 1 | 0.050943 | 25.1151 | 25.1151 | 25
TC1 | D4 | 22 | 9999 | 2015-01-31 10:00 | 2015-01-31 11:00 | 490 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 1 | 0.075472 | 37.2075 | 37.2075 | 37
TC1 | D4 | 23 | 9999 | 2015-01-31 11:00 | 2015-01-31 16:07 | 538 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Derate for heat rate testing on the unit. | Trimble | Derate | Coal | 3 | 2015 | 1 | 5.1167 | -0.077233 | -38.0757 | 0 | 0
TC1 | D1 | 24 | 870 | 2015-02-05 22:00 | 2015-02-06 00:01 | 400 | 530 | 493 | Soot blowers - steam | F540Derate to repair leak in SH spray line, but job was cancelled due to load requirem | Trimble | Derate | Coal | 3 | 2015 | 2 | 2.0167 | 0.49465 | 243.8645 | 120.9245 | 121
TC1 | D4 | 25 | 280 | 2015-02-06 08:15 | 2015-02-06 09:20 | 375 | 530 | 493 | Pulverizer fires | FR00Derate due to fire in 1B coal mill. Mill taken out of service for inspection and | Trimble | Derate | Coal | 3 | 2015 | 2 | 1.0833 | 0.31682 | 156.1942 | 144.1792 | 144
TC1 | D1 | 26 | 280 | 2015-02-06 09:20 | 2015-02-06 09:40 | 496 | 530 | 493 | Pulverizer fires | FR00Derate while bringing mill on-line following removal of 1B mill from service after | Trimble | Derate | Coal | 3 | 2015 | 2 | 0.33333 | 0.021384 | 10.5421 | 31.6264 | 32
TC1 | D4 | 27 | 870 | 2015-02-07 | 2015-02-07 01:18 | 325 | 530 | 493 | Soot blowers - steam | F540Planned maintenance derate to repair leak on SH spray line. | Trimble | Derate | Coal | 3 | 2015 | 2 | 1.3 | 0.50283 | 247.8953 | 190.6887 | 191
TC1 | D1 | 28 | 1493 | 2015-02-11 07:11 | 2015-03-03 17:06 | 530 | 530 | 493 | Air heater fouling (regenerative) | FF00Differential pressure across the AH increased and required a derate in order to ke | Trimble | Derate | Coal | 3 | 2015 | 2 | 489.9167 | 0 | 0 | 0 | 0
TC1 | D1 | 29 | 310 | 2015-02-19 13:35 | 2015-02-19 14:20 | 375 | 530 | 493 | Pulverizer mills | FR00Unit derated due to 1D coal mill fire. D mill taken offline and out of service fo | Trimble | Derate | Coal | 3 | 2015 | 2 | 0.75 | 0.21934 | 108.1344 | 144.1792 | 144
TC1 | D1 | 30 | 310 | 2015-02-22 07:33 | 2015-02-22 08:49 | 420 | 530 | 493 | Pulverizer mills | FR00Derate due to fire in 1B coal mill. Coal mill was removed from service for inspec | Trimble | Derate | Coal | 3 | 2015 | 2 | 1.2667 | 0.26289 | 129.6063 | 102.3208 | 102
TC1 | D1 | 31 | 280 | 2015-02-24 00:41 | 2015-02-24 04:46 | 360 | 530 | 493 | Pulverizer fires | FR00The 1D coal mill had elevated temperatures and the mill was tripped. Inspection f | Trimble | Derate | Coal | 3 | 2015 | 2 | 4.0833 | 1.3097 | 645.706 | 158.1321 | 158
TC1 | D1 | 32 | 280 | 2015-02-28 19:14 | 2015-02-28 20:10 | 375 | 530 | 493 | Pulverizer fires | FR00Unit derated due to D coal mill fire. | Trimble | Derate | Coal | 3 | 2015 | 2 | 0.93333 | 0.27296 | 134.5673 | 144.1792 | 144
TC1 | D1 | 33 | 310 | 2015-03-01 09:25 | 2015-03-02 05:50 | 510 | 530 | 493 | Pulverizer mills | F400Unit derated due to B and D coal mills unavailable. Trouble shooting causes of mi | Trimble | Derate | Coal | 3 | 2015 | 3 | 20.4167 | 0.77044 | 379.827 | 18.6038 | 19
TC1 | D1 | 34 | 310 | 2015-03-02 05:50 | 2015-03-03 16:10 | 510 | 530 | 493 | Pulverizer mills | F400Unit derated to 510 due to 1B and 1D coal mill unavailable for troubleshooting err | Trimble | Derate | Coal | 3 | 2015 | 3 | 34.3333 | 1.2956 | 638.7296 | 18.6038 | 19
TC1 | D1 | 35 | 310 | 2015-03-03 17:06 | 2015-03-04 19:24 | 510 | 530 | 493 | Pulverizer mills | F400Unit is derated due to unknown issues causing the 1B and 1D mills to operate errat | Trimble | Derate | Coal | 3 | 2015 | 3 | 26.3 | 0.99245 | 489.2792 | 18.6038 | 19
TC1 | D1 | 36 | 9270 | 2015-03-04 19:24 | 2015-03-05 11:45 | 490 | 530 | 493 | Wet coal | FW00Unit was further derated due to wet coal affecting mill performance. 1B and 1D mi | Trimble | Derate | Coal | 3 | 2015 | 3 | 16.35 | 1.234 | 608.3434 | 37.2075 | 37
TC1 | D1 | 37 | 1493 | 2015-03-05 11:45 | 2015-03-05 20:55 | 530 | 530 | 493 | Air heater fouling (regenerative) | FF00Differential pressure across the AH is elevated and requires a derate in order to | Trimble | Derate | Coal | 3 | 2015 | 3 | 9.1667 | 0 | 0 | 0 | 0
TC1 | D1 | 38 | 310 | 2015-03-05 20:55 | 2015-03-05 21:33 | 510 | 530 | 493 | Pulverizer mills | F400Unit derated due to1B and 1D coal mill unavailable for troubleshooting erratic ope | Trimble | Derate | Coal | 3 | 2015 | 3 | 0.63333 | 0.023899 | 11.7824 | 18.6038 | 19
TC1 | D1 | 39 | 310 | 2015-03-05 21:33 | 2015-03-06 07:50 | 490 | 530 | 493 | Pulverizer mills | F400Unit derated due to 1B and 1D coal mill unavailable for troubleshooting erratic op | Trimble | Derate | Coal | 3 | 2015 | 3 | 10.2833 | 0.7761 | 382.6176 | 37.2075 | 37
TC1 | D1 | 40 | 1493 | 2015-03-06 07:50 | 2015-03-08 09:15 | 530 | 530 | 493 | Air heater fouling (regenerative) | FF00Differential pressure across the AH is elevated and requires a derate in order to | Trimble | Derate | Coal | 3 | 2015 | 3 | 49.4167 | 0 | 0 | 0 | 0
TC1 | D1 | 41 | 280 | 2015-03-08 09:15 | 2015-03-08 17:49 | 375 | 530 | 493 | Pulverizer fires | FR00Derate due to fire in the 1A coal mill with 1B and 1D mill unavailable for trouble | Trimble | Derate | Coal | 3 | 2015 | 3 | 8.5667 | 2.5053 | 1235.1355 | 144.1792 | 144
TC1 | D1 | 42 | 1493 | 2015-03-08 17:49 | 2015-03-14 07:22 | 530 | 530 | 493 | Air heater fouling (regenerative) | FF00Differential pressure across the AH is elevated and requires a derate in order to | Trimble | Derate | Coal | 3 | 2015 | 3 | 133.55 | 0 | 0 | 0 | 0
TC1 | D1 | 43 | 310 | 2015-03-14 07:22 | 2015-03-14 08:35 | 500 | 530 | 493 | Pulverizer mills | FW00Derate required due to wet coal causing mills to have elevated amps. | Trimble | Derate | Coal | 3 | 2015 | 3 | 1.2167 | 0.068868 | 33.9519 | 27.9057 | 28
TC1 | D1 | 44 | 310 | 2015-03-14 08:35 | 2015-03-14 12:20 | 490 | 530 | 493 | Pulverizer mills | FW00Derate required due to wet coal causing mills to have elevated amps. | Trimble | Derate | Coal | 3 | 2015 | 3 | 3.75 | 0.28302 | 139.5283 | 37.2075 | 37
TC1 | D1 | 45 | 1493 | 2015-03-14 12:20 | 2015-03-16 12:00 | 530 | 530 | 493 | Air heater fouling (regenerative) | FF00Differential pressure across the AH is elevated and requires a derate in order to | Trimble | Derate | Coal | 3 | 2015 | 3 | 47.6667 | 0 | 0 | 0 | 0
TC1 | D1 | 46 | 250 | 2015-03-16 12:00 | 2015-03-16 12:40 | 375 | 530 | 493 | Pulverizer feeders | F820The 1F coal mill feeder tripped causing the unit derate. Inspection found no issu | Trimble | Derate | Coal | 3 | 2015 | 3 | 0.66667 | 0.19497 | 96.1195 | 144.1792 | 144
TC1 | D1 | 47 | 1493 | 2015-03-16 12:40 | 2015-03-16 18:10 | 530 | 530 | 493 | Air heater fouling (regenerative) | FF00Differential pressure across the AH is elevated and requires a derate in order to | Trimble | Derate | Coal | 3 | 2015 | 3 | 5.5 | 0 | 0 | 0 | 0
TC1 | D1 | 48 | 340 | 2015-03-16 18:10 | 2015-03-16 20:29 | 490 | 530 | 493 | Other pulverizer problems | F0601F coal mill had a plug which blew out of the primary air duct which needed to be | Trimble | Derate | Coal | 3 | 2015 | 3 | 2.3167 | 0.17484 | 86.1975 | 37.2075 | 37
TC1 | D1 | 49 | 1493 | 2015-03-16 20:29 | 2015-03-17 15:50 | 530 | 530 | 493 | Air heater fouling (regenerative) | FF00Differential pressure across the AH is elevated and requires a derate in order to | Trimble | Derate | Coal | 3 | 2015 | 3 | 19.35 | 0 | 0 | 0 | 0
TC1 | D1 | 50 | 360 | 2015-03-17 15:50 | 2015-03-18 10:27 | 490 | 530 | 493 | Burners | F780F4 burner came in alarm with high temperature reading. F coal mill was taken out | Trimble | Derate | Coal | 3 | 2015 | 3 | 18.6167 | 1.405 | 692.6805 | 37.2075 | 37
TC1 | D1 | 51 | 3416 | 2015-03-18 10:27 | 2015-03-19 00:29 | 525 | 530 | 493 | Other feedwater pump problems | F790Testing was done on the 1B TDBFP prior to the planned maintenance outage which req | Trimble | Derate | Coal | 3 | 2015 | 3 | 14.0333 | 0.13239 | 65.2682 | 4.6509 | 5
TC1 | MO | 52 | 1493 | 2015-03-19 00:29 | 2015-03-23 11:21 | 0 | 530 | 493 | Air heater fouling (regenerative) | FF00Unit was taken out of service to conduct air heater wash on the unit. Other addit | Trimble | Maintenance | Coal | 3 | 2015 | 3 | 106.8667 | 106.8667 | 52685.2667 | 493 | 493
TC1 | D1 | 53 | 3412 | 2015-03-23 11:21 | 2015-03-24 04:15 | 525 | 530 | 493 | Feedwater pump drive - steam turbine | F610Derate during unit ramping while 1B TDBFP was not available while the trip device | Trimble | Derate | Coal | 3 | 2015 | 3 | 16.9 | 0.15943 | 78.6009 | 4.6509 | 5
TC1 | D1 | 54 | 360 | 2015-03-27 12:40 | 2015-03-27 18:48 | 530 | 530 | 493 | Burners | F590Derate to allow for 1C coal mill burner maintenance with other mills unavailable f | Trimble | Derate | Coal | 3 | 2015 | 3 | 6.1333 | 0 | 0 | 0 | 0
TC1 | D1 | 55 | 310 | 2015-03-29 16:39 | 2015-03-29 17:58 | 530 | 530 | 493 | Pulverizer mills | F700The 1C coal mill needed a card replaced and the 1B coal mill had an electrical hol | Trimble | Derate | Coal | 3 | 2015 | 3 | 1.3167 | 0 | 0 | 0 | 0
TC1 | D1 | 56 | 310 | 2015-03-30 09:30 | 2015-03-30 13:00 | 530 | 530 | 493 | Pulverizer mills | F700The 1C coal mill had electrical issues requiring maintenance response and put TC1 | Trimble | Derate | Coal | 3 | 2015 | 3 | 3.5 | 0 | 0 | 0 | 0
TC1 | D1 | 57 | 250 | 2015-04-04 07:21 | 2015-04-04 09:07 | 415 | 530 | 493 | Pulverizer feeders | FW00Due to wet coal we de-rated the unit to allow us to clean out the coal feeders and | Trimble | Derate | Coal | 3 | 2015 | 4 | 1.7667 | 0.38333 | 188.9833 | 106.9717 | 107
TC1 | D1 | 58 | 310 | 2015-04-04 19:36 | 2015-04-04 20:56 | 500 | 530 | 493 | Pulverizer mills | F400The 1C coal mill tripped requiring a unit derate. Reset of the breaker brought th | Trimble | Derate | Coal | 3 | 2015 | 4 | 1.3333 | 0.075472 | 37.2075 | 27.9057 | 28
TC1 | D1 | 59 | 250 | 2015-04-05 07:14 | 2015-04-05 11:00 | 440 | 530 | 493 | Pulverizer feeders | FW00Due to wet coal we de-rated the unit to allow us to clean out the coal feeders and | Trimble | Derate | Coal | 3 | 2015 | 4 | 3.7667 | 0.63962 | 315.334 | 83.717 | 84
TC1 | D1 | 60 | 250 | 2015-04-08 21:02 | 2015-04-08 21:48 | 450 | 530 | 493 | Pulverizer feeders | FW00C coal mill feeder needed to be cleaned off from wet coal issues. Unit derated wh | Trimble | Derate | Coal | 3 | 2015 | 4 | 0.76667 | 0.11572 | 57.0516 | 74.4151 | 74
TC1 | D1 | 61 | 250 | 2015-04-10 09:01 | 2015-04-10 11:17 | 440 | 530 | 493 | Pulverizer feeders | FW00Due to wet coal we de-rated the unit to allow us to clean out the coal feeders and | Trimble | Derate | Coal | 3 | 2015 | 4 | 2.2667 | 0.38491 | 189.7585 | 83.717 | 84
TC1 | D1 | 62 | 280 | 2015-04-11 17:38 | 2015-04-11 18:48 | 525 | 530 | 493 | Pulverizer fires | FR00D coal mill lit off and put the unit in run back. Unit derated until C mill could | Trimble | Derate | Coal | 3 | 2015 | 4 | 1.1667 | 0.011006 | 5.4261 | 4.6509 | 5
TC1 | NC | 63 | 1190 | 2015-04-11 22:00 | 2015-04-12 04:00 | 0 | 530 | 493 | Other tube slagging or fouling | FS00Planned, non-curtailing derate to conduct boiler deslag. Unit was available to re | Trimble | Other | Coal | 3 | 2015 | 4 | 6 | 6 | 2958 | 493 | 493
TC1 | D1 | 64 | 250 | 2015-04-12 14:26 | 2015-04-12 15:53 | 460 | 530 | 493 | Pulverizer feeders | FW00Due to wet coal we de-rated the unit to allow us to clean out the coal feeders and | Trimble | Derate | Coal | 3 | 2015 | 4 | 1.45 | 0.19151 | 94.4142 | 65.1132 | 65
TC1 | D1 | 65 | 310 | 2015-04-21 19:05 | 2015-04-21 21:00 | 525 | 530 | 493 | Pulverizer mills | FR00Derate on the unit due to fire in the 1A coal mill. 1C coal mill was put in servi | Trimble | Derate | Coal | 3 | 2015 | 4 | 1.9167 | 0.018082 | 8.9143 | 4.6509 | 5
TC1 | D1 | 66 | 250 | 2015-04-24 13:00 | 2015-04-24 19:22 | 500 | 530 | 493 | Pulverizer feeders | F490The 1F coal feeder tripped due to clean out conveyor going to ground. I/E swapped | Trimble | Derate | Coal | 3 | 2015 | 4 | 6.3667 | 0.36038 | 177.666 | 27.9057 | 28
TC1 | U1 | 67 | 1740 | 2015-05-02 00:54 | 2015-05-02 04:14 | 0 | 530 | 493 | Boiler drum gage glasses/level indicator | F420During maintenance on the the intercept control valves, both control valves were s | Trimble | Outage | Coal | 3 | 2015 | 5 | 3.3333 | 3.3333 | 1643.3333 | 493 | 493
TC1 | NC | 68 | 1850 | 2015-05-02 13:34 | 2015-05-03 02:14 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Silica hold on TC1 until boiler water chemistry returned to normal. | Trimble | Other | Coal | 3 | 2015 | 5 | 12.6667 | 12.6667 | 6244.6667 | 493 | 493
TC1 | D1 | 69 | 335 | 2015-05-08 11:03 | 2015-05-08 14:51 | 510 | 530 | 493 | Pulverizer lube oil system | F5901D Coal Mill lube oil pump changeout. | Trimble | Derate | Coal | 3 | 2015 | 5 | 3.8 | 0.1434 | 70.6943 | 18.6038 | 19
TC1 | D1 | 70 | 310 | 2015-05-16 15:39 | 2015-05-16 16:01 | 510 | 530 | 493 | Pulverizer mills | F4001A coal mill ran back to minimum and was removed from service, S/M inspected the m | Trimble | Derate | Coal | 3 | 2015 | 5 | 0.36667 | 0.013836 | 6.8214 | 18.6038 | 19
TC1 | D1 | 71 | 310 | 2015-05-16 16:01 | 2015-05-17 16:26 | 505 | 530 | 493 | Pulverizer mills | F400Unit had issues with 1A, 1C, and 1D mills that required derate to inspect issues. | Trimble | Derate | Coal | 3 | 2015 | 5 | 24.4167 | 1.1517 | 567.8027 | 23.2547 | 23
TC1 | D4 | 72 | 3412 | 2015-06-05 23:00 | 2015-06-06 03:09 | 500 | 530 | 493 | Feedwater pump drive - steam turbine | F590Trip solenoid replacement for the 1A TDBFP which required derate to take the pump | Trimble | Derate | Coal | 3 | 2015 | 6 | 4.15 | 0.23491 | 115.8085 | 27.9057 | 28
TC1 | D1 | 73 | 60 | 2015-06-13 10:30 | 2015-06-13 12:10 | 511 | 530 | 493 | Coal crushers including motors | F660TC1 A and F Mills not functioning.A Mill: Excessive rumbling caused the equipm | Trimble | Derate | Coal | 3 | 2015 | 6 | 1.6667 | 0.059748 | 29.456 | 17.6736 | 18
TC1 | NC | 74 | 8812 | 2015-06-15 14:00 | 2015-06-15 18:12 | 0 | 530 | 493 | SCR NOxCatalyst | F790SCR Catalyst tuning - TC1 was at full load while catalyst testing was occurring. T | Trimble | Other | Coal | 3 | 2015 | 6 | 4.2 | 4.2 | 2070.6 | 493 | 493
TC1 | D1 | 75 | 344 | 2015-06-16 01:09 | 2015-06-16 12:47 | 525 | 530 | 493 | Pulverizer inspection | F530A and D mills have been having continuing problems, so they were taken offline for | Trimble | Derate | Coal | 3 | 2015 | 6 | 11.6333 | 0.10975 | 54.106 | 4.6509 | 5
TC1 | NC | 76 | 8812 | 2015-06-16 07:00 | 2015-06-16 18:15 | 0 | 530 | 493 | SCR NOxCatalyst | F790SCR testing is underway; during SCR testing, the unit is out of AGC mode. | Trimble | Other | Coal | 3 | 2015 | 6 | 11.25 | 11.25 | 5546.25 | 493 | 493
TC1 | NC | 77 | 8812 | 2015-06-17 08:00 | 2015-06-17 17:15 | 0 | 530 | 493 | SCR NOxCatalyst | F790SCR Catalyst Tuning - Unit out of AGC mode for the duration of this time. | Trimble | Other | Coal | 3 | 2015 | 6 | 9.25 | 9.25 | 4560.25 | 493 | 493
TC1 | NC | 78 | 8812 | 2015-06-18 08:00 | 2015-06-18 18:07 | 0 | 530 | 493 | SCR NOxCatalyst | F790SCR Catalyst Tuning - Unit out of AGC mode for the duration of this time. | Trimble | Other | Coal | 3 | 2015 | 6 | 10.1167 | 10.1167 | 4987.5167 | 493 | 493
TC1 | D1 | 79 | 85 | 2015-06-23 14:22 | 2015-06-23 14:49 | 375 | 530 | 493 | Bunker feeder coal scales | F1301A Mill was taken out of service due to excessive rumbling. 1D Mill was put in ser | Trimble | Derate | Coal | 3 | 2015 | 6 | 0.45 | 0.1316 | 64.8807 | 144.1792 | 144
TC1 | D4 | 80 | 1990 | 2015-06-25 06:00 | 2015-06-25 10:00 | 520 | 530 | 493 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Unit 1 has taken a derate to 520 for performance testing. | Trimble | Derate | Coal | 3 | 2015 | 6 | 4 | 0.075472 | 37.2075 | 9.3019 | 9
TC1 | NC | 81 | 1990 | 2015-06-25 10:00 | 2015-06-25 16:00 | 0 | 530 | 493 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Non-curtailing event to conduct full load boiler performance testing. | Trimble | Other | Coal | 3 | 2015 | 6 | 6 | 6 | 2958 | 493 | 493
TC1 | MO | 82 | 3110 | 2015-06-26 22:43 | 2015-06-30 05:02 | 0 | 530 | 493 | Condenser tube leaks | F540Maintenance outage to repair suspect condenser tube leak. Large quantity (60+) of | Trimble | Maintenance | Coal | 3 | 2015 | 6 | 78.3167 | 78.3167 | 38610.1167 | 493 | 493
TC1 | U1 | 83 | 3330 | 2015-06-30 09:32 | 2015-07-01 01:48 | 0 | 530 | 493 | Condensate valves | F400Unit come off on a forced outage due to erratic operation of the condensate contro | Trimble | Outage | Coal | 3 | 2015 | 6 | 16.2667 | 16.2667 | 8019.4667 | 493 | 493
TC1 | U1 | 84 | 380 | 2015-07-01 03:04 | 2015-07-01 03:51 | 0 | 530 | 493 | Light-off (igniter) systems (including fuel supply) | F460Unit MFT due to oil igniter flameout. | Trimble | Outage | Coal | 3 | 2015 | 7 | 0.78333 | 0.78333 | 386.1833 | 493 | 493
TC1 | U1 | 85 | 380 | 2015-07-01 04:56 | 2015-07-01 05:43 | 0 | 530 | 493 | Light-off (igniter) systems (including fuel supply) | F460Unit MFT due to oil igniter flameout. | Trimble | Outage | Coal | 3 | 2015 | 7 | 0.78333 | 0.78333 | 386.1833 | 493 | 493
TC1 | D1 | 86 | 3352 | 2015-07-01 18:50 | 2015-07-01 20:06 | 430 | 530 | 493 | Feedwater chemistry (not specific to condenser | FA00Derate due to Silica restrictions in feedwater chemistry. | Trimble | Derate | Coal | 3 | 2015 | 7 | 1.2667 | 0.23899 | 117.8239 | 93.0189 | 93
TC1 | U1 | 87 | 3110 | 2015-07-01 20:06 | 2015-07-03 12:15 | 0 | 530 | 493 | Condenser tube leaks | F830Condenser tube leak caused the unit to enter into a forced outage. | Trimble | Outage | Coal | 3 | 2015 | 7 | 40.15 | 40.15 | 19793.95 | 493 | 493
TC1 | D1 | 88 | 3352 | 2015-07-03 23:00 | 2015-07-04 02:30 | 450 | 530 | 493 | Feedwater chemistry (not specific to condenser | FA00Derate due to Silica restrictions in feedwater chemistry. | Trimble | Derate | Coal | 3 | 2015 | 7 | 3.5 | 0.5283 | 260.4528 | 74.4151 | 74
TC1 | D1 | 89 | 3352 | 2015-07-04 02:30 | 2015-07-04 03:45 | 480 | 530 | 493 | Feedwater chemistry (not specific to condenser | FA00Derate due to Silica restrictions in feedwater chemistry. | Trimble | Derate | Coal | 3 | 2015 | 7 | 1.25 | 0.11792 | 58.1368 | 46.5094 | 47
TC1 | D1 | 90 | 3352 | 2015-07-04 03:45 | 2015-07-04 06:00 | 515 | 530 | 493 | Feedwater chemistry (not specific to condenser | FA00Derate due to Silica restrictions in feedwater chemistry. | Trimble | Derate | Coal | 3 | 2015 | 7 | 2.25 | 0.063679 | 31.3939 | 13.9528 | 14
TC1 | D1 | 91 | 3352 | 2015-07-04 06:00 | 2015-07-04 10:00 | 525 | 530 | 493 | Feedwater chemistry (not specific to condenser | FA00Derate due to Silica restrictions in feedwater chemistry. | Trimble | Derate | Coal | 3 | 2015 | 7 | 4 | 0.037736 | 18.6038 | 4.6509 | 5
TC1 | D1 | 92 | 3440 | 2015-07-06 06:33 | 2015-07-06 13:13 | 475 | 530 | 493 | High pressure heater tube leaks | F540High Pressure Feedwater Heaters 5 and 6 are out of service. Feedwater Heater 6 was | Trimble | Derate | Coal | 3 | 2015 | 7 | 6.6667 | 0.69182 | 341.0692 | 51.1604 | 51
TC1 | NC | 93 | 4700 | 2015-07-24 09:15 | 2015-07-24 12:04 | 0 | 530 | 493 | Generator voltage control | F790VAR testing was performed while Unit was good for full load. Unit was good for ful | Trimble | Other | Coal | 3 | 2015 | 7 | 2.8167 | 2.8167 | 1388.6167 | 493 | 493
TC1 | U1 | 94 | 4260 | 2015-08-20 00:10 | 2015-08-21 02:11 | 0 | 530 | 493 | Main stop valves | F830During a Main Stop Valve test the #2 Main Stop Valve successfully closed but would | Trimble | Outage | Coal | 3 | 2015 | 8 | 26.0167 | 26.0167 | 12826.2167 | 493 | 493
TC1 | D1 | 95 | 3352 | 2015-08-21 13:45 | 2015-08-21 14:06 | 480 | 530 | 493 | Feedwater chemistry (not specific to condenser | FA00Silica levels in water caused a derate until water cleanliness met acceptable leve | Trimble | Derate | Coal | 3 | 2015 | 8 | 0.35 | 0.033019 | 16.2783 | 46.5094 | 47
TC1 | PD | 96 | 1140 | 2015-08-29 22:00 | 2015-08-29 22:16 | 400 | 530 | 493 | First superheater A | F540Maintenance to repair packing leak on SH Spray valve. | Trimble | Derate | Coal | 3 | 2015 | 8 | 0.26667 | 0.065409 | 32.2465 | 120.9245 | 121
TC1 | PD | 97 | 1140 | 2015-08-29 22:16 | 2015-08-30 02:17 | 300 | 530 | 493 | First superheater A | F540Further maintenance on SH Spray valve - Unit was taken from 400 to 300 for full va | Trimble | Derate | Coal | 3 | 2015 | 8 | 4.0167 | 1.7431 | 859.3393 | 213.9434 | 214
TC1 | PD | 98 | 1140 | 2015-09-02 23:00 | 2015-09-03 04:15 | 400 | 530 | 493 | First superheater A | F540Continued maintenance on the SH spray valve. | Trimble | Derate | Coal | 3 | 2015 | 9 | 5.25 | 1.2877 | 634.8538 | 120.9245 | 121
TC1 | D1 | 99 | 310 | 2015-09-11 10:02 | 2015-09-12 01:01 | 450 | 530 | 493 | Pulverizer mills | F660Unit was placed on a derate due to coal mill issues - differential pressure alarms | Trimble | Derate | Coal | 3 | 2015 | 9 | 14.9833 | 2.2616 | 1114.9862 | 74.4151 | 74
TC1 | D1 | 100 | 310 | 2015-09-14 07:10 | 2015-09-14 14:27 | 450 | 530 | 493 | Pulverizer mills | F660B Mill taken out of service due to high DP and coal chute pluggage. Investigation | Trimble | Derate | Coal | 3 | 2015 | 9 | 7.2833 | 1.0994 | 541.9899 | 74.4151 | 74
TC1 | D1 | 101 | 310 | 2015-09-14 15:00 | 2015-09-14 20:32 | 475 | 530 | 493 | Pulverizer mills | F6601B Mill placed back in service - continued high DP problems across bowl. Inspectio | Trimble | Derate | Coal | 3 | 2015 | 9 | 5.5333 | 0.57421 | 283.0874 | 51.1604 | 51
TC1 | D1 | 102 | 280 | 2015-09-15 00:17 | 2015-09-15 01:30 | 475 | 530 | 493 | Pulverizer fires | F6601B Mill put in service at 45% feed rate due to the high bowl DP. Soon after, there | Trimble | Derate | Coal | 3 | 2015 | 9 | 1.2167 | 0.12626 | 62.2451 | 51.1604 | 51
TC1 | D1 | 103 | 280 | 2015-09-16 17:21 | 2015-09-16 19:45 | 525 | 530 | 493 | Pulverizer fires | F6601B Mill fire - taken out of service for cool down and cleaning. | Trimble | Derate | Coal | 3 | 2015 | 9 | 2.4 | 0.022642 | 11.1623 | 4.6509 | 5
TC1 | NC | 104 | 1980 | 2015-10-01 22:56 | 2015-10-02 02:13 | 0 | 530 | 493 | Boiler safety valve test | F790Non-curtailing derate for Main Steam Safety Valve testing. Unit was available for | Trimble | Other | Coal | 3 | 2015 | 10 | 3.2833 | 3.2833 | 1618.6833 | 493 | 493
TC1 | NC | 105 | 1980 | 2015-10-06 21:56 | 2015-10-07 00:58 | 0 | 530 | 493 | Boiler safety valve test | F790Non-curtailing derate for Main Steam Safety Valve testing. Unit was available for | Trimble | Other | Coal | 3 | 2015 | 10 | 3.0333 | 3.0333 | 1495.4333 | 493 | 493
TC1 | D1 | 106 | 310 | 2015-10-08 20:53 | 2015-10-09 03:49 | 435 | 530 | 493 | Pulverizer mills | F660A Mill had a high DP level and the A Mill was amping out, causing the unit to run | Trimble | Derate | Coal | 3 | 2015 | 10 | 6.9333 | 1.2428 | 612.6843 | 88.3679 | 88
TC1 | D1 | 107 | 310 | 2015-10-09 03:49 | 2015-10-09 23:48 | 420 | 530 | 493 | Pulverizer mills | F660Continued problems with the TC1 coal mills. | Trimble | Derate | Coal | 3 | 2015 | 10 | 19.9833 | 4.1475 | 2044.7097 | 102.3208 | 102
TC1 | PO | 108 | 8650 | 2015-10-09 23:48 | 2015-11-23 | 0 | 530 | 493 | Baghouse systems | F590TC1 Fall 2015 Outage - planned outage involving baghouse tie-in and other maintena | Trimble | Other | Coal | 3 | 2015 | 10 | 1056.2 | 1056.2 | 520706.6 | 493 | 493
TC1 | PE | 109 | 8650 | 2015-11-23 | 2015-12-11 21:51 | 0 | 530 | 493 | Baghouse systems | F590Planned Extension of the TC1 2015 Fall Outage. | Trimble | Other | Coal | 3 | 2015 | 11 | 453.85 | 453.85 | 223748.05 | 493 | 493
TC1 | NC | 110 | 1850 | 2015-12-13 10:47 | 2015-12-13 11:55 | 0 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00Non-curtailing derate due to silica hold on the unit until the boiler water chemis | Trimble | Other | Coal | 3 | 2015 | 12 | 1.1333 | 1.1333 | 558.7333 | 493 | 493
TC1 | U1 | 111 | 1090 | 2015-12-13 11:55 | 2015-12-18 11:55 | 0 | 530 | 493 | Other boiler tube leaks | F830Unit was taken offline due to a set of boiler tube leaks. | Trimble | Outage | Coal | 3 | 2015 | 12 | 120 | 120 | 59160 | 493 | 493
TC1 | U1 | 112 | 8650 | 2015-12-18 11:55 | 2015-12-19 03:22 | 0 | 530 | 493 | Baghouse systems | F590Fires out to coat the new TC1 Baghouse bags. | Trimble | Outage | Coal | 3 | 2015 | 12 | 15.45 | 15.45 | 7616.85 | 493 | 493
TC1 | NC | 113 | 9999 | 2015-12-22 06:00 | 2015-12-22 12:00 | 0 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Non-curtailing event during testing of AGC. | Trimble | Other | Coal | 3 | 2015 | 12 | 6 | 6 | 2958 | 493 | 493
TC1 | D1 | 114 | 250 | 2015-12-25 03:05 | 2015-12-25 03:20 | 440 | 530 | 493 | Pulverizer feeders | F400Derate due to 1C coal feeder runback. | Trimble | Derate | Coal | 3 | 2015 | 12 | 0.25 | 0.042453 | 20.9292 | 83.717 | 84
TC1 | D1 | 115 | 3412 | 2015-12-26 03:01 | 2015-12-26 04:23 | 300 | 530 | 493 | Feedwater pump drive - steam turbine | F820While testing the overspeed for the 1B TDBFP, the pump failed the test and tripped | Trimble | Derate | Coal | 3 | 2015 | 12 | 1.3667 | 0.59308 | 292.3893 | 213.9434 | 214
TC1 | D1 | 116 | 9270 | 2015-12-29 06:49 | 2015-12-29 07:00 | 438 | 530 | 493 | Wet coal | FW00Unit derate due to wet coal. | Trimble | Derate | Coal | 3 | 2015 | 12 | 0.18333 | 0.031824 | 15.6892 | 85.5774 | 86
TC1 | D1 | 117 | 9270 | 2015-12-29 07:00 | 2015-12-29 07:47 | 418 | 530 | 493 | Wet coal | FW00Unit derate due to wet coal. | Trimble | Derate | Coal | 3 | 2015 | 12 | 0.78333 | 0.16553 | 81.6086 | 104.1811 | 104
TC1 | D1 | 118 | 340 | 2015-12-29 18:27 | 2015-12-29 19:35 | 350 | 530 | 493 | Other pulverizer problems | F640The 1B Mill became overheated, requiring the plant to take it out of service. The | Trimble | Derate | Coal | 3 | 2015 | 12 | 1.1333 | 0.38491 | 189.7585 | 167.434 | 167
TC1 | D1 | 119 | 340 | 2015-12-30 11:27 | 2015-12-30 11:56 | 402 | 530 | 493 | Other pulverizer problems | F460The 1F Mill caught fire and was taken out of service. The 1D Mill was put in servi | Trimble | Derate | Coal | 3 | 2015 | 12 | 0.48333 | 0.11673 | 57.5477 | 119.0642 | 119
TC1 | D1 | 120 | 340 | 2015-12-31 09:57 | 2015-12-31 10:25 | 420 | 530 | 493 | Other pulverizer problems | F4601B Mill caught fire, causing the equipment to be taken out of service. | Trimble | Derate | Coal | 3 | 2015 | 12 | 0.46667 | 0.096855 | 47.7497 | 102.3208 | 102
TC1 | D1 | 1 | 100 | 2016-01-04 02:20 | 2016-01-04 03:25 | 385 | 530 | 493 | Bunker gates | F1201C Coal Feeder had no coal on belt and came in with an alarm due to uneven coal fl | Trimble | Derate | Coal | 3 | 2016 | 1 | 1.0833 | 0.29638 | 146.1171 | 134.8774 | 135
TC1 | D1 | 2 | 100 | 2016-01-04 04:45 | 2016-01-04 05:16 | 385 | 530 | 493 | Bunker gates | F1201C Coal Feeder had no coal on belt and came in with an alarm due to uneven coal fl | Trimble | Derate | Coal | 3 | 2016 | 1 | 0.51667 | 0.14135 | 69.6866 | 134.8774 | 135
TC1 | NC | 3 | 4261 | 2016-01-04 09:00 | 2016-01-04 23:42 | 0 | 530 | 493 | Control valves | F790Non-curtailing derate for control valve testing. The unit was available for full l | Trimble | Other | Coal | 3 | 2016 | 1 | 14.7 | 14.7 | 7247.1 | 493 | 493
TC1 | D1 | 4 | 4261 | 2016-01-05 23:00 | 2016-01-06 01:00 | 495 | 530 | 493 | Control valves | F790Tuning of the TC1 control valves without sufficient notice to dispatch. | Trimble | Derate | Coal | 3 | 2016 | 1 | 2 | 0.13208 | 65.1132 | 32.5566 | 33
TC1 | D1 | 5 | 340 | 2016-01-10 08:12 | 2016-01-10 09:00 | 500 | 530 | 493 | Other pulverizer problems | F060The relays in the 1C Coal Mill Hydraulic Unit has failed to operate correctly, kee | Trimble | Derate | Coal | 3 | 2016 | 1 | 0.8 | 0.045283 | 22.3245 | 27.9057 | 28
TC1 | D1 | 6 | 340 | 2016-01-10 09:00 | 2016-01-10 09:30 | 500 | 530 | 493 | Other pulverizer problems | F060Testing of the TC1 Baghouse system was going on at this time to fix the Hydrated L | Trimble | Derate | Coal | 3 | 2016 | 1 | 0.5 | 0.028302 | 13.9528 | 27.9057 | 28
TC1 | D1 | 7 | 340 | 2016-01-10 09:30 | 2016-01-10 10:40 | 460 | 530 | 493 | Other pulverizer problems | F060Continued problems with the C and B Mills kept the unit on a derate. | Trimble | Derate | Coal | 3 | 2016 | 1 | 1.1667 | 0.15409 | 75.9654 | 65.1132 | 65
TC1 | D1 | 8 | 340 | 2016-01-10 10:40 | 2016-01-10 17:19 | 500 | 530 | 493 | Other pulverizer problems | F060Testing was going on at this time to correct the ratio of Hydrated Lime to flyash. | Trimble | Derate | Coal | 3 | 2016 | 1 | 6.65 | 0.37642 | 185.5726 | 27.9057 | 28
TC1 | NC | 9 | 8650 | 2016-01-10 17:19 | 2016-01-10 22:30 | 0 | 530 | 493 | Baghouse systems | F790Non-curtailing testing of the unit to correct the ratio of Hydrated Lime to flyash | Trimble | Other | Coal | 3 | 2016 | 1 | 5.1833 | 5.1833 | 2555.3833 | 493 | 493
TC1 | D1 | 10 | 280 | 2016-01-12 15:40 | 2016-01-12 21:00 | 525 | 530 | 493 | Pulverizer fires | FR001F Mill caught on fire and 1B Mill was put in service. 1B was taken out of service | Trimble | Derate | Coal | 3 | 2016 | 1 | 5.3333 | 0.050314 | 24.805 | 4.6509 | 5
TC1 | D1 | 11 | 300 | 2016-01-12 21:00 | 2016-01-12 23:10 | 395 | 530 | 493 | Pulverizer motors and drives | F700Continued problems with the F and B Mills, combined with the loss of control power | Trimble | Derate | Coal | 3 | 2016 | 1 | 2.1667 | 0.55189 | 272.0802 | 125.5755 | 126
TC1 | PD | 12 | 280 | 2016-01-13 12:25 | 2016-01-13 19:11 | 525 | 530 | 493 | Pulverizer fires | FR001F Mill caught on fire, after being cooled and put in service. 1C Mill was put in | Trimble | Derate | Coal | 3 | 2016 | 1 | 6.7667 | 0.063836 | 31.4714 | 4.6509 | 5
TC1 | NC | 13 | 8650 | 2016-01-14 06:00 | 2016-01-14 18:39 | 0 | 530 | 493 | Baghouse systems | F790Non-Curtailing full load testing on the Unit due to the introduction of the new ba | Trimble | Other | Coal | 3 | 2016 | 1 | 12.65 | 12.65 | 6236.45 | 493 | 493
TC1 | NC | 14 | 8650 | 2016-01-14 18:50 | 2016-01-14 22:06 | 0 | 530 | 493 | Baghouse systems | F790Non-Curtailing derate for full load testing on the Unit due to the introduction of | Trimble | Other | Coal | 3 | 2016 | 1 | 3.2667 | 3.2667 | 1610.4667 | 493 | 493
TC1 | NC | 15 | 8650 | 2016-01-15 06:00 | 2016-01-15 20:48 | 0 | 530 | 493 | Baghouse systems | F790Non-Curtailing derate for full load testing on the Unit due to the introduction of | Trimble | Other | Coal | 3 | 2016 | 1 | 14.8 | 14.8 | 7296.4 | 493 | 493
TC1 | NC | 16 | 8650 | 2016-01-16 06:30 | 2016-01-16 20:19 | 0 | 530 | 493 | Baghouse systems | F790Non-Curtailing derate for full load testing on the Unit due to the introduction of | Trimble | Other | Coal | 3 | 2016 | 1 | 13.8167 | 13.8167 | 6811.6167 | 493 | 493
TC1 | D1 | 17 | 250 | 2016-01-18 15:47 | 2016-01-18 16:17 | 400 | 530 | 493 | Pulverizer feeders | F1201A Coal Mill tripped on feeder flooding. Derate while placing 1C Coal Mill in serv | Trimble | Derate | Coal | 3 | 2016 | 1 | 0.5 | 0.12264 | 60.4623 | 120.9245 | 121
TC1 | D1 | 18 | 280 | 2016-01-19 01:50 | 2016-01-19 02:11 | 400 | 530 | 493 | Pulverizer fires | FR001F Coal Mill caught fire, placing the unit in a derated status. | Trimble | Derate | Coal | 3 | 2016 | 1 | 0.35 | 0.085849 | 42.3236 | 120.9245 | 121
TC1 | D1 | 19 | 280 | 2016-01-19 05:04 | 2016-01-19 05:53 | 380 | 530 | 493 | Pulverizer fires | FR001B Mill was taken out of service due to a mill fire, placing the Unit in a derated | Trimble | Derate | Coal | 3 | 2016 | 1 | 0.81667 | 0.23113 | 113.9481 | 139.5283 | 140
TC1 | D1 | 20 | 280 | 2016-01-19 22:01 | 2016-01-19 23:28 | 374 | 530 | 493 | Pulverizer fires | FR001F Mill was lost while 1A and 1B Mill were already out of service. The Unit was pl | Trimble | Derate | Coal | 3 | 2016 | 1 | 1.45 | 0.42679 | 210.4087 | 145.1094 | 145
TC1 | D1 | 21 | 280 | 2016-01-19 23:28 | 2016-01-20 00:12 | 450 | 530 | 493 | Pulverizer fires | FR001F Mill was placed back in service and 1A and 1B Mills were still out of service. | Trimble | Derate | Coal | 3 | 2016 | 1 | 0.73333 | 0.11069 | 54.5711 | 74.4151 | 74
TC1 | D1 | 22 | 280 | 2016-01-20 00:12 | 2016-01-20 01:48 | 525 | 530 | 493 | Pulverizer fires | FR001A and 1B Mills were still unavailable, placing the Unit on a derate. | Trimble | Derate | Coal | 3 | 2016 | 1 | 1.6 | 0.015094 | 7.4415 | 4.6509 | 5
TC1 | NC | 23 | 8812 | 2016-01-25 12:00 | 2016-01-25 19:08 | 0 | 530 | 493 | SCR NOxCatalyst | F790Performance testing on the SCR. Unit was available for full load if requested by d | Trimble | Other | Coal | 3 | 2016 | 1 | 7.1333 | 7.1333 | 3516.7333 | 493 | 493
TC1 | NC | 24 | 8812 | 2016-01-26 07:00 | 2016-01-26 18:08 | 0 | 530 | 493 | SCR NOxCatalyst | F790Performance testing on the SCR. Unit was available for full load if requested by d | Trimble | Other | Coal | 3 | 2016 | 1 | 11.1333 | 11.1333 | 5488.7333 | 493 | 493
TC1 | NC | 25 | 8812 | 2016-01-27 07:00 | 2016-01-27 09:54 | 0 | 530 | 493 | SCR NOxCatalyst | F790Performance testing on the SCR. Unit was available for full load if requested by d | Trimble | Other | Coal | 3 | 2016 | 1 | 2.9 | 2.9 | 1429.7 | 493 | 493
TC1 | D1 | 26 | 8140 | 2016-01-27 09:54 | 2016-01-27 10:59 | 465 | 530 | 493 | Reaction tanks including agitators | F3401B Reaction Tank level went into 'High-High' alarm range, and was brought down bef | Trimble | Derate | Coal | 3 | 2016 | 1 | 1.0833 | 0.13286 | 65.5008 | 60.4623 | 60
TC1 | NC | 27 | 8700 | 2016-01-28 07:00 | 2016-01-28 17:08 | 0 | 530 | 493 | CEMS Certification and Recertification | F790CEMS Performance testing while at full load. The unit was available for full load | Trimble | Other | Coal | 3 | 2016 | 1 | 10.1333 | 10.1333 | 4995.7333 | 493 | 493
TC1 | NC | 28 | 8812 | 2016-01-29 07:00 | 2016-01-29 08:35 | 0 | 530 | 493 | SCR NOxCatalyst | F790Performance testing on the SCR. Unit was available for full load if requested by d | Trimble | Other | Coal | 3 | 2016 | 1 | 1.5833 | 1.5833 | 780.5833 | 493 | 493
TC1 | NC | 29 | 8812 | 2016-02-01 13:00 | 2016-02-01 18:00 | 0 | 530 | 493 | SCR NOxCatalyst | F790Performance testing on the SCR. Unit was available for full load if requested by d | Trimble | Other | Coal | 3 | 2016 | 2 | 5 | 5 | 2465 | 493 | 493
TC1 | NC | 30 | 8812 | 2016-02-02 07:00 | 2016-02-02 14:25 | 0 | 530 | 493 | SCR NOxCatalyst | F790Performance testing on the SCR. Unit was available for full load if requested by d | Trimble | Other | Coal | 3 | 2016 | 2 | 7.4167 | 7.4167 | 3656.4167 | 493 | 493
TC1 | D1 | 31 | 280 | 2016-02-12 01:27 | 2016-02-12 01:55 | 375 | 530 | 493 | Pulverizer fires | FR00The B Mill caught on fire, reducing the number of available coal mills and placing | Trimble | Derate | Coal | 3 | 2016 | 2 | 0.46667 | 0.13648 | 67.2836 | 144.1792 | 144
TC1 | D1 | 32 | 360 | 2016-02-13 10:21 | 2016-02-13 12:30 | 375 | 530 | 493 | Burners | F780The B Burner began to overheat, and it was taken out of service. With the C Mill a | Trimble | Derate | Coal | 3 | 2016 | 2 | 2.15 | 0.62877 | 309.9854 | 144.1792 | 144
TC1 | D1 | 33 | 280 | 2016-02-16 08:08 | 2016-02-17 16:35 | 525 | 530 | 493 | Pulverizer fires | FR00The 1B mill caught fire which resulted in a unit derate while the equipment was un | Trimble | Derate | Coal | 3 | 2016 | 2 | 32.45 | 0.30613 | 150.9231 | 4.6509 | 5
TC1 | NC | 34 | 9656 | 2016-02-17 07:00 | 2016-02-18 07:00 | 0 | 530 | 493 | Other stack or exhaust emissions testing - fossil | F790Non-curtailing derate for Emissions testing. The unit was at full load during test | Trimble | Other | Coal | 3 | 2016 | 2 | 24 | 24 | 11832 | 493 | 493
TC1 | NC | 35 | 9656 | 2016-02-18 07:00 | 2016-02-18 18:00 | 0 | 530 | 493 | Other stack or exhaust emissions testing - fossil | F790Non-curtailing derate for Emissions testing. The unit was at full load during test | Trimble | Other | Coal | 3 | 2016 | 2 | 11 | 11 | 5423 | 493 | 493
TC1 | NC | 36 | 9656 | 2016-02-18 18:00 | 2016-02-18 21:48 | 0 | 530 | 493 | Other stack or exhaust emissions testing - fossil | F790Non-curtailing derate for Emissions testing. The unit was at full load during test | Trimble | Other | Coal | 3 | 2016 | 2 | 3.8 | 3.8 | 1873.4 | 493 | 493
TC1 | NC | 37 | 9656 | 2016-02-19 07:00 | 2016-02-19 12:10 | 0 | 530 | 493 | Other stack or exhaust emissions testing - fossil | F790Non-curtailing derate for Emissions testing. The unit was at full load during test | Trimble | Other | Coal | 3 | 2016 | 2 | 5.1667 | 5.1667 | 2547.1667 | 493 | 493
TC1 | D1 | 38 | 250 | 2016-02-25 06:58 | 2016-02-25 07:15 | 390 | 530 | 493 | Pulverizer feeders | F520A series of issues with 1A, 1C, and 1D coal feeder alarms showed a 'no coal on bel | Trimble | Derate | Coal | 3 | 2016 | 2 | 0.28333 | 0.074843 | 36.8975 | 130.2264 | 130
TC1 | D1 | 39 | 250 | 2016-02-25 08:10 | 2016-02-25 08:30 | 460 | 530 | 493 | Pulverizer feeders | F520Continued problems with the coal feeder indication alarms. The 1C Feeder came in w | Trimble | Derate | Coal | 3 | 2016 | 2 | 0.33333 | 0.044025 | 21.7044 | 65.1132 | 65
TC1 | D1 | 40 | 8499 | 2016-02-29 03:12 | 2016-02-29 07:50 | 460 | 530 | 493 | Other miscellaneous wet scrubber problems | F060The B1 FGD Module outlet damper chain broke, causing the damper to fall and close | Trimble | Derate | Coal | 3 | 2016 | 2 | 4.6333 | 0.61195 | 301.6912 | 65.1132 | 65
TC1 | D1 | 41 | 3502 | 2016-03-11 09:06 | 2016-03-12 00:30 | 525 | 530 | 493 | Heater level control | F210TC1 Feedwater Heater 6 was taken out of service for repairs on a corroded level sw | Trimble | Derate | Coal | 3 | 2016 | 3 | 15.4 | 0.14528 | 71.6245 | 4.6509 | 5
TC1 | NC | 42 | 9999 | 2016-03-15 06:00 | 2016-03-15 11:05 | 0 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Non-curtailing event for full load heat rate testing. The unit was available for f | Trimble | Other | Coal | 3 | 2016 | 3 | 5.0833 | 5.0833 | 2506.0833 | 493 | 493
TC1 | D1 | 43 | 9270 | 2016-03-15 21:57 | 2016-03-15 22:33 | 456 | 530 | 493 | Wet coal | FW00Derate for operating with wet fuel. | Trimble | Derate | Coal | 3 | 2016 | 3 | 0.6 | 0.083774 | 41.3004 | 68.834 | 69
TC1 | U1 | 44 | 1455 | 2016-03-24 08:06 | 2016-03-24 15:19 | 0 | 530 | 493 | Induced draft fans | F820ID Fans tripped causing TC1 to MFT. | Trimble | Outage | Coal | 3 | 2016 | 3 | 7.2167 | 7.2167 | 3557.8167 | 493 | 493
TC1 | SF | 45 | 520 | 2016-03-24 15:19 | 2016-03-27 20:48 | 0 | 530 | 493 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | F060Main Steam Non-Return/Superheat Stop valve component failed and the valve has been | Trimble | Outage | Coal | 3 | 2016 | 3 | 77.4833 | 77.4833 | 38199.2833 | 493 | 493
TC1 | D1 | 46 | 95 | 2016-04-01 12:00 | 2016-04-01 22:59 | 515 | 530 | 493 | Bunker flow problems | F120F Coal Silo feeder plugged. | Trimble | Derate | Coal | 3 | 2016 | 4 | 10.9833 | 0.31085 | 153.2486 | 13.9528 | 14
TC1 | D1 | 47 | 95 | 2016-04-02 09:09 | 2016-04-03 00:49 | 520 | 530 | 493 | Bunker flow problems | F090F Coal Mill feeder was carded out for flow controls recalibration following the pl | Trimble | Derate | Coal | 3 | 2016 | 4 | 15.6667 | 0.2956 | 145.7296 | 9.3019 | 9
TC1 | D1 | 48 | 340 | 2016-04-03 07:00 | 2016-04-03 07:45 | 450 | 530 | 493 | Other pulverizer problems | F650Due to existing high DP issues with the F Mill, and an emergent high DP problem wi | Trimble | Derate | Coal | 3 | 2016 | 4 | 0.75 | 0.11321 | 55.8113 | 74.4151 | 74
TC1 | D1 | 49 | 340 | 2016-04-03 08:00 | 2016-04-03 09:30 | 500 | 530 | 493 | Other pulverizer problems | F650Due to existing high DP issues with the F Mill, and an emergent high DP problem wi | Trimble | Derate | Coal | 3 | 2016 | 4 | 1.5 | 0.084906 | 41.8585 | 27.9057 | 28
TC1 | NC | 50 | 8460 | 2016-04-05 06:00 | 2016-04-05 18:00 | 0 | 530 | 493 | Testing A | F790Non-curtailing derate for testing of the scrubber system. The unit was available f | Trimble | Other | Coal | 3 | 2016 | 4 | 12 | 12 | 5916 | 493 | 493
TC1 | NC | 51 | 4490 | 2016-04-07 11:00 | 2016-04-07 15:42 | 0 | 530 | 493 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Non-curtailing derate for steam flow testing. The unit was available for full load | Trimble | Other | Coal | 3 | 2016 | 4 | 4.7 | 4.7 | 2317.1 | 493 | 493
TC1 | D1 | 52 | 310 | 2016-04-11 12:46 | 2016-04-11 13:24 | 345 | 530 | 493 | Pulverizer mills | F660The unit was derated due to a loss of the 1A Mill. | Trimble | Derate | Coal | 3 | 2016 | 4 | 0.63333 | 0.22107 | 108.9871 | 172.0849 | 172
TC1 | D1 | 53 | 95 | 2016-04-17 09:23 | 2016-04-17 09:35 | 400 | 530 | 493 | Bunker flow problems | F660No coal on the 1D Feeder, The 1D Coal Feeder lost coal on the feeder belt and had | Trimble | Derate | Coal | 3 | 2016 | 4 | 0.2 | 0.049057 | 24.1849 | 120.9245 | 121
TC1 | D1 | 54 | 3836 | 2016-04-26 09:01 | 2016-04-26 09:47 | 525 | 530 | 493 | Steam Transfer to Other Unit | F780Steam transfer for TC2 startup. | Trimble | Derate | Coal | 3 | 2016 | 4 | 0.76667 | 0.0072327 | 3.5657 | 4.6509 | 5
TC1 | D1 | 55 | 3836 | 2016-04-26 09:47 | 2016-04-27 20:00 | 510 | 530 | 493 | Steam Transfer to Other Unit | F780Steam transfer for TC2 startup. | Trimble | Derate | Coal | 3 | 2016 | 4 | 34.2167 | 1.2912 | 636.5591 | 18.6038 | 19
TC1 | D1 | 56 | 3836 | 2016-04-27 20:00 | 2016-04-28 03:30 | 520 | 530 | 493 | Steam Transfer to Other Unit | F780Steam transfer for TC2 startup. | Trimble | Derate | Coal | 3 | 2016 | 4 | 7.5 | 0.14151 | 69.7642 | 9.3019 | 9
TC1 | D1 | 57 | 3836 | 2016-04-28 22:13 | 2016-04-29 04:42 | 510 | 530 | 493 | Steam Transfer to Other Unit | F780Steam transfer for TC2 startup. | Trimble | Derate | Coal | 3 | 2016 | 4 | 6.4833 | 0.24465 | 120.6145 | 18.6038 | 19
TC1 | D1 | 58 | 3836 | 2016-04-29 04:42 | 2016-04-29 13:52 | 525 | 530 | 493 | Steam Transfer to Other Unit | F780Steam transfer for TC2 startup. | Trimble | Derate | Coal | 3 | 2016 | 4 | 9.1667 | 0.086478 | 42.6336 | 4.6509 | 5
TC1 | D1 | 59 | 3836 | 2016-04-29 13:52 | 2016-04-29 15:54 | 515 | 530 | 493 | Steam Transfer to Other Unit | F780Steam transfer for TC2 startup. | Trimble | Derate | Coal | 3 | 2016 | 4 | 2.0333 | 0.057547 | 28.3708 | 13.9528 | 14
TC1 | PD | 60 | 1999 | 2016-05-02 05:25 | 2016-05-05 | 530 | 530 | 493 | Boiler | F660The unit load was restricted to nameplate steaming capacity of the boiler. | Trimble | Derate | Coal | 3 | 2016 | 5 | 66.5833 | 0 | 0 | 0 | 0
TC1 | D1 | 61 | 3836 | 2016-05-12 09:48 | 2016-05-13 03:32 | 507 | 530 | 493 | Steam Transfer to Other Unit | F780Steam transfer for TC2 startup. | Trimble | Derate | Coal | 3 | 2016 | 5 | 17.7333 | 0.76956 | 379.393 | 21.3943 | 21
TC1 | MO | 62 | 3831 | 2016-05-14 23:15 | 2016-05-15 16:25 | 0 | 530 | 493 | Auxiliary steam piping | F540Maintenance outage to repair leaking steam supply to TC2. | Trimble | Maintenance | Coal | 3 | 2016 | 5 | 17.1667 | 17.1667 | 8463.1667 | 493 | 493
TC1 | D1 | 63 | 310 | 2016-05-17 06:37 | 2016-05-17 08:22 | 412 | 530 | 493 | Pulverizer mills | F7801A and 1B Coal Mills were taken out of service due to high temperature. | Trimble | Derate | Coal | 3 | 2016 | 5 | 1.75 | 0.38962 | 192.084 | 109.7623 | 110
TC1 | D1 | 64 | 1455 | 2016-05-17 14:35 | 2016-05-17 15:10 | 500 | 530 | 493 | Induced draft fans | F660ID Fan flow issues resulted in a derated unit status. | Trimble | Derate | Coal | 3 | 2016 | 5 | 0.58333 | 0.033019 | 16.2783 | 27.9057 | 28
TC1 | D1 | 65 | 3836 | 2016-05-17 15:10 | 2016-05-17 19:44 | 515 | 530 | 493 | Steam Transfer to Other Unit | F780Steam transfer to TC2. | Trimble | Derate | Coal | 3 | 2016 | 5 | 4.5667 | 0.12925 | 63.7179 | 13.9528 | 14
TC1 | D1 | 66 | 310 | 2016-05-17 19:44 | 2016-05-17 20:30 | 440 | 530 | 493 | Pulverizer mills | F7801F Coal Mill was taken out of service due to high temperature, resulting in a unit | Trimble | Derate | Coal | 3 | 2016 | 5 | 0.76667 | 0.13019 | 64.183 | 83.717 | 84
TC1 | D1 | 67 | 3836 | 2016-05-17 20:30 | 2016-05-18 01:58 | 515 | 530 | 493 | Steam Transfer to Other Unit | F780Steam transfer to TC2. | Trimble | Derate | Coal | 3 | 2016 | 5 | 5.4667 | 0.15472 | 76.2755 | 13.9528 | 14
TC1 | D1 | 68 | 280 | 2016-05-18 15:07 | 2016-05-18 15:45 | 400 | 530 | 493 | Pulverizer fires | FR001C Coal Mill caught fire and was removed from service, resulting in a unit derate. | Trimble | Derate | Coal | 3 | 2016 | 5 | 0.63333 | 0.15535 | 76.5855 | 120.9245 | 121
TC1 | D1 | 69 | 3836 | 2016-05-18 19:30 | 2016-05-19 05:25 | 515 | 530 | 493 | Steam Transfer to Other Unit | F780Steam transfer to TC2. | Trimble | Derate | Coal | 3 | 2016 | 5 | 9.9167 | 0.28066 | 138.3656 | 13.9528 | 14
TC1 | D1 | 70 | 280 | 2016-05-19 10:20 | 2016-05-19 10:59 | 400 | 530 | 493 | Pulverizer fires | FR001F Coal Mill was removed from service due to a mill fire, resulting in a unit dera | Trimble | Derate | Coal | 3 | 2016 | 5 | 0.65 | 0.15943 | 78.6009 | 120.9245 | 121
TC1 | D1 | 71 | 3836 | 2016-05-19 11:44 | 2016-05-20 05:14 | 515 | 530 | 493 | Steam Transfer to Other Unit | F780Steam transfer to TC2. | Trimble | Derate | Coal | 3 | 2016 | 5 | 17.5 | 0.49528 | 244.1745 | 13.9528 | 14
TC1 | D1 | 72 | 280 | 2016-05-27 05:21 | 2016-05-27 05:43 | 386 | 530 | 493 | Pulverizer fires | FR001F Mill caught fire resulting in a unit derate. | Trimble | Derate | Coal | 3 | 2016 | 5 | 0.36667 | 0.099623 | 49.114 | 133.9472 | 134
TC1 | NC | 73 | 9630 | 2016-06-08 10:00 | 2016-06-08 11:25 | 0 | 530 | 493 | Opacity (fossil) | F790Non-curtailing event for Method 9 testing. The unit was at full load during this e | Trimble | Other | Coal | 3 | 2016 | 6 | 1.4167 | 1.4167 | 698.4167 | 493 | 493
TC1 | U1 | 74 | 1471 | 2016-06-20 07:28 | 2016-06-21 23:03 | 0 | 530 | 493 | Induced draft fan motors - variable speed | F5401A ID Fan tripped due to a VFD transformer coolant leak. | Trimble | Outage | Coal | 3 | 2016 | 6 | 39.5833 | 39.5833 | 19514.5833 | 493 | 493
TC1 | U1 | 75 | 1488 | 2016-06-26 15:49 | 2016-06-26 20:55 | 0 | 530 | 493 | Air heater (regenerative) | F780Water from a hydroveyor gasket leak caused the MCC suppling power to the Air Heate | Trimble | Outage | Coal | 3 | 2016 | 6 | 5.1 | 5.1 | 2514.3 | 493 | 493
TC1 | D1 | 76 | 280 | 2016-07-04 18:47 | 2016-07-04 19:33 | 375 | 530 | 493 | Pulverizer fires | FR001F Mill caught on fire and was removed from service. | Trimble | Derate | Coal | 3 | 2016 | 7 | 0.76667 | 0.22421 | 110.5374 | 144.1792 | 144
TC1 | D1 | 77 | 894 | 2016-07-05 12:35 | 2016-07-05 12:57 | 485 | 530 | 493 | Bottom ash piping and valves | F060Derate due to water spraying up the boiler slope due to a broken bottom ash jet pu | Trimble | Derate | Coal | 3 | 2016 | 7 | 0.36667 | 0.031132 | 15.3481 | 41.8585 | 42
TC1 | D1 | 78 | 280 | 2016-07-06 17:41 | 2016-07-06 18:15 | 375 | 530 | 493 | Pulverizer fires | FR00The 1B Coal Mill was taken out of service due to a mill fire. | Trimble | Derate | Coal | 3 | 2016 | 7 | 0.56667 | 0.16572 | 81.7016 | 144.1792 | 144
TC1 | D1 | 79 | 280 | 2016-07-07 04:12 | 2016-07-07 04:41 | 375 | 530 | 493 | Pulverizer fires | FR00The 1F Coal Mill was taken out of service due to a mill fire. | Trimble | Derate | Coal | 3 | 2016 | 7 | 0.48333 | 0.14135 | 69.6866 | 144.1792 | 144
TC1 | D1 | 80 | 280 | 2016-07-10 05:27 | 2016-07-10 06:01 | 375 | 530 | 493 | Pulverizer fires | FR00The 1F Coal Mill was taken out of service due to a mill fire. | Trimble | Derate | Coal | 3 | 2016 | 7 | 0.56667 | 0.16572 | 81.7016 | 144.1792 | 144
TC1 | D1 | 81 | 9271 | 2016-07-25 07:10 | 2016-07-25 07:20 | 452 | 530 | 493 | Wet coal (not outside management control) | FW00Derate due to wet fuel supply. | Trimble | Derate | Coal | 3 | 2016 | 7 | 0.16667 | 0.024528 | 12.0925 | 72.5547 | 73
TC1 | D1 | 82 | 280 | 2016-07-26 22:15 | 2016-07-26 22:29 | 375 | 530 | 493 | Pulverizer fires | FR00The 1B Mill caught fire, resulting in a derate. | Trimble | Derate | Coal | 3 | 2016 | 7 | 0.23333 | 0.068239 | 33.6418 | 144.1792 | 144
TC1 | D1 | 83 | 4292 | 2016-08-11 10:08 | 2016-08-11 10:55 | 490 | 530 | 493 | Hydraulic system filters | F170The #3 Main Steam Control valve's servo feedback was showing an incorrect value po | Trimble | Derate | Coal | 3 | 2016 | 8 | 0.78333 | 0.059119 | 29.1459 | 37.2075 | 37
TC1 | D1 | 84 | 4292 | 2016-08-11 13:30 | 2016-08-11 16:51 | 360 | 530 | 493 | Hydraulic system filters | F170Due to the issues with the #3 Main Steam Control valve servo (TC1 Event 83), load | Trimble | Derate | Coal | 3 | 2016 | 8 | 3.35 | 1.0745 | 529.7425 | 158.1321 | 158
TC1 | D1 | 85 | 1475 | 2016-08-21 11:39 | 2016-08-21 13:41 | 465 | 530 | 493 | Induced draft fan controls | F340TC1 ID Fan communication module failed and did not switch over to the backup. The | Trimble | Derate | Coal | 3 | 2016 | 8 | 2.0333 | 0.24937 | 122.9399 | 60.4623 | 60
TC1 | NC | 86 | 9999 | 2016-08-24 09:00 | 2016-08-24 14:20 | 0 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790This Non-Curtailing event was for Incremental Heat Rate testing of the unit. The u | Trimble | Other | Coal | 3 | 2016 | 8 | 5.3333 | 5.3333 | 2629.3333 | 493 | 493
TC1 | U1 | 87 | 3681 | 2016-09-01 22:38 | 2016-09-02 06:32 | 0 | 530 | 493 | Other voltage system breakers | F330A 120 VAC limit switch shorted and the circuit breaker remained closed. The distri | Trimble | Outage | Coal | 3 | 2016 | 9 | 7.9 | 7.9 | 3894.7 | 493 | 493
TC1 | D1 | 88 | 335 | 2016-09-07 05:02 | 2016-09-07 05:31 | 449 | 530 | 493 | Pulverizer lube oil system | F660Unit was placed on a derate due to the 1A Coal Mill being out of service. A faulty | Trimble | Derate | Coal | 3 | 2016 | 9 | 0.48333 | 0.073868 | 36.4169 | 75.3453 | 75
TC1 | U1 | 89 | 3681 | 2016-09-07 16:20 | 2016-09-07 19:58 | 0 | 530 | 493 | Other voltage system breakers | F330A 120 VAC limit switch shorted and the circuit breaker remained closed. The distri | Trimble | Outage | Coal | 3 | 2016 | 9 | 3.6333 | 3.6333 | 1791.2333 | 493 | 493
TC1 | D1 | 90 | 280 | 2016-09-09 10:45 | 2016-09-09 11:01 | 415 | 530 | 493 | Pulverizer fires | FR00The unit was placed on a derate when the 1F Coal Mill caught fire and was taken ou | Trimble | Derate | Coal | 3 | 2016 | 9 | 0.26667 | 0.057862 | 28.5258 | 106.9717 | 107
TC1 | D1 | 91 | 325 | 2016-09-12 06:48 | 2016-09-12 07:17 | 380 | 530 | 493 | Pulverizer skidding | FV00The 1E Pulverizer was fed with a large concentration of pyrites and was unable to | Trimble | Derate | Coal | 3 | 2016 | 9 | 0.48333 | 0.13679 | 67.4387 | 139.5283 | 140
TC1 | D1 | 92 | 280 | 2016-09-12 08:38 | 2016-09-12 16:18 | 375 | 530 | 493 | Pulverizer fires | FR001F Coal Mill caught fire, resulting in a derate. | Trimble | Derate | Coal | 3 | 2016 | 9 | 7.6667 | 2.2421 | 1105.3742 | 144.1792 | 144
TC1 | U1 | 93 | 1475 | 2016-09-14 10:53 | 2016-09-14 12:39 | 0 | 530 | 493 | Induced draft fan controls | FP00Due to issues controlling a coal feeder rate, the airflow to the boiler increased, | Trimble | Outage | Coal | 3 | 2016 | 9 | 1.7667 | 1.7667 | 870.9667 | 493 | 493
TC1 | NC | 94 | 9999 | 2016-09-15 19:00 | 2016-09-15 23:00 | 0 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Non-curtailing derate for scheduled unit Heat Rate testing. The unit was available | Trimble | Other | Coal | 3 | 2016 | 9 | 4 | 4 | 1972 | 493 | 493
TC1 | PD | 95 | 9999 | 2016-09-15 23:00 | 2016-09-16 | 477 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Planned derate for scheduled unit Heat Rate testing. | Trimble | Derate | Coal | 3 | 2016 | 9 | 1 | 0.1 | 49.3 | 49.3 | 49
TC1 | PD | 96 | 9999 | 2016-09-16 | 2016-09-16 01:00 | 452 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Planned derate for scheduled unit Heat Rate testing. | Trimble | Derate | Coal | 3 | 2016 | 9 | 1 | 0.14717 | 72.5547 | 72.5547 | 73
TC1 | PD | 97 | 9999 | 2016-09-16 01:00 | 2016-09-16 02:00 | 377 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Planned derate for scheduled unit Heat Rate testing. | Trimble | Derate | Coal | 3 | 2016 | 9 | 1 | 0.28868 | 142.3189 | 142.3189 | 142
TC1 | PD | 98 | 9999 | 2016-09-16 02:00 | 2016-09-16 03:00 | 352 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Planned derate for scheduled unit Heat Rate testing. | Trimble | Derate | Coal | 3 | 2016 | 9 | 1 | 0.33585 | 165.5736 | 165.5736 | 166
TC1 | PD | 99 | 9999 | 2016-09-16 03:00 | 2016-09-16 04:00 | 277 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Planned derate for scheduled unit Heat Rate testing. | Trimble | Derate | Coal | 3 | 2016 | 9 | 1 | 0.47736 | 235.3377 | 235.3377 | 235
TC1 | PD | 100 | 9999 | 2016-09-16 04:00 | 2016-09-16 05:00 | 237 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Planned derate for scheduled unit Heat Rate testing. | Trimble | Derate | Coal | 3 | 2016 | 9 | 1 | 0.55283 | 272.5453 | 272.5453 | 273
TC1 | PD | 101 | 9999 | 2016-09-16 05:00 | 2016-09-16 05:10 | 452 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Planned derate for scheduled unit Heat Rate testing. | Trimble | Derate | Coal | 3 | 2016 | 9 | 0.16667 | 0.024528 | 12.0925 | 72.5547 | 73
TC1 | NC | 102 | 8700 | 2016-09-20 07:00 | 2016-09-20 15:10 | 0 | 530 | 493 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2016 | 9 | 8.1667 | 8.1667 | 4026.1667 | 493 | 493
TC1 | NC | 103 | 8700 | 2016-09-21 07:05 | 2016-09-21 11:24 | 0 | 530 | 493 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2016 | 9 | 4.3167 | 4.3167 | 2128.1167 | 493 | 493
TC1 | D1 | 104 | 263 | 2016-09-22 04:08 | 2016-09-24 01:14 | 460 | 530 | 493 | Primary air fan drives | F160The 1A PA Fan inlet vane damper drive had a faulty circuit board, which resulted i | Trimble | Derate | Coal | 3 | 2016 | 9 | 45.1 | 5.9566 | 2936.6057 | 65.1132 | 65
TC1 | PO | 105 | 3620 | 2016-10-15 01:20 | 2016-10-24 03:14 | 0 | 530 | 493 | Main transformer | F590Planned Outage with multiple outage scopes, with a focus on TC1 ID Fan VFD work an | Trimble | Other | Coal | 3 | 2016 | 10 | 217.9 | 217.9 | 107424.7 | 493 | 493
TC1 | U1 | 106 | 3979 | 2016-11-03 04:46 | 2016-11-03 17:59 | 0 | 530 | 493 | Other DCS problems | F340A DCS Controller failed and rebooted while its backup was also out of service. The | Trimble | Outage | Coal | 3 | 2016 | 11 | 13.2167 | 13.2167 | 6515.8167 | 493 | 493
TC1 | D1 | 107 | 360 | 2016-11-11 21:42 | 2016-11-11 22:06 | 397 | 530 | 493 | Burners | FR00The F4 Burner caught fire, resulting in the mill being taken out of service. The u | Trimble | Derate | Coal | 3 | 2016 | 11 | 0.4 | 0.10038 | 49.486 | 123.7151 | 124
TC1 | NC | 108 | 8700 | 2016-11-14 10:00 | 2016-11-14 15:00 | 0 | 530 | 493 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2016 | 11 | 5 | 5 | 2465 | 493 | 493
TC1 | NC | 109 | 8700 | 2016-11-15 08:00 | 2016-11-15 15:36 | 0 | 530 | 493 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2016 | 11 | 7.6 | 7.6 | 3746.8 | 493 | 493
TC1 | PD | 110 | 8700 | 2016-11-16 21:30 | 2016-11-16 21:50 | 255 | 530 | 493 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Derate | Coal | 3 | 2016 | 11 | 0.33333 | 0.17296 | 85.2673 | 255.8019 | 256
TC1 | PD | 111 | 8700 | 2016-11-16 21:50 | 2016-11-17 01:00 | 275 | 530 | 493 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Derate | Coal | 3 | 2016 | 11 | 3.1667 | 1.5236 | 751.1274 | 237.1981 | 237
TC1 | PD | 112 | 8700 | 2016-11-17 01:00 | 2016-11-17 04:55 | 390 | 530 | 493 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Derate | Coal | 3 | 2016 | 11 | 3.9167 | 1.0346 | 510.0535 | 130.2264 | 130
TC1 | U1 | 113 | 1475 | 2016-11-26 06:03 | 2016-11-26 15:44 | 0 | 530 | 493 | Induced draft fan controls | F600A DCS card failed, resulting in a loss of I/O control of the ID fan system. The ca | Trimble | Outage | Coal | 3 | 2016 | 11 | 9.6833 | 9.6833 | 4773.8833 | 493 | 493
TC1 | D1 | 114 | 360 | 2016-11-26 21:11 | 2016-11-27 00:48 | 400 | 530 | 493 | Burners | FR00The unit was derated when the B2 burner caught fire and we had to remove that mill | Trimble | Derate | Coal | 3 | 2016 | 11 | 3.6167 | 0.88711 | 437.3437 | 120.9245 | 121
TC1 | D1 | 115 | 360 | 2016-11-27 00:48 | 2016-11-27 02:18 | 375 | 530 | 493 | Burners | FR00Load was further reduced due to burner fire until replacement mill could be placed | Trimble | Derate | Coal | 3 | 2016 | 11 | 1.5 | 0.43868 | 216.2689 | 144.1792 | 144
TC1 | D1 | 116 | 310 | 2016-11-28 15:13 | 2016-11-28 16:00 | 375 | 530 | 493 | Pulverizer mills | F340The 1A Mill discharge valves closed, which required a shutdown of the mill. The un | Trimble | Derate | Coal | 3 | 2016 | 11 | 0.78333 | 0.22909 | 112.9404 | 144.1792 | 144
TC1 | D1 | 117 | 330 | 2016-12-03 03:50 | 2016-12-03 15:12 | 450 | 530 | 493 | Pulverizer coal leak (pulverizers only) | F5401A Mill had a coal leak at the conduit discharge valve. The unit was on a derate u | Trimble | Derate | Coal | 3 | 2016 | 12 | 11.3667 | 1.7157 | 845.8516 | 74.4151 | 74
TC1 | D1 | 118 | 310 | 2016-12-03 18:00 | 2016-12-03 21:48 | 480 | 530 | 493 | Pulverizer mills | F780The 1B Mill temperature became too high causing it to be taken out of service. Add | Trimble | Derate | Coal | 3 | 2016 | 12 | 3.8 | 0.35849 | 176.7358 | 46.5094 | 47
TC1 | D1 | 119 | 1471 | 2016-12-08 04:45 | 2016-12-08 13:04 | 230 | 530 | 493 | Induced draft fan motors - variable speed | F520The 1A ID Fan VFD tripped on low coolant flow. A flow transmitter was reading a ze | Trimble | Derate | Coal | 3 | 2016 | 12 | 8.3167 | 4.7075 | 2320.8208 | 279.0566 | 279
TC1 | D1 | 120 | 280 | 2016-12-14 10:10 | 2016-12-14 10:38 | 375 | 530 | 493 | Pulverizer fires | FR00The unit was placed on a derate as a result of the 1B Mill catching fire. | Trimble | Derate | Coal | 3 | 2016 | 12 | 0.46667 | 0.13648 | 67.2836 | 144.1792 | 144
TC1 | D1 | 121 | 280 | 2016-12-19 05:16 | 2016-12-19 05:49 | 375 | 530 | 493 | Pulverizer fires | FR00The unit was placed on a derate due to a fire in the 1F Mill. | Trimble | Derate | Coal | 3 | 2016 | 12 | 0.55 | 0.16085 | 79.2986 | 144.1792 | 144
TC1 | D1 | 122 | 8006 | 2016-12-22 14:45 | 2016-12-22 18:28 | 400 | 530 | 493 | Weigh feeders B | F340The limestone rock silo had bolt failures, causing it to rest against the feeder a | Trimble | Derate | Coal | 3 | 2016 | 12 | 3.7167 | 0.91164 | 449.4362 | 120.9245 | 121
TC1 | D1 | 1 | 280 | 2017-01-04 10:50 | 2017-01-04 12:42 | 375 | 530 | 493 | Pulverizer fires | FR00The 1F Mill caught fire and was taken out of service. At this time, the 1B and 1D | Trimble | Derate | Coal | 3 | 2017 | 1 | 1.8667 | 0.54591 | 269.1346 | 144.1792 | 144
TC1 | D1 | 2 | 280 | 2017-01-04 18:12 | 2017-01-04 20:20 | 375 | 530 | 493 | Pulverizer fires | FR00The 1F Mill caught fire and was taken out of service. At this time the 1B and 1D M | Trimble | Derate | Coal | 3 | 2017 | 1 | 2.1333 | 0.6239 | 307.5824 | 144.1792 | 144
TC1 | NC | 3 | 8601 | 2017-01-05 07:00 | 2017-01-05 16:55 | 0 | 530 | 493 | SO3 mitigation | F790Non-curtailing event for HCl/SO3 removal level testing. The unit was available dur | Trimble | Other | Coal | 3 | 2017 | 1 | 9.9167 | 9.9167 | 4888.9167 | 493 | 493
TC1 | NC | 4 | 8601 | 2017-01-06 07:00 | 2017-01-06 15:03 | 0 | 530 | 493 | SO3 mitigation | F790Non-curtailing event for HCl/SO3 removal levels testing. The testing did not effec | Trimble | Other | Coal | 3 | 2017 | 1 | 8.05 | 8.05 | 3968.65 | 493 | 493
TC1 | D1 | 5 | 280 | 2017-01-06 13:30 | 2017-01-06 14:09 | 490 | 530 | 493 | Pulverizer fires | FR00The 1F Mill caught fire and was taken out of service. At this time, the 1B Mill wa | Trimble | Derate | Coal | 3 | 2017 | 1 | 0.65 | 0.049057 | 24.1849 | 37.2075 | 37
TC1 | D1 | 6 | 280 | 2017-01-06 15:52 | 2017-01-06 17:04 | 490 | 530 | 493 | Pulverizer fires | FR00The 1B Mill caught fire and was taken out of service. At this time, the 1F was als | Trimble | Derate | Coal | 3 | 2017 | 1 | 1.2 | 0.090566 | 44.6491 | 37.2075 | 37
TC1 | U1 | 7 | 1750 | 2017-01-26 19:00 | 2017-01-26 23:27 | 0 | 530 | 493 | Burner management system | F490When placing a start on the AB oil guns, a ground fault went back to the Burner Ma | Trimble | Outage | Coal | 3 | 2017 | 1 | 4.45 | 4.45 | 2193.85 | 493 | 493
TC1 | D1 | 8 | 310 | 2017-02-01 16:58 | 2017-02-01 18:12 | 375 | 530 | 493 | Pulverizer mills | F780The unit was placed on a derate when the 1E Mill temperature went high. The mill w | Trimble | Derate | Coal | 3 | 2017 | 2 | 1.2333 | 0.36069 | 177.8211 | 144.1792 | 144
TC1 | D1 | 9 | 280 | 2017-02-01 20:04 | 2017-02-01 20:29 | 375 | 530 | 493 | Pulverizer fires | FR00The unit was placed on a derate when the 1B Mill temperature went high and the mil | Trimble | Derate | Coal | 3 | 2017 | 2 | 0.41667 | 0.12186 | 60.0747 | 144.1792 | 144
TC1 | NC | 10 | 8700 | 2017-02-07 08:00 | 2017-02-07 15:06 | 0 | 530 | 493 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2017 | 2 | 7.1 | 7.1 | 3500.3 | 493 | 493
TC1 | D1 | 11 | 280 | 2017-02-09 05:12 | 2017-02-09 05:51 | 375 | 530 | 493 | Pulverizer fires | FR00The unit was placed on a derate when the 1B Mill caught fire. It was removed from | Trimble | Derate | Coal | 3 | 2017 | 2 | 0.65 | 0.19009 | 93.7165 | 144.1792 | 144
TC1 | D1 | 12 | 280 | 2017-02-16 11:26 | 2017-02-16 12:16 | 375 | 530 | 493 | Pulverizer fires | FR00The unit was placed on a derate when the 1F Mill had a fire in the seal ring heade | Trimble | Derate | Coal | 3 | 2017 | 2 | 0.83333 | 0.24371 | 120.1494 | 144.1792 | 144
TC1 | D1 | 13 | 250 | 2017-02-25 21:09 | 2017-02-25 21:47 | 350 | 530 | 493 | Pulverizer feeders | F520The 1C Mill Feeder tripped due to the tachometer speed switch not operating correc | Trimble | Derate | Coal | 3 | 2017 | 2 | 0.63333 | 0.21509 | 106.0415 | 167.434 | 167
TC1 | NC | 14 | 9999 | 2017-02-27 06:00 | 2017-02-27 12:04 | 0 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790Non-Curtailing Event for Unit Winter Capability testing. The unit was available fo | Trimble | Other | Coal | 3 | 2017 | 2 | 6.0667 | 6.0667 | 2990.8667 | 493 | 493
TC1 | D1 | 15 | 280 | 2017-03-11 11:19 | 2017-03-11 11:47 | 365 | 530 | 493 | Pulverizer fires | FR00The unit was placed on a derate when the 1F Coal Mill caught fire. The 1F Mill was | Trimble | Derate | Coal | 3 | 2017 | 3 | 0.46667 | 0.14528 | 71.6245 | 153.4811 | 153
TC1 | D1 | 16 | 280 | 2017-03-17 05:48 | 2017-03-17 06:18 | 365 | 530 | 493 | Pulverizer fires | F780The unit was placed on a derate when the 1B Coal Mill caught fire. The 1B Mill was | Trimble | Derate | Coal | 3 | 2017 | 3 | 0.5 | 0.15566 | 76.7406 | 153.4811 | 153
TC1 | D1 | 17 | 280 | 2017-03-18 12:40 | 2017-03-18 12:57 | 365 | 530 | 493 | Pulverizer fires | F780The unit was placed on a derate when the 1F Coal Mill caught fire. The 1F Mill was | Trimble | Derate | Coal | 3 | 2017 | 3 | 0.28333 | 0.088208 | 43.4863 | 153.4811 | 153
TC1 | D1 | 18 | 280 | 2017-03-19 08:29 | 2017-03-19 08:43 | 375 | 530 | 493 | Pulverizer fires | F780The unit was placed on a derate when the 1F Coal Mill caught fire. The 1F Mill was | Trimble | Derate | Coal | 3 | 2017 | 3 | 0.23333 | 0.068239 | 33.6418 | 144.1792 | 144
TC1 | D1 | 20 | 280 | 2017-03-19 19:37 | 2017-03-19 20:14 | 375 | 530 | 493 | Pulverizer fires | F780The unit was placed on a derate when the 1B Coal Mill caught fire. The 1B Mill was | Trimble | Derate | Coal | 3 | 2017 | 3 | 0.61667 | 0.18035 | 88.9105 | 144.1792 | 144
TC1 | D1 | 19 | 280 | 2017-03-20 05:13 | 2017-03-20 05:35 | 375 | 530 | 493 | Pulverizer fires | F780The unit was placed on a derate when the 1F Coal Mill caught fire. The 1F Mill was | Trimble | Derate | Coal | 3 | 2017 | 3 | 0.36667 | 0.10723 | 52.8657 | 144.1792 | 144
TC1 | D1 | 21 | 280 | 2017-03-21 18:51 | 2017-03-21 19:07 | 375 | 530 | 493 | Pulverizer fires | F780The unit was placed on a derate when the 1F Coal Mill caught fire. The 1F Mill was | Trimble | Derate | Coal | 3 | 2017 | 3 | 0.26667 | 0.077987 | 38.4478 | 144.1792 | 144
TC1 | D1 | 22 | 250 | 2017-03-21 23:56 | 2017-03-22 00:17 | 370 | 530 | 493 | Pulverizer feeders | F690The 1B Coal Feeder belt was not moving. The 1B Mill was taken out of service and t | Trimble | Derate | Coal | 3 | 2017 | 3 | 0.35 | 0.10566 | 52.0906 | 148.8302 | 149
TC1 | D1 | 23 | 280 | 2017-03-22 12:16 | 2017-03-22 12:46 | 375 | 530 | 493 | Pulverizer fires | F780The unit was placed on a derate when the 1F Coal Mill caught fire. The 1F Mill was | Trimble | Derate | Coal | 3 | 2017 | 3 | 0.5 | 0.14623 | 72.0896 | 144.1792 | 144
TC1 | D1 | 24 | 590 | 2017-03-30 | 2017-03-30 01:47 | 375 | 530 | 493 | Desuperheater/attemperator valves | F540Load was dropped on the unit to reduce heat in the boiler and therefore the need f | Trimble | Derate | Coal | 3 | 2017 | 3 | 1.7833 | 0.52154 | 257.1197 | 144.1792 | 144
TC1 | D1 | 25 | 280 | 2017-03-30 23:13 | 2017-03-30 23:35 | 400 | 530 | 493 | Pulverizer fires | F780The unit was placed on a derate when the 1B Coal Mill caught fire. The 1B Mill was | Trimble | Derate | Coal | 3 | 2017 | 3 | 0.36667 | 0.089937 | 44.339 | 120.9245 | 121
TC1 | D1 | 26 | 310 | 2017-04-08 02:30 | 2017-04-08 07:57 | 500 | 530 | 493 | Pulverizer mills | F660The unit was deraed when arflow issues occured during a coal mill startup. Once th | Trimble | Derate | Coal | 3 | 2017 | 4 | 5.45 | 0.30849 | 152.0858 | 27.9057 | 28
TC1 | D1 | 27 | 280 | 2017-04-11 03:50 | 2017-04-11 04:23 | 375 | 530 | 493 | Pulverizer fires | F780The unit was placed on a derate when the 1F Coal Mill caught fire. The 1BFMill was | Trimble | Derate | Coal | 3 | 2017 | 4 | 0.55 | 0.16085 | 79.2986 | 144.1792 | 144
TC1 | PO | 28 | 1493 | 2017-04-12 02:42 | 2017-04-15 10:42 | 0 | 530 | 493 | Air heater fouling (regenerative) | F590The unit was placed on a Planned Outage for multiple maintenance scopes. The criti | Trimble | Other | Coal | 3 | 2017 | 4 | 80 | 80 | 39440 | 493 | 493
TC1 | U1 | 29 | 1000 | 2017-04-16 21:04 | 2017-04-18 12:48 | 0 | 530 | 493 | Waterwall (Furnace wall) A | F540The unit was taken offline and placed on a Forced Outage for repairs on a leaking | Trimble | Outage | Coal | 3 | 2017 | 4 | 39.7333 | 39.7333 | 19588.5333 | 493 | 493
TC1 | NC | 30 | 8812 | 2017-04-24 13:00 | 2017-04-24 18:34 | 0 | 530 | 493 | SCR NOxCatalyst | F790Performance testing on the SCR. Unit was available for full load if requested by d | Trimble | Other | Coal | 3 | 2017 | 4 | 5.5667 | 5.5667 | 2744.3667 | 493 | 493
TC1 | NC | 31 | 8812 | 2017-04-25 06:00 | 2017-04-25 16:19 | 0 | 530 | 493 | SCR NOxCatalyst | F790Performance testing on the SCR. Unit was available for full load if requested by d | Trimble | Other | Coal | 3 | 2017 | 4 | 10.3167 | 10.3167 | 5086.1167 | 493 | 493
TC1 | NC | 32 | 8812 | 2017-04-26 06:00 | 2017-04-26 15:30 | 0 | 530 | 493 | SCR NOxCatalyst | F790Performance testing on the SCR. Unit was available for full load if requested by d | Trimble | Other | Coal | 3 | 2017 | 4 | 9.5 | 9.5 | 4683.5 | 493 | 493
TC1 | NC | 33 | 8812 | 2017-04-27 06:00 | 2017-04-27 17:56 | 0 | 530 | 493 | SCR NOxCatalyst | F790Performance testing on the SCR. Unit was available for full load if requested by d | Trimble | Other | Coal | 3 | 2017 | 4 | 11.9333 | 11.9333 | 5883.1333 | 493 | 493
TC1 | U1 | 34 | 1000 | 2017-04-27 17:56 | 2017-04-30 11:29 | 0 | 530 | 493 | Waterwall (Furnace wall) A | F540The unit was placed on a Forced Outage for repairs to an identified tube leak. | Trimble | Outage | Coal | 3 | 2017 | 4 | 65.55 | 65.55 | 32316.15 | 493 | 493
TC1 | D1 | 35 | 250 | 2017-05-01 00:30 | 2017-05-01 01:22 | 375 | 530 | 493 | Pulverizer feeders | F300The unit was placed on a derate when the 1B Coal Feeder tripped due to debris on t | Trimble | Derate | Coal | 3 | 2017 | 5 | 0.86667 | 0.25346 | 124.9553 | 144.1792 | 144
TC1 | D1 | 36 | 310 | 2017-05-12 07:21 | 2017-05-12 07:58 | 500 | 530 | 493 | Pulverizer mills | F660The 1C and 1D Mills both experienced high bowl DP and load was dropped to accommod | Trimble | Derate | Coal | 3 | 2017 | 5 | 0.61667 | 0.034906 | 17.2085 | 27.9057 | 28
TC1 | D1 | 37 | 310 | 2017-05-12 15:09 | 2017-05-12 15:37 | 495 | 530 | 493 | Pulverizer mills | F780The unit was placed on a derate when the1D Mill temperature went high, and it was | Trimble | Derate | Coal | 3 | 2017 | 5 | 0.46667 | 0.030818 | 15.1931 | 32.5566 | 33
TC1 | PD | 38 | 8812 | 2017-05-12 22:00 | 2017-05-13 02:20 | 450 | 530 | 493 | SCR NOxCatalyst | F790The unit was placed on a Planned Derate for SCR Catalyst testing at reduced loads. | Trimble | Derate | Coal | 3 | 2017 | 5 | 4.3333 | 0.65409 | 322.4654 | 74.4151 | 74
TC1 | PD | 39 | 8812 | 2017-05-13 02:20 | 2017-05-13 03:00 | 415 | 530 | 493 | SCR NOxCatalyst | F790The unit was placed on a Planned Derate for SCR Catalyst testing at reduced loads. | Trimble | Derate | Coal | 3 | 2017 | 5 | 0.66667 | 0.14465 | 71.3145 | 106.9717 | 107
TC1 | PD | 40 | 8812 | 2017-05-13 03:00 | 2017-05-13 05:00 | 380 | 530 | 493 | SCR NOxCatalyst | F790The unit was placed on a Planned Derate for SCR Catalyst testing at reduced loads. | Trimble | Derate | Coal | 3 | 2017 | 5 | 2 | 0.56604 | 279.0566 | 139.5283 | 140
TC1 | PD | 41 | 8812 | 2017-05-13 05:00 | 2017-05-13 06:00 | 385 | 530 | 493 | SCR NOxCatalyst | F790The unit was placed on a Planned Derate for SCR Catalyst testing at reduced loads. | Trimble | Derate | Coal | 3 | 2017 | 5 | 1 | 0.27358 | 134.8774 | 134.8774 | 135
TC1 | PD | 42 | 8812 | 2017-05-13 06:00 | 2017-05-13 14:05 | 380 | 530 | 493 | SCR NOxCatalyst | F790The unit was placed on a Planned Derate for SCR Catalyst testing at reduced loads. | Trimble | Derate | Coal | 3 | 2017 | 5 | 8.0833 | 2.2877 | 1127.8538 | 139.5283 | 140
TC1 | PD | 43 | 8812 | 2017-05-13 14:05 | 2017-05-14 11:33 | 450 | 530 | 493 | SCR NOxCatalyst | F790The unit was placed on a Planned Derate for SCR Catalyst testing at reduced loads. | Trimble | Derate | Coal | 3 | 2017 | 5 | 21.4667 | 3.2403 | 1597.444 | 74.4151 | 74
TC1 | D1 | 44 | 310 | 2017-05-14 11:33 | 2017-05-14 12:00 | 375 | 530 | 493 | Pulverizer mills | F780The unit was placed on a derate when the 1B Mill temperature went high, and was re | Trimble | Derate | Coal | 3 | 2017 | 5 | 0.45 | 0.1316 | 64.8807 | 144.1792 | 144
TC1 | PD | 45 | 8812 | 2017-05-14 12:00 | 2017-05-14 13:47 | 450 | 530 | 493 | SCR NOxCatalyst | F790The unit was placed on a Planned Derate for SCR Catalyst testing at reduced loads. | Trimble | Derate | Coal | 3 | 2017 | 5 | 1.7833 | 0.26918 | 132.7069 | 74.4151 | 74
TC1 | D1 | 46 | 310 | 2017-05-14 13:47 | 2017-05-14 14:51 | 375 | 530 | 493 | Pulverizer mills | F780The unit was placed on a derate when the 1B Mill temperature went high and the 1F | Trimble | Derate | Coal | 3 | 2017 | 5 | 1.0667 | 0.31195 | 153.7912 | 144.1792 | 144
TC1 | PD | 47 | 8812 | 2017-05-14 14:51 | 2017-05-14 23:43 | 450 | 530 | 493 | SCR NOxCatalyst | F790The unit was placed on a Planned Derate for SCR Catalyst testing at reduced loads. | Trimble | Derate | Coal | 3 | 2017 | 5 | 8.8667 | 1.3384 | 659.8138 | 74.4151 | 74
TC1 | D1 | 48 | 310 | 2017-05-14 23:43 | 2017-05-15 00:13 | 375 | 530 | 493 | Pulverizer mills | F130The 1A Mill tripped due to the closing of the mill discharge valve. The valve was | Trimble | Derate | Coal | 3 | 2017 | 5 | 0.5 | 0.14623 | 72.0896 | 144.1792 | 144
TC1 | PD | 49 | 8812 | 2017-05-15 00:13 | 2017-05-15 00:46 | 450 | 530 | 493 | SCR NOxCatalyst | F790The unit was placed on a Planned Derate for SCR Catalyst testing at reduced loads. | Trimble | Derate | Coal | 3 | 2017 | 5 | 0.55 | 0.083019 | 40.9283 | 74.4151 | 74
TC1 | D1 | 50 | 310 | 2017-05-15 00:46 | 2017-05-15 01:06 | 375 | 530 | 493 | Pulverizer mills | F130The 1A Mill tripped due to the closing of the mill discharge valve. The valve was | Trimble | Derate | Coal | 3 | 2017 | 5 | 0.33333 | 0.097484 | 48.0597 | 144.1792 | 144
TC1 | PD | 51 | 8812 | 2017-05-15 01:06 | 2017-05-15 04:00 | 450 | 530 | 493 | SCR NOxCatalyst | F790The unit was placed on a Planned Derate for SCR Catalyst testing at reduced loads. | Trimble | Derate | Coal | 3 | 2017 | 5 | 2.9 | 0.43774 | 215.8038 | 74.4151 | 74
TC1 | NC | 52 | 8812 | 2017-05-15 07:00 | 2017-05-15 11:55 | 0 | 530 | 493 | SCR NOxCatalyst | F790This event documents a Non-Curtailing event for SCR Catalyst testing at full load. | Trimble | Other | Coal | 3 | 2017 | 5 | 4.9167 | 4.9167 | 2423.9167 | 493 | 493
TC1 | PD | 53 | 4260 | 2017-05-24 23:00 | 2017-05-25 00:03 | 450 | 530 | 493 | Main stop valves | F120Planned Derate for replacement of the servo block on the #2 Main Steam Stop Valve. | Trimble | Derate | Coal | 3 | 2017 | 5 | 1.05 | 0.15849 | 78.1358 | 74.4151 | 74
TC1 | D1 | 54 | 280 | 2017-06-02 14:34 | 2017-06-02 15:15 | 375 | 530 | 493 | Pulverizer fires | F780The unit was placed on a derate when the 1B Mill caught on fire. The 1F Mill was t | Trimble | Derate | Coal | 3 | 2017 | 6 | 0.68333 | 0.19984 | 98.5225 | 144.1792 | 144
TC1 | MO | 55 | 1000 | 2017-06-09 10:09 | 2017-06-11 23:41 | 0 | 530 | 493 | Waterwall (Furnace wall) A | F540The unit was placed on a Maintenance Outage for a repairs on an identified tube le | Trimble | Maintenance | Coal | 3 | 2017 | 6 | 61.5333 | 61.5333 | 30335.9333 | 493 | 493
TC1 | D1 | 56 | 3829 | 2017-06-12 10:47 | 2017-06-12 21:23 | 300 | 530 | 493 | Other closed cooling water system problems A | F780The unit was placed on a Derate due to elevated Closed Cooling Water temperature. | Trimble | Derate | Coal | 3 | 2017 | 6 | 10.6 | 4.6 | 2267.8 | 213.9434 | 214
TC1 | D1 | 57 | 1475 | 2017-06-13 04:46 | 2017-06-13 08:45 | 275 | 530 | 493 | Induced draft fan controls | F520The 1A ID Fan tripped on high Flue Gas temperature. The root cause appeared to be | Trimble | Derate | Coal | 3 | 2017 | 6 | 3.9833 | 1.9165 | 944.8392 | 237.1981 | 237
TC1 | PD | 58 | 590 | 2017-06-17 | 2017-06-17 04:17 | 430 | 530 | 493 | Desuperheater/attemperator valves | F540The unit was placed on a Planned Derate to address a leak on the B Superheat Spray | Trimble | Derate | Coal | 3 | 2017 | 6 | 4.2833 | 0.80818 | 398.4308 | 93.0189 | 93
TC1 | D1 | 59 | 4640 | 2017-06-17 01:45 | 2017-06-17 04:17 | 375 | 530 | 493 | Seal oil system and seals A | F520The unit was placed on a Derate when the Generator Main Seal Oil Pumps tripped, re | Trimble | Derate | Coal | 3 | 2017 | 6 | 2.5333 | 0.74088 | 365.2541 | 144.1792 | 144
TC1 | PD | 60 | 590 | 2017-06-17 04:17 | 2017-06-17 10:42 | 375 | 530 | 493 | Desuperheater/attemperator valves | F540The unit was placed on a Planned Derate to finish addressing a leak on the B Super | Trimble | Derate | Coal | 3 | 2017 | 6 | 6.4167 | 1.8766 | 925.1502 | 144.1792 | 144
TC1 | MO | 61 | 1000 | 2017-06-25 12:09 | 2017-06-27 21:11 | 0 | 530 | 493 | Waterwall (Furnace wall) A | F540Maintenance Outage for the repair of an identified waterwall tube leak. | Trimble | Maintenance | Coal | 3 | 2017 | 6 | 57.0333 | 57.0333 | 28117.4333 | 493 | 493
TC1 | D1 | 62 | 3352 | 2017-06-28 05:24 | 2017-06-28 09:10 | 500 | 530 | 493 | Feedwater chemistry (not specific to condenser | FA00The unit was placed on a derate for silica levels in the condensate. | Trimble | Derate | Coal | 3 | 2017 | 6 | 3.7667 | 0.21321 | 105.1113 | 27.9057 | 28
TC1 | D1 | 63 | 3352 | 2017-06-28 09:10 | 2017-06-28 12:36 | 510 | 530 | 493 | Feedwater chemistry (not specific to condenser | FA00The unit was placed on a derate for silica levels in the condensate. | Trimble | Derate | Coal | 3 | 2017 | 6 | 3.4333 | 0.12956 | 63.873 | 18.6038 | 19
TC1 | D1 | 64 | 3352 | 2017-06-28 12:36 | 2017-06-28 19:24 | 520 | 530 | 493 | Feedwater chemistry (not specific to condenser | FA00The unit was placed on a derate for silica levels in the condensate. | Trimble | Derate | Coal | 3 | 2017 | 6 | 6.8 | 0.1283 | 63.2528 | 9.3019 | 9
TC1 | D4 | 65 | 4842 | 2017-07-27 04:00 | 2017-07-27 06:00 | 450 | 530 | 493 | Reactive and capability testing | F790The unit was placed on a Maintenance Derate for VAR testing. The unit was returned | Trimble | Derate | Coal | 3 | 2017 | 7 | 2 | 0.30189 | 148.8302 | 74.4151 | 74
TC1 | NC | 66 | 8700 | 2017-08-01 07:00 | 2017-08-01 18:28 | 0 | 530 | 493 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2017 | 8 | 11.4667 | 11.4667 | 5653.0667 | 493 | 493
TC1 | D1 | 67 | 335 | 2017-08-03 13:09 | 2017-08-03 13:30 | 375 | 530 | 493 | Pulverizer lube oil system | F570Issues with the 1D Mill lube oil filters caused the Mill to be taken out of servic | Trimble | Derate | Coal | 3 | 2017 | 8 | 0.35 | 0.10236 | 50.4627 | 144.1792 | 144
TC1 | D1 | 68 | 270 | 2017-08-03 13:45 | 2017-08-03 14:05 | 450 | 530 | 493 | Primary air duct and dampers | F130Contractor personnel inadvertently closed the 1F Mill Primary Air damper, tripping | Trimble | Derate | Coal | 3 | 2017 | 8 | 0.33333 | 0.050314 | 24.805 | 74.4151 | 74
TC1 | NC | 69 | 9656 | 2017-08-07 06:15 | 2017-08-07 16:00 | 0 | 530 | 493 | Other stack or exhaust emissions testing - fossil | F790TC1 was placed in a Non-Curtailing state for testing of SCR response to a new coal | Trimble | Other | Coal | 3 | 2017 | 8 | 9.75 | 9.75 | 4806.75 | 493 | 493
TC1 | NC | 70 | 9656 | 2017-08-08 06:00 | 2017-08-08 15:45 | 0 | 530 | 493 | Other stack or exhaust emissions testing - fossil | F790TC1 was placed in a Non-Curtailing state for testing of SCR response to a new coal | Trimble | Other | Coal | 3 | 2017 | 8 | 9.75 | 9.75 | 4806.75 | 493 | 493
TC1 | NC | 71 | 9656 | 2017-08-09 06:00 | 2017-08-09 15:00 | 0 | 530 | 493 | Other stack or exhaust emissions testing - fossil | F790TC1 was placed in a Non-Curtailing state for testing of SCR response to a new coal | Trimble | Other | Coal | 3 | 2017 | 8 | 9 | 9 | 4437 | 493 | 493
TC1 | NC | 72 | 9656 | 2017-08-10 06:00 | 2017-08-10 14:25 | 0 | 530 | 493 | Other stack or exhaust emissions testing - fossil | F790TC1 was placed in a Non-Curtailing state for testing of SCR response to a new coal | Trimble | Other | Coal | 3 | 2017 | 8 | 8.4167 | 8.4167 | 4149.4167 | 493 | 493
TC1 | D4 | 73 | 4842 | 2017-08-15 05:00 | 2017-08-15 05:30 | 450 | 530 | 493 | Reactive and capability testing | F790The unit was placed on a Maintenance Derate for VAR testing. The unit was returned | Trimble | Derate | Coal | 3 | 2017 | 8 | 0.5 | 0.075472 | 37.2075 | 74.4151 | 74
TC1 | NC | 74 | 9999 | 2017-08-16 08:00 | 2017-08-16 12:20 | 0 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790The unit was placed on a Non-Curtailing event during this timeframe for heat rate | Trimble | Other | Coal | 3 | 2017 | 8 | 4.3333 | 4.3333 | 2136.3333 | 493 | 493
TC1 | NC | 75 | 9656 | 2017-08-22 10:00 | 2017-08-22 12:01 | 0 | 530 | 493 | Other stack or exhaust emissions testing - fossil | F790The unit was placed on a Non-Curtailing event for MATS testing at full load. The u | Trimble | Other | Coal | 3 | 2017 | 8 | 2.0167 | 2.0167 | 994.2167 | 493 | 493
TC1 | D4 | 76 | 4842 | 2017-08-30 04:00 | 2017-08-30 05:00 | 450 | 530 | 493 | Reactive and capability testing | F790The unit was placed on a Planned Derate for VAR testing. The unit was returned to | Trimble | Derate | Coal | 3 | 2017 | 8 | 1 | 0.15094 | 74.4151 | 74.4151 | 74
TC1 | D4 | 78 | 510 | 2017-09-07 | 2017-09-07 01:52 | 450 | 530 | 493 | Main steam relief/safety valves off superheater | F590Maintenance Derate for routine safety valve setting. | Trimble | Derate | Coal | 3 | 2017 | 9 | 1.8667 | 0.28176 | 138.9082 | 74.4151 | 74
TC1 | D1 | 79 | 280 | 2017-09-13 00:42 | 2017-09-13 00:57 | 400 | 530 | 493 | Pulverizer fires | F780The unit was placed on an unplanned derate when the 1B Mill experienced a mill fir | Trimble | Derate | Coal | 3 | 2017 | 9 | 0.25 | 0.061321 | 30.2311 | 120.9245 | 121
TC1 | D4 | 80 | 9999 | 2017-09-18 01:00 | 2017-09-18 03:30 | 375 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790The unit was placed on a Maintenance Derate for performance testing. | Trimble | Derate | Coal | 3 | 2017 | 9 | 2.5 | 0.73113 | 360.4481 | 144.1792 | 144
TC1 | D4 | 81 | 9999 | 2017-09-18 03:30 | 2017-09-18 06:00 | 450 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790The unit was placed on a Maintenance Derate for performance testing. | Trimble | Derate | Coal | 3 | 2017 | 9 | 2.5 | 0.37736 | 186.0377 | 74.4151 | 74
TC1 | PO | 82 | 4400 | 2017-09-24 01:45 | 2017-11-25 02:05 | 0 | 530 | 493 | Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | F590Planned Outage for multiple scopes, main scope being a total turbine maintenance p | Trimble | Other | Coal | 3 | 2017 | 9 | 1488.3333 | 1488.3333 | 733748.3333 | 493 | 493
TC1 | PO | 83 | 4040 | 2017-11-25 02:05 | 2017-11-25 23:48 | 0 | 530 | 493 | Bearings C | F590The unit was placed on a Planned Outage to address bearing #1 vibration issues. | Trimble | Other | Coal | 3 | 2017 | 11 | 21.7167 | 21.7167 | 10706.3167 | 493 | 493
TC1 | MO | 84 | 4040 | 2017-11-26 00:13 | 2017-11-26 01:58 | 0 | 530 | 493 | Bearings C | F850The LP bearing vibrations were not with-in normal limits so the unit was returned | Trimble | Maintenance | Coal | 3 | 2017 | 11 | 1.75 | 1.75 | 862.75 | 493 | 493
TC1 | MO | 85 | 4040 | 2017-11-26 04:20 | 2017-11-26 14:27 | 0 | 530 | 493 | Bearings C | F850The LP bearing vibrations were not with-in normal limits so the unit was returned | Trimble | Maintenance | Coal | 3 | 2017 | 11 | 10.1167 | 10.1167 | 4987.5167 | 493 | 493
TC1 | D1 | 86 | 1850 | 2017-11-27 14:33 | 2017-11-27 16:06 | 375 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00The unit was placed on an Unplanned Derate due to a boiler water silica restrictio | Trimble | Derate | Coal | 3 | 2017 | 11 | 1.55 | 0.4533 | 223.4778 | 144.1792 | 144
TC1 | D1 | 87 | 1850 | 2017-11-27 16:06 | 2017-11-28 01:22 | 392 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00The unit was placed on an Unplanned Derate due to a boiler water silica restrictio | Trimble | Derate | Coal | 3 | 2017 | 11 | 9.2667 | 2.4128 | 1189.5253 | 128.366 | 128
TC1 | D1 | 88 | 1850 | 2017-11-28 01:22 | 2017-11-28 06:00 | 430 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00The unit was placed on an Unplanned Derate due to a boiler water silica restrictio | Trimble | Derate | Coal | 3 | 2017 | 11 | 4.6333 | 0.87421 | 430.9874 | 93.0189 | 93
TC1 | D1 | 89 | 1850 | 2017-11-28 06:00 | 2017-11-28 06:44 | 460 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00The unit was placed on an Unplanned Derate due to a boiler water silica restrictio | Trimble | Derate | Coal | 3 | 2017 | 11 | 0.73333 | 0.096855 | 47.7497 | 65.1132 | 65
TC1 | D1 | 90 | 256 | 2017-11-28 06:44 | 2017-11-28 07:46 | 375 | 530 | 493 | Seal air system (air to pulverizers) | F660While the unit was on a derate due to silica restriction, the 1C Mill tripped due | Trimble | Derate | Coal | 3 | 2017 | 11 | 1.0333 | 0.3022 | 148.9852 | 144.1792 | 144
TC1 | D1 | 91 | 1850 | 2017-11-28 07:46 | 2017-11-28 09:48 | 450 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00The unit was placed on an Unplanned Derate due to a boiler water silica restrictio | Trimble | Derate | Coal | 3 | 2017 | 11 | 2.0333 | 0.30692 | 151.3107 | 74.4151 | 74
TC1 | D1 | 92 | 280 | 2017-11-28 09:48 | 2017-11-28 10:32 | 375 | 530 | 493 | Pulverizer fires | FR00While the unit was derated due to silica restriction, the 1B Mill tripped due to h | Trimble | Derate | Coal | 3 | 2017 | 11 | 0.73333 | 0.21447 | 105.7314 | 144.1792 | 144
TC1 | D1 | 93 | 1850 | 2017-11-28 10:32 | 2017-11-28 11:46 | 446 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00The unit was placed on an Unplanned Derate due to a boiler water silica restrictio | Trimble | Derate | Coal | 3 | 2017 | 11 | 1.2333 | 0.19547 | 96.3675 | 78.1358 | 78
TC1 | D1 | 94 | 1850 | 2017-11-28 11:46 | 2017-11-28 16:30 | 476 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00The unit was placed on an Unplanned Derate due to a boiler water silica restrictio | Trimble | Derate | Coal | 3 | 2017 | 11 | 4.7333 | 0.48226 | 237.7562 | 50.2302 | 50
TC1 | D1 | 95 | 3310 | 2017-11-28 16:30 | 2017-11-28 17:12 | 275 | 530 | 493 | Condensate/hotwell pumps | F120While the unit was derated due to a silica restriction, the hotwell pump screens w | Trimble | Derate | Coal | 3 | 2017 | 11 | 0.7 | 0.33679 | 166.0387 | 237.1981 | 237
TC1 | D1 | 96 | 3310 | 2017-11-28 17:12 | 2017-11-28 18:00 | 250 | 530 | 493 | Condensate/hotwell pumps | F120While the unit was derated due to a silica restriction, the hotwell pump screens w | Trimble | Derate | Coal | 3 | 2017 | 11 | 0.8 | 0.42264 | 208.3623 | 260.4528 | 260
TC1 | U1 | 97 | 3344 | 2017-11-28 18:00 | 2017-11-28 19:58 | 0 | 530 | 493 | Deaerator (including level control) | F660The unit was placed on an Unplanned Outage due to low tank level in the deaerator. | Trimble | Outage | Coal | 3 | 2017 | 11 | 1.9667 | 1.9667 | 969.5667 | 493 | 493
TC1 | D1 | 98 | 1850 | 2017-11-28 19:59 | 2017-11-28 21:06 | 476 | 530 | 493 | Boiler water condition (not feedwater water quality) | FA00The unit was placed on an Unplanned Derate due to a boiler water silica restrictio | Trimble | Derate | Coal | 3 | 2017 | 11 | 1.1167 | 0.11377 | 56.0904 | 50.2302 | 50
TC1 | U2 | 99 | 4040 | 2017-11-28 21:06 | 2017-11-30 07:47 | 0 | 530 | 493 | Bearings C | F850The LP bearing vibrations were not with-in normal limits so the unit was returned | Trimble | Outage | Coal | 3 | 2017 | 11 | 34.6833 | 34.6833 | 17098.8833 | 493 | 493
TC1 | U2 | 100 | 4260 | 2017-11-30 18:04 | 2017-12-02 22:23 | 0 | 530 | 493 | Main stop valves | F660The unit was taken offline to address high differential pressure across the screen | Trimble | Outage | Coal | 3 | 2017 | 11 | 52.3167 | 52.3167 | 25792.1167 | 493 | 493
TC1 | U1 | 101 | 710 | 2017-12-02 22:23 | 2017-12-03 19:57 | 0 | 530 | 493 | Blowdown system piping B | F540The unit was placed on an Unplanned Outage after the main header for the blowdown | Trimble | Outage | Coal | 3 | 2017 | 12 | 21.5667 | 21.5667 | 10632.3667 | 493 | 493
TC1 | D1 | 102 | 4551 | 2017-12-12 06:54 | 2017-12-12 07:47 | 500 | 530 | 493 | Generator bearings | F850The unit was placed on an Immediate Derate due to elevated vibration levels in Bea | Trimble | Derate | Coal | 3 | 2017 | 12 | 0.88333 | 0.05 | 24.65 | 27.9057 | 28
TC1 | D1 | 103 | 3415 | 2017-12-12 18:37 | 2017-12-12 19:34 | 415 | 530 | 493 | Feedwater pump/drive lube oil system | F660The unit was placed on an Immediate Dreate when the MDBFP lube oil filter was swap | Trimble | Derate | Coal | 3 | 2017 | 12 | 0.95 | 0.20613 | 101.6231 | 106.9717 | 107
TC1 | NC | 104 | 8700 | 2017-12-14 08:00 | 2017-12-14 17:50 | 0 | 530 | 493 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2017 | 12 | 9.8333 | 9.8333 | 4847.8333 | 493 | 493
TC1 | NC | 105 | 9656 | 2017-12-15 09:30 | 2017-12-15 12:00 | 0 | 530 | 493 | Other stack or exhaust emissions testing - fossil | F790The unit was placed on a Non-Curtailing state for MATS testing at full load. The u | Trimble | Other | Coal | 3 | 2017 | 12 | 2.5 | 2.5 | 1232.5 | 493 | 493
TC1 | NC | 106 | 8700 | 2017-12-15 12:40 | 2017-12-15 14:04 | 0 | 530 | 493 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2017 | 12 | 1.4 | 1.4 | 690.2 | 493 | 493
TC1 | D1 | 107 | 3661 | 2017-12-17 18:16 | 2017-12-17 19:08 | 450 | 530 | 493 | 4160-volt circuit breakers | F820The unit was placed on an Immediate Derate when a Feeder Breaker was tripped when | Trimble | Derate | Coal | 3 | 2017 | 12 | 0.86667 | 0.13082 | 64.4931 | 74.4151 | 74
TC1 | NC | 108 | 8812 | 2017-12-19 07:00 | 2017-12-19 17:20 | 0 | 530 | 493 | SCR NOxCatalyst | F790This event documents a Non-Curtailing event for SCR Catalyst testing at full load. | Trimble | Other | Coal | 3 | 2017 | 12 | 10.3333 | 10.3333 | 5094.3333 | 493 | 493
TC1 | NC | 109 | 8812 | 2017-12-20 07:15 | 2017-12-20 16:33 | 0 | 530 | 493 | SCR NOxCatalyst | F790This event documents a Non-Curtailing event for SCR Catalyst testing at full load. | Trimble | Other | Coal | 3 | 2017 | 12 | 9.3 | 9.3 | 4584.9 | 493 | 493
TC1 | NC | 110 | 8812 | 2017-12-21 07:00 | 2017-12-21 10:36 | 0 | 530 | 493 | SCR NOxCatalyst | F790This event documents a Non-Curtailing event for SCR Catalyst testing at full load. | Trimble | Other | Coal | 3 | 2017 | 12 | 3.6 | 3.6 | 1774.8 | 493 | 493
TC1 | D1 | 1 | 897 | 2018-01-02 04:05 | 2018-01-02 11:00 | 400 | 530 | 493 | Bottom ash rotary (drag chain type) conveyor and motor | F720The unit was placed on a Derate when the submerged scraper conveyor secondary chai | Trimble | Derate | Coal | 3 | 2018 | 1 | 6.9167 | 1.6965 | 836.3947 | 120.9245 | 121
TC1 | D1 | 2 | 897 | 2018-01-02 11:00 | 2018-01-02 16:45 | 360 | 530 | 493 | Bottom ash rotary (drag chain type) conveyor and motor | F720The unit was placed on a Derate when the submerged scraper conveyor secondary chai | Trimble | Derate | Coal | 3 | 2018 | 1 | 5.75 | 1.8443 | 909.2594 | 158.1321 | 158
TC1 | MO | 3 | 4551 | 2018-01-20 01:21 | 2018-01-22 12:31 | 0 | 530 | 493 | Generator bearings | FV00The unit was placed on a Maintenance Outage to correct bearing vibrations in the T | Trimble | Maintenance | Coal | 3 | 2018 | 1 | 59.1667 | 59.1667 | 29169.1667 | 493 | 493
TC1 | D1 | 4 | 4610 | 2018-01-31 07:30 | 2018-01-31 14:32 | 500 | 530 | 493 | Hydrogen cooling system piping and valves | F590The unit was placed on an unplanned derate for maintenance on the stator cooling s | Trimble | Derate | Coal | 3 | 2018 | 1 | 7.0333 | 0.39811 | 196.2698 | 27.9057 | 28
TC1 | PD | 5 | 9999 | 2018-01-31 21:00 | 2018-01-31 22:03 | 200 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790The unit was placed on a planned derate for Incremental Heat Rate Testing. | Trimble | Derate | Coal | 3 | 2018 | 1 | 1.05 | 0.65377 | 322.3104 | 306.9623 | 307
TC1 | U1 | 6 | 4470 | 2018-01-31 22:03 | 2018-02-01 05:08 | 0 | 530 | 493 | Differential expansion | F780As the unit was coming down for the Incremental Heat Rate test, the differential e | Trimble | Outage | Coal | 3 | 2018 | 1 | 7.0833 | 7.0833 | 3492.0833 | 493 | 493
TC1 | MO | 7 | 4610 | 2018-02-03 12:10 | 2018-02-03 21:56 | 0 | 530 | 493 | Hydrogen cooling system piping and valves | F590The unit was placed on a Maintenance Outage for repairs to the stator cooling line | Trimble | Maintenance | Coal | 3 | 2018 | 2 | 9.7667 | 9.7667 | 4814.9667 | 493 | 493
TC1 | NC | 8 | 9999 | 2018-02-07 07:00 | 2018-02-07 12:08 | 0 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790The unit underwent Heat Rate Testing on a Non-Curtailing basis. | Trimble | Other | Coal | 3 | 2018 | 2 | 5.1333 | 5.1333 | 2530.7333 | 493 | 493
TC1 | PD | 9 | 9999 | 2018-02-15 17:00 | 2018-02-15 20:00 | 450 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790The unit was placed on a Planned Derate for Incremental Heat Rate testing. | Trimble | Derate | Coal | 3 | 2018 | 2 | 3 | 0.45283 | 223.2453 | 74.4151 | 74
TC1 | PD | 10 | 9999 | 2018-02-15 20:00 | 2018-02-16 00:59 | 350 | 530 | 493 | Total unit performance testing (use appropriate codes for individual component testing) | F790The unit was placed on a Planned Derate for Incremental Heat Rate testing. | Trimble | Derate | Coal | 3 | 2018 | 2 | 4.9833 | 1.6925 | 834.3792 | 167.434 | 167
TC1 | MO | 11 | 4551 | 2018-02-16 00:59 | 2018-02-19 02:36 | 0 | 530 | 493 | Generator bearings | FV00The unit was placed on a Maintenance Outage to correct bearing vibrations in the T | Trimble | Maintenance | Coal | 3 | 2018 | 2 | 73.6167 | 73.6167 | 36293.0167 | 493 | 493
TC1 | D1 | 12 | 250 | 2018-02-24 17:38 | 2018-02-25 01:45 | 450 | 530 | 493 | Pulverizer feeders | FW00Wet coal caused an issue with pluggage on the 1F Coal Feeder. | Trimble | Derate | Coal | 3 | 2018 | 2 | 8.1167 | 1.2252 | 604.0025 | 74.4151 | 74
TC1 | D1 | 13 | 250 | 2018-02-26 04:36 | 2018-02-26 05:20 | 400 | 530 | 493 | Pulverizer feeders | FW00Wet coal created an issue where mills are rotated in operation to allow for cleani | Trimble | Derate | Coal | 3 | 2018 | 2 | 0.73333 | 0.17987 | 88.678 | 120.9245 | 121
TC1 | D1 | 14 | 310 | 2018-02-27 04:29 | 2018-02-27 05:42 | 375 | 530 | 493 | Pulverizer mills | FW00Wet coal created an issue with the 1A Mill, and was taken out of service, causing | Trimble | Derate | Coal | 3 | 2018 | 2 | 1.2167 | 0.35582 | 175.4181 | 144.1792 | 144
TC1 | D1 | 15 | 310 | 2018-02-27 05:42 | 2018-02-27 07:29 | 450 | 530 | 493 | Pulverizer mills | FW00Wet coal created an issue with the 1A Mill, and was taken out of service, causing | Trimble | Derate | Coal | 3 | 2018 | 2 | 1.7833 | 0.26918 | 132.7069 | 74.4151 | 74
TC1 | D1 | 16 | 310 | 2018-02-28 14:56 | 2018-02-28 15:49 | 400 | 530 | 493 | Pulverizer mills | FW00Wet coal created airflow problems in the 1A Coal Mill, causing a derate. | Trimble | Derate | Coal | 3 | 2018 | 2 | 0.88333 | 0.21667 | 106.8167 | 120.9245 | 121
TC1 | U1 | 17 | 1400 | 2018-03-07 03:01 | 2018-03-07 15:03 | 0 | 530 | 493 | Forced draft fans | F660TC1 tripped on furnace pressure after a clinker caused boiler to pressurize. | Trimble | Outage | Coal | 3 | 2018 | 3 | 12.0333 | 12.0333 | 5932.4333 | 493 | 493
TC1 | D1 | 18 | 330 | 2018-03-10 21:30 | 2018-03-10 22:00 | 375 | 530 | 493 | Pulverizer coal leak (pulverizers only) | F540The unit was placed on a derate due to a leak on the 1A Coal Mill. | Trimble | Derate | Coal | 3 | 2018 | 3 | 0.5 | 0.14623 | 72.0896 | 144.1792 | 144
TC1 | D1 | 19 | 280 | 2018-03-31 04:09 | 2018-03-31 04:34 | 375 | 530 | 493 | Pulverizer fires | FR00The unit was placed on an Immediate Derate when the 1D Mill caught fire and the 1A | Trimble | Derate | Coal | 3 | 2018 | 3 | 0.41667 | 0.12186 | 60.0747 | 144.1792 | 144
TC1 | D1 | 20 | 280 | 2018-03-31 04:57 | 2018-03-31 07:17 | 375 | 530 | 493 | Pulverizer fires | FR00The unit was placed on an Immediate Derate when the 1D Mill caught fire and the 1A | Trimble | Derate | Coal | 3 | 2018 | 3 | 2.3333 | 0.68239 | 336.4182 | 144.1792 | 144
TC1 | D1 | 21 | 331 | 2018-04-29 23:02 | 2018-04-29 23:53 | 380 | 530 | 493 | Pulverizer system coal leaks (other than pulverizers | F540The unit was placed on an Unplanned Derate due to a coal conduit leak on the 1D Mi | Trimble | Derate | Coal | 3 | 2018 | 4 | 0.85 | 0.24057 | 118.5991 | 139.5283 | 140
TC2 | U1 | 1 | 4240 | 2013-01-01 | 2013-01-07 18:06 | 0 | 795 | 747 | Bearings E | F780The # 7 and 8 LP Turbine bearings failed just after the unit returned from planned | Trimble | Outage | Coal | 3 | 2013 | 1 | 162.1 | 162.1 | 121088.7 | 747 | 747
TC2 | NC | 2 | 338 | 2013-01-07 18:06 | 2013-01-08 03:30 | 0 | 795 | 747 | Pulverizer control systems (temperature and pressure) | F780The unit is on line and ramping up. The mills are not with-in temp. limits so we a | Trimble | Other | Coal | 3 | 2013 | 1 | 9.4 | 9.4 | 7021.8 | 747 | 747
TC2 | D1 | 3 | 338 | 2013-01-08 03:30 | 2013-01-08 15:15 | 660 | 795 | 747 | Pulverizer control systems (temperature and pressure) | F780The "2C" and "2F" Mills would not start due to temp. limits and limit switch issue | Trimble | Derate | Coal | 3 | 2013 | 1 | 11.75 | 1.9953 | 1490.4764 | 126.8491 | 127
TC2 | D1 | 4 | 338 | 2013-01-08 15:15 | 2013-01-08 17:00 | 785 | 795 | 747 | Pulverizer control systems (temperature and pressure) | F780The "2C" Mill would not start due to temp. limits and limit switch issues. I/E and | Trimble | Derate | Coal | 3 | 2013 | 1 | 1.75 | 0.022013 | 16.4434 | 9.3962 | 9
TC2 | D1 | 5 | 9610 | 2013-01-08 19:15 | 2013-01-08 22:25 | 449 | 795 | 747 | NOx stack emissions (fossil) | FE00The ammonia system for the unit was not controlling and the load had to be reduced | Trimble | Derate | Coal | 3 | 2013 | 1 | 3.1667 | 1.3782 | 1029.5132 | 325.1094 | 325
TC2 | D1 | 6 | 9610 | 2013-01-08 22:25 | 2013-01-09 03:50 | 619 | 795 | 747 | NOx stack emissions (fossil) | FE00The ammonia system for the unit was not controlling and the load had to be reduced | Trimble | Derate | Coal | 3 | 2013 | 1 | 5.4167 | 1.1992 | 895.7736 | 165.3736 | 165
TC2 | D1 | 7 | 4099 | 2013-01-09 04:00 | 2013-01-09 09:00 | 794 | 795 | 747 | Other high pressure turbine problems | F800The Turbine OEM limit on steam flow was at the max allowable for the unit so load | Trimble | Derate | Coal | 3 | 2013 | 1 | 5 | 0.0062893 | 4.6981 | 0.93962 | 1
TC2 | PD | 8 | 360 | 2013-01-09 09:00 | 2013-01-09 14:30 | 390 | 795 | 747 | Burners | F790This planned de-rate was to allow testing on the "2F" burners by Doosan and Bechte | Trimble | Derate | Coal | 3 | 2013 | 1 | 5.5 | 2.8019 | 2093.0094 | 380.5472 | 381
TC2 | PD | 9 | 360 | 2013-01-09 14:30 | 2013-01-09 17:00 | 445 | 795 | 747 | Burners | F790This planned de-rate was to allow testing on the "2F" burners by Doosan and Bechte | Trimble | Derate | Coal | 3 | 2013 | 1 | 2.5 | 1.1006 | 822.1698 | 328.8679 | 329
TC2 | PD | 10 | 360 | 2013-01-09 17:00 | 2013-01-10 04:00 | 399 | 795 | 747 | Burners | F790This planned de-rate was to allow testing on the "2F" burners by Doosan and Bechte | Trimble | Derate | Coal | 3 | 2013 | 1 | 11 | 5.4792 | 4092.9962 | 372.0906 | 372
TC2 | D1 | 11 | 385 | 2013-01-10 04:00 | 2013-01-10 05:00 | 499 | 795 | 747 | Igniters | F460The oil guns were causing a delay on increasing load, The oil guns would not light | Trimble | Derate | Coal | 3 | 2013 | 1 | 1 | 0.37233 | 278.1283 | 278.1283 | 278
TC2 | D1 | 12 | 9610 | 2013-01-10 05:00 | 2013-01-10 07:00 | 650 | 795 | 747 | NOx stack emissions (fossil) | FE00The ammonia pumps would not stay running, causing an emissions issue on the unit. | Trimble | Derate | Coal | 3 | 2013 | 1 | 2 | 0.36478 | 272.4906 | 136.2453 | 136
TC2 | D1 | 13 | 9610 | 2013-01-10 15:30 | 2013-01-11 06:30 | 469 | 795 | 747 | NOx stack emissions (fossil) | FE00The ammonia pumps would not stay running, causing an emissions issue on the unit. | Trimble | Derate | Coal | 3 | 2013 | 1 | 15 | 6.1509 | 4594.7547 | 306.317 | 306
TC2 | D1 | 14 | 4099 | 2013-01-11 06:30 | 2013-01-11 10:10 | 779 | 795 | 747 | Other high pressure turbine problems | F800The Turbine OEM limit on steam flow was at the max allowable for the unit so load | Trimble | Derate | Coal | 3 | 2013 | 1 | 3.6667 | 0.073795 | 55.1245 | 15.034 | 15
TC2 | D1 | 15 | 9610 | 2013-01-11 10:10 | 2013-01-12 | 777 | 795 | 747 | NOx stack emissions (fossil) | FE00The ammonia system for the unit was not controlling and the load had to be reduced | Trimble | Derate | Coal | 3 | 2013 | 1 | 13.8333 | 0.31321 | 233.966 | 16.9132 | 17
TC2 | D1 | 16 | 9270 | 2013-01-14 08:45 | 2013-01-14 22:00 | 789 | 795 | 747 | Wet coal | FW00The unit was limited due to issues related to wet coal the hot air dampers on the | Trimble | Derate | Coal | 3 | 2013 | 1 | 13.25 | 0.1 | 74.7 | 5.6377 | 6
TC2 | D1 | 17 | 9600 | 2013-01-16 02:00 | 2013-01-16 03:15 | 764 | 795 | 747 | SO2 stack emissions (fossil) | FE00SO2 emission issues required a derate to avoid being out of compliance | Trimble | Derate | Coal | 3 | 2013 | 1 | 1.25 | 0.048742 | 36.4104 | 29.1283 | 29
TC2 | D1 | 18 | 9600 | 2013-01-16 03:15 | 2013-01-16 04:00 | 789 | 795 | 747 | SO2 stack emissions (fossil) | FE00The SO2 emissions allowed for a slight increase in load, but SO2 was still causing | Trimble | Derate | Coal | 3 | 2013 | 1 | 0.75 | 0.0056604 | 4.2283 | 5.6377 | 6
TC2 | D1 | 19 | 9600 | 2013-01-16 06:20 | 2013-01-16 10:00 | 789 | 795 | 747 | SO2 stack emissions (fossil) | FE00SO2 issues returned and required a derate for compliance | Trimble | Derate | Coal | 3 | 2013 | 1 | 3.6667 | 0.027673 | 20.6717 | 5.6377 | 6
TC2 | D4 | 20 | 920 | 2013-01-19 00:01 | 2013-01-19 06:00 | 435 | 795 | 747 | Other slag and ash removal problems A | FS00TC2 was derated in order to perform the weekly planned deslag of the boiler as rec | Trimble | Derate | Coal | 3 | 2013 | 1 | 5.9833 | 2.7094 | 2023.9472 | 338.2642 | 338
TC2 | D4 | 21 | 920 | 2013-01-19 06:00 | 2013-01-19 06:30 | 680 | 795 | 747 | Other slag and ash removal problems A | FS00TC2 was ramped up in load to complete the weekly deslag of the boiler as recommend | Trimble | Derate | Coal | 3 | 2013 | 1 | 0.5 | 0.072327 | 54.0283 | 108.0566 | 108
TC2 | D1 | 22 | 1455 | 2013-01-25 10:12 | 2013-01-25 12:15 | 784 | 795 | 747 | Induced draft fans | F660TC2 was reduced 25MW due to the ID Fan suction pressure low and running near trip | Trimble | Derate | Coal | 3 | 2013 | 1 | 2.05 | 0.028365 | 21.1885 | 10.3358 | 10
TC2 | D1 | 23 | 9610 | 2013-01-29 21:15 | 2013-01-29 22:30 | 500 | 795 | 747 | NOx stack emissions (fossil) | FE00The 2A dilution air fan trip due to a plugged suction filter on the fan. This res | Trimble | Derate | Coal | 3 | 2013 | 1 | 1.25 | 0.46384 | 346.4858 | 277.1887 | 277
TC2 | D1 | 24 | 9610 | 2013-01-29 22:30 | 2013-01-30 00:45 | 425 | 795 | 747 | NOx stack emissions (fossil) | FE00Further derate to 425MW due to 2A dilution air fan trip and subsequent issues resu | Trimble | Derate | Coal | 3 | 2013 | 1 | 2.25 | 1.0472 | 782.2358 | 347.6604 | 348
TC2 | D1 | 25 | 9610 | 2013-01-30 00:45 | 2013-01-30 01:30 | 650 | 795 | 747 | NOx stack emissions (fossil) | FE00Load was increased to 650MW as control was returned. Further affect of to 2A dilu | Trimble | Derate | Coal | 3 | 2013 | 1 | 0.75 | 0.13679 | 102.184 | 136.2453 | 136
TC2 | D1 | 26 | 9270 | 2013-01-30 16:15 | 2013-01-30 21:00 | 800 | 795 | 747 | Wet coal | FW00TC2 expeirenced issues with wet coal which reduced load to 800MW for a short durat | Trimble | Derate | Coal | 3 | 2013 | 1 | 4.75 | -0.029874 | -22.316 | 0 | 0
TC2 | D1 | 27 | 310 | 2013-02-03 18:00 | 2013-02-03 19:00 | 650 | 795 | 747 | Pulverizer mills | F820The 2D coal mill tripped with support fuel in. C Mill was put back in service to r | Trimble | Derate | Coal | 3 | 2013 | 2 | 1 | 0.18239 | 136.2453 | 136.2453 | 136
TC2 | D1 | 28 | 3710 | 2013-02-05 01:10 | 2013-02-05 01:26 | 600 | 795 | 747 | Transmission line (connected to powerhouse switchyard to 1st Substation) | F700At 0106 we had a switchyard event. The 4542 A phase coupling capacitor/wave trap l | Trimble | Derate | Coal | 3 | 2013 | 2 | 0.26667 | 0.065409 | 48.8604 | 183.2264 | 183
TC2 | U1 | 29 | 1480 | 2013-02-05 01:26 | 2013-02-07 17:15 | 0 | 795 | 747 | Other induced draft fan problems | F820Following the cascade of equipment trips from the switchyard event, the FD and ID | Trimble | Outage | Coal | 3 | 2013 | 2 | 63.8167 | 63.8167 | 47671.05 | 747 | 747
TC2 | U1 | 30 | 3499 | 2013-02-07 18:12 | 2013-02-08 03:11 | 0 | 795 | 747 | Other feedwater system problems | F820During ramping the feedwater flow became low and resulted in an MFT. | Trimble | Outage | Coal | 3 | 2013 | 2 | 8.9833 | 8.9833 | 6710.55 | 747 | 747
TC2 | U1 | 31 | 530 | 2013-02-08 04:25 | 2013-02-08 05:35 | 0 | 795 | 747 | Other main steam system problems | F820During ramping the main steam temperature became low and caused a turbine trip. T | Trimble | Outage | Coal | 3 | 2013 | 2 | 1.1667 | 1.1667 | 871.5 | 747 | 747
TC2 | D1 | 32 | 8650 | 2013-02-08 16:14 | 2013-02-08 18:17 | 729 | 795 | 747 | Baghouse systems | F660The baghouse differential pressure was running high while the baghouse was running | Trimble | Derate | Coal | 3 | 2013 | 2 | 2.05 | 0.17019 | 127.1309 | 62.0151 | 62
TC2 | U1 | 33 | 1035 | 2013-02-08 18:17 | 2013-02-10 21:27 | 0 | 795 | 747 | Platen superheater | F540Unit 2 came offline for a tube leak in the south most panel of the platen superhea | Trimble | Outage | Coal | 3 | 2013 | 2 | 51.1667 | 51.1667 | 38221.5 | 747 | 747
TC2 | D1 | 34 | 550 | 2013-02-11 03:13 | 2013-02-11 11:46 | 521 | 795 | 747 | Reheat steam relief/safety valves | F540After the tube leak outage, a Reheat Safety valve was found to be leaking through. | Trimble | Derate | Coal | 3 | 2013 | 2 | 8.55 | 2.9468 | 2201.254 | 257.4566 | 257
TC2 | U1 | 35 | 550 | 2013-02-11 11:46 | 2013-02-13 13:13 | 0 | 795 | 747 | Reheat steam relief/safety valves | F540Following the derate, the decision was made to remove TC2 from service to investig | Trimble | Outage | Coal | 3 | 2013 | 2 | 49.45 | 49.45 | 36939.15 | 747 | 747
TC2 | D1 | 36 | 550 | 2013-02-13 23:45 | 2013-02-21 14:29 | 750 | 795 | 747 | Reheat steam relief/safety valves | F610With 2-HR-PSV-915 being plugged, steam flow must be reduced since a safety is out | Trimble | Derate | Coal | 3 | 2013 | 2 | 182.7333 | 10.3434 | 7726.517 | 42.283 | 42
TC2 | D1 | 37 | 8825 | 2013-02-21 14:29 | 2013-02-21 15:40 | 660 | 795 | 747 | Other SCR NOx problems | F820While unloading an ammonia truck for U1, the transmitter being used (out of the 3 | Trimble | Derate | Coal | 3 | 2013 | 2 | 1.1833 | 0.20094 | 150.1047 | 126.8491 | 127
TC2 | D1 | 38 | 8825 | 2013-02-21 15:40 | 2013-02-21 16:13 | 505 | 795 | 747 | Other SCR NOx problems | F820Complete details attributed to this derate are explained in Event No. 37. Further | Trimble | Derate | Coal | 3 | 2013 | 2 | 0.55 | 0.20063 | 149.8698 | 272.4906 | 272
TC2 | D1 | 39 | 8823 | 2013-02-21 16:13 | 2013-02-21 17:30 | 360 | 795 | 747 | SCR NOx Other ammonia system problems | FE00Due to the ammonia system being out of service (event 37 and 38), NOx issues were | Trimble | Derate | Coal | 3 | 2013 | 2 | 1.2833 | 0.7022 | 524.5443 | 408.7358 | 409
TC2 | D1 | 40 | 8823 | 2013-02-21 17:30 | 2013-02-21 21:00 | 498 | 795 | 747 | SCR NOx Other ammonia system problems | FE00Unit load was increased to 498MW as NOx limits began to come under control and ris | Trimble | Derate | Coal | 3 | 2013 | 2 | 3.5 | 1.3075 | 976.7377 | 279.0679 | 279
TC2 | D4 | 41 | 9656 | 2013-02-21 21:00 | 2013-02-22 00:45 | 498 | 795 | 747 | Other stack or exhaust emissions testing - fossil | F790Unit derate of 498 was maintained to conduct the low load RATA testing. This test | Trimble | Derate | Coal | 3 | 2013 | 2 | 3.75 | 1.4009 | 1046.5047 | 279.0679 | 279
TC2 | D4 | 42 | 9656 | 2013-02-22 00:45 | 2013-02-22 05:30 | 625 | 795 | 747 | Other stack or exhaust emissions testing - fossil | F790Load was increased to 625MW to conduct the final stage of RATA testing which was m | Trimble | Derate | Coal | 3 | 2013 | 2 | 4.75 | 1.0157 | 758.7453 | 159.7358 | 160
TC2 | D1 | 43 | 550 | 2013-02-22 05:30 | 2013-02-25 06:30 | 750 | 795 | 747 | Reheat steam relief/safety valves | F610Unit load was returned to 750MW following the completion of the RATA testing. Thi | Trimble | Derate | Coal | 3 | 2013 | 2 | 73 | 4.1321 | 3086.6604 | 42.283 | 42
TC2 | D1 | 44 | 1495 | 2013-02-25 06:30 | 2013-02-25 08:00 | 650 | 795 | 747 | Other air heater fouling (heat pipe | F660Differential pressure on the air heater began to rise and load was reduced while i | Trimble | Derate | Coal | 3 | 2013 | 2 | 1.5 | 0.27358 | 204.3679 | 136.2453 | 136
TC2 | D1 | 45 | 360 | 2013-02-25 08:00 | 2013-02-25 09:15 | 605 | 795 | 747 | Burners | F780The C coal mill burner temperature alarm came in due to high temperature indicatio | Trimble | Derate | Coal | 3 | 2013 | 2 | 1.25 | 0.29874 | 223.1604 | 178.5283 | 179
TC2 | D1 | 46 | 1495 | 2013-02-25 09:15 | 2013-02-25 11:00 | 605 | 795 | 747 | Other air heater fouling (heat pipe | F660The air heater differential remained high after 2C mill was removed from service. | Trimble | Derate | Coal | 3 | 2013 | 2 | 1.75 | 0.41824 | 312.4245 | 178.5283 | 179
TC2 | D1 | 47 | 1495 | 2013-02-25 11:00 | 2013-02-25 15:19 | 542 | 795 | 747 | Other air heater fouling (heat pipe | F660The air heater differential remained high so further unit derate was required. Lo | Trimble | Derate | Coal | 3 | 2013 | 2 | 4.3167 | 1.3737 | 1026.1775 | 237.7245 | 238
TC2 | U1 | 48 | 1495 | 2013-02-25 15:19 | 2013-02-28 14:48 | 0 | 795 | 747 | Other air heater fouling (heat pipe | FF00With the air heater differential remaining an issue and increasing, the decision t | Trimble | Outage | Coal | 3 | 2013 | 2 | 71.4833 | 71.4833 | 53398.05 | 747 | 747
TC2 | D1 | 49 | 4640 | 2013-02-28 20:00 | 2013-03-01 03:00 | 265 | 795 | 747 | Seal oil system and seals A | F820The emergency seal oil pump failed and caused the pump to fail. Issue was a burnt | Trimble | Derate | Coal | 3 | 2013 | 2 | 7 | 4.6667 | 3486 | 498 | 498
TC2 | D1 | 50 | 4640 | 2013-03-01 03:00 | 2013-03-01 07:30 | 509 | 795 | 747 | Seal oil system and seals A | F070The seal oil pump trip was due to a burned over current relay (as explained in eve | Trimble | Derate | Coal | 3 | 2013 | 3 | 4.5 | 1.6189 | 1209.2943 | 268.7321 | 269
TC2 | D1 | 51 | 550 | 2013-03-01 07:30 | 2013-04-13 10:55 | 750 | 795 | 747 | Reheat steam relief/safety valves | F610Unit load was returned to 750MW following the return from the emergency seal oil p | Trimble | Derate | Coal | 3 | 2013 | 3 | 1035.4167 | 58.6085 | 43780.5425 | 42.283 | 42
TC2 | D1 | 52 | 9270 | 2013-03-12 00:45 | 2013-03-12 02:10 | 734 | 795 | 747 | Wet coal | FW00Wet coal issues for Unit 2 required a de-rate. During this time there was also an | Trimble | Derate | Coal | 3 | 2013 | 3 | 1.4167 | 0.1087 | 81.1991 | 57.317 | 57
TC2 | D1 | 53 | 9270 | 2013-03-12 02:10 | 2013-03-12 07:37 | 719 | 795 | 747 | Wet coal | FW00Continued wet coal issues required further de-rate | Trimble | Derate | Coal | 3 | 2013 | 3 | 5.45 | 0.52101 | 389.1917 | 71.4113 | 71
TC2 | D1 | 54 | 9270 | 2013-03-12 07:37 | 2013-03-12 10:00 | 704 | 795 | 747 | Wet coal | FW00Continued wet coal required further de-rate. Still seeing issues with the Air Hea | Trimble | Derate | Coal | 3 | 2013 | 3 | 2.3833 | 0.27281 | 203.7885 | 85.5057 | 86
TC2 | D1 | 55 | 1999 | 2013-03-12 10:00 | 2013-03-12 19:00 | 604 | 795 | 747 | Boiler | F400Unit 2 began experiences continued boiler swings after the wet coal issue was reso | Trimble | Derate | Coal | 3 | 2013 | 3 | 9 | 2.1623 | 1615.2113 | 179.4679 | 179
TC2 | D1 | 56 | 1999 | 2013-03-12 19:00 | 2013-03-13 | 545 | 795 | 747 | Boiler | F400Continued experiencing boiler swings and reduced load further to attempt to mitiga | Trimble | Derate | Coal | 3 | 2013 | 3 | 5 | 1.5723 | 1174.5283 | 234.9057 | 235
TC2 | D1 | 57 | 1999 | 2013-03-13 | 2013-03-13 11:00 | 550 | 795 | 747 | Boiler | F400Continued experiencing boiler swings but increased load slightly to test out boile | Trimble | Derate | Coal | 3 | 2013 | 3 | 11 | 3.3899 | 2532.283 | 230.2075 | 230
TC2 | D1 | 58 | 1999 | 2013-03-13 11:00 | 2013-03-13 14:00 | 470 | 795 | 747 | Boiler | F400Boiler swings still occurring and load had to be reduced further to regain boiler | Trimble | Derate | Coal | 3 | 2013 | 3 | 3 | 1.2264 | 916.1321 | 305.3774 | 305
TC2 | D1 | 59 | 1999 | 2013-03-13 14:00 | 2013-03-17 17:13 | 500 | 795 | 747 | Boiler | F400Load was able to be increased to 500 MW with boiler swings no longer being an issu | Trimble | Derate | Coal | 3 | 2013 | 3 | 99.2167 | 36.8162 | 27501.7368 | 277.1887 | 277
TC2 | U1 | 60 | 1999 | 2013-03-17 17:13 | 2013-03-24 05:47 | 0 | 795 | 747 | Boiler | F400The boiler swings were unable to be controlled further. Unit was taken offline an | Trimble | Outage | Coal | 3 | 2013 | 3 | 156.5667 | 156.5667 | 116955.3 | 747 | 747
TC2 | PO | 61 | 360 | 2013-03-24 05:47 | 2013-04-15 | 0 | 795 | 747 | Burners | FE00The Unit 2 outage was planned for complete modifications to the A, B, C, D, and E | Trimble | Other | Coal | 3 | 2013 | 3 | 522.2167 | 522.2167 | 390095.85 | 747 | 747
TC2 | PE | 62 | 4289 | 2013-04-15 | 2013-05-30 05:30 | 0 | 795 | 747 | Other lube oil system problems | F180The original scope of the PO was completed, but additional scope identified with t | Trimble | Other | Coal | 3 | 2013 | 4 | 1085.5 | 1085.5 | 810868.5 | 747 | 747
TC2 | SF | 63 | 4499 | 2013-05-30 05:30 | 2013-05-30 13:10 | 0 | 795 | 747 | Other miscellaneous steam turbine problems | F780Turbine shell expansion indication was not reading so we held the unit start-up un | Trimble | Outage | Coal | 3 | 2013 | 5 | 7.6667 | 7.6667 | 5727 | 747 | 747
TC2 | SF | 64 | 4899 | 2013-05-30 13:10 | 2013-06-02 13:09 | 0 | 795 | 747 | Other miscellaneous generator problems | F870Generator lock-out occurred when flashing the field on (pulled fires out of the bo | Trimble | Outage | Coal | 3 | 2013 | 5 | 71.9833 | 71.9833 | 53771.55 | 747 | 747
TC2 | U1 | 65 | 4609 | 2013-06-02 14:30 | 2013-06-02 22:45 | 0 | 795 | 747 | Other exciter problems | F830Had to place the bolts back on the Generator Pot fuse links. We were able to hold | Trimble | Outage | Coal | 3 | 2013 | 6 | 8.25 | 8.25 | 6162.75 | 747 | 747
TC2 | U1 | 66 | 9930 | 2013-06-03 00:21 | 2013-06-03 08:32 | 0 | 795 | 747 | Operating procedure error | F420Operator failed to change over from MK VI to DCS | Trimble | Outage | Coal | 3 | 2013 | 6 | 8.1833 | 8.1833 | 6112.95 | 747 | 747
TC2 | U1 | 67 | 1000 | 2013-06-03 08:32 | 2013-06-05 16:52 | 0 | 795 | 747 | Waterwall (Furnace wall) A | F540Leak in tube weld near spiral balance header. | Trimble | Outage | Coal | 3 | 2013 | 6 | 56.3333 | 56.3333 | 42081 | 747 | 747
TC2 | D4 | 68 | 360 | 2013-06-06 02:00 | 2013-06-06 12:00 | 438 | 795 | 747 | Burners | F790Post outage tuning per Doosan request. Hold at 400 MW for testing and tuning of b | Trimble | Derate | Coal | 3 | 2013 | 6 | 10 | 4.4906 | 3354.4528 | 335.4453 | 335
TC2 | PD | 69 | 360 | 2013-06-06 12:00 | 2013-06-07 04:15 | 475 | 795 | 747 | Burners | F790Further tuning at a variable de-rate following 400 MW hold increasing to 550 MW ov | Trimble | Derate | Coal | 3 | 2013 | 6 | 16.25 | 6.5409 | 4886.0377 | 300.6792 | 301
TC2 | D1 | 70 | 9620 | 2013-06-07 04:15 | 2013-06-07 13:00 | 595 | 795 | 747 | Particulate stack emissions (fossil) | FE00Derate hold at 550MW is due to CEM particulate matter indication. This believed t | Trimble | Derate | Coal | 3 | 2013 | 6 | 8.75 | 2.2013 | 1644.3396 | 187.9245 | 188
TC2 | D1 | 71 | 9620 | 2013-06-07 13:00 | 2013-06-07 14:00 | 660 | 795 | 747 | Particulate stack emissions (fossil) | FE00Derate hold at 660MW is due to CEM particulate matter indication. This believed t | Trimble | Derate | Coal | 3 | 2013 | 6 | 1 | 0.16981 | 126.8491 | 126.8491 | 127
TC2 | D1 | 72 | 9620 | 2013-06-07 14:00 | 2013-06-07 15:00 | 690 | 795 | 747 | Particulate stack emissions (fossil) | FE00Derate hold at 690MW is due to CEM particulate matter indication. This believed t | Trimble | Derate | Coal | 3 | 2013 | 6 | 1 | 0.13208 | 98.6604 | 98.6604 | 99
TC2 | D1 | 73 | 9620 | 2013-06-07 15:00 | 2013-06-07 16:00 | 710 | 795 | 747 | Particulate stack emissions (fossil) | FE00Derate hold at 710MW is due to CEM particulate matter indication. This believed t | Trimble | Derate | Coal | 3 | 2013 | 6 | 1 | 0.10692 | 79.8679 | 79.8679 | 80
TC2 | D1 | 74 | 9620 | 2013-06-07 16:00 | 2013-06-07 19:25 | 690 | 795 | 747 | Particulate stack emissions (fossil) | FE00Derate hold at 690MW is due to CEM particulate matter indication. This believed t | Trimble | Derate | Coal | 3 | 2013 | 6 | 3.4167 | 0.45126 | 337.0896 | 98.6604 | 99
TC2 | D1 | 75 | 3441 | 2013-06-07 19:25 | 2013-06-07 21:00 | 730 | 795 | 747 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F5408A high pressure feedwater had the indicator level flange leaking. Reduced load t | Trimble | Derate | Coal | 3 | 2013 | 6 | 1.5833 | 0.12945 | 96.7028 | 61.0755 | 61
TC2 | D1 | 76 | 3441 | 2013-06-07 21:00 | 2013-06-07 21:30 | 750 | 795 | 747 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F5408A high pressure FWH had a leaking flange on the indication level and was repaired | Trimble | Derate | Coal | 3 | 2013 | 6 | 0.5 | 0.028302 | 21.1415 | 42.283 | 42
TC2 | D1 | 77 | 1455 | 2013-06-07 21:30 | 2013-06-08 | 375 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 2.5 | 1.3208 | 986.6038 | 394.6415 | 395
TC2 | D1 | 78 | 1455 | 2013-06-08 | 2013-06-08 05:00 | 480 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 5 | 1.9811 | 1479.9057 | 295.9811 | 296
TC2 | D1 | 79 | 1455 | 2013-06-08 05:00 | 2013-06-08 12:00 | 700 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 7 | 0.83648 | 624.8491 | 89.2642 | 89
TC2 | D1 | 80 | 1455 | 2013-06-08 12:00 | 2013-06-08 15:00 | 760 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 3 | 0.13208 | 98.6604 | 32.8868 | 33
TC2 | D1 | 81 | 1455 | 2013-06-08 15:00 | 2013-06-08 17:00 | 680 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 2 | 0.28931 | 216.1132 | 108.0566 | 108
TC2 | D1 | 82 | 1455 | 2013-06-08 17:00 | 2013-06-08 17:19 | 660 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 0.31667 | 0.053774 | 40.1689 | 126.8491 | 127
TC2 | D1 | 83 | 1455 | 2013-06-08 17:19 | 2013-06-08 18:00 | 615 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 0.68333 | 0.15472 | 115.5736 | 169.1321 | 169
TC2 | D1 | 84 | 1455 | 2013-06-08 18:00 | 2013-06-09 | 575 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 6 | 1.6604 | 1240.3019 | 206.717 | 207
TC2 | D1 | 85 | 1455 | 2013-06-09 | 2013-06-09 00:15 | 670 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 0.25 | 0.039308 | 29.3632 | 117.4528 | 117
TC2 | D1 | 86 | 1455 | 2013-06-09 00:15 | 2013-06-10 02:24 | 620 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 26.15 | 5.7563 | 4299.9481 | 164.434 | 164
TC2 | D1 | 87 | 1455 | 2013-06-10 02:24 | 2013-06-10 03:22 | 600 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 0.96667 | 0.23711 | 177.1189 | 183.2264 | 183
TC2 | D1 | 88 | 1455 | 2013-06-10 03:22 | 2013-06-10 12:30 | 580 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 9.1333 | 2.47 | 1845.1057 | 202.0189 | 202
TC2 | D1 | 89 | 1455 | 2013-06-12 14:40 | 2013-06-12 17:30 | 750 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 2.8333 | 0.16038 | 119.8019 | 42.283 | 42
TC2 | D1 | 90 | 1455 | 2013-06-13 14:30 | 2013-06-13 18:30 | 695 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 4 | 0.50314 | 375.8491 | 93.9623 | 94
TC2 | D1 | 91 | 1455 | 2013-06-14 04:00 | 2013-06-14 04:50 | 650 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 0.83333 | 0.15199 | 113.5377 | 136.2453 | 136
TC2 | D1 | 92 | 1455 | 2013-06-14 04:50 | 2013-06-14 05:20 | 623 | 795 | 747 | Induced draft fans | F660Fan stall issues using original fan stall ring, I/E regularly cleaned ports and ch | Trimble | Derate | Coal | 3 | 2013 | 6 | 0.5 | 0.10818 | 80.8075 | 161.6151 | 162
TC2 | D1 | 93 | 1455 | 2013-06-14 05:20 | 2013-06-14 10:10 | 270 | 795 | 747 | Induced draft fans | F660Changed from original stall ring instrumentation to newly installed fan stall ring | Trimble | Derate | Coal | 3 | 2013 | 6 | 4.8333 | 3.1918 | 2384.2925 | 493.3019 | 493
TC2 | D1 | 94 | 9610 | 2013-06-14 10:10 | 2013-06-14 13:45 | 445 | 795 | 747 | NOx stack emissions (fossil) | FE00During the fan stall ring change-out, load level required ammonia injection to be | Trimble | Derate | Coal | 3 | 2013 | 6 | 3.5833 | 1.5776 | 1178.4434 | 328.8679 | 329
TC2 | D1 | 95 | 9616 | 2013-06-19 07:35 | 2013-06-19 09:53 | 690 | 795 | 747 | CO stack emissions | FE00During boiler tuning, spikes in CO brought the unit close to the exceedance limit | Trimble | Derate | Coal | 3 | 2013 | 6 | 2.3 | 0.30377 | 226.9189 | 98.6604 | 99
TC2 | D4 | 96 | 920 | 2013-06-22 23:00 | 2013-06-23 05:30 | 450 | 795 | 747 | Other slag and ash removal problems A | FS00TC2 was derated in order to perform the weekly planned deslag of the boiler as rec | Trimble | Derate | Coal | 3 | 2013 | 6 | 6.5 | 2.8208 | 2107.1038 | 324.1698 | 324
TC2 | D1 | 97 | 9620 | 2013-06-26 01:47 | 2013-06-26 02:11 | 732 | 795 | 747 | Particulate stack emissions (fossil) | FE00High particulate readings required load derate. | Trimble | Derate | Coal | 3 | 2013 | 6 | 0.4 | 0.031698 | 23.6785 | 59.1962 | 59
TC2 | D1 | 98 | 9620 | 2013-06-26 02:11 | 2013-06-26 02:44 | 685 | 795 | 747 | Particulate stack emissions (fossil) | FE00High particulate readings required load derate. | Trimble | Derate | Coal | 3 | 2013 | 6 | 0.55 | 0.076101 | 56.8472 | 103.3585 | 103
TC2 | D1 | 99 | 9620 | 2013-06-26 02:44 | 2013-06-26 07:00 | 650 | 795 | 747 | Particulate stack emissions (fossil) | FE00High particulate readings required load derate. | Trimble | Derate | Coal | 3 | 2013 | 6 | 4.2667 | 0.7782 | 581.3132 | 136.2453 | 136
TC2 | D1 | 100 | 9620 | 2013-06-27 18:00 | 2013-06-28 | 680 | 795 | 747 | Particulate stack emissions (fossil) | FE00High particulate readings required load derate. | Trimble | Derate | Coal | 3 | 2013 | 6 | 6 | 0.86792 | 648.3396 | 108.0566 | 108
TC2 | D4 | 101 | 920 | 2013-06-30 | 2013-06-30 09:00 | 450 | 795 | 747 | Other slag and ash removal problems A | FS00Weekly deslag for Unit 2 based on OEM recommendations for cleaning the boiler. | Trimble | Derate | Coal | 3 | 2013 | 6 | 9 | 3.9057 | 2917.5283 | 324.1698 | 324
TC2 | NC | 102 | 920 | 2013-07-07 00:01 | 2013-07-08 03:45 | 0 | 795 | 747 | Other slag and ash removal problems A | FS00Weekly deslag planned for Unit 2 based on OEM recommendations | Trimble | Other | Coal | 3 | 2013 | 7 | 27.7333 | 27.7333 | 20716.8 | 747 | 747
TC2 | D1 | 103 | 9620 | 2013-07-08 03:45 | 2013-07-08 06:15 | 680 | 795 | 747 | Particulate stack emissions (fossil) | FE00High particulates required a de-rate to avoid exceeding limits. | Trimble | Derate | Coal | 3 | 2013 | 7 | 2.5 | 0.36164 | 270.1415 | 108.0566 | 108
TC2 | D1 | 104 | 9600 | 2013-07-08 16:20 | 2013-07-09 00:25 | 650 | 795 | 747 | SO2 stack emissions (fossil) | FE00SO2 emissions running high, derate initiated to avoid exceedance of daily limit. | Trimble | Derate | Coal | 3 | 2013 | 7 | 8.0833 | 1.4743 | 1101.316 | 136.2453 | 136
TC2 | D1 | 105 | 9600 | 2013-07-09 21:07 | 2013-07-10 | 700 | 795 | 747 | SO2 stack emissions (fossil) | FE00SO2 emissions running high, derate initiated to avoid exceedance of daily limit. | Trimble | Derate | Coal | 3 | 2013 | 7 | 2.8833 | 0.34455 | 257.3783 | 89.2642 | 89
TC2 | D1 | 106 | 8650 | 2013-07-10 01:30 | 2013-07-10 02:00 | 739 | 795 | 747 | Baghouse systems | F660Fabric fitler differential pressure ran high requiring derate. | Trimble | Derate | Coal | 3 | 2013 | 7 | 0.5 | 0.03522 | 26.3094 | 52.6189 | 53
TC2 | D1 | 107 | 9620 | 2013-07-11 04:05 | 2013-07-11 07:00 | 725 | 795 | 747 | Particulate stack emissions (fossil) | FE00Particulates ran at a higher rate, derate initiated to avoid exceedance of daily l | Trimble | Derate | Coal | 3 | 2013 | 7 | 2.9167 | 0.25681 | 191.8396 | 65.7736 | 66
TC2 | NC | 108 | 8810 | 2013-07-16 | 2013-07-16 03:00 | 0 | 795 | 747 | SCR NOx Reactor | F790Tuning of the SCR by Doosan was scheduled and required a low removal rate in order | Trimble | Other | Coal | 3 | 2013 | 7 | 3 | 3 | 2241 | 747 | 747
TC2 | NC | 109 | 1190 | 2013-07-21 | 2013-07-21 07:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00This load reduction was for weekly boiler de-slag. The load could have been return | Trimble | Other | Coal | 3 | 2013 | 7 | 7 | 7 | 5229 | 747 | 747
TC2 | D1 | 110 | 4250 | 2013-07-21 22:00 | 2013-07-22 | 750 | 795 | 747 | Other low pressure turbine problems | F660The load drop was due to high steam flow >5150KPPH. This was due to having the 7A | Trimble | Derate | Coal | 3 | 2013 | 7 | 2 | 0.11321 | 84.566 | 42.283 | 42
TC2 | NC | 111 | 1190 | 2013-07-28 | 2013-07-28 09:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00This load reduction was for weekly boiler de-slag. The load could have been return | Trimble | Other | Coal | 3 | 2013 | 7 | 9 | 9 | 6723 | 747 | 747
TC2 | NC | 112 | 1990 | 2013-07-30 08:00 | 2013-07-30 12:00 | 0 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Non-curtailing event to perform unit heat rate and capability test. | Trimble | Other | Coal | 3 | 2013 | 7 | 4 | 4 | 2988 | 747 | 747
TC2 | D1 | 113 | 8125 | 2013-08-01 17:50 | 2013-08-01 20:23 | 680 | 795 | 747 | Scrubber recycle (liquid) pumps | F820The 2C Recycle Pump tripped due to high temperature (203 degF). Placed it back in | Trimble | Derate | Coal | 3 | 2013 | 8 | 2.55 | 0.36887 | 275.5443 | 108.0566 | 108
TC2 | NC | 114 | 1190 | 2013-08-04 | 2013-08-04 09:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to execute OEM recommended weekly boiler deslag on TC2. Ful | Trimble | Other | Coal | 3 | 2013 | 8 | 9 | 9 | 6723 | 747 | 747
TC2 | D1 | 115 | 9616 | 2013-08-07 01:20 | 2013-08-07 02:55 | 681 | 795 | 747 | CO stack emissions | FE00High CO readings required a derate to avoid exceedances. | Trimble | Derate | Coal | 3 | 2013 | 8 | 1.5833 | 0.22704 | 169.6019 | 107.117 | 107
TC2 | D1 | 116 | 310 | 2013-08-07 11:06 | 2013-08-07 12:00 | 650 | 795 | 747 | Pulverizer mills | F8202A coal mill tripped due to loss of sufficient PA flow. Derate required, then swa | Trimble | Derate | Coal | 3 | 2013 | 8 | 0.9 | 0.16415 | 122.6208 | 136.2453 | 136
TC2 | NC | 117 | 1190 | 2013-08-11 | 2013-08-11 08:15 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Weekly OEM suggested derate for boiler deslag. Unit available for full load if re | Trimble | Other | Coal | 3 | 2013 | 8 | 8.25 | 8.25 | 6162.75 | 747 | 747
TC2 | NC | 118 | 1190 | 2013-08-18 | 2013-08-18 09:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Weekly boiler deslag for cleaning of the furnace based on OEM recommendations. Ab | Trimble | Other | Coal | 3 | 2013 | 8 | 9 | 9 | 6723 | 747 | 747
TC2 | D4 | 119 | 3441 | 2013-08-23 20:30 | 2013-08-24 | 450 | 795 | 747 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F540Planned derate to conduct maintenance on the 8A HP FW Heater due to bypass valve n | Trimble | Derate | Coal | 3 | 2013 | 8 | 3.5 | 1.5189 | 1134.5943 | 324.1698 | 324
TC2 | NC | 120 | 1190 | 2013-08-24 | 2013-08-24 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Weekly boiler deslag as recommended by boiler OEM. Deslag was performed at 450 MW | Trimble | Other | Coal | 3 | 2013 | 8 | 8 | 8 | 5976 | 747 | 747
TC2 | D1 | 121 | 9616 | 2013-08-31 19:53 | 2013-08-31 21:00 | 685 | 795 | 747 | CO stack emissions | FE00Derate due to CO spike. | Trimble | Derate | Coal | 3 | 2013 | 8 | 1.1167 | 0.15451 | 115.417 | 103.3585 | 103
TC2 | D1 | 122 | 9616 | 2013-09-01 16:48 | 2013-09-01 17:58 | 681 | 795 | 747 | CO stack emissions | FE00CO emission issues continued with the unit and required derate. | Trimble | Derate | Coal | 3 | 2013 | 9 | 1.1667 | 0.1673 | 124.9698 | 107.117 | 107
TC2 | D1 | 123 | 1455 | 2013-09-01 17:58 | 2013-09-01 19:30 | 700 | 795 | 747 | Induced draft fans | F660ID Fan stall alarms required derate to avoid unit trip. | Trimble | Derate | Coal | 3 | 2013 | 9 | 1.5333 | 0.18323 | 136.8717 | 89.2642 | 89
TC2 | D1 | 124 | 9616 | 2013-09-01 19:55 | 2013-09-02 | 750 | 795 | 747 | CO stack emissions | FE00Emissions issues involving CO levels following the low suction pressure on the ID | Trimble | Derate | Coal | 3 | 2013 | 9 | 4.0833 | 0.23113 | 172.6557 | 42.283 | 42
TC2 | NC | 125 | 1190 | 2013-09-02 | 2013-09-02 07:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing event to conduct boiler deslag as recommended by OEM at 450 MW. Un | Trimble | Other | Coal | 3 | 2013 | 9 | 7 | 7 | 5229 | 747 | 747
TC2 | D1 | 126 | 9616 | 2013-09-02 12:00 | 2013-09-02 13:30 | 680 | 795 | 747 | CO stack emissions | FE00Continued CO issues along with FD Fan issues required derate to 680 MW. | Trimble | Derate | Coal | 3 | 2013 | 9 | 1.5 | 0.21698 | 162.0849 | 108.0566 | 108
TC2 | D1 | 127 | 250 | 2013-09-03 18:57 | 2013-09-03 20:00 | 699 | 795 | 747 | Pulverizer feeders | F8202B Mill Feeder tripped requiring derate. | Trimble | Derate | Coal | 3 | 2013 | 9 | 1.05 | 0.12679 | 94.714 | 90.2038 | 90
TC2 | D1 | 128 | 250 | 2013-09-03 20:00 | 2013-09-04 05:00 | 659 | 795 | 747 | Pulverizer feeders | F060Following the mill trip, it was found that the feeder for the 2B mill was damaged. | Trimble | Derate | Coal | 3 | 2013 | 9 | 9 | 1.5396 | 1150.0981 | 127.7887 | 128
TC2 | NC | 129 | 1190 | 2013-09-06 21:00 | 2013-09-07 06:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Planned weekly boiler deslag as recommended by OEM. Unit available for full load | Trimble | Other | Coal | 3 | 2013 | 9 | 9 | 9 | 6723 | 747 | 747
TC2 | D1 | 130 | 266 | 2013-09-10 10:57 | 2013-09-10 11:30 | 764 | 795 | 747 | Primary air heater fouling | F660Derate required due to AH Differntial increase due to suspected pluggage. Air hea | Trimble | Derate | Coal | 3 | 2013 | 9 | 0.55 | 0.021447 | 16.0206 | 29.1283 | 29
TC2 | D1 | 131 | 1400 | 2013-09-10 15:17 | 2013-09-11 06:00 | 771 | 795 | 747 | Forced draft fans | F660Derate required due to FD Fan stall. Air heater wash planned for weekend outage. | Trimble | Derate | Coal | 3 | 2013 | 9 | 14.7167 | 0.44428 | 331.8747 | 22.5509 | 23
TC2 | D1 | 132 | 1400 | 2013-09-11 06:00 | 2013-09-11 19:04 | 749 | 795 | 747 | Forced draft fans | F660Derate required due to FD Fan stall. Air heater wash planned for weekend outage. | Trimble | Derate | Coal | 3 | 2013 | 9 | 13.0667 | 0.75606 | 564.7758 | 43.2226 | 43
TC2 | D1 | 133 | 1400 | 2013-09-11 19:04 | 2013-09-12 00:06 | 729 | 795 | 747 | Forced draft fans | F660Derate required due to FD Fan stall. Air heater wash planned for weekend outage. | Trimble | Derate | Coal | 3 | 2013 | 9 | 5.0333 | 0.41786 | 312.1426 | 62.0151 | 62
TC2 | D1 | 134 | 1400 | 2013-09-12 00:06 | 2013-09-12 09:32 | 719 | 795 | 747 | Forced draft fans | F660Derate required due to FD Fan stall. Air heater wash planned for weekend outage. | Trimble | Derate | Coal | 3 | 2013 | 9 | 9.4333 | 0.9018 | 673.6468 | 71.4113 | 71
TC2 | D1 | 135 | 1400 | 2013-09-12 09:32 | 2013-09-12 15:02 | 680 | 795 | 747 | Forced draft fans | F660Derate required due to FD Fan stall. | Trimble | Derate | Coal | 3 | 2013 | 9 | 5.5 | 0.7956 | 594.3113 | 108.0566 | 108
TC2 | D1 | 136 | 1400 | 2013-09-12 15:02 | 2013-09-12 16:16 | 275 | 795 | 747 | Forced draft fans | F660Derate required due to FD Fan stall. | Trimble | Derate | Coal | 3 | 2013 | 9 | 1.2333 | 0.80671 | 602.6113 | 488.6038 | 489
TC2 | U1 | 137 | 1400 | 2013-09-12 16:16 | 2013-09-12 19:17 | 0 | 795 | 747 | Forced draft fans | F660FD Fan stall runback alarms started coming in and the F/D Fans went into a run bac | Trimble | Outage | Coal | 3 | 2013 | 9 | 3.0167 | 3.0167 | 2253.45 | 747 | 747
TC2 | MO | 138 | 266 | 2013-09-12 19:17 | 2013-09-16 15:57 | 0 | 795 | 747 | Primary air heater fouling | FF00Maintenance outage to perform AH wash. Additional maintenance work for repairing | Trimble | Maintenance | Coal | 3 | 2013 | 9 | 92.6667 | 92.6667 | 69222 | 747 | 747
TC2 | D1 | 139 | 1415 | 2013-09-17 02:00 | 2013-09-17 08:00 | 650 | 795 | 747 | Forced draft fan controls | F400Unit derate was due to air flow issues for the burners from the FD fans. Root cau | Trimble | Derate | Coal | 3 | 2013 | 9 | 6 | 1.0943 | 817.4717 | 136.2453 | 136
TC2 | NC | 140 | 1190 | 2013-09-20 17:00 | 2013-09-20 23:15 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Boiler deslag conducted at 450 MW based on OEM recommendations. Unit available to | Trimble | Other | Coal | 3 | 2013 | 9 | 6.25 | 6.25 | 4668.75 | 747 | 747
TC2 | D1 | 141 | 250 | 2013-09-21 11:56 | 2013-09-21 12:45 | 665 | 795 | 747 | Pulverizer feeders | F8202F Coal mill tripped due to "Feeder discharge plugged". Fixed issues and returned | Trimble | Derate | Coal | 3 | 2013 | 9 | 0.81667 | 0.13354 | 99.7566 | 122.1509 | 122
TC2 | D1 | 142 | 9305 | 2013-09-22 23:15 | 2013-09-23 01:00 | 730 | 795 | 747 | Ash disposal problem | F060The level trasmitter on the Submerged Scraper Conveyor failed and water level drop | Trimble | Derate | Coal | 3 | 2013 | 9 | 1.75 | 0.14308 | 106.8821 | 61.0755 | 61
TC2 | D1 | 143 | 310 | 2013-09-23 21:40 | 2013-09-23 23:52 | 650 | 795 | 747 | Pulverizer mills | F820Derate was due to loss of 2D coal mill. The Coal Mill trip required putting the b | Trimble | Derate | Coal | 3 | 2013 | 9 | 2.2 | 0.40126 | 299.7396 | 136.2453 | 136
TC2 | NC | 144 | 1190 | 2013-09-29 00:01 | 2013-09-29 08:15 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Boiler deslag conducted at 450 MW based on OEM recommendations. Unit available to | Trimble | Other | Coal | 3 | 2013 | 9 | 8.2333 | 8.2333 | 6150.3 | 747 | 747
TC2 | D1 | 145 | 510 | 2013-10-01 00:30 | 2013-10-01 08:21 | 804 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 7.85 | -0.088868 | -66.3843 | 0 | 0
TC2 | D1 | 146 | 9616 | 2013-10-01 08:21 | 2013-10-01 10:30 | 704 | 795 | 747 | CO stack emissions | FE00Excess CO emissions required a derate to keep the Unit from experiencing an exceda | Trimble | Derate | Coal | 3 | 2013 | 10 | 2.15 | 0.2461 | 183.8372 | 85.5057 | 86
TC2 | D1 | 147 | 510 | 2013-10-01 10:30 | 2013-10-02 10:04 | 804 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 23.5667 | -0.26679 | -199.294 | 0 | 0
TC2 | D1 | 148 | 510 | 2013-10-02 10:04 | 2013-10-02 11:04 | 799 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 1 | -0.0050314 | -3.7585 | 0 | 0
TC2 | D1 | 149 | 510 | 2013-10-02 11:04 | 2013-10-02 13:13 | 804 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 2.15 | -0.02434 | -18.1817 | 0 | 0
TC2 | D1 | 150 | 510 | 2013-10-02 13:13 | 2013-10-06 00:01 | 799 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 82.8 | -0.4166 | -311.203 | 0 | 0
TC2 | NC | 151 | 1190 | 2013-10-06 00:01 | 2013-10-06 09:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00OEM recommended deslag of the boiler. Unit available to return to full load if di | Trimble | Other | Coal | 3 | 2013 | 10 | 8.9833 | 8.9833 | 6710.55 | 747 | 747
TC2 | D1 | 152 | 510 | 2013-10-06 09:00 | 2013-10-13 | 799 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 159 | -0.8 | -597.6 | 0 | 0
TC2 | NC | 153 | 1190 | 2013-10-13 | 2013-10-13 09:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for Boiler OEM recommended deslag. Unit available if requir | Trimble | Other | Coal | 3 | 2013 | 10 | 9 | 9 | 6723 | 747 | 747
TC2 | D1 | 154 | 510 | 2013-10-13 09:00 | 2013-10-14 16:41 | 799 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 31.6833 | -0.15941 | -119.0815 | 0 | 0
TC2 | D1 | 155 | 8821 | 2013-10-14 16:41 | 2013-10-14 18:00 | 676 | 795 | 747 | SCR NOx Ammonia tanks | F8202B Ammonia Pump tripped and ammonia flow lost to unit. Had to derate due to loss | Trimble | Derate | Coal | 3 | 2013 | 10 | 1.3167 | 0.19709 | 147.2232 | 111.8151 | 112
TC2 | D1 | 156 | 510 | 2013-10-14 18:00 | 2013-10-20 | 799 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 126 | -0.63396 | -473.5698 | 0 | 0
TC2 | NC | 157 | 1190 | 2013-10-20 | 2013-10-20 07:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for Boiler OEM recommended deslag. Unit available for full | Trimble | Other | Coal | 3 | 2013 | 10 | 7 | 7 | 5229 | 747 | 747
TC2 | D1 | 158 | 510 | 2013-10-20 07:00 | 2013-10-20 08:58 | 799 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 1.9667 | -0.0098952 | -7.3917 | 0 | 0
TC2 | D1 | 159 | 9616 | 2013-10-20 08:58 | 2013-10-20 11:00 | 699 | 795 | 747 | CO stack emissions | FE00CO Emission issues due to O2 trim setting issues returning from deslag. | Trimble | Derate | Coal | 3 | 2013 | 10 | 2.0333 | 0.24553 | 183.4143 | 90.2038 | 90
TC2 | D1 | 160 | 510 | 2013-10-20 11:00 | 2013-10-27 | 799 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 157 | -0.78994 | -590.083 | 0 | 0
TC2 | NC | 161 | 1190 | 2013-10-27 | 2013-10-27 03:29 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for OEM recommended weekly deslag. Unit available for full | Trimble | Other | Coal | 3 | 2013 | 10 | 3.4833 | 3.4833 | 2602.05 | 747 | 747
TC2 | U1 | 162 | 3150 | 2013-10-27 03:29 | 2013-10-27 07:00 | 0 | 795 | 747 | Hot well level controls | F820High hotwell level transmitter readings caused the unit to MFT following end of un | Trimble | Outage | Coal | 3 | 2013 | 10 | 3.5167 | 3.5167 | 2626.95 | 747 | 747
TC2 | SF | 163 | 385 | 2013-10-27 07:00 | 2013-10-27 17:05 | 0 | 795 | 747 | Igniters | F460Start-up failure was caused by loss of instrument air pressure due to use of tempo | Trimble | Outage | Coal | 3 | 2013 | 10 | 10.0833 | 10.0833 | 7532.25 | 747 | 747
TC2 | D1 | 164 | 510 | 2013-10-27 22:15 | 2013-10-28 12:10 | 799 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 13.9167 | -0.070021 | -52.3057 | 0 | 0
TC2 | D1 | 165 | 8823 | 2013-10-28 12:10 | 2013-10-28 13:00 | 699 | 795 | 747 | SCR NOx Other ammonia system problems | F820Ammonia pumps tripped causing loss of ammonia feed requiring derate until pumps co | Trimble | Derate | Coal | 3 | 2013 | 10 | 0.83333 | 0.10063 | 75.1698 | 90.2038 | 90
TC2 | D1 | 166 | 510 | 2013-10-28 13:00 | 2013-10-30 06:00 | 799 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 41 | -0.20629 | -154.0981 | 0 | 0
TC2 | D1 | 167 | 510 | 2013-10-30 06:00 | 2013-10-30 07:00 | 699 | 795 | 747 | Main steam relief/safety valves off superheater | F540System over pressure caused the SH Safeties to lift, began leaking through. Had t | Trimble | Derate | Coal | 3 | 2013 | 10 | 1 | 0.12075 | 90.2038 | 90.2038 | 90
TC2 | D1 | 168 | 510 | 2013-10-30 07:00 | 2013-10-31 13:09 | 799 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 30.15 | -0.1517 | -113.3185 | 0 | 0
TC2 | D1 | 169 | 510 | 2013-10-31 13:09 | 2013-10-31 16:00 | 699 | 795 | 747 | Main steam relief/safety valves off superheater | F590Precision was brought in to reset the Main Steam safety valves, which required der | Trimble | Derate | Coal | 3 | 2013 | 10 | 2.85 | 0.34415 | 257.0808 | 90.2038 | 90
TC2 | D1 | 170 | 510 | 2013-10-31 16:00 | 2013-11-01 09:30 | 799 | 795 | 747 | Main steam relief/safety valves off superheater | F540Both electromatic relief valves are isolated on Unit 2 due to leaking gaskets. St | Trimble | Derate | Coal | 3 | 2013 | 10 | 17.5 | -0.08805 | -65.7736 | 0 | 0
TC2 | D1 | 171 | 510 | 2013-11-01 09:30 | 2013-11-01 10:00 | 659 | 795 | 747 | Main steam relief/safety valves off superheater | F690The #3 Safety on the south side of unit 2 will not lift. Derate taken to decrease | Trimble | Derate | Coal | 3 | 2013 | 11 | 0.5 | 0.085535 | 63.8943 | 127.7887 | 128
TC2 | D1 | 172 | 510 | 2013-11-01 10:00 | 2013-11-03 | 709 | 795 | 747 | Main steam relief/safety valves off superheater | F690The #3 Safety on the south side of unit 2 will not lift. Able to increase load fr | Trimble | Derate | Coal | 3 | 2013 | 11 | 38 | 4.1107 | 3070.6868 | 80.8075 | 81
TC2 | NC | 173 | 1190 | 2013-11-03 | 2013-11-03 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for Boiler OEM recommended weekly deslag. Unit available to | Trimble | Other | Coal | 3 | 2013 | 11 | 8 | 8 | 5976 | 747 | 747
TC2 | D1 | 174 | 510 | 2013-11-03 08:00 | 2013-11-10 | 709 | 795 | 747 | Main steam relief/safety valves off superheater | F690The #3 Safety on the south side of unit 2 will not lift. Unit derate is required | Trimble | Derate | Coal | 3 | 2013 | 11 | 160 | 17.3082 | 12929.2075 | 80.8075 | 81
TC2 | NC | 175 | 1190 | 2013-11-10 | 2013-11-10 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for OEM recommended weekly deslag. Unit available for full | Trimble | Other | Coal | 3 | 2013 | 11 | 8 | 8 | 5976 | 747 | 747
TC2 | D1 | 176 | 510 | 2013-11-10 08:00 | 2013-11-16 02:01 | 709 | 795 | 747 | Main steam relief/safety valves off superheater | F690The #3 Safety on the south side of unit 2 will not lift. Unit derate is required | Trimble | Derate | Coal | 3 | 2013 | 11 | 138.0167 | 14.9301 | 11152.7883 | 80.8075 | 81
TC2 | MO | 177 | 510 | 2013-11-16 02:01 | 2013-11-18 17:40 | 0 | 795 | 747 | Main steam relief/safety valves off superheater | F590Various safety valves on Unit 2 required maintenance. Superheat safety valve woul | Trimble | Maintenance | Coal | 3 | 2013 | 11 | 63.65 | 63.65 | 47546.55 | 747 | 747
TC2 | U1 | 178 | 3431 | 2013-11-19 03:04 | 2013-11-21 01:41 | 0 | 795 | 747 | Other feedwater valves | F830The TC2 7B FW Bypass valve packing began leaking during operation of the valve. U | Trimble | Outage | Coal | 3 | 2013 | 11 | 46.6167 | 46.6167 | 34822.65 | 747 | 747
TC2 | D1 | 179 | 9610 | 2013-11-21 16:00 | 2013-11-22 01:00 | 649 | 795 | 747 | NOx stack emissions (fossil) | FE00During start-up and ramping, there was a delay in introducing ammonia. Additional | Trimble | Derate | Coal | 3 | 2013 | 11 | 9 | 1.6528 | 1234.6642 | 137.1849 | 137
TC2 | D1 | 180 | 9610 | 2013-11-22 01:00 | 2013-11-22 01:53 | 750 | 795 | 747 | NOx stack emissions (fossil) | FE00Derate necessary to ensure no NOx exceedance. See event 179 for additional detail | Trimble | Derate | Coal | 3 | 2013 | 11 | 0.88333 | 0.05 | 37.35 | 42.283 | 42
TC2 | D1 | 181 | 9616 | 2013-11-23 13:32 | 2013-11-23 15:00 | 709 | 795 | 747 | CO stack emissions | FE00Unit 2 combustion issues created high CO requiring derate to minimize exceedance. | Trimble | Derate | Coal | 3 | 2013 | 11 | 1.4667 | 0.15866 | 118.5177 | 80.8075 | 81
TC2 | D1 | 182 | 9616 | 2013-11-27 08:25 | 2013-11-27 08:35 | 749 | 795 | 747 | CO stack emissions | FE00Elevated CO required unit derate to avoid an exceedance. | Trimble | Derate | Coal | 3 | 2013 | 11 | 0.16667 | 0.0096436 | 7.2038 | 43.2226 | 43
TC2 | D1 | 183 | 9616 | 2013-11-27 08:35 | 2013-11-27 10:00 | 709 | 795 | 747 | CO stack emissions | FE00Elevated CO required unit derate to avoid an exceedance. | Trimble | Derate | Coal | 3 | 2013 | 11 | 1.4167 | 0.15325 | 114.4774 | 80.8075 | 81
TC2 | D1 | 184 | 9616 | 2013-11-27 10:00 | 2013-11-27 12:00 | 737 | 795 | 747 | CO stack emissions | FE00Elevated CO required unit derate to avoid an exceedance. | Trimble | Derate | Coal | 3 | 2013 | 11 | 2 | 0.14591 | 108.9962 | 54.4981 | 54
TC2 | D1 | 185 | 9616 | 2013-11-27 12:00 | 2013-11-27 13:00 | 686 | 795 | 747 | CO stack emissions | FE00Elevated CO required unit derate to avoid an exceedance. | Trimble | Derate | Coal | 3 | 2013 | 11 | 1 | 0.13711 | 102.4189 | 102.4189 | 102
TC2 | D1 | 186 | 9616 | 2013-11-27 13:00 | 2013-11-29 00:01 | 754 | 795 | 747 | CO stack emissions | FE00Elevated CO required unit derate to avoid an exceedance. | Trimble | Derate | Coal | 3 | 2013 | 11 | 35.0167 | 1.8059 | 1349.0006 | 38.5245 | 39
TC2 | NC | 187 | 1190 | 2013-11-29 00:01 | 2013-11-29 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Planned non curtailing derate to conduct OEM recommended boiler deslag. Unit avai | Trimble | Other | Coal | 3 | 2013 | 11 | 7.9833 | 7.9833 | 5963.55 | 747 | 747
TC2 | NC | 188 | 1190 | 2013-12-01 | 2013-12-01 09:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Planned non curtailing derate to conduct OEM recommended boiler deslag. Unit avai | Trimble | Other | Coal | 3 | 2013 | 12 | 9 | 9 | 6723 | 747 | 747
TC2 | D1 | 189 | 8821 | 2013-12-04 03:12 | 2013-12-04 05:00 | 709 | 795 | 747 | SCR NOx Ammonia tanks | F820An ammonia pump on TC2 tripped. Unit had to be derated in order to avoid a NOx ex | Trimble | Derate | Coal | 3 | 2013 | 12 | 1.8 | 0.19472 | 145.4536 | 80.8075 | 81
TC2 | MO | 190 | 1495 | 2013-12-04 15:09 | 2013-12-07 19:11 | 0 | 795 | 747 | Other air heater fouling (heat pipe | F320TC2 Air heater pressure differential rose to too high of a level and required a ma | Trimble | Maintenance | Coal | 3 | 2013 | 12 | 76.0333 | 76.0333 | 56796.9 | 747 | 747
TC2 | U1 | 191 | 897 | 2013-12-16 03:12 | 2013-12-19 10:17 | 0 | 795 | 747 | Bottom ash rotary (drag chain type) conveyor and motor | F820Submerged scraper conveyor failure and broken components brought the unit offline. | Trimble | Outage | Coal | 3 | 2013 | 12 | 79.0833 | 79.0833 | 59075.25 | 747 | 747
TC2 | U1 | 192 | 1700 | 2013-12-19 13:32 | 2013-12-19 18:26 | 0 | 795 | 747 | Feedwater controls (report local controls --- feedwater pump | F820MFT due to feedwater. The unit was in a swing due to a Turbine control hold and wh | Trimble | Outage | Coal | 3 | 2013 | 12 | 4.9 | 4.9 | 3660.3 | 747 | 747
TC2 | D1 | 193 | 9616 | 2013-12-23 13:36 | 2013-12-23 14:00 | 709 | 795 | 747 | CO stack emissions | FE00High CO emissions required derate to avoid an exceedance on CO. | Trimble | Derate | Coal | 3 | 2013 | 12 | 0.4 | 0.04327 | 32.323 | 80.8075 | 81
TC2 | D1 | 194 | 9616 | 2013-12-23 14:00 | 2013-12-23 17:00 | 659 | 795 | 747 | CO stack emissions | FE00High CO emissions required derate to avoid an exceedance on CO. | Trimble | Derate | Coal | 3 | 2013 | 12 | 3 | 0.51321 | 383.366 | 127.7887 | 128
TC2 | D1 | 195 | 310 | 2013-12-29 07:30 | 2013-12-29 08:00 | 669 | 795 | 747 | Pulverizer mills | F400Mill operational issues and erratic behavior caused unit derate until issues could | Trimble | Derate | Coal | 3 | 2013 | 12 | 0.5 | 0.079245 | 59.1962 | 118.3925 | 118
TC2 | D1 | 196 | 3439 | 2013-12-30 23:00 | 2013-12-31 | 749 | 795 | 747 | HP heater head leaks | F5407A feedwater head leaks required unit derate to isolate heater in order to allow m | Trimble | Derate | Coal | 3 | 2013 | 12 | 1 | 0.057862 | 43.2226 | 43.2226 | 43
TC2 | D1 | 197 | 4250 | 2013-12-31 02:00 | 2013-12-31 04:30 | 802 | 795 | 747 | Other low pressure turbine problems | F660The load drop was due to high steam flow and feedrates from having 7A HP heater ou | Trimble | Derate | Coal | 3 | 2013 | 12 | 2.5 | -0.022013 | -16.4434 | 0 | 0
TC2 | D1 | 198 | 4250 | 2013-12-31 04:30 | 2013-12-31 06:30 | 797 | 795 | 747 | Other low pressure turbine problems | F660The load drop was due to high steam flow and feedrates from having 7A HP heater ou | Trimble | Derate | Coal | 3 | 2013 | 12 | 2 | -0.0050314 | -3.7585 | 0 | 0
TC2 | D1 | 199 | 3439 | 2013-12-31 06:30 | 2014-01-01 | 752 | 795 | 747 | HP heater head leaks | F5407A FWH is out of service due to a heater head leak and unit derate required until | Trimble | Derate | Coal | 3 | 2013 | 12 | 17.5 | 0.94654 | 707.066 | 40.4038 | 40
TC2 | D1 | 1 | 3439 | 2014-01-01 | 2014-01-04 02:00 | 752 | 795 | 747 | HP heater head leaks | F5407A FWH is out of service due to a heater head leak and unit derate required until | Trimble | Derate | Coal | 3 | 2014 | 1 | 74 | 4.0025 | 2989.8792 | 40.4038 | 40
TC2 | NC | 2 | 1190 | 2014-01-04 12:00 | 2014-01-04 17:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate due to boiler OEM recommended deslag, unit available to retu | Trimble | Other | Coal | 3 | 2014 | 1 | 5 | 5 | 3735 | 747 | 747
TC2 | NC | 3 | 1190 | 2014-01-11 | 2014-01-11 05:23 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate at 561MW for boiler OEM recommended weekly deslag. Unit ava | Trimble | Other | Coal | 3 | 2014 | 1 | 5.3833 | 5.3833 | 4021.35 | 747 | 747
TC2 | D1 | 4 | 8000 | 2014-01-11 05:23 | 2014-01-11 19:09 | 610 | 795 | 747 | Chemical feed storage | F060Reactant supply C Limestone conveyor belt broke and issues with running backup con | Trimble | Derate | Coal | 3 | 2014 | 1 | 13.7667 | 3.2036 | 2393.0623 | 173.8302 | 174
TC2 | D1 | 5 | 8000 | 2014-01-11 19:09 | 2014-01-12 02:45 | 480 | 795 | 747 | Chemical feed storage | F060Reactant supply C Limestone conveyor belt broke and issues with running backup con | Trimble | Derate | Coal | 3 | 2014 | 1 | 7.6 | 3.0113 | 2249.4566 | 295.9811 | 296
TC2 | D1 | 6 | 8650 | 2014-01-17 19:30 | 2014-01-17 22:15 | 649 | 795 | 747 | Baghouse systems | FE00The bags in the baghouse are deteriorating and the holes in the bags allow particu | Trimble | Derate | Coal | 3 | 2014 | 1 | 2.75 | 0.50503 | 377.2585 | 137.1849 | 137
TC2 | D1 | 7 | 8650 | 2014-01-18 04:15 | 2014-01-18 05:45 | 649 | 795 | 747 | Baghouse systems | FE00The bags in the baghouse are deteriorating and the holes in the bags allow particu | Trimble | Derate | Coal | 3 | 2014 | 1 | 1.5 | 0.27547 | 205.7774 | 137.1849 | 137
TC2 | D1 | 8 | 9620 | 2014-01-18 11:25 | 2014-01-18 14:00 | 709 | 795 | 747 | Particulate stack emissions (fossil) | FE00High particulate matter readings required derate to avoid an exceedance. | Trimble | Derate | Coal | 3 | 2014 | 1 | 2.5833 | 0.27945 | 208.7528 | 80.8075 | 81
TC2 | D1 | 9 | 9620 | 2014-01-18 17:55 | 2014-01-18 18:10 | 649 | 795 | 747 | Particulate stack emissions (fossil) | FE00The bags in the baghouse are deteriorating and the holes in the bags allow particu | Trimble | Derate | Coal | 3 | 2014 | 1 | 0.25 | 0.045912 | 34.2962 | 137.1849 | 137
TC2 | D1 | 10 | 9620 | 2014-01-18 18:10 | 2014-01-18 19:15 | 729 | 795 | 747 | Particulate stack emissions (fossil) | FE00The bags in the baghouse are deteriorating and the holes in the bags allow particu | Trimble | Derate | Coal | 3 | 2014 | 1 | 1.0833 | 0.089937 | 67.183 | 62.0151 | 62
TC2 | NC | 11 | 1190 | 2014-01-19 | 2014-01-19 06:15 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended deslag. Unit available to | Trimble | Other | Coal | 3 | 2014 | 1 | 6.25 | 6.25 | 4668.75 | 747 | 747
TC2 | D1 | 12 | 9620 | 2014-01-19 10:29 | 2014-01-19 13:00 | 709 | 795 | 747 | Particulate stack emissions (fossil) | FE00High particulate readings required unit derate to avoid an exceedance from emissio | Trimble | Derate | Coal | 3 | 2014 | 1 | 2.5167 | 0.27224 | 203.3657 | 80.8075 | 81
TC2 | D1 | 13 | 9620 | 2014-01-19 17:50 | 2014-01-19 20:15 | 709 | 795 | 747 | Particulate stack emissions (fossil) | FE00High particulate readings required unit derate to avoid an exceedance from emissio | Trimble | Derate | Coal | 3 | 2014 | 1 | 2.4167 | 0.26143 | 195.2849 | 80.8075 | 81
TC2 | D1 | 14 | 9610 | 2014-01-20 01:45 | 2014-01-20 16:30 | 709 | 795 | 747 | NOx stack emissions (fossil) | FE00High NOx readings required unit derate to avoid exceedance. Mill configuration ma | Trimble | Derate | Coal | 3 | 2014 | 1 | 14.75 | 1.5956 | 1191.9113 | 80.8075 | 81
TC2 | NC | 15 | 1190 | 2014-01-26 12:00 | 2014-01-26 18:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate at 561 MW to conduct boiler OEM recommended deslag. Unit av | Trimble | Other | Coal | 3 | 2014 | 1 | 6 | 6 | 4482 | 747 | 747
TC2 | NC | 16 | 1190 | 2014-02-01 00:01 | 2014-02-01 06:15 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate at 550 MW to conduct boiler OEM recommended deslag. Unit av | Trimble | Other | Coal | 3 | 2014 | 2 | 6.2333 | 6.2333 | 4656.3 | 747 | 747
TC2 | D1 | 17 | 310 | 2014-02-02 16:30 | 2014-02-02 19:00 | 679 | 795 | 747 | Pulverizer mills | F400The 2D mill was performing poorly and was taken off-line to investigate. Some mil | Trimble | Derate | Coal | 3 | 2014 | 2 | 2.5 | 0.36478 | 272.4906 | 108.9962 | 109
TC2 | D1 | 18 | 1455 | 2014-02-04 15:45 | 2014-02-04 16:15 | 784 | 795 | 747 | Induced draft fans | F660Derate required on the unit due to ID fan stall alarms. Required derate to avoid | Trimble | Derate | Coal | 3 | 2014 | 2 | 0.5 | 0.0069182 | 5.1679 | 10.3358 | 10
TC2 | PO | 20 | 360 | 2014-02-08 03:21 | 2014-05-26 | 0 | 795 | 747 | Burners | F610TC2 began the planned outage for the replacement of all 30 burners. This effort i | Trimble | Other | Coal | 3 | 2014 | 2 | 2564.65 | 2564.65 | 1915793.55 | 747 | 747
TC2 | PE | 21 | 360 | 2014-05-26 | 2014-05-28 04:59 | 0 | 795 | 747 | Burners | F610Planned outage extension on the burner modifications due to delays in comissioning | Trimble | Other | Coal | 3 | 2014 | 5 | 52.9833 | 52.9833 | 39578.55 | 747 | 747
TC2 | U1 | 22 | 3499 | 2014-05-28 07:35 | 2014-05-28 14:15 | 0 | 795 | 747 | Other feedwater system problems | F820Forced outage due to excessive feedwater flow which caused the unit trip. High fe | Trimble | Outage | Coal | 3 | 2014 | 5 | 6.6667 | 6.6667 | 4980 | 747 | 747
TC2 | U1 | 23 | 4303 | 2014-05-28 20:48 | 2014-05-29 08:55 | 0 | 795 | 747 | Exhaust hood and spray controls | F820TC2 unit trip was from high steam temperature at the turbine due to inadequate sup | Trimble | Outage | Coal | 3 | 2014 | 5 | 12.1167 | 12.1167 | 9051.15 | 747 | 747
TC2 | D4 | 24 | 360 | 2014-05-29 23:15 | 2014-06-01 13:49 | 430 | 795 | 747 | Burners | F790TC2 is being held at 430MW for combustion testing and tuning following the install | Trimble | Derate | Coal | 3 | 2014 | 5 | 62.5667 | 28.7256 | 21458.0057 | 342.9623 | 343
TC2 | U1 | 25 | 3853 | 2014-06-01 13:49 | 2014-06-02 03:20 | 0 | 795 | 747 | Instrument air dryers | F820TC2 tripped offline when the instrument air dryer de-pressurized. | Trimble | Outage | Coal | 3 | 2014 | 6 | 13.5167 | 13.5167 | 10096.95 | 747 | 747
TC2 | SF | 26 | 1455 | 2014-06-02 03:20 | 2014-06-02 20:00 | 0 | 795 | 747 | Induced draft fans | F850During restart, following the forced outage, the 2A ID Fan OB vibration came in al | Trimble | Outage | Coal | 3 | 2014 | 6 | 16.6667 | 16.6667 | 12450 | 747 | 747
TC2 | D1 | 27 | 3441 | 2014-06-03 06:00 | 2014-06-03 07:00 | 724 | 795 | 747 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F520TC2 was derated to 724MW due to the 7A feedwater heater level transmitter going ba | Trimble | Derate | Coal | 3 | 2014 | 6 | 1 | 0.089308 | 66.7132 | 66.7132 | 67
TC2 | D4 | 28 | 1710 | 2014-06-03 13:05 | 2014-06-04 | 774 | 795 | 747 | Combustion/steam condition controls (report local controls --- burners | F790Planned derate to conduct boiler tuning following installation of 30 new burners o | Trimble | Derate | Coal | 3 | 2014 | 6 | 10.9167 | 0.28836 | 215.4085 | 19.7321 | 20
TC2 | NC | 29 | 1190 | 2014-06-07 22:00 | 2014-06-08 09:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for the boiler OEM recommended deslag. Unit was available t | Trimble | Other | Coal | 3 | 2014 | 6 | 11.5 | 11.5 | 8590.5 | 747 | 747
TC2 | D1 | 30 | 9610 | 2014-06-09 19:00 | 2014-06-09 20:00 | 681 | 795 | 747 | NOx stack emissions (fossil) | FE00During a tank swap while free flowing ammonia to the TC2 SCR, a check valve closed | Trimble | Derate | Coal | 3 | 2014 | 6 | 1 | 0.1434 | 107.117 | 107.117 | 107
TC2 | D1 | 31 | 1100 | 2014-06-10 09:00 | 2014-06-10 13:15 | 650 | 795 | 747 | Waterwall (Furnace wall) B | FS00TC2 was experiencing heavy slagging and required a unit derate to allow for some u | Trimble | Derate | Coal | 3 | 2014 | 6 | 4.25 | 0.77516 | 579.0425 | 136.2453 | 136
TC2 | D1 | 32 | 380 | 2014-06-10 13:15 | 2014-06-10 16:00 | 659 | 795 | 747 | Light-off (igniter) systems (including fuel supply) | F460Unplanned derate due to loss of B mill oil gun when trying to put the B mill in se | Trimble | Derate | Coal | 3 | 2014 | 6 | 2.75 | 0.47044 | 351.4189 | 127.7887 | 128
TC2 | D1 | 33 | 9616 | 2014-06-14 03:36 | 2014-06-15 00:01 | 681 | 795 | 747 | CO stack emissions | FE00Derate required to try to avoid environmental exceedences due to high CO during co | Trimble | Derate | Coal | 3 | 2014 | 6 | 20.4167 | 2.9277 | 2186.9717 | 107.117 | 107
TC2 | NC | 34 | 1190 | 2014-06-15 00:01 | 2014-06-15 09:50 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended deslag. Unit available if | Trimble | Other | Coal | 3 | 2014 | 6 | 9.8167 | 9.8167 | 7333.05 | 747 | 747
TC2 | D1 | 35 | 9616 | 2014-06-15 09:50 | 2014-06-15 13:00 | 681 | 795 | 747 | CO stack emissions | FE00Derate required on the unit to avoid environmental exceedance due to high CO emiss | Trimble | Derate | Coal | 3 | 2014 | 6 | 3.1667 | 0.45409 | 339.2038 | 107.117 | 107
TC2 | D1 | 36 | 9616 | 2014-06-15 13:00 | 2014-06-15 18:00 | 659 | 795 | 747 | CO stack emissions | FE00Derate required on the unit to avoid environmental exceedance due to high CO emiss | Trimble | Derate | Coal | 3 | 2014 | 6 | 5 | 0.85535 | 638.9434 | 127.7887 | 128
TC2 | D4 | 37 | 9616 | 2014-06-15 18:00 | 2014-06-16 21:00 | 681 | 795 | 747 | CO stack emissions | FE00Planned unit derate to allow combustion tuning to continue and avoid environmental | Trimble | Derate | Coal | 3 | 2014 | 6 | 27 | 3.8717 | 2892.1585 | 107.117 | 107
TC2 | D1 | 38 | 385 | 2014-06-24 05:30 | 2014-06-24 10:30 | 740 | 795 | 747 | Igniters | F400There were operating issues with the 2D and 2C oil guns as well as the 2D mill tha | Trimble | Derate | Coal | 3 | 2014 | 6 | 5 | 0.34591 | 258.3962 | 51.6792 | 52
TC2 | NC | 39 | 1190 | 2014-06-25 23:00 | 2014-06-26 05:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Planned unit derate to conduct boiler OEM recommended deslag. Unit was available | Trimble | Other | Coal | 3 | 2014 | 6 | 6 | 6 | 4482 | 747 | 747
TC2 | D1 | 40 | 310 | 2014-06-26 05:00 | 2014-06-26 06:15 | 449 | 795 | 747 | Pulverizer mills | F820When attempting to return unit to full load following planned deslag, the B2 fuel | Trimble | Derate | Coal | 3 | 2014 | 6 | 1.25 | 0.54403 | 406.3868 | 325.1094 | 325
TC2 | U1 | 41 | 4299 | 2014-06-29 00:45 | 2014-07-12 04:30 | 0 | 795 | 747 | Other hydraulic system problems | F830The unit was taken offline due to EHC system and turbine valve issues. | Trimble | Outage | Coal | 3 | 2014 | 6 | 315.75 | 315.75 | 235865.25 | 747 | 747
TC2 | SF | 42 | 4309 | 2014-07-12 04:30 | 2014-07-12 17:37 | 0 | 795 | 747 | Other turbine instrument and control problems | F780Turbine temperature control issues caused the reheat temperature to elevate and re | Trimble | Outage | Coal | 3 | 2014 | 7 | 13.1167 | 13.1167 | 9798.15 | 747 | 747
TC2 | SF | 43 | 4309 | 2014-07-12 17:37 | 2014-07-13 07:12 | 0 | 795 | 747 | Other turbine instrument and control problems | F400Startup failure due to Mark VI controls on the turbine valves not working properly | Trimble | Outage | Coal | 3 | 2014 | 7 | 13.5833 | 13.5833 | 10146.75 | 747 | 747
TC2 | D1 | 44 | 9616 | 2014-07-14 03:00 | 2014-07-14 09:00 | 705 | 795 | 747 | CO stack emissions | FE00High CO emissions on the unit required a derate to avoid environmental exceedances | Trimble | Derate | Coal | 3 | 2014 | 7 | 6 | 0.67925 | 507.3962 | 84.566 | 85
TC2 | D1 | 45 | 310 | 2014-07-15 08:00 | 2014-07-15 10:50 | 717 | 795 | 747 | Pulverizer mills | F790Derate to conduct coal mill testing by Doosan. | Trimble | Derate | Coal | 3 | 2014 | 7 | 2.8333 | 0.27799 | 207.6566 | 73.2906 | 73
TC2 | D1 | 46 | 3340 | 2014-07-16 12:00 | 2014-07-18 18:45 | 668 | 795 | 747 | LP heater tube leaks | F540Derate to locate suspected tube leaks on LP FWH 3 and 4. Leaks found at gaskets o | Trimble | Derate | Coal | 3 | 2014 | 7 | 54.75 | 8.7462 | 6533.4311 | 119.3321 | 119
TC2 | NC | 47 | 1190 | 2014-07-19 23:15 | 2014-07-20 09:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended weekly deslag. Unit avail | Trimble | Other | Coal | 3 | 2014 | 7 | 10.25 | 10.25 | 7656.75 | 747 | 747
TC2 | NC | 48 | 4842 | 2014-07-22 11:43 | 2014-07-22 14:06 | 0 | 795 | 747 | Reactive and capability testing | F790TC2 was at full load for VAR testing, non-curtailing event. | Trimble | Other | Coal | 3 | 2014 | 7 | 2.3833 | 2.3833 | 1780.35 | 747 | 747
TC2 | U1 | 49 | 3671 | 2014-07-23 12:22 | 2014-07-25 13:39 | 0 | 795 | 747 | 12kV circuit breakers | F82014kV switch gear failed causing unit trip. The failure was from a plugged AC unit | Trimble | Outage | Coal | 3 | 2014 | 7 | 49.2833 | 49.2833 | 36814.65 | 747 | 747
TC2 | D1 | 50 | 360 | 2014-07-27 01:00 | 2014-07-27 02:00 | 721 | 795 | 747 | Burners | F790To continue testing and tuning of the new burners a mill swap was necessary and re | Trimble | Derate | Coal | 3 | 2014 | 7 | 1 | 0.093082 | 69.5321 | 69.5321 | 70
TC2 | D1 | 51 | 310 | 2014-08-01 16:17 | 2014-08-01 18:15 | 625 | 795 | 747 | Pulverizer mills | F820Derate to 625MW due to loss of B coal mill. | Trimble | Derate | Coal | 3 | 2014 | 8 | 1.9667 | 0.42055 | 314.1472 | 159.7358 | 160
TC2 | NC | 52 | 1190 | 2014-08-02 | 2014-08-03 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to deslag the boiler. Unit was available to return to full | Trimble | Other | Coal | 3 | 2014 | 8 | 32 | 32 | 23904 | 747 | 747
TC2 | D1 | 53 | 310 | 2014-08-04 10:50 | 2014-08-04 11:50 | 620 | 795 | 747 | Pulverizer mills | F820Derate to 620MW due to loss of B coal mill. | Trimble | Derate | Coal | 3 | 2014 | 8 | 1 | 0.22013 | 164.434 | 164.434 | 164
TC2 | NC | 54 | 1190 | 2014-08-10 | 2014-08-10 06:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to 449MW to conduct boiler OEM recommended deslag of the boi | Trimble | Other | Coal | 3 | 2014 | 8 | 6 | 6 | 4482 | 747 | 747
TC2 | U1 | 55 | 4750 | 2014-08-11 00:48 | 2014-08-12 13:15 | 0 | 795 | 747 | Other generator controls and metering problems | F820During control valve testing, the master trip block in the EHC system had a soleno | Trimble | Outage | Coal | 3 | 2014 | 8 | 36.45 | 36.45 | 27228.15 | 747 | 747
TC2 | NC | 56 | 1190 | 2014-08-17 | 2014-08-17 08:45 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended deslag. Unit available to | Trimble | Other | Coal | 3 | 2014 | 8 | 8.75 | 8.75 | 6536.25 | 747 | 747
TC2 | NC | 57 | 1190 | 2014-08-24 | 2014-08-24 07:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended deslag. Unit available to | Trimble | Other | Coal | 3 | 2014 | 8 | 7.5 | 7.5 | 5602.5 | 747 | 747
TC2 | NC | 58 | 1190 | 2014-08-31 00:02 | 2014-08-31 10:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended deslag. Unit available to | Trimble | Other | Coal | 3 | 2014 | 8 | 9.9667 | 9.9667 | 7445.1 | 747 | 747
TC2 | D1 | 59 | 9600 | 2014-09-03 22:00 | 2014-09-04 12:30 | 681 | 795 | 747 | SO2 stack emissions (fossil) | FE00SO2 emissions were increasing and potential exceedance was avoided by derating the | Trimble | Derate | Coal | 3 | 2014 | 9 | 14.5 | 2.0792 | 1553.1962 | 107.117 | 107
TC2 | NC | 60 | 1190 | 2014-09-07 | 2014-09-07 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct OEM recommended boiler deslag. Unit was availabl | Trimble | Other | Coal | 3 | 2014 | 9 | 8 | 8 | 5976 | 747 | 747
TC2 | NC | 61 | 360 | 2014-09-09 00:01 | 2014-09-09 05:00 | 0 | 795 | 747 | Burners | F790During the capability testing of the new set of burners, a ramp rate test was sche | Trimble | Other | Coal | 3 | 2014 | 9 | 4.9833 | 4.9833 | 3722.55 | 747 | 747
TC2 | D1 | 62 | 250 | 2014-09-12 00:30 | 2014-09-12 02:30 | 650 | 795 | 747 | Pulverizer feeders | F8202C Mill feeder trip due to discharge valve limit switch. Mill clearout conducted | Trimble | Derate | Coal | 3 | 2014 | 9 | 2 | 0.36478 | 272.4906 | 136.2453 | 136
TC2 | NC | 63 | 1190 | 2014-09-14 | 2014-09-14 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended deslag on the unit. Unit | Trimble | Other | Coal | 3 | 2014 | 9 | 8 | 8 | 5976 | 747 | 747
TC2 | U1 | 64 | 1030 | 2014-09-14 13:10 | 2014-09-19 10:33 | 0 | 795 | 747 | Boiler screen | F540Unit on forced outage due to tube leak. Screen tube failure lead to 7 other tube | Trimble | Outage | Coal | 3 | 2014 | 9 | 117.3833 | 117.3833 | 87685.35 | 747 | 747
TC2 | NC | 65 | 1990 | 2014-09-21 02:00 | 2014-09-21 06:45 | 0 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Non-curtailing, variable derate to conduct unit ramp testing for new capability te | Trimble | Other | Coal | 3 | 2014 | 9 | 4.75 | 4.75 | 3548.25 | 747 | 747
TC2 | D1 | 66 | 3431 | 2014-09-22 | 2014-09-22 09:50 | 430 | 795 | 747 | Other feedwater valves | F540Derate on the unit due to a packing leak on a feedwater bypass valve. | Trimble | Derate | Coal | 3 | 2014 | 9 | 9.8333 | 4.5147 | 3372.4623 | 342.9623 | 343
TC2 | U1 | 67 | 3431 | 2014-09-22 09:50 | 2014-09-23 02:00 | 0 | 795 | 747 | Other feedwater valves | F540Packing leak on feedwater start-up bypass valve required unit to be taken off-line | Trimble | Outage | Coal | 3 | 2014 | 9 | 16.1667 | 16.1667 | 12076.5 | 747 | 747
TC2 | NC | 68 | 1190 | 2014-09-28 | 2014-09-28 09:16 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended unit deslag. The unit was | Trimble | Other | Coal | 3 | 2014 | 9 | 9.2667 | 9.2667 | 6922.2 | 747 | 747
TC2 | MO | 69 | 775 | 2014-10-04 03:38 | 2014-10-06 18:54 | 0 | 795 | 747 | Economizer piping | F540TC2 was taken offline for a maintenance outage to repair a leak in the economizer | Trimble | Maintenance | Coal | 3 | 2014 | 10 | 63.2667 | 63.2667 | 47260.2 | 747 | 747
TC2 | D1 | 70 | 335 | 2014-10-07 10:02 | 2014-10-07 13:00 | 669 | 795 | 747 | Pulverizer lube oil system | F540The unit was derated to 669MW due to a lube oil leak on the 2B mill. Additionally | Trimble | Derate | Coal | 3 | 2014 | 10 | 2.9667 | 0.47019 | 351.2309 | 118.3925 | 118
TC2 | D1 | 71 | 1400 | 2014-10-07 16:45 | 2014-10-07 18:30 | 779 | 795 | 747 | Forced draft fans | F400During a mill swap air flow issues arose so to avoid a fan stall, operations put a | Trimble | Derate | Coal | 3 | 2014 | 10 | 1.75 | 0.03522 | 26.3094 | 15.034 | 15
TC2 | D1 | 72 | 310 | 2014-10-08 10:15 | 2014-10-08 17:54 | 669 | 795 | 747 | Pulverizer mills | FR00TC2 was derated to 669MW due to a fire in the 2E coal mill. Additionally, a leak | Trimble | Derate | Coal | 3 | 2014 | 10 | 7.65 | 1.2125 | 905.7023 | 118.3925 | 118
TC2 | NC | 73 | 1190 | 2014-10-12 00:01 | 2014-10-12 10:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended unit deslag. Unit was ava | Trimble | Other | Coal | 3 | 2014 | 10 | 9.9833 | 9.9833 | 7457.55 | 747 | 747
TC2 | NC | 74 | 4490 | 2014-10-16 09:00 | 2014-10-16 10:30 | 0 | 795 | 747 | Turbine performance testing (use code 9999 for total unit performance testing) | F790Non-curtailing derate to conduct a turbine follow ramp test on the unit. Unit was | Trimble | Other | Coal | 3 | 2014 | 10 | 1.5 | 1.5 | 1120.5 | 747 | 747
TC2 | NC | 75 | 1190 | 2014-10-19 | 2014-10-19 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler deslag. Unit was available for full load | Trimble | Other | Coal | 3 | 2014 | 10 | 8 | 8 | 5976 | 747 | 747
TC2 | NC | 76 | 4267 | 2014-10-20 | 2014-10-20 06:00 | 0 | 795 | 747 | Control valve testing | F790Non-curtailing derate to conduct turbine bypass control valve testing. Unit was a | Trimble | Other | Coal | 3 | 2014 | 10 | 6 | 6 | 4482 | 747 | 747
TC2 | PD | 77 | 1990 | 2014-10-21 | 2014-10-21 06:00 | 784 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct unit performance testing following upgrade of combustion | Trimble | Derate | Coal | 3 | 2014 | 10 | 6 | 0.083019 | 62.0151 | 10.3358 | 10
TC2 | D1 | 78 | 1990 | 2014-10-22 08:30 | 2014-10-22 11:15 | 777 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Derate to conduct unit performance testing following upgrade of combustion system. | Trimble | Derate | Coal | 3 | 2014 | 10 | 2.75 | 0.062264 | 46.5113 | 16.9132 | 17
TC2 | D1 | 79 | 1990 | 2014-10-22 11:15 | 2014-10-22 13:45 | 787 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Derate to conduct unit performance testing following upgrade of combustion system. | Trimble | Derate | Coal | 3 | 2014 | 10 | 2.5 | 0.025157 | 18.7925 | 7.517 | 8
TC2 | D1 | 80 | 1990 | 2014-10-22 13:45 | 2014-10-22 17:00 | 792 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Derate to conduct unit performance testing following upgrade of combustion system. | Trimble | Derate | Coal | 3 | 2014 | 10 | 3.25 | 0.012264 | 9.1613 | 2.8189 | 3
TC2 | PD | 81 | 1990 | 2014-10-23 09:30 | 2014-10-23 17:45 | 792 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to allow performance testing of new combustion system by Doosan. | Trimble | Derate | Coal | 3 | 2014 | 10 | 8.25 | 0.031132 | 23.2557 | 2.8189 | 3
TC2 | D1 | 82 | 1990 | 2014-10-24 10:00 | 2014-10-24 18:00 | 792 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to allow performance testing of new combustion system by Doosan. | Trimble | Derate | Coal | 3 | 2014 | 10 | 8 | 0.030189 | 22.5509 | 2.8189 | 3
TC2 | NC | 83 | 1190 | 2014-10-26 00:01 | 2014-10-26 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended deslag. Unit was availabl | Trimble | Other | Coal | 3 | 2014 | 10 | 7.9833 | 7.9833 | 5963.55 | 747 | 747
TC2 | PD | 84 | 1990 | 2014-10-29 13:00 | 2014-10-29 15:00 | 762 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Unit was on a planned, variable derate to conduct ramp testing on the unit for the | Trimble | Derate | Coal | 3 | 2014 | 10 | 2 | 0.083019 | 62.0151 | 31.0075 | 31
TC2 | PD | 85 | 1990 | 2014-10-30 14:00 | 2014-10-30 15:00 | 660 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 10 | 1 | 0.16981 | 126.8491 | 126.8491 | 127
TC2 | PD | 86 | 1990 | 2014-10-31 10:00 | 2014-10-31 11:00 | 695 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 10 | 1 | 0.12579 | 93.9623 | 93.9623 | 94
TC2 | PD | 87 | 1990 | 2014-10-31 12:30 | 2014-10-31 13:30 | 695 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 10 | 1 | 0.12579 | 93.9623 | 93.9623 | 94
TC2 | PD | 88 | 1990 | 2014-10-31 15:00 | 2014-10-31 16:26 | 695 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 10 | 1.4333 | 0.18029 | 134.6792 | 93.9623 | 94
TC2 | PD | 89 | 1990 | 2014-11-01 11:00 | 2014-11-01 12:00 | 658 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 11 | 1 | 0.17233 | 128.7283 | 128.7283 | 129
TC2 | PD | 90 | 1990 | 2014-11-01 12:00 | 2014-11-01 13:00 | 480 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 11 | 1 | 0.39623 | 295.9811 | 295.9811 | 296
TC2 | PD | 91 | 1990 | 2014-11-01 13:00 | 2014-11-01 14:00 | 658 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 11 | 1 | 0.17233 | 128.7283 | 128.7283 | 129
TC2 | PD | 92 | 1990 | 2014-11-01 14:00 | 2014-11-01 15:00 | 480 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 11 | 1 | 0.39623 | 295.9811 | 295.9811 | 296
TC2 | PD | 93 | 1990 | 2014-11-01 15:00 | 2014-11-01 16:00 | 658 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 11 | 1 | 0.17233 | 128.7283 | 128.7283 | 129
TC2 | PD | 94 | 1990 | 2014-11-01 16:00 | 2014-11-01 17:00 | 480 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 11 | 1 | 0.39623 | 295.9811 | 295.9811 | 296
TC2 | PD | 95 | 1990 | 2014-11-01 17:00 | 2014-11-01 18:00 | 650 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 11 | 1 | 0.18239 | 136.2453 | 136.2453 | 136
TC2 | PD | 96 | 1990 | 2014-11-02 09:15 | 2014-11-02 12:00 | 658 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 11 | 2.75 | 0.4739 | 354.0028 | 128.7283 | 129
TC2 | PD | 97 | 1990 | 2014-11-02 12:00 | 2014-11-02 13:00 | 499 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 11 | 1 | 0.37233 | 278.1283 | 278.1283 | 278
TC2 | PD | 98 | 1990 | 2014-11-02 13:00 | 2014-11-02 15:00 | 658 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 11 | 2 | 0.34465 | 257.4566 | 128.7283 | 129
TC2 | PD | 99 | 1990 | 2014-11-02 16:00 | 2014-11-02 17:00 | 499 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp testing on the unit following the boiler combustion | Trimble | Derate | Coal | 3 | 2014 | 11 | 1 | 0.37233 | 278.1283 | 278.1283 | 278
TC2 | PD | 100 | 1990 | 2014-11-03 10:00 | 2014-11-03 11:00 | 650 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Conducted planned ramp test on the unit. | Trimble | Derate | Coal | 3 | 2014 | 11 | 1 | 0.18239 | 136.2453 | 136.2453 | 136
TC2 | PD | 101 | 1990 | 2014-11-03 13:00 | 2014-11-03 14:00 | 650 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Conducted planned ramp test on the unit. | Trimble | Derate | Coal | 3 | 2014 | 11 | 1 | 0.18239 | 136.2453 | 136.2453 | 136
TC2 | PD | 102 | 1990 | 2014-11-03 15:00 | 2014-11-03 16:00 | 650 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Conducted planned ramp test on the unit. | Trimble | Derate | Coal | 3 | 2014 | 11 | 1 | 0.18239 | 136.2453 | 136.2453 | 136
TC2 | NC | 103 | 1190 | 2014-11-09 | 2014-11-09 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing unit derate to conduct boiler OEM recommended unit deslag. Unit wa | Trimble | Other | Coal | 3 | 2014 | 11 | 8 | 8 | 5976 | 747 | 747
TC2 | D1 | 104 | 370 | 2014-11-09 08:00 | 2014-11-09 09:50 | 650 | 795 | 747 | Burner instruments and controls (except light-off) | F400Issues with the C-row oil guns caused a unit derate until issues could be resolved | Trimble | Derate | Coal | 3 | 2014 | 11 | 1.8333 | 0.33438 | 249.783 | 136.2453 | 136
TC2 | NC | 105 | 1190 | 2014-11-11 23:00 | 2014-11-12 05:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler deslag. Unit was available to return to fu | Trimble | Other | Coal | 3 | 2014 | 11 | 6 | 6 | 4482 | 747 | 747
TC2 | NC | 106 | 1190 | 2014-11-16 | 2014-11-16 06:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler deslag. Unit was available to return to fu | Trimble | Other | Coal | 3 | 2014 | 11 | 6 | 6 | 4482 | 747 | 747
TC2 | NC | 107 | 1190 | 2014-11-23 00:01 | 2014-11-23 06:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate on the unit to conduct boiler deslag. Unit available to ret | Trimble | Other | Coal | 3 | 2014 | 11 | 5.9833 | 5.9833 | 4469.55 | 747 | 747
TC2 | D4 | 108 | 1190 | 2014-11-30 00:01 | 2014-11-30 06:24 | 400 | 795 | 747 | Other tube slagging or fouling | FS00Derate to conduct boiler deslag. Unit was available to return to full load if req | Trimble | Derate | Coal | 3 | 2014 | 11 | 6.3833 | 3.1716 | 2369.1802 | 371.1509 | 371
TC2 | D1 | 109 | 385 | 2014-11-30 06:34 | 2014-11-30 08:00 | 659 | 795 | 747 | Igniters | F830Issues with the C1 oil gun during start-up caused a unit derate until an alternate | Trimble | Derate | Coal | 3 | 2014 | 11 | 1.4333 | 0.2452 | 183.1638 | 127.7887 | 128
TC2 | D4 | 110 | 3439 | 2014-12-06 | 2014-12-06 04:54 | 749 | 795 | 747 | HP heater head leaks | F540Planned derate to repair head leak on 8A FW heater. | Trimble | Derate | Coal | 3 | 2014 | 12 | 4.9 | 0.28352 | 211.7909 | 43.2226 | 43
TC2 | U1 | 111 | 3441 | 2014-12-06 04:54 | 2014-12-07 16:55 | 0 | 795 | 747 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F540While attempting to isolate the 8A heater for repair, the 8A heater bypass valve p | Trimble | Outage | Coal | 3 | 2014 | 12 | 36.0167 | 36.0167 | 26904.45 | 747 | 747
TC2 | SF | 112 | 250 | 2014-12-07 16:55 | 2014-12-07 17:18 | 0 | 795 | 747 | Pulverizer feeders | F0602E Coal Mill clean out conveyor issues. | Trimble | Outage | Coal | 3 | 2014 | 12 | 0.38333 | 0.38333 | 286.35 | 747 | 747
TC2 | SF | 113 | 3499 | 2014-12-07 17:18 | 2014-12-07 23:47 | 0 | 795 | 747 | Other feedwater system problems | F660Feedwater flow limit during mill swap. | Trimble | Outage | Coal | 3 | 2014 | 12 | 6.4833 | 6.4833 | 4843.05 | 747 | 747
TC2 | D4 | 114 | 1190 | 2014-12-13 23:59 | 2014-12-14 07:00 | 434 | 795 | 747 | Other tube slagging or fouling | FS00Unit derate to conduct boiler OEM recommended unit deslag. Unit was available to | Trimble | Derate | Coal | 3 | 2014 | 12 | 7.0167 | 3.1862 | 2380.0798 | 339.2038 | 339
TC2 | U1 | 115 | 1035 | 2014-12-17 13:10 | 2014-12-20 16:29 | 0 | 795 | 747 | Platen superheater | F540Unit came offline due to a boiler tube leak on the Superheater Platen tube, Elemen | Trimble | Outage | Coal | 3 | 2014 | 12 | 75.3167 | 75.3167 | 56261.55 | 747 | 747
TC2 | D4 | 1 | 1990 | 2015-01-03 | 2015-01-03 02:00 | 709 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Planned derate to conduct ramp test in preperation for AGC mode. | Trimble | Derate | Coal | 3 | 2015 | 1 | 2 | 0.21635 | 161.6151 | 80.8075 | 81
TC2 | NC | 2 | 1190 | 2015-01-03 02:00 | 2015-01-03 10:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing unit derate to conduct boiler OEM recommended unit deslag. Unit wa | Trimble | Other | Coal | 3 | 2015 | 1 | 8 | 8 | 5976 | 747 | 747
TC2 | NC | 3 | 1190 | 2015-01-11 11:00 | 2015-01-11 17:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended deslag. Unit was availabl | Trimble | Other | Coal | 3 | 2015 | 1 | 6 | 6 | 4482 | 747 | 747
TC2 | D1 | 4 | 4269 | 2015-01-12 08:30 | 2015-01-12 14:00 | 799 | 795 | 747 | Other turbine valves | F540Unit was derated due to HP turbine bypass valve leak through. Due to HP turbine b | Trimble | Derate | Coal | 3 | 2015 | 1 | 5.5 | -0.027673 | -20.6717 | 0 | 0
TC2 | D1 | 5 | 4269 | 2015-01-12 14:00 | 2015-01-12 19:00 | 549 | 795 | 747 | Other turbine valves | F540Due to the HP turbine bypass valve leak through, the unit required a further derat | Trimble | Derate | Coal | 3 | 2015 | 1 | 5 | 1.5472 | 1155.7358 | 231.1472 | 231
TC2 | D1 | 6 | 4269 | 2015-01-12 19:00 | 2015-03-04 16:00 | 789 | 795 | 747 | Other turbine valves | F540Unit was derated 20MW due to HP turbine bypass valve leak through. This required | Trimble | Derate | Coal | 3 | 2015 | 1 | 1221 | 9.2151 | 6883.6755 | 5.6377 | 6
TC2 | NC | 7 | 1190 | 2015-01-17 22:00 | 2015-01-18 04:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended deslag of the unit. Load | Trimble | Other | Coal | 3 | 2015 | 1 | 6 | 6 | 4482 | 747 | 747
TC2 | NC | 8 | 1190 | 2015-01-24 23:59 | 2015-01-25 07:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended boiler deslag. Unit was a | Trimble | Other | Coal | 3 | 2015 | 1 | 7.0167 | 7.0167 | 5241.45 | 747 | 747
TC2 | NC | 9 | 1190 | 2015-02-01 | 2015-02-01 07:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conducte boiler OEM recommended weekly deslag. Unit was | Trimble | Other | Coal | 3 | 2015 | 2 | 7 | 7 | 5229 | 747 | 747
TC2 | D4 | 10 | 1190 | 2015-02-08 | 2015-02-08 07:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler OEM recommended weekly deslag. Unit was a | Trimble | Derate | Coal | 3 | 2015 | 2 | 7 | 3.0465 | 2275.766 | 325.1094 | 325
TC2 | NC | 11 | 1190 | 2015-02-22 00:01 | 2015-02-22 07:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler deslag. Unit was available to return to f | Trimble | Other | Coal | 3 | 2015 | 2 | 6.9833 | 6.9833 | 5216.55 | 747 | 747
TC2 | NC | 12 | 1190 | 2015-03-01 00:01 | 2015-03-01 07:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler deslag. Unit was available to return to f | Trimble | Other | Coal | 3 | 2015 | 3 | 6.9833 | 6.9833 | 5216.55 | 747 | 747
TC2 | D4 | 13 | 1980 | 2015-03-04 | 2015-03-04 02:03 | 749 | 795 | 747 | Boiler safety valve test | F790Planned derate to conduct safety valve test in preparation of upcoming planned uni | Trimble | Derate | Coal | 3 | 2015 | 3 | 2.05 | 0.11862 | 88.6064 | 43.2226 | 43
TC2 | D1 | 14 | 550 | 2015-03-04 16:00 | 2015-03-08 07:00 | 777 | 795 | 747 | Reheat steam relief/safety valves | F690Unit is derated due to reheat safety valve that will not lift, which was discovere | Trimble | Derate | Coal | 3 | 2015 | 3 | 87 | 1.9698 | 1471.4491 | 16.9132 | 17
TC2 | NC | 15 | 1190 | 2015-03-08 | 2015-03-08 07:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct weekly boiler deslag. Unit was available to retu | Trimble | Other | Coal | 3 | 2015 | 3 | 7 | 7 | 5229 | 747 | 747
TC2 | D1 | 16 | 550 | 2015-03-08 07:00 | 2015-03-14 19:40 | 777 | 795 | 747 | Reheat steam relief/safety valves | F690Unit is derated due to reheat safety valve that will not lift, which was discovere | Trimble | Derate | Coal | 3 | 2015 | 3 | 156.6667 | 3.5472 | 2649.7358 | 16.9132 | 17
TC2 | D1 | 17 | 310 | 2015-03-14 19:40 | 2015-03-14 20:00 | 650 | 795 | 747 | Pulverizer mills | F820The unit was derated when the 2C coal mill tripped from feeder issues. The 2E mil | Trimble | Derate | Coal | 3 | 2015 | 3 | 0.33333 | 0.060797 | 45.4151 | 136.2453 | 136
TC2 | D1 | 18 | 310 | 2015-03-14 20:00 | 2015-03-14 22:45 | 630 | 795 | 747 | Pulverizer mills | F820The unit was derated when the 2C coal mill tripped from feeder issues. The 2E mil | Trimble | Derate | Coal | 3 | 2015 | 3 | 2.75 | 0.57075 | 426.3538 | 155.0377 | 155
TC2 | D1 | 19 | 550 | 2015-03-14 22:45 | 2015-03-15 07:15 | 777 | 795 | 747 | Reheat steam relief/safety valves | F690Unit is derated due to reheat safety valve that will not lift, which was discovere | Trimble | Derate | Coal | 3 | 2015 | 3 | 8.5 | 0.19245 | 143.7623 | 16.9132 | 17
TC2 | NC | 20 | 1190 | 2015-03-15 | 2015-03-15 07:15 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler deslag. Unit was available to return to f | Trimble | Other | Coal | 3 | 2015 | 3 | 7.25 | 7.25 | 5415.75 | 747 | 747
TC2 | D1 | 21 | 550 | 2015-03-15 07:15 | 2015-03-22 07:40 | 777 | 795 | 747 | Reheat steam relief/safety valves | F690Unit is derated due to reheat safety valve that will not lift, which was discovere | Trimble | Derate | Coal | 3 | 2015 | 3 | 168.4167 | 3.8132 | 2848.466 | 16.9132 | 17
TC2 | NC | 22 | 1190 | 2015-03-22 | 2015-03-22 07:40 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler deslag. Unit was available to return to f | Trimble | Other | Coal | 3 | 2015 | 3 | 7.6667 | 7.6667 | 5727 | 747 | 747
TC2 | D1 | 23 | 550 | 2015-03-22 07:40 | 2015-03-28 03:04 | 777 | 795 | 747 | Reheat steam relief/safety valves | F690Unit is derated due to reheat safety valve that will not lift, which was discovere | Trimble | Derate | Coal | 3 | 2015 | 3 | 139.4 | 3.1562 | 2357.7011 | 16.9132 | 17
TC2 | PO | 24 | 1812 | 2015-03-28 03:04 | 2015-04-20 | 0 | 795 | 747 | Boiler Inspections - scheduled or routine | F590Planned outage for boiler inspection and necessary maintenance of the waterwall Am | Trimble | Other | Coal | 3 | 2015 | 3 | 548.9333 | 548.9333 | 410053.2 | 747 | 747
TC2 | PE | 25 | 385 | 2015-04-20 | 2015-04-20 16:43 | 0 | 795 | 747 | Igniters | F590Planned outage extension due to igniter issues. | Trimble | Other | Coal | 3 | 2015 | 4 | 16.7167 | 16.7167 | 12487.35 | 747 | 747
TC2 | D1 | 26 | 3412 | 2015-04-20 16:43 | 2015-04-20 17:45 | 390 | 795 | 747 | Feedwater pump drive - steam turbine | F570The 2A and 2B TDBFPs had lube oil trip off while still on turning gear, and the TD | Trimble | Derate | Coal | 3 | 2015 | 4 | 1.0333 | 0.52642 | 393.2321 | 380.5472 | 381
TC2 | U1 | 27 | 3979 | 2015-04-20 17:45 | 2015-04-20 23:17 | 0 | 795 | 747 | Other DCS problems | F400DCS control issues required a manual unit MFT. MW setpoint increased to 180 and w | Trimble | Outage | Coal | 3 | 2015 | 4 | 5.5333 | 5.5333 | 4133.4 | 747 | 747
TC2 | D1 | 28 | 3412 | 2015-04-20 23:17 | 2015-04-21 07:10 | 390 | 795 | 747 | Feedwater pump drive - steam turbine | F570The 2A and 2B TDBFPs had lube oil trip off while still on turning gear, and the TD | Trimble | Derate | Coal | 3 | 2015 | 4 | 7.8833 | 4.016 | 2999.9802 | 380.5472 | 381
TC2 | D1 | 29 | 3412 | 2015-04-21 07:10 | 2015-05-02 19:30 | 400 | 795 | 747 | Feedwater pump drive - steam turbine | F570Unit was able to be raised by 10 MW by increasing MDBFP performance. The 2A and 2 | Trimble | Derate | Coal | 3 | 2015 | 4 | 276.3333 | 137.2977 | 102561.3774 | 371.1509 | 371
TC2 | D1 | 30 | 3412 | 2015-05-02 19:30 | 2015-05-03 00:30 | 469 | 795 | 747 | Feedwater pump drive - steam turbine | F570Continued issues with TDBFP. | Trimble | Derate | Coal | 3 | 2015 | 5 | 5 | 2.0503 | 1531.5849 | 306.317 | 306
TC2 | D1 | 31 | 3412 | 2015-05-03 00:30 | 2015-05-03 02:40 | 761 | 795 | 747 | Feedwater pump drive - steam turbine | F570Continued issues with 2A TDBFP. | Trimble | Derate | Coal | 3 | 2015 | 5 | 2.1667 | 0.092662 | 69.2189 | 31.9472 | 32
TC2 | U1 | 32 | 4261 | 2015-05-03 02:40 | 2015-05-04 12:25 | 0 | 795 | 747 | Control valves | F540Cold Reheat valve CRH 2-CR-CV-054A has a gasket leak | Trimble | Outage | Coal | 3 | 2015 | 5 | 33.75 | 33.75 | 25211.25 | 747 | 747
TC2 | D1 | 33 | 3412 | 2015-05-04 20:00 | 2015-05-05 09:30 | 775 | 795 | 747 | Feedwater pump drive - steam turbine | F820Continued issues with 2A TDBFP. | Trimble | Derate | Coal | 3 | 2015 | 5 | 13.5 | 0.33962 | 253.6981 | 18.7925 | 19
TC2 | D1 | 34 | 3412 | 2015-05-05 09:30 | 2015-05-05 22:30 | 781 | 795 | 747 | Feedwater pump drive - steam turbine | F820 Due to 2A TDBFP issues, MDBFP's must be started. | Trimble | Derate | Coal | 3 | 2015 | 5 | 13 | 0.22893 | 171.0113 | 13.1547 | 13
TC2 | D4 | 35 | 3414 | 2015-05-05 22:30 | 2015-05-05 23:45 | 449 | 795 | 747 | Feedwater pump local controls | F610Planned derate for logic changes in the 2B TDBFP controls. | Trimble | Derate | Coal | 3 | 2015 | 5 | 1.25 | 0.54403 | 406.3868 | 325.1094 | 325
TC2 | D4 | 36 | 3408 | 2015-05-05 23:45 | 2015-05-06 06:26 | 409 | 795 | 747 | Feedwater pump drive - local controls | F610Continued work on the 2B TDBFP logic changes. | Trimble | Derate | Coal | 3 | 2015 | 5 | 6.6833 | 3.245 | 2424.0072 | 362.6943 | 363
TC2 | D1 | 37 | 3456 | 2015-05-06 06:26 | 2015-05-06 23:00 | 781 | 795 | 747 | Feedwater Booster Pump Drive - Steam Turbine | F820TC2 was able to get back to a Gross Capacity of 781 MW but was unable to meet Net | Trimble | Derate | Coal | 3 | 2015 | 5 | 16.5667 | 0.29174 | 217.9298 | 13.1547 | 13
TC2 | D4 | 38 | 3414 | 2015-05-06 23:00 | 2015-05-07 01:44 | 409 | 795 | 747 | Feedwater pump local controls | F610Control logic maintenance on 2B TDBFP. | Trimble | Derate | Coal | 3 | 2015 | 5 | 2.7333 | 1.3271 | 991.3645 | 362.6943 | 363
TC2 | U1 | 39 | 3416 | 2015-05-07 01:44 | 2015-05-07 07:03 | 0 | 795 | 747 | Other feedwater pump problems | F820While switching operation from MDBFP's to TDBFP's, the TDBFP's are designed to ram | Trimble | Outage | Coal | 3 | 2015 | 5 | 5.3167 | 5.3167 | 3971.55 | 747 | 747
TC2 | D1 | 40 | 3412 | 2015-05-07 07:03 | 2015-05-11 12:20 | 781 | 795 | 747 | Feedwater pump drive - steam turbine | F820 Gross Capacity is able to be met, but Net Capacity is reduced be | Trimble | Derate | Coal | 3 | 2015 | 5 | 101.2833 | 1.7836 | 1332.3536 | 13.1547 | 13
TC2 | D1 | 41 | 3412 | 2015-05-11 12:20 | 2015-05-11 18:38 | 771 | 795 | 747 | Feedwater pump drive - steam turbine | F8202A TDBFP out of service due to controls up-grade and testing so load reduced while | Trimble | Derate | Coal | 3 | 2015 | 5 | 6.3 | 0.19019 | 142.0709 | 22.5509 | 23
TC2 | D1 | 42 | 3440 | 2015-05-11 18:38 | 2015-05-11 19:44 | 670 | 795 | 747 | High pressure heater tube leaks | F540The 6A HP Feedwater heater had tube leaks and unit required derate while heater is | Trimble | Derate | Coal | 3 | 2015 | 5 | 1.1 | 0.17296 | 129.1981 | 117.4528 | 117
TC2 | D1 | 43 | 3440 | 2015-05-11 19:44 | 2015-05-11 21:30 | 560 | 795 | 747 | High pressure heater tube leaks | F540The 6A HP Feedwater heater had tube leaks and unit required derate while heater is | Trimble | Derate | Coal | 3 | 2015 | 5 | 1.7667 | 0.52222 | 390.1 | 220.8113 | 221
TC2 | D1 | 44 | 3440 | 2015-05-11 21:30 | 2015-05-12 00:47 | 670 | 795 | 747 | High pressure heater tube leaks | F540The 6A HP Feedwater heater had tube leaks and unit required derate while heater is | Trimble | Derate | Coal | 3 | 2015 | 5 | 3.2833 | 0.51625 | 385.6368 | 117.4528 | 117
TC2 | D1 | 45 | 3440 | 2015-05-12 00:47 | 2015-05-14 09:48 | 720 | 795 | 747 | High pressure heater tube leaks | F540The 6A HP Feedwater heater had tube leaks and unit required derate while heater is | Trimble | Derate | Coal | 3 | 2015 | 5 | 57.0167 | 5.3789 | 4018.0613 | 70.4717 | 70
TC2 | U1 | 46 | 4293 | 2015-05-14 09:48 | 2015-05-15 06:45 | 0 | 795 | 747 | Hydraulic system pipes and valves | F060A bolt sheared on the 2A control valve hydraulic manifold which resulted in unit t | Trimble | Outage | Coal | 3 | 2015 | 5 | 20.95 | 20.95 | 15649.65 | 747 | 747
TC2 | MO | 47 | 270 | 2015-05-15 06:45 | 2015-05-16 18:20 | 0 | 795 | 747 | Primary air duct and dampers | F810Maintenance outage to replace a primary air duct expansion joint which had failed, | Trimble | Maintenance | Coal | 3 | 2015 | 5 | 35.5833 | 35.5833 | 26580.75 | 747 | 747
TC2 | D1 | 48 | 3412 | 2015-05-17 00:34 | 2015-05-17 05:04 | 409 | 795 | 747 | Feedwater pump drive - steam turbine | F790Derate required to conduct testing of the turbine driven boiler feed pump modified | Trimble | Derate | Coal | 3 | 2015 | 5 | 4.5 | 2.1849 | 1632.1245 | 362.6943 | 363
TC2 | U1 | 49 | 3431 | 2015-05-17 05:04 | 2015-05-17 15:33 | 0 | 795 | 747 | Other feedwater valves | F540The 8A HP feedwater heater bypass valve was leaking and we had to remove the unit | Trimble | Outage | Coal | 3 | 2015 | 5 | 10.4833 | 10.4833 | 7831.05 | 747 | 747
TC2 | SF | 50 | 385 | 2015-05-17 15:33 | 2015-05-18 00:57 | 0 | 795 | 747 | Igniters | F460Unit MFT due to loss of D2 oil gun, causing 2D coal mill to trip off. Due to this | Trimble | Outage | Coal | 3 | 2015 | 5 | 9.4 | 9.4 | 7021.8 | 747 | 747
TC2 | D1 | 51 | 3412 | 2015-05-18 00:57 | 2015-05-18 21:15 | 781 | 795 | 747 | Feedwater pump drive - steam turbine | F8202A TDBFP out of service for maintenance and testing following past issues with lub | Trimble | Derate | Coal | 3 | 2015 | 5 | 20.3 | 0.35748 | 267.0408 | 13.1547 | 13
TC2 | D4 | 52 | 3412 | 2015-05-18 21:15 | 2015-05-19 05:00 | 409 | 795 | 747 | Feedwater pump drive - steam turbine | F610Planned unit derate to conduct turbine driven boiler feed pump turbine from recent | Trimble | Derate | Coal | 3 | 2015 | 5 | 7.75 | 3.7629 | 2810.8811 | 362.6943 | 363
TC2 | D1 | 53 | 3412 | 2015-05-19 05:00 | 2015-05-19 05:53 | 620 | 795 | 747 | Feedwater pump drive - steam turbine | F610Following the planned turbine driven boiler feed pump testing from recent controls | Trimble | Derate | Coal | 3 | 2015 | 5 | 0.88333 | 0.19444 | 145.25 | 164.434 | 164
TC2 | NC | 54 | 1190 | 2015-05-24 | 2015-05-25 07:45 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler deslag. Unit available to return to full | Trimble | Other | Coal | 3 | 2015 | 5 | 31.75 | 31.75 | 23717.25 | 747 | 747
TC2 | D1 | 55 | 1480 | 2015-05-28 15:31 | 2015-05-28 22:39 | 400 | 795 | 747 | Other induced draft fan problems | F520One of two pressure transmitters for the A ID fan inlet measurement failed and the | Trimble | Derate | Coal | 3 | 2015 | 5 | 7.1333 | 3.5442 | 2647.5434 | 371.1509 | 371
TC2 | NC | 56 | 1190 | 2015-05-31 | 2015-05-31 07:45 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler deslag. Unit was available to return to f | Trimble | Other | Coal | 3 | 2015 | 5 | 7.75 | 7.75 | 5789.25 | 747 | 747
TC2 | NC | 57 | 1190 | 2015-06-07 | 2015-06-07 11:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler deslag. Unit available to return to full | Trimble | Other | Coal | 3 | 2015 | 6 | 11 | 11 | 8217 | 747 | 747
TC2 | D4 | 58 | 550 | 2015-06-08 | 2015-06-08 07:15 | 759 | 795 | 747 | Reheat steam relief/safety valves | F590Planned derate to set the safeties on the steam lines. | Trimble | Derate | Coal | 3 | 2015 | 6 | 7.25 | 0.3283 | 245.2415 | 33.8264 | 34
TC2 | NC | 59 | 1190 | 2015-06-14 | 2015-06-14 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Deslag of TC2. Unit was available to return to full load if requested by dispatch. | Trimble | Other | Coal | 3 | 2015 | 6 | 8 | 8 | 5976 | 747 | 747
TC2 | D4 | 60 | 4308 | 2015-06-17 10:00 | 2015-06-17 11:15 | 694 | 795 | 747 | Automatic turbine control systems - digital control and monitoring | F790Maintenance Derate to conduct ramp testing on the unit to ensure proper operation | Trimble | Derate | Coal | 3 | 2015 | 6 | 1.25 | 0.15881 | 118.6274 | 94.9019 | 95
TC2 | D4 | 61 | 4308 | 2015-06-18 21:00 | 2015-06-18 22:15 | 705 | 795 | 747 | Automatic turbine control systems - digital control and monitoring | F790Maintenance Derate to conduct ramp testing on the unit to ensure proper operation | Trimble | Derate | Coal | 3 | 2015 | 6 | 1.25 | 0.14151 | 105.7075 | 84.566 | 85
TC2 | D4 | 62 | 4308 | 2015-06-18 23:00 | 2015-06-19 00:15 | 705 | 795 | 747 | Automatic turbine control systems - digital control and monitoring | F790Maintenance Derate to conduct ramp testing on the unit to ensure proper operation | Trimble | Derate | Coal | 3 | 2015 | 6 | 1.25 | 0.14151 | 105.7075 | 84.566 | 85
TC2 | D4 | 63 | 4308 | 2015-06-19 01:00 | 2015-06-19 02:15 | 705 | 795 | 747 | Automatic turbine control systems - digital control and monitoring | F790Maintenance Derate to conduct ramp testing on the unit to ensure proper operation | Trimble | Derate | Coal | 3 | 2015 | 6 | 1.25 | 0.14151 | 105.7075 | 84.566 | 85
TC2 | D4 | 64 | 4308 | 2015-06-19 21:00 | 2015-06-19 22:15 | 694 | 795 | 747 | Automatic turbine control systems - digital control and monitoring | F790Maintenance Derate to conduct ramp testing on the unit to ensure proper operation | Trimble | Derate | Coal | 3 | 2015 | 6 | 1.25 | 0.15881 | 118.6274 | 94.9019 | 95
TC2 | D4 | 65 | 4308 | 2015-06-20 | 2015-06-20 01:15 | 669 | 795 | 747 | Automatic turbine control systems - digital control and monitoring | F790Maintenance Derate to conduct ramp testing on the unit to ensure proper operation | Trimble | Derate | Coal | 3 | 2015 | 6 | 1.25 | 0.19811 | 147.9906 | 118.3925 | 118
TC2 | D4 | 66 | 4308 | 2015-06-20 02:00 | 2015-06-20 03:15 | 669 | 795 | 747 | Automatic turbine control systems - digital control and monitoring | F790Maintenance Derate to conduct ramp testing on the unit to ensure proper operation | Trimble | Derate | Coal | 3 | 2015 | 6 | 1.25 | 0.19811 | 147.9906 | 118.3925 | 118
TC2 | NC | 67 | 1190 | 2015-06-21 | 2015-06-21 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-Curtailing Unit Derate to conduct boiler deslag. Unit was available to return | Trimble | Other | Coal | 3 | 2015 | 6 | 8 | 8 | 5976 | 747 | 747
TC2 | D4 | 68 | 4308 | 2015-06-21 23:00 | 2015-06-22 08:30 | 647 | 795 | 747 | Automatic turbine control systems - digital control and monitoring | F790Maintenance Derate to conduct ramp testing on the unit to ensure proper operation | Trimble | Derate | Coal | 3 | 2015 | 6 | 9.5 | 1.7686 | 1321.1094 | 139.0642 | 139
TC2 | D1 | 69 | 350 | 2015-06-22 08:30 | 2015-06-22 10:07 | 674 | 795 | 747 | Pulverized fuel and air piping (from pulverizer to wind box) | F3502B3 Elevation of the 2B Mill's coal piping began leaking. While it was being repai | Trimble | Derate | Coal | 3 | 2015 | 6 | 1.6167 | 0.24606 | 183.8058 | 113.6943 | 114
TC2 | D4 | 70 | 1990 | 2015-06-22 22:00 | 2015-06-23 05:00 | 593 | 795 | 747 | Boiler performance testing (use code 9999 for total unit performance testing) | F790Unit was under performance testing during the duration of the derate. Over the 7 h | Trimble | Derate | Coal | 3 | 2015 | 6 | 7 | 1.7786 | 1328.6264 | 189.8038 | 190
TC2 | D1 | 71 | 9616 | 2015-06-26 15:46 | 2015-06-26 17:00 | 724 | 795 | 747 | CO stack emissions | FE00Unit began to experience elevated CO emissions. A derate was taken to avoid an ex | Trimble | Derate | Coal | 3 | 2015 | 6 | 1.2333 | 0.11015 | 82.2796 | 66.7132 | 67
TC2 | NC | 72 | 1190 | 2015-06-28 | 2015-06-28 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to conduct boiler deslag. Unit was available to return to f | Trimble | Other | Coal | 3 | 2015 | 6 | 8 | 8 | 5976 | 747 | 747
TC2 | NC | 73 | 1190 | 2015-07-05 | 2015-07-05 07:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing unit derate to conduct boiler deslag. Unit was available to return | Trimble | Other | Coal | 3 | 2015 | 7 | 7 | 7 | 5229 | 747 | 747
TC2 | NC | 74 | 1190 | 2015-07-12 00:01 | 2015-07-12 07:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate was taken to perform a boiler deslag. Unit was available to | Trimble | Other | Coal | 3 | 2015 | 7 | 6.9833 | 6.9833 | 5216.55 | 747 | 747
TC2 | NC | 75 | 1190 | 2015-07-19 | 2015-07-19 08:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate was taken to perform a boiler deslag. The unit was available | Trimble | Other | Coal | 3 | 2015 | 7 | 8 | 8 | 5976 | 747 | 747
TC2 | MO | 76 | 561 | 2015-07-25 02:23 | 2015-07-26 06:55 | 0 | 795 | 747 | Other cold reheat steam valves (not including turbine stop or intercept valves) | F540Cold Reheat check valve was leaking at the valve packing - weekend maintenance out | Trimble | Maintenance | Coal | 3 | 2015 | 7 | 28.5333 | 28.5333 | 21314.4 | 747 | 747
TC2 | U1 | 77 | 3441 | 2015-07-26 08:55 | 2015-07-28 14:37 | 0 | 795 | 747 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F820The Economizer Inlet Bypass Valve (191) had corroded terminals on the valve actuat | Trimble | Outage | Coal | 3 | 2015 | 7 | 53.7 | 53.7 | 40113.9 | 747 | 747
TC2 | D1 | 78 | 3410 | 2015-07-28 20:00 | 2015-07-28 20:30 | 340 | 795 | 747 | Feedwater pump | F820After switching from Motor Drive Boiler Feed Pumps to TD's, 2B Turbine Drive Boile | Trimble | Derate | Coal | 3 | 2015 | 7 | 0.5 | 0.28616 | 213.7642 | 427.5283 | 428
TC2 | D1 | 79 | 3410 | 2015-07-28 20:30 | 2015-07-29 02:30 | 340 | 795 | 747 | Feedwater pump | F820After 2B TDBFP was tripped, 2A Turbine Drive Boiler Feed Pump tripped due to contr | Trimble | Derate | Coal | 3 | 2015 | 7 | 6 | 3.434 | 2565.1698 | 427.5283 | 428
TC2 | D1 | 80 | 3410 | 2015-07-29 02:30 | 2015-07-29 04:45 | 626 | 795 | 747 | Feedwater pump | F780In the process of ramping up, variable load and average is given. | Trimble | Derate | Coal | 3 | 2015 | 7 | 2.25 | 0.4783 | 357.2915 | 158.7962 | 159
TC2 | D1 | 81 | 3440 | 2015-07-29 04:45 | 2015-07-29 05:45 | 756 | 795 | 747 | High pressure heater tube leaks | F540HP Heater 6A and 6B are having leaking problems - 6A has had a channel-side safety | Trimble | Derate | Coal | 3 | 2015 | 7 | 1 | 0.049057 | 36.6453 | 36.6453 | 37
TC2 | D1 | 82 | 3440 | 2015-07-29 05:45 | 2015-07-29 06:10 | 731 | 795 | 747 | High pressure heater tube leaks | F540This derate is due to continued problems with the 6A and 6B heaters. | Trimble | Derate | Coal | 3 | 2015 | 7 | 0.41667 | 0.033543 | 25.0566 | 60.1358 | 60
TC2 | D1 | 83 | 3440 | 2015-07-29 06:10 | 2015-08-03 | 715 | 795 | 747 | High pressure heater tube leaks | F540This derate is due to continued problems with the 6A and 6B heaters. | Trimble | Derate | Coal | 3 | 2015 | 7 | 113.8333 | 11.4549 | 8556.8302 | 75.1698 | 75
TC2 | D1 | 84 | 3441 | 2015-08-03 | 2015-08-03 18:00 | 715 | 795 | 747 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F540HP Heaters 6A and 6B were put back in service but Heater 7A's safety is being repl | Trimble | Derate | Coal | 3 | 2015 | 8 | 18 | 1.8113 | 1353.0566 | 75.1698 | 75
TC2 | NC | 85 | 1190 | 2015-08-09 21:00 | 2015-08-10 05:10 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for Unit Deslag. Unit was available for full load if request | Trimble | Other | Coal | 3 | 2015 | 8 | 8.1667 | 8.1667 | 6100.5 | 747 | 747
TC2 | D1 | 86 | 331 | 2015-08-10 05:10 | 2015-08-10 10:30 | 585 | 795 | 747 | Pulverizer system coal leaks (other than pulverizers | F5402C Mill Coal Conduit leak - this mill, along with 2D Mill (carded out) are out of | Trimble | Derate | Coal | 3 | 2015 | 8 | 5.3333 | 1.4088 | 1052.3774 | 197.3208 | 197
TC2 | D1 | 87 | 3441 | 2015-08-10 10:30 | 2015-08-10 16:30 | 739 | 795 | 747 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F540Due to the same feedwater pressure 'excursion' that caused issues with the 6A&B HP | Trimble | Derate | Coal | 3 | 2015 | 8 | 6 | 0.42264 | 315.7132 | 52.6189 | 53
TC2 | D1 | 88 | 3441 | 2015-08-10 16:30 | 2015-08-12 04:00 | 764 | 795 | 747 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F540Continued problems with the HP 7 Heater. | Trimble | Derate | Coal | 3 | 2015 | 8 | 35.5 | 1.3843 | 1034.0547 | 29.1283 | 29
TC2 | PD | 89 | 3441 | 2015-08-14 21:30 | 2015-08-15 08:00 | 449 | 795 | 747 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F540Repairs were being done on the 8A and 8B FWH safeties due to the earlier TC2 FW pr | Trimble | Derate | Coal | 3 | 2015 | 8 | 10.5 | 4.5698 | 3413.6491 | 325.1094 | 325
TC2 | PD | 90 | 3441 | 2015-08-15 08:00 | 2015-08-17 03:00 | 764 | 795 | 747 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F540The deslag was finished and repairs continued on the 8A and 8B FWH safeties. | Trimble | Derate | Coal | 3 | 2015 | 8 | 43 | 1.6767 | 1252.517 | 29.1283 | 29
TC2 | D1 | 91 | 340 | 2015-08-21 21:00 | 2015-08-21 23:50 | 700 | 795 | 747 | Other pulverizer problems | F660Unit was put on derate during D Mill Bowl DP problems: first, the bowl DP alarm ca | Trimble | Derate | Coal | 3 | 2015 | 8 | 2.8333 | 0.33857 | 252.9151 | 89.2642 | 89
TC2 | NC | 92 | 1190 | 2015-08-23 | 2015-08-23 06:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-Curtailing derate for Unit to complete scheduled boiler tube deslag. Unit was | Trimble | Other | Coal | 3 | 2015 | 8 | 6 | 6 | 4482 | 747 | 747
TC2 | D1 | 93 | 310 | 2015-08-27 08:35 | 2015-08-27 12:45 | 669 | 795 | 747 | Pulverizer mills | F5402B Coal Mill tripped due to low oil level in resevoir - lube oil began leaking dur | Trimble | Derate | Coal | 3 | 2015 | 8 | 4.1667 | 0.66038 | 493.3019 | 118.3925 | 118
TC2 | NC | 94 | 1190 | 2015-08-29 22:00 | 2015-08-30 07:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for scheduled boiler tube deslag. Unit was available for ful | Trimble | Other | Coal | 3 | 2015 | 8 | 9.5 | 9.5 | 7096.5 | 747 | 747
TC2 | D1 | 95 | 310 | 2015-08-30 19:50 | 2015-08-30 20:45 | 659 | 795 | 747 | Pulverizer mills | F0702D Mill began spitting fireflies and smoke out of the pyrite chute. Since TC2 need | Trimble | Derate | Coal | 3 | 2015 | 8 | 0.91667 | 0.15681 | 117.1396 | 127.7887 | 128
TC2 | D1 | 96 | 3431 | 2015-09-01 | 2015-09-01 05:00 | 449 | 795 | 747 | Other feedwater valves | F540Load was dropped so a contractor could safely work on a feedwater valve packing le | Trimble | Derate | Coal | 3 | 2015 | 9 | 5 | 2.1761 | 1625.5472 | 325.1094 | 325
TC2 | D1 | 97 | 335 | 2015-09-05 01:42 | 2015-09-05 02:57 | 650 | 795 | 747 | Pulverizer lube oil system | F520Problems with the 2E Coal Mill - false low flow alarms came in for both the lube o | Trimble | Derate | Coal | 3 | 2015 | 9 | 1.25 | 0.22799 | 170.3066 | 136.2453 | 136
TC2 | NC | 98 | 1190 | 2015-09-06 | 2015-09-06 07:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate to perform routine boiler deslag. Unit was available to retu | Trimble | Other | Coal | 3 | 2015 | 9 | 7.5 | 7.5 | 5602.5 | 747 | 747
TC2 | D1 | 99 | 340 | 2015-09-11 08:57 | 2015-09-11 10:50 | 660 | 795 | 747 | Other pulverizer problems | F1201B Mill tripped due to a low primary air fan alarm - the transmitter was plugged a | Trimble | Derate | Coal | 3 | 2015 | 9 | 1.8833 | 0.31981 | 238.8991 | 126.8491 | 127
TC2 | NC | 100 | 1190 | 2015-09-13 | 2015-09-13 07:45 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. The unit was available to return to full | Trimble | Other | Coal | 3 | 2015 | 9 | 7.75 | 7.75 | 5789.25 | 747 | 747
TC2 | PD | 101 | 870 | 2015-09-16 21:00 | 2015-09-17 06:51 | 449 | 795 | 747 | Soot blowers - steam | F340Planned Derate for sootblower maintenance items and boiler deslag. | Trimble | Derate | Coal | 3 | 2015 | 9 | 9.85 | 4.2869 | 3202.3279 | 325.1094 | 325
TC2 | NC | 102 | 1190 | 2015-09-20 | 2015-09-20 07:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. Unit was available for full load if reque | Trimble | Other | Coal | 3 | 2015 | 9 | 7.5 | 7.5 | 5602.5 | 747 | 747
TC2 | D1 | 103 | 520 | 2015-09-21 05:00 | 2015-09-21 09:05 | 449 | 795 | 747 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | F540Main Steam non-return MOV packing is blowing steam. Unit derated due to leak. | Trimble | Derate | Coal | 3 | 2015 | 9 | 4.0833 | 1.7771 | 1327.5302 | 325.1094 | 325
TC2 | U1 | 104 | 520 | 2015-09-21 09:05 | 2015-09-23 07:58 | 0 | 795 | 747 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | F540Forced outage due to the packing leak in the Non-Return Main Steam MOV. | Trimble | Outage | Coal | 3 | 2015 | 9 | 46.8833 | 46.8833 | 35021.85 | 747 | 747
TC2 | U1 | 105 | 3974 | 2015-09-23 10:47 | 2015-09-23 17:19 | 0 | 795 | 747 | DCS - logic problems | F040While ramping and placing three mills in service, a logic problem caused the mills | Trimble | Outage | Coal | 3 | 2015 | 9 | 6.5333 | 6.5333 | 4880.4 | 747 | 747
TC2 | U1 | 106 | 380 | 2015-09-23 17:57 | 2015-09-23 22:31 | 0 | 795 | 747 | Light-off (igniter) systems (including fuel supply) | F820As unit was firing, oil guns were lost on the A Mill. This caused a trip on the A | Trimble | Outage | Coal | 3 | 2015 | 9 | 4.5667 | 4.5667 | 3411.3 | 747 | 747
TC2 | U1 | 107 | 3974 | 2015-09-23 23:36 | 2015-09-24 03:13 | 0 | 795 | 747 | DCS - logic problems | F820Despite the Feedwater Storage Vessel being at high level, the unit was calling for | Trimble | Outage | Coal | 3 | 2015 | 9 | 3.6167 | 3.6167 | 2701.65 | 747 | 747
TC2 | D1 | 108 | 3979 | 2015-09-24 07:27 | 2015-09-24 11:30 | 360 | 795 | 747 | Other DCS problems | F660Due to low load of unit while ramping, there was problem transferring from MDBFP t | Trimble | Derate | Coal | 3 | 2015 | 9 | 4.05 | 2.216 | 1655.3802 | 408.7358 | 409
TC2 | D1 | 109 | 3979 | 2015-09-24 11:30 | 2015-09-24 18:56 | 400 | 795 | 747 | Other DCS problems | F660Continued problems solving the feedwater issue. We were holding load down until we | Trimble | Derate | Coal | 3 | 2015 | 9 | 7.4333 | 3.6933 | 2758.8887 | 371.1509 | 371
TC2 | D1 | 110 | 4261 | 2015-10-01 06:00 | 2015-10-01 12:43 | 800 | 795 | 747 | Control valves | F340Switching of unit operating mode for wintertime operations caused a problem with t | Trimble | Derate | Coal | 3 | 2015 | 10 | 6.7167 | -0.042243 | -31.5557 | 0 | 0
TC2 | NC | 111 | 1190 | 2015-10-04 | 2015-10-04 07:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. Unit was available for full load if reque | Trimble | Other | Coal | 3 | 2015 | 10 | 7.5 | 7.5 | 5602.5 | 747 | 747
TC2 | D1 | 112 | 1455 | 2015-10-06 | 2015-10-06 01:45 | 769 | 795 | 747 | Induced draft fans | F660Due to caution against tripping the unit on low ID Inlet Duct pressure, a derate w | Trimble | Derate | Coal | 3 | 2015 | 10 | 1.75 | 0.057233 | 42.7528 | 24.4302 | 24
TC2 | D1 | 113 | 8823 | 2015-10-09 16:50 | 2015-10-09 17:51 | 720 | 795 | 747 | SCR NOx Other ammonia system problems | FE00Unit was derated to stay within NOx limits - Ammonia Pump tripped and unit began t | Trimble | Derate | Coal | 3 | 2015 | 10 | 1.0167 | 0.095912 | 71.6462 | 70.4717 | 70
TC2 | D1 | 114 | 8823 | 2015-10-09 17:51 | 2015-10-09 20:30 | 709 | 795 | 747 | SCR NOx Other ammonia system problems | FE00Continued problems due to Ammonia Pump trip. Derate was in effect until NOx levels | Trimble | Derate | Coal | 3 | 2015 | 10 | 2.65 | 0.28667 | 214.14 | 80.8075 | 81
TC2 | NC | 115 | 1190 | 2015-10-11 | 2015-10-11 07:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. Unit was available for full load if reque | Trimble | Other | Coal | 3 | 2015 | 10 | 7.5 | 7.5 | 5602.5 | 747 | 747
TC2 | D1 | 116 | 100 | 2015-10-14 21:00 | 2015-10-15 01:00 | 774 | 795 | 747 | Bunker gates | F780Operators reduced load by the above amount for a coal mill swap to allow room for | Trimble | Derate | Coal | 3 | 2015 | 10 | 4 | 0.10566 | 78.9283 | 19.7321 | 20
TC2 | NC | 117 | 1190 | 2015-10-17 23:00 | 2015-10-18 05:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Unit was on a non-curtailing derate to perform a boiler deslag. The unit was avail | Trimble | Other | Coal | 3 | 2015 | 10 | 6.5 | 6.5 | 4855.5 | 747 | 747
TC2 | D1 | 118 | 3502 | 2015-10-19 22:30 | 2015-10-22 03:00 | 760 | 795 | 747 | Heater level control | F400The unit was derated while solving an extraction steam problem. During isolation o | Trimble | Derate | Coal | 3 | 2015 | 10 | 52.5 | 2.3113 | 1726.5566 | 32.8868 | 33
TC2 | NC | 119 | 1190 | 2015-10-25 | 2015-10-25 07:15 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for unit deslag. The unit was available for full load if req | Trimble | Other | Coal | 3 | 2015 | 10 | 7.25 | 7.25 | 5415.75 | 747 | 747
TC2 | D2 | 120 | 3431 | 2015-10-26 18:13 | 2015-10-27 14:55 | 440 | 795 | 747 | Other feedwater valves | F540Feedwater Bypass Valve BLS MOV 501 had a packing leak. Unit was on a derate until | Trimble | Derate | Coal | 3 | 2015 | 10 | 20.7 | 9.2434 | 6904.817 | 333.566 | 334
TC2 | NC | 121 | 1190 | 2015-11-01 | 2015-11-01 05:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate due to boiler deslag. Unit was available for full load if re | Trimble | Other | Coal | 3 | 2015 | 11 | 5 | 5 | 3735 | 747 | 747
TC2 | NC | 122 | 1190 | 2015-11-04 22:00 | 2015-11-05 05:15 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. The unit was available for full load if r | Trimble | Other | Coal | 3 | 2015 | 11 | 7.25 | 7.25 | 5415.75 | 747 | 747
TC2 | D1 | 123 | 1090 | 2015-11-05 11:20 | 2015-11-05 16:17 | 480 | 795 | 747 | Other boiler tube leaks | F540Immediate derate due to dropping load for boiler tube leak repair. The capacity re | Trimble | Derate | Coal | 3 | 2015 | 11 | 4.95 | 1.9613 | 1465.1066 | 295.9811 | 296
TC2 | U1 | 124 | 1090 | 2015-11-05 16:17 | 2015-11-09 10:16 | 0 | 795 | 747 | Other boiler tube leaks | F540Forced outage due to tube leak repair - two (2) tube leaks were found and repaired | Trimble | Outage | Coal | 3 | 2015 | 11 | 89.9833 | 89.9833 | 67217.55 | 747 | 747
TC2 | D1 | 125 | 4261 | 2015-11-11 06:18 | 2015-11-11 15:11 | 794 | 795 | 747 | Control valves | F850The Unit was placed in Boiler Follow + MW mode, which dropped the effective load o | Trimble | Derate | Coal | 3 | 2015 | 11 | 8.8833 | 0.011174 | 8.347 | 0.93962 | 1
TC2 | NC | 126 | 1190 | 2015-11-15 | 2015-11-15 07:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. Unit was available for full load if reque | Trimble | Other | Coal | 3 | 2015 | 11 | 7 | 7 | 5229 | 747 | 747
TC2 | U1 | 127 | 3412 | 2015-11-16 21:22 | 2015-11-17 06:42 | 0 | 795 | 747 | Feedwater pump drive - steam turbine | F820The unit lost the 2A TDBFP and then the 2F mill, starting a runback and then tripp | Trimble | Outage | Coal | 3 | 2015 | 11 | 9.3333 | 9.3333 | 6972 | 747 | 747
TC2 | U1 | 128 | 3412 | 2015-11-17 07:13 | 2015-11-17 13:04 | 0 | 795 | 747 | Feedwater pump drive - steam turbine | F820Continued problems with the 2A TDBFP - tripped on low flow due to turbine blade is | Trimble | Outage | Coal | 3 | 2015 | 11 | 5.85 | 5.85 | 4369.95 | 747 | 747
TC2 | D1 | 129 | 3412 | 2015-11-17 20:00 | 2015-11-20 22:30 | 794 | 795 | 747 | Feedwater pump drive - steam turbine | F060Due to broken steam turbine blade on 2A TDBFP, the MDBFP must be run to make load. | Trimble | Derate | Coal | 3 | 2015 | 11 | 74.5 | 0.093711 | 70.0019 | 0.93962 | 1
TC2 | NC | 130 | 1190 | 2015-11-20 22:30 | 2015-11-21 05:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. Unit was available for full gross-capacit | Trimble | Other | Coal | 3 | 2015 | 11 | 7 | 7 | 5229 | 747 | 747
TC2 | D1 | 131 | 3412 | 2015-11-21 05:30 | 2015-11-26 21:30 | 794 | 795 | 747 | Feedwater pump drive - steam turbine | F060Continued problems with the 2A TDBFP turbine. The running of the MDBFP reduces net | Trimble | Derate | Coal | 3 | 2015 | 11 | 136 | 0.17107 | 127.7887 | 0.93962 | 1
TC2 | NC | 132 | 1190 | 2015-11-26 21:30 | 2015-11-27 07:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. The unit was available for full load if r | Trimble | Other | Coal | 3 | 2015 | 11 | 9.5 | 9.5 | 7096.5 | 747 | 747
TC2 | D1 | 133 | 3456 | 2015-11-27 07:00 | 2015-11-30 02:35 | 794 | 795 | 747 | Feedwater Booster Pump Drive - Steam Turbine | F060Continued problems with the 2A TDBFP. | Trimble | Derate | Coal | 3 | 2015 | 11 | 67.5833 | 0.08501 | 63.5028 | 0.93962 | 1
TC2 | U1 | 134 | 1400 | 2015-11-30 02:35 | 2015-12-01 04:12 | 0 | 795 | 747 | Forced draft fans | F8502A Forced Draft fan vibration caused unit to MFT. | Trimble | Outage | Coal | 3 | 2015 | 11 | 25.6167 | 25.6167 | 19135.65 | 747 | 747
TC2 | D1 | 135 | 3412 | 2015-12-01 04:12 | 2015-12-06 | 794 | 795 | 747 | Feedwater pump drive - steam turbine | F060Repairs are still outstanding on 2A TDBFP, requiring the use of the MDBFP. This ca | Trimble | Derate | Coal | 3 | 2015 | 12 | 115.8 | 0.14566 | 108.8083 | 0.93962 | 1
TC2 | NC | 136 | 1190 | 2015-12-06 | 2015-12-06 08:15 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. The unit was available for full load if r | Trimble | Other | Coal | 3 | 2015 | 12 | 8.25 | 8.25 | 6162.75 | 747 | 747
TC2 | D1 | 137 | 3412 | 2015-12-06 08:15 | 2015-12-09 03:38 | 794 | 795 | 747 | Feedwater pump drive - steam turbine | F060The 2A TDBFP is out of service, requiring the use of the MDBFP. The running of the | Trimble | Derate | Coal | 3 | 2015 | 12 | 67.3833 | 0.084759 | 63.3149 | 0.93962 | 1
TC2 | U1 | 138 | 1480 | 2015-12-09 03:38 | 2015-12-09 20:28 | 0 | 795 | 747 | Other induced draft fan problems | F820The Radial Y Vibration probe on the TC 2A ID Fans was reading incorrectly, causing | Trimble | Outage | Coal | 3 | 2015 | 12 | 16.8333 | 16.8333 | 12574.5 | 747 | 747
TC2 | D1 | 139 | 3456 | 2015-12-09 20:28 | 2015-12-10 13:00 | 794 | 795 | 747 | Feedwater Booster Pump Drive - Steam Turbine | F060Continued problems with the 2A TDBFP. | Trimble | Derate | Coal | 3 | 2015 | 12 | 16.5333 | 0.020797 | 15.5351 | 0.93962 | 1
TC2 | D1 | 140 | 510 | 2015-12-10 13:00 | 2015-12-10 15:00 | 669 | 795 | 747 | Main steam relief/safety valves off superheater | F540A leak in a main steam safety valve has reduced gross available capacity. | Trimble | Derate | Coal | 3 | 2015 | 12 | 2 | 0.31698 | 236.7849 | 118.3925 | 118
TC2 | D1 | 141 | 510 | 2015-12-10 15:00 | 2015-12-11 19:40 | 760 | 795 | 747 | Main steam relief/safety valves off superheater | F540Operating with temporary measures on the leaking safety relief valve to allow us t | Trimble | Derate | Coal | 3 | 2015 | 12 | 28.6667 | 1.2621 | 942.7547 | 32.8868 | 33
TC2 | D1 | 142 | 3409 | 2015-12-11 19:40 | 2015-12-13 | 794 | 795 | 747 | Feedwater pump drive motor - variable speed | F060Regardless of the main steam safety being fixed, we are having continued problems | Trimble | Derate | Coal | 3 | 2015 | 12 | 28.3333 | 0.035639 | 26.6226 | 0.93962 | 1
TC2 | NC | 143 | 1190 | 2015-12-13 | 2015-12-13 07:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. Unit was available for full load if reque | Trimble | Other | Coal | 3 | 2015 | 12 | 7.5 | 7.5 | 5602.5 | 747 | 747
TC2 | D1 | 144 | 3409 | 2015-12-13 07:30 | 2015-12-20 07:30 | 794 | 795 | 747 | Feedwater pump drive motor - variable speed | F060Continued net derate due to the broken turbine blades on the 2A TDBFP, requiring t | Trimble | Derate | Coal | 3 | 2015 | 12 | 168 | 0.21132 | 157.8566 | 0.93962 | 1
TC2 | D1 | 145 | 3412 | 2015-12-20 07:30 | 2015-12-20 16:30 | 749 | 795 | 747 | Feedwater pump drive - steam turbine | F060Continued problems with the 2A TDBFP. | Trimble | Derate | Coal | 3 | 2015 | 12 | 9 | 0.52075 | 389.0038 | 43.2226 | 43
TC2 | NC | 146 | 1190 | 2015-12-20 22:00 | 2015-12-21 04:15 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. The unit was available for full load if r | Trimble | Other | Coal | 3 | 2015 | 12 | 6.25 | 6.25 | 4668.75 | 747 | 747
TC2 | D1 | 147 | 3441 | 2015-12-21 20:00 | 2015-12-23 | 750 | 795 | 747 | Other high pressure heater problems (see condensate system for LP and IP heater codes) | F540The 7A high pressure feedwater heater had to be removed from service to allow for | Trimble | Derate | Coal | 3 | 2015 | 12 | 28 | 1.5849 | 1183.9245 | 42.283 | 42
TC2 | D1 | 148 | 95 | 2015-12-31 17:16 | 2015-12-31 18:50 | 750 | 795 | 747 | Bunker flow problems | F720D Coal Mill was running wthout coal on belt; the equipment was taken out of servic | Trimble | Derate | Coal | 3 | 2015 | 12 | 1.5667 | 0.088679 | 66.2434 | 42.283 | 42
TC2 | NC | 149 | 1190 | 2015-12-31 23:00 | 2016-01-01 |  | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. Unit was available for full load if reque | Trimble | Other | Coal | 3 | 2015 | 12 | 1 | 1 | 747 | 747 | 747
TC2 | NC | 11 | 1190 | 2016-01-01 | 2016-01-01 06:30 |  | 795 | 747 | Other tube slagging or fouling | FS00Continuation of event 149 from 2015. This was a Non-Curtailing Derate for a unit d | Trimble | Other | Coal | 3 | 2016 | 1 | 6.5 | 6.5 | 4855.5 | 747 | 747
TC2 | D1 | 1 | 3310 | 2016-01-01 07:11 | 2016-01-01 15:00 | 760 | 795 | 747 | Condensate/hotwell pumps | F660Problems with the 2B Hotwell Pumps placed the unit on a derate. Swapping pumps did | Trimble | Derate | Coal | 3 | 2016 | 1 | 7.8167 | 0.34413 | 257.0651 | 32.8868 | 33
TC2 | D1 | 2 | 3985 | 2016-01-07 09:45 | 2016-01-07 12:00 | 796 | 795 | 747 | PLC - upgrades | F610Unit Control Mode was changed to view how the unit behaved in a boiler swing under | Trimble | Derate | Coal | 3 | 2016 | 1 | 2.25 | -0.0028302 | -2.1142 | 0 | 0
TC2 | D1 | 3 | 310 | 2016-01-08 01:15 | 2016-01-08 04:00 | 740 | 795 | 747 | Pulverizer mills | F660Mill swap from 2B to 2D Coal Mills resulted in a unit derate. | Trimble | Derate | Coal | 3 | 2016 | 1 | 2.75 | 0.19025 | 142.1179 | 51.6792 | 52
TC2 | NC | 4 | 1190 | 2016-01-09 | 2016-01-09 07:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. The unit was available for full load if r | Trimble | Other | Coal | 3 | 2016 | 1 | 7.5 | 7.5 | 5602.5 | 747 | 747
TC2 | D1 | 5 | 3210 | 2016-01-10 09:40 | 2016-01-10 10:00 | 750 | 795 | 747 | Circulating water pumps | F480Despite the pump operating normally, the 2B Cooling Tower Pump discharge pressure | Trimble | Derate | Coal | 3 | 2016 | 1 | 0.33333 | 0.018868 | 14.0943 | 42.283 | 42
TC2 | D1 | 6 | 9290 | 2016-01-11 15:50 | 2016-01-12 01:00 | 760 | 795 | 747 | Other fuel quality problems | FW00Low fuel quality caused a unit derate. | Trimble | Derate | Coal | 3 | 2016 | 1 | 9.1667 | 0.40356 | 301.4623 | 32.8868 | 33
TC2 | D1 | 7 | 310 | 2016-01-12 01:00 | 2016-01-12 05:00 | 719 | 795 | 747 | Pulverizer mills | F660Problems with the 2D and 2C coal mills contributed to a derate while swapping mill | Trimble | Derate | Coal | 3 | 2016 | 1 | 4 | 0.38239 | 285.6453 | 71.4113 | 71
TC2 | D1 | 8 | 9290 | 2016-01-12 05:00 | 2016-01-12 08:30 | 760 | 795 | 747 | Other fuel quality problems | FW00Problems with fuel quality. | Trimble | Derate | Coal | 3 | 2016 | 1 | 3.5 | 0.15409 | 115.1038 | 32.8868 | 33
TC2 | D1 | 9 | 9290 | 2016-01-12 08:30 | 2016-01-13 09:56 | 780 | 795 | 747 | Other fuel quality problems | FW00Problems with fuel quality. | Trimble | Derate | Coal | 3 | 2016 | 1 | 25.4333 | 0.47987 | 358.466 | 14.0943 | 14
TC2 | NC | 10 | 1190 | 2016-01-16 | 2016-01-16 07:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. Unit was available for full load if reque | Trimble | Other | Coal | 3 | 2016 | 1 | 7.5 | 7.5 | 5602.5 | 747 | 747
TC2 | NC | 12 | 1190 | 2016-01-22 22:00 | 2016-01-23 05:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. The Unit was available for full load if r | Trimble | Other | Coal | 3 | 2016 | 1 | 7.5 | 7.5 | 5602.5 | 747 | 747
TC2 | NC | 13 | 1190 | 2016-01-30 22:00 | 2016-01-31 05:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. The Unit was available for full load if r | Trimble | Other | Coal | 3 | 2016 | 1 | 7.5 | 7.5 | 5602.5 | 747 | 747
TC2 | D1 | 14 | 1488 | 2016-02-03 22:00 | 2016-02-04 | 709 | 795 | 747 | Air heater (regenerative) | F660The unit load was dropped due to airflow issues when swapping mills. The Air Heate | Trimble | Derate | Coal | 3 | 2016 | 2 | 2 | 0.21635 | 161.6151 | 80.8075 | 81
TC2 | U1 | 15 | 1000 | 2016-02-06 12:49 | 2016-02-09 01:21 | 0 | 795 | 747 | Waterwall (Furnace wall) A | F540Unit was manually taken offline for a boiler tuble leak. The leak was located on t | Trimble | Outage | Coal | 3 | 2016 | 2 | 60.5333 | 60.5333 | 45218.4 | 747 | 747
TC2 | D1 | 16 | 280 | 2016-02-09 10:15 | 2016-02-09 11:00 | 669 | 795 | 747 | Pulverizer fires | FR00Both 2D and 2E coal mills were unavailable at this time due to fires. | Trimble | Derate | Coal | 3 | 2016 | 2 | 0.75 | 0.11887 | 88.7943 | 118.3925 | 118
TC2 | D1 | 17 | 280 | 2016-02-09 11:00 | 2016-02-09 20:00 | 659 | 795 | 747 | Pulverizer fires | FR00Both 2D and 2E coal mills were unavailable at this time due to fires. | Trimble | Derate | Coal | 3 | 2016 | 2 | 9 | 1.5396 | 1150.0981 | 127.7887 | 128
TC2 | D1 | 18 | 280 | 2016-02-12 05:25 | 2016-02-12 07:00 | 650 | 795 | 747 | Pulverizer fires | FR00Derate for continued problems with D Mill fires. | Trimble | Derate | Coal | 3 | 2016 | 2 | 1.5833 | 0.28878 | 215.7217 | 136.2453 | 136
TC2 | PD | 19 | 4842 | 2016-02-15 20:00 | 2016-02-15 23:00 | 752 | 795 | 747 | Reactive and capability testing | F790Pllanned derate for flux probe testing on the unit generator. The unit needed to b | Trimble | Derate | Coal | 3 | 2016 | 2 | 3 | 0.16226 | 121.2113 | 40.4038 | 40
TC2 | NC | 20 | 1190 | 2016-02-15 23:00 | 2016-02-16 06:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for deslag. The unit was available for full load if requeste | Trimble | Other | Coal | 3 | 2016 | 2 | 7 | 7 | 5229 | 747 | 747
TC2 | NC | 21 | 1190 | 2016-02-20 22:00 | 2016-02-21 05:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler delsag. Unit was available for full load if reque | Trimble | Other | Coal | 3 | 2016 | 2 | 7.5 | 7.5 | 5602.5 | 747 | 747
TC2 | D1 | 22 | 1488 | 2016-02-24 01:00 | 2016-02-24 02:16 | 759 | 795 | 747 | Air heater (regenerative) | F660The unit load was dropped due to airflow issues when swapping mills. The Air Heate | Trimble | Derate | Coal | 3 | 2016 | 2 | 1.2667 | 0.057358 | 42.8468 | 33.8264 | 34
TC2 | NC | 23 | 1190 | 2016-02-26 21:30 | 2016-02-27 07:00 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. The unit was available for full load if r | Trimble | Other | Coal | 3 | 2016 | 2 | 9.5 | 9.5 | 7096.5 | 747 | 747
TC2 | PD | 24 | 1488 | 2016-03-01 | 2016-03-01 02:30 | 709 | 795 | 747 | Air heater (regenerative) | F660The unit load was dropped due to airflow issues when swapping mills. The Air Heate | Trimble | Derate | Coal | 3 | 2016 | 3 | 2.5 | 0.27044 | 202.0189 | 80.8075 | 81
TC2 | PD | 25 | 1488 | 2016-03-03 01:00 | 2016-03-03 02:45 | 709 | 795 | 747 | Air heater (regenerative) | F660The unit load was dropped during a coal mill swap, due to restricted airflow to th | Trimble | Derate | Coal | 3 | 2016 | 3 | 1.75 | 0.18931 | 141.4132 | 80.8075 | 81
TC2 | D1 | 26 | 280 | 2016-03-03 07:30 | 2016-03-03 08:30 | 699 | 795 | 747 | Pulverizer fires | FR00The unit was on a derated status due to the 2D Mill catching on fire. | Trimble | Derate | Coal | 3 | 2016 | 3 | 1 | 0.12075 | 90.2038 | 90.2038 | 90
TC2 | D1 | 27 | 280 | 2016-03-03 08:30 | 2016-03-03 10:30 | 656 | 795 | 747 | Pulverizer fires | FR00Further derated status due to continued problems with the 2D Mill fire. | Trimble | Derate | Coal | 3 | 2016 | 3 | 2 | 0.34969 | 261.2151 | 130.6075 | 131
TC2 | PD | 28 | 4263 | 2016-03-05 17:45 | 2016-03-06 | 779 | 795 | 747 | Reheat stop valves | F590Planned derate for setting the reheat safeties. | Trimble | Derate | Coal | 3 | 2016 | 3 | 6.25 | 0.12579 | 93.9623 | 15.034 | 15
TC2 | NC | 29 | 1190 | 2016-03-06 | 2016-03-06 09:15 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. The unit was available for full load if r | Trimble | Other | Coal | 3 | 2016 | 3 | 9.25 | 9.25 | 6909.75 | 747 | 747
TC2 | NC | 30 | 1190 | 2016-03-11 22:00 | 2016-03-12 05:30 | 0 | 795 | 747 | Other tube slagging or fouling | FS00Non-curtailing derate for boiler deslag. The unit was available for full load if r | Trimble | Other | Coal | 3 | 2016 | 3 | 7.5 | 7.5 | 5602.5 | 747 | 747
TC2 | PD | 31 | 4260 | 2016-03-12 05:30 | 2016-03-12 07:15 | 698 | 795 | 747 | Main stop valves | F610Planned derate for safety valve setting. | Trimble | Derate | Coal | 3 | 2016 | 3 | 1.75 | 0.21352 | 159.5009 | 91.1434 | 91
TC2 | PD | 32 | 4260 | 2016-03-12 07:15 | 2016-03-12 11:15 | 648 | 795 | 747 | Main stop valves | F610Planned derate for safey valve setting - the unit was placed in a further derated | Trimble | Derate | Coal | 3 | 2016 | 3 | 4 | 0.73962 | 552.4981 | 138.1245 | 138
TC2 | PD | 33 | 1488 | 2016-03-15 23:00 | 2016-03-16 | 748 | 795 | 747 | Air heater (regenerative) | F660Planned derate to swap mills. Due to airflow issues with the air heater, load must | Trimble | Derate | Coal | 3 | 2016 | 3 | 1 | 0.059119 | 44.1623 | 44.1623 | 44
TC2 | U1 | 34 | 1000 | 2016-03-16 11:50 | 2016-03-18 15:27 | 0 | 795 | 747 | Waterwall (Furnace wall) A | F540Forced outage due to a boiler tube leak. | Trimble | Outage | Coal | 3 | 2016 | 3 | 51.6167 | 51.6167 | 38557.65 | 747 | 747
TC2 | SF | 35 | 1000 | 2016-03-18 15:27 | 2016-03-20 14:17 | 0 | 795 | 747 | Waterwall (Furnace wall) A | F540As the boiler was coming back online from an outage due to a tube leak when anothe | Trimble | Outage | Coal | 3 | 2016 | 3 | 46.8333 | 46.8333 | 34984.5 | 747 | 747
TC2 | D1 | 36 | 1488 | 2016-03-21 19:30 | 2016-03-21 23:04 | 709 | 795 | 747 | Air heater (regenerative) | F660Swap from 2B Coal Mill to 2F Mill - due to airflow issues through Air Heater, load | Trimble | Derate | Coal | 3 | 2016 | 3 | 3.5667 | 0.38583 | 288.2136 | 80.8075 | 81
TC2 | D1 | 37 | 1488 | 2016-03-22 01:20 | 2016-03-22 06:22 | 775 | 795 | 747 | Air heater (regenerative) | F660Load was dropped due to high Air Heater Differential Pressure. | Trimble | Derate | Coal | 3 | 2016 | 3 | 5.0333 | 0.12662 | 94.5887 | 18.7925 | 19
TC2 | U1 | 38 | 1000 | 2016-03-22 06:22 | 2016-03-23 09:00 | 0 | 795 | 747 | Waterwall (Furnace wall) A | F540Boiler tube leak caused the unit to be taken offline. | Trimble | Outage | Coal | 3 | 2016 | 3 | 26.6333 | 26.6333 | 19895.1 | 747 | 747
TC2 | PO | 39 | 1812 | 2016-03-23 09:00 | 2016-04-28 22:30 | 0 | 795 | 747 | Boiler Inspections - scheduled or routine | F590Spring 2016 Planned Outage - multiple scopes in progress. | Trimble | Other | Coal | 3 | 2016 | 3 | 877.5 | 877.5 | 655492.5 | 747 | 747
TC2 | PE | 40 | 4307 | 2016-04-28 22:30 | 2016-04-30 01:27 | 0 | 795 | 747 | Automatic turbine control systems - electro-hydraulic - digital | F540Adaptor plate in EHC system was not sealed properly, requiring additional maintena | Trimble | Other | Coal | 3 | 2016 | 4 | 26.95 | 26.95 | 20131.65 | 747 | 747
TC2 | PE | 41 | 380 | 2016-04-30 01:27 | 2016-04-30 09:59 | 0 | 795 | 747 | Light-off (igniter) systems (including fuel supply) | F340Loss of 2A-4 Flame Scanner. | Trimble | Other | Coal | 3 | 2016 | 4 | 8.5333 | 8.5333 | 6374.4 | 747 | 747
TC2 | MO | 42 | 4240 | 2016-04-30 16:06 | 2016-05-09 06:47 | 0 | 795 | 747 | Bearings E | F780Unit was taken offline for high LP turbine bearing temperature. The Turbine crew c | Trimble | Maintenance | Coal | 3 | 2016 | 4 | 206.6833 | 206.6833 | 154392.45 | 747 | 747
TC2 | U1 | 43 | 4700 | 2016-05-09 09:45 | 2016-05-09 16:18 | 0 | 795 | 747 | Generator voltage control | F870Generator protection relay trip. | Trimble | Outage | Coal | 3 | 2016 | 5 | 6.55 | 6.55 | 4892.85 | 747 | 747
TC2 | D1 | 44 | 330 | 2016-05-10 | 2016-05-10 01:37 | 690 | 795 | 747 | Pulverizer coal leak (pulverizers only) | F540Derate due to three mills with coal leaks . | Trimble | Derate | Coal | 3 | 2016 | 5 | 1.6167 | 0.21352 | 159.5009 | 98.6604 | 99
TC2 | D1 | 45 | 330 | 2016-05-10 01:37 | 2016-05-10 05:00 | 650 | 795 | 747 | Pulverizer coal leak (pulverizers only) | F540Derate due to three mills with coal leaks. | Trimble | Derate | Coal | 3 | 2016 | 5 | 3.3833 | 0.61709 | 460.9632 | 136.2453 | 136
TC2 | D1 | 46 | 9600 | 2016-05-10 10:45 | 2016-05-10 18:31 | 685 | 795 | 747 | SO2 stack emissions (fossil) | FE00Load derated due to high SO2 emissions. | Trimble | Derate | Coal | 3 | 2016 | 5 | 7.7667 | 1.0746 | 802.7509 | 103.3585 | 103
TC2 | U1 | 47 | 799 | 2016-05-10 18:31 | 2016-05-13 05:10 | 0 | 795 | 747 | Other miscellaneous piping system problems | F540Unit taken offline to repair boiler drain leak. | Trimble | Outage | Coal | 3 | 2016 | 5 | 58.65 | 58.65 | 43811.55 | 747 | 747
TC2 | MO | 48 | 8560 | 2016-05-16 03:44 | 2016-05-18 06:29 | 0 | 795 | 747 | Electrostatic precipitator problems | F540Unit taken offline due to problems with WESP flue gas and water containment. | Trimble | Maintenance | Coal | 3 | 2016 | 5 | 50.75 | 50.75 | 37910.25 | 747 | 747
TC2 | D1 | 49 | 4500 | 2016-05-18 10:24 | 2016-05-18 12:20 | 290 | 795 | 747 | Rotor windings (including damper windings and fan blades on hydro units) | F870High vibration levels on Turbine-Generator bearing #9 caused the unit to be place | Trimble | Derate | Coal | 3 | 2016 | 5 | 1.9333 | 1.2281 | 917.3849 | 474.5094 | 475
TC2 | D1 | 50 | 4500 | 2016-05-18 12:20 | 2016-05-18 13:20 | 350 | 795 | 747 | Rotor windings (including damper windings and fan blades on hydro units) | F870High vibration levels on Turbine-Generator bearing #9 caused the unit to be place | Trimble | Derate | Coal | 3 | 2016 | 5 | 1 | 0.55975 | 418.1321 | 418.1321 | 418
TC2 | D1 | 51 | 4500 | 2016-05-18 13:20 | 2016-05-18 19:23 | 388 | 795 | 747 | Rotor windings (including damper windings and fan blades on hydro units) | F870High vibration levels on Turbine-Generator bearing #9 caused the unit to be place | Trimble | Derate | Coal | 3 | 2016 | 5 | 6.05 | 3.0973 | 2313.6798 | 382.4264 | 382
TC2 | U1 | 52 | 4500 | 2016-05-18 19:23 | 2016-05-19 08:26 | 0 | 795 | 747 | Rotor windings (including damper windings and fan blades on hydro units) | F870High vibration levels on Turbine-Generator bearing #9 caused the unit to be taken | Trimble | Outage | Coal | 3 | 2016 | 5 | 13.05 | 13.05 | 9748.35 | 747 | 747
TC2 | U1 | 53 | 4500 | 2016-05-19 11:17 | 2016-06-01 | 0 | 795 | 747 | Rotor windings (including damper windings and fan blades on hydro units) | F870Unit continued to have problems with bearing #9 vibration and tripped on low steam | Trimble | Outage | Coal | 3 | 2016 | 5 | 300.7167 | 300.7167 | 224635.35 | 747 | 747
TC2 | U1 | 61 | 4500 | 2016-06-01 | 2016-07-15 05:45 | 0 | 795 | 747 | Rotor windings (including damper windings and fan blades on hydro units) | F870Unit continued to have problems with bearing #9 vibration and tripped on low steam | Trimble | Outage | Coal | 3 | 2016 | 6 | 1061.75 | 1061.75 | 793127.25 | 747 | 747
TC2 | SF | 54 | 4609 | 2016-07-15 05:45 | 2016-07-15 07:59 | 0 | 795 | 747 | Other exciter problems | F420Unit was unable to startup due to missing components, the secondary fuses were not | Trimble | Outage | Coal | 3 | 2016 | 7 | 2.2333 | 2.2333 | 1668.3 | 747 | 747
TC2 | U1 | 55 | 3499 | 2016-07-15 12:45 | 2016-07-15 18:12 | 0 | 795 | 747 | Other feedwater system problems | F660The unit tripped due to low FW flow. | Trimble | Outage | Coal | 3 | 2016 | 7 | 5.45 | 5.45 | 4071.15 | 747 | 747
TC2 | D1 | 56 | 9616 | 2016-07-16 08:53 | 2016-07-16 09:00 | 561 | 795 | 747 | CO stack emissions | FE00Unit load was held due to CO emission levels and O2 probe problems. | Trimble | Derate | Coal | 3 | 2016 | 7 | 0.11667 | 0.03434 | 25.6517 | 219.8717 | 220
TC2 | D1 | 57 | 9616 | 2016-07-16 09:00 | 2016-07-16 12:00 | 499 | 795 | 747 | CO stack emissions | FE00Unit load was held due to CO emission levels and O2 probe problems. | Trimble | Derate | Coal | 3 | 2016 | 7 | 3 | 1.117 | 834.3849 | 278.1283 | 278
TC2 | D1 | 58 | 9616 | 2016-07-16 12:00 | 2016-07-16 13:00 | 569 | 795 | 747 | CO stack emissions | FE00Unit load was held due to CO emission levels and O2 probe problems. | Trimble | Derate | Coal | 3 | 2016 | 7 | 1 | 0.28428 | 212.3547 | 212.3547 | 212
TC2 | D1 | 59 | 9616 | 2016-07-16 13:00 | 2016-07-16 17:45 | 657 | 795 | 747 | CO stack emissions | FE00Unit load was held due to CO emission levels and O2 probe problems. | Trimble | Derate | Coal | 3 | 2016 | 7 | 4.75 | 0.82453 | 615.9226 | 129.6679 | 130
TC2 | U1 | 60 | 1475 | 2016-07-18 12:32 | 2016-07-19 23:59 | 0 | 795 | 747 | Induced draft fan controls | F520The unit tripped due to a malfunctioned vibration sensor. The unit stayed offline | Trimble | Outage | Coal | 3 | 2016 | 7 | 35.45 | 35.45 | 26481.15 | 747 | 747
TC2 | D1 | 62 | 312 | 2016-07-25 22:00 | 2016-07-26 01:00 | 655 | 795 | 747 | Pulverizer mill classifiers | F340A problem with the 2F Coal Mill classifiers caused an derate when trying to swap m | Trimble | Derate | Coal | 3 | 2016 | 7 | 3 | 0.5283 | 394.6415 | 131.5472 | 132
TC2 | U1 | 63 | 1488 | 2016-07-31 07:42 | 2016-07-31 18:56 | 0 | 795 | 747 | Air heater (regenerative) | FP00The unit came offline due to the loss of the 2A Main Air Heater drive motor during | Trimble | Outage | Coal | 3 | 2016 | 7 | 11.2333 | 11.2333 | 8391.3 | 747 | 747
TC2 | U1 | 64 | 3681 | 2016-07-31 19:19 | 2016-08-01 02:59 | 0 | 795 | 747 | Other voltage system breakers | F340When transferring the 14kV 2B bus to the 2B Main Aux main breaker the 14kV 2B main | Trimble | Outage | Coal | 3 | 2016 | 7 | 7.6667 | 7.6667 | 5727 | 747 | 747
TC2 | NC | 65 | 8810 | 2016-08-04 06:00 | 2016-08-04 18:00 | 0 | 795 | 747 | SCR NOx Reactor | F790Non-curtailing derate for SCR tuning during full load. | Trimble | Other | Coal | 3 | 2016 | 8 | 12 | 12 | 8964 | 747 | 747
TC2 | NC | 66 | 9999 | 2016-08-09 10:00 | 2016-08-09 21:00 | 0 | 795 | 747 | Total unit performance testing (use appropriate codes for individual component testing) | F790Non-curtailing derate for unit heat rate testing. | Trimble | Other | Coal | 3 | 2016 | 8 | 11 | 11 | 8217 | 747 | 747
TC2 | PD | 67 | 1190 | 2016-08-14 02:00 | 2016-08-14 11:00 | 469 | 795 | 747 | Other tube slagging or fouling | FS00Planned derate for boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 8 | 9 | 3.6906 | 2756.8528 | 306.317 | 306
TC2 | PD | 68 | 1190 | 2016-08-21 02:00 | 2016-08-21 06:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for routine boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 8 | 4 | 1.7409 | 1300.4377 | 325.1094 | 325
TC2 | PD | 69 | 1190 | 2016-08-27 | 2016-08-27 09:00 | 400 | 795 | 747 | Other tube slagging or fouling | FS00Planned Derate for routine boiler deslag and safety valve setting. | Trimble | Derate | Coal | 3 | 2016 | 8 | 9 | 4.4717 | 3340.3585 | 371.1509 | 371
TC2 | PD | 70 | 100 | 2016-09-01 01:00 | 2016-09-01 03:00 | 755 | 795 | 747 | Bunker gates | F610Load was dropped due to a mill swap and temperature control on the unit. The spare | Trimble | Derate | Coal | 3 | 2016 | 9 | 2 | 0.10063 | 75.1698 | 37.5849 | 38
TC2 | PD | 71 | 3420 | 2016-09-03 00:01 | 2016-09-03 05:00 | 698 | 795 | 747 | Feedwater piping and supports | F280Unit was placed on a planned derate to repair a cracked nipple connection on the 7 | Trimble | Derate | Coal | 3 | 2016 | 9 | 4.9833 | 0.60803 | 454.1979 | 91.1434 | 91
TC2 | PD | 72 | 1190 | 2016-09-04 | 2016-09-04 07:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00Unit was placed on a Planned Derate for a boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 9 | 7 | 3.0553 | 2282.3434 | 326.0491 | 326
TC2 | PD | 73 | 1190 | 2016-09-11 | 2016-09-11 01:31 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for a routine boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 9 | 1.5167 | 0.66199 | 494.5077 | 326.0491 | 326
TC2 | U1 | 74 | 4311 | 2016-09-11 01:31 | 2016-09-11 14:58 | 0 | 795 | 747 | Steam Turbine Control System - hardware problems (including card failure) | F400A problem with the B Main Steam Control Vavle positioning feedback sensor caused a | Trimble | Outage | Coal | 3 | 2016 | 9 | 13.45 | 13.45 | 10047.15 | 747 | 747
TC2 | PD | 75 | 1190 | 2016-09-25 00:01 | 2016-09-25 10:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a planned derate for a scheduled boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 9 | 9.9833 | 4.3575 | 3255.0564 | 326.0491 | 326
TC2 | U1 | 76 | 267 | 2016-09-27 06:46 | 2016-09-27 14:43 | 0 | 795 | 747 | Primary air flow instrumentation | F160The unit was tripped when a plug on a Primary Air transmitter reference line vibra | Trimble | Outage | Coal | 3 | 2016 | 9 | 7.95 | 7.95 | 5938.65 | 747 | 747
TC2 | PD | 77 | 1190 | 2016-10-02 00:01 | 2016-10-02 09:30 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a planned derate for routine boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 10 | 9.4833 | 4.1393 | 3092.0319 | 326.0491 | 326
TC2 | PD | 78 | 9999 | 2016-10-08 19:00 | 2016-10-09 02:12 | 448 | 795 | 747 | Total unit performance testing (use appropriate codes for individual component testing) | F790Planned Derate for Incremental Heat Rate curve testing. During this time, a boiler | Trimble | Derate | Coal | 3 | 2016 | 10 | 7.2 | 3.1426 | 2347.5532 | 326.0491 | 326
TC2 | D1 | 79 | 4311 | 2016-10-09 02:12 | 2016-10-09 10:00 | 440 | 795 | 747 | Steam Turbine Control System - hardware problems (including card failure) | F340The 2B Main Steam control valve had an additional LVDT fail, resulting in one of t | Trimble | Derate | Coal | 3 | 2016 | 10 | 7.8 | 3.483 | 2601.8151 | 333.566 | 334
TC2 | D1 | 80 | 4311 | 2016-10-09 15:30 | 2016-10-10 12:00 | 700 | 795 | 747 | Steam Turbine Control System - hardware problems (including card failure) | F340Continued problems with the 2B Main Steam control valve LVDT's. After jumpering t | Trimble | Derate | Coal | 3 | 2016 | 10 | 20.5 | 2.4497 | 1829.9151 | 89.2642 | 89
TC2 | D1 | 81 | 4311 | 2016-10-10 12:00 | 2016-10-16 00:01 | 778 | 795 | 747 | Steam Turbine Control System - hardware problems (including card failure) | F340Continued problems with the 2B Main Steam control valve LVDT's. After jumpering t | Trimble | Derate | Coal | 3 | 2016 | 10 | 132.0167 | 2.823 | 2108.7794 | 15.9736 | 16
TC2 | PD | 82 | 1190 | 2016-10-16 00:01 | 2016-10-16 08:46 | 448 | 795 | 747 | Other tube slagging or fouling | FS00Planned Derate for boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 10 | 8.75 | 3.8192 | 2852.9292 | 326.0491 | 326
TC2 | D1 | 83 | 310 | 2016-10-16 08:46 | 2016-10-16 09:38 | 585 | 795 | 747 | Pulverizer mills | F340The 2F Coal Mill breaker was not engaging and the unit was placed on a derate whil | Trimble | Derate | Coal | 3 | 2016 | 10 | 0.86667 | 0.22893 | 171.0113 | 197.3208 | 197
TC2 | D1 | 84 | 4311 | 2016-10-16 09:38 | 2016-10-23 00:01 | 778 | 795 | 747 | Steam Turbine Control System - hardware problems (including card failure) | F340The 2B Main Steam control valve had an additional LVDT fail, resulting in one of t | Trimble | Derate | Coal | 3 | 2016 | 10 | 158.3833 | 3.3868 | 2529.9496 | 15.9736 | 16
TC2 | PD | 85 | 1190 | 2016-10-23 00:01 | 2016-10-23 08:58 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was on a Planned Derate for a routine boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 10 | 8.95 | 3.9065 | 2918.1391 | 326.0491 | 326
TC2 | D1 | 86 | 310 | 2016-10-23 08:58 | 2016-10-23 13:43 | 670 | 795 | 747 | Pulverizer mills | F520When coming back to normal operation from deslag, issues with the 2C and 2F Mills | Trimble | Derate | Coal | 3 | 2016 | 10 | 4.75 | 0.74686 | 557.9009 | 117.4528 | 117
TC2 | D1 | 87 | 4311 | 2016-10-23 13:43 | 2016-10-30 | 778 | 795 | 747 | Steam Turbine Control System - hardware problems (including card failure) | F340The 2B Main Steam control valve had an additional LVDT fail, resulting in one of t | Trimble | Derate | Coal | 3 | 2016 | 10 | 154.2833 | 3.2991 | 2464.4579 | 15.9736 | 16
TC2 | PD | 88 | 1190 | 2016-10-30 | 2016-10-30 08:46 | 448 | 795 | 747 | Other tube slagging or fouling | FS00Planned Derate for a routine boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 10 | 8.7667 | 3.8265 | 2858.3634 | 326.0491 | 326
TC2 | U1 | 89 | 4311 | 2016-10-30 08:46 | 2016-10-30 21:26 | 0 | 795 | 747 | Steam Turbine Control System - hardware problems (including card failure) | F860When coming back up to full load from the routine deslag, the third and final LVDT | Trimble | Outage | Coal | 3 | 2016 | 10 | 12.6667 | 12.6667 | 9462 | 747 | 747
TC2 | U1 | 90 | 3431 | 2016-10-30 22:03 | 2016-10-31 01:41 | 0 | 795 | 747 | Other feedwater valves | F400While coming back online, the Feedwater Discharge valve closed and the unit trippe | Trimble | Outage | Coal | 3 | 2016 | 10 | 3.6333 | 3.6333 | 2714.1 | 747 | 747
TC2 | U1 | 91 | 3431 | 2016-10-31 02:17 | 2016-10-31 09:00 | 0 | 795 | 747 | Other feedwater valves | F400Continued issues with feedwater flow as the unit was coming back online. The unit | Trimble | Outage | Coal | 3 | 2016 | 10 | 6.7167 | 6.7167 | 5017.35 | 747 | 747
TC2 | D1 | 92 | 4311 | 2016-10-31 15:00 | 2016-11-01 08:00 | 778 | 795 | 747 | Steam Turbine Control System - hardware problems (including card failure) | F340The unit was held at a derate while sorting through the past LVDT issues on the # | Trimble | Derate | Coal | 3 | 2016 | 10 | 17 | 0.36352 | 271.5509 | 15.9736 | 16
TC2 | PD | 93 | 1190 | 2016-11-05 | 2016-11-05 09:30 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was on a Planned Derate for routine boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 11 | 9.5 | 4.1465 | 3097.466 | 326.0491 | 326
TC2 | NC | 94 | 8700 | 2016-11-08 08:00 | 2016-11-08 15:33 | 0 | 795 | 747 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2016 | 11 | 7.55 | 7.55 | 5639.85 | 747 | 747
TC2 | NC | 95 | 8700 | 2016-11-09 08:00 | 2016-11-09 16:00 | 0 | 795 | 747 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2016 | 11 | 8 | 8 | 5976 | 747 | 747
TC2 | NC | 96 | 8700 | 2016-11-10 08:00 | 2016-11-10 15:10 | 0 | 795 | 747 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2016 | 11 | 7.1667 | 7.1667 | 5353.5 | 747 | 747
TC2 | PD | 97 | 1190 | 2016-11-13 | 2016-11-13 09:30 | 448 | 795 | 747 | Other tube slagging or fouling | FS00Planned Derate for routine boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 11 | 9.5 | 4.1465 | 3097.466 | 326.0491 | 326
TC2 | PD | 98 | 1190 | 2016-11-19 | 2016-11-19 09:30 | 448 | 795 | 747 | Other tube slagging or fouling | FS00Planned Derate for routine boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 11 | 9.5 | 4.1465 | 3097.466 | 326.0491 | 326
TC2 | PD | 99 | 1190 | 2016-11-26 | 2016-11-26 09:30 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for a routine boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 11 | 9.5 | 4.1465 | 3097.466 | 326.0491 | 326
TC2 | PD | 100 | 1190 | 2016-12-04 | 2016-12-04 09:30 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2016 | 12 | 9.5 | 4.1465 | 3097.466 | 326.0491 | 326
TC2 | PD | 101 | 1190 | 2016-12-11 | 2016-12-11 09:30 | 449 | 795 | 747 | Other tube slagging or fouling | FS00Planned Derate for a routine boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 12 | 9.5 | 4.1346 | 3088.5396 | 325.1094 | 325
TC2 | D1 | 102 | 267 | 2016-12-12 13:54 | 2016-12-12 18:20 | 625 | 795 | 747 | Primary air flow instrumentation | F120The 2A Coal Mill Primary Air transmitter was plugged and caused the mill to trip o | Trimble | Derate | Coal | 3 | 2016 | 12 | 4.4333 | 0.94801 | 708.1623 | 159.7358 | 160
TC2 | PD | 103 | 1190 | 2016-12-17 22:00 | 2016-12-18 07:30 | 449 | 795 | 747 | Other tube slagging or fouling | FS00Planned Derate for a routine boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 12 | 9.5 | 4.1346 | 3088.5396 | 325.1094 | 325
TC2 | D1 | 104 | 8006 | 2016-12-22 14:45 | 2016-12-22 19:00 | 649 | 795 | 747 | Weigh feeders B | F340The limestone rock silo had bolt failures, causing it to rest against the feeder a | Trimble | Derate | Coal | 3 | 2016 | 12 | 4.25 | 0.7805 | 583.0358 | 137.1849 | 137
TC2 | D1 | 105 | 312 | 2016-12-22 19:00 | 2016-12-22 23:50 | 489 | 795 | 747 | Pulverizer mill classifiers | F780While the unit was still on a derate due to the Reactant Prep issues, the 2E Mill | Trimble | Derate | Coal | 3 | 2016 | 12 | 4.8333 | 1.8604 | 1389.7019 | 287.5245 | 288
TC2 | PD | 106 | 1190 | 2016-12-23 | 2016-12-23 09:30 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for routine boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 12 | 9.5 | 4.1346 | 3088.5396 | 325.1094 | 325
TC2 | D1 | 107 | 346 | 2016-12-26 10:42 | 2016-12-26 19:00 | 649 | 795 | 747 | Pulverizer pyrite removal system | F120The unit was on a derate due to having only four of the six coal mills available f | Trimble | Derate | Coal | 3 | 2016 | 12 | 8.3 | 1.5243 | 1138.6347 | 137.1849 | 137
TC2 | D1 | 108 | 1488 | 2016-12-29 09:01 | 2016-12-29 14:00 | 759 | 795 | 747 | Air heater (regenerative) | F660The unit was placed on a derate to keep the A FD Fan from reaching its stall point | Trimble | Derate | Coal | 3 | 2016 | 12 | 4.9833 | 0.22566 | 168.5683 | 33.8264 | 34
TC2 | D1 | 109 | 1488 | 2016-12-29 14:13 | 2016-12-29 19:00 | 774 | 795 | 747 | Air heater (regenerative) | F660The unit was placed on a derate to keep the A FD Fan from reaching its stall point | Trimble | Derate | Coal | 3 | 2016 | 12 | 4.7833 | 0.12635 | 94.3851 | 19.7321 | 20
TC2 | D1 | 110 | 1488 | 2016-12-29 19:00 | 2016-12-29 23:00 | 789 | 795 | 747 | Air heater (regenerative) | F660The unit was placed on a derate to keep the A FD Fan from reaching its stall point | Trimble | Derate | Coal | 3 | 2016 | 12 | 4 | 0.030189 | 22.5509 | 5.6377 | 6
TC2 | D1 | 111 | 1488 | 2016-12-29 23:00 | 2016-12-30 01:00 | 689 | 795 | 747 | Air heater (regenerative) | F660The unit was placed on a derate to swap coal mills. This was done due to airflow r | Trimble | Derate | Coal | 3 | 2016 | 12 | 2 | 0.26667 | 199.2 | 99.6 | 100
TC2 | D1 | 112 | 1488 | 2016-12-30 01:00 | 2016-12-30 08:24 | 789 | 795 | 747 | Air heater (regenerative) | F660The unit was placed on a derate to keep the A FD Fan from reaching its stall point | Trimble | Derate | Coal | 3 | 2016 | 12 | 7.4 | 0.055849 | 41.7192 | 5.6377 | 6
TC2 | PD | 113 | 1190 | 2016-12-30 22:00 | 2016-12-31 07:30 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for routine boiler deslag. | Trimble | Derate | Coal | 3 | 2016 | 12 | 9.5 | 4.1346 | 3088.5396 | 325.1094 | 325
TC2 | D1 | 1 | 1488 | 2017-01-02 18:19 | 2017-01-10 09:00 | 759 | 795 | 747 | Air heater (regenerative) | F660The unit was placed on a derate to keep the A FD Fan from reaching its stall point | Trimble | Derate | Coal | 3 | 2017 | 1 | 182.6833 | 8.2725 | 6179.5223 | 33.8264 | 34
TC2 | NC | 2 | 8601 | 2017-01-07 07:00 | 2017-01-07 17:00 | 0 | 795 | 747 | SO3 mitigation | F790Non-curtailing event for HCl/SO3 removal levels testing. The unit was derated due | Trimble | Other | Coal | 3 | 2017 | 1 | 10 | 10 | 7470 | 747 | 747
TC2 | NC | 3 | 8601 | 2017-01-08 07:03 | 2017-01-08 17:00 | 0 | 795 | 747 | SO3 mitigation | F790Non-curtailing event for HCl/SO3 removal levels testing. The unit was derated due | Trimble | Other | Coal | 3 | 2017 | 1 | 9.95 | 9.95 | 7432.65 | 747 | 747
TC2 | D1 | 4 | 1488 | 2017-01-10 09:00 | 2017-01-12 05:43 | 709 | 795 | 747 | Air heater (regenerative) | F660The unit was placed on a derate to keep the A FD Fan from reaching its stall point | Trimble | Derate | Coal | 3 | 2017 | 1 | 44.7167 | 4.8373 | 3613.4442 | 80.8075 | 81
TC2 | MO | 5 | 1493 | 2017-01-12 05:43 | 2017-01-15 06:31 | 0 | 795 | 747 | Air heater fouling (regenerative) | FC00The unit was placed on a Maintenance Outage for Air Heater washing to remedy the e | Trimble | Maintenance | Coal | 3 | 2017 | 1 | 72.8 | 72.8 | 54381.6 | 747 | 747
TC2 | D1 | 6 | 346 | 2017-01-17 10:30 | 2017-01-17 12:00 | 759 | 795 | 747 | Pulverizer pyrite removal system | F120The unit was placed on a derate when the 2F Mill needed to be taken out of service | Trimble | Derate | Coal | 3 | 2017 | 1 | 1.5 | 0.067925 | 50.7396 | 33.8264 | 34
TC2 | PD | 7 | 1190 | 2017-01-22 | 2017-01-22 09:30 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for a routine boiler deslag. | Trimble | Derate | Coal | 3 | 2017 | 1 | 9.5 | 4.1346 | 3088.5396 | 325.1094 | 325
TC2 | PD | 8 | 1190 | 2017-01-28 22:00 | 2017-01-29 07:30 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for a routine boiler deslag. | Trimble | Derate | Coal | 3 | 2017 | 1 | 9.5 | 4.1346 | 3088.5396 | 325.1094 | 325
TC2 | PD | 9 | 1190 | 2017-02-04 22:00 | 2017-02-05 09:30 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 2 | 11.5 | 5.005 | 3738.7585 | 325.1094 | 325
TC2 | NC | 10 | 9999 | 2017-02-09 07:30 | 2017-02-09 14:30 | 0 | 795 | 747 | Total unit performance testing (use appropriate codes for individual component testing) | F790Non-curtailing event for a Unit Capability Test while the unit was available for f | Trimble | Other | Coal | 3 | 2017 | 2 | 7 | 7 | 5229 | 747 | 747
TC2 | D1 | 11 | 310 | 2017-02-12 11:30 | 2017-02-12 13:00 | 769 | 795 | 747 | Pulverizer mills | F340The 2C Mill began to have performance issues, and an additional mill was prepared | Trimble | Derate | Coal | 3 | 2017 | 2 | 1.5 | 0.049057 | 36.6453 | 24.4302 | 24
TC2 | D1 | 12 | 890 | 2017-02-14 09:30 | 2017-02-14 14:38 | 449 | 795 | 747 | Bottom ash systems (wet or dry) | F340The unit was placed on a derate due to faulty controls in the Submerged Scraper Co | Trimble | Derate | Coal | 3 | 2017 | 2 | 5.1333 | 2.2341 | 1668.8951 | 325.1094 | 325
TC2 | U1 | 13 | 890 | 2017-02-14 14:38 | 2017-02-17 02:05 | 0 | 795 | 747 | Bottom ash systems (wet or dry) | F340The unit was placed on a Forced Outage due to the previous event involving the Sub | Trimble | Outage | Coal | 3 | 2017 | 2 | 59.45 | 59.45 | 44409.15 | 747 | 747
TC2 | U1 | 14 | 4605 | 2017-02-21 22:30 | 2017-02-25 23:32 | 0 | 795 | 747 | Exciter transformer | F540A water leak from the roof of the turbine building ran onto the TC2 Exciter Transf | Trimble | Outage | Coal | 3 | 2017 | 2 | 97.0333 | 97.0333 | 72483.9 | 747 | 747
TC2 | PO | 15 | 380 | 2017-02-25 23:32 | 2017-04-03 | 0 | 795 | 747 | Light-off (igniter) systems (including fuel supply) | F590Planned 2017 Spring Outage for TC2 with multiple scopes in progress. A primary sco | Trimble | Other | Coal | 3 | 2017 | 2 | 864.4667 | 864.4667 | 645756.6 | 747 | 747
TC2 | PE | 16 | 380 | 2017-04-03 | 2017-04-09 23:46 | 0 | 795 | 747 | Light-off (igniter) systems (including fuel supply) | F790Planned Extension for testing on the newly installed Gas Igniter system. | Trimble | Other | Coal | 3 | 2017 | 4 | 167.7667 | 167.7667 | 125321.7 | 747 | 747
TC2 | D1 | 17 | 8750 | 2017-04-11 04:23 | 2017-04-11 12:30 | 685 | 795 | 747 | O2 analyzer problems | F520The unit was placed on a derate when C0 readings were out of acceptable ranges. Th | Trimble | Derate | Coal | 3 | 2017 | 4 | 8.1167 | 1.1231 | 838.9264 | 103.3585 | 103
TC2 | NC | 18 | 8812 | 2017-04-18 07:00 | 2017-04-18 19:00 | 0 | 795 | 747 | SCR NOxCatalyst | F790The unit was available for full load during a Non-Curtailing SCR testing event. | Trimble | Other | Coal | 3 | 2017 | 4 | 12 | 12 | 8964 | 747 | 747
TC2 | D1 | 19 | 1190 | 2017-04-19 19:30 | 2017-04-20 04:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a derate for boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 4 | 8.5 | 3.7101 | 2771.417 | 326.0491 | 326
TC2 | PD | 20 | 1190 | 2017-04-22 23:00 | 2017-04-23 09:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 4 | 10 | 4.3648 | 3260.4906 | 326.0491 | 326
TC2 | U1 | 21 | 1090 | 2017-04-26 18:30 | 2017-05-03 17:01 | 0 | 795 | 747 | Other boiler tube leaks | F540The unit was placed on a Forced Outage for repairs to identified tube leaks. | Trimble | Outage | Coal | 3 | 2017 | 4 | 166.5167 | 166.5167 | 124387.95 | 747 | 747
TC2 | D1 | 22 | 3344 | 2017-05-04 05:30 | 2017-05-04 07:30 | 708 | 795 | 747 | Deaerator (including level control) | F400During startup, the Deaerator level went low and load was dropped until an accepta | Trimble | Derate | Coal | 3 | 2017 | 5 | 2 | 0.21887 | 163.4943 | 81.7472 | 82
TC2 | PD | 23 | 3339 | 2017-05-09 | 2017-05-09 04:00 | 748 | 795 | 747 | LP heater head leaks | F540Load was dropped to isolate the 6A Heater head to address head bolt issues. | Trimble | Derate | Coal | 3 | 2017 | 5 | 4 | 0.23648 | 176.6491 | 44.1623 | 44
TC2 | D1 | 24 | 3339 | 2017-05-09 21:20 | 2017-05-09 23:00 | 743 | 795 | 747 | LP heater head leaks | F540The unit was placed on a derate due to low Deaerator level. The DA level was influ | Trimble | Derate | Coal | 3 | 2017 | 5 | 1.6667 | 0.10901 | 81.434 | 48.8604 | 49
TC2 | D1 | 25 | 3339 | 2017-05-09 23:00 | 2017-05-10 07:00 | 758 | 795 | 747 | LP heater head leaks | F540The unit was placed on a derate due to low Deaerator level. The DA level was influ | Trimble | Derate | Coal | 3 | 2017 | 5 | 8 | 0.37233 | 278.1283 | 34.766 | 35
TC2 | D1 | 26 | 3339 | 2017-05-10 07:00 | 2017-05-11 14:00 | 748 | 795 | 747 | LP heater head leaks | F540The unit was placed on a derate due to low Deaerator level. The DA level was influ | Trimble | Derate | Coal | 3 | 2017 | 5 | 31 | 1.8327 | 1369.0302 | 44.1623 | 44
TC2 | PD | 27 | 1190 | 2017-05-21 | 2017-05-21 10:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 5 | 10 | 4.3648 | 3260.4906 | 326.0491 | 326
TC2 | D1 | 28 | 1455 | 2017-05-22 21:45 | 2017-05-23 09:00 | 755 | 795 | 747 | Induced draft fans | F850Due to high vibration levels in the outboard bearing of the 2A ID Fan, load was dr | Trimble | Derate | Coal | 3 | 2017 | 5 | 11.25 | 0.56604 | 422.8302 | 37.5849 | 38
TC2 | PD | 29 | 1190 | 2017-05-28 | 2017-05-28 10:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 5 | 10 | 4.3648 | 3260.4906 | 326.0491 | 326
TC2 | U1 | 30 | 3410 | 2017-05-31 13:51 | 2017-06-04 02:31 | 0 | 795 | 747 | Feedwater pump | F520The A TDBFP tripped after receiving incorrect flow feedback from the DCS, tripping | Trimble | Outage | Coal | 3 | 2017 | 5 | 84.6667 | 84.6667 | 63246 | 747 | 747
TC2 | U1 | 31 | 3410 | 2017-06-04 15:46 | 2017-06-08 15:18 | 0 | 795 | 747 | Feedwater pump | FV00The unit tripped when it experienced a loss of feedwater flow due to a trip on the | Trimble | Outage | Coal | 3 | 2017 | 6 | 95.5333 | 95.5333 | 71363.4 | 747 | 747
TC2 | SF | 32 | 4700 | 2017-06-08 15:18 | 2017-06-08 17:28 | 0 | 795 | 747 | Generator voltage control | F870The Generator Differential alarm came in and caused the unit to fail to start. | Trimble | Outage | Coal | 3 | 2017 | 6 | 2.1667 | 2.1667 | 1618.5 | 747 | 747
TC2 | D1 | 33 | 3413 | 2017-06-08 17:29 | 2017-06-09 14:00 | 765 | 795 | 747 | Feedwater pump coupling and drive shaft | FU00The A TDBFP was out of service during this timeframe. The unit ran with the MDBFP | Trimble | Derate | Coal | 3 | 2017 | 6 | 20.5167 | 0.77421 | 578.3377 | 28.1887 | 28
TC2 | D1 | 34 | 3413 | 2017-06-09 14:00 | 2017-06-14 | 755 | 795 | 747 | Feedwater pump coupling and drive shaft | FV00During this timeframe, the A TDBFP was out of service. In addition, the MDBFP was | Trimble | Derate | Coal | 3 | 2017 | 6 | 106 | 5.3333 | 3984 | 37.5849 | 38
TC2 | PD | 35 | 3410 | 2017-06-14 | 2017-06-14 03:30 | 658 | 795 | 747 | Feedwater pump | F790The unit was placed on a Planned Derate for testing of the repaired 2A TDBFP. | Trimble | Derate | Coal | 3 | 2017 | 6 | 3.5 | 0.60314 | 450.5491 | 128.7283 | 129
TC2 | PD | 36 | 1190 | 2017-06-18 | 2017-06-18 10:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 6 | 10 | 4.3522 | 3251.0943 | 325.1094 | 325
TC2 | PD | 37 | 1190 | 2017-06-25 | 2017-06-25 10:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00Planned Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 6 | 10 | 4.3522 | 3251.0943 | 325.1094 | 325
TC2 | PD | 38 | 1190 | 2017-07-02 | 2017-07-02 07:05 | 449 | 795 | 747 | Other tube slagging or fouling | FS00Planned Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 7 | 7.0833 | 3.0828 | 2302.8585 | 325.1094 | 325
TC2 | D1 | 39 | 897 | 2017-07-02 07:05 | 2017-07-03 07:00 | 435 | 795 | 747 | Bottom ash rotary (drag chain type) conveyor and motor | F060A Submerged Scraper Conveyor chain link broke and caused the unit to be placed on | Trimble | Derate | Coal | 3 | 2017 | 7 | 23.9167 | 10.8302 | 8090.1509 | 338.2642 | 338
TC2 | D1 | 40 | 3439 | 2017-07-03 10:38 | 2017-07-04 22:00 | 754 | 795 | 747 | HP heater head leaks | F540The unit was placed on a derate due to a leak in the 6A Feedwater Heater head. Loa | Trimble | Derate | Coal | 3 | 2017 | 7 | 35.3667 | 1.8239 | 1362.4842 | 38.5245 | 39
TC2 | D1 | 41 | 3439 | 2017-07-04 22:00 | 2017-07-05 03:30 | 485 | 795 | 747 | HP heater head leaks | F540The unit was placed on a derate due to a leak in the 6A Feedwater Heater head. Loa | Trimble | Derate | Coal | 3 | 2017 | 7 | 5.5 | 2.1447 | 1602.0566 | 291.283 | 291
TC2 | D1 | 42 | 3439 | 2017-07-05 03:30 | 2017-07-06 13:38 | 754 | 795 | 747 | HP heater head leaks | F540The unit was placed on a derate due to a leak in the 6A Feedwater Heater head. Loa | Trimble | Derate | Coal | 3 | 2017 | 7 | 34.1333 | 1.7603 | 1314.9706 | 38.5245 | 39
TC2 | PD | 43 | 1190 | 2017-07-09 | 2017-07-09 10:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Planned Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 7 | 10 | 4.3522 | 3251.0943 | 325.1094 | 325
TC2 | D4 | 44 | 1190 | 2017-07-16 | 2017-07-16 10:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 7 | 10 | 4.3522 | 3251.0943 | 325.1094 | 325
TC2 | D4 | 45 | 1190 | 2017-07-22 23:00 | 2017-07-23 11:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 7 | 12 | 5.2226 | 3901.3132 | 325.1094 | 325
TC2 | U2 | 46 | 1000 | 2017-07-30 00:53 | 2017-08-03 19:06 | 0 | 795 | 747 | Waterwall (Furnace wall) A | F540The unit was placed on a Forced Outage after the boiler experienced a waterwall tu | Trimble | Outage | Coal | 3 | 2017 | 7 | 114.2167 | 114.2167 | 85319.85 | 747 | 747
TC2 | D1 | 47 | 3431 | 2017-08-04 03:00 | 2017-08-04 05:00 | 449 | 795 | 747 | Other feedwater valves | F340TC2 experienced an Immediate Derate when the 2A TDBFP recirc valve would not respo | Trimble | Derate | Coal | 3 | 2017 | 8 | 2 | 0.87044 | 650.2189 | 325.1094 | 325
TC2 | D1 | 48 | 3431 | 2017-08-04 05:00 | 2017-08-04 08:00 | 390 | 795 | 747 | Other feedwater valves | F340TC2 experienced an Immediate Derate when the 2A TDBFP recirc valve would not respo | Trimble | Derate | Coal | 3 | 2017 | 8 | 3 | 1.5283 | 1141.6415 | 380.5472 | 381
TC2 | NC | 49 | 8700 | 2017-08-09 21:00 | 2017-08-10 06:00 | 0 | 795 | 747 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2017 | 8 | 9 | 9 | 6723 | 747 | 747
TC2 | NC | 50 | 8700 | 2017-08-10 20:00 | 2017-08-11 05:00 | 0 | 795 | 747 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2017 | 8 | 9 | 9 | 6723 | 747 | 747
TC2 | D4 | 51 | 1190 | 2017-08-13 | 2017-08-13 10:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 8 | 10 | 4.3522 | 3251.0943 | 325.1094 | 325
TC2 | D4 | 52 | 1190 | 2017-08-20 | 2017-08-20 10:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 8 | 10 | 4.3522 | 3251.0943 | 325.1094 | 325
TC2 | NC | 53 | 8700 | 2017-08-23 07:00 | 2017-08-23 18:00 | 0 | 795 | 747 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2017 | 8 | 11 | 11 | 8217 | 747 | 747
TC2 | NC | 54 | 8700 | 2017-08-24 07:00 | 2017-08-24 18:00 | 0 | 795 | 747 | CEMS Certification and Recertification | F790Non-curtailing event for a RATA test, an audit of the unit's CEMS monitors. The un | Trimble | Other | Coal | 3 | 2017 | 8 | 11 | 11 | 8217 | 747 | 747
TC2 | D4 | 55 | 1190 | 2017-08-27 | 2017-08-27 10:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 8 | 10 | 4.3522 | 3251.0943 | 325.1094 | 325
TC2 | D4 | 56 | 1190 | 2017-09-03 | 2017-09-03 10:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00Routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 9 | 10 | 4.3648 | 3260.4906 | 326.0491 | 326
TC2 | D1 | 57 | 3245 | 2017-09-07 23:35 | 2017-09-08 04:00 | 700 | 795 | 747 | Other cooling tower problems | F540The TC2 Cooling Tower basin level came in low after a leak occurred in a makeup li | Trimble | Derate | Coal | 3 | 2017 | 9 | 4.4167 | 0.52778 | 394.25 | 89.2642 | 89
TC2 | D4 | 58 | 1190 | 2017-09-10 | 2017-09-10 06:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 9 | 6 | 2.6189 | 1956.2943 | 326.0491 | 326
TC2 | PD | 59 | 9999 | 2017-09-10 06:00 | 2017-09-10 06:30 | 430 | 795 | 747 | Total unit performance testing (use appropriate codes for individual component testing) | F790TC2 was placed on a Planned Derate for annual heat rate testing. The unit was at v | Trimble | Derate | Coal | 3 | 2017 | 9 | 0.5 | 0.22956 | 171.4811 | 342.9623 | 343
TC2 | D1 | 60 | 310 | 2017-09-10 06:30 | 2017-09-10 06:52 | 478 | 795 | 747 | Pulverizer mills | F340TC2 was placed on a derate when the 2A Coal Mill had problems during its startup s | Trimble | Derate | Coal | 3 | 2017 | 9 | 0.36667 | 0.14621 | 109.2155 | 297.8604 | 298
TC2 | PD | 61 | 9999 | 2017-09-10 06:52 | 2017-09-10 15:04 | 650 | 795 | 747 | Total unit performance testing (use appropriate codes for individual component testing) | F790TC2 was placed on a Planned Derate for annual heat rate testing. The unit was at v | Trimble | Derate | Coal | 3 | 2017 | 9 | 8.2 | 1.4956 | 1117.2113 | 136.2453 | 136
TC2 | D4 | 62 | 1190 | 2017-09-17 | 2017-09-17 10:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 9 | 10 | 4.3648 | 3260.4906 | 326.0491 | 326
TC2 | U3 | 63 | 590 | 2017-09-22 23:57 | 2017-09-23 13:39 | 0 | 795 | 747 | Desuperheater/attemperator valves | F540The unit was placed on a Forced Outage due to a leak found in the superheat spray | Trimble | Outage | Coal | 3 | 2017 | 9 | 13.7 | 13.7 | 10233.9 | 747 | 747
TC2 | D4 | 64 | 1190 | 2017-10-01 | 2017-10-01 10:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00Maintenance Derate for routine boiler deslagging. The unit was returned to being a | Trimble | Derate | Coal | 3 | 2017 | 10 | 10 | 4.3648 | 3260.4906 | 326.0491 | 326
TC2 | D4 | 65 | 1190 | 2017-10-08 | 2017-10-08 10:00 | 435 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 10 | 10 | 4.5283 | 3382.6415 | 338.2642 | 338
TC2 | D1 | 66 | 310 | 2017-10-11 23:58 | 2017-10-12 07:00 | 493 | 795 | 747 | Pulverizer mills | F520Due to a failure in an I/O card, the B, D, and F Mills tripped and the unit was pl | Trimble | Derate | Coal | 3 | 2017 | 10 | 7.0333 | 2.6718 | 1995.8211 | 283.766 | 284
TC2 | D4 | 67 | 1190 | 2017-10-15 | 2017-10-15 10:00 | 435 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 10 | 10 | 4.5283 | 3382.6415 | 338.2642 | 338
TC2 | D4 | 68 | 1190 | 2017-10-22 | 2017-10-22 07:30 | 435 | 795 | 747 | Other tube slagging or fouling | FS00Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 10 | 7.5 | 3.3962 | 2536.9811 | 338.2642 | 338
TC2 | D1 | 69 | 310 | 2017-10-22 07:30 | 2017-10-22 07:57 | 435 | 795 | 747 | Pulverizer mills | FR00The unit was placed on a derate due to issues with the 2A Coal Mill. The unit was | Trimble | Derate | Coal | 3 | 2017 | 10 | 0.45 | 0.20377 | 152.2189 | 338.2642 | 338
TC2 | D4 | 70 | 1190 | 2017-10-22 07:57 | 2017-10-22 10:00 | 435 | 795 | 747 | Other tube slagging or fouling | FS00Maintenance Derate for routine boiler delsagging. | Trimble | Derate | Coal | 3 | 2017 | 10 | 2.05 | 0.9283 | 693.4415 | 338.2642 | 338
TC2 | D4 | 71 | 1190 | 2017-10-29 | 2017-10-29 09:55 | 448 | 795 | 747 | Other tube slagging or fouling | FS00Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 10 | 9.9167 | 4.3284 | 3233.3198 | 326.0491 | 326
TC2 | D1 | 72 | 300 | 2017-10-30 16:07 | 2017-10-30 17:47 | 625 | 795 | 747 | Pulverizer motors and drives | F340The unit was placed on a forced derate when the 2E Coal Mill motor failed to start | Trimble | Derate | Coal | 3 | 2017 | 10 | 1.6667 | 0.35639 | 266.2264 | 159.7358 | 160
TC2 | D4 | 73 | 1190 | 2017-11-04 | 2017-11-04 10:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 11 | 10 | 4.3648 | 3260.4906 | 326.0491 | 326
TC2 | D1 | 74 | 3504 | 2017-11-10 05:00 | 2017-11-10 10:50 | 748 | 795 | 747 | Heater drain valves | F410The unit was placed on an Immediate Derate when the 6B normal drain relay failed. | Trimble | Derate | Coal | 3 | 2017 | 11 | 5.8333 | 0.34486 | 257.6132 | 44.1623 | 44
TC2 | D4 | 75 | 1190 | 2017-11-11 22:00 | 2017-11-12 02:34 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for a routine boiler deslag. | Trimble | Derate | Coal | 3 | 2017 | 11 | 4.5667 | 1.9932 | 1488.9574 | 326.0491 | 326
TC2 | D1 | 76 | 310 | 2017-11-12 02:34 | 2017-11-12 03:10 | 292 | 795 | 747 | Pulverizer mills | F660The unit was placed on an immediate derate when the 2D Coal Mill tripped due to er | Trimble | Derate | Coal | 3 | 2017 | 11 | 0.6 | 0.37962 | 283.5781 | 472.6302 | 473
TC2 | D4 | 77 | 1190 | 2017-11-12 03:10 | 2017-11-12 07:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate to complete the routine boiler deslag. | Trimble | Derate | Coal | 3 | 2017 | 11 | 3.8333 | 1.6732 | 1249.8547 | 326.0491 | 326
TC2 | D1 | 78 | 85 | 2017-11-12 17:54 | 2017-11-12 18:40 | 625 | 795 | 747 | Bunker feeder coal scales | F520TC2 was placed on an immediate derate when the 2F Mill tripped due to a loss of co | Trimble | Derate | Coal | 3 | 2017 | 11 | 0.76667 | 0.16394 | 122.4642 | 159.7358 | 160
TC2 | D4 | 79 | 1190 | 2017-11-18 | 2017-11-18 10:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 11 | 10 | 4.3648 | 3260.4906 | 326.0491 | 326
TC2 | D4 | 80 | 1190 | 2017-11-26 | 2017-11-26 10:00 | 448 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for a routine boiler deslag. | Trimble | Derate | Coal | 3 | 2017 | 11 | 10 | 4.3648 | 3260.4906 | 326.0491 | 326
TC2 | D1 | 81 | 3399 | 2017-12-01 08:05 | 2017-12-01 13:51 | 790 | 795 | 747 | Other miscellaneous condensate system problems | F660The unit was de-rated due to Condensate flow issues. The condensdate control valve | Trimble | Derate | Coal | 3 | 2017 | 12 | 5.7667 | 0.036268 | 27.0925 | 4.6981 | 5
TC2 | D4 | 82 | 1190 | 2017-12-03 | 2017-12-03 10:00 | 430 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 12 | 10 | 4.5912 | 3429.6226 | 342.9623 | 343
TC2 | D1 | 83 | 9291 | 2017-12-08 14:30 | 2017-12-08 16:10 | 805 | 795 | 747 | Other fuel quality problems (not outside management control) | F600The unit was placed on an Immediate Derate due to fuel quality issues. | Trimble | Derate | Coal | 3 | 2017 | 12 | 1.6667 | -0.020964 | -15.6604 | 0 | 0
TC2 | D1 | 84 | 8750 | 2017-12-08 16:10 | 2017-12-08 18:00 | 765 | 795 | 747 | O2 analyzer problems | FE00Due to issues with the O2 probes, CO levels rose and load was dropped to accommoda | Trimble | Derate | Coal | 3 | 2017 | 12 | 1.8333 | 0.069182 | 51.6792 | 28.1887 | 28
TC2 | D1 | 85 | 9291 | 2017-12-08 18:00 | 2017-12-09 | 805 | 795 | 747 | Other fuel quality problems (not outside management control) | F600The unit was placed on an Immediate Derate due to fuel quality issues. | Trimble | Derate | Coal | 3 | 2017 | 12 | 6 | -0.075472 | -56.3774 | 0 | 0
TC2 | D4 | 86 | 1190 | 2017-12-09 | 2017-12-09 10:00 | 430 | 795 | 747 | Other tube slagging or fouling | FS00The unmti was placed on a Maintenance Derate for a routine boiler deslag. | Trimble | Derate | Coal | 3 | 2017 | 12 | 10 | 4.5912 | 3429.6226 | 342.9623 | 343
TC2 | D1 | 87 | 3344 | 2017-12-09 15:56 | 2017-12-10 00:17 | 800 | 795 | 747 | Deaerator (including level control) | F660The unit was placed on an Immediate Derate due to steam flow issues caused by the | Trimble | Derate | Coal | 3 | 2017 | 12 | 8.35 | -0.052516 | -39.2292 | 0 | 0
TC2 | U1 | 88 | 1000 | 2017-12-10 00:17 | 2017-12-13 14:00 | 0 | 795 | 747 | Waterwall (Furnace wall) A | F540The unit was placed on an Unplanned Outage due to multiple waterwall leaks, which | Trimble | Outage | Coal | 3 | 2017 | 12 | 85.7167 | 85.7167 | 64030.35 | 747 | 747
TC2 | D1 | 89 | 3431 | 2017-12-14 03:00 | 2017-12-16 | 755 | 795 | 747 | Other feedwater valves | F060Issues with the 2A TDBFP Recirculating Valve caused flow problems in the Feedwater | Trimble | Derate | Coal | 3 | 2017 | 12 | 45 | 2.2642 | 1691.3208 | 37.5849 | 38
TC2 | D4 | 90 | 1190 | 2017-12-16 | 2017-12-16 06:00 | 549 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2017 | 12 | 6 | 1.8566 | 1386.883 | 231.1472 | 231
TC2 | D1 | 91 | 3431 | 2017-12-16 06:00 | 2017-12-17 21:30 | 755 | 795 | 747 | Other feedwater valves | F060Issues with the 2A TDBFP Recirculating Valve caused flow problems in the Feedwater | Trimble | Derate | Coal | 3 | 2017 | 12 | 39.5 | 1.9874 | 1484.6038 | 37.5849 | 38
TC2 | D1 | 92 | 3431 | 2017-12-17 21:30 | 2017-12-18 03:00 | 549 | 795 | 747 | Other feedwater valves | F060In order to work on the 2A TDBFP Recirculating Valve, the MDBFP was brought into s | Trimble | Derate | Coal | 3 | 2017 | 12 | 5.5 | 1.7019 | 1271.3094 | 231.1472 | 231
TC2 | D1 | 93 | 3431 | 2017-12-18 03:00 | 2017-12-20 06:34 | 789 | 795 | 747 | Other feedwater valves | F060The unit was placed on an Immediate Derate while the MDBFP was running, as this co | Trimble | Derate | Coal | 3 | 2017 | 12 | 51.5667 | 0.38918 | 290.7192 | 5.6377 | 6
TC2 | MO | 94 | 1000 | 2017-12-20 06:34 | 2017-12-22 11:54 | 0 | 795 | 747 | Waterwall (Furnace wall) A | F540The unit was placed on a Maintenance Outage for repairs on a leaking waterwall slo | Trimble | Maintenance | Coal | 3 | 2017 | 12 | 53.3333 | 53.3333 | 39840 | 747 | 747
TC2 | U1 | 95 | 1000 | 2017-12-29 19:31 | 2018-01-01 |  | 795 | 747 | Waterwall (Furnace wall) A | F540The unit was placed on a Forced Outage for repairs to a tube leak on the left wate | Trimble | Outage | Coal | 3 | 2017 | 12 | 52.4833 | 52.4833 | 39205.05 | 747 | 747
TC2 | U1 | 1 | 1000 | 2018-01-01 | 2018-01-01 11:56 |  | 795 | 747 | Waterwall (Furnace wall) A | F540The unit was placed on a Forced Outage for repairs to a tube leak on the left wate | Trimble | Outage | Coal | 3 | 2018 | 1 | 11.9333 | 11.9333 | 8914.2 | 747 | 747
TC2 | D4 | 2 | 1190 | 2018-01-09 21:00 | 2018-01-10 05:30 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for a routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2018 | 1 | 8.5 | 3.6994 | 2763.4302 | 325.1094 | 325
TC2 | D1 | 3 | 385 | 2018-01-10 05:30 | 2018-01-10 07:42 | 630 | 795 | 747 | Igniters | F340Unit 2 was derated because the 3C gas igniter would not light which prevented the | Trimble | Derate | Coal | 3 | 2018 | 1 | 2.2 | 0.4566 | 341.083 | 155.0377 | 155
TC2 | D4 | 4 | 1190 | 2018-01-10 07:42 | 2018-01-10 09:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for the completion of routine boiler d | Trimble | Derate | Coal | 3 | 2018 | 1 | 1.3 | 0.56579 | 422.6423 | 325.1094 | 325
TC2 | D4 | 5 | 1190 | 2018-01-13 | 2018-01-13 10:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2018 | 1 | 10 | 4.3522 | 3251.0943 | 325.1094 | 325
TC2 | D4 | 6 | 1190 | 2018-01-21 | 2018-01-21 10:00 | 440 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2018 | 1 | 10 | 4.4654 | 3335.6604 | 333.566 | 334
TC2 | D1 | 7 | 3399 | 2018-01-22 18:27 | 2018-01-23 | 790 | 795 | 747 | Other miscellaneous condensate system problems | F780The unit was placed on an unplanned derate due to ambient temperatures issues. The | Trimble | Derate | Coal | 3 | 2018 | 1 | 5.55 | 0.034906 | 26.0745 | 4.6981 | 5
TC2 | D1 | 8 | 9271 | 2018-01-24 17:00 | 2018-01-24 19:15 | 750 | 795 | 747 | Wet coal (not outside management control) | FW00The unit was placed on an Unplanned Derate due to wet coal supply. | Trimble | Derate | Coal | 3 | 2018 | 1 | 2.25 | 0.12736 | 95.1368 | 42.283 | 42
TC2 | D1 | 9 | 310 | 2018-01-25 01:00 | 2018-01-25 02:25 | 710 | 795 | 747 | Pulverizer mills | F660The unit was placed on a derate due to winter rating airflow issues during a mill | Trimble | Derate | Coal | 3 | 2018 | 1 | 1.4167 | 0.15147 | 113.1462 | 79.8679 | 80
TC2 | D1 | 10 | 310 | 2018-01-26 03:00 | 2018-01-26 05:30 | 710 | 795 | 747 | Pulverizer mills | F660The unit was placed on a derate due to winter rating airflow issues during a mill | Trimble | Derate | Coal | 3 | 2018 | 1 | 2.5 | 0.2673 | 199.6698 | 79.8679 | 80
TC2 | D1 | 11 | 9271 | 2018-01-26 09:18 | 2018-01-26 17:23 | 799 | 795 | 747 | Wet coal (not outside management control) | FW00The unit was placed on an Unplanned Derate due to wet coal supply. | Trimble | Derate | Coal | 3 | 2018 | 1 | 8.0833 | -0.040671 | -30.3811 | 0 | 0
TC2 | D4 | 12 | 1190 | 2018-01-28 | 2018-01-28 07:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2018 | 1 | 7 | 3.0465 | 2275.766 | 325.1094 | 325
TC2 | D1 | 13 | 310 | 2018-01-31 01:30 | 2018-01-31 02:30 | 759 | 795 | 747 | Pulverizer mills | F660The unit was placed on a derate due to winter rating airflow issues during a mill | Trimble | Derate | Coal | 3 | 2018 | 1 | 1 | 0.045283 | 33.8264 | 33.8264 | 34
TC2 | D4 | 14 | 1190 | 2018-02-04 | 2018-02-04 10:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslag. | Trimble | Derate | Coal | 3 | 2018 | 2 | 10 | 4.3522 | 3251.0943 | 325.1094 | 325
TC2 | D1 | 15 | 310 | 2018-02-06 02:30 | 2018-02-06 03:30 | 759 | 795 | 747 | Pulverizer mills | F660The unit was placed on a derate due to winter rating airflow issues during a mill | Trimble | Derate | Coal | 3 | 2018 | 2 | 1 | 0.045283 | 33.8264 | 33.8264 | 34
TC2 | D1 | 16 | 9291 | 2018-02-07 06:00 | 2018-02-07 16:10 | 804 | 795 | 747 | Other fuel quality problems (not outside management control) | F610The unit was placed on a derate for issues with the fuel supply. | Trimble | Derate | Coal | 3 | 2018 | 2 | 10.1667 | -0.11509 | -85.9755 | 0 | 0
TC2 | D1 | 17 | 310 | 2018-02-08 02:19 | 2018-02-08 02:29 | 785 | 795 | 747 | Pulverizer mills | F660The unit was placed on a derate due to winter rating airflow issues during a mill | Trimble | Derate | Coal | 3 | 2018 | 2 | 0.16667 | 0.0020964 | 1.566 | 9.3962 | 9
TC2 | D4 | 18 | 1190 | 2018-02-10 21:00 | 2018-02-11 10:00 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate for routine boiler deslagging. | Trimble | Derate | Coal | 3 | 2018 | 2 | 13 | 5.6579 | 4226.4226 | 325.1094 | 325
TC2 | D4 | 19 | 1190 | 2018-02-17 22:00 | 2018-02-18 | 449 | 795 | 747 | Other tube slagging or fouling | FS00The unit was placed on a Maintenance Derate four a routine boiler deslag. | Trimble | Derate | Coal | 3 | 2018 | 2 | 2 | 0.87044 | 650.2189 | 325.1094 | 325
TC2 | D1 | 20 | 1455 | 2018-02-19 15:13 | 2018-02-21 09:30 | 800 | 795 | 747 | Induced draft fans | F660The unit was placed on a derate due to winter rating airflow issues with the ID Fa | Trimble | Derate | Coal | 3 | 2018 | 2 | 42.2833 | -0.26593 | -198.6519 | 0 | 0
TC2 | PD | 21 | 310 | 2018-02-22 | 2018-02-22 02:30 | 779 | 795 | 747 | Pulverizer mills | F660The unit was placed on a planned derate due to winter rating airflow issues during | Trimble | Derate | Coal | 3 | 2018 | 2 | 2.5 | 0.050314 | 37.5849 | 15.034 | 15
TC2 | D1 | 22 | 1455 | 2018-02-22 13:30 | 2018-02-23 | 799 | 795 | 747 | Induced draft fans | F780The unit was placed on a derate due to winter rating ambient temperature issues. | Trimble | Derate | Coal | 3 | 2018 | 2 | 10.5 | -0.05283 | -39.4642 | 0 | 0
TC2 | PO | 23 | 4400 | 2018-02-23 23:30 | 2018-04-30 | 0 | 795 | 747 | Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | F590Planned Outage for multiple scopes, main scope being a total turbine maintenance p | Trimble | Other | Coal | 3 | 2018 | 2 | 1560.5 | 1560.5 | 1165693.5 | 747 | 747

## Lookup
[24 empty] | 150 | 360
[24 empty] | Small Units (<150) | Medium Units (<360) | Large Units (>360) | Size | 1 | 2 | 3 | 3 | 3 | 3 | 3 | 1 | 1 | 2 | 2 | 3 | 3 | 3 | 3
|  |  | Net |  | Gross |  | Net | [15 empty] | Derate (MW) | 0 | 0 | 0 |  | BR1 | BR2 | BR3 | GH1 | GH2 | GH3 | GH4 | GR3 | GR4 | MC1 | MC2 | MC3 | MC4 | TC1 | TC2
Plant Name in Unit Rating sheet | UnitName | Plant Name | Winter | Summer | Winter | Summer | Minimum | UnitName | UnitNo | Coal Units | Max Capacity (MW) | Min Capacity | Max Derate | Size | UnitName | 5 | 4 | 3 | 2 | 1 |  |  | 1 | 10 | 20 | 40 |  | 8.571% | 7.619% | 19.1% | 19.57% | 12.92% | 41.18% | 39.61% | #N/A | #N/A | 5.019% | 19.31% | 15.87% | 35.14% | 38.66% | 19.9%
Brown 1 | BR1 | Brown | 107 | 106 | 114 | 113 | 36 | BR1 | 1 | Brown.1 | 107 | 36 | 71 | 1 | BR1 | 37 | 74 | 77 | 87 | 97 |  |  | 2 | 20 | 40 | 80 |  | 12.86% | 19.05% | 8.543% | 50% | 54.17% | 18.24% | 22.08% | #N/A | #N/A | 8.178% | 5.792% | 24.91% | 12.27% | 18.29% | 12.53%
Brown 2 | BR2 | Brown | 168 | 166 | 180 | 177 | 64 | BR2 | 2 | Brown.2 | 168 | 64 | 104 | 2 | BR2 | 64 | 78 | 88 | 128 | 148 |  |  | 3 | 30 | 80 | 160 |  | 31.43% | 63.81% | 55.28% | 13.59% | 15.83% | 19.41% | 18.83% | #N/A | #N/A | 44.05% | 27.22% | 51.37% | 35.34% | 29.4% | 31.2%
Brown 3 | BR3 | Brown | 413 | 409 | 457 | 455 | 140 | BR3 | 3 | Brown.3 | 413 | 140 | 273 | 3 | BR3 | 140 | 223 | 253 | 333 | 373 |  |  | 4 | 33 | 90 | 190 |  | 20% | 0.9524% | 4.523% | 4.348% | 4.583% | 3.529% | 1.299% | #N/A | #N/A | 24.16% | 28.38% | 3.242% | 4.782% | 1.389% | 3.44%
Ghent 1 | GH1 | Ghent | 479 | 475 | 520 | 520 | 218 | GH1 | 4 | Ghent.1 | 479 | 218 | 261 | 3 | GH1 | 218 | 289 | 319 | 399 | 439 |  |  | 5 | 70 | 150 | 320 |  | 24.29% | 4.762% | 5.528% | 11.41% | 11.25% | 14.12% | 14.94% | #N/A | #N/A | 11.15% | 11.97% | 4.608% | 8.524% | 5.324% | 7.862%
Ghent 2 | GH2 | Ghent | 486 | 485 | 520 | 520 | 225 | GH2 | 5 | Ghent.2 | 486 | 225 | 261 | 3 | GH2 | 225 | 296 | 326 | 406 | 446 |  |  | 6 | 100 | 220 | 400 |  | 2.857% | 3.81% | 7.035% | 0.5435% | 0.4167% | 1.176% | 0.6494% | NA | NA | 6.877% | 6.95% | 0% | 2.287% | 0% | 15.97%
Ghent 3 | GH3 | Ghent | 476 | 481 | 525 | 530 | 210 | GH3 | 6 | Ghent.3 | 481 | 210 | 271 | 3 | GH3 | 210 | 291 | 321 | 401 | 441 |  |  | 7 | 150 | 360 | 480 |  | NA | NA | 0% | 0.5435% | 0% | 0.5882% | 0% | NA | NA | 0.5576% | 0.3861% | 0% | 0% | 0% | 1.72%
Ghent 4 | GH4 | Ghent | 478 | 478 | 525 | 525 | 215 | GH4 | 7 | Ghent.4 | 478 | 215 | 263 | 3 | GH4 | 215 | 288 | 318 | 398 | 438
Green River 3 | GR3 | Green River | 71 | 68 | 75 | 72 | 37 | GR3 | 8 | Green.River.3 | 71 | 37 | 34 | 1 | GR3 | 37 | 38 | 41 | 51 | 61
Green River 4 | GR4 | Green River | 98 | 93 | 105 | 100 | 37 | GR4 | 9 | Green.River.4 | 98 | 37 | 61 | 1 | GR4 | 37 | 65 | 68 | 78 | 88
Mill Creek 1 | MC1 | Mill Creek | 300 | 300 | 330 | 330 | 115 | MC1 | 10 | Mill.Creek.1 | 300 | 115 | 185 | 2 | MC1 | 150 | 210 | 220 | 260 | 280
Mill Creek 2 | MC2 | Mill Creek | 295 | 297 | 330 | 330 | 115 | MC2 | 11 | Mill.Creek.2 | 297 | 115 | 182 | 2 | MC2 | 147 | 207 | 217 | 257 | 277
Mill Creek 3 | MC3 | Mill Creek | 394 | 391 | 423 | 422 | 170 | MC3 | 12 | Mill.Creek.3 | 394 | 170 | 224 | 3 | MC3 | 170 | 204 | 234 | 314 | 354
Mill Creek 4 | MC4 | Mill Creek | 486 | 477 | 525 | 517 | 175 | MC4 | 13 | Mill.Creek.4 | 486 | 175 | 311 | 3 | MC4 | 175 | 296 | 326 | 406 | 446
Trimble County 1 | TC1 | Trimble | 493 | 493 | 530 | 530 | 188 | TC1 | 14 | Trimble.County.1 | 493 | 188 | 305 | 3 | TC1 | 188 | 303 | 333 | 413 | 453
Trimble County 2 | TC2 | Trimble | 760 | 732 | 809 | 781 | 420 | TC2 | 15 | Trimble.County.2 | 760 | 420 | 340 | 3 | TC2 | 440 | 570 | 600 | 680 | 720
[8 empty] | BR1 | BR2 | BR3 | GH1 | GH2 | GH3 | GH4 | GR3 | GR4 | MC1 | MC2 | MC3 | MC4 | TC1 | TC2
[8 empty] | 37 | 64 | 140 | 218 | 225 | 210 | 215 | 37 | 37 | 150 | 147 | 170 | 175 | 188 | 440
[8 empty] | 74 | 78 | 223 | 289 | 296 | 291 | 288 | 38 | 65 | 210 | 207 | 204 | 296 | 303 | 570
[8 empty] | 77 | 88 | 253 | 319 | 326 | 321 | 318 | 41 | 68 | 220 | 217 | 234 | 326 | 333 | 600
[8 empty] | 87 | 128 | 333 | 399 | 406 | 401 | 398 | 51 | 78 | 260 | 257 | 314 | 406 | 413 | 680
[8 empty] | 97 | 148 | 373 | 439 | 446 | 441 | 438 | 61 | 88 | 280 | 277 | 354 | 446 | 453 | 720

## INP-Calc Hist Outage Rates
2013 | [10 empty] | 2014 | [10 empty] | 2015 | [10 empty] | 2016 | [10 empty] | 2017 | [10 empty] | 2013 - 2017
Units | NDC | FOH | EFDH | MOH | Act SH | FOR | EFDR | EFOR | MOR | EUOR | Units | NDC | FOH | EFDH | MOH | Act SH | FOR | EFDR | EFOR | MOR | EUOR | Units | NDC | FOH | EFDH | MOH | Act SH | FOR | EFDR | EFOR | MOR | EUOR | Units | NDC | FOH | EFDH | MOH | Act SH | FOR | EFDR | EFOR | MOR | EUOR | Units | NDC | FOH | EFDH | MOH | Act SH | FOR | EFDR | EFOR | MOR | EUOR | Units | NDC | FOH | EFDH | MOH | Act SH | FOR | EFDR | EFOR | MOR | EUOR | EFDH/FOH | Avg SH | Units | NDC
GH1 | 471.5 | 153.85 | 271.218 | 62.233 | 8152.7 | 1.852% | 3.327% | 5.117% | 0.7576% | 5.823% | GH1 | 480 | 49.65 | 141.304 | 158.133 | 8003.783 | 0.6165% | 1.765% | 2.371% | 1.937% | 4.251% | GH1 | 480 | 386.3 | 24.351 | 208.233 | 6563.333 | 5.559% | 0.371% | 5.909% | 3.075% | 8.646% | GH1 | 476 | 276.933 | 39.03 | 52 | 7720.45 | 3.463% | 0.5055% | 3.951% | 0.669% | 4.571% | GH1 | 476 | 197.567 | 40.474 | 227.05 | 7670.817 | 2.511% | 0.5276% | 3.025% | 2.875% | 5.745% | GH1 | 476.7 | 1064.3 | 516.377 | 707.649 | 38111.083 | 2.717% | 1.355% | 4.035% | 1.823% | 5.738% | 48.52% | 7622.2166 | GH1 | 476.7
GH2 | 475 | 104.583 | 39.958 | 155.4 | 8397.5 | 1.23% | 0.4758% | 1.7% | 1.817% | 3.465% | GH2 | 486 | 9.35 | 49.909 | 148.633 | 8277.067 | 0.1128% | 0.603% | 0.7151% | 1.764% | 2.465% | GH2 | 486 | 78.167 | 88.651 | 16.283 | 6866.15 | 1.126% | 1.291% | 2.402% | 0.2366% | 2.631% | GH2 | 495 | 61.833 | 25.89 | 97.317 | 7987.883 | 0.7681% | 0.3241% | 1.09% | 1.204% | 2.271% | GH2 | 493 | 66.1 | 10.159 | 111.2 | 7946.783 | 0.8249% | 0.1278% | 0.9517% | 1.38% | 2.307% | GH2 | 487 | 320.033 | 214.567 | 528.833 | 39475.383 | 0.8042% | 0.5435% | 1.343% | 1.322% | 2.637% | 67.05% | 7895.0766 | GH2 | 487
GH3 | 481 | 58.883 | 221.821 | 417.583 | 7813.617 | 0.748% | 2.839% | 3.566% | 5.073% | 8.423% | GH3 | 485.5 | 56.833 | 81.732 | 343.617 | 7165.383 | 0.7869% | 1.141% | 1.919% | 4.576% | 6.373% | GH3 | 485.5 | 230.15 | 48.76 | 324.667 | 7461.717 | 2.992% | 0.6535% | 3.626% | 4.17% | 7.529% | GH3 | 485 | 269.217 | 46.4 | 417.15 | 7270.267 | 3.571% | 0.6382% | 4.186% | 5.426% | 9.21% | GH3 | 485 | 184.433 | 19.161 | 21.617 | 7528.9 | 2.391% | 0.2545% | 2.64% | 0.2863% | 2.912% | GH3 | 484.4 | 799.516 | 417.874 | 1524.634 | 37239.884 | 2.102% | 1.122% | 3.2% | 3.933% | 6.931% | 52.27% | 7447.9768 | GH3 | 484.4
GH4 | 480 | 282.483 | 193.235 | 529.683 | 7618.5 | 3.575% | 2.536% | 6.021% | 6.501% | 11.93% | GH4 | 480 | 148.267 | 58.631 | 369.983 | 6919.95 | 2.098% | 0.8473% | 2.927% | 5.075% | 7.756% | GH4 | 480 | 93.317 | 78.148 | 281.883 | 8172.783 | 1.129% | 0.9562% | 2.074% | 3.334% | 5.304% | GH4 | 487 | 253.083 | 71.05 | 125.767 | 7700.833 | 3.182% | 0.9226% | 4.075% | 1.607% | 5.568% | GH4 | 487 | 213.8 | 74.964 | 0 | 8060.417 | 2.584% | 0.93% | 3.49% | 0% | 3.49% | GH4 | 482.8 | 990.95 | 476.028 | 1307.316 | 38472.483 | 2.511% | 1.237% | 3.717% | 3.286% | 6.805% | 48.04% | 7694.4966 | GH4 | 482.8
GH Sta. | 1907.5 | 599.799 | 726.232 | 1164.899 | 31982.317 | 1.842% | 2.271% | 4.071% | 3.532% | 7.399% | GH Sta. | 1931.5 | 264.1 | 331.576 | 1020.366 | 30366.183 | 0.8595% | 1.09% | 1.941% | 3.25% | 5.101% | GH Sta. | 1931.5 | 787.934 | 239.91 | 831.066 | 29063.983 | 2.636% | 0.8263% | 3.441% | 2.777% | 6.053% | GH Sta. | 1943 | 861.066 | 182.37 | 692.234 | 30679.433 | 2.717% | 0.5937% | 3.294% | 2.208% | 5.373% | GH Sta. | 1941 | 661.9 | 144.758 | 359.867 | 31206.917 | 2.07% | 0.4627% | 2.523% | 1.132% | 3.604% | GH Sta. | 1930.9 | 3174.799 | 1624.846 | 4068.432 | 153298.833 | 2.024% | 1.058% | 3.061% | 2.586% | 5.518% | 51.18% | 7665.3974 | GH Sta. | 1930.9
2013 STEAM TARGETS : | [7 empty] | 4.4% |  | 6.82% | 2014 STEAM TARGETS : | [7 empty] | 5% |  | 7.3% | 2015 STEAM TARGETS : | [7 empty] | 4.91% |  |  | 2016 STEAM TARGETS : | [7 empty] | 4.91% |  |  | 2017 STEAM TARGETS : | [7 empty] | 4.91%
BR1 | 101.5 | 68.567 | 146.519 | 319.983 | 7521.7 | 0.9034% | 1.948% | 2.834% | 4.081% | 6.764% | BR1 | 106.5 | 108.05 | 26.276 | 90.983 | 7414.817 | 1.436% | 0.3544% | 1.786% | 1.212% | 2.959% | BR1 | 106.5 | 34.417 | 12.878 | 715.883 | 4499.333 | 0.7591% | 0.2862% | 1.043% | 13.73% | 14.54% | BR1 | 106.5 | 44.683 | 2.027 | 230.283 | 4924.833 | 0.8991% | 0.04116% | 0.9399% | 4.467% | 5.327% | BR1 | 106.5 | 72.633 | 1.893 | 28.617 | 1182.617 | 5.786% | 0.1601% | 5.937% | 2.363% | 8.034% | BR1 | 105.5 | 328.35 | 189.593 | 1385.749 | 25543.3 | 1.269% | 0.7422% | 2.002% | 5.146% | 6.984% | 57.74% | 5108.66 | BR1 | 105.5
BR2 | 168 | 149.25 | 110.448 | 118.417 | 7671.917 | 1.908% | 1.44% | 3.32% | 1.52% | 4.762% | BR2 | 167.5 | 82.367 | 126.851 | 403.833 | 7534.75 | 1.081% | 1.684% | 2.747% | 5.087% | 7.643% | BR2 | 167.5 | 8.867 | 12.563 | 165.8 | 7271.383 | 0.1218% | 0.1728% | 0.2944% | 2.229% | 2.514% | BR2 | 167.5 | 16.217 | 27.742 | 444.183 | 4990.5 | 0.3239% | 0.5559% | 0.878% | 8.173% | 8.955% | BR2 | 167.5 | 29.633 | 11.279 | 38.433 | 3984.867 | 0.7381% | 0.283% | 1.019% | 0.9553% | 1.958% | BR2 | 167.6 | 286.334 | 288.883 | 1170.666 | 31453.417 | 0.9021% | 0.9184% | 1.812% | 3.588% | 5.305% | 100.9% | 6290.6834 | BR2 | 167.6
BR3 | 418 | 526.35 | 569.749 | 316.233 | 7120.35 | 6.883% | 8.002% | 14.33% | 4.252% | 17.74% | BR3 | 412 | 516.217 | 61.684 | 403.433 | 6664.617 | 7.189% | 0.9255% | 8.048% | 5.708% | 12.94% | BR3 | 412 | 86.417 | 123.566 | 108.367 | 5933.9 | 1.435% | 2.082% | 3.488% | 1.793% | 5.194% | BR3 | 414 | 522.367 | 65.429 | 643.217 | 5518.85 | 8.647% | 1.186% | 9.73% | 10.44% | 18.42% | BR3 | 413 | 164.467 | 16.145 | 202.083 | 5603.333 | 2.851% | 0.2881% | 3.131% | 3.481% | 6.41% | BR3 | 413.8 | 1815.818 | 836.573 | 1673.333 | 30841.05 | 5.56% | 2.713% | 8.122% | 5.146% | 12.6% | 46.07% | 6168.21 | BR3 | 413.8
BR Sta. | 687.5 | 744.167 | 826.716 | 754.633 | 22313.967 | 4.773% | 5.401% | 9.916% | 3.54% | 12.96% | BR Sta. | 686 | 706.634 | 214.811 | 898.249 | 21614.184 | 4.726% | 1.031% | 5.708% | 4.831% | 10.06% | BR Sta. | 686 | 129.701 | 149.007 | 990.05 | 17704.616 | 0.9744% | 1.313% | 2.275% | 3.465% | 5.629% | BR Sta. | 688 | 583.267 | 95.198 | 1317.683 | 15434.183 | 5.783% | 0.8765% | 6.609% | 9.107% | 14.66% | BR Sta. | 687 | 266.733 | 29.317 | 269.133 | 10770.817 | 2.529% | 0.2818% | 2.804% | 2.904% | 5.557% | BR Sta. | 686.9 | 2430.502 | 1315.049 | 4229.748 | 87837.767 | 3.868% | 2% | 5.791% | 4.755% | 10.1% | 54.11% | 6035.3581 | BR Sta. | 686.9
2013 STEAM TARGETS : | [7 empty] | 5% |  | 7.51% | 2014 STEAM TARGETS : | [7 empty] | 5.6% |  | 8.25% | 2015 STEAM TARGETS : | [7 empty] | 3.81% |  |  | 2016 STEAM TARGETS : | [7 empty] | 3.81% |  |  | 2017 STEAM TARGETS : | [7 empty] | 3.81%
GR3 | 69.5 | 34.583 | 24.242 | 67.133 | 7091.6 | 0.4853% | 0.3418% | 0.8255% | 0.9378% | 1.751% | GR3 | 69.5 | 173.967 | 33.747 | 97.333 | 7664.95 | 2.219% | 0.4403% | 2.65% | 1.254% | 3.844% | GR3 | 69.5 | 173.967 | 33.747 | 97.333 | 7664.95 | 2.219% | 0.4403% | 2.65% | 1.254% | 3.844% | GR3 | 69.5 | 173.967 | 33.747 | 97.333 | 7664.95 | 2.219% | 0.4403% | 2.65% | 1.254% | 3.844% | GR3 | 69.5 | 173.967 | 33.747 | 97.333 | 7664.95 | 2.219% | 0.4403% | 2.65% | 1.254% | 3.844% | GR3 | 69.5 | 730.451 | 159.23 | 456.465 | 37751.4 | 1.898% | 0.4218% | 2.312% | 1.195% | 3.457% | 21.8% | 7550.28 | GR3 | 69.5
GR4 | 98.5 | 357.3 | 158.479 | 162.75 | 7632.467 | 4.472% | 2.076% | 6.455% | 2.088% | 8.323% | GR4 | 95.5 | 562.567 | 40.832 | 64.417 | 7793.1 | 6.733% | 0.524% | 7.221% | 0.8198% | 7.931% | GR4 | 95.5 | 562.567 | 40.832 | 64.417 | 7793.1 | 6.733% | 0.524% | 7.221% | 0.8198% | 7.931% | GR4 | 95.5 | 562.567 | 40.832 | 64.417 | 7793.1 | 6.733% | 0.524% | 7.221% | 0.8198% | 7.931% | GR4 | 95.5 | 562.567 | 40.832 | 64.417 | 7793.1 | 6.733% | 0.524% | 7.221% | 0.8198% | 7.931% | GR4 | 96.1 | 2607.568 | 321.807 | 420.418 | 38804.867 | 6.297% | 0.8293% | 7.074% | 1.072% | 8.008% | 12.34% | 7760.9734 | GR4 | 96.1
GR Sta. | 168 | 391.883 | 182.721 | 229.883 | 14724.067 | 2.932% | 1.39% | 4.281% | 1.636% | 5.801% | GR Sta. | 165 | 736.534 | 74.579 | 161.75 | 15458.05 | 4.901% | 0.489% | 5.367% | 1.001% | 6.268% | GR Sta. | 165 | 736.534 | 74.579 | 161.75 | 15458.05 | 4.901% | 0.489% | 5.367% | 1.001% | 6.268% | GR Sta. | 165 | 736.534 | 74.579 | 161.75 | 15458.05 | 4.901% | 0.489% | 5.367% | 1.001% | 6.268% | GR Sta. | 165 | 736.534 | 74.579 | 161.75 | 15458.05 | 4.901% | 0.489% | 5.367% | 1.001% | 6.268% | GR Sta. | 165.6 | 3338.019 | 481.037 | 876.883 | 76556.267 | 4.529% | 0.661% | 5.16% | 1.123% | 6.177% | 14.41% | 7672.5483 | GR Sta. | 165.6
2013 STEAM TARGETS : | [7 empty] | 5.3% |  | 8.76% | 2014 STEAM TARGETS : | [7 empty] | 6.8% |  | 7.65% | 2015 STEAM TARGETS : | [7 empty] | 4.88% |  |  | 2016 STEAM TARGETS : | [7 empty] | 4.88% |  |  | 2017 STEAM TARGETS : | [7 empty] | 4.88%
MC1 | 303 | 175.833 | 68.62 | 264.017 | 6303.65 | 2.714% | 1.089% | 3.773% | 4.02% | 7.54% | MC1 | 303 | 43.5 | 157.3133 | 444.65 | 8105.133 | 0.5338% | 1.941% | 2.464% | 5.201% | 7.511% | MC1 | 303 | 204.43 | 85.11 | 351.77 | 6823.77 | 2.909% | 1.247% | 4.12% | 4.902% | 8.69% | MC1 | 300 | 64.98 | 73.97 | 256.6 | 8225.42 | 0.7838% | 0.8993% | 1.676% | 3.025% | 4.628% | MC1 | 300 | 70.55 | 93.782 | 185.15 | 7777.5 | 0.8989% | 1.206% | 2.094% | 2.325% | 4.35% | MC1 | 301.8 | 559.293 | 478.7953 | 1502.187 | 37235.473 | 1.48% | 1.286% | 2.747% | 3.878% | 6.464% | 85.61% | 7447.0946 | MC1 | 301.8
MC2 | 300 | 264.6 | 259.96 | 374.467 | 8057.167 | 3.18% | 3.226% | 6.303% | 4.441% | 10.34% | MC2 | 300 | 333.483 | 156.644 | 403.1 | 7306.9 | 4.365% | 2.144% | 6.415% | 5.228% | 11.1% | MC2 | 300 | 232.07 | 68.35 | 327.83 | 6866.15 | 3.269% | 0.9955% | 4.232% | 4.557% | 8.46% | MC2 | 297 | 23.9 | 99.08 | 83.35 | 7798.78 | 0.3055% | 1.27% | 1.572% | 1.057% | 2.61% | MC2 | 295 | 6.95 | 183.829 | 72.633 | 8062.083 | 0.08613% | 2.28% | 2.364% | 0.8929% | 3.235% | MC2 | 298.4 | 861.003 | 767.863 | 1261.38 | 38091.08 | 2.21% | 2.016% | 4.182% | 3.205% | 7.187% | 89.18% | 7618.216 | MC2 | 298.4
MC3 | 394 | 910.267 | 202.654 | 167.883 | 6859.817 | 11.72% | 2.954% | 14.32% | 2.389% | 16.14% | MC3 | 392.5 | 193.683 | 75.124 | 116.667 | 8157.733 | 2.319% | 0.9209% | 3.219% | 1.41% | 4.552% | MC3 | 392.5 | 86.17 | 128.03 | 628.28 | 7585.02 | 1.123% | 1.688% | 2.792% | 7.65% | 10.15% | MC3 | 394 | 281.42 | 125.96 | 194.27 | 6766.45 | 3.993% | 1.862% | 5.78% | 2.791% | 8.308% | MC3 | 394 | 38.883 | 18.334 | 55.333 | 8492.7 | 0.4558% | 0.2159% | 0.6706% | 0.6473% | 1.311% | MC3 | 393.4 | 1510.423 | 550.102 | 1162.433 | 37861.72 | 3.836% | 1.453% | 5.233% | 2.979% | 7.951% | 36.42% | 7572.344 | MC3 | 393.4
MC4 | 484.5 | 714.35 | 116.564 | 450.317 | 7203.667 | 9.022% | 1.618% | 10.49% | 5.883% | 15.31% | MC4 | 481.5 | 455.65 | 195.2047 | 211.5 | 6047.117 | 7.007% | 3.228% | 10.01% | 3.379% | 12.84% | MC4 | 481.5 | 73.13 | 31.79 | 493.47 | 7840.58 | 0.9241% | 0.4055% | 1.326% | 5.921% | 7.118% | MC4 | 486 | 191.15 | 11.06 | 0 | 7338.43 | 2.539% | 0.1507% | 2.686% | 0% | 2.686% | MC4 | 486 | 166.917 | 28.121 | 125.567 | 7694.817 | 2.123% | 0.3655% | 2.481% | 1.606% | 4.014% | MC4 | 483.9 | 1601.197 | 382.7397 | 1280.854 | 36124.611 | 4.244% | 1.059% | 5.259% | 3.424% | 8.37% | 23.9% | 7224.9222 | MC4 | 483.9
MC Sta. | 1481.5 | 2065.05 | 647.798 | 1256.684 | 28424.301 | 7.373% | 2.235% | 9.443% | 4.335% | 13.09% | MC Sta. | 1477 | 1026.316 | 584.286 | 1175.917 | 29616.883 | 3.658% | 2.027% | 5.611% | 3.612% | 8.9% | MC Sta. | 1477 | 595.8 | 313.28 | 1801.35 | 29115.52 | 1.81% | 1.028% | 2.82% | 5.957% | 8.51% | MC Sta. | 1477 | 561.45 | 310.07 | 534.22 | 30129.08 | 2.048% | 0.9678% | 2.996% | 1.593% | 4.51% | MC Sta. | 1475 | 283.3 | 324.066 | 438.683 | 32027.1 | 1.004% | 0.8752% | 1.871% | 1.336% | 3.169% | MC Sta. | 1477.5 | 4531.916 | 2179.5 | 5206.854 | 149312.884 | 3.161% | 1.41% | 4.527% | 3.352% | 7.629% | 48.09% | 7442.2394 | MC Sta. | 1477.5
2013 STEAM TARGETS : | [7 empty] | 4.4% |  | 7.03% | 2014 STEAM TARGETS : | [7 empty] | 5% |  | 7.3% | 2015 STEAM TARGETS : | [7 empty] | 4.45% |  |  | 2016 STEAM TARGETS : | [7 empty] | 4.45% |  |  | 2017 STEAM TARGETS : | [7 empty] | 4.45%
TC1 | 513 | 150.45 | 53.9 | 305.55 | 7553.217 | 1.953% | 0.7136% | 2.653% | 3.888% | 6.366% | TC1 | 510.6667 | 267.067 | 74.8775 | 249.433 | 8243.5 | 3.138% | 0.9083% | 4.018% | 2.937% | 6.751% | TC1 | 510.6667 | 222.783 | 61.16 | 185.183 | 6841.983 | 3.153% | 0.8939% | 4.019% | 2.635% | 6.471% | TC1 | 510.6667 | 165.583 | 37.825 | 17.167 | 8383.35 | 1.937% | 0.4512% | 2.379% | 0.2044% | 2.575% | TC1 | 510.6667 | 220.267 | 19.876 | 130.433 | 6819.25 | 3.129% | 0.2915% | 3.411% | 1.877% | 5.168% | TC1 | 511.1333 | 1026.15 | 247.6385 | 887.766 | 37841.3 | 2.64% | 0.6544% | 3.277% | 2.292% | 5.437% | 24.13% | 7568.26 | TC1 | 511.1333
TC2 | 760 | 864.367 | 213.263 | 232.35 | 6055.567 | 12.49% | 3.522% | 15.57% | 3.695% | 18.32% | TC2 | 746 | 728.9 | 44.0969 | 63.267 | 5350.2 | 11.99% | 0.8242% | 12.72% | 1.169% | 13.61% | TC2 | 746 | 348.35 | 271.11 | 64.117 | 7781.883 | 4.285% | 3.484% | 7.619% | 0.8172% | 8.342% | TC2 | 760 | 1708.783 | 38.81 | 464.433 | 5904.8 | 22.44% | 0.6573% | 22.95% | 7.292% | 27.38% | TC2 | 760 | 771.483 | 62.517 | 126.133 | 6830.15 | 10.15% | 0.9153% | 10.97% | 1.813% | 12.42% | TC2 | 754.4 | 4421.883 | 629.7969 | 950.3 | 31922.6 | 12.17% | 1.973% | 13.9% | 2.891% | 16.09% | 14.24% | 6384.52 | TC2 | 754.4
TC Sta. | 1273 | 1014.817 | 267.163 | 537.9 | 13608.784 | 7.97% | 2.238% | 10.03% | 3.783% | 13.17% | TC Sta. | 1256.6667 | 995.967 | 118.9744 | 312.7 | 13593.7 | 7.658% | 0.8674% | 8.459% | 2.084% | 10.22% | TC Sta. | 1256.6667 | 571.133 | 332.27 | 249.3 | 14623.866 | 3.863% | 2.511% | 6.276% | 1.508% | 7.636% | TC Sta. | 1270.6667 | 1874.366 | 76.635 | 481.6 | 14288.15 | 13.63% | 0.5567% | 14.11% | 3.962% | 17.06% | TC Sta. | 1270.6667 | 991.75 | 82.393 | 256.566 | 13649.4 | 7.456% | 0.6648% | 8.072% | 1.839% | 9.638% | TC Sta. | 1265.5333 | 5448.033 | 877.4354 | 1838.066 | 69763.9 | 8.164% | 1.386% | 9.437% | 2.625% | 11.62% | 16.11% | 6862.618 | TC Sta. | 1265.5333
2013 STEAM TARGETS : | [7 empty] | 3.3% | 1.4% | 4.61% | 2014 STEAM TARGETS : | [7 empty] | 4.05% |  | 6.54% | 2015 STEAM TARGETS : | [7 empty] | 3.88% |  | 6.25% | 2016 STEAM TARGETS : | [7 empty] | 3.3% |  |  | 2017 STEAM TARGETS : | [7 empty] | 3.3% | [13 empty] | 34.23% | 107353.9302

## INP-Calc EFOR&EUOR - 2019Plan
LG&E & KU
REGULATED GENERATION
CAPACITY WEIGHTED EFOR HISTORY, BENCHMARKS, and TARGETS
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
|  | 2019 Plan | [5 empty] | 2019 Plan | [5 empty] | 2019 Plan | [5 empty] | 2019 Plan | [5 empty] | 2019 Plan
|  | EFOR TARGETS | [5 empty] | EUOR TARGETS | [5 empty] | MOR TARGETS | [5 empty] | FOR TARGETS | [5 empty] | EFDR TARGETS
STATION | NDC | 2018 | 2019 | 2020 | 2021 | 2022 |  | 2018 | 2019 | 2020 | 2021 | 2022 |  | 2018 | 2019 | 2020 | 2021 | 2022 |  | 2018 | 2019 | 2020 | 2021 | 2022 |  | 2018 | 2019 | 2020 | 2021 | 2022
BR1 | 107 | 5.7% | 5.7% | 5.7% | 5.7% | 5.7% |  | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% |  | 2.8% | 2.8% | 2.8% | 2.8% | 2.8% |  | 3.699% | 3.699% | 3.699% | 3.699% | 3.699% |  | 2.078% | 2.078% | 2.078% | 2.078% | 2.078%
BR2 | 168 | 5.7% | 5.7% | 5.7% | 5.7% | 5.7% |  | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% |  | 2.8% | 2.8% | 2.8% | 2.8% | 2.8% |  | 3.699% | 3.699% | 3.699% | 3.699% | 3.699% |  | 2.078% | 2.078% | 2.078% | 2.078% | 2.078%
BR3 | 413 | 5.7% | 5.7% | 5.7% | 5.7% | 5.7% |  | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% |  | 2.8% | 2.8% | 2.8% | 2.8% | 2.8% |  | 3.699% | 3.699% | 3.699% | 3.699% | 3.699% |  | 2.078% | 2.078% | 2.078% | 2.078% | 2.078%
BROWN | 688 | 5.7% | 5.7% | 5.7% | 5.7% | 5.7% |  | 8.5% | 8.5% | 8.5% | 8.5% | 8.5% |  | 2.8% | 2.8% | 2.8% | 2.8% | 2.8% |  | 3.699% | 3.699% | 3.699% | 3.699% | 3.699% |  | 2.078% | 2.078% | 2.078% | 2.078% | 2.078%
GH1 | 479 | 5.2% | 5.2% | 5.2% | 5.2% | 5.2% |  | 7.4% | 7.4% | 7.4% | 7.4% | 7.4% |  | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% |  | 3.44% | 3.44% | 3.44% | 3.44% | 3.44% |  | 1.823% | 1.823% | 1.823% | 1.823% | 1.823%
GH2 | 486 | 5.2% | 5.2% | 5.2% | 5.2% | 5.2% |  | 7.4% | 7.4% | 7.4% | 7.4% | 7.4% |  | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% |  | 3.44% | 3.44% | 3.44% | 3.44% | 3.44% |  | 1.823% | 1.823% | 1.823% | 1.823% | 1.823%
GH3 | 481 | 5.2% | 5.2% | 5.2% | 5.2% | 5.2% |  | 7.4% | 7.4% | 7.4% | 7.4% | 7.4% |  | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% |  | 3.44% | 3.44% | 3.44% | 3.44% | 3.44% |  | 1.823% | 1.823% | 1.823% | 1.823% | 1.823%
GH4 | 478 | 5.2% | 5.2% | 5.2% | 5.2% | 5.2% |  | 7.4% | 7.4% | 7.4% | 7.4% | 7.4% |  | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% |  | 3.44% | 3.44% | 3.44% | 3.44% | 3.44% |  | 1.823% | 1.823% | 1.823% | 1.823% | 1.823%
GHENT | 1924 | 5.2% | 5.2% | 5.2% | 5.2% | 5.2% |  | 7.4% | 7.4% | 7.4% | 7.4% | 7.4% |  | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% |  | 3.44% | 3.44% | 3.44% | 3.44% | 3.44% |  | 1.823% | 1.823% | 1.823% | 1.823% | 1.823%
GR3 | 71 | 7.8% | 8.1% | 8.4% | 8.7% | 9% |  | 11% | 11.3% | 11.6% | 11.9% | 12.2% |  | 3.2% | 3.2% | 3.2% | 3.2% | 3.2% |  | 6.818% | 7.08% | 7.342% | 7.604% | 7.866% |  | 1.054% | 1.098% | 1.142% | 1.186% | 1.23%
GR4 | 98 | 7.8% | 8.1% | 8.4% | 8.7% | 9% |  | 11% | 11.3% | 11.6% | 11.9% | 12.2% |  | 3.2% | 3.2% | 3.2% | 3.2% | 3.2% |  | 6.818% | 7.08% | 7.342% | 7.604% | 7.866% |  | 1.054% | 1.098% | 1.142% | 1.186% | 1.23%
GREEN RIVER | 169 | 7.8% | 8.1% | 8.4% | 8.7% | 9% |  | 11% | 11.3% | 11.6% | 11.9% | 12.2% |  | 3.2% | 3.2% | 3.2% | 3.2% | 3.2% |  | 6.818% | 7.08% | 7.866% | 7.866% | 7.866% |  | 1.054% | 1.098% | 1.23% | 1.23% | 1.23%
MC1 | 300 | 5.2% | 5.2% | 5.2% | 5.2% | 5.2% |  | 7.4% | 7.4% | 7.4% | 7.4% | 7.4% |  | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% |  | 3.511% | 3.511% | 3.511% | 3.511% | 3.511% |  | 1.75% | 1.75% | 1.75% | 1.75% | 1.75%
MC2 | 297 | 5.2% | 5.2% | 5.2% | 5.2% | 5.2% |  | 7.4% | 7.4% | 7.4% | 7.4% | 7.4% |  | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% |  | 3.511% | 3.511% | 3.511% | 3.511% | 3.511% |  | 1.75% | 1.75% | 1.75% | 1.75% | 1.75%
MC3 | 394 | 5.2% | 5.2% | 5.2% | 5.2% | 5.2% |  | 7.4% | 7.4% | 7.4% | 7.4% | 7.4% |  | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% |  | 3.511% | 3.511% | 3.511% | 3.511% | 3.511% |  | 1.75% | 1.75% | 1.75% | 1.75% | 1.75%
MC4 | 486 | 5.2% | 5.2% | 5.2% | 5.2% | 5.2% |  | 7.4% | 7.4% | 7.4% | 7.4% | 7.4% |  | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% |  | 3.511% | 3.511% | 3.511% | 3.511% | 3.511% |  | 1.75% | 1.75% | 1.75% | 1.75% | 1.75%
MILL CREEK | 1477 | 5.2% | 5.2% | 5.2% | 5.2% | 5.2% |  | 7.4% | 7.4% | 7.4% | 7.4% | 7.4% |  | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% |  | 3.511% | 3.511% | 3.511% | 3.511% | 3.511% |  | 1.75% | 1.75% | 1.75% | 1.75% | 1.75%
TC1 | 493 | 5.2% | 5.2% | 5.2% | 5.2% | 5.2% |  | 7.4% | 7.4% | 7.4% | 7.4% | 7.4% |  | 2.2% | 2.2% | 2.2% | 2.2% | 2.2% |  | 4.189% | 4.189% | 4.189% | 4.189% | 4.189% |  | 1.055% | 1.055% | 1.055% | 1.055% | 1.055%
TC2 | 760 | 9.3% | 9.3% | 9.3% | 9.3% | 9.3% |  | 13.1% | 13.1% | 13.1% | 13.1% | 13.1% |  | 3.8% | 3.8% | 3.8% | 3.8% | 3.8% |  | 8.141% | 8.141% | 8.141% | 8.141% | 8.141% |  | 1.262% | 1.262% | 1.262% | 1.262% | 1.262%
TRIMBLE CO. | 1253 | 7.687% | 7.687% | 7.687% | 7.687% | 7.687% |  | 10.86% | 10.86% | 10.86% | 10.86% | 10.86% |  | 3.17% | 3.17% | 3.17% | 3.17% | 3.17% |  | 6.621% | 6.621% | 6.621% | 6.621% | 6.621% |  | 1.142% | 1.142% | 1.142% | 1.142% | 1.142%
LGE/KU (coal only) | 5511 | 5.908% | 5.917% | 5.926% | 5.935% | 5.944% |  | 8.434% | 8.443% | 8.452% | 8.461% | 8.471% |  | 2.526% | 2.526% | 2.526% | 2.526% | 2.526% |  | 4.401% | 4.408% | 4.415% | 4.422% | 4.428% |  | 1.576% | 1.578% | 1.581% | 1.584% | 1.586%
5.848%

## Calc-Pivot HistoricalDerates
Event Category | Derate
Year | (All)
Size | (All)
Sum of Duration_Hrs
UnitName | Derate_RND | Total | UnitName | Derate_RND | Hours | MWAvail | UnitNo | Bin
BR1 | 2 | 0.23333 | BR1 | 2 | 0.23333 | 105 | 1 | 97
| 4 | 121.0833 | BR1 | 4 | 121.0833 | 103 | 1 | 97
| 7 | 2 | BR1 | 7 | 2 | 100 | 1 | 97
| 8 | 188.2 | BR1 | 8 | 188.2 | 99 | 1 | 97
| 12 | 42.4667 | BR1 | 12 | 42.4667 | 95 | 1 | 87
| 13 | 34.8 | BR1 | 13 | 34.8 | 94 | 1 | 87
| 18 | 48.7667 | BR1 | 18 | 48.7667 | 89 | 1 | 87
| 20 | 1.8833 | BR1 | 20 | 1.8833 | 87 | 1 | 87
| 22 | 4.25 | BR1 | 22 | 4.25 | 85 | 1 | 77
| 23 | 207.05 | BR1 | 23 | 207.05 | 84 | 1 | 77
| 26 | 0.066667 | BR1 | 26 | 0.066667 | 81 | 1 | 77
| 27 | 75.3667 | BR1 | 27 | 75.3667 | 80 | 1 | 77
| 32 | 83.7667 | BR1 | 32 | 83.7667 | 75 | 1 | 74
| 33 | 2.25 | BR1 | 33 | 2.25 | 74 | 1 | 74
| 37 | 5.4833 | BR1 | 37 | 5.4833 | 70 | 1 | 37
| 38 | 0.96667 | BR1 | 38 | 0.96667 | 69 | 1 | 37
| 45 | 0.91667 | BR1 | 45 | 0.91667 | 62 | 1 | 37
| 46 | 1.4 | BR1 | 46 | 1.4 | 61 | 1 | 37
| 48 | 3.8167 | BR1 | 48 | 3.8167 | 59 | 1 | 37
| 51 | 12.0833 | BR1 | 51 | 12.0833 | 56 | 1 | 37
| 52 | 2.75 | BR1 | 52 | 2.75 | 55 | 1 | 37
| 55 | 267.5667 | BR1 | 55 | 267.5667 | 52 | 1 | 37
| 60 | 7.0167 | BR1 | 60 | 7.0167 | 47 | 1 | 37
| 69 | 10.5167 | BR1 | 69 | 10.5167 | 38 | 1 | 37
| 95 | 0.25 | BR1 | 95 | 0.25 | 12 | 1 | 0
| 99 | 0.78333 | BR1 | 99 | 0.78333 | 8 | 1 | 0
BR2 | 8 | 4.0833 | BR2 | 8 | 4.0833 | 160 | 2 | 148
| 13 | 16.0667 | BR2 | 13 | 16.0667 | 155 | 2 | 148
| 18 | 51.4 | BR2 | 18 | 51.4 | 150 | 2 | 148
| 27 | 137.0167 | BR2 | 27 | 137.0167 | 141 | 2 | 128
| 32 | 9.8 | BR2 | 32 | 9.8 | 136 | 2 | 128
| 36 | 139.8333 | BR2 | 36 | 139.8333 | 132 | 2 | 128
| 41 | 102.5333 | BR2 | 41 | 102.5333 | 127 | 2 | 88
| 46 | 293.6167 | BR2 | 46 | 293.6167 | 122 | 2 | 88
| 50 | 41.2667 | BR2 | 50 | 41.2667 | 118 | 2 | 88
| 52 | 2.5 | BR2 | 52 | 2.5 | 116 | 2 | 88
| 55 | 19.6833 | BR2 | 55 | 19.6833 | 113 | 2 | 88
| 60 | 41.75 | BR2 | 60 | 41.75 | 108 | 2 | 88
| 64 | 188.4833 | BR2 | 64 | 188.4833 | 104 | 2 | 88
| 69 | 164.7833 | BR2 | 69 | 164.7833 | 99 | 2 | 88
| 74 | 2.9667 | BR2 | 74 | 2.9667 | 94 | 2 | 88
| 75 | 20.5333 | BR2 | 75 | 20.5333 | 93 | 2 | 88
| 83 | 7.8667 | BR2 | 83 | 7.8667 | 85 | 2 | 78
| 92 | 13 | BR2 | 92 | 13 | 76 | 2 | 64
| 112 | 1.7833 | BR2 | 112 | 1.7833 | 56 | 2 | 0
| 153 | 1.9667 | BR2 | 153 | 1.9667 | 15 | 2 | 0
| 158 | 8.4 | BR2 | 158 | 8.4 | 10 | 2 | 0
BR3 | 14 | 382.6833 | BR3 | 14 | 382.6833 | 399 | 3 | 373
| 19 | 254.1833 | BR3 | 19 | 254.1833 | 394 | 3 | 373
| 23 | 171.8667 | BR3 | 23 | 171.8667 | 390 | 3 | 373
| 25 | 0.28333 | BR3 | 25 | 0.28333 | 388 | 3 | 373
| 28 | 486.45 | BR3 | 28 | 486.45 | 385 | 3 | 373
| 32 | 184.6 | BR3 | 32 | 184.6 | 381 | 3 | 373
| 34 | 0.18333 | BR3 | 34 | 0.18333 | 379 | 3 | 373
| 43 | 0.43333 | BR3 | 43 | 0.43333 | 370 | 3 | 333
| 46 | 1.4 | BR3 | 46 | 1.4 | 367 | 3 | 333
| 50 | 26.0833 | BR3 | 50 | 26.0833 | 363 | 3 | 333
| 59 | 5.4667 | BR3 | 59 | 5.4667 | 354 | 3 | 333
| 60 | 3.8167 | BR3 | 60 | 3.8167 | 353 | 3 | 333
| 69 | 1.3833 | BR3 | 69 | 1.3833 | 344 | 3 | 333
| 73 | 788.3333 | BR3 | 73 | 788.3333 | 340 | 3 | 333
| 78 | 23.25 | BR3 | 78 | 23.25 | 335 | 3 | 333
| 82 | 19.2667 | BR3 | 82 | 19.2667 | 331 | 3 | 253
| 87 | 418.3 | BR3 | 87 | 418.3 | 326 | 3 | 253
| 91 | 55.25 | BR3 | 91 | 55.25 | 322 | 3 | 253
| 96 | 217.1333 | BR3 | 96 | 217.1333 | 317 | 3 | 253
| 100 | 1.1 | BR3 | 100 | 1.1 | 313 | 3 | 253
| 105 | 24.7167 | BR3 | 105 | 24.7167 | 308 | 3 | 253
| 109 | 4.15 | BR3 | 109 | 4.15 | 304 | 3 | 253
| 114 | 9.7 | BR3 | 114 | 9.7 | 299 | 3 | 253
| 118 | 208.1 | BR3 | 118 | 208.1 | 295 | 3 | 253
| 123 | 689.8 | BR3 | 123 | 689.8 | 290 | 3 | 253
| 127 | 9.35 | BR3 | 127 | 9.35 | 286 | 3 | 253
| 130 | 61.0833 | BR3 | 130 | 61.0833 | 283 | 3 | 253
| 132 | 889.15 | BR3 | 132 | 889.15 | 281 | 3 | 253
| 136 | 29.8 | BR3 | 136 | 29.8 | 277 | 3 | 253
| 141 | 111.05 | BR3 | 141 | 111.05 | 272 | 3 | 253
| 145 | 0.81667 | BR3 | 145 | 0.81667 | 268 | 3 | 253
| 148 | 0.1 | BR3 | 148 | 0.1 | 265 | 3 | 253
| 150 | 112.1333 | BR3 | 150 | 112.1333 | 263 | 3 | 253
| 154 | 4.5167 | BR3 | 154 | 4.5167 | 259 | 3 | 253
| 159 | 31.0833 | BR3 | 159 | 31.0833 | 254 | 3 | 253
| 163 | 3.1 | BR3 | 163 | 3.1 | 250 | 3 | 223
| 168 | 0.81667 | BR3 | 168 | 0.81667 | 245 | 3 | 223
| 177 | 1.55 | BR3 | 177 | 1.55 | 236 | 3 | 223
| 186 | 21.1667 | BR3 | 186 | 21.1667 | 227 | 3 | 223
| 190 | 0.6 | BR3 | 190 | 0.6 | 223 | 3 | 223
| 195 | 8.05 | BR3 | 195 | 8.05 | 218 | 3 | 140
| 208 | 3.6667 | BR3 | 208 | 3.6667 | 205 | 3 | 140
| 231 | 0.73333 | BR3 | 231 | 0.73333 | 182 | 3 | 140
| 249 | 44.6 | BR3 | 249 | 44.6 | 164 | 3 | 140
| 267 | 2.1333 | BR3 | 267 | 2.1333 | 146 | 3 | 140
| 280 | 0.66667 | BR3 | 280 | 0.66667 | 133 | 3 | 0
| 285 | 3.2667 | BR3 | 285 | 3.2667 | 128 | 3 | 0
| 316 | 0.73333 | BR3 | 316 | 0.73333 | 97 | 3 | 0
| 325 | 0.46667 | BR3 | 325 | 0.46667 | 88 | 3 | 0
| 336 | 5.3667 | BR3 | 336 | 5.3667 | 77 | 3 | 0
| 351 | 4.5333 | BR3 | 351 | 4.5333 | 62 | 3 | 0
| 357 | 0.5 | BR3 | 357 | 0.5 | 56 | 3 | 0
| 360 | 3.2833 | BR3 | 360 | 3.2833 | 53 | 3 | 0
| 361 | 5.4 | BR3 | 361 | 5.4 | 52 | 3 | 0
| 369 | 4.65 | BR3 | 369 | 4.65 | 44 | 3 | 0
| 388 | 1.8833 | BR3 | 388 | 1.8833 | 25 | 3 | 0
GH1 | 9 | 924.2 | GH1 | 9 | 924.2 | 470 | 4 | 439
| 13 | 3.4 | GH1 | 13 | 3.4 | 466 | 4 | 439
| 18 | 339.1833 | GH1 | 18 | 339.1833 | 461 | 4 | 439
| 24 | 2.7333 | GH1 | 24 | 2.7333 | 455 | 4 | 439
| 28 | 24.25 | GH1 | 28 | 24.25 | 451 | 4 | 439
| 32 | 3.3667 | GH1 | 32 | 3.3667 | 447 | 4 | 439
| 37 | 33.1667 | GH1 | 37 | 33.1667 | 442 | 4 | 439
| 38 | 4.9333 | GH1 | 38 | 4.9333 | 441 | 4 | 439
| 39 | 1.4 | GH1 | 39 | 1.4 | 440 | 4 | 439
| 41 | 15.1 | GH1 | 41 | 15.1 | 438 | 4 | 399
| 46 | 44.4667 | GH1 | 46 | 44.4667 | 433 | 4 | 399
| 50 | 3.6833 | GH1 | 50 | 3.6833 | 429 | 4 | 399
| 55 | 875.9667 | GH1 | 55 | 875.9667 | 424 | 4 | 399
| 60 | 1.4333 | GH1 | 60 | 1.4333 | 419 | 4 | 399
| 64 | 1354.5667 | GH1 | 64 | 1354.5667 | 415 | 4 | 399
| 67 | 11.2667 | GH1 | 67 | 11.2667 | 412 | 4 | 399
| 73 | 47.35 | GH1 | 73 | 47.35 | 406 | 4 | 399
| 78 | 2.5833 | GH1 | 78 | 2.5833 | 401 | 4 | 399
| 83 | 52.1667 | GH1 | 83 | 52.1667 | 396 | 4 | 319
| 87 | 8.3 | GH1 | 87 | 8.3 | 392 | 4 | 319
| 92 | 4.3 | GH1 | 92 | 4.3 | 387 | 4 | 319
| 96 | 3.1833 | GH1 | 96 | 3.1833 | 383 | 4 | 319
| 100 | 3.1833 | GH1 | 100 | 3.1833 | 379 | 4 | 319
| 101 | 5.3167 | GH1 | 101 | 5.3167 | 378 | 4 | 319
| 105 | 2.7667 | GH1 | 105 | 2.7667 | 374 | 4 | 319
| 110 | 26.95 | GH1 | 110 | 26.95 | 369 | 4 | 319
| 119 | 46.3833 | GH1 | 119 | 46.3833 | 360 | 4 | 319
| 133 | 11.3667 | GH1 | 133 | 11.3667 | 346 | 4 | 319
| 138 | 0.53333 | GH1 | 138 | 0.53333 | 341 | 4 | 319
| 142 | 0.85 | GH1 | 142 | 0.85 | 337 | 4 | 319
| 156 | 31.5 | GH1 | 156 | 31.5 | 323 | 4 | 319
| 165 | 0.56667 | GH1 | 165 | 0.56667 | 314 | 4 | 289
| 167 | 48.2667 | GH1 | 167 | 48.2667 | 312 | 4 | 289
| 174 | 17.7833 | GH1 | 174 | 17.7833 | 305 | 4 | 289
| 179 | 1.7667 | GH1 | 179 | 1.7667 | 300 | 4 | 289
| 183 | 2.3167 | GH1 | 183 | 2.3167 | 296 | 4 | 289
| 186 | 187.1667 | GH1 | 186 | 187.1667 | 293 | 4 | 289
| 188 | 0.61667 | GH1 | 188 | 0.61667 | 291 | 4 | 289
| 202 | 3.9667 | GH1 | 202 | 3.9667 | 277 | 4 | 218
| 204 | 79.95 | GH1 | 204 | 79.95 | 275 | 4 | 218
| 257 | 36.4667 | GH1 | 257 | 36.4667 | 222 | 4 | 218
| 271 | 4.3333 | GH1 | 271 | 4.3333 | 208 | 4 | 0
| 275 | 14.4333 | GH1 | 275 | 14.4333 | 204 | 4 | 0
| 280 | 11.1833 | GH1 | 280 | 11.1833 | 199 | 4 | 0
| 294 | 112.1 | GH1 | 294 | 112.1 | 185 | 4 | 0
| 303 | 9 | GH1 | 303 | 9 | 176 | 4 | 0
| 312 | 4.3167 | GH1 | 312 | 4.3167 | 167 | 4 | 0
| 385 | 1.3333 | GH1 | 385 | 1.3333 | 94 | 4 | 0
| 444 | 0.51667 | GH1 | 444 | 0.51667 | 35 | 4 | 0
GH2 | 0 | 521.9 | GH2 | 0 | 521.9 | 486 | 5 | 446
| 6 | 7.7 | GH2 | 6 | 7.7 | 480 | 5 | 446
| 8 | 0.7 | GH2 | 8 | 0.7 | 478 | 5 | 446
| 9 | 77.9667 | GH2 | 9 | 77.9667 | 477 | 5 | 446
| 12 | 1.2667 | GH2 | 12 | 1.2667 | 474 | 5 | 446
| 14 | 309.3333 | GH2 | 14 | 309.3333 | 472 | 5 | 446
| 19 | 2.5833 | GH2 | 19 | 2.5833 | 467 | 5 | 446
| 23 | 4.5 | GH2 | 23 | 4.5 | 463 | 5 | 446
| 28 | 28.7 | GH2 | 28 | 28.7 | 458 | 5 | 446
| 33 | 17.5667 | GH2 | 33 | 17.5667 | 453 | 5 | 446
| 35 | 305.65 | GH2 | 35 | 305.65 | 451 | 5 | 446
| 37 | 59.95 | GH2 | 37 | 59.95 | 449 | 5 | 446
| 40 | 3.1 | GH2 | 40 | 3.1 | 446 | 5 | 446
| 42 | 9.2167 | GH2 | 42 | 9.2167 | 444 | 5 | 406
| 47 | 16.9 | GH2 | 47 | 16.9 | 439 | 5 | 406
| 51 | 17.6833 | GH2 | 51 | 17.6833 | 435 | 5 | 406
| 54 | 1.85 | GH2 | 54 | 1.85 | 432 | 5 | 406
| 56 | 1593.6833 | GH2 | 56 | 1593.6833 | 430 | 5 | 406
| 60 | 2 | GH2 | 60 | 2 | 426 | 5 | 406
| 61 | 12.1167 | GH2 | 61 | 12.1167 | 425 | 5 | 406
| 65 | 312.0833 | GH2 | 65 | 312.0833 | 421 | 5 | 406
| 67 | 3.8 | GH2 | 67 | 3.8 | 419 | 5 | 406
| 75 | 80.5 | GH2 | 75 | 80.5 | 411 | 5 | 406
| 77 | 31.7 | GH2 | 77 | 31.7 | 409 | 5 | 406
| 84 | 11.6667 | GH2 | 84 | 11.6667 | 402 | 5 | 326
| 87 | 0.8 | GH2 | 87 | 0.8 | 399 | 5 | 326
| 89 | 0.4 | GH2 | 89 | 0.4 | 397 | 5 | 326
| 90 | 28.2 | GH2 | 90 | 28.2 | 396 | 5 | 326
| 93 | 37.5 | GH2 | 93 | 37.5 | 393 | 5 | 326
| 96 | 4.7167 | GH2 | 96 | 4.7167 | 390 | 5 | 326
| 103 | 2.2167 | GH2 | 103 | 2.2167 | 383 | 5 | 326
| 105 | 1.8333 | GH2 | 105 | 1.8333 | 381 | 5 | 326
| 107 | 11.3333 | GH2 | 107 | 11.3333 | 379 | 5 | 326
| 112 | 11.1 | GH2 | 112 | 11.1 | 374 | 5 | 326
| 120 | 36.4667 | GH2 | 120 | 36.4667 | 366 | 5 | 326
| 122 | 5.45 | GH2 | 122 | 5.45 | 364 | 5 | 326
| 125 | 0.7 | GH2 | 125 | 0.7 | 361 | 5 | 326
| 135 | 5.6833 | GH2 | 135 | 5.6833 | 351 | 5 | 326
| 136 | 56.6 | GH2 | 136 | 56.6 | 350 | 5 | 326
| 140 | 6.7833 | GH2 | 140 | 6.7833 | 346 | 5 | 326
| 150 | 24.5833 | GH2 | 150 | 24.5833 | 336 | 5 | 326
| 159 | 24.1667 | GH2 | 159 | 24.1667 | 327 | 5 | 326
| 162 | 0.66667 | GH2 | 162 | 0.66667 | 324 | 5 | 296
| 164 | 12.4 | GH2 | 164 | 12.4 | 322 | 5 | 296
| 168 | 2.7 | GH2 | 168 | 2.7 | 318 | 5 | 296
| 178 | 3.8833 | GH2 | 178 | 3.8833 | 308 | 5 | 296
| 182 | 4.2667 | GH2 | 182 | 4.2667 | 304 | 5 | 296
| 187 | 20.15 | GH2 | 187 | 20.15 | 299 | 5 | 296
| 206 | 15.6 | GH2 | 206 | 15.6 | 280 | 5 | 225
| 207 | 4.3 | GH2 | 207 | 4.3 | 279 | 5 | 225
| 220 | 0.71667 | GH2 | 220 | 0.71667 | 266 | 5 | 225
| 224 | 2.1833 | GH2 | 224 | 2.1833 | 262 | 5 | 225
| 243 | 0.95 | GH2 | 243 | 0.95 | 243 | 5 | 225
| 248 | 3.5333 | GH2 | 248 | 3.5333 | 238 | 5 | 225
| 252 | 24.7167 | GH2 | 252 | 24.7167 | 234 | 5 | 225
| 262 | 7.95 | GH2 | 262 | 7.95 | 224 | 5 | 0
| 273 | 1.3 | GH2 | 273 | 1.3 | 213 | 5 | 0
| 276 | 1.1333 | GH2 | 276 | 1.1333 | 210 | 5 | 0
| 280 | 0.88333 | GH2 | 280 | 0.88333 | 206 | 5 | 0
| 281 | 7.9833 | GH2 | 281 | 7.9833 | 205 | 5 | 0
| 290 | 5 | GH2 | 290 | 5 | 196 | 5 | 0
| 299 | 45.2 | GH2 | 299 | 45.2 | 187 | 5 | 0
| 308 | 2.1667 | GH2 | 308 | 2.1667 | 178 | 5 | 0
| 318 | 0.33333 | GH2 | 318 | 0.33333 | 168 | 5 | 0
| 377 | 6.1833 | GH2 | 377 | 6.1833 | 109 | 5 | 0
| 412 | 2.9167 | GH2 | 412 | 2.9167 | 74 | 5 | 0
| 422 | 4.2 | GH2 | 422 | 4.2 | 64 | 5 | 0
| 463 | 4.3667 | GH2 | 463 | 4.3667 | 23 | 5 | 0
GH3 | 0 | 181.6833 | GH3 | 0 | 181.6833 | 481 | 6 | 441
| 2 | 42.6 | GH3 | 2 | 42.6 | 479 | 6 | 441
| 3 | 348.2667 | GH3 | 3 | 348.2667 | 478 | 6 | 441
| 5 | 407.4167 | GH3 | 5 | 407.4167 | 476 | 6 | 441
| 7 | 2139.1833 | GH3 | 7 | 2139.1833 | 474 | 6 | 441
| 9 | 48.6333 | GH3 | 9 | 48.6333 | 472 | 6 | 441
| 10 | 3.6833 | GH3 | 10 | 3.6833 | 471 | 6 | 441
| 11 | 507.1 | GH3 | 11 | 507.1 | 470 | 6 | 441
| 12 | 2075.1833 | GH3 | 12 | 2075.1833 | 469 | 6 | 441
| 13 | 82.1167 | GH3 | 13 | 82.1167 | 468 | 6 | 441
| 15 | 142.7 | GH3 | 15 | 142.7 | 466 | 6 | 441
| 16 | 160.0667 | GH3 | 16 | 160.0667 | 465 | 6 | 441
| 18 | 76.45 | GH3 | 18 | 76.45 | 463 | 6 | 441
| 21 | 469.3833 | GH3 | 21 | 469.3833 | 460 | 6 | 441
| 22 | 161.5667 | GH3 | 22 | 161.5667 | 459 | 6 | 441
| 24 | 0.91667 | GH3 | 24 | 0.91667 | 457 | 6 | 441
| 25 | 61.1167 | GH3 | 25 | 61.1167 | 456 | 6 | 441
| 33 | 20.85 | GH3 | 33 | 20.85 | 448 | 6 | 441
| 34 | 126.55 | GH3 | 34 | 126.55 | 447 | 6 | 441
| 36 | 30.0167 | GH3 | 36 | 30.0167 | 445 | 6 | 441
| 39 | 2.6 | GH3 | 39 | 2.6 | 442 | 6 | 441
| 41 | 12.9333 | GH3 | 41 | 12.9333 | 440 | 6 | 401
| 42 | 1.9 | GH3 | 42 | 1.9 | 439 | 6 | 401
| 44 | 20.7167 | GH3 | 44 | 20.7167 | 437 | 6 | 401
| 48 | 5.1833 | GH3 | 48 | 5.1833 | 433 | 6 | 401
| 50 | 14.9833 | GH3 | 50 | 14.9833 | 431 | 6 | 401
| 53 | 22.7667 | GH3 | 53 | 22.7667 | 428 | 6 | 401
| 57 | 7.5833 | GH3 | 57 | 7.5833 | 424 | 6 | 401
| 62 | 4.05 | GH3 | 62 | 4.05 | 419 | 6 | 401
| 63 | 31.1167 | GH3 | 63 | 31.1167 | 418 | 6 | 401
| 64 | 5.0333 | GH3 | 64 | 5.0333 | 417 | 6 | 401
| 67 | 16.8167 | GH3 | 67 | 16.8167 | 414 | 6 | 401
| 71 | 38.2167 | GH3 | 71 | 38.2167 | 410 | 6 | 401
| 75 | 7.4 | GH3 | 75 | 7.4 | 406 | 6 | 401
| 80 | 2.1 | GH3 | 80 | 2.1 | 401 | 6 | 401
| 84 | 4.35 | GH3 | 84 | 4.35 | 397 | 6 | 321
| 85 | 0.83333 | GH3 | 85 | 0.83333 | 396 | 6 | 321
| 86 | 4.1167 | GH3 | 86 | 4.1167 | 395 | 6 | 321
| 89 | 2 | GH3 | 89 | 2 | 392 | 6 | 321
| 93 | 174.6833 | GH3 | 93 | 174.6833 | 388 | 6 | 321
| 94 | 0.66667 | GH3 | 94 | 0.66667 | 387 | 6 | 321
| 98 | 25.8333 | GH3 | 98 | 25.8333 | 383 | 6 | 321
| 103 | 0.45 | GH3 | 103 | 0.45 | 378 | 6 | 321
| 107 | 2.9333 | GH3 | 107 | 2.9333 | 374 | 6 | 321
| 116 | 11.2333 | GH3 | 116 | 11.2333 | 365 | 6 | 321
| 118 | 0.91667 | GH3 | 118 | 0.91667 | 363 | 6 | 321
| 125 | 0.96667 | GH3 | 125 | 0.96667 | 356 | 6 | 321
| 134 | 1.3333 | GH3 | 134 | 1.3333 | 347 | 6 | 321
| 136 | 11.5167 | GH3 | 136 | 11.5167 | 345 | 6 | 321
| 139 | 2.3333 | GH3 | 139 | 2.3333 | 342 | 6 | 321
| 161 | 3.5833 | GH3 | 161 | 3.5833 | 320 | 6 | 291
| 171 | 0.81667 | GH3 | 171 | 0.81667 | 310 | 6 | 291
| 184 | 22.9833 | GH3 | 184 | 22.9833 | 297 | 6 | 291
| 189 | 1.4 | GH3 | 189 | 1.4 | 292 | 6 | 291
| 202 | 10.5833 | GH3 | 202 | 10.5833 | 279 | 6 | 210
| 207 | 10.6167 | GH3 | 207 | 10.6167 | 274 | 6 | 210
| 216 | 11.3333 | GH3 | 216 | 11.3333 | 265 | 6 | 210
| 220 | 1.5667 | GH3 | 220 | 1.5667 | 261 | 6 | 210
| 230 | 1.4 | GH3 | 230 | 1.4 | 251 | 6 | 210
| 243 | 0.41667 | GH3 | 243 | 0.41667 | 238 | 6 | 210
| 252 | 66.9833 | GH3 | 252 | 66.9833 | 229 | 6 | 210
| 261 | 2.5833 | GH3 | 261 | 2.5833 | 220 | 6 | 210
| 270 | 4.6333 | GH3 | 270 | 4.6333 | 211 | 6 | 210
| 271 | 6.4667 | GH3 | 271 | 6.4667 | 210 | 6 | 210
| 279 | 7.45 | GH3 | 279 | 7.45 | 202 | 6 | 0
| 284 | 3.5 | GH3 | 284 | 3.5 | 197 | 6 | 0
| 288 | 3.5833 | GH3 | 288 | 3.5833 | 193 | 6 | 0
| 290 | 4.8333 | GH3 | 290 | 4.8333 | 191 | 6 | 0
| 293 | 21.0167 | GH3 | 293 | 21.0167 | 188 | 6 | 0
| 298 | 84.85 | GH3 | 298 | 84.85 | 183 | 6 | 0
| 308 | 69.75 | GH3 | 308 | 69.75 | 173 | 6 | 0
| 316 | 13.5167 | GH3 | 316 | 13.5167 | 165 | 6 | 0
| 338 | 0.43333 | GH3 | 338 | 0.43333 | 143 | 6 | 0
| 366 | 1.8667 | GH3 | 366 | 1.8667 | 115 | 6 | 0
| 470 | 18.75 | GH3 | 470 | 18.75 | 11 | 6 | 0
GH4 | 0 | 974.5167 | GH4 | 0 | 974.5167 | 478 | 7 | 438
| 4 | 547.0667 | GH4 | 4 | 547.0667 | 474 | 7 | 438
| 5 | 1.5833 | GH4 | 5 | 1.5833 | 473 | 7 | 438
| 6 | 0.16667 | GH4 | 6 | 0.16667 | 472 | 7 | 438
| 9 | 4629.35 | GH4 | 9 | 4629.35 | 469 | 7 | 438
| 12 | 58.9333 | GH4 | 12 | 58.9333 | 466 | 7 | 438
| 13 | 296.6667 | GH4 | 13 | 296.6667 | 465 | 7 | 438
| 14 | 797.2333 | GH4 | 14 | 797.2333 | 464 | 7 | 438
| 15 | 1.9333 | GH4 | 15 | 1.9333 | 463 | 7 | 438
| 16 | 2.1667 | GH4 | 16 | 2.1667 | 462 | 7 | 438
| 18 | 121.85 | GH4 | 18 | 121.85 | 460 | 7 | 438
| 23 | 402.3167 | GH4 | 23 | 402.3167 | 455 | 7 | 438
| 27 | 16.0167 | GH4 | 27 | 16.0167 | 451 | 7 | 438
| 29 | 21.6 | GH4 | 29 | 21.6 | 449 | 7 | 438
| 30 | 11.75 | GH4 | 30 | 11.75 | 448 | 7 | 438
| 32 | 49.5833 | GH4 | 32 | 49.5833 | 446 | 7 | 438
| 36 | 2.2667 | GH4 | 36 | 2.2667 | 442 | 7 | 438
| 39 | 10 | GH4 | 39 | 10 | 439 | 7 | 438
| 41 | 5.4833 | GH4 | 41 | 5.4833 | 437 | 7 | 398
| 44 | 19.55 | GH4 | 44 | 19.55 | 434 | 7 | 398
| 46 | 3.8333 | GH4 | 46 | 3.8333 | 432 | 7 | 398
| 49 | 6.7333 | GH4 | 49 | 6.7333 | 429 | 7 | 398
| 50 | 4.1 | GH4 | 50 | 4.1 | 428 | 7 | 398
| 51 | 6.5167 | GH4 | 51 | 6.5167 | 427 | 7 | 398
| 53 | 3.3333 | GH4 | 53 | 3.3333 | 425 | 7 | 398
| 59 | 5.1 | GH4 | 59 | 5.1 | 419 | 7 | 398
| 68 | 24.7167 | GH4 | 68 | 24.7167 | 410 | 7 | 398
| 71 | 10.25 | GH4 | 71 | 10.25 | 407 | 7 | 398
| 73 | 5.2 | GH4 | 73 | 5.2 | 405 | 7 | 398
| 76 | 31.6333 | GH4 | 76 | 31.6333 | 402 | 7 | 398
| 77 | 8.65 | GH4 | 77 | 8.65 | 401 | 7 | 398
| 84 | 0.43333 | GH4 | 84 | 0.43333 | 394 | 7 | 318
| 86 | 3.1667 | GH4 | 86 | 3.1667 | 392 | 7 | 318
| 91 | 25.6 | GH4 | 91 | 25.6 | 387 | 7 | 318
| 96 | 11.3 | GH4 | 96 | 11.3 | 382 | 7 | 318
| 101 | 1.5167 | GH4 | 101 | 1.5167 | 377 | 7 | 318
| 104 | 0.23333 | GH4 | 104 | 0.23333 | 374 | 7 | 318
| 105 | 2.65 | GH4 | 105 | 2.65 | 373 | 7 | 318
| 106 | 4 | GH4 | 106 | 4 | 372 | 7 | 318
| 109 | 1.7333 | GH4 | 109 | 1.7333 | 369 | 7 | 318
| 111 | 1.0667 | GH4 | 111 | 1.0667 | 367 | 7 | 318
| 114 | 7.45 | GH4 | 114 | 7.45 | 364 | 7 | 318
| 123 | 0.75 | GH4 | 123 | 0.75 | 355 | 7 | 318
| 137 | 3.75 | GH4 | 137 | 3.75 | 341 | 7 | 318
| 141 | 2.45 | GH4 | 141 | 2.45 | 337 | 7 | 318
| 143 | 63.3333 | GH4 | 143 | 63.3333 | 335 | 7 | 318
| 150 | 1.0333 | GH4 | 150 | 1.0333 | 328 | 7 | 318
| 159 | 7.2833 | GH4 | 159 | 7.2833 | 319 | 7 | 318
| 165 | 3.4333 | GH4 | 165 | 3.4333 | 313 | 7 | 288
| 168 | 0.81667 | GH4 | 168 | 0.81667 | 310 | 7 | 288
| 175 | 11.7333 | GH4 | 175 | 11.7333 | 303 | 7 | 288
| 178 | 1 | GH4 | 178 | 1 | 300 | 7 | 288
| 196 | 7.0667 | GH4 | 196 | 7.0667 | 282 | 7 | 215
| 200 | 0.3 | GH4 | 200 | 0.3 | 278 | 7 | 215
| 205 | 8.15 | GH4 | 205 | 8.15 | 273 | 7 | 215
| 214 | 6.7833 | GH4 | 214 | 6.7833 | 264 | 7 | 215
| 223 | 2.5167 | GH4 | 223 | 2.5167 | 255 | 7 | 215
| 224 | 3.5167 | GH4 | 224 | 3.5167 | 254 | 7 | 215
| 232 | 3.4 | GH4 | 232 | 3.4 | 246 | 7 | 215
| 259 | 5.3167 | GH4 | 259 | 5.3167 | 219 | 7 | 215
| 269 | 3.7167 | GH4 | 269 | 3.7167 | 209 | 7 | 0
| 273 | 1.5333 | GH4 | 273 | 1.5333 | 205 | 7 | 0
| 278 | 5 | GH4 | 278 | 5 | 200 | 7 | 0
| 282 | 4.7167 | GH4 | 282 | 4.7167 | 196 | 7 | 0
| 287 | 15.9667 | GH4 | 287 | 15.9667 | 191 | 7 | 0
| 296 | 150.1333 | GH4 | 296 | 150.1333 | 182 | 7 | 0
| 305 | 134.2333 | GH4 | 305 | 134.2333 | 173 | 7 | 0
| 314 | 0.86667 | GH4 | 314 | 0.86667 | 164 | 7 | 0
| 332 | 6.5 | GH4 | 332 | 6.5 | 146 | 7 | 0
| 375 | 1.8 | GH4 | 375 | 1.8 | 103 | 7 | 0
MC1 | 5 | 65.0667 | MC1 | 5 | 65.0667 | 295 | 10 | 280
| 6 | 7.3333 | MC1 | 6 | 7.3333 | 294 | 10 | 280
| 9 | 74.2667 | MC1 | 9 | 74.2667 | 291 | 10 | 280
| 11 | 0.91667 | MC1 | 11 | 0.91667 | 289 | 10 | 280
| 12 | 2.6667 | MC1 | 12 | 2.6667 | 288 | 10 | 280
| 14 | 87.8833 | MC1 | 14 | 87.8833 | 286 | 10 | 280
| 18 | 195.45 | MC1 | 18 | 195.45 | 282 | 10 | 280
| 19 | 7.3 | MC1 | 19 | 7.3 | 281 | 10 | 280
| 23 | 18.9333 | MC1 | 23 | 18.9333 | 277 | 10 | 260
| 24 | 6.45 | MC1 | 24 | 6.45 | 276 | 10 | 260
| 25 | 6.0667 | MC1 | 25 | 6.0667 | 275 | 10 | 260
| 27 | 119.6667 | MC1 | 27 | 119.6667 | 273 | 10 | 260
| 29 | 8.0833 | MC1 | 29 | 8.0833 | 271 | 10 | 260
| 32 | 14.2833 | MC1 | 32 | 14.2833 | 268 | 10 | 260
| 35 | 26.1167 | MC1 | 35 | 26.1167 | 265 | 10 | 260
| 36 | 41.7 | MC1 | 36 | 41.7 | 264 | 10 | 260
| 40 | 1.4167 | MC1 | 40 | 1.4167 | 260 | 10 | 260
| 41 | 13.0833 | MC1 | 41 | 13.0833 | 259 | 10 | 220
| 45 | 95.85 | MC1 | 45 | 95.85 | 255 | 10 | 220
| 47 | 4.2833 | MC1 | 47 | 4.2833 | 253 | 10 | 220
| 48 | 2.9667 | MC1 | 48 | 2.9667 | 252 | 10 | 220
| 50 | 64.2 | MC1 | 50 | 64.2 | 250 | 10 | 220
| 55 | 342.0333 | MC1 | 55 | 342.0333 | 245 | 10 | 220
| 56 | 9.4833 | MC1 | 56 | 9.4833 | 244 | 10 | 220
| 58 | 5.7167 | MC1 | 58 | 5.7167 | 242 | 10 | 220
| 59 | 18.85 | MC1 | 59 | 18.85 | 241 | 10 | 220
| 60 | 0.43333 | MC1 | 60 | 0.43333 | 240 | 10 | 220
| 61 | 12.1833 | MC1 | 61 | 12.1833 | 239 | 10 | 220
| 63 | 0.33333 | MC1 | 63 | 0.33333 | 237 | 10 | 220
| 64 | 74.4 | MC1 | 64 | 74.4 | 236 | 10 | 220
| 68 | 31.0833 | MC1 | 68 | 31.0833 | 232 | 10 | 220
| 69 | 0.53333 | MC1 | 69 | 0.53333 | 231 | 10 | 220
| 71 | 1.1167 | MC1 | 71 | 1.1167 | 229 | 10 | 220
| 73 | 474.6667 | MC1 | 73 | 474.6667 | 227 | 10 | 220
| 75 | 2.4167 | MC1 | 75 | 2.4167 | 225 | 10 | 220
| 77 | 277.4167 | MC1 | 77 | 277.4167 | 223 | 10 | 220
| 82 | 591.8 | MC1 | 82 | 591.8 | 218 | 10 | 210
| 83 | 2.4167 | MC1 | 83 | 2.4167 | 217 | 10 | 210
| 85 | 59.4 | MC1 | 85 | 59.4 | 215 | 10 | 210
| 86 | 27.9667 | MC1 | 86 | 27.9667 | 214 | 10 | 210
| 87 | 2.2333 | MC1 | 87 | 2.2333 | 213 | 10 | 210
| 89 | 1.2 | MC1 | 89 | 1.2 | 211 | 10 | 210
| 91 | 168.5667 | MC1 | 91 | 168.5667 | 209 | 10 | 150
| 95 | 14.0833 | MC1 | 95 | 14.0833 | 205 | 10 | 150
| 96 | 1.5 | MC1 | 96 | 1.5 | 204 | 10 | 150
| 100 | 24.9667 | MC1 | 100 | 24.9667 | 200 | 10 | 150
| 105 | 3.25 | MC1 | 105 | 3.25 | 195 | 10 | 150
| 106 | 9.15 | MC1 | 106 | 9.15 | 194 | 10 | 150
| 107 | 3.2833 | MC1 | 107 | 3.2833 | 193 | 10 | 150
| 109 | 1.4167 | MC1 | 109 | 1.4167 | 191 | 10 | 150
| 114 | 2.9167 | MC1 | 114 | 2.9167 | 186 | 10 | 150
| 118 | 20.9167 | MC1 | 118 | 20.9167 | 182 | 10 | 150
| 123 | 8.5667 | MC1 | 123 | 8.5667 | 177 | 10 | 150
| 124 | 1.8667 | MC1 | 124 | 1.8667 | 176 | 10 | 150
| 127 | 6.05 | MC1 | 127 | 6.05 | 173 | 10 | 150
| 132 | 4.5333 | MC1 | 132 | 4.5333 | 168 | 10 | 150
| 136 | 5.8 | MC1 | 136 | 5.8 | 164 | 10 | 150
| 140 | 0.9 | MC1 | 140 | 0.9 | 160 | 10 | 150
| 141 | 10.7333 | MC1 | 141 | 10.7333 | 159 | 10 | 150
| 150 | 5.25 | MC1 | 150 | 5.25 | 150 | 10 | 150
| 155 | 6.4 | MC1 | 155 | 6.4 | 145 | 10 | 0
| 156 | 3.4833 | MC1 | 156 | 3.4833 | 144 | 10 | 0
| 159 | 2.8 | MC1 | 159 | 2.8 | 141 | 10 | 0
| 164 | 26.5333 | MC1 | 164 | 26.5333 | 136 | 10 | 0
| 165 | 3.2 | MC1 | 165 | 3.2 | 135 | 10 | 0
| 167 | 9.3833 | MC1 | 167 | 9.3833 | 133 | 10 | 0
| 168 | 6.9167 | MC1 | 168 | 6.9167 | 132 | 10 | 0
| 173 | 7.4167 | MC1 | 173 | 7.4167 | 127 | 10 | 0
| 177 | 11.3 | MC1 | 177 | 11.3 | 123 | 10 | 0
| 180 | 3.25 | MC1 | 180 | 3.25 | 120 | 10 | 0
| 182 | 19.45 | MC1 | 182 | 19.45 | 118 | 10 | 0
| 186 | 12.8667 | MC1 | 186 | 12.8667 | 114 | 10 | 0
| 191 | 22.2667 | MC1 | 191 | 22.2667 | 109 | 10 | 0
| 209 | 7 | MC1 | 209 | 7 | 91 | 10 | 0
| 227 | 1.1667 | MC1 | 227 | 1.1667 | 73 | 10 | 0
| 241 | 0.81667 | MC1 | 241 | 0.81667 | 59 | 10 | 0
| 255 | 1.95 | MC1 | 255 | 1.95 | 45 | 10 | 0
MC2 | 4 | 4.2333 | MC2 | 4 | 4.2333 | 293 | 11 | 277
| 5 | 980.8 | MC2 | 5 | 980.8 | 292 | 11 | 277
| 6 | 8.9167 | MC2 | 6 | 8.9167 | 291 | 11 | 277
| 7 | 22.3167 | MC2 | 7 | 22.3167 | 290 | 11 | 277
| 8 | 13.25 | MC2 | 8 | 13.25 | 289 | 11 | 277
| 9 | 1056.1333 | MC2 | 9 | 1056.1333 | 288 | 11 | 277
| 10 | 1937.5167 | MC2 | 10 | 1937.5167 | 287 | 11 | 277
| 11 | 2110.6833 | MC2 | 11 | 2110.6833 | 286 | 11 | 277
| 12 | 23.0167 | MC2 | 12 | 23.0167 | 285 | 11 | 277
| 13 | 152.1833 | MC2 | 13 | 152.1833 | 284 | 11 | 277
| 14 | 3.7 | MC2 | 14 | 3.7 | 283 | 11 | 277
| 15 | 5.55 | MC2 | 15 | 5.55 | 282 | 11 | 277
| 16 | 1.6333 | MC2 | 16 | 1.6333 | 281 | 11 | 277
| 18 | 421.85 | MC2 | 18 | 421.85 | 279 | 11 | 277
| 20 | 65.2333 | MC2 | 20 | 65.2333 | 277 | 11 | 277
| 22 | 6.2 | MC2 | 22 | 6.2 | 275 | 11 | 257
| 26 | 1.55 | MC2 | 26 | 1.55 | 271 | 11 | 257
| 27 | 63.35 | MC2 | 27 | 63.35 | 270 | 11 | 257
| 30 | 15.5333 | MC2 | 30 | 15.5333 | 267 | 11 | 257
| 31 | 25.1833 | MC2 | 31 | 25.1833 | 266 | 11 | 257
| 33 | 4.1333 | MC2 | 33 | 4.1333 | 264 | 11 | 257
| 36 | 119.3333 | MC2 | 36 | 119.3333 | 261 | 11 | 257
| 40 | 56.0333 | MC2 | 40 | 56.0333 | 257 | 11 | 257
| 41 | 4.5667 | MC2 | 41 | 4.5667 | 256 | 11 | 217
| 45 | 138.4167 | MC2 | 45 | 138.4167 | 252 | 11 | 217
| 48 | 13.8833 | MC2 | 48 | 13.8833 | 249 | 11 | 217
| 49 | 34.8667 | MC2 | 49 | 34.8667 | 248 | 11 | 217
| 51 | 10.4167 | MC2 | 51 | 10.4167 | 246 | 11 | 217
| 52 | 18.4333 | MC2 | 52 | 18.4333 | 245 | 11 | 217
| 54 | 115.2667 | MC2 | 54 | 115.2667 | 243 | 11 | 217
| 55 | 8.9333 | MC2 | 55 | 8.9333 | 242 | 11 | 217
| 56 | 9.9333 | MC2 | 56 | 9.9333 | 241 | 11 | 217
| 57 | 1.1333 | MC2 | 57 | 1.1333 | 240 | 11 | 217
| 58 | 59.1167 | MC2 | 58 | 59.1167 | 239 | 11 | 217
| 59 | 7.7 | MC2 | 59 | 7.7 | 238 | 11 | 217
| 60 | 5.55 | MC2 | 60 | 5.55 | 237 | 11 | 217
| 61 | 13.8 | MC2 | 61 | 13.8 | 236 | 11 | 217
| 63 | 109.1333 | MC2 | 63 | 109.1333 | 234 | 11 | 217
| 65 | 36.65 | MC2 | 65 | 36.65 | 232 | 11 | 217
| 66 | 17.8 | MC2 | 66 | 17.8 | 231 | 11 | 217
| 67 | 33.2167 | MC2 | 67 | 33.2167 | 230 | 11 | 217
| 68 | 14.2667 | MC2 | 68 | 14.2667 | 229 | 11 | 217
| 71 | 21.8667 | MC2 | 71 | 21.8667 | 226 | 11 | 217
| 72 | 273.5667 | MC2 | 72 | 273.5667 | 225 | 11 | 217
| 74 | 26.7667 | MC2 | 74 | 26.7667 | 223 | 11 | 217
| 76 | 67.0833 | MC2 | 76 | 67.0833 | 221 | 11 | 217
| 81 | 841.6167 | MC2 | 81 | 841.6167 | 216 | 11 | 207
| 84 | 18.2 | MC2 | 84 | 18.2 | 213 | 11 | 207
| 85 | 53.9 | MC2 | 85 | 53.9 | 212 | 11 | 207
| 86 | 0.65 | MC2 | 86 | 0.65 | 211 | 11 | 207
| 87 | 2 | MC2 | 87 | 2 | 210 | 11 | 207
| 90 | 130.6833 | MC2 | 90 | 130.6833 | 207 | 11 | 207
| 93 | 28.2167 | MC2 | 93 | 28.2167 | 204 | 11 | 147
| 94 | 16.65 | MC2 | 94 | 16.65 | 203 | 11 | 147
| 95 | 6.9 | MC2 | 95 | 6.9 | 202 | 11 | 147
| 97 | 20.0833 | MC2 | 97 | 20.0833 | 200 | 11 | 147
| 98 | 3.1167 | MC2 | 98 | 3.1167 | 199 | 11 | 147
| 99 | 17.15 | MC2 | 99 | 17.15 | 198 | 11 | 147
| 100 | 9 | MC2 | 100 | 9 | 197 | 11 | 147
| 103 | 2.5167 | MC2 | 103 | 2.5167 | 194 | 11 | 147
| 104 | 29.9833 | MC2 | 104 | 29.9833 | 193 | 11 | 147
| 105 | 8.0167 | MC2 | 105 | 8.0167 | 192 | 11 | 147
| 108 | 4.0167 | MC2 | 108 | 4.0167 | 189 | 11 | 147
| 111 | 1.15 | MC2 | 111 | 1.15 | 186 | 11 | 147
| 112 | 36.65 | MC2 | 112 | 36.65 | 185 | 11 | 147
| 113 | 4.5667 | MC2 | 113 | 4.5667 | 184 | 11 | 147
| 117 | 19.3 | MC2 | 117 | 19.3 | 180 | 11 | 147
| 126 | 75.0667 | MC2 | 126 | 75.0667 | 171 | 11 | 147
| 130 | 8.8333 | MC2 | 130 | 8.8333 | 167 | 11 | 147
| 131 | 39.5167 | MC2 | 131 | 39.5167 | 166 | 11 | 147
| 135 | 3.4 | MC2 | 135 | 3.4 | 162 | 11 | 147
| 139 | 62.75 | MC2 | 139 | 62.75 | 158 | 11 | 147
| 144 | 32.6333 | MC2 | 144 | 32.6333 | 153 | 11 | 147
| 147 | 5.55 | MC2 | 147 | 5.55 | 150 | 11 | 147
| 148 | 19.8 | MC2 | 148 | 19.8 | 149 | 11 | 147
| 152 | 35.1 | MC2 | 152 | 35.1 | 145 | 11 | 0
| 157 | 31.3333 | MC2 | 157 | 31.3333 | 140 | 11 | 0
| 161 | 44.3833 | MC2 | 161 | 44.3833 | 136 | 11 | 0
| 163 | 6.5 | MC2 | 163 | 6.5 | 134 | 11 | 0
| 166 | 5.15 | MC2 | 166 | 5.15 | 131 | 11 | 0
| 170 | 35 | MC2 | 170 | 35 | 127 | 11 | 0
| 184 | 6.9 | MC2 | 184 | 6.9 | 113 | 11 | 0
| 188 | 3.0167 | MC2 | 188 | 3.0167 | 109 | 11 | 0
| 194 | 7.9833 | MC2 | 194 | 7.9833 | 103 | 11 | 0
| 206 | 4.4667 | MC2 | 206 | 4.4667 | 91 | 11 | 0
| 224 | 1.3333 | MC2 | 224 | 1.3333 | 73 | 11 | 0
| 238 | 1.05 | MC2 | 238 | 1.05 | 59 | 11 | 0
MC3 | 5 | 3.5 | MC3 | 5 | 3.5 | 389 | 12 | 354
| 6 | 1.8667 | MC3 | 6 | 1.8667 | 388 | 12 | 354
| 7 | 19.7667 | MC3 | 7 | 19.7667 | 387 | 12 | 354
| 10 | 1.4667 | MC3 | 10 | 1.4667 | 384 | 12 | 354
| 12 | 42.6333 | MC3 | 12 | 42.6333 | 382 | 12 | 354
| 14 | 1.9167 | MC3 | 14 | 1.9167 | 380 | 12 | 354
| 15 | 6.4333 | MC3 | 15 | 6.4333 | 379 | 12 | 354
| 16 | 143.75 | MC3 | 16 | 143.75 | 378 | 12 | 354
| 17 | 174 | MC3 | 17 | 174 | 377 | 12 | 354
| 18 | 28.9167 | MC3 | 18 | 28.9167 | 376 | 12 | 354
| 19 | 7.6167 | MC3 | 19 | 7.6167 | 375 | 12 | 354
| 20 | 1.0333 | MC3 | 20 | 1.0333 | 374 | 12 | 354
| 21 | 178.45 | MC3 | 21 | 178.45 | 373 | 12 | 354
| 22 | 7.9167 | MC3 | 22 | 7.9167 | 372 | 12 | 354
| 25 | 4.3167 | MC3 | 25 | 4.3167 | 369 | 12 | 354
| 26 | 48.4167 | MC3 | 26 | 48.4167 | 368 | 12 | 354
| 28 | 12.5833 | MC3 | 28 | 12.5833 | 366 | 12 | 354
| 31 | 49.95 | MC3 | 31 | 49.95 | 363 | 12 | 354
| 33 | 8.7667 | MC3 | 33 | 8.7667 | 361 | 12 | 354
| 35 | 21.5667 | MC3 | 35 | 21.5667 | 359 | 12 | 354
| 38 | 14.7167 | MC3 | 38 | 14.7167 | 356 | 12 | 354
| 40 | 13.7667 | MC3 | 40 | 13.7667 | 354 | 12 | 354
| 42 | 10.15 | MC3 | 42 | 10.15 | 352 | 12 | 314
| 45 | 42.8 | MC3 | 45 | 42.8 | 349 | 12 | 314
| 46 | 0.36667 | MC3 | 46 | 0.36667 | 348 | 12 | 314
| 47 | 1.4833 | MC3 | 47 | 1.4833 | 347 | 12 | 314
| 49 | 35.7 | MC3 | 49 | 35.7 | 345 | 12 | 314
| 52 | 1.35 | MC3 | 52 | 1.35 | 342 | 12 | 314
| 53 | 9.65 | MC3 | 53 | 9.65 | 341 | 12 | 314
| 54 | 12.65 | MC3 | 54 | 12.65 | 340 | 12 | 314
| 57 | 7.6667 | MC3 | 57 | 7.6667 | 337 | 12 | 314
| 59 | 62.9667 | MC3 | 59 | 62.9667 | 335 | 12 | 314
| 63 | 26.7667 | MC3 | 63 | 26.7667 | 331 | 12 | 314
| 65 | 11.7 | MC3 | 65 | 11.7 | 329 | 12 | 314
| 68 | 416.1 | MC3 | 68 | 416.1 | 326 | 12 | 314
| 71 | 7.25 | MC3 | 71 | 7.25 | 323 | 12 | 314
| 72 | 27.7667 | MC3 | 72 | 27.7667 | 322 | 12 | 314
| 73 | 20.1667 | MC3 | 73 | 20.1667 | 321 | 12 | 314
| 74 | 14.7 | MC3 | 74 | 14.7 | 320 | 12 | 314
| 77 | 232.4833 | MC3 | 77 | 232.4833 | 317 | 12 | 314
| 80 | 4.25 | MC3 | 80 | 4.25 | 314 | 12 | 314
| 81 | 3.1 | MC3 | 81 | 3.1 | 313 | 12 | 234
| 82 | 128.1 | MC3 | 82 | 128.1 | 312 | 12 | 234
| 84 | 5.4 | MC3 | 84 | 5.4 | 310 | 12 | 234
| 85 | 0.86667 | MC3 | 85 | 0.86667 | 309 | 12 | 234
| 86 | 468.7667 | MC3 | 86 | 468.7667 | 308 | 12 | 234
| 87 | 6.5167 | MC3 | 87 | 6.5167 | 307 | 12 | 234
| 88 | 15.6 | MC3 | 88 | 15.6 | 306 | 12 | 234
| 90 | 7.7667 | MC3 | 90 | 7.7667 | 304 | 12 | 234
| 91 | 272.8 | MC3 | 91 | 272.8 | 303 | 12 | 234
| 92 | 7.3167 | MC3 | 92 | 7.3167 | 302 | 12 | 234
| 93 | 0.61667 | MC3 | 93 | 0.61667 | 301 | 12 | 234
| 96 | 336.3 | MC3 | 96 | 336.3 | 298 | 12 | 234
| 97 | 37.45 | MC3 | 97 | 37.45 | 297 | 12 | 234
| 100 | 31.9167 | MC3 | 100 | 31.9167 | 294 | 12 | 234
| 102 | 5.05 | MC3 | 102 | 5.05 | 292 | 12 | 234
| 103 | 8.9333 | MC3 | 103 | 8.9333 | 291 | 12 | 234
| 105 | 23.15 | MC3 | 105 | 23.15 | 289 | 12 | 234
| 110 | 6.3333 | MC3 | 110 | 6.3333 | 284 | 12 | 234
| 111 | 12.1 | MC3 | 111 | 12.1 | 283 | 12 | 234
| 114 | 80.3667 | MC3 | 114 | 80.3667 | 280 | 12 | 234
| 116 | 23.8833 | MC3 | 116 | 23.8833 | 278 | 12 | 234
| 118 | 4.3167 | MC3 | 118 | 4.3167 | 276 | 12 | 234
| 119 | 11.65 | MC3 | 119 | 11.65 | 275 | 12 | 234
| 122 | 1.3 | MC3 | 122 | 1.3 | 272 | 12 | 234
| 123 | 0.91667 | MC3 | 123 | 0.91667 | 271 | 12 | 234
| 124 | 13.4167 | MC3 | 124 | 13.4167 | 270 | 12 | 234
| 128 | 7.5667 | MC3 | 128 | 7.5667 | 266 | 12 | 234
| 133 | 81.6167 | MC3 | 133 | 81.6167 | 261 | 12 | 234
| 138 | 2.1167 | MC3 | 138 | 2.1167 | 256 | 12 | 234
| 142 | 8.5833 | MC3 | 142 | 8.5833 | 252 | 12 | 234
| 147 | 0.75 | MC3 | 147 | 0.75 | 247 | 12 | 234
| 151 | 10.2167 | MC3 | 151 | 10.2167 | 243 | 12 | 234
| 161 | 28.95 | MC3 | 161 | 28.95 | 233 | 12 | 204
| 167 | 4.5667 | MC3 | 167 | 4.5667 | 227 | 12 | 204
| 170 | 7.15 | MC3 | 170 | 7.15 | 224 | 12 | 204
| 175 | 0.13333 | MC3 | 175 | 0.13333 | 219 | 12 | 204
| 179 | 19.5333 | MC3 | 179 | 19.5333 | 215 | 12 | 204
| 181 | 4.9 | MC3 | 181 | 4.9 | 213 | 12 | 204
| 184 | 7.3 | MC3 | 184 | 7.3 | 210 | 12 | 204
| 189 | 1.5 | MC3 | 189 | 1.5 | 205 | 12 | 204
| 193 | 9.05 | MC3 | 193 | 9.05 | 201 | 12 | 170
| 198 | 56.0333 | MC3 | 198 | 56.0333 | 196 | 12 | 170
| 207 | 27.3 | MC3 | 207 | 27.3 | 187 | 12 | 170
| 216 | 3.5 | MC3 | 216 | 3.5 | 178 | 12 | 170
| 226 | 8.1833 | MC3 | 226 | 8.1833 | 168 | 12 | 0
| 228 | 45.9667 | MC3 | 228 | 45.9667 | 166 | 12 | 0
| 230 | 11.0167 | MC3 | 230 | 11.0167 | 164 | 12 | 0
| 235 | 2.4667 | MC3 | 235 | 2.4667 | 159 | 12 | 0
| 237 | 48.0833 | MC3 | 237 | 48.0833 | 157 | 12 | 0
| 244 | 43.3333 | MC3 | 244 | 43.3333 | 150 | 12 | 0
| 249 | 4.5167 | MC3 | 249 | 4.5167 | 145 | 12 | 0
| 263 | 3.5833 | MC3 | 263 | 3.5833 | 131 | 12 | 0
| 272 | 7.8667 | MC3 | 272 | 7.8667 | 122 | 12 | 0
| 277 | 16.8167 | MC3 | 277 | 16.8167 | 117 | 12 | 0
| 280 | 1.5167 | MC3 | 280 | 1.5167 | 114 | 12 | 0
| 285 | 12.5 | MC3 | 285 | 12.5 | 109 | 12 | 0
MC4 | 0 | 781.25 | MC4 | 0 | 781.25 | 486 | 13 | 446
| 1 | 170 | MC4 | 1 | 170 | 485 | 13 | 446
| 3 | 436.2333 | MC4 | 3 | 436.2333 | 483 | 13 | 446
| 4 | 27.6167 | MC4 | 4 | 27.6167 | 482 | 13 | 446
| 5 | 15.7 | MC4 | 5 | 15.7 | 481 | 13 | 446
| 6 | 222.8833 | MC4 | 6 | 222.8833 | 480 | 13 | 446
| 7 | 97.2 | MC4 | 7 | 97.2 | 479 | 13 | 446
| 8 | 239.2 | MC4 | 8 | 239.2 | 478 | 13 | 446
| 9 | 96.9 | MC4 | 9 | 96.9 | 477 | 13 | 446
| 10 | 376.8667 | MC4 | 10 | 376.8667 | 476 | 13 | 446
| 11 | 23.5 | MC4 | 11 | 23.5 | 475 | 13 | 446
| 12 | 66.1333 | MC4 | 12 | 66.1333 | 474 | 13 | 446
| 13 | 6.15 | MC4 | 13 | 6.15 | 473 | 13 | 446
| 14 | 25.9833 | MC4 | 14 | 25.9833 | 472 | 13 | 446
| 15 | 520.8 | MC4 | 15 | 520.8 | 471 | 13 | 446
| 16 | 76.2667 | MC4 | 16 | 76.2667 | 470 | 13 | 446
| 17 | 1.1667 | MC4 | 17 | 1.1667 | 469 | 13 | 446
| 18 | 152.0167 | MC4 | 18 | 152.0167 | 468 | 13 | 446
| 19 | 758.9833 | MC4 | 19 | 758.9833 | 467 | 13 | 446
| 20 | 10.2833 | MC4 | 20 | 10.2833 | 466 | 13 | 446
| 21 | 27.25 | MC4 | 21 | 27.25 | 465 | 13 | 446
| 23 | 1078.4167 | MC4 | 23 | 1078.4167 | 463 | 13 | 446
| 24 | 120.4667 | MC4 | 24 | 120.4667 | 462 | 13 | 446
| 26 | 0.75 | MC4 | 26 | 0.75 | 460 | 13 | 446
| 27 | 27.3667 | MC4 | 27 | 27.3667 | 459 | 13 | 446
| 29 | 25.65 | MC4 | 29 | 25.65 | 457 | 13 | 446
| 33 | 117.1167 | MC4 | 33 | 117.1167 | 453 | 13 | 446
| 34 | 0.6 | MC4 | 34 | 0.6 | 452 | 13 | 446
| 35 | 0.26667 | MC4 | 35 | 0.26667 | 451 | 13 | 446
| 36 | 5.3167 | MC4 | 36 | 5.3167 | 450 | 13 | 446
| 38 | 47.7333 | MC4 | 38 | 47.7333 | 448 | 13 | 446
| 43 | 25.95 | MC4 | 43 | 25.95 | 443 | 13 | 406
| 44 | 15.7167 | MC4 | 44 | 15.7167 | 442 | 13 | 406
| 45 | 14.4667 | MC4 | 45 | 14.4667 | 441 | 13 | 406
| 47 | 40.2 | MC4 | 47 | 40.2 | 439 | 13 | 406
| 52 | 49.0667 | MC4 | 52 | 49.0667 | 434 | 13 | 406
| 54 | 5.6 | MC4 | 54 | 5.6 | 432 | 13 | 406
| 56 | 25.25 | MC4 | 56 | 25.25 | 430 | 13 | 406
| 57 | 17.6167 | MC4 | 57 | 17.6167 | 429 | 13 | 406
| 61 | 63.7833 | MC4 | 61 | 63.7833 | 425 | 13 | 406
| 66 | 34.2 | MC4 | 66 | 34.2 | 420 | 13 | 406
| 68 | 14.6667 | MC4 | 68 | 14.6667 | 418 | 13 | 406
| 70 | 4.7167 | MC4 | 70 | 4.7167 | 416 | 13 | 406
| 74 | 2.2833 | MC4 | 74 | 2.2833 | 412 | 13 | 406
| 75 | 25.55 | MC4 | 75 | 25.55 | 411 | 13 | 406
| 78 | 9.6333 | MC4 | 78 | 9.6333 | 408 | 13 | 406
| 80 | 10.9333 | MC4 | 80 | 10.9333 | 406 | 13 | 406
| 84 | 159.8167 | MC4 | 84 | 159.8167 | 402 | 13 | 326
| 89 | 124.8 | MC4 | 89 | 124.8 | 397 | 13 | 326
| 93 | 132.1333 | MC4 | 93 | 132.1333 | 393 | 13 | 326
| 95 | 5.0667 | MC4 | 95 | 5.0667 | 391 | 13 | 326
| 98 | 1.8 | MC4 | 98 | 1.8 | 388 | 13 | 326
| 103 | 28.0833 | MC4 | 103 | 28.0833 | 383 | 13 | 326
| 105 | 7.3167 | MC4 | 105 | 7.3167 | 381 | 13 | 326
| 106 | 0.63333 | MC4 | 106 | 0.63333 | 380 | 13 | 326
| 107 | 10.35 | MC4 | 107 | 10.35 | 379 | 13 | 326
| 110 | 2.9833 | MC4 | 110 | 2.9833 | 376 | 13 | 326
| 112 | 47.1333 | MC4 | 112 | 47.1333 | 374 | 13 | 326
| 117 | 9.5667 | MC4 | 117 | 9.5667 | 369 | 13 | 326
| 119 | 8.4167 | MC4 | 119 | 8.4167 | 367 | 13 | 326
| 120 | 6.1 | MC4 | 120 | 6.1 | 366 | 13 | 326
| 121 | 46.1167 | MC4 | 121 | 46.1167 | 365 | 13 | 326
| 126 | 12.4833 | MC4 | 126 | 12.4833 | 360 | 13 | 326
| 129 | 6.5 | MC4 | 129 | 6.5 | 357 | 13 | 326
| 130 | 19.3667 | MC4 | 130 | 19.3667 | 356 | 13 | 326
| 131 | 10.3333 | MC4 | 131 | 10.3333 | 355 | 13 | 326
| 135 | 4.5 | MC4 | 135 | 4.5 | 351 | 13 | 326
| 140 | 54.3667 | MC4 | 140 | 54.3667 | 346 | 13 | 326
| 144 | 26.8667 | MC4 | 144 | 26.8667 | 342 | 13 | 326
| 149 | 27.6167 | MC4 | 149 | 27.6167 | 337 | 13 | 326
| 153 | 0.15 | MC4 | 153 | 0.15 | 333 | 13 | 326
| 154 | 4.8333 | MC4 | 154 | 4.8333 | 332 | 13 | 326
| 158 | 34.7 | MC4 | 158 | 34.7 | 328 | 13 | 326
| 163 | 4.65 | MC4 | 163 | 4.65 | 323 | 13 | 296
| 167 | 21.35 | MC4 | 167 | 21.35 | 319 | 13 | 296
| 172 | 9.7 | MC4 | 172 | 9.7 | 314 | 13 | 296
| 175 | 14.3333 | MC4 | 175 | 14.3333 | 311 | 13 | 296
| 177 | 50.6333 | MC4 | 177 | 50.6333 | 309 | 13 | 296
| 181 | 9.35 | MC4 | 181 | 9.35 | 305 | 13 | 296
| 186 | 9.6667 | MC4 | 186 | 9.6667 | 300 | 13 | 296
| 195 | 3.2 | MC4 | 195 | 3.2 | 291 | 13 | 175
| 198 | 0.23333 | MC4 | 198 | 0.23333 | 288 | 13 | 175
| 200 | 2.1 | MC4 | 200 | 2.1 | 286 | 13 | 175
| 204 | 63.8667 | MC4 | 204 | 63.8667 | 282 | 13 | 175
| 214 | 10.5833 | MC4 | 214 | 10.5833 | 272 | 13 | 175
| 218 | 12.8333 | MC4 | 218 | 12.8333 | 268 | 13 | 175
| 223 | 10.4667 | MC4 | 223 | 10.4667 | 263 | 13 | 175
| 228 | 21.05 | MC4 | 228 | 21.05 | 258 | 13 | 175
| 232 | 1.4667 | MC4 | 232 | 1.4667 | 254 | 13 | 175
| 246 | 0.13333 | MC4 | 246 | 0.13333 | 240 | 13 | 175
| 251 | 0.65 | MC4 | 251 | 0.65 | 235 | 13 | 175
| 260 | 3 | MC4 | 260 | 3 | 226 | 13 | 175
| 265 | 5.0667 | MC4 | 265 | 5.0667 | 221 | 13 | 175
| 278 | 2.9167 | MC4 | 278 | 2.9167 | 208 | 13 | 175
| 292 | 0.83333 | MC4 | 292 | 0.83333 | 194 | 13 | 175
| 297 | 13.7833 | MC4 | 297 | 13.7833 | 189 | 13 | 175
| 306 | 0.35 | MC4 | 306 | 0.35 | 180 | 13 | 175
| 315 | 8.1167 | MC4 | 315 | 8.1167 | 171 | 13 | 0
| 325 | 0.2 | MC4 | 325 | 0.2 | 161 | 13 | 0
| 338 | 2.45 | MC4 | 338 | 2.45 | 148 | 13 | 0
| 339 | 0.38333 | MC4 | 339 | 0.38333 | 147 | 13 | 0
| 343 | 2.1333 | MC4 | 343 | 2.1333 | 143 | 13 | 0
| 352 | 11.3167 | MC4 | 352 | 11.3167 | 134 | 13 | 0
| 362 | 0.86667 | MC4 | 362 | 0.86667 | 124 | 13 | 0
| 366 | 7.7833 | MC4 | 366 | 7.7833 | 120 | 13 | 0
| 389 | 11.6667 | MC4 | 389 | 11.6667 | 97 | 13 | 0
TC1 | 0 | 1196.7 | TC1 | 0 | 1196.7 | 493 | 14 | 453
| 3 | 0.1 | TC1 | 3 | 0.1 | 490 | 14 | 453
| 5 | 1204.5167 | TC1 | 5 | 1204.5167 | 488 | 14 | 453
| 9 | 121.6333 | TC1 | 9 | 121.6333 | 484 | 14 | 453
| 12 | 0.61667 | TC1 | 12 | 0.61667 | 481 | 14 | 453
| 14 | 137.8333 | TC1 | 14 | 137.8333 | 479 | 14 | 453
| 18 | 1.6667 | TC1 | 18 | 1.6667 | 475 | 14 | 453
| 19 | 174.5667 | TC1 | 19 | 174.5667 | 474 | 14 | 453
| 21 | 19.8167 | TC1 | 21 | 19.8167 | 472 | 14 | 453
| 23 | 29.9167 | TC1 | 23 | 29.9167 | 470 | 14 | 453
| 25 | 1 | TC1 | 25 | 1 | 468 | 14 | 453
| 28 | 100.5 | TC1 | 28 | 100.5 | 465 | 14 | 453
| 32 | 0.33333 | TC1 | 32 | 0.33333 | 461 | 14 | 453
| 33 | 2.4667 | TC1 | 33 | 2.4667 | 460 | 14 | 453
| 34 | 7.25 | TC1 | 34 | 7.25 | 459 | 14 | 453
| 37 | 59.7167 | TC1 | 37 | 59.7167 | 456 | 14 | 453
| 38 | 3.15 | TC1 | 38 | 3.15 | 455 | 14 | 453
| 39 | 0.46667 | TC1 | 39 | 0.46667 | 454 | 14 | 453
| 42 | 8.7667 | TC1 | 42 | 8.7667 | 451 | 14 | 413
| 47 | 11.6167 | TC1 | 47 | 11.6167 | 446 | 14 | 413
| 49 | 1 | TC1 | 49 | 1 | 444 | 14 | 413
| 50 | 5.85 | TC1 | 50 | 5.85 | 443 | 14 | 413
| 51 | 45.4167 | TC1 | 51 | 45.4167 | 442 | 14 | 413
| 56 | 5.9167 | TC1 | 56 | 5.9167 | 437 | 14 | 413
| 60 | 4.1167 | TC1 | 60 | 4.1167 | 433 | 14 | 413
| 63 | 2.0833 | TC1 | 63 | 2.0833 | 430 | 14 | 413
| 65 | 65.55 | TC1 | 65 | 65.55 | 428 | 14 | 413
| 69 | 0.6 | TC1 | 69 | 0.6 | 424 | 14 | 413
| 73 | 1.3333 | TC1 | 73 | 1.3333 | 420 | 14 | 413
| 74 | 130.7667 | TC1 | 74 | 130.7667 | 419 | 14 | 413
| 75 | 0.48333 | TC1 | 75 | 0.48333 | 418 | 14 | 413
| 76 | 6.6667 | TC1 | 76 | 6.6667 | 417 | 14 | 413
| 78 | 1.2333 | TC1 | 78 | 1.2333 | 415 | 14 | 413
| 79 | 1 | TC1 | 79 | 1 | 414 | 14 | 413
| 84 | 7.05 | TC1 | 84 | 7.05 | 409 | 14 | 333
| 86 | 7.35 | TC1 | 86 | 7.35 | 407 | 14 | 333
| 88 | 7.9 | TC1 | 88 | 7.9 | 405 | 14 | 333
| 91 | 15.5333 | TC1 | 91 | 15.5333 | 402 | 14 | 333
| 93 | 13.0333 | TC1 | 93 | 13.0333 | 400 | 14 | 333
| 102 | 21.7167 | TC1 | 102 | 21.7167 | 391 | 14 | 333
| 104 | 0.78333 | TC1 | 104 | 0.78333 | 389 | 14 | 333
| 107 | 10.2 | TC1 | 107 | 10.2 | 386 | 14 | 333
| 110 | 1.75 | TC1 | 110 | 1.75 | 383 | 14 | 333
| 112 | 0.66667 | TC1 | 112 | 0.66667 | 381 | 14 | 333
| 116 | 2 | TC1 | 116 | 2 | 377 | 14 | 333
| 119 | 0.48333 | TC1 | 119 | 0.48333 | 374 | 14 | 333
| 121 | 36.6667 | TC1 | 121 | 36.6667 | 372 | 14 | 333
| 124 | 0.4 | TC1 | 124 | 0.4 | 369 | 14 | 333
| 126 | 2.1667 | TC1 | 126 | 2.1667 | 367 | 14 | 333
| 128 | 9.2667 | TC1 | 128 | 9.2667 | 365 | 14 | 333
| 130 | 16.5167 | TC1 | 130 | 16.5167 | 363 | 14 | 333
| 134 | 0.36667 | TC1 | 134 | 0.36667 | 359 | 14 | 333
| 135 | 6.2667 | TC1 | 135 | 6.2667 | 358 | 14 | 333
| 140 | 49.3667 | TC1 | 140 | 49.3667 | 353 | 14 | 333
| 142 | 1 | TC1 | 142 | 1 | 351 | 14 | 333
| 144 | 75.1167 | TC1 | 144 | 75.1167 | 349 | 14 | 333
| 145 | 1.45 | TC1 | 145 | 1.45 | 348 | 14 | 333
| 149 | 4.5333 | TC1 | 149 | 4.5333 | 344 | 14 | 333
| 153 | 1.25 | TC1 | 153 | 1.25 | 340 | 14 | 333
| 156 | 2 | TC1 | 156 | 2 | 337 | 14 | 333
| 158 | 17.5167 | TC1 | 158 | 17.5167 | 335 | 14 | 333
| 163 | 0.41667 | TC1 | 163 | 0.41667 | 330 | 14 | 303
| 166 | 1 | TC1 | 166 | 1 | 327 | 14 | 303
| 167 | 6.75 | TC1 | 167 | 6.75 | 326 | 14 | 303
| 170 | 1 | TC1 | 170 | 1 | 323 | 14 | 303
| 172 | 0.63333 | TC1 | 172 | 0.63333 | 321 | 14 | 303
| 177 | 2.25 | TC1 | 177 | 2.25 | 316 | 14 | 303
| 191 | 1.3 | TC1 | 191 | 1.3 | 302 | 14 | 188
| 198 | 1 | TC1 | 198 | 1 | 295 | 14 | 188
| 203 | 1 | TC1 | 203 | 1 | 290 | 14 | 188
| 209 | 5.1 | TC1 | 209 | 5.1 | 284 | 14 | 188
| 214 | 51.8 | TC1 | 214 | 51.8 | 279 | 14 | 188
| 235 | 1 | TC1 | 235 | 1 | 258 | 14 | 188
| 237 | 9.75 | TC1 | 237 | 9.75 | 256 | 14 | 188
| 256 | 0.33333 | TC1 | 256 | 0.33333 | 237 | 14 | 188
| 260 | 3.7167 | TC1 | 260 | 3.7167 | 233 | 14 | 188
| 262 | 1 | TC1 | 262 | 1 | 231 | 14 | 188
| 273 | 1 | TC1 | 273 | 1 | 220 | 14 | 188
| 279 | 8.3167 | TC1 | 279 | 8.3167 | 214 | 14 | 188
| 293 | 1 | TC1 | 293 | 1 | 200 | 14 | 188
| 300 | 1 | TC1 | 300 | 1 | 193 | 14 | 188
| 302 | 1 | TC1 | 302 | 1 | 191 | 14 | 188
| 307 | 1.05 | TC1 | 307 | 1.05 | 186 | 14 | 0
TC2 | 0 | 806.35 | TC2 | 0 | 806.35 | 760 | 15 | 720
| 1 | 688.0167 | TC2 | 1 | 688.0167 | 759 | 15 | 720
| 3 | 19.5 | TC2 | 3 | 19.5 | 757 | 15 | 720
| 5 | 11.3167 | TC2 | 5 | 11.3167 | 755 | 15 | 720
| 6 | 1301.6333 | TC2 | 6 | 1301.6333 | 754 | 15 | 720
| 8 | 2.5 | TC2 | 8 | 2.5 | 752 | 15 | 720
| 9 | 1.9167 | TC2 | 9 | 1.9167 | 751 | 15 | 720
| 10 | 8.55 | TC2 | 10 | 8.55 | 750 | 15 | 720
| 13 | 151.15 | TC2 | 13 | 151.15 | 747 | 15 | 720
| 14 | 25.4333 | TC2 | 14 | 25.4333 | 746 | 15 | 720
| 15 | 14.1667 | TC2 | 15 | 14.1667 | 745 | 15 | 720
| 16 | 461.6833 | TC2 | 16 | 461.6833 | 744 | 15 | 720
| 17 | 576.5667 | TC2 | 17 | 576.5667 | 743 | 15 | 720
| 19 | 18.5333 | TC2 | 19 | 18.5333 | 741 | 15 | 720
| 20 | 19.7 | TC2 | 20 | 19.7 | 740 | 15 | 720
| 23 | 21.0167 | TC2 | 23 | 21.0167 | 737 | 15 | 720
| 24 | 3.25 | TC2 | 24 | 3.25 | 736 | 15 | 720
| 28 | 22.35 | TC2 | 28 | 22.35 | 732 | 15 | 720
| 29 | 80.3 | TC2 | 29 | 80.3 | 731 | 15 | 720
| 31 | 2 | TC2 | 31 | 2 | 729 | 15 | 720
| 32 | 2.1667 | TC2 | 32 | 2.1667 | 728 | 15 | 720
| 33 | 104.65 | TC2 | 33 | 104.65 | 727 | 15 | 720
| 34 | 199.6833 | TC2 | 34 | 199.6833 | 726 | 15 | 720
| 35 | 8 | TC2 | 35 | 8 | 725 | 15 | 720
| 37 | 1 | TC2 | 37 | 1 | 723 | 15 | 720
| 38 | 203.75 | TC2 | 38 | 203.75 | 722 | 15 | 720
| 39 | 104.5167 | TC2 | 39 | 104.5167 | 721 | 15 | 720
| 40 | 94.5 | TC2 | 40 | 94.5 | 720 | 15 | 720
| 42 | 1333.6 | TC2 | 42 | 1333.6 | 718 | 15 | 680
| 43 | 30.1833 | TC2 | 43 | 30.1833 | 717 | 15 | 680
| 44 | 41.8333 | TC2 | 44 | 41.8333 | 716 | 15 | 680
| 49 | 1.6667 | TC2 | 49 | 1.6667 | 711 | 15 | 680
| 52 | 7.75 | TC2 | 52 | 7.75 | 708 | 15 | 680
| 53 | 6.5 | TC2 | 53 | 6.5 | 707 | 15 | 680
| 54 | 2 | TC2 | 54 | 2 | 706 | 15 | 680
| 57 | 1.4167 | TC2 | 57 | 1.4167 | 703 | 15 | 680
| 59 | 0.4 | TC2 | 59 | 0.4 | 701 | 15 | 680
| 60 | 0.41667 | TC2 | 60 | 0.41667 | 700 | 15 | 680
| 61 | 3.3333 | TC2 | 61 | 3.3333 | 699 | 15 | 680
| 62 | 8.1667 | TC2 | 62 | 8.1667 | 698 | 15 | 680
| 66 | 2.9167 | TC2 | 66 | 2.9167 | 694 | 15 | 680
| 67 | 2.2333 | TC2 | 67 | 2.2333 | 693 | 15 | 680
| 70 | 59.0333 | TC2 | 70 | 59.0333 | 690 | 15 | 680
| 71 | 18.8833 | TC2 | 71 | 18.8833 | 689 | 15 | 680
| 73 | 2.8333 | TC2 | 73 | 2.8333 | 687 | 15 | 680
| 75 | 131.8333 | TC2 | 75 | 131.8333 | 685 | 15 | 680
| 80 | 4.9167 | TC2 | 80 | 4.9167 | 680 | 15 | 680
| 81 | 422.55 | TC2 | 81 | 422.55 | 679 | 15 | 600
| 82 | 2 | TC2 | 82 | 2 | 678 | 15 | 600
| 85 | 9.75 | TC2 | 85 | 9.75 | 675 | 15 | 600
| 86 | 4.5333 | TC2 | 86 | 4.5333 | 674 | 15 | 600
| 89 | 39.1667 | TC2 | 89 | 39.1667 | 671 | 15 | 600
| 90 | 8.7667 | TC2 | 90 | 8.7667 | 670 | 15 | 600
| 91 | 6.7333 | TC2 | 91 | 6.7333 | 669 | 15 | 600
| 94 | 7.4333 | TC2 | 94 | 7.4333 | 666 | 15 | 600
| 95 | 2.5 | TC2 | 95 | 2.5 | 665 | 15 | 600
| 99 | 8.3333 | TC2 | 99 | 8.3333 | 661 | 15 | 600
| 100 | 2 | TC2 | 100 | 2 | 660 | 15 | 600
| 102 | 1 | TC2 | 102 | 1 | 658 | 15 | 600
| 103 | 17.55 | TC2 | 103 | 17.55 | 657 | 15 | 600
| 107 | 68.8333 | TC2 | 107 | 68.8333 | 653 | 15 | 600
| 108 | 20.55 | TC2 | 108 | 20.55 | 652 | 15 | 600
| 109 | 2.5 | TC2 | 109 | 2.5 | 651 | 15 | 600
| 112 | 1.3167 | TC2 | 112 | 1.3167 | 648 | 15 | 600
| 114 | 1.6167 | TC2 | 114 | 1.6167 | 646 | 15 | 600
| 117 | 9.3833 | TC2 | 117 | 9.3833 | 643 | 15 | 600
| 118 | 20.5333 | TC2 | 118 | 20.5333 | 642 | 15 | 600
| 119 | 54.75 | TC2 | 119 | 54.75 | 641 | 15 | 600
| 122 | 0.81667 | TC2 | 122 | 0.81667 | 638 | 15 | 600
| 127 | 17.1333 | TC2 | 127 | 17.1333 | 633 | 15 | 600
| 128 | 31.6 | TC2 | 128 | 31.6 | 632 | 15 | 600
| 129 | 11.25 | TC2 | 129 | 11.25 | 631 | 15 | 600
| 130 | 4.75 | TC2 | 130 | 4.75 | 630 | 15 | 600
| 131 | 2 | TC2 | 131 | 2 | 629 | 15 | 600
| 132 | 3 | TC2 | 132 | 3 | 628 | 15 | 600
| 136 | 54.3667 | TC2 | 136 | 54.3667 | 624 | 15 | 600
| 137 | 26.05 | TC2 | 137 | 26.05 | 623 | 15 | 600
| 138 | 4 | TC2 | 138 | 4 | 622 | 15 | 600
| 139 | 9.5 | TC2 | 139 | 9.5 | 621 | 15 | 600
| 155 | 4.95 | TC2 | 155 | 4.95 | 605 | 15 | 600
| 159 | 2.25 | TC2 | 159 | 2.25 | 601 | 15 | 600
| 160 | 13.5833 | TC2 | 160 | 13.5833 | 600 | 15 | 600
| 162 | 0.5 | TC2 | 162 | 0.5 | 598 | 15 | 570
| 164 | 28.0333 | TC2 | 164 | 28.0333 | 596 | 15 | 570
| 165 | 5.4167 | TC2 | 165 | 5.4167 | 595 | 15 | 570
| 169 | 0.68333 | TC2 | 169 | 0.68333 | 591 | 15 | 570
| 174 | 13.7667 | TC2 | 174 | 13.7667 | 586 | 15 | 570
| 179 | 12 | TC2 | 179 | 12 | 581 | 15 | 570
| 183 | 1.2333 | TC2 | 183 | 1.2333 | 577 | 15 | 570
| 188 | 8.75 | TC2 | 188 | 8.75 | 572 | 15 | 570
| 190 | 7 | TC2 | 190 | 7 | 570 | 15 | 570
| 197 | 6.2 | TC2 | 197 | 6.2 | 563 | 15 | 440
| 202 | 9.1333 | TC2 | 202 | 9.1333 | 558 | 15 | 440
| 207 | 6 | TC2 | 207 | 6 | 553 | 15 | 440
| 212 | 1 | TC2 | 212 | 1 | 548 | 15 | 440
| 220 | 0.11667 | TC2 | 220 | 0.11667 | 540 | 15 | 440
| 221 | 1.7667 | TC2 | 221 | 1.7667 | 539 | 15 | 440
| 230 | 11 | TC2 | 230 | 11 | 530 | 15 | 440
| 231 | 16.5 | TC2 | 231 | 16.5 | 529 | 15 | 440
| 235 | 5 | TC2 | 235 | 5 | 525 | 15 | 440
| 238 | 4.3167 | TC2 | 238 | 4.3167 | 522 | 15 | 440
| 257 | 8.55 | TC2 | 257 | 8.55 | 503 | 15 | 440
| 269 | 4.5 | TC2 | 269 | 4.5 | 491 | 15 | 440
| 272 | 0.55 | TC2 | 272 | 0.55 | 488 | 15 | 440
| 277 | 100.4667 | TC2 | 277 | 100.4667 | 483 | 15 | 440
| 278 | 6 | TC2 | 278 | 6 | 482 | 15 | 440
| 279 | 7.25 | TC2 | 279 | 7.25 | 481 | 15 | 440
| 284 | 7.0333 | TC2 | 284 | 7.0333 | 476 | 15 | 440
| 288 | 4.8333 | TC2 | 288 | 4.8333 | 472 | 15 | 440
| 291 | 5.5 | TC2 | 291 | 5.5 | 469 | 15 | 440
| 296 | 20.55 | TC2 | 296 | 20.55 | 464 | 15 | 440
| 298 | 0.36667 | TC2 | 298 | 0.36667 | 462 | 15 | 440
| 301 | 16.25 | TC2 | 301 | 16.25 | 459 | 15 | 440
| 305 | 3 | TC2 | 305 | 3 | 455 | 15 | 440
| 306 | 29 | TC2 | 306 | 29 | 454 | 15 | 440
| 324 | 19 | TC2 | 324 | 19 | 436 | 15 | 0
| 325 | 262.6167 | TC2 | 325 | 262.6167 | 435 | 15 | 0
| 326 | 231.9667 | TC2 | 326 | 231.9667 | 434 | 15 | 0
| 329 | 6.0833 | TC2 | 329 | 6.0833 | 431 | 15 | 0
| 334 | 38.5 | TC2 | 334 | 38.5 | 426 | 15 | 0
| 335 | 10 | TC2 | 335 | 10 | 425 | 15 | 0
| 338 | 59.9 | TC2 | 338 | 59.9 | 422 | 15 | 0
| 339 | 7.0167 | TC2 | 339 | 7.0167 | 421 | 15 | 0
| 343 | 92.9 | TC2 | 343 | 92.9 | 417 | 15 | 0
| 348 | 2.25 | TC2 | 348 | 2.25 | 412 | 15 | 0
| 363 | 21.6667 | TC2 | 363 | 21.6667 | 397 | 15 | 0
| 371 | 306.2833 | TC2 | 371 | 306.2833 | 389 | 15 | 0
| 372 | 11 | TC2 | 372 | 11 | 388 | 15 | 0
| 381 | 17.4167 | TC2 | 381 | 17.4167 | 379 | 15 | 0
| 382 | 6.05 | TC2 | 382 | 6.05 | 378 | 15 | 0
| 395 | 2.5 | TC2 | 395 | 2.5 | 365 | 15 | 0
| 409 | 5.3333 | TC2 | 409 | 5.3333 | 351 | 15 | 0
| 418 | 1 | TC2 | 418 | 1 | 342 | 15 | 0
| 428 | 6.5 | TC2 | 428 | 6.5 | 332 | 15 | 0
| 473 | 0.6 | TC2 | 473 | 0.6 | 287 | 15 | 0
| 475 | 1.9333 | TC2 | 475 | 1.9333 | 285 | 15 | 0
| 489 | 1.2333 | TC2 | 489 | 1.2333 | 271 | 15 | 0
| 493 | 4.8333 | TC2 | 493 | 4.8333 | 267 | 15 | 0
| 498 | 7 | TC2 | 498 | 7 | 262 | 15 | 0
Grand Total |  | 69122.45

## Calc-Pivot Table-Derates
EventType | (Multiple Items)
Row Labels | Count of Derate
BR1 | 70
BR2 | 105
BR3 | 199
GH1 | 184
GH2 | 240
GH3 | 170
GH4 | 154
MC1 | 538
MC2 | 518
MC3 | 586
MC4 | 481
TC1 | 432
TC2 | 407
Grand Total | 4084

## Calc-Pivot abvals
|  | Total Hours |  | 46703.9833
Sum of Hours | [5 empty] | 1 | a2 | a3 | a4 | a5
UnitName | Bin | Total | Derate Occurance % | Xs |  | 1 | 2 | 3 | 4 | 5
BR1 | 0 | 1.0333 | 2.2125e-05 | 1 | BR1 | 1 | 302.4355 | 83.2419 | 277.4839 | 123.7903
| 37 | 312.5167 | 0.0066914 | 302.4355 | BR2 | 1 | 0.039003 | 0.041731 | 0.025253 | 2.8188
| 74 | 86.0167 | 0.0018417 | 83.2419 | BR3 | 1 | 0.24961 | 0.10727 | 0.20647 | 0.095006
| 77 | 286.7333 | 0.0061394 | 277.4839 | GH1 | 1 | 0.29351 | 0.51103 | 0.054276 | 0.04156
| 87 | 127.9167 | 0.0027389 | 123.7903 | GH2 | 1 | 0.76136 | 9.1163 | 5.1711 | 0.3467
| 97 | 311.5167 | 0.00667 | 1 | GH3 | 1 | 0.84744 | 5.1962 | 40.0295 | 25.7869
BR2 | 0 | 12.15 | 0.00026015 | 0.039003 | GH4 | 1 | 0.50788 | 0.12539 | 1.0637 | 0.83119
| 64 | 13 | 0.00027835 | 0.041731 | MC1 | 1 | 0.045776 | 0.0052271 | 0.002396 | 0.019434
| 78 | 7.8667 | 0.00016844 | 0.025253 | MC2 | 1 | 58.8083 | 1.0822 | 2.1743 | 5.0704
| 88 | 878.1167 | 0.018802 | 2.8188 | MC3 | 1 | 0.16961 | 0.30808 | 0.12733 | 0.31786
| 128 | 286.65 | 0.0061376 | 1 | MC4 | 1 | 0.99553 | 0.27823 | 6.5011 | 0.1966
| 148 | 71.55 | 0.001532 | 0.24961 | TC1 | 1 | 0.77212 | 16.9454 | 9.8658 | 8.2741
BR3 | 0 | 30.75 | 0.0006584 | 0.10727 | TC2 | 1 | 3.3959 | 2.6646 | 17.6334 | 8.0067
| 140 | 59.1833 | 0.0012672 | 0.20647 |  | b1 | b2 | b3 | b4 | b5 | Max
| 223 | 27.2333 | 0.00058311 | 0.095006 | UnitName | 1 | 2 | 3 | 4 | 5 | 6
| 253 | 2896.6 | 0.06202 | 1 | BR1 | 37 | 74 | 77 | 87 | 97 | 107
| 333 | 850.1667 | 0.018203 | 0.29351 | BR2 | 64 | 78 | 88 | 128 | 148 | 168
| 373 | 1480.25 | 0.031694 | 0.51103 | BR3 | 140 | 223 | 253 | 333 | 373 | 413
GH1 | 0 | 157.2167 | 0.0033662 | 0.054276 | GH1 | 218 | 289 | 319 | 399 | 439 | 479
| 218 | 120.3833 | 0.0025776 | 0.04156 | GH2 | 225 | 296 | 326 | 406 | 446 | 486
| 289 | 258.4833 | 0.0055345 | 1 | GH3 | 210 | 291 | 321 | 401 | 441 | 481
| 319 | 196.8 | 0.0042138 | 0.76136 | GH4 | 215 | 288 | 318 | 398 | 438 | 478
| 399 | 2356.4167 | 0.050454 | 9.1163 | MC1 | 150 | 210 | 220 | 260 | 280 | 300
| 439 | 1336.6333 | 0.028619 | 5.1711 | MC2 | 147 | 207 | 217 | 257 | 277 | 297
GH2 | 0 | 89.6167 | 0.0019188 | 0.3467 | MC3 | 170 | 204 | 234 | 314 | 354 | 394
| 225 | 52 | 0.0011134 | 1 | MC4 | 175 | 296 | 326 | 406 | 446 | 486
| 296 | 44.0667 | 0.00094353 | 0.84744 | TC1 | 188 | 303 | 333 | 413 | 453 | 493
| 326 | 270.2 | 0.0057854 | 5.1962 | TC2 | 440 | 570 | 600 | 680 | 720 | 760
| 406 | 2081.5333 | 0.044569 | 40.0295
| 446 | 1340.9167 | 0.028711 | 25.7869
GH3 | 0 | 229.55 | 0.004915 | 1
| 210 | 116.5833 | 0.0024962 | 0.50788
| 291 | 28.7833 | 0.00061629 | 0.12539
| 321 | 244.1667 | 0.005228 | 1.0637
| 401 | 190.8 | 0.0040853 | 0.83119
| 441 | 7088.0833 | 0.15177 | 1
GH4 | 0 | 324.4667 | 0.0069473 | 0.045776
| 215 | 37.05 | 0.00079329 | 0.0052271
| 288 | 16.9833 | 0.00036364 | 0.002396
| 318 | 137.75 | 0.0029494 | 0.019434
| 398 | 135.1 | 0.0028927 | 1
| 438 | 7945 | 0.17011 | 58.8083
MC1 | 0 | 146.2 | 0.0031304 | 1.0822
| 150 | 293.75 | 0.0062896 | 2.1743
| 210 | 685.0167 | 0.014667 | 5.0704
| 220 | 1431.05 | 0.030641 | 1
| 260 | 242.7167 | 0.0051969 | 0.16961
| 280 | 440.8833 | 0.00944 | 0.30808
MC2 | 0 | 182.2167 | 0.0039015 | 0.12733
| 147 | 454.8667 | 0.0097394 | 0.31786
| 207 | 1047.05 | 0.022419 | 1
| 217 | 1042.3667 | 0.022319 | 0.99553
| 257 | 291.3167 | 0.0062375 | 0.27823
| 277 | 6807.0167 | 0.14575 | 6.5011
MC3 | 0 | 205.85 | 0.0044075 | 0.1966
| 170 | 95.8833 | 0.002053 | 1
| 204 | 74.0333 | 0.0015852 | 0.77212
| 234 | 1624.7833 | 0.034789 | 16.9454
| 314 | 945.9667 | 0.020255 | 9.8658
| 354 | 793.35 | 0.016987 | 8.2741
MC4 | 0 | 44.9167 | 0.00096173 | 1
| 175 | 152.5333 | 0.003266 | 3.3959
| 296 | 119.6833 | 0.0025626 | 2.6646
| 326 | 792.0333 | 0.016959 | 17.6334
| 406 | 359.6333 | 0.0077003 | 8.0067
| 446 | 5556.0667 | 0.11896 | 1
TC1 | 0 | 1.05 | 2.2482e-05 | 0.00018898
| 188 | 88.3167 | 0.001891 | 0.015896
| 303 | 12.05 | 0.00025801 | 0.0021688
| 333 | 312.35 | 0.0066879 | 0.056218
| 413 | 292.4 | 0.0062607 | 1
| 453 | 3062.25 | 0.065567 | 10.4728
TC2 | 0 | 1123.5833 | 0.024058 | 3.8426
| 440 | 274.8833 | 0.0058857 | 0.94009
| 570 | 77.3833 | 0.0016569 | 0.26465
| 600 | 897.05 | 0.019207 | 3.0679
| 680 | 1659.9167 | 0.035541 | 5.6769
| 720 | 4954.2 | 0.10608 | 16.9432
Grand Total |  | 69122.45 | 1.48

## Calc- Prosym Setup
Calculated Availablity for Unit Blocks in PROSYM
Utilizing KU/LGE Historical GADS Data
| 2018 | [6 empty] | 2019 | [6 empty] | 2020 | [6 empty] | 2021 | [6 empty] | 2022
Brown.1 | BR1 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8% | BR1 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8% | BR1 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8% | BR1 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8% | BR1 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | 37 | 74 | 77 | 87 | 97 | 107 | 107 | 37 | 74 | 77 | 87 | 97 | 107 | 107 | 37 | 74 | 77 | 87 | 97 | 107 | 107 | 37 | 74 | 77 | 87 | 97 | 107 | 107 | 37 | 74 | 77 | 87 | 97 | 107 | 107
GADS Yr Availability: GADS only (C) | 0.01107% | 3.349% | 0.9219% | 3.073% | 1.371% | 84.77% | 93.5% | 0.01107% | 3.349% | 0.9219% | 3.073% | 1.371% | 84.77% | 93.5% | 0.01107% | 3.349% | 0.9219% | 3.073% | 1.371% | 84.77% | 93.5% | 0.01107% | 3.349% | 0.9219% | 3.073% | 1.371% | 84.77% | 93.5% | 0.01107% | 3.349% | 0.9219% | 3.073% | 1.371% | 84.77% | 93.5%
Brown.2 | BR2 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8% | BR2 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8% | BR2 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8% | BR2 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8% | BR2 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | 64 | 78 | 88 | 128 | 148 | 168 | 168 | 64 | 78 | 88 | 128 | 148 | 168 | 168 | 64 | 78 | 88 | 128 | 148 | 168 | 168 | 64 | 78 | 88 | 128 | 148 | 168 | 168 | 64 | 78 | 88 | 128 | 148 | 168 | 168
GADS Yr Availability: GADS only (C) | 1.998% | 0.07794% | 0.0834% | 0.05047% | 5.633% | 85.66% | 93.5% | 1.998% | 0.07794% | 0.0834% | 0.05047% | 5.633% | 85.66% | 93.5% | 1.998% | 0.07794% | 0.0834% | 0.05047% | 5.633% | 85.66% | 93.5% | 1.998% | 0.07794% | 0.0834% | 0.05047% | 5.633% | 85.66% | 93.5% | 1.998% | 0.07794% | 0.0834% | 0.05047% | 5.633% | 85.66% | 93.5%
Brown.3 | BR3 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8% | BR3 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8% | BR3 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8% | BR3 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8% | BR3 | FOR: | 3.699% | EFDR: | 2.078% | MOR: | 2.8%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | 140 | 223 | 253 | 333 | 373 | 413 | 413 | 140 | 223 | 253 | 333 | 373 | 413 | 413 | 140 | 223 | 253 | 333 | 373 | 413 | 413 | 140 | 223 | 253 | 333 | 373 | 413 | 413 | 140 | 223 | 253 | 333 | 373 | 413 | 413
GADS Yr Availability: GADS only (C) | 2.309% | 0.5764% | 0.2477% | 0.4768% | 0.2194% | 89.67% | 93.5% | 2.309% | 0.5764% | 0.2477% | 0.4768% | 0.2194% | 89.67% | 93.5% | 2.309% | 0.5764% | 0.2477% | 0.4768% | 0.2194% | 89.67% | 93.5% | 2.309% | 0.5764% | 0.2477% | 0.4768% | 0.2194% | 89.67% | 93.5% | 2.309% | 0.5764% | 0.2477% | 0.4768% | 0.2194% | 89.67% | 93.5%
Ghent.1 | GH1 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH1 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH1 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH1 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH1 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | 218 | 289 | 319 | 399 | 439 | 479 | 479 | 218 | 289 | 319 | 399 | 439 | 479 | 479 | 218 | 289 | 319 | 399 | 439 | 479 | 479 | 218 | 289 | 319 | 399 | 439 | 479 | 479 | 218 | 289 | 319 | 399 | 439 | 479 | 479
GADS Yr Availability: GADS only (C) | 2.084% | 0.6118% | 1.065% | 0.1131% | 0.08663% | 90.4% | 94.36% | 2.084% | 0.6118% | 1.065% | 0.1131% | 0.08663% | 90.4% | 94.36% | 2.084% | 0.6118% | 1.065% | 0.1131% | 0.08663% | 90.4% | 94.36% | 2.084% | 0.6118% | 1.065% | 0.1131% | 0.08663% | 90.4% | 94.36% | 2.084% | 0.6118% | 1.065% | 0.1131% | 0.08663% | 90.4% | 94.36%
Ghent.2 | GH2 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH2 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH2 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH2 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH2 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | 225 | 296 | 326 | 406 | 446 | 486 | 486 | 225 | 296 | 326 | 406 | 446 | 486 | 486 | 225 | 296 | 326 | 406 | 446 | 486 | 486 | 225 | 296 | 326 | 406 | 446 | 486 | 486 | 225 | 296 | 326 | 406 | 446 | 486 | 486
GADS Yr Availability: GADS only (C) | 0.3733% | 0.2842% | 3.403% | 1.93% | 0.1294% | 88.24% | 94.36% | 0.3733% | 0.2842% | 3.403% | 1.93% | 0.1294% | 88.24% | 94.36% | 0.3733% | 0.2842% | 3.403% | 1.93% | 0.1294% | 88.24% | 94.36% | 0.3733% | 0.2842% | 3.403% | 1.93% | 0.1294% | 88.24% | 94.36% | 0.3733% | 0.2842% | 3.403% | 1.93% | 0.1294% | 88.24% | 94.36%
Ghent.3 | GH3 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH3 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH3 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH3 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH3 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | 210 | 291 | 321 | 401 | 441 | 481 | 481 | 210 | 291 | 321 | 401 | 441 | 481 | 481 | 210 | 291 | 321 | 401 | 441 | 481 | 481 | 210 | 291 | 321 | 401 | 441 | 481 | 481 | 210 | 291 | 321 | 401 | 441 | 481 | 481
GADS Yr Availability: GADS only (C) | 0.154% | 0.1305% | 0.8004% | 6.166% | 3.972% | 83.14% | 94.36% | 0.154% | 0.1305% | 0.8004% | 6.166% | 3.972% | 83.14% | 94.36% | 0.154% | 0.1305% | 0.8004% | 6.166% | 3.972% | 83.14% | 94.36% | 0.154% | 0.1305% | 0.8004% | 6.166% | 3.972% | 83.14% | 94.36% | 0.154% | 0.1305% | 0.8004% | 6.166% | 3.972% | 83.14% | 94.36%
Ghent.4 | GH4 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH4 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH4 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH4 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2% | GH4 | FOR: | 3.44% | EFDR: | 1.823% | MOR: | 2.2%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | 215 | 288 | 318 | 398 | 438 | 478 | 478 | 215 | 288 | 318 | 398 | 438 | 478 | 478 | 215 | 288 | 318 | 398 | 438 | 478 | 478 | 215 | 288 | 318 | 398 | 438 | 478 | 478 | 215 | 288 | 318 | 398 | 438 | 478 | 478
GADS Yr Availability: GADS only (C) | 1.69% | 0.8583% | 0.2119% | 1.798% | 1.405% | 88.4% | 94.36% | 1.69% | 0.8583% | 0.2119% | 1.798% | 1.405% | 88.4% | 94.36% | 1.69% | 0.8583% | 0.2119% | 1.798% | 1.405% | 88.4% | 94.36% | 1.69% | 0.8583% | 0.2119% | 1.798% | 1.405% | 88.4% | 94.36% | 1.69% | 0.8583% | 0.2119% | 1.798% | 1.405% | 88.4% | 94.36%
Green.River.3 | GR3 | FOR: | 6.818% | EFDR: | 1.054% | MOR: | 3.2% | GR3 | FOR: | 7.08% | EFDR: | 1.098% | MOR: | 3.2% | GR3 | FOR: | 7.342% | EFDR: | 1.142% | MOR: | 3.2% | GR3 | FOR: | 7.604% | EFDR: | 1.186% | MOR: | 3.2% | GR3 | FOR: | 7.866% | EFDR: | 1.23% | MOR: | 3.2%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 71 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 71 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 71 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 71 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 71
GADS Yr Availability: GADS only (C) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Green.River.4 | GR4 | FOR: | 6.818% | EFDR: | 1.054% | MOR: | 3.2% | GR4 | FOR: | 7.08% | EFDR: | 1.098% | MOR: | 3.2% | GR4 | FOR: | 7.342% | EFDR: | 1.142% | MOR: | 3.2% | GR4 | FOR: | 7.604% | EFDR: | 1.186% | MOR: | 3.2% | GR4 | FOR: | 7.866% | EFDR: | 1.23% | MOR: | 3.2%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 98 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 98 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 98 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 98 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 98
GADS Yr Availability: GADS only (C) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Mill.Creek.1 | MC1 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC1 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC1 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC1 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC1 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | 150 | 210 | 220 | 260 | 280 | 300 | 300 | 150 | 210 | 220 | 260 | 280 | 300 | 300 | 150 | 210 | 220 | 260 | 280 | 300 | 300 | 150 | 210 | 220 | 260 | 280 | 300 | 300 | 150 | 210 | 220 | 260 | 280 | 300 | 300
GADS Yr Availability: GADS only (C) | 3.268% | 0.1496% | 0.01708% | 0.00783% | 0.06351% | 90.78% | 94.29% | 3.268% | 0.1496% | 0.01708% | 0.00783% | 0.06351% | 90.78% | 94.29% | 3.268% | 0.1496% | 0.01708% | 0.00783% | 0.06351% | 90.78% | 94.29% | 3.268% | 0.1496% | 0.01708% | 0.00783% | 0.06351% | 90.78% | 94.29% | 3.268% | 0.1496% | 0.01708% | 0.00783% | 0.06351% | 90.78% | 94.29%
Mill.Creek.2 | MC2 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC2 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC2 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC2 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC2 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | 147 | 207 | 217 | 257 | 277 | 297 | 297 | 147 | 207 | 217 | 257 | 277 | 297 | 297 | 147 | 207 | 217 | 257 | 277 | 297 | 297 | 147 | 207 | 217 | 257 | 277 | 297 | 297 | 147 | 207 | 217 | 257 | 277 | 297 | 297
GADS Yr Availability: GADS only (C) | 0.08772% | 5.158% | 0.09492% | 0.1907% | 0.4448% | 88.31% | 94.29% | 0.08772% | 5.158% | 0.09492% | 0.1907% | 0.4448% | 88.31% | 94.29% | 0.08772% | 5.158% | 0.09492% | 0.1907% | 0.4448% | 88.31% | 94.29% | 0.08772% | 5.158% | 0.09492% | 0.1907% | 0.4448% | 88.31% | 94.29% | 0.08772% | 5.158% | 0.09492% | 0.1907% | 0.4448% | 88.31% | 94.29%
Mill.Creek.3 | MC3 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC3 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC3 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC3 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC3 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | 170 | 204 | 234 | 314 | 354 | 394 | 394 | 170 | 204 | 234 | 314 | 354 | 394 | 394 | 170 | 204 | 234 | 314 | 354 | 394 | 394 | 170 | 204 | 234 | 314 | 354 | 394 | 394 | 170 | 204 | 234 | 314 | 354 | 394 | 394
GADS Yr Availability: GADS only (C) | 2.026% | 0.3436% | 0.6241% | 0.258% | 0.6439% | 90.39% | 94.29% | 2.026% | 0.3436% | 0.6241% | 0.258% | 0.6439% | 90.39% | 94.29% | 2.026% | 0.3436% | 0.6241% | 0.258% | 0.6439% | 90.39% | 94.29% | 2.026% | 0.3436% | 0.6241% | 0.258% | 0.6439% | 90.39% | 94.29% | 2.026% | 0.3436% | 0.6241% | 0.258% | 0.6439% | 90.39% | 94.29%
Mill.Creek.4 | MC4 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC4 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC4 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC4 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2% | MC4 | FOR: | 3.511% | EFDR: | 1.75% | MOR: | 2.2%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | 175 | 296 | 326 | 406 | 446 | 486 | 486 | 175 | 296 | 326 | 406 | 446 | 486 | 486 | 175 | 296 | 326 | 406 | 446 | 486 | 486 | 175 | 296 | 326 | 406 | 446 | 486 | 486 | 175 | 296 | 326 | 406 | 446 | 486 | 486
GADS Yr Availability: GADS only (C) | 0.7651% | 0.7617% | 0.2129% | 4.974% | 0.1504% | 87.42% | 94.29% | 0.7651% | 0.7617% | 0.2129% | 4.974% | 0.1504% | 87.42% | 94.29% | 0.7651% | 0.7617% | 0.2129% | 4.974% | 0.1504% | 87.42% | 94.29% | 0.7651% | 0.7617% | 0.2129% | 4.974% | 0.1504% | 87.42% | 94.29% | 0.7651% | 0.7617% | 0.2129% | 4.974% | 0.1504% | 87.42% | 94.29%
Trimble.County.1 | TC1 | FOR: | 4.189% | EFDR: | 1.055% | MOR: | 2.2% | TC1 | FOR: | 4.189% | EFDR: | 1.055% | MOR: | 2.2% | TC1 | FOR: | 4.189% | EFDR: | 1.055% | MOR: | 2.2% | TC1 | FOR: | 4.189% | EFDR: | 1.055% | MOR: | 2.2% | TC1 | FOR: | 4.189% | EFDR: | 1.055% | MOR: | 2.2%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | 141 | 227.25 | 249.75 | 309.75 | 339.75 | 369.75 | 493 | 141 | 227.25 | 249.75 | 309.75 | 339.75 | 369.75 | 493 | 141 | 227.25 | 249.75 | 309.75 | 339.75 | 369.75 | 493 | 141 | 227.25 | 249.75 | 309.75 | 339.75 | 369.75 | 493 | 141 | 227.25 | 249.75 | 309.75 | 339.75 | 369.75 | 493
GADS Yr Availability: GADS only (C) | 0.1164% | 0.08984% | 1.972% | 1.148% | 0.9628% | 89.32% | 93.61% | 0.1164% | 0.08984% | 1.972% | 1.148% | 0.9628% | 89.32% | 93.61% | 0.1164% | 0.08984% | 1.972% | 1.148% | 0.9628% | 89.32% | 93.61% | 0.1164% | 0.08984% | 1.972% | 1.148% | 0.9628% | 89.32% | 93.61% | 0.1164% | 0.08984% | 1.972% | 1.148% | 0.9628% | 89.32% | 93.61%
Trimble.County.2 | TC2 | FOR: | 8.141% | EFDR: | 1.262% | MOR: | 3.8% | TC2 | FOR: | 8.141% | EFDR: | 1.262% | MOR: | 3.8% | TC2 | FOR: | 8.141% | EFDR: | 1.262% | MOR: | 3.8% | TC2 | FOR: | 8.141% | EFDR: | 1.262% | MOR: | 3.8% | TC2 | FOR: | 8.141% | EFDR: | 1.262% | MOR: | 3.8%
BLOCK: | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit | 1 | 2 | 3 | 4 | 5 | 6 | Tot Unit
State Capacity (I) | 330 | 427.5 | 450 | 510 | 540 | 570 | 760 | 330 | 427.5 | 450 | 510 | 540 | 570 | 760 | 330 | 427.5 | 450 | 510 | 540 | 570 | 760 | 330 | 427.5 | 450 | 510 | 540 | 570 | 760 | 330 | 427.5 | 450 | 510 | 540 | 570 | 760
GADS Yr Availability: GADS only (C) | 0.2822% | 0.9583% | 0.7519% | 4.976% | 2.259% | 78.83% | 88.06% | 0.2822% | 0.9583% | 0.7519% | 4.976% | 2.259% | 78.83% | 88.06% | 0.2822% | 0.9583% | 0.7519% | 4.976% | 2.259% | 78.83% | 88.06% | 0.2822% | 0.9583% | 0.7519% | 4.976% | 2.259% | 78.83% | 88.06% | 0.2822% | 0.9583% | 0.7519% | 4.976% | 2.259% | 78.83% | 88.06%

## AvailableStates
2018 |  |  | X | X*a2 | X*a3 | X*a4 | X*a5 | Y | Checking
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | Calculated EUOR | EUOR Target | Difference
1 | BR1 | 2018 | 0.00011075 | 0.033494 | 0.0092189 | 0.030731 | 0.01371 | 84.77% | 0.085 | 0.085 | 0
1 | BR1 | 2019 | 0.00011075 | 0.033494 | 0.0092189 | 0.030731 | 0.01371 | 84.77% | 0.085 | 0.085 | 0
1 | BR1 | 2020 | 0.00011075 | 0.033494 | 0.0092189 | 0.030731 | 0.01371 | 84.77% | 0.085 | 0.085 | 0
1 | BR1 | 2021 | 0.00011075 | 0.033494 | 0.0092189 | 0.030731 | 0.01371 | 84.77% | 0.085 | 0.085 | 0
1 | BR1 | 2022 | 0.00011075 | 0.033494 | 0.0092189 | 0.030731 | 0.01371 | 84.77% | 0.085 | 0.085 | 0
2 | BR2 | 2018 | 0.019984 | 0.00077945 | 0.00083398 | 0.00050466 | 0.056333 | 85.66% | 0.085 | 0.085 | -1.5266e-16
2 | BR2 | 2019 | 0.019984 | 0.00077945 | 0.00083398 | 0.00050466 | 0.056333 | 85.66% | 0.085 | 0.085 | -1.5266e-16
2 | BR2 | 2020 | 0.019984 | 0.00077945 | 0.00083398 | 0.00050466 | 0.056333 | 85.66% | 0.085 | 0.085 | -1.5266e-16
2 | BR2 | 2021 | 0.019984 | 0.00077945 | 0.00083398 | 0.00050466 | 0.056333 | 85.66% | 0.085 | 0.085 | -1.5266e-16
2 | BR2 | 2022 | 0.019984 | 0.00077945 | 0.00083398 | 0.00050466 | 0.056333 | 85.66% | 0.085 | 0.085 | -1.5266e-16
3 | BR3 | 2018 | 0.023093 | 0.0057642 | 0.0024773 | 0.0047679 | 0.002194 | 89.67% | 0.085 | 0.085 | 0
3 | BR3 | 2019 | 0.023093 | 0.0057642 | 0.0024773 | 0.0047679 | 0.002194 | 89.67% | 0.085 | 0.085 | 0
3 | BR3 | 2020 | 0.023093 | 0.0057642 | 0.0024773 | 0.0047679 | 0.002194 | 89.67% | 0.085 | 0.085 | 0
3 | BR3 | 2021 | 0.023093 | 0.0057642 | 0.0024773 | 0.0047679 | 0.002194 | 89.67% | 0.085 | 0.085 | 0
3 | BR3 | 2022 | 0.023093 | 0.0057642 | 0.0024773 | 0.0047679 | 0.002194 | 89.67% | 0.085 | 0.085 | 0
4 | GH1 | 2018 | 0.020844 | 0.0061179 | 0.010652 | 0.0011313 | 0.00086629 | 90.4% | 0.074 | 0.074 | 0
4 | GH1 | 2019 | 0.020844 | 0.0061179 | 0.010652 | 0.0011313 | 0.00086629 | 90.4% | 0.074 | 0.074 | 0
4 | GH1 | 2020 | 0.020844 | 0.0061179 | 0.010652 | 0.0011313 | 0.00086629 | 90.4% | 0.074 | 0.074 | 0
4 | GH1 | 2021 | 0.020844 | 0.0061179 | 0.010652 | 0.0011313 | 0.00086629 | 90.4% | 0.074 | 0.074 | 0
4 | GH1 | 2022 | 0.020844 | 0.0061179 | 0.010652 | 0.0011313 | 0.00086629 | 90.4% | 0.074 | 0.074 | 0
5 | GH2 | 2018 | 0.003733 | 0.0028422 | 0.034032 | 0.019304 | 0.0012942 | 88.24% | 0.074 | 0.074 | 0
5 | GH2 | 2019 | 0.003733 | 0.0028422 | 0.034032 | 0.019304 | 0.0012942 | 88.24% | 0.074 | 0.074 | 0
5 | GH2 | 2020 | 0.003733 | 0.0028422 | 0.034032 | 0.019304 | 0.0012942 | 88.24% | 0.074 | 0.074 | 0
5 | GH2 | 2021 | 0.003733 | 0.0028422 | 0.034032 | 0.019304 | 0.0012942 | 88.24% | 0.074 | 0.074 | 0
5 | GH2 | 2022 | 0.003733 | 0.0028422 | 0.034032 | 0.019304 | 0.0012942 | 88.24% | 0.074 | 0.074 | 0
6 | GH3 | 2018 | 0.0015403 | 0.0013053 | 0.0080037 | 0.061658 | 0.03972 | 83.14% | 0.074 | 0.074 | 0
6 | GH3 | 2019 | 0.0015403 | 0.0013053 | 0.0080037 | 0.061658 | 0.03972 | 83.14% | 0.074 | 0.074 | 0
6 | GH3 | 2020 | 0.0015403 | 0.0013053 | 0.0080037 | 0.061658 | 0.03972 | 83.14% | 0.074 | 0.074 | 0
6 | GH3 | 2021 | 0.0015403 | 0.0013053 | 0.0080037 | 0.061658 | 0.03972 | 83.14% | 0.074 | 0.074 | 0
6 | GH3 | 2022 | 0.0015403 | 0.0013053 | 0.0080037 | 0.061658 | 0.03972 | 83.14% | 0.074 | 0.074 | 0
7 | GH4 | 2018 | 0.0169 | 0.0085832 | 0.0021191 | 0.017976 | 0.014047 | 88.4% | 0.074 | 0.074 | 1.8041e-16
7 | GH4 | 2019 | 0.0169 | 0.0085832 | 0.0021191 | 0.017976 | 0.014047 | 88.4% | 0.074 | 0.074 | 1.8041e-16
7 | GH4 | 2020 | 0.0169 | 0.0085832 | 0.0021191 | 0.017976 | 0.014047 | 88.4% | 0.074 | 0.074 | 1.8041e-16
7 | GH4 | 2021 | 0.0169 | 0.0085832 | 0.0021191 | 0.017976 | 0.014047 | 88.4% | 0.074 | 0.074 | 1.8041e-16
7 | GH4 | 2022 | 0.0169 | 0.0085832 | 0.0021191 | 0.017976 | 0.014047 | 88.4% | 0.074 | 0.074 | 1.8041e-16
8 | MC1 | 2018 | 0.032679 | 0.0014959 | 0.00017082 | 7.8301e-05 | 0.00063509 | 90.78% | 0.074 | 0.074 | 0
8 | MC1 | 2019 | 0.032679 | 0.0014959 | 0.00017082 | 7.8301e-05 | 0.00063509 | 90.78% | 0.074 | 0.074 | 0
8 | MC1 | 2020 | 0.032679 | 0.0014959 | 0.00017082 | 7.8301e-05 | 0.00063509 | 90.78% | 0.074 | 0.074 | 0
8 | MC1 | 2021 | 0.032679 | 0.0014959 | 0.00017082 | 7.8301e-05 | 0.00063509 | 90.78% | 0.074 | 0.074 | 0
8 | MC1 | 2022 | 0.032679 | 0.0014959 | 0.00017082 | 7.8301e-05 | 0.00063509 | 90.78% | 0.074 | 0.074 | 0
9 | MC2 | 2018 | 0.00087716 | 0.051585 | 0.00094923 | 0.0019072 | 0.0044476 | 88.31% | 0.074 | 0.074 | -1.5266e-16
9 | MC2 | 2019 | 0.00087716 | 0.051585 | 0.00094923 | 0.0019072 | 0.0044476 | 88.31% | 0.074 | 0.074 | -1.5266e-16
9 | MC2 | 2020 | 0.00087716 | 0.051585 | 0.00094923 | 0.0019072 | 0.0044476 | 88.31% | 0.074 | 0.074 | -1.5266e-16
9 | MC2 | 2021 | 0.00087716 | 0.051585 | 0.00094923 | 0.0019072 | 0.0044476 | 88.31% | 0.074 | 0.074 | -1.5266e-16
9 | MC2 | 2022 | 0.00087716 | 0.051585 | 0.00094923 | 0.0019072 | 0.0044476 | 88.31% | 0.074 | 0.074 | -1.5266e-16
10 | MC3 | 2018 | 0.020259 | 0.003436 | 0.0062414 | 0.0025796 | 0.0064394 | 90.39% | 0.074 | 0.074 | -1.5266e-16
10 | MC3 | 2019 | 0.020259 | 0.003436 | 0.0062414 | 0.0025796 | 0.0064394 | 90.39% | 0.074 | 0.074 | -1.5266e-16
10 | MC3 | 2020 | 0.020259 | 0.003436 | 0.0062414 | 0.0025796 | 0.0064394 | 90.39% | 0.074 | 0.074 | -1.5266e-16
10 | MC3 | 2021 | 0.020259 | 0.003436 | 0.0062414 | 0.0025796 | 0.0064394 | 90.39% | 0.074 | 0.074 | -1.5266e-16
10 | MC3 | 2022 | 0.020259 | 0.003436 | 0.0062414 | 0.0025796 | 0.0064394 | 90.39% | 0.074 | 0.074 | -1.5266e-16
11 | MC4 | 2018 | 0.0076513 | 0.0076171 | 0.0021288 | 0.049742 | 0.0015042 | 87.42% | 0.074 | 0.074 | 0
11 | MC4 | 2019 | 0.0076513 | 0.0076171 | 0.0021288 | 0.049742 | 0.0015042 | 87.42% | 0.074 | 0.074 | 0
11 | MC4 | 2020 | 0.0076513 | 0.0076171 | 0.0021288 | 0.049742 | 0.0015042 | 87.42% | 0.074 | 0.074 | 0
11 | MC4 | 2021 | 0.0076513 | 0.0076171 | 0.0021288 | 0.049742 | 0.0015042 | 87.42% | 0.074 | 0.074 | 0
11 | MC4 | 2022 | 0.0076513 | 0.0076171 | 0.0021288 | 0.049742 | 0.0015042 | 87.42% | 0.074 | 0.074 | 0
12 | TC1 | 2018 | 0.0011636 | 0.00089844 | 0.019718 | 0.01148 | 0.0096277 | 89.32% | 0.074 | 0.074 | 0
12 | TC1 | 2019 | 0.0011636 | 0.00089844 | 0.019718 | 0.01148 | 0.0096277 | 89.32% | 0.074 | 0.074 | 0
12 | TC1 | 2020 | 0.0011636 | 0.00089844 | 0.019718 | 0.01148 | 0.0096277 | 89.32% | 0.074 | 0.074 | 0
12 | TC1 | 2021 | 0.0011636 | 0.00089844 | 0.019718 | 0.01148 | 0.0096277 | 89.32% | 0.074 | 0.074 | 0
12 | TC1 | 2022 | 0.0011636 | 0.00089844 | 0.019718 | 0.01148 | 0.0096277 | 89.32% | 0.074 | 0.074 | 0
13 | TC2 | 2018 | 0.002822 | 0.0095833 | 0.0075194 | 0.049762 | 0.022595 | 78.83% | 0.131 | 0.131 | 0
13 | TC2 | 2019 | 0.002822 | 0.0095833 | 0.0075194 | 0.049762 | 0.022595 | 78.83% | 0.131 | 0.131 | 0
13 | TC2 | 2020 | 0.002822 | 0.0095833 | 0.0075194 | 0.049762 | 0.022595 | 78.83% | 0.131 | 0.131 | 0
13 | TC2 | 2021 | 0.002822 | 0.0095833 | 0.0075194 | 0.049762 | 0.022595 | 78.83% | 0.131 | 0.131 | 0
13 | TC2 | 2022 | 0.002822 | 0.0095833 | 0.0075194 | 0.049762 | 0.022595 | 78.83% | 0.131 | 0.131 | 0

## Output-Prosym Outage Rate File
!********************************************************************************************************************************************************************************************************************************************************************************
! 2018 -2022 PROSYM Budget (Outage Rates / Availability Information)
!
!
! Target period is 2018 - 2022
!
!
!********************************************************************************************************************************************************************************************************************************************************************************
Stations Section
!********************************************************************************************************************************************************************************************************************************************************************************
Brown.1
| Statecaps | [v6] | [2018] | 37 | 74 | 77 | 87 | 97 | 107
| Stateavail | [v6] | [2018] | 0.00011075 | 0.033494 | 0.0092189 | 0.030731 | 0.01371 | /ADD 0.8477 @IncFOR / | - | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 0
|  |  | [2019] | 0.00011075 | 0.033494 | 0.0092189 | 0.030731 | 0.01371 | /ADD 0.8477 @IncFOR / | - | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 0
|  |  | [2020] | 0.00011075 | 0.033494 | 0.0092189 | 0.030731 | 0.01371 | /ADD 0.8477 @IncFOR / | - | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 0
|  |  | [2021] | 0.00011075 | 0.033494 | 0.0092189 | 0.030731 | 0.01371 | /ADD 0.8477 @IncFOR / | - | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 0
|  |  | [2022] | 0.00011075 | 0.033494 | 0.0092189 | 0.030731 | 0.01371 | /ADD 0.8477 @IncFOR / |  | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 0
Brown.2
| Statecaps | [v6] | [2018] | 64 | 78 | 88 | 128 | 148 | 168
| Stateavail | [v6] | [2018] | 0.019984 | 0.00077945 | 0.00083398 | 0.00050466 | 0.056333 | /ADD 0.8566 @IncFOR / | - | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 1
|  |  | [2019] | 0.019984 | 0.00077945 | 0.00083398 | 0.00050466 | 0.056333 | /ADD 0.8566 @IncFOR / | - | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 1
|  |  | [2020] | 0.019984 | 0.00077945 | 0.00083398 | 0.00050466 | 0.056333 | /ADD 0.8566 @IncFOR / | - | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 1
|  |  | [2021] | 0.019984 | 0.00077945 | 0.00083398 | 0.00050466 | 0.056333 | /ADD 0.8566 @IncFOR / | - | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 1
|  |  | [2022] | 0.019984 | 0.00077945 | 0.00083398 | 0.00050466 | 0.056333 | /ADD 0.8566 @IncFOR / |  | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 1
Brown.3
| Statecaps | [v6] | [2018] | 140 | 223 | 253 | 333 | 373 | 413
| Stateavail | [v6] | [2018] | 0.023093 | 0.0057642 | 0.0024773 | 0.0047679 | 0.002194 | /ADD 0.8967 @IncFOR / | - | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 2
|  |  | [2019] | 0.023093 | 0.0057642 | 0.0024773 | 0.0047679 | 0.002194 | /ADD 0.8967 @IncFOR / | - | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 2
|  |  | [2020] | 0.023093 | 0.0057642 | 0.0024773 | 0.0047679 | 0.002194 | /ADD 0.8967 @IncFOR / | - | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 2
|  |  | [2021] | 0.023093 | 0.0057642 | 0.0024773 | 0.0047679 | 0.002194 | /ADD 0.8967 @IncFOR / | - | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 2
|  |  | [2022] | 0.023093 | 0.0057642 | 0.0024773 | 0.0047679 | 0.002194 | /ADD 0.8967 @IncFOR / |  | ! EUOR= | 8.5% | EFOR= | 5.7% | FOR= | 3.699% | MOR= | 2.8% | EFDR= | 2.078% | 2
Ghent.1
| Statecaps | [v6] | [2018] | 218 | 289 | 319 | 399 | 439 | 479
| Stateavail | [v6] | [2018] | 0.020844 | 0.0061179 | 0.010652 | 0.0011313 | 0.00086629 | /ADD 0.9040 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 3
|  |  | [2019] | 0.020844 | 0.0061179 | 0.010652 | 0.0011313 | 0.00086629 | /ADD 0.9040 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 3
|  |  | [2020] | 0.020844 | 0.0061179 | 0.010652 | 0.0011313 | 0.00086629 | /ADD 0.9040 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 3
|  |  | [2021] | 0.020844 | 0.0061179 | 0.010652 | 0.0011313 | 0.00086629 | /ADD 0.9040 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 3
|  |  | [2022] | 0.020844 | 0.0061179 | 0.010652 | 0.0011313 | 0.00086629 | /ADD 0.9040 @IncFOR / |  | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 3
Ghent.2
| Statecaps | [v6] | [2018] | 225 | 296 | 326 | 406 | 446 | 486
| Stateavail | [v6] | [2018] | 0.003733 | 0.0028422 | 0.034032 | 0.019304 | 0.0012942 | /ADD 0.8824 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 4
|  |  | [2019] | 0.003733 | 0.0028422 | 0.034032 | 0.019304 | 0.0012942 | /ADD 0.8824 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 4
|  |  | [2020] | 0.003733 | 0.0028422 | 0.034032 | 0.019304 | 0.0012942 | /ADD 0.8824 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 4
|  |  | [2021] | 0.003733 | 0.0028422 | 0.034032 | 0.019304 | 0.0012942 | /ADD 0.8824 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 4
|  |  | [2022] | 0.003733 | 0.0028422 | 0.034032 | 0.019304 | 0.0012942 | /ADD 0.8824 @IncFOR / |  | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 4
Ghent.3
| Statecaps | [v6] | [2018] | 210 | 291 | 321 | 401 | 441 | 481
| Stateavail | [v6] | [2018] | 0.0015403 | 0.0013053 | 0.0080037 | 0.061658 | 0.03972 | /ADD 0.8314 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 5
|  |  | [2019] | 0.0015403 | 0.0013053 | 0.0080037 | 0.061658 | 0.03972 | /ADD 0.8314 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 5
|  |  | [2020] | 0.0015403 | 0.0013053 | 0.0080037 | 0.061658 | 0.03972 | /ADD 0.8314 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 5
|  |  | [2021] | 0.0015403 | 0.0013053 | 0.0080037 | 0.061658 | 0.03972 | /ADD 0.8314 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 5
|  |  | [2022] | 0.0015403 | 0.0013053 | 0.0080037 | 0.061658 | 0.03972 | /ADD 0.8314 @IncFOR / |  | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 5
Ghent.4
| Statecaps | [v6] | [2018] | 215 | 288 | 318 | 398 | 438 | 478
| Stateavail | [v6] | [2018] | 0.0169 | 0.0085832 | 0.0021191 | 0.017976 | 0.014047 | /ADD 0.8840 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 6
|  |  | [2019] | 0.0169 | 0.0085832 | 0.0021191 | 0.017976 | 0.014047 | /ADD 0.8840 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 6
|  |  | [2020] | 0.0169 | 0.0085832 | 0.0021191 | 0.017976 | 0.014047 | /ADD 0.8840 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 6
|  |  | [2021] | 0.0169 | 0.0085832 | 0.0021191 | 0.017976 | 0.014047 | /ADD 0.8840 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 6
|  |  | [2022] | 0.0169 | 0.0085832 | 0.0021191 | 0.017976 | 0.014047 | /ADD 0.8840 @IncFOR / |  | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.44% | MOR= | 2.2% | EFDR= | 1.823% | 6
Mill.Creek.1
| Statecaps | [v6] | [2018] | 150 | 210 | 220 | 260 | 280 | 300
| Stateavail | [v6] | [2018] | 0.032679 | 0.0014959 | 0.00017082 | 7.8301e-05 | 0.00063509 | /ADD 0.9078 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 9
|  |  | [2019] | 0.032679 | 0.0014959 | 0.00017082 | 7.8301e-05 | 0.00063509 | /ADD 0.9078 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 9
|  |  | [2020] | 0.032679 | 0.0014959 | 0.00017082 | 7.8301e-05 | 0.00063509 | /ADD 0.9078 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 9
|  |  | [2021] | 0.032679 | 0.0014959 | 0.00017082 | 7.8301e-05 | 0.00063509 | /ADD 0.9078 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 9
|  |  | [2022] | 0.032679 | 0.0014959 | 0.00017082 | 7.8301e-05 | 0.00063509 | /ADD 0.9078 @IncFOR / |  | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 9
Mill.Creek.2
| Statecaps | [v6] | [2018] | 147 | 207 | 217 | 257 | 277 | 297
| Stateavail | [v6] | [2018] | 0.00087716 | 0.051585 | 0.00094923 | 0.0019072 | 0.0044476 | /ADD 0.8831 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 10
|  |  | [2019] | 0.00087716 | 0.051585 | 0.00094923 | 0.0019072 | 0.0044476 | /ADD 0.8831 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 10
|  |  | [2020] | 0.00087716 | 0.051585 | 0.00094923 | 0.0019072 | 0.0044476 | /ADD 0.8831 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 10
|  |  | [2021] | 0.00087716 | 0.051585 | 0.00094923 | 0.0019072 | 0.0044476 | /ADD 0.8831 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 10
|  |  | [2022] | 0.00087716 | 0.051585 | 0.00094923 | 0.0019072 | 0.0044476 | /ADD 0.8831 @IncFOR / |  | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 10
Mill.Creek.3
| Statecaps | [v6] | [2018] | 170 | 204 | 234 | 314 | 354 | 394
| Stateavail | [v6] | [2018] | 0.020259 | 0.003436 | 0.0062414 | 0.0025796 | 0.0064394 | /ADD 0.9039 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 11
|  |  | [2019] | 0.020259 | 0.003436 | 0.0062414 | 0.0025796 | 0.0064394 | /ADD 0.9039 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 11
|  |  | [2020] | 0.020259 | 0.003436 | 0.0062414 | 0.0025796 | 0.0064394 | /ADD 0.9039 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 11
|  |  | [2021] | 0.020259 | 0.003436 | 0.0062414 | 0.0025796 | 0.0064394 | /ADD 0.9039 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 11
|  |  | [2022] | 0.020259 | 0.003436 | 0.0062414 | 0.0025796 | 0.0064394 | /ADD 0.9039 @IncFOR / |  | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 11
Mill.Creek.4
| Statecaps | [v6] | [2018] | 175 | 296 | 326 | 406 | 446 | 486
| Stateavail | [v6] | [2018] | 0.0076513 | 0.0076171 | 0.0021288 | 0.049742 | 0.0015042 | /ADD 0.8742 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 12
|  |  | [2019] | 0.0076513 | 0.0076171 | 0.0021288 | 0.049742 | 0.0015042 | /ADD 0.8742 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 12
|  |  | [2020] | 0.0076513 | 0.0076171 | 0.0021288 | 0.049742 | 0.0015042 | /ADD 0.8742 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 12
|  |  | [2021] | 0.0076513 | 0.0076171 | 0.0021288 | 0.049742 | 0.0015042 | /ADD 0.8742 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 12
|  |  | [2022] | 0.0076513 | 0.0076171 | 0.0021288 | 0.049742 | 0.0015042 | /ADD 0.8742 @IncFOR / |  | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 3.511% | MOR= | 2.2% | EFDR= | 1.75% | 12
Trimble.County.1
| Statecaps | [v6] | [2018] | 141 | 227.25 | 249.75 | 309.75 | 339.75 | 369.75
| Stateavail | [v6] | [2018] | 0.0011636 | 0.00089844 | 0.019718 | 0.01148 | 0.0096277 | /ADD 0.8932 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 4.189% | MOR= | 2.2% | EFDR= | 1.055% | 13
|  |  | [2019] | 0.0011636 | 0.00089844 | 0.019718 | 0.01148 | 0.0096277 | /ADD 0.8932 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 4.189% | MOR= | 2.2% | EFDR= | 1.055% | 13
|  |  | [2020] | 0.0011636 | 0.00089844 | 0.019718 | 0.01148 | 0.0096277 | /ADD 0.8932 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 4.189% | MOR= | 2.2% | EFDR= | 1.055% | 13
|  |  | [2021] | 0.0011636 | 0.00089844 | 0.019718 | 0.01148 | 0.0096277 | /ADD 0.8932 @IncFOR / | - | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 4.189% | MOR= | 2.2% | EFDR= | 1.055% | 13
|  |  | [2022] | 0.0011636 | 0.00089844 | 0.019718 | 0.01148 | 0.0096277 | /ADD 0.8932 @IncFOR / |  | ! EUOR= | 7.4% | EFOR= | 5.2% | FOR= | 4.189% | MOR= | 2.2% | EFDR= | 1.055% | 13
Trimble.County.2
| Statecaps | [v6] | [2018] | 330 | 427.5 | 450 | 510 | 540 | 570
| Stateavail | [v6] | [2018] | 0.002822 | 0.0095833 | 0.0075194 | 0.049762 | 0.022595 | /ADD 0.7883 @IncFOR / | - | ! EUOR= | 13.1% | EFOR= | 9.3% | FOR= | 8.141% | MOR= | 3.8% | EFDR= | 1.262% | 14
|  |  | [2019] | 0.002822 | 0.0095833 | 0.0075194 | 0.049762 | 0.022595 | /ADD 0.7883 @IncFOR / | - | ! EUOR= | 13.1% | EFOR= | 9.3% | FOR= | 8.141% | MOR= | 3.8% | EFDR= | 1.262% | 14
|  |  | [2020] | 0.002822 | 0.0095833 | 0.0075194 | 0.049762 | 0.022595 | /ADD 0.7883 @IncFOR / | - | ! EUOR= | 13.1% | EFOR= | 9.3% | FOR= | 8.141% | MOR= | 3.8% | EFDR= | 1.262% | 14
|  |  | [2021] | 0.002822 | 0.0095833 | 0.0075194 | 0.049762 | 0.022595 | /ADD 0.7883 @IncFOR / | - | ! EUOR= | 13.1% | EFOR= | 9.3% | FOR= | 8.141% | MOR= | 3.8% | EFDR= | 1.262% | 14
|  |  | [2022] | 0.002822 | 0.0095833 | 0.0075194 | 0.049762 | 0.022595 | /ADD 0.7883 @IncFOR / |  | ! EUOR= | 13.1% | EFOR= | 9.3% | FOR= | 8.141% | MOR= | 3.8% | EFDR= | 1.262% | 14

## Outage Formulas
| Formulas | GADS Event Code | Prosym Format
FOR = | FOH | U1 ,U2 ,U3 ,SF | 1 | 2 | 3 | 4 | 5 | 6
| FOH + SH |  | 37 | 74 | 77 | 87 | 97 | 107 | b1 | b2 | b3 | b4 | b5 | Max
|  |  | 0.6707% | 0.3079% | 3.084% | 2.282% | 4.494% | 82.58% | X | X*a2 | X*a3 | X*a4 | X*a5 | Y
MOR = | MOH | U4, MO
MOH + SH
EFOR = | FOH + EFDH | U1 ,U2 ,U3 ,SF, D1, D2, D3, D4 | 1-Y= (1+a2+a3+a4+a5)*X+(FOR+MOR)
| FOH + SH |  | Y=1- (1+a2+a3+a4+a5)*X-(FOR+MOR)
EUOR=1-(b1*X+b2*a2*X+b3*a3*X+b4*a4*X+b5*a5*X+Y*Max)/Max
EFDR = | EFDH | D1, D2, D3, D4 | Y=((1-EUOR)*Max-X*(b1+a2*b2+a3*b3+a4*b4+a5*b5))/Max
SH
TFOR: FOR + MOR = | FOH + MOH | U1 ,U2 ,U3 ,SF, U4, MO
FOH + MOH+ SH
EUOR = | FOH + EFDH + MOH | U1 ,U2 ,U3 ,SF, D1, D2, D3, D4, U4, MO
FOH + MOH+ SH
FOR: Forced Outage Rate
MOR: Maintenance Outage Rate
EFOR: Equivalent Forced Outage Rate
EFDR: Equivalent Forced Derate Rate
TFOR: Total Forced Outage Rate
EUOR: Equivalent Unit Outage Rate
FOH: Forced Outage Hours
MOH: Maintenance Outage Hours
SH: Service Hours
EFDH: Equivalent Forced Derate Hours