## Test Results
Test Results of 2007 Sample Meters - Year 14
Serial No. | Maximum | Intermediate | Minimum | Total Water Flow | Testing Date
34107783 | 99 | 100 | 99 | 347457.2 | 2021-10-29
34107749 | 99.2 | 100 | 101 | 649309.7 | 2021-10-29
34107795 | 98.9 | 100 | 100 | 518644.6 | 2021-10-29
34107762 | 98.9 | 101 | 100 | 737420.4 | 2021-10-29
34107718 | 99.6 | 101 | 100 | 526191.8 | 2021-10-29
34107724 | 99.4 | 101 | 99 | 696047.8 | 2021-10-29
34107743 | 98.8 | 101 | 99 | 892273.2 | 2021-10-29

## Maximum
ANSI Standard for Maximum Flow
Test Results
1 | Sample Size: n | 7 | 99
2 | Sum of Measurements | 693.8 | 99.2
3 | Sum of Squared Measurements | 68766.02 | 98.9
4 | Correction Factor (CF) | 68765.4914 | 98.9
5 | Corrected Sum of Squares (SS) | 0.52857 | 99.6
6 | Variance (V) | 0.088095 | 99.4
7 | Estimate of Lot Standard Deviation | 0.29681 | 98.8
8 | Sample Mean | 99.1143
9 | Upper Specification Limit | 101.5
10 | Lower Specification Limit | 98.5
11 | Quality Index: QU (upper) | 8.0379
12 | Quality Index: QL (lower) | 2.0696
ANSI Standard Table B-5 used to derive values below
13 | Est. of Lot Percent NcF above Upper | 0%
14 | Est. of Lot Percent NcF below Lower | 0.21%
15 | Total Est. Percent NcF in Lot (p) | 0.21%
16 | Max. Allowable Percent NcF (M) | 8.4%
17 | Acceptability Criterion (to accept, P<M) | Accepted

## Intermediate
ANSI Standard for Intermediate Flow
Test Results
1 | Sample Size: n | 7 | 100
2 | Sum of Measurements | 704 | 100
3 | Sum of Squared Measurements | 70804 | 100
4 | Correction Factor (CF) | 70802.2857 | 101
5 | Corrected Sum of Squares (SS) | 1.7143 | 101
6 | Variance (V) | 0.28571 | 101
7 | Estimate of Lot Standard Deviation | 0.53452 | 101
8 | Sample Mean | 100.5714
9 | Upper Specification Limit | 101.5
10 | Lower Specification Limit | 98.5
11 | Quality Index: QU (upper) | 1.7372
12 | Quality Index: QL (lower) | 3.8753
ANSI Standard Table B-5 used to derive values below
13 | Est. of Lot Percent NcF above Upper | 2.2%
14 | Est. of Lot Percent NcF below Lower | 0%
15 | Total Est. Percent NcF in Lot (p) | 2.2%
16 | Max. Allowable Percent NcF (M) | 8.4%
17 | Acceptability Criterion (to accept, P<M) | Accepted

## Minimum
ANSI Standard for Minimum Flow
Test Results
1 | Sample Size: n | 3 | 99
2 | Sum of Measurements | 298 | 100
3 | Sum of Squared Measurements | 29602 | 99
4 | Correction Factor (CF) | 29601.3333
5 | Corrected Sum of Squares (SS) | 0.66667
6 | Variance (V) | 0.33333
7 | Estimate of Lot Standard Deviation | 0.57735
8 | Sample Mean | 99.3333
9 | Lower Specification Limit | 90
10 | Quality Index: QL (lower) | 16.1658
ANSI Standard Table B-5 used to derive values below
11 | Est. of Lot Percent NcF | 0%
12 | Max. Allowable Percent NcF (M) | 40.47%
13 | Acceptability Criterion (to accept, P<M) | Accepted