## Test Results
Test Results of 2008 Sample Meters - Year 13
Serial No. | Maximum | Intermediate | Minimum | Total Water Flow | Testing Date
235123516 | 99.3 | 101 | 98 | 34858.1 | 2021-12-03
234986564 | 98.6 | 101 | 98 | 2322475.55 | 2021-12-01
235123346 | 99.4 | 101 | 99 | 624991.7 | 2021-12-03
235123423 | 99.4 | 100 | 99 | 287523.4 | 2021-12-03
234824550 | 99.1 | 100 | 98 | 498689 | 2021-12-03
234986519 | 98.8 | 101 | 99 | 744001.9 | 2021-12-01
234986482 | 99.6 | 101 | 100 | 374674.2 | 2021-12-01
234986585 | 99.3 | 100 | 98 | 530986.4 | 2021-12-03
235123666 | 99.4 | 100 | 99 | 756381.4 | 2021-12-03
235123401 | 99.3 | 101 | 99 | 584428.8 | 2021-12-01
235123315 | 99.1 | 101 | 99 | 125404.4 | 2021-12-01
234824517 | 99.2 | 100 | 98 | 870950.4 | 2021-12-01
234986550 | 99.4 | 101 | 100 | 615333.5 | 2021-12-03
234824501 | 99.8 | 101 | 97 | 321322.9 | 2021-12-01
234824704 | 98.9 | 100 | 98 | 782051.2 | 2021-12-01
234986351 | 99.5 | 101 | 100 | 101136.6 | 2021-12-03
235123243 | 99.2 | 100 | 99 | 717787.2 | 2021-12-03
235123128 | 99.2 | 101 | 99 | 834511.6 | 2021-12-03
235123343 | 99.4 | 101 | 98 | 361644.4 | 2021-12-03
234986393 | 98.8 | 100 | 97 | 286027.2 | 2021-11-12
235123297 | 99.4 | 101 | 98 | 237850.2 | 2021-11-12
235123535 | 99.6 | 101 | 100 | 392433.85 | 2021-12-01
234986571 | 99.2 | 100 | 99 | 647141.2 | 2021-12-01
234824746 | 98.9 | 100 | 96 | 799360 | 2021-11-12
234824744 | 98.9 | 101 | 97 | 677136.1 | 2021-11-12
234986454 | 99 | 101 | 98 | 667096.8 | 2021-11-12
234986383 | 98.7 | 101 | 96 | 834038 | 2021-11-12
235123355 | 99.6 | 100 | 100 | 183543.9 | 2021-12-03
234824680 | 99 | 100 | 97 | 225991.4 | 2021-11-12
235123628 | 99.1 | 100 | 97 | 8567285.4 | 2021-12-01
234986587 | 99.6 | 101 | 98 | 414569.4 | 2021-11-12
234824582 | 99.6 | 100 | 97 | 817752.8 | 2021-12-01
234824597 | 98.7 | 100 | 98 | 193716.2 | 2021-12-01
234824752 | 98.6 | 100 | 97 | 309275.65 | 2021-12-01
234986418 | 98.7 | 100 | 97 | 1197630 | 2021-12-01

## Maximum
ANSI Standard for Maximum Flow
Test Results
1 | Sample Size: n | 35 | 99.3
2 | Sum of Measurements | 3471.3 | 98.6
3 | Sum of Squared Measurements | 344287.21 | 99.4
4 | Correction Factor (CF) | 344283.534 | 99.4
5 | Corrected Sum of Squares (SS) | 3.676 | 99.1
6 | Variance (V) | 0.10812 | 98.8
7 | Estimate of Lot Standard Deviation | 0.32881 | 99.6
8 | Sample Mean | 99.18 | 99.3
9 | Upper Specification Limit | 101.5 | 99.4
10 | Lower Specification Limit | 98.5 | 99.3
11 | Quality Index: QU (upper) | 7.0557 | 99.1
12 | Quality Index: QL (lower) | 2.068 | 99.2
ANSI Standard Table B-5 used to derive values below |  |  | 99.4
13 | Est. of Lot Percent NcF above Upper | 0% | 99.8
14 | Est. of Lot Percent NcF below Lower | 1.68% | 98.9
15 | Total Est. Percent NcF in Lot (p) | 1.68% | 99.5
16 | Max. Allowable Percent NcF (M) | 5.58% | 99.2
17 | Acceptability Criterion (to accept, P<M) | Accepted | 99.2
99.4
98.8
99.4
99.6
99.2
98.9
98.9
99
98.7
99.6
99
99.1
99.6
99.6
98.7
98.6
98.7

## Intermediate
ANSI Standard for Intermediate Flow
Test Results
1 | Sample Size: n | 35 | 101
2 | Sum of Measurements | 3518 | 101
3 | Sum of Squared Measurements | 353618 | 101
4 | Correction Factor (CF) | 353609.2571 | 100
5 | Corrected Sum of Squares (SS) | 8.7429 | 100
6 | Variance (V) | 0.25714 | 101
7 | Estimate of Lot Standard Deviation | 0.50709 | 101
8 | Sample Mean | 100.5143 | 100
9 | Upper Specification Limit | 101.5 | 100
10 | Lower Specification Limit | 98.5 | 101
11 | Quality Index: QU (upper) | 1.9439 | 101
12 | Quality Index: QL (lower) | 3.9722 | 100
ANSI Standard Table B-5 used to derive values below |  |  | 101
13 | Est. of Lot Percent NcF above Upper | 2.37% | 101
14 | Est. of Lot Percent NcF below Lower | 0% | 100
15 | Total Est. Percent NcF in Lot (p) | 2.37% | 101
16 | Max. Allowable Percent NcF (M) | 5.58% | 100
17 | Acceptability Criterion (to accept, P<M) | Accepted | 101
101
100
101
101
100
100
101
101
101
100
100
100
101
100
100
100
100

## Minimum
ANSI Standard for Minimum Flow
Test Results
1 | Sample Size: n | 7 | 98
2 | Sum of Measurements | 686 | 99
3 | Sum of Squared Measurements | 67232 | 98
4 | Correction Factor (CF) | 67228 | 99
5 | Corrected Sum of Squares (SS) | 4 | 97
6 | Variance (V) | 0.66667 | 98
7 | Estimate of Lot Standard Deviation | 0.8165 | 97
8 | Sample Mean | 98
9 | Lower Specification Limit | 90
10 | Quality Index: QL (lower) | 9.798
ANSI Standard Table B-5 used to derive values below
11 | Est. of Lot Percent NcF | 0%
12 | Max. Allowable Percent NcF (M) | 30.5%
13 | Acceptability Criterion (to accept, P<M) | Accepted