## Test Results
Test Results of 2006 Sample Meters - Year 13
Serial No. | Maximum | Intermediate | Minimum | Total Water Flow | Testing Date
32579088 | 99.13 | 100.14 | 99 | 178183.15 | 2019-12-17
32579085 | 99.08 | 100.54 | 98.9 | 474926.1 | 2019-12-17
32579090 | 98.82 | 99.84 | 98.9 | 362197.35 | 2019-12-17

## Maximum
ANSI Standard for Maximum Flow
Test Results
1 | Sample Size: n | 3 | 99.13
2 | Sum of Measurements | 297.03 | 99.08
3 | Sum of Squared Measurements | 29408.9957 | 98.82
4 | Correction Factor (CF) | 29408.9403
5 | Corrected Sum of Squares (SS) | 0.0554
6 | Variance (V) | 0.0277
7 | Estimate of Lot Standard Deviation | 0.16643
8 | Sample Mean | 99.01
9 | Upper Specification Limit | 101.5
10 | Lower Specification Limit | 98.5
11 | Quality Index: QU (upper) | 14.961
12 | Quality Index: QL (lower) | 3.0643
ANSI Standard Table B-5 used to derive values below
13 | Est. of Lot Percent NcF above Upper | 0%
14 | Est. of Lot Percent NcF below Lower | 0%
15 | Total Est. Percent NcF in Lot (p) | 0%
16 | Max. Allowable Percent NcF (M) | 7.59%
17 | Acceptability Criterion (to accept, P<M) | Accepted

## Intermediate
ANSI Standard for Intermediate Flow
Test Results
1 | Sample Size: n | 3 | 100.14
2 | Sum of Measurements | 300.52 | 100.54
3 | Sum of Squared Measurements | 30104.3368 | 99.84
4 | Correction Factor (CF) | 30104.0901
5 | Corrected Sum of Squares (SS) | 0.24667
6 | Variance (V) | 0.12333
7 | Estimate of Lot Standard Deviation | 0.35119
8 | Sample Mean | 100.1733
9 | Upper Specification Limit | 101.5
10 | Lower Specification Limit | 98.5
11 | Quality Index: QU (upper) | 3.7776
12 | Quality Index: QL (lower) | 4.7648
ANSI Standard Table B-5 used to derive values below
13 | Est. of Lot Percent NcF above Upper | 0%
14 | Est. of Lot Percent NcF below Lower | 0%
15 | Total Est. Percent NcF in Lot (p) | 0%
16 | Max. Allowable Percent NcF (M) | 7.59%
17 | Acceptability Criterion (to accept, P<M) | Accepted

## Minimum
ANSI Standard for Minimum Flow
Test Results
1 | Sample Size: n | 3 | 99
2 | Sum of Measurements | 296.8 | 98.9
3 | Sum of Squared Measurements | 29363.42 | 98.9
4 | Correction Factor (CF) | 29363.4133
5 | Corrected Sum of Squares (SS) | 0.0066667
6 | Variance (V) | 0.0033333
7 | Estimate of Lot Standard Deviation | 0.057735
8 | Sample Mean | 98.9333
9 | Lower Specification Limit | 90
10 | Quality Index: QL (lower) | 154.7299
ANSI Standard Table B-5 used to derive values below
11 | Est. of Lot Percent NcF | 0%
12 | Max. Allowable Percent NcF (M) | 40.47%
13 | Acceptability Criterion (to accept, P<M) | Accepted