## HMPL Decommisioning Summary
Station II Decommissioning Scope of Work
Item Number | Scope Item | Team Lead(s) | Work Description | Before or After Feb 1st | Ramp Down or Decommission | Capital or FDE | Completed
or Decommission
1 | H-1 Shut Down Time Line | Jeff Francis | Operation will start the process of H-1 shut down at 18:00 on Jan 31st | After | Ramp Down | FDE
2 | H-2 Shut Down Time Line | Jeff Francis | Operation will start the process of H-2 shut down at 18:00 on Jan 31st | After | Ramp Down | FDE
3 | HMPL Demo Cleaning | Jeff Francis | Cleaning of H1 and H2 will be done by contactors. | After | Ramp Down | FDE
4 | Asbestos Abatement | Barrett Cheatham | Asbestos located in Station II will be identified and properly disposed of by Contractors. | After | Ramp Down | FDE
5 | Electrical Power Disconnect | Don Shelton Teresa Taylor | All electrical items and equipment will need to be disconnected where they are linked between Station II and Reid Stations. Also all switchyard equipment connected to Station II will be disconnected too. | After | Ramp Down | Capital
6 | Water Disconnect | Barrett Cheatham | All water supplies from Station II to R-1 will be disconnected. | After | Ramp Down | FDE
7 | Air Disconnect | Barrett Cheatham | The air supply to the Booth System is going to be disconnected at the east end of the Trestle and capped. | After | Ramp Down | FDE
8 | Draining Water and Steam | Jeff Francis Richard Parker | Before Decommissioning Station II all water and steam will need to be drained from all the vessels on site, including boilers, heaters, and the circulating water systems. | After | Ramp Down | FDE
9 | Remove Hydrogen | Jeff Francis Richard Parker | The generators will need to be purged from hydrogen to air. All hydrogen cylinders will need to be properly removed from Station II. | After | Ramp Down | FDE
10 | Remove Sulfuric Acid | Chad Phillips | The acid and caustic chemicals will be removed from the bulk tanks, day tanks, and piping systems. The chemicals will then be transferred to Green and the tanks and piping would be cleaned for safe destruction. | After | Ramp Down | FDE
11 | Remove Oils | Barrett Cheatham | The oils in the equipment and storage tanks will properly drained and disposed. The Emergency Diesel generator fuel oil tank in H2 basement will also need to be disconnected. | After | Ramp Down | FDE
12 | Remove Freon | Don Shelton | The Freon onsite at Station II will be removed from equipment and captured by contractors. The contractor will dispose of the Freon according to environmental regulations. | After | Ramp Down | FDE
13 | Remove Ammonia | Chad Phillips | Paul Akers Inc., will compress any remaining Ammonia in the tanks and haul it offsite. An environmental contractor would then come to clean the ammonia tanks so they are safe for disposal. | After | Ramp Down | FDE
14 | Remove Coal | Troy Pollard Jeff Francis | Transfer any remaining coal from Station II to Green once an agreement is in place. | After | Ramp Down | FDE
15 | Maintain FAA Stack Lighting | Don Shelton Teresa Taylor | The FAA stack lighting will need to be maintained as long as the stacks are standing. The power feeds need to be moved to Reid 1 from Station II. | After | Ramp Down | FDE
16 | Mooring Cell Warning Lights | Don Shelton | Mooring cell Navigation Lights will remain powered by the intake and the Barge unloader. Which cells will be powered by either the intake or the Barge unloader will be determined by their location on site. | After | Ramp Down | FDE
17 | All Batteries | Chad Phillips | The batteries onsite that will need to be removed are: H1, H2, Scrubber, and the Diesel Fire Pump batteries. These will be removed by contractors and properly disposed of. | After | Ramp Down | FDE
18 | Mercury Filled Equipment | Teresa Taylor | All equipment and instruments on site that have mercury (see mercury tab) in them will need to be properly identified and disposed of during the decommissioning of Station II. | After | Decommission | FDE
19 | Relocate Potable Water Line | Tom Lilly Barrett Cheatham | Station II potable water disconnect will require that the two isolation valves, which are located in the gas turbine switch yard and east of the Burns and Roe building, closed and permanently isolated. | Before | Ramp Down | Capital
20 | Disconnect Natural Gas to Reid | Barrett Cheatham | The Natural Gas line that runs to Reid will need to be properly capped and vented. The capping will be done close to the reducing station. | Before | Ramp Down | FDE | 2019-01-07
21 | Disconnect Hydrogen to Reid | Barrett Cheatham | The Hydrogen supply lines will be disconnected. The original line runs along the support beam structure between R1 and H1. | After | Ramp Down | FDE
22 | Disconnect Fly Ash to Reid | Barrett Cheatham | The fly ash lines will be disconnected at Reid 1 on the west side for Precip, Dust Collector, and Economizer seep lines. The bottom ash system will be disconnected on the 2nd floor landing. | Before | Ramp Down | FDE | 2019-01-08
23 | Fencing to Separate Reid/SII Basement | Gary Bunch | Perimeter fencing/barriers will be installed to separate Reid and Station II before decommissioning starts. | After | Decommission | FDE
24 | Relocate Backup Feed for Microwave System | Don Shelton Teresa Taylor | Currently the Microwave systems power feed are coming from Reid and Station II. A secondary feed will need to be created before Station II is disconnected for redundancies. | After | Ramp Down | Capital
25 | Relocate electrical feed for Coal Handling | Don Shelton Teresa Taylor | Currently the backup electrical feed is through Reid Station. If a redundant line is needed it will have to be ran. | After | Ramp Down | Capital
26 | Relocate R-1 Controls | Teresa Taylor | The Reid 1 controls relocation project includes all existing equipment that is currently used for miscellaneous operations that needs to be operable after the decommissioning of H1 and H2. The list includes the controls for the #1 and #3 Circulating Water Pumps for the HWU contract, the electrical switching controls for the Start Up transformer and the 4KV switchgear, and the Condenser Inlet and Outlet valve controls that are used for the Water Permit. This project will install a Allen Bradley PLC in the Reid Conference Room with an HMI for control at Reid and in the Green Control Room. | Before | Ramp Down | FDE
27 | Close Ash Pond | Gary Bunch | The closing of the ash ponds at Station II will be done by contractors. The contractors currently reviewing this is Aecom. | After | Decommission | FDE
29 | Nuclear Sources | Jeff Brown | All nuclear sources on site at Station II will be identified, removed and disposed of | After | Ramp Down | FDE
30 | Install Site Security | Gary Bunch | Before decommissioning, to separate Reid facilities from Station II activities locks will be installed on all access into the plant, the warehouse, and other Reid structures. | After | Ramp Down | FDE
31 | Remove Industrial gases (welding, Refrigeration) | Mary Holmes | All industrial gases used on site at Station II will be identified and removed. They will be collected and removed by Airgas. | After | Ramp Down | FDE
32 | Switchyard breakers opened and Locked | Don Shelton Teresa Taylor | The switchyard breakers will need to be opened and permanently locked in the open position during decommissioning. BREC's ET&S team will complete this on site. | After | Ramp Down | FDE
33 | Drain Oil filled Transformers | Don Shelton | BREC electric personnel will drain and collect all oil from small transformers on site at Station II. The oil will be properly disposed of according to environmental regulations. | After | Decommission | FDE
34 | Responsibility for Property Taxes | Headquarters
35 | Responsibility for Insurance | Headquarters
36 | Fire Protection Systems Maintained | Jeff Francis Richard Parker | The fire protection onsite will be maintained up to the point of demolition. | After | Decommission | FDE
37 | Sump Pumps Maintained in Service | Barrett Cheatham | Sumps on Reid will have to remain in operation and discharge line redirected | After | Ramp Down | FDE
38 | Remove Fuel Oil and Gasoline | Jeff Francis Richard Parker | All fuel oil will need to be removed from the lines leading into the Station II units and disposed of properly. | After | Ramp Down | FDE
39 | Structure Connections | Barrett Cheatham | All catwalks that connect Reid 1 to Station II will need to be removed. | After | Decommission | Capital
40 | Plant Sewage and Waste Pump | Barrett Cheatham | This pump is used only on HMPL it can be disconnected | After | Ramp Down | FDE
41 | Gas Turbine Electric Feed | Teresa Taylor | The Gas Turbine currently has a transformer that provides power to auxiliary equipment when the GT is not running. (i.e. oil pumps, hydrogen seal, etc.) | After | Ramp Down | Capital
42 | R1 Fuel oil pumps | Barrett Cheatham | The R-1 fuel oil transfer pumps are located in H-1 basement | Before | Ramp Down | FDE
2019-01-10

## Cost Summary
Covers the cost for both units
| Descriptions | Decommissioning | Ramp Down
1 | Vacuum and Washing | 301000 | 70000
2 | Asbestos Abatement | 1913784
3 | Tank Cleaning | 140000
5 | Batteries Disposal | 0
6 | Mercury Disposal | 6000
7 | Potable Water Line | 30966.31 | 30966.31
8 | Back Up feed for Microwave | 0
9 | Coal Handel Feed | 0 | 0
10 | R-1 Control relocate | 66466.85 | 66466.85
11 | Nuclear Sources Disposal | 10000 | 10000
12 | Gas Turbine Back up Feed | 25000 | 25000
Total |  | 2493217.16 | 202433.16
The Tab "Ramp Down" identify the items needed to be complete before Jan 31st.
Note on E8: Keith L Scott: Contractor to be onsite to give a cost estimate on 1/10/19

## H-1 Shut Down Time Line
Henderson 1 Shut down Timeline
Task |  | Date | Time
H1 | Stop feeding chlorine to cooling tower | 2019-01-29 | 1600 Hrs
H1 | Stop running coal to H1 | 2019-01-31 | 1000 Hrs
H1 | Run bunkers low as possible /empty | 2019-01-31 | 1700 Hrs
H1 | Unit offline | 2019-01-31 | 1800 Hrs
H1 | Drain Boiler | 2019-01-31 | 1900 Hrs
H1 | Start vacuuming bunkers | 2019-02-01 | 0600 Hrs
H1 | Start Boiler Deslag (explosive cleaning) | 2019-02-01 | 0600 Hrs
H1 | Start Purging generator to CO2 and then to air | 2019-02-01 | 0800 Hrs
H1 | Drain feedwater systems | 2019-02-01 | 1000 Hrs
H1 | Deslag Complete | 2019-02-01 | 1400 Hrs
H1 | Purging of Generator Complete | 2019-02-01 | 1600 hrs
H1 | Pull wet bottom | 2019-02-01 | 1700 Hrs
H1 | Start draining circulating water systems | 2019-02-02 | 0700 Hrs
H1 | Cleaning wet seal/wet bottom pit | 2019-02-02 | 1000 Hrs
H1 | Start draining condensate water system | 2019-02-02 | 1800 Hrs
H1 | Start draining Auxiliary water system | 2019-02-03 | 0700 Hrs
H1 | Turbine off gear shut down lube oil and seal oil systems | 2019-02-03 | 1800 Hrs
H1 | H1 Ready | 2019-02-03 | 2200 Hrs
Area's to be cleaned
H1 | Fan boiler through SCR's 100 degrees gas In
H1 | Shut all fans down, open boiler and SCR doors
H1 | Vacuum Mill balls
H1 | Boiler backpass (explosive cleaning)
H1 | Vacuuming of penthouse
H1 | Vacuuming SCR's top layer
H1 | Pull catalyst seals vacuum between catalyst
H1 | vacuum middle layer of catalyst
H1 | Pull catalyst seals vacuum between catalyst
H1 | vacuum scr slope area and hoppers
H1 | vacuum scr ductwork and diverter dampers
H1 | Scrubbers - start washing at the stack inlet and work down through the absorber module and clean out the reaction tank

## H-2 Shut Down Time Line
Henderson 2 Shut down Timeline
Task |  | Date | Time
H2 | Stop feeding chlorine to cooling tower | 2019-01-29 | 0800 Hrs
H2 | Stop running coal to H2 | 2019-01-31 | 1000 Hrs
H2 | Run bunkers low as possible /empty | 2019-01-31 | 1700 Hrs
H2 | Unit offline | 2019-01-31 | 1800 Hrs
H2 | Drain Boiler | 2019-01-31 | 1900 Hrs
H2 | Start draining cirulating water systems | 2019-02-01 | 0600 Hrs
H2 | Start vacuuming bunkers | 2019-02-01 | 0700 Hrs
H2 | Start Purging generator to CO2 than air | 2019-02-01 | 0800 Hrs
H2 | Drain feedwater systems | 2019-02-01 | 1000 Hrs
H2 | Start Deslag Boiler (explosive cleaning) | 2019-02-01 | 1600 Hrs
H2 | Deslag Complete | 2019-02-02 | 0400 Hrs
H2 | Pull wet bottom | 2019-02-02 | 0500 Hrs
H2 | Start Purging generator to CO2 than air | 2019-02-02 | 0800 Hrs
H2 | Start draining condensate water system | 2019-02-02 | 0800 Hrs
H2 | Start draining Auxiliary water system | 2019-02-02 | 1200 Hrs
H2 | Start draining circulating water systems | 2019-02-02 | 1600 Hrs
H2 | Purging of Generator Complete | 2019-02-03 | 1800 Hrs
H2 | Turbine off gear shut down lube oil and seal oil systems | 2019-02-03 | 1800 Hrs
H2 | H2 Ready | 2019-02-03 | 2200 Hrs
Area's to be cleaned
H2 | Fan boiler through SCR's 100 degrees gas In
H2 | Shut all fans down, open boiler and SCR doors
H2 | Vacuum Mill balls
H2 | Boiler backpass (explosive cleaning)
H2 | Vacuuming of penthouse
H2 | Vacuuming SCR's top layer
H2 | Pull catalyst seals vacuum between catalyst
H2 | vacuum middle layer of catalyst
H2 | Pull catalyst seals vacuum between catalyst
H2 | vacuum scr slope area and hoppers
H2 | vacuum scr ductwork and diverter dampers
H2 | Scrubbers - start washing at the stack inlet and work down through the absorber module and clean out the reaction tank

## HMPL Demo Cleaning
HMPL UNITS Cleaning
Description | Est. Cost | Ramp Down
Penthouse vacuuming | 25000
Boiler Blasting (Explosive Cleaning) | 30000 | 30000
Backpass and Econ blasting (Explosive cleaning) | 25000
Econ vacuuming | 5000
Dead Air Spaces | 10000
SCR Reactor and Catalyst vacuuming | 12000
SCR slope and ash hoppers | 15000
SCR ductwork and Diverter dampers area | 5000
Air Heater Gas inlets and outlets | 8000
Air heater wash | 15000 | 15000
Precip wash | 10000
Air heater air out ductwork | 5000
Precip outlet duct | 5000
Ductwork from FGD inlet damper to Booster fan | 7000
Booster Fan and outlet duct to absorber | 5000
Top hat duct to stack | 5000
ME panels top and bottom | 9000
ME wash piping | 8000
Recycle tray area | 5000
Recycle headers and nozzles | 8000
Absorber and Suction lines | 9000
Bleed lines | 0
Thickener Return lines Steel and Fiberglass | 0
Wet bottom and wet seal | 5000 | 5000
Mill Balls | 20000
PA Ductwork | 5000
Coal Bunkers | 20000 | 20000
Flyash silo | 15000
Booth system | 5000
Dry Flyash system and piping | 5000
EST.Total ( Both units) | 301000 | 70000

## Asbestos Abatement
HMP&L 1&2 ASBESTOS ABATEMENT PROJECT SUMMARY
FOR THE PURPOSE OF ABATEMENT PIPING IS MEASURED AS LINEAR FEET AND SURFACE MATERIAL IS MEASURED IN SQ. FEET
Location |  | SQ. FEET (APPROX.) | EST. Cost
H1 Unit piping systems insulation |  | 3270 | 567983
H2 Unit piping systems insulation |  | 4997 | 1010301
Pipiing Total |  | 8267 | 1578284
COOLING TOWERS
LOCATION |  | SQ. FEET (APPROX.) | EST.Cost
#1 (SOUTH) COOLING TOWER PANELS |  | 25960 | 169500
#2 (NORTH) COOLING TOWER PANELS |  | 24948 | 164000
Cooling Tower Total |  | 50908 | 333500
Acr Chutes
| 4KV | H2 | Qty
| 52-301 | Main 2A | 3
| 52-302 | CWP C | 3
| 52-303 | PPC 2A | 3
| 52-304 | Bus Tie 2A | 3
| 52-305 | Ash Sluice Pump D | 3
| 52-306 | Scrubber Emerg. Fdr. | 3
| 52-307 | PA Fan 2A | 3
| 52-308 | FD Fan 2A | 3
| 52-309 | Mill 2A | 3
| 52-310 | BFP 2A | 3
| 52-311 | Condensate Pump 2A | 3
| 52-312 | 480V LC -2A | 3
|  | Spare Breakers | 21
57
480V
H1 and H2 LC A&B
|  | 1600A Bkrs | 36
|  | 600A Bkrs | 36
72
Scrubber
| Breaker Total |  | 2000
|  | Asbestos Removal Total | 1913784

## Electrical Powr Disconnect
HMP'L SHUTDOWN ELECTRICAL POWER SYSTEMS DISCONNECTS
COMPLETED
Reid Barge Unloader: Currently fed from H1 4160V switchgear. Need to put alternate feed in service from the intake to barge unloader. Note: No protective relaying trip for the stacker transformer.
Microwave Tower: Normal feed is from H2. Standby fed is from Reid. Potentially could be replaced with option 3 from Substation Building in Switchyard. 2nd option is to install diesel generator at microwave tower building.
Reid Circulator #1 & #3: Needs to stay in service to supply water to HWU water treatment plant. Currently controls are located at Station II control room. Need to move to Reid (See T. Taylor for details).
Silo Sump Pumps: Needed for basement sump and street drains. Currently fed from H1 & H2.
Gas Turbine Alt Feed: Currently fed from H2 load center. Needed to keep oil pumps and battery charger in service if main transformer is out of service. Potentially could be replaced with option 3 from Substation Building in Switchyard. 2nd option is to add a diesel generator backup at gas turbine.
Heavy Equipment Building: Currently fed from H1 MCC. Need to maintain power until relocated.
Basement Sewage Pump: Currently located in H1 basement and fed from H1. Needs to stay in service as Reid building is being used (B. Cheatham working on solution).
Light Fixtures: Universal waste (Mercury). Remove, box, and store properly any fluorescent or metal halide bulbs for a disposal company. Need to keep lighting in service as long as possible for safety concerns.
GE Breakers: GE 4160V magna blast breakers and GE 480V AK breakers contain asbestos in the arc chutes. Need asbestos abatement company to dispose of properly. Some breakers need to stay in service for power and lights.
OCB’s: OCB 0166 and 0186 must be transferred to Big Rivers and stay in service. OCB 0162 and 0182 need to be determined. Control and DC power are currently located at HMPL. Need to relocate to the substation building.
Reid Essential Power: Back Up feed is currently running from H1, need to relocate this feed to an alternate source.
Construction Power: H1 FD pad 200 amp disconnect is currently fed from Reid. This can be disconnected at the Reid FD pad disconnect at any time.
Power Panel: 240V power panel located on H1 near the chop saw is currently only feeding pipe threader. Need to relocate pipe threader if needed.
Reid Aux Transformer: Overcurrent relays are currently located in the old computer room. Relays will have to be relocated if the Reid unit is in service or if we back feed thru the aux transformer.
Gai-Tronics: Must be isolated from the HMP'L units.
GTE Phones: Cables go to HMPL old computer room, wiring needs to be unhooked to keep from shorting out system. Phones in Reid offices can stay on the same system if needed. Need to reroute and/or replace phone system for Reid boiler, barge unloader, gas turbine, and substation building.
Harris Communication Cabinet: ETS needs to decide what’s needed in this cabinet located in the old computer room.
Controls Moved to Reid: 4160V Breakers-52-1 Main, 52-2 Unit 1 480V Transformer, 52-3 Intake Transformer, 52-5 Startup 480V Transformer, 52-6 Coal Handling, 52-7 Startup. 480V Breakers-52-10 Startup 480V Main, 52-8 Unit #1 480V Main, 52-9 Tie Breaker 480V
Crusher House: If the crusher house is removed the Central Machine shop feed will have to be rerouted so that power is still available.
Reid Auxiliary Circulating Water Pump: Need to determine is this pump will be needed after shutdown. If it is still needed the controls will have to be relocated.
Reid Bearing Cooling Water Pumps: Need to determine if this pump will be needed after shutdown. If it is still needed the controls will have to be relocated.
Reid AC Bearing Oil Pumps A&B, DC Bearing Oil pump, Vapor Extractor: Can these be unhooked now or are they staying in service to roll turbine.
Emergency/Weather alarm: Output being moved to PLC, but gai-tronic box that generates alarm will have to be relocated to Reid and tied back to page system.
DC Power Panel Normal and Standby Supply, AC Power Panel normal and Standby Supply: These can be disconnected after all equipment moved from Reid Bench board.
Fuel Oil Transfer Pumps: Currently the fuel oil transfer pumps supplying fuel to Green’s fuel storage tank is fed from H1 and H2.
Option 1-Keep the current fuel unloading station in place. Unloading pumps are already fed from the Gas Turbine. Power and controls to the transfer pumps will have to be rerouted either from Reid, Gas Turbine (If buckets/load capacity are available), old crusher house, or Green coal handling building.
Option 2-Relocate fuel unloading station at Green fuel storage tank. Do modifications need to be made to accommodate this? In this case you would only need to supply power and controls to the unloading pumps from green station.
Substation Building in Switchyard: Currently the substation normal feed is from H1 “A” Load center. Standby feed is from Reid Startup 480V power panel. The standby feed conduit is routed on the H1 side of the I-beams. Is this an issue? The question is where do we end up getting our 2nd source of power.
Option 1- Add diesel generator at substation building.
Option 2-Feed from green cooling tower (If bucket/load capacity are available).
Option 3-Replace existing scrubber transformer or add 69KV/480V transformer with enough load capacity for substation, alt feed to gas turbine, and microwave tower.
Non Essential Equipment that can be unhooked now from Reid bench board
Red is control wiring that has been disconnected from R-1 to Station II Control Room | 2019-01-11
Start-up Vacuum Pump 2 & 3, Condensate transfer pump, Drip pump, fuel oil header valve, fuel oil transfer pump 1 & 2, burner lighter oil pump A & B, ignitor control power, PA fan start permissive ind, FD fan A & B, PA fan A & B, seal air fan A & B, mill A & B, coal feeder A & B, BFP A, B, & C, feed water manual bypass valve, start-up feed water bypass valve, air heater drive, air heater lube oil pump, air heater air drive, EMR valve, scanner blower A & B, emergency lights indication, turning gear indication, turbine stop valve indication, mill emergency roll, governor control, voltage regulator controls

## All Batteries
American Power Systems will be the contractors that will be removing the batteries offsite.
Description | Manufacturer | Cells
H1 Station Battery | GNB NCX-17 | 60
H2 Station Battery | GNB NCX-13 | 60
Scrubber Station Battery | GNB ABSOLYTE | 60
Diesel Fire Pump Battery | CATAPILLER 1000 CCA | 6
| Est. Deposal Cost | 0
Note on C14: Keith L Scott: Contractor to be onsite to give a cost estimate on 1/10/19

## Tank Cleaning
Description | EST. COST
Reid water plant acid tanks. Tank already empty, disconnected from cation & mixed bed tanks, rinse acid piping and bulk tank. Rinse water to be used on site | 10000
Reid water plant caustic tank. Tank already empty, disconnected from anion & mixed bed tanks, rinse caustic piping and bulk tank. Rinse water to be used on site | 10000
Both acid & caustic day tanks at water plant will be drained & rinsed by BREC personnel.
HMPL cooling tower bulk acid. Tank empty already, disconnected from acid metering pumps, rinse piping and bulk tank. Rinse water to be used on site | 10000
Anhydrous ammonia. Paul Akers to remove gaseous material with portable tanks and burn off aqua ammonia. Based on previous work | 20000
Anhydrous ammonia tanks. Summit to vent & rinse tanks/piping. A&B Tanks | 50000
Heavy equipment fuel tank. Tank will need to be pumped down. Sludge removed, tank cleaned & waste disposed by Summit | 15000
Reid Ignition fuel tank. Tank will need to be pumped down. Sludge removed, tank cleaned & waste disposed by Summit | 25000
TOTAL | 140000

## Mercury Filled Equipment
H1 Mercury
2018-12-14
# of switches
4th floor | brg. Water tank | 1
3rd floor | #6 heater | 3
| #5 heater | 3
| da | 3
| cooling water tank | 1
2nd floor | # 3 heater | 3
| #2 heater | 3
1st floor | seal air gauge board | 2
| #1 heater | 2
| gb22-5 turning gear oil | 1
| booster fan oil level | 2
basement | bfp switches | 6
| g.b. 21-1 Circ. Water | 1
| Generator Gas | 1
| Seal Drain | 1
| Gauge board for centac cooling water | 2
| g.b.21-3 Brg. Water Header | 2
| g.b. 21-4 | 3
| condensate drain tank | 2
| bowser | 3
| Burner Deck | 4
| g.b 21-2 Inst. Air | 2
51
H 2 Mercury
2018-12-14
# of switches
4th floor | brg. Water tank | 1
3rd floor | #6 heater | 3
| #5 heater | 3
| da | 3
| cooling water tank | 1
2nd floor | # 3 heater | 3
| #2 heater | 3
1st floor | seal air gauge board | 3
| #1 heater | 2
| gb32-5 turning gear oil | 1
| booster fan oil level | 2
circ. Water pump make up pit in switchyard
basement | bfp switches | 6
| condensate drain tank | 2
| bowser | 3
| hotwell | 2
| g.b. 31-4 | 3
| g.b.31-3 | 2
| seal oil unit | 2
| g.b. 31-1 | 2
burner deck |  | 4
| Total Switches | 51
| EST. Deposal Cost | 6000

## Relocate Potable Water Line
A&S Services to provide labor, Equipment and BREC will provide the Material to hook onto Existing 6" Potable water line by HMPL cooling tower.
| A&S Labor | 16950
| Brec Material | 14016.31
| Total | 30966.31

## Relocate R-1 Controls
The Reid 1 controls relocation project includes all existing equipment that are currently used for miscellaneous operations that needs to be operable after the decommissioning of H1 and H2. The list includes the controls for the #1 and #3 Circulating Water Pumps for the HWU contract, the electrical switching controls for the Start Up transformer and the 4KV switchgear, and the Condenser Inlet and Outlet valve controls that are used for the Water Permit. This project will install a Allen Bradley PLC in the Reid Conference Room with an HMI for control at Reid and in the Green Control Room.
Description of Work | EST. Comp . Date | Completed Date
Clean out old control room and remove cabinet covering the terminations. | 2018-12-21 | 2018-12-21
Run Fiber Optic cable to Reid Communications Room | 2018-12-27 | 2018-12-27
Set new PLC cabinet | 2019-01-02 | 2019-01-02
Run power for PLC cabinet. | 2019-01-04 | 2019-01-03
Run cables - need estimate of length and cable type | 2019-01-04
Reivew I/O list for completion | 2019-01-04 | 2019-01-03
Run new cables | 2019-01-11
ID wiring to be terminated | 2019-01-04
Hang Interposing Relay cabinet | 2019-01-04 | 2019-01-04
Need Interposing relay type and number to order | 2019-01-04
Install new PLC | 2019-01-04
Need panel for relays | 2019-01-04
Cut holes in wall for conduits | 2019-01-18
Run cables | 2019-01-11
Program PLC with I/O | 2019-01-21
Program PLC with logic | 2019-01-21
#1 CWP | 2019-01-21
#3 CWP | 2019-01-22
Condenser Valves | 2019-01-23
Misc. Points | 2019-01-24
Ash Sluice Pump 1 | 2019-01-25 | 2019-01-07
Ash Sluice Pump 2 | 2019-01-26 | 2019-01-07
Electrical Controls | 2019-01-28
Install HMI in Green Control Room | 2019-01-29
Relocate controls one system at a time | 2019-01-30
Cover Terminations Panels | 2019-01-31
Train Operations | 2019-02-01
The cost for the new PLC with all the I O | 37466.85
Relays for transformers | 29000
Total | 66466.85
DI
DO
AI
AO

## Nuclear Sources
The HMP&L Scrubber Nuclear Sources is not in use and can be removed by Jeff Brown In-house.
|  | Supplier: | K-Ray, |  | Removed
Location/Description |  | Designation | Texas Nuclear
| HMP&L Scrubber | H1 | Texas Nuclear | 2500 | 2019-01-04
| HMP&L Slakers | #1 | Texas Nuclear | 2500
|  | #2 | Texas Nuclear | 2500
|  | #3 | Texas Nuclear | 2500
|  |  | EST. Cost | 10000

## Switchyard Breakers Opened
Unit | Description | Disconnect Red Tags | Mechanical Disconnection | Responsible Party
H1 | Generator Side Power | Generator Disconnects | Disconnect Transfromers (3) from plant bus | WARREN | Do not need with unit off line
H2 | Generator Side Power | Generator Disconnects | Disconnect Transfromers (2) from plant bus | WARREN | Do not need with unit off line
H1/H2 | Start Up Power | Switch 416-2 | Disconnect Bus from H1/H2 4KV switchgear | Electricians | Need for lights until all abatement work complete
| Scrubber | Scrubber Transfromer High Side Disconnects | Disconnect Bus at Scrubber 4KV Switchgear | Electricians | Do not need with unit off line
H1 | Coal Handling Feeder |  | Disconnect cables from Switchgear | Electricians | Need to switch to R1 feed for Barge Unloader power
H2 | Scrubber Emergency Feed |  | Disconnect Bus at Scrubber 4KV Switchgear | Electricians | Do not need with unit off line
H1 | Cooling Tower PCC A&B |  | Disconnect Bus at CT Transformers | Electricians | Do not need with unit off line
H2 | Cooling Tower PCC A&B |  | Disconnect Bus at CT Transformers | Electricians | Do not need with unit off line

## Transformers
Serial Number | Description | Location | Manufacturer | Gallons of Oil | MVA | HV | HV Amps | LV | LV Amps | Imp. % |  | PM Made | Interval | WO for testing | Test Date | Instruction Manual
7026674 | CH 4160/480V Transformer | Coal Handling Old Crusher House | Westinghouse | 188 | 0.5 | 4160 | 69.4 | 480/277 | 601.4 | 4.8 | 20 |  | 2016 |  |  |  | Behind Old Crusher House MCC Bldg
PAV-8655-1 | CH 4160V/480V Transformer | Coal Handling New Crusher House | Westinghouse | 188 | 0.5 | 4160 | 69.4 | 480/277 | 601 | 4.7 | 31 |  | 2016 | 6158955 Need Outage code | 3/31/2015 Retest |  | Behind New Crusher House MCC Bldg
31170-A 110471 | CH Barge Unloader 4160V/480V Transformer | Barge Unloader Cell | Olsun | Dry | 0.15 | 4160 | 208 | 480/277 | 1804 | 6.18 | N/A |  | 2016
TVA 8897-01 | CH Machine Shop Transformer | Central Machine Shop |  |  | 0.15 | 4160 |  | 480/277 |  | 6.01
G-854744A | H1 A Load Center Transformer | H1 Ground floor | GE | Dry | 1.333 | 4160 | 185 | 480/277 | 1605 | 8.06 | FA |  | 2018
G-854744c | H1 B Load Center Transformer | H1 Ground floor | GE | Dry | 1.333 | 4160 | 185 | 480/277 | 1605 | 8.04 | FA |  | 2018
G-854744D | H2 A Load Center Transformer | H2 Ground floor | GE | Dry | 1.333 | 4160 | 185 | 480/277 | 1605 | 7.87 | FA |  |  |  | 2013-04-30 | GEK 34814
G-854744B | H2 B Load Center Transformer | H2 Ground floor | GE | Dry | 1.333 | 4160 | 185 | 480/277 | 1605 | 8.12 | FA |  |  |  | 2013-04-30 | GEK 34814
7023817 | HMP&L Intake 4160/480V Transformer | Intake Bldg. West Side | Westinghouse | 265 | 0.3 | 4160 | 41.6 | 480/277 | 360.9 | 4.8 | 29 |  |  |  | 2014-02-14
PBV 8684-2 | PCC 1A 4160V/480V Transformer | South Cooling Tower | Westinghouse | 210 | 0.966 | 4160 | 119.7 | 480 | 1037 | 5.5 | 11 |  | 2016 | 6134875 Need outage code
PBV 8654-2 | PCC 1B 4160V/480V Transformer | South Cooling Tower | Westinghouse | 210 | 0.966 | 4160 | 119.7 | 480 | 1037 | 5.5 | 24 |  | 2016 | 6134876 Need outage code
PBV 8684-1 | PCC 2A 4160V/480V Transformer | North Cooling Tower | Westinghouse | 210 | 0.966 | 4160 | 119.7 | 480 | 1037 | 5.5 | 18 |  |  | Replace | 2015-03-30
PBV 8654-1 | PCC 2B 4160V/480V Transformer | North Cooling Tower | Westinghouse | 210 | 0.966 | 4160 | 119.7 | 480 | 1037 | 5.5 | 9 |  |  | 6158953 Need outage code | 3/30/2015 Retest
F485251-64P | R1 Neutral Grounding Transformer | Reid 1st floor | Eastern |  | 0.96 | 4160/2400 | 40 |  |  | 2.1/ph | [5 empty] | PMR427988
7025345 | R1 Start Up Transformer | Reid 1st floor | Westinghouse |  | 0.7 | 4160 | 138 | 480 | 1203 | 5.4 |  |  | 2016 |  |  | 48-510-C2062
7025344 | R1 Unit Transformer | Reid 1st floor | Westinghouse |  | 0.7 | 4160 | 138 | 480 | 1203 | 5.4 |  |  | 2016 |  |  | 48-510-C2062
P11058-7LUBD5807520001 | Scrubber Dilution Air Transformer | Small Bldg by Scrubber | GE | Dry | 1.5 | 4160 | 208 | 480 | 1804 | 6.07
R276904A | Scrubber Swgr A Transformer | Scrubber Bldg | GE | Dry | 2 | 4160 | 278 | 480 | 2405 | 5.72 |  |  | 2016 | 6134877 Need outage code |  | GEK5697
R276904B | Scrubber Swgr B Transformer | Scrubber Bldg | GE | Dry | 2 | 4160 | 278 | 480 | 2405 | 5.72 |  |  | 2016 | 6134874 Need outage code |  | GEK5697

## Gas Turbine Electric Feed
The Gas Turbine currently has a transformer that provides power to auxiliary equipment when the GT is not running. (i.e. oil pumps, hydrogen seal, etc.) There is also a 480V 600A service feed on H2 that provides Back Up power to the Gas Turbine if power is lost from the switchyard transformer. There are five options for replacing this feed. Option 2 is the recommended option because it provides the needed back up power feed for the gas turbine and the option for additional power feeds near the Gas Turbine in the future. Other power options are located at Reid 1 or Green 1, and quoted costs are substantially higher than this option. A diesel generator option is even higher than routing a power feed from Reid.
Option 1: Set new 4KV/480V transformer beside Scrubber transformer and run cable feed to the existing 480V breaker on the main power transformer. We will still need the scrubber transformer but eliminates the switch gear. Estimate: $25K. (New transformer, 150’ cable)
Pro: Cheaper than running From Reid 1 |  | Cons: No ability to add equipment with this option.
Option 2: (Recommended) Use existing Scrubber Transformer and FGD 4KV Dilution Air Switchgear spare breaker and run cable to existing 480 breaker on the main power transformer. Estimate: $20K. (5000’ cable run, pull 4KV feed to this switchgear from Scrubber switchgear.)
Pro: This option leaves us with spare breaker space for additional equipment and the ability to add breakers in the future. This equipment is housed in its ow building. |  | Con: Requires moving the feed from the Scrubber Transformer from the Scrubber 4KV switchgear, down to the Dilution air switchgear.
| Option 1 |  | EST. Cost | 20000
| Option 2 |  | EST. Cost | 25000

## Schweitzer Relays
In 2012 ET&S and Plant Engineers agreed to begin replacing the existing electromechanical relays with the SEL brand of digital relays. H-1 and H-2 has SEL relays installed on the new Powell switchgear and can be used as part of the Green relay replacement project that is budgeted over the next 4 years There on three models of relays on H1 and H2. The SEL 700G relays can be used on the G1 and G2 generator relay replacement, the SEL 751A feeder relays can be used on the G1 and G2 feeder busses and the SEL 710 motor relays can be used on the 4KV motors. These relays would be used first before additional relays would need to be purchased to complete the project.
There are 6 Generator SEL 700G relays, 10 Feeder SEL 750a relays and 29 Motor SEL 710 relays. The average cost of SEL relays is $2,000.
The total for these relays is estimated. |  | 90000
BREC share |  | 60000
HMPL share |  | 30000
Based on split 115/312
GREEN UNIT ONE RELAYS
Equipment | RELAY TYPE | EXISTING RELAYS
1A
PULVERIZER 1C | SEL-710-5 | 50/49
50G
50/51/83
PULVERIZER 1A | SEL-710-5 | 50/49
50G
50/51/83
ID FAN 1A UPPER | SEL-710-5 | 50/51/83
49/50
87
50G
ID FAN 1A LOWER | SEL-710-5 | 50/51/83
49/50
87
BOILER FEED PUMP 1A | SEL-710-5 | 50/51/83
49/50
87
50G
PRIMARY AIR FAN 1A | SEL-710-5 | 50/51/83
49/50
50G
FORCED DRAFT FAN 1A | SEL-710-5 | 50/51/83
49/50
50G
CONDENSTATE PUMP 1A | SEL-710-5 | 50/51/83
49/50
50G
USS 1A1 | SEL-751A | 50/51
50G
USS 1A2 | SEL-751A | 50/51
50G
USS 1A3 | SEL-751A | 50/51
50G
SOLID WASTE DISPOSAL SYSTEM | SEL-751A | 50/51
50G
CIR WATER PUMP 1A | SEL-710-5 | 50/51/83
49/50
50G
MAIN BREAKER 1A | SEL-751A | 50/51
86G
PT AND CT | SEL-751A | 25
64ATX
27X1
27
27X1
ASH SLUICE PUMP 1A
AIR COMPRESSOR 1A
EXISTING DIGITAL RELAY
1B
PULVERIZER 1B | SEL-710-5 | 50/49
50G
50/51/83
PULVERIZER 1D | SEL-710-5 | 50/49
50G
50/51/83
ID FAN 1B UPPER | SEL-710-5 | 50/51/83
49/50
87
50G
ID FAN 1B LOWER | SEL-710-5 | 50/51/83
49/50
87
BOILER FEED PUMP 1B | SEL-710-5 | 50/51/83
49/50
87
50G
PRIMARY AIR FAN 1B | SEL-710-5 | 50/51/83
49/50
50G
FORCED DRAFT FAN 1B | SEL-710-5 | 50/51/83
49/50
50G
CONDENSATE PUMP 1B | SEL-710-5 | 50/51/83
49/50
50G
USS 1B1 | SEL-751A | 50/51
50G
USS 1B2 | SEL-751A | 50/51
50G
USS 1B3 | SEL-751A | 50/51
50G
ASH SLUICE PUMP 1B | SEL-710-5 | 50/51/83
49/50
50G
CIR WATER PUMP 1B | SEL-710-5 | 50/51/83
49/50
50G
MAIN BREAKER 1B | SEL-751A | 50/51
86G
PT AND CT | SEL-751A | 25
64ATX
27X1
27
27X1
G1 Generator Relay Replacement
Replace 10 existing electromagnetic relays with 3-4 SEL 700G relays.
Loss of Field | SEL-700G | 40
Phase Distance | SEL-700G | 21
Generator Differential | SEL-700G | 87G1
Generator Instantaneous Back Up' | SEL-700G | 50BU
Phase Distance Timer | SEL-700G | 21X
Generator Start Up Residual Overcurrent | SEL-700G | 51NMT
Generator Voltage Balance | SEL-700G | 60G
Generator Ground | SEL-700G | 64G1
Generator Negative Sequence | SEL-700G | 46
Generator Ground Backup | SEL-700G | 64GB
Generator Reverse Power Primary | SEL-700G | 32P
Generator Reverse Power Back Up | SEL-700G | 32BU
GREEN UNIT TWO RELAYS
Equipment | RELAY TYPE | EXISTING RELAYS | Done in 2017
2A
PULVERIZER 2C | SEL-710-5 | 50/49 | +
50G
50/51/83
PULVERIZER 2A | SEL-710-5 | 50/49
50G
50/51/83
ID FAN 2A UPPER | SEL-710-5 | 50/51/83 | +
49/50
87
50G
ID FAN 2A LOWER | SEL-710-5 | 50/51/83 | +
49/50
87
BOILER FEED PUMP 2A | SEL-710-5 | 50/51/83 | +
49/50
87
50G
PRIMARY AIR FAN 2A | SEL-710-5 | 50/51/83 | +
49/50
50G
FORCED DRAFT FAN 2A | SEL-710-5 | 50/51/83 | +
49/50
50G
CONDENSATE PUMP 2A | SEL-710-5 | 50/51/83 | +
49/50
50G
USS 2A1 | SEL-751A | 50/51
50G
USS 2A2 | SEL-751A | 50/51
50G
USS 2A3 | SEL-751A | 50/51
50G
SOLID WASTE DISPOSAL (ALT FDR) | SEL-751A | 50/51
50G
CIR WATER PUMP 2A | SEL-710-5 | 50/51/83 | +
49/50
50G
INCOMING BREAKER 2A | SEL-751A | 50/51
86G
PT AND CT | SEL-751A | 25
64ATX
27X1
27
27X1
2B
PULVERIZER 2B | SEL-710-5 | 50/49
50G
50/51/83
PULVERIZER 2D | SEL-710-5 | 50/49
50G
50/51/83
ID FAN 2B UPPER | SEL-710-5 | 50/51/83
49/50
87
50G
ID FAN 2B LOWER | SEL-710-5 | 50/51/83
49/50
87
BOILER FEED PUMP 2B | SEL-710-5 | 50/51/83
49/50
87
50G
PRIMARY AIR FAN 2B | SEL-710-5 | 50/51/83
49/50
50G
FORCED DRAFT FAN 2B | SEL-710-5 | 50/51/83
49/50
50G
CONDENSATE PUMP 2B | SEL-710-5 | 50/51/83
49/50
50G
USS 2B1 | SEL-751A | 50/51
50G
USS 2B2 | SEL-751A | 50/51
50G
USS 2B3 | SEL-751A | 50/51
50G
ASH SLUICE PUMP 2B C | SEL-710-5 | 50/51/83
49/50
50G
CIR WATER PUMP 2B | SEL-710-5 | 50/51/83
49/50
50G
INCOMING BREAKER 2B | SEL-751A | 50/51
86G
PT AND CT | SEL-751A | 25
64ATX
27X1
27
27X1
G2 Generator Relay Replacement
Replace 10 existing electromagnetic relays with 3-4 SEL 700G relays.
Loss of Field | SEL-700G
Phase Distance | SEL-700G
Generator Differential | SEL-700G
Generator Instantaneous Back Up' | SEL-700G
Phase Distance Timer | SEL-700G
Generator Start Up Residual Overcurrent | SEL-700G
Generator Voltage Balance | SEL-700G
Generator Ground | SEL-700G
Generator Negative Sequence | SEL-700G
Generator Ground Backup | SEL-700G
Generator Reverse Power Primary | SEL-700G
Generator Reverse Power Back Up | SEL-700G