## Battery Inputs
Battery Input Model
Capacity Element | Capacity Rating of Element (MVA) | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016-2017 load forecast
Ramey Sta. (Howard Collins OL) | 12.89 | 12.32 | 12.42 | 12.52 | 12.62 | 12.72 | 12.82 | 12.92 | 13.02 | 13.12 | 13.22 | 13.32
Capacity Deficit (MVA) |  | -0.57 | -0.47 | -0.37 | -0.27 | -0.17 | -0.07 | 0.03 | 0.13 | 0.23 | 0.33 | 0.43
Peak Hrs of Violation (peak day) |  | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 4 | 4 | 4
MWhr Battery Requirement |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.52 | 0.92 | 1.32 | 1.72
MW Battery Requirement |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.13 | 0.23 | 0.33 | 0.43
Battery Size (MW) | bar: 2016-2017 load forecast 12.89
Battery Size (Hrs at Rated MW) | 2016-2017 load forecast 12.89: 4
MWhr Requirement | 2016-2017 load forecast 12.89: 4
Cost of Battery (000s) | 2016-2017 load forecast 12.89: 2800
Balance of System Cost (000s) | 2016-2017 load forecast 12.89: 1150
Installed Cost of Battery (000s) | 2016-2017 load forecast 12.89: 3950
Comments: | 2016-2017 load forecast 12.89: Space constrained at this location.
Selection Table for Battery Cost | 2016-2017 load forecast 12.89: $ per MWhr
MW/Hr | 2016-2017 load forecast 12.89: 1; 2016-2017 load forecast 12.32: 2; 2016-2017 load forecast 12.42: 3; 2016-2017 load forecast 12.52: 4; 2016-2017 load forecast 12.62: 5; 2016-2017 load forecast 12.72: 6
1 | 2016-2017 load forecast 12.89: 700000; 2016-2017 load forecast 12.32: 1200000; 2016-2017 load forecast 12.42: 1800000; 2016-2017 load forecast 12.52: 2400000; 2016-2017 load forecast 12.62: 3000000; 2016-2017 load forecast 12.72: 3600000
2 | 2016-2017 load forecast 12.89: 1400000; 2016-2017 load forecast 12.32: 2400000; 2016-2017 load forecast 12.42: 3600000; 2016-2017 load forecast 12.52: 4800000; 2016-2017 load forecast 12.62: 6000000; 2016-2017 load forecast 12.72: 7200000
3 | 2016-2017 load forecast 12.89: 2100000; 2016-2017 load forecast 12.32: 3600000; 2016-2017 load forecast 12.42: 5400000; 2016-2017 load forecast 12.52: 7200000; 2016-2017 load forecast 12.62: 9000000; 2016-2017 load forecast 12.72: 10800000
4 | 2016-2017 load forecast 12.89: 2800000; 2016-2017 load forecast 12.32: 4800000; 2016-2017 load forecast 12.42: 7200000; 2016-2017 load forecast 12.52: 9600000; 2016-2017 load forecast 12.62: 12000000; 2016-2017 load forecast 12.72: 14400000
5 | 2016-2017 load forecast 12.89: 3500000; 2016-2017 load forecast 12.32: 6000000; 2016-2017 load forecast 12.42: 9000000; 2016-2017 load forecast 12.52: 12000000; 2016-2017 load forecast 12.62: 15000000; 2016-2017 load forecast 12.72: 18000000
6 | 2016-2017 load forecast 12.89: 4200000; 2016-2017 load forecast 12.32: 7200000; 2016-2017 load forecast 12.42: 18800000; 2016-2017 load forecast 12.52: 14400000; 2016-2017 load forecast 12.62: 18000000; 2016-2017 load forecast 12.72: 21600000
7 | 2016-2017 load forecast 12.89: 4900000; 2016-2017 load forecast 12.32: 8400000; 2016-2017 load forecast 12.42: 12600000; 2016-2017 load forecast 12.52: 16800000; 2016-2017 load forecast 12.62: 21000000; 2016-2017 load forecast 12.72: 25200000
8 | 2016-2017 load forecast 12.89: 5600000; 2016-2017 load forecast 12.32: 9600000; 2016-2017 load forecast 12.42: 14400000; 2016-2017 load forecast 12.52: 19200000; 2016-2017 load forecast 12.62: 24000000; 2016-2017 load forecast 12.72: 28800000
9 | 2016-2017 load forecast 12.89: 6300000; 2016-2017 load forecast 12.32: 10800000; 2016-2017 load forecast 12.42: 16200000; 2016-2017 load forecast 12.52: 21600000; 2016-2017 load forecast 12.62: 27000000; 2016-2017 load forecast 12.72: 32400000
10 | 2016-2017 load forecast 12.89: 7000000; 2016-2017 load forecast 12.32: 12000000; 2016-2017 load forecast 12.42: 18000000; 2016-2017 load forecast 12.52: 24000000; 2016-2017 load forecast 12.62: 30000000; 2016-2017 load forecast 12.72: 36000000
Note on C2: AEP: Current year associated with recorded peak
Note on B3: AEP: DLF forecast being utilized
Note on A4: AEP: name of capacity element being studied
Note on C4: AEP: MVA peak by year per DLF load forecast

## Battery Financial Model
Battery Financial Model
Carrying cost rate (%) | 17%
Inflation rate (%) | 2%
Discount rate (%) | 7%
Ramey Sta. (Howard Collins OL) |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
Traditional Solution
Installed Cost (000s) | 4824 | 2024: 5432.6075
Carrying Cost (000s) |  | 0 | 0 | 0 | 0 | 0 | 0 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433
Deferral Period (yrs) | 6
Traditional Solution
Carrying Cost (000s) no deferral |  | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08
Alternative Cap Solution
Installed Cost (000s) | 3950
Carrying Cost (000s) |  | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5 | 671.5
20-Yr NPV Capital Cost Traditional Solution (including deferral) | = | 2018: 5604.9728
20-Yr NPV Traditional Solution Capital Cost (no deferral) | = | 2018: 8885.9993
20-Yr NPV Alternative Capacity Solution | = | 2018: 7276.0566
Net Savings / (Loss) | = | 2018: -3995.0301
Comments: | Not financially viable.
Note on C7: AEP: Year of overload (in red in DLF)

## Solar Inputs
Solar Input Model
Capacity Element | Capacity Rating of Element (MVA) | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016-2017 load forecast
Ramey Sta. (Howard Collins OL) | 12.89 | 12.32 | 12.42 | 12.52 | 12.62 | 12.72 | 12.82 | 12.92 | 13.02 | 13.12 | 13.22 | 13.32
Capacity Deficit (MVA) |  | -0.57 | -0.47 | -0.37 | -0.27 | -0.17 | -0.07 | 0.03 | 0.13 | 0.23 | 0.33 | 0.43
Peak Hour |  | 17:00 | 17:00 | 17:00 | 17:00 | 17:00 | 17:00 | 17:00 | 17:00 | 17:00 | 17:00 | 17:00
Coincident Factor (%) |  | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40% | 40%
MW Solar Requirement |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.075 | 0.325 | 0.575 | 0.825 | 1.075
Solar Capacity (MW) | bar: 2016-2017 load forecast 12.89
No. of Years of Capacity Deferred | 2016-2017 load forecast 12.89: 6
Cost of Solar (000s) | 2016-2017 load forecast 12.89: 2300
Balance of System Cost (000s) | 2016-2017 load forecast 12.89: 1150
Installed Cost of Solar (000s) | 2016-2017 load forecast 12.89: 3450
Comments: | 2016-2017 load forecast 12.89: Added additional costs for land.
Summer Solar Coincident Factors | 2016-2017 load forecast 12.52: PV Capacity Tier; 2016-2017 load forecast 12.72: 5 - 20 kW; 2016-2017 load forecast 12.92: 100 - 400 kW; 2016-2017 load forecast 13.12: 2,000 - 12,000 kW
Peak Hour | 2016-2017 load forecast 12.89: Coincident Factor (%); 2016-2017 load forecast 12.52: Install Cost per KW; 2016-2017 load forecast 12.72: 4500; 2016-2017 load forecast 12.92: 3500; 2016-2017 load forecast 13.12: 2300
0:00 | bar: 2016-2017 load forecast 12.89
1:00 | bar: 2016-2017 load forecast 12.89
2:00 | bar: 2016-2017 load forecast 12.89
3:00 | bar: 2016-2017 load forecast 12.89
4:00 | bar: 2016-2017 load forecast 12.89
5:00 | bar: 2016-2017 load forecast 12.89
6:00 | bar: 2016-2017 load forecast 12.89
7:00 | bar: 2016-2017 load forecast 12.89
8:00 | 2016-2017 load forecast 12.89: 10%
9:00 | 2016-2017 load forecast 12.89: 30%
10:00 | 2016-2017 load forecast 12.89: 60%
11:00 | 2016-2017 load forecast 12.89: 70%
12:00 | 2016-2017 load forecast 12.89: 70%
13:00 | 2016-2017 load forecast 12.89: 70%
14:00 | 2016-2017 load forecast 12.89: 80%
15:00 | 2016-2017 load forecast 12.89: 60%
16:00 | 2016-2017 load forecast 12.89: 50%
17:00 | 2016-2017 load forecast 12.89: 40%
18:00 | 2016-2017 load forecast 12.89: 20%
19:00 | 2016-2017 load forecast 12.89: 10%
20:00 | bar: 2016-2017 load forecast 12.89
21:00 | bar: 2016-2017 load forecast 12.89
22:00 | bar: 2016-2017 load forecast 12.89
23:00 | bar: 2016-2017 load forecast 12.89
Note on C2: AEP: Current year associated with recorded peak

## Solar Financial Model
Solar Financial Model
Carrying cost rate (%) | 17%
Inflation rate (%) | 2%
Discount rate (%) | 7%
Ramey Sta. (Howard Collins OL) |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
Traditional Solution
Installed Cost (000s) | 4824 | 2024: 5432.6075
Carrying Cost (000s) |  | 0 | 0 | 0 | 0 | 0 | 0 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433 | 923.5433
Deferral Period (yrs) | 6
Traditional Solution
Carrying Cost (000s) no deferral |  | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08 | 820.08
Alternative Cap Solution
Installed Cost (000s) | 3450
Carrying Cost (000s) |  | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5 | 586.5
20-Yr NPV Capital Cost Traditional Solution (including deferral) | = | 2018: 5604.9728
20-Yr NPV Traditional Solution Capital Cost (no deferral) | = | 2018: 8885.9993
20-Yr NPV Alternative Capacity Solution | = | 2018: 6355.0368
Net Savings / (Loss) | = | 2018: -3074.0103
Comments: | Solar financial model based on size sufficient to achieve peak which extends beyond 17:00.
Note on C7: AEP: Year of overload (in red in DLF)

## Sheet1
No data - values estimated.