## Battery Inputs
Battery Input Model
Capacity Element | Capacity Rating of Element (MVA) | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016-2017 load forecast
Marion Branch (Fords Branch OL) | 42.07 | 29.99 | 42.14 | 42.29 | 42.44 | 42.59 | 42.74 | 42.89 | 43.04 | 43.19 | 43.34 | 43.49
Capacity Deficit (MVA) |  | -12.08 | 0.07 | 0.22 | 0.37 | 0.52 | 0.67 | 0.82 | 0.97 | 1.12 | 1.27 | 1.42
Peak Hrs of Violation (peak day) |  | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
MWhr Battery Requirement |  | 0 | 0.35 | 1.1 | 1.85 | 2.6 | 3.35 | 4.1 | 4.85 | 5.6 | 6.35 | 7.1
MW Battery Requirement |  | 0 | 0.07 | 0.22 | 0.37 | 0.52 | 0.67 | 0.82 | 0.97 | 1.12 | 1.27 | 1.42
Battery Size (MW) | 2
Battery Size (Hrs at Rated MW) | 5
MWhr Requirement | 10
Cost of Battery (000s) | 6000
Balance of System Cost (000s) | 1450
Installed Cost of Battery (000s) | 7450
Comments: | Space constrained at this location.
Selection Table for Battery Cost | $ per MWhr
MW/Hr | 1 | 2016: 2; 2017: 3; 2018: 4; 2019: 5; 2020: 6
1 | 700000 | 2016: 1200000; 2017: 1800000; 2018: 2400000; 2019: 3000000; 2020: 3600000
2 | 1400000 | 2016: 2400000; 2017: 3600000; 2018: 4800000; 2019: 6000000; 2020: 7200000
3 | 2100000 | 2016: 3600000; 2017: 5400000; 2018: 7200000; 2019: 9000000; 2020: 10800000
4 | 2800000 | 2016: 4800000; 2017: 7200000; 2018: 9600000; 2019: 12000000; 2020: 14400000
5 | 3500000 | 2016: 6000000; 2017: 9000000; 2018: 12000000; 2019: 15000000; 2020: 18000000
6 | 4200000 | 2016: 7200000; 2017: 18800000; 2018: 14400000; 2019: 18000000; 2020: 21600000
7 | 4900000 | 2016: 8400000; 2017: 12600000; 2018: 16800000; 2019: 21000000; 2020: 25200000
8 | 5600000 | 2016: 9600000; 2017: 14400000; 2018: 19200000; 2019: 24000000; 2020: 28800000
9 | 6300000 | 2016: 10800000; 2017: 16200000; 2018: 21600000; 2019: 27000000; 2020: 32400000
10 | 7000000 | 2016: 12000000; 2017: 18000000; 2018: 24000000; 2019: 30000000; 2020: 36000000
Note on C2: AEP: Current year associated with recorded peak
Note on B3: AEP: DLF forecast being utilized
Note on A4: AEP: name of capacity element being studied
Note on C4: AEP: MVA peak by year per DLF load forecast

## Battery Financial Model
Battery Financial Model
Carrying cost rate (%) | 17%
Inflation rate (%) | 2%
Discount rate (%) | 7%
Marion Branch (Fords Branch OL) |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
Traditional Solution
Installed Cost (000s) | 7025 | 2027: 8395.5253
Carrying Cost (000s) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393
Deferral Period (yrs) | 9
Traditional Solution
Carrying Cost (000s) no deferral |  | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25
Alternative Cap Solution
Installed Cost (000s) | 7450
Carrying Cost (000s) |  | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5 | 1266.5
20-Yr NPV Capital Cost Traditional Solution (including deferral) | = | 2018: 6166.0949
20-Yr NPV Traditional Solution Capital Cost (no deferral) | = | 2018: 12940.3285
20-Yr NPV Alternative Capacity Solution | = | 2018: 13723.1954
Net Savings / (Loss) | = | 2018: -6948.9618
Comments: | Not financially viable.
Note on C7: AEP: Year of overload (in red in DLF)

## Solar Inputs
Solar Input Model
Capacity Element | Capacity Rating of Element (MVA) | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016-2017 load forecast
Marion Branch (Fords Branch OL) | 42.07 | 29.99 | 42.14 | 42.29 | 42.44 | 42.59 | 42.74 | 42.89 | 43.04 | 43.19 | 43.34 | 43.49
Capacity Deficit (MVA) |  | -12.08 | 0.07 | 0.22 | 0.37 | 0.52 | 0.67 | 0.82 | 0.97 | 1.12 | 1.27 | 1.42
Peak Hour |  | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00
Coincident Factor (%) | bar: 2016 to 2026
MW Solar Requirement |  | 0 | 1.4 | 4.4 | 7.4 | 10.4 | 13.4 | 16.4 | 19.4 | 22.4 | 25.4 | 28.4
Solar Capacity (MW) | 28.4
No. of Years of Capacity Deferred | 9
Cost of Solar (000s) | 65300
Balance of System Cost (000s) | 500
Installed Cost of Solar (000s) | 65800
Comments: | Need at 7 AM - solution not viable. Did not factor land costs.
Summer Solar Coincident Factors |  | 2018: PV Capacity Tier; 2020: 5 - 20 kW; 2022: 100 - 400 kW; 2024: 2,000 - 12,000 kW
Peak Hour | Coincident Factor (%) | 2018: Install Cost per KW; 2020: 4500; 2022: 3500; 2024: 2300
0:00 | 0%
1:00 | 0%
2:00 | 0%
3:00 | 0%
4:00 | 0%
5:00 | 0%
6:00 | 0%
7:00 | 5%
8:00 | 10%
9:00 | 30%
10:00 | 60%
11:00 | 70%
12:00 | 70%
13:00 | 70%
14:00 | 80%
15:00 | 60%
16:00 | 50%
17:00 | 40%
18:00 | 20%
19:00 | 10%
20:00 | 0%
21:00 | 0%
22:00 | 0%
23:00 | 0%
Note on C2: AEP: Current year associated with recorded peak

## Solar Financial Model
Solar Financial Model
Carrying cost rate (%) | 17%
Inflation rate (%) | 2%
Discount rate (%) | 7%
Marion Branch (Fords Branch OL) |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
Traditional Solution
Installed Cost (000s) | 7025 | 2027: 8395.5253
Carrying Cost (000s) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393 | 1427.2393
Deferral Period (yrs) | 9
Traditional Solution
Carrying Cost (000s) no deferral |  | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25 | 1194.25
Alternative Cap Solution
Installed Cost (000s) | 65800
Carrying Cost (000s) |  | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186 | 11186
20-Yr NPV Capital Cost Traditional Solution (including deferral) | = | 2018: 6166.0949
20-Yr NPV Traditional Solution Capital Cost (no deferral) | = | 2018: 12940.3285
20-Yr NPV Alternative Capacity Solution | = | 2018: 121206.2087
Net Savings / (Loss) | = | 2018: -114431.9752
Comments: | Solar financial model based on size sufficient to achieve 10 year deferral of capacity
Note on C7: AEP: Year of overload (in red in DLF)

## Sheet1
Crossings at 5 and 10 AM - 7 AM peak and 5 hours of need for winter.