## Battery Inputs
Battery Input Model
Capacity Element | Capacity Rating of Element (MVA) | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016-2017 load forecast
Grays Branch | 10 | 9.89 | 9.99 | 10.09 | 10.19 | 10.29 | 10.39 | 10.49 | 10.59 | 10.69 | 10.79 | 10.89
Capacity Deficit (MVA) |  | -0.11 | -0.01 | 0.09 | 0.19 | 0.29 | 0.39 | 0.49 | 0.59 | 0.69 | 0.79 | 0.89
Peak Hrs of Violation (peak day) |  | 0 | 0 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
MWhr Battery Requirement |  | 0 | 0 | 0.54 | 1.14 | 1.74 | 2.34 | 2.94 | 3.54 | 4.14 | 4.74 | 5.34
MW Battery Requirement |  | 0 | 0 | 0.09 | 0.19 | 0.29 | 0.39 | 0.49 | 0.59 | 0.69 | 0.79 | 0.89
Battery Size (MW) | 1
Battery Size (Hrs at Rated MW) | 6
MWhr Requirement | 6
Cost of Battery (000s) | 4200
Balance of System Cost (000s) | 1150
Installed Cost of Battery (000s) | 5350
Comments: | No SCADA at this location
Selection Table for Battery Cost | $ per MWhr
MW/Hr | 1 | 0: 2; 0: 3; 0.09: 4; 0.19: 5; 0.29: 6
1 | 700000 | 0: 1200000; 0: 1800000; 0.09: 2400000; 0.19: 3000000; 0.29: 3600000
2 | 1400000 | 0: 2400000; 0: 3600000; 0.09: 4800000; 0.19: 6000000; 0.29: 7200000
3 | 2100000 | 0: 3600000; 0: 5400000; 0.09: 7200000; 0.19: 9000000; 0.29: 10800000
4 | 2800000 | 0: 4800000; 0: 7200000; 0.09: 9600000; 0.19: 12000000; 0.29: 14400000
5 | 3500000 | 0: 6000000; 0: 9000000; 0.09: 12000000; 0.19: 15000000; 0.29: 18000000
6 | 4200000 | 0: 7200000; 0: 18800000; 0.09: 14400000; 0.19: 18000000; 0.29: 21600000
7 | 4900000 | 0: 8400000; 0: 12600000; 0.09: 16800000; 0.19: 21000000; 0.29: 25200000
8 | 5600000 | 0: 9600000; 0: 14400000; 0.09: 19200000; 0.19: 24000000; 0.29: 28800000
9 | 6300000 | 0: 10800000; 0: 16200000; 0.09: 21600000; 0.19: 27000000; 0.29: 32400000
10 | 7000000 | 0: 12000000; 0: 18000000; 0.09: 24000000; 0.19: 30000000; 0.29: 36000000
Note on C2: AEP: Current year associated with recorded peak
Note on B3: AEP: DLF forecast being utilized
Note on A4: AEP: name of capacity element being studied
Note on C4: AEP: MVA peak by year per DLF load forecast

## Battery Financial Model
Battery Financial Model
Carrying cost rate (%) | 17%
Inflation rate (%) | 2%
Discount rate (%) | 7%
Grays Branch |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
Traditional Solution
Installed Cost (000s) | 3975 | 2028: 4845.5028
Carrying Cost (000s) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355
Deferral Period (yrs) | 10
Traditional Solution
Carrying Cost (000s) no deferral |  | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75
Alternative Cap Solution
Installed Cost (000s) | 5350
Carrying Cost (000s) |  | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5 | 909.5
20-Yr NPV Capital Cost Traditional Solution (including deferral) | = | 2018: 3140.035
20-Yr NPV Traditional Solution Capital Cost (no deferral) | = | 2018: 7322.1076
20-Yr NPV Alternative Capacity Solution | = | 2018: 9854.9121
Net Savings / (Loss) | = | 2018: -5672.8395
Comments: | Not financially viable.
Note on C7: AEP: Year of overload (in red in DLF)

## Solar Inputs
Solar Input Model
Capacity Element | Capacity Rating of Element (MVA) | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2016-2017 load forecast
Grays Branch | 10 | 9.89 | 9.99 | 10.09 | 10.19 | 10.29 | 10.39 | 10.49 | 10.59 | 10.69 | 10.79 | 10.89
Capacity Deficit (MVA) |  | -0.11 | -0.01 | 0.09 | 0.19 | 0.29 | 0.39 | 0.49 | 0.59 | 0.69 | 0.79 | 0.89
Peak Hour |  | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00
Coincident Factor (%) | bar: 2016-2017 load forecast 9.89 -0.11 to 2016-2017 load forecast 10.89 0.89
MW Solar Requirement |  | 0 | 0 | 1.8 | 3.8 | 5.8 | 7.8 | 9.8 | 11.8 | 13.8 | 15.8 | 17.8
Solar Capacity (MW) | 18
No. of Years of Capacity Deferred | 9
Cost of Solar (000s) | 41400
Balance of System Cost (000s) | 1500
Installed Cost of Solar (000s) | 42900
Comments: | Need at 7 AM - solution not viable. Winter peak time assumed.
Summer Solar Coincident Factors |  | 2016-2017 load forecast 10.09 0.09: PV Capacity Tier; 2016-2017 load forecast 10.29 0.29: 5 - 20 kW; 2016-2017 load forecast 10.49 0.49: 100 - 400 kW; 2016-2017 load forecast 10.69 0.69: 2,000 - 12,000 kW
Peak Hour | Coincident Factor (%) | 2016-2017 load forecast 10.09 0.09: Install Cost per KW; 2016-2017 load forecast 10.29 0.29: 4500; 2016-2017 load forecast 10.49 0.49: 3500; 2016-2017 load forecast 10.69 0.69: 2300
0:00 | 0%
1:00 | 0%
2:00 | 0%
3:00 | 0%
4:00 | 0%
5:00 | 0%
6:00 | 0%
7:00 | 5%
8:00 | 10%
9:00 | 30%
10:00 | 60%
11:00 | 70%
12:00 | 70%
13:00 | 70%
14:00 | 80%
15:00 | 60%
16:00 | 50%
17:00 | 40%
18:00 | 20%
19:00 | 10%
20:00 | 0%
21:00 | 0%
22:00 | 0%
23:00 | 0%
Note on C2: AEP: Current year associated with recorded peak

## Solar Financial Model
Solar Financial Model
Carrying cost rate (%) | 17%
Inflation rate (%) | 2%
Discount rate (%) | 7%
Grays Branch |  | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038
Traditional Solution
Installed Cost (000s) | 3975 | 2028: 4845.5028
Carrying Cost (000s) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355 | 823.7355
Deferral Period (yrs) | 10
Traditional Solution
Carrying Cost (000s) no deferral |  | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75 | 675.75
Alternative Cap Solution
Installed Cost (000s) | 42900
Carrying Cost (000s) |  | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293 | 7293
20-Yr NPV Capital Cost Traditional Solution (including deferral) | = | 2018: 3140.035
20-Yr NPV Traditional Solution Capital Cost (no deferral) | = | 2018: 7322.1076
20-Yr NPV Alternative Capacity Solution | = | 2018: 79023.5008
Net Savings / (Loss) | = | 2018: -74841.4282
Comments: | Solar financial model based on size sufficient to achieve 10 year deferral of capacity
Note on C7: AEP: Year of overload (in red in DLF)

## Sheet1
No data assumed 7 AM peak and 6 hours of need for winter.