## Battery Inputs
Battery Input Model
Capacity Element | Capacity Rating of Element (MVA) | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2015-2016 load forecast
Daisy Station | 8.62 | 7.64 | 8.49 | 8.54 | 8.64 | 8.69 | 8.74 | 8.79 | 8.84 | 8.89 | 8.94 | 8.99
Capacity Deficit (MVA) |  | -0.98 | -0.13 | -0.08 | 0.02 | 0.07 | 0.12 | 0.17 | 0.22 | 0.27 | 0.32 | 0.37
Peak Hrs of Violation (peak day) |  | 0 | 0 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
MWhr Battery Requirement |  | 0 | 0 | 0 | 0.16 | 0.56 | 0.96 | 1.36 | 1.76 | 2.16 | 2.56 | 2.96
MW Battery Requirement |  | 0 | 0 | 0 | 0.02 | 0.07 | 0.12 | 0.17 | 0.22 | 0.27 | 0.32 | 0.37
Battery Size (MW) | 1
Battery Size (Hrs at Rated MW) | 8
MWhr Requirement | 8
Cost of Battery (000s) | 5600
Balance of System Cost (000s) | 850
Installed Cost of Battery (000s) | 6450
Comments: | Property may be difficult to acquire here.
Selection Table for Battery Cost | $ per MWhr
MW/Hr | 1 | 0: 2; 0: 3; 0: 4; 0.02: 5; 0.07: 6
1 | 700000 | 0: 1200000; 0: 1800000; 0: 2400000; 0.02: 3000000; 0.07: 3600000
2 | 1400000 | 0: 2400000; 0: 3600000; 0: 4800000; 0.02: 6000000; 0.07: 7200000
3 | 2100000 | 0: 3600000; 0: 5400000; 0: 7200000; 0.02: 9000000; 0.07: 10800000
4 | 2800000 | 0: 4800000; 0: 7200000; 0: 9600000; 0.02: 12000000; 0.07: 14400000
5 | 3500000 | 0: 6000000; 0: 9000000; 0: 12000000; 0.02: 15000000; 0.07: 18000000
6 | 4200000 | 0: 7200000; 0: 18800000; 0: 14400000; 0.02: 18000000; 0.07: 21600000
7 | 4900000 | 0: 8400000; 0: 12600000; 0: 16800000; 0.02: 21000000; 0.07: 25200000
8 | 5600000 | 0: 9600000; 0: 14400000; 0: 19200000; 0.02: 24000000; 0.07: 28800000
9 | 6300000 | 0: 10800000; 0: 16200000; 0: 21600000; 0.02: 27000000; 0.07: 32400000
10 | 7000000 | 0: 12000000; 0: 18000000; 0: 24000000; 0.02: 30000000; 0.07: 36000000
Note on C2: AEP: Current year associated with recorded peak
Note on B3: AEP: DLF forecast being utilized
Note on A4: AEP: name of capacity element being studied
Note on C4: AEP: MVA peak by year per DLF load forecast

## Battery Financial Model
Battery Financial Model
Carrying cost rate (%) | 17%
Inflation rate (%) | 2%
Discount rate (%) | 7%
Daisy 1X replace |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
Traditional Solution
Installed Cost (000s) | 5050 | 2027: 5916.8799
Carrying Cost (000s) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696
Deferral Period (yrs) | 8
Traditional Solution
Carrying Cost (000s) no deferral |  | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5
Alternative Cap Solution
Installed Cost (000s) | 6450
Carrying Cost (000s) |  | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5 | 1096.5
20-Yr NPV Capital Cost Traditional Solution (including deferral) | = | 2019: 4892.7798
20-Yr NPV Traditional Solution Capital Cost (no deferral) | = | 2019: 9302.3002
20-Yr NPV Alternative Capacity Solution | = | 2019: 11881.1557
Net Savings / (Loss) | = | 2019: -7471.6353
Comments: | Not financially viable.
Note on C7: AEP: Year of overload (in red in DLF)

## Solar Inputs
Solar Input Model
Capacity Element | Capacity Rating of Element (MVA) | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2015-2016 load forecast
Daisy Station | 8.62 | 7.64 | 8.49 | 8.54 | 8.64 | 8.69 | 8.74 | 8.79 | 8.84 | 8.89 | 8.94 | 8.99
Capacity Deficit (MVA) |  | -0.98 | -0.13 | -0.08 | 0.02 | 0.07 | 0.12 | 0.17 | 0.22 | 0.27 | 0.32 | 0.37
Peak Hour |  | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00 | 7:00
Coincident Factor (%) | bar: 2015-2016 load forecast 7.64 -0.98 to 2015-2016 load forecast 8.99 0.37
MW Solar Requirement |  | 0 | 0 | 0 | 0.4 | 1.4 | 2.4 | 3.4 | 4.4 | 5.4 | 6.4 | 7.4
Solar Capacity (MW) | 8
No. of Years of Capacity Deferred | 8
Cost of Solar (000s) | 18400
Balance of System Cost (000s) | 500
Installed Cost of Solar (000s) | 18900
Comments: | Need prior to 7 AM - solution not viable, did not add land costs.
Summer Solar Coincident Factors |  | 2015-2016 load forecast 8.54 -0.08: PV Capacity Tier; 2015-2016 load forecast 8.69 0.07: 5 - 20 kW; 2015-2016 load forecast 8.79 0.17: 100 - 400 kW; 2015-2016 load forecast 8.89 0.27: 2,000 - 12,000 kW
Peak Hour | Coincident Factor (%) | 2015-2016 load forecast 8.54 -0.08: Install Cost per KW; 2015-2016 load forecast 8.69 0.07: 4500; 2015-2016 load forecast 8.79 0.17: 3500; 2015-2016 load forecast 8.89 0.27: 2300
0:00 | 0%
1:00 | 0%
2:00 | 0%
3:00 | 0%
4:00 | 0%
5:00 | 0%
6:00 | 0%
7:00 | 5%
8:00 | 10%
9:00 | 30%
10:00 | 60%
11:00 | 70%
12:00 | 70%
13:00 | 70%
14:00 | 80%
15:00 | 60%
16:00 | 50%
17:00 | 40%
18:00 | 20%
19:00 | 10%
20:00 | 0%
21:00 | 0%
22:00 | 0%
23:00 | 0%
Note on C2: AEP: Current year associated with recorded peak

## Solar Financial Model
Solar Financial Model
Carrying cost rate (%) | 17%
Inflation rate (%) | 2%
Discount rate (%) | 7%
Daisy 1X replace |  | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
Traditional Solution
Installed Cost (000s) | 5050 | 2027: 5916.8799
Carrying Cost (000s) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696 | 1005.8696
Deferral Period (yrs) | 8
Traditional Solution
Carrying Cost (000s) no deferral |  | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5 | 858.5
Alternative Cap Solution
Installed Cost (000s) | 18900
Carrying Cost (000s) |  | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213 | 3213
20-Yr NPV Capital Cost Traditional Solution (including deferral) | = | 2019: 4892.7798
20-Yr NPV Traditional Solution Capital Cost (no deferral) | = | 2019: 9302.3002
20-Yr NPV Alternative Capacity Solution | = | 2019: 34814.5493
Net Savings / (Loss) | = | 2019: -30405.0289
Comments: | Solar financial model based on size sufficient to achieve 10 year deferral of capacity
Note on C7: AEP: Year of overload (in red in DLF)

## Sheet1
Crossings at 2 AM and 10:15 AM