## Case3
DRAFT - PRELIMINARY
2019 KP IRP
2019H1 Low Band Commodity Pricing
KP Optimization Expansion Plan (Supply-side, Renewables, VVO, DR, EE)
| Planning Peak Load (MW) | Required Generation Capacity (MW) | Firm Generation Capacity without New Additions (MW) | 15 MW CHP Capacity (MW) | 216 MW RICE Firm Capacity (MW) | 256 MW (50% Share of 497 MW) GE 7F.05 Firm Capacity (MW) | 325 MW (25% Share of 1,603 MW) M 501 JAC Firm Capacity (MW) | 125 MW LM 6000 CT Firm Capacity (MW) | Big Sandy Site 216 MW RICE Firm Capacity (MW) | Big Sandy Site 256 MW (50% Share of 497 MW) GE 7F.05 Firm Capacity (MW) | Big Sandy Site 325 MW (25% Share of 1,603 MW) M 501 JAC Firm Capacity (MW) | Big Sandy Site Repower 443 MW Firm Capacity | Commercial DR Firm Capacity (MW) | Residential DR Firm Capacity (MW) | Commercial DSM Firm Capacity (MW) | Residential DSM Firm Capacity (MW) | Distributed Solar Firm Capacity (MW) | Utility Solar Firm Capacity (MW) | CVR Firm Capacity (MW) | Wind Firm Capacity (MW) | Short Term PPA Capacity (MW) | Firm Generation Capacity with New Additions (MW) | Capacity Reserves Above Required Generation without New Additions (MW) | Reserve Margin without New Capacity Additions (%) | Capacity Reserves Above Required Generation with New Capacity Additions (MW) | Reserve Margin with New Capacity Additions (%) | Nameplate Solar | Nameplate Wind
2020 | 978.4483 | 1065.5302 | 1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1302 | 236.4698 | 33.0678 | 236.4698 | 33.0678 | 0 | 0 | 2020 | 0
2021 | 982.7561 | 1069.6317 | 1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1302 | 232.3683 | 32.4846 | 232.3683 | 32.4846 | 0 | 0 | 2021 | 0
2022 | 988.7169 | 1076.4161 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7352 | 0.71804 | 0 | 0 | 0 | 0 | 150 | 1090.6733 | -141.1961 | -5.4107 | 14.2572 | 10.312 | 0 | 0 | 2022 | 0
2023 | 988.9349 | 1076.6534 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3841 | 1.3818 | 1.022 | 25.856 | 0 | 24.6 | 100 | 1097.4638 | -141.4334 | -5.4316 | 20.8104 | 10.9743 | 50.5988 | 200 | 2023 | 0
2024 | 986.2338 | 1073.7128 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.9178 | 2.0115 | 1.533 | 103.424 | 0 | 24.6 | 0 | 1078.7063 | -138.4928 | -5.1726 | 4.9935 | 9.3763 | 202.3953 | 200 | 2024 | 0
2025 | 983.648 | 1070.8976 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8048 | 1.8714 | 1.533 | 103.424 | 0 | 24.6 | 0 | 1077.4532 | -135.6776 | -4.9233 | 6.5556 | 9.5365 | 202.3953 | 200 | 2025 | 0
2026 | 981.351 | 1068.3969 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6243 | 1.7055 | 1.533 | 103.424 | 0 | 24.6 | 0 | 1076.1068 | -133.1769 | -4.7008 | 7.7099 | 9.6556 | 202.3953 | 200 | 2026 | 0
2027 | 980.0358 | 1066.9649 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4914 | 1.5213 | 2.044 | 103.424 | 0 | 24.6 | 0 | 1075.3007 | -131.7449 | -4.5729 | 8.3357 | 9.7206 | 202.3953 | 200 | 2027 | 0
2028 | 979.1785 | 1066.0316 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.233 | 1.3267 | 2.044 | 103.424 | 0 | 24.6 | 0 | 1073.8477 | -130.8116 | -4.4893 | 7.8161 | 9.6682 | 202.3953 | 200 | 2028 | 0
2029 | 979.2926 | 1066.1559 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8599 | 1.1117 | 2.555 | 103.424 | 0 | 24.6 | 0 | 1072.7706 | -130.9359 | -4.5005 | 6.6148 | 9.5455 | 202.3953 | 200 | 2029 | 0
2030 | 978.398 | 1065.1819 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5667 | 3.1512 | 3.066 | 155.136 | 0 | 24.6 | 0 | 1125.7399 | -129.9619 | -4.4131 | 60.558 | 15.0595 | 303.593 | 200 | 2030 | 0
2031 | 978.3642 | 1065.1451 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4055 | 5.7286 | 3.577 | 232.704 | 0 | 24.6 | 0 | 1065.3351 | -391.8251 | -31.179 | 0.19006 | 8.8894 | 455.3894 | 200 | 2031 | 122
2032 | 978.3962 | 1065.18 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4088 | 6.58 | 3.577 | 232.704 | 0 | 24.6 | 0 | 1065.1899 | -391.86 | -31.1813 | 0.0098577 | 8.871 | 455.3894 | 200 | 2032 | 122
2033 | 978.2687 | 1065.0411 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5949 | 6.7371 | 4.088 | 232.704 | 0 | 24.6 | 0 | 1065.044 | -391.7211 | -31.1723 | 0.0028857 | 8.8703 | 455.3894 | 200 | 2033 | 122
2034 | 978.9426 | 1065.7748 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91312 | 5.894 | 4.599 | 232.704 | 2.7798 | 24.6 | 0 | 1066.8099 | -392.4548 | -31.2197 | 1.0351 | 8.9757 | 455.3894 | 200 | 2034 | 122
2035 | 979.3191 | 1066.1848 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0.43902 | 4.8353 | 4.599 | 232.704 | 7.0496 | 24.6 | 0 | 1069.5469 | -392.8648 | -31.2461 | 3.3622 | 9.2133 | 455.3894 | 200 | 2035 | 122
2036 | 980.3504 | 1067.3075 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15491 | 3.8259 | 5.11 | 232.704 | 7.0496 | 24.6 | 0 | 1068.7644 | -393.9875 | -31.3184 | 1.4569 | 9.0186 | 455.3894 | 200 | 2036 | 122
2037 | 980.0782 | 1067.0111 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049478 | 2.8087 | 5.11 | 232.704 | 7.0496 | 24.6 | 0 | 1067.6417 | -393.6911 | -31.2994 | 0.63061 | 8.9343 | 455.3894 | 200 | 2037 | 122
2038 | 980.5898 | 1067.5681 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0.020478 | 2.2679 | 5.621 | 232.704 | 7.0496 | 24.6 | 0 | 1067.583 | -394.2481 | -31.3352 | 0.014873 | 8.8715 | 455.3894 | 200 | 2038 | 122
2039 | 981.0352 | 1068.053 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044529 | 1.5 | 5.621 | 232.704 | 10.3337 | 24.6 | 0 | 1070.0831 | -394.733 | -31.3664 | 2.0301 | 9.0769 | 455.3894 | 200 | 2039 | 122
2040 | 982.7065 | 1069.8726 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97755 | 6.132 | 232.704 | 10.3337 | 24.6 | 0 | 1070.0673 | -396.5526 | -31.4831 | 0.19465 | 8.8898 | 455.3894 | 200 | 2040 | 122
2041 | 982.8782 | 1070.0595 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61697 | 6.132 | 232.704 | 11.5115 | 24.6 | 0 | 1070.8845 | -396.7395 | -31.4951 | 0.82499 | 8.9539 | 455.3894 | 200 | 2041 | 122
2042 | 983.3314 | 1070.5529 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33603 | 6.643 | 232.704 | 11.5115 | 24.6 | 0 | 1071.1145 | -397.2329 | -31.5266 | 0.56159 | 8.9271 | 455.3894 | 200 | 2042 | 122
2043 | 983.5293 | 1070.7683 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14061 | 7.154 | 232.704 | 11.5115 | 24.6 | 0 | 1071.4301 | -397.4483 | -31.5404 | 0.6618 | 8.9373 | 455.3894 | 200 | 2043 | 122
2044 | 983.9902 | 1071.2701 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030549 | 7.154 | 232.704 | 11.5115 | 24.6 | 0 | 1071.32 | -397.9501 | -31.5725 | 0.049921 | 8.8751 | 455.3894 | 200 | 2044 | 122
2045 | 984.6379 | 1071.9753 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0.23212 | 0 | 0 | 0 | 7.665 | 232.704 | 11.5115 | 24.6 | 0 | 1072.0326 | -398.6553 | -31.6175 | 0.05728 | 8.8758 | 455.3894 | 200 | 2045 | 122
2046 | 984.58 | 1071.9122 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0.23212 | 0 | 0 | 0 | 8.176 | 232.704 | 11.5115 | 24.6 | 0 | 1072.5436 | -398.5922 | -31.6135 | 0.63137 | 8.9341 | 455.3894 | 200 | 2046 | 122
2047 | 984.19 | 1071.4877 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0.23212 | 0 | 0 | 0 | 8.687 | 232.704 | 11.5115 | 24.6 | 0 | 1073.0546 | -398.1677 | -31.5864 | 1.567 | 9.0292 | 455.3894 | 200 | 2047 | 122
2048 | 984.04 | 1071.3243 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0.23212 | 0 | 0 | 0 | 9.198 | 232.704 | 11.5115 | 24.6 | 0 | 1073.5656 | -398.0043 | -31.576 | 2.2413 | 9.0978 | 455.3894 | 200 | 2048 | 122
2049 | 983.28 | 1070.4969 | 673.32 | 0 | 0 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | 0.23212 | 0 | 0 | 0 | 9.198 | 232.704 | 8.7317 | 24.6 | 0 | 1070.7858 | -397.1769 | -31.5231 | 0.28888 | 8.8994 | 455.3894 | 200 | 2049 | 122

## Market Only-Low
DRAFT - PRELIMINARY
2019 KP IRP
2019H1 Low Band Commodity Pricing
KP Optimization Expansion Plan (Supply-side, Renewables, VVO, DR, EE) for Stakeholder 2022-2024 Market Purchase Scenario
| Planning Peak Load (MW) | Required Generation Capacity (MW) | Firm Generation Capacity without New Additions (MW) | 15 MW CHP Capacity (MW) | 216 MW RICE Firm Capacity (MW) | 256 MW (50% Share of 497 MW) GE 7F.05 Firm Capacity (MW) | 325 MW (25% Share of 1,603 MW) M 501 JAC Firm Capacity (MW) | 125 MW LM 6000 CT Firm Capacity (MW) | Big Sandy Site 216 MW RICE Firm Capacity (MW) | Big Sandy Site 256 MW (50% Share of 497 MW) GE 7F.05 Firm Capacity (MW) | Big Sandy Site 325 MW (25% Share of 1,603 MW) M 501 JAC Firm Capacity (MW) | Big Sandy Site Repower 443 MW Firm Capacity | Commercial DR Firm Capacity (MW) | Residential DR Firm Capacity (MW) | Commercial DSM Firm Capacity (MW) | Residential DSM Firm Capacity (MW) | Distributed Solar Firm Capacity (MW) | Utility Solar Firm Capacity (MW) | CVR Firm Capacity (MW) | Wind Firm Capacity (MW) | Short Term PPA Capacity (MW) | Firm Generation Capacity with New Additions (MW) | Capacity Reserves Above Required Generation without New Additions (MW) | Reserve Margin without New Capacity Additions (%) | Capacity Reserves Above Required Generation with New Capacity Additions (MW) | Reserve Margin with New Capacity Additions (%) | Nameplate Solar | Nameplate Wind |  | New Nat Gas
2020 | 978.4483 | 1065.5302 | 1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1302 | 236.4698 | 33.0678 | 236.4698 | 33.0678 | 0 | 0 | 2020 | 0
2021 | 982.7561 | 1069.6317 | 1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1302 | 232.3683 | 32.4846 | 232.3683 | 32.4846 | 0 | 0 | 2021 | 0
2022 | 988.7169 | 1076.4161 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1085.22 | -141.1961 | -5.4107 | 8.8039 | 9.7604 | 0 | 0 | 2022 | 0
2023 | 988.9349 | 1076.6534 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.022 | 0 | 0 | 0 | 150 | 1086.242 | -141.4334 | -5.4316 | 9.5886 | 9.8396 | 0 | 0 | 2023 | 0
2024 | 986.2338 | 1073.7128 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.533 | 0 | 0 | 0 | 150 | 1086.753 | -138.4928 | -5.1726 | 13.0402 | 10.1922 | 0 | 0 | 2024 | 0
2025 | 983.648 | 1070.8976 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17808 | 4.7787 | 1.533 | 129.28 | 0 | 0 | 0 | 1070.9898 | -135.6776 | -4.9233 | 0.092218 | 8.8794 | 252.9941 | 0 | 2025 | 0
2026 | 981.351 | 1068.3969 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.33095 | 4.445 | 1.533 | 129.28 | 0 | 0 | 0 | 1070.8089 | -133.1769 | -4.7008 | 2.412 | 9.1158 | 252.9941 | 0 | 2026 | 0
2027 | 980.0358 | 1066.9649 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45872 | 3.8377 | 2.044 | 129.28 | 0 | 0 | 0 | 1070.8404 | -131.7449 | -4.5729 | 3.8755 | 9.2654 | 252.9941 | 0 | 2027 | 0
2028 | 979.1785 | 1066.0316 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55189 | 3.4211 | 2.044 | 129.28 | 0 | 0 | 0 | 1070.517 | -130.8116 | -4.4893 | 4.4854 | 9.3281 | 252.9941 | 0 | 2028 | 0
2029 | 979.2926 | 1066.1559 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52589 | 2.4639 | 2.555 | 129.28 | 0 | 0 | 0 | 1070.0448 | -130.9359 | -4.5005 | 3.8889 | 9.2671 | 252.9941 | 0 | 2029 | 0
2030 | 978.398 | 1065.1819 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51815 | 2.5904 | 3.066 | 129.28 | 0 | 0 | 0 | 1070.6746 | -129.9619 | -4.4131 | 5.4927 | 9.4314 | 252.9941 | 0 | 2030 | 0
2031 | 978.3642 | 1065.1451 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0.43541 | 2.0789 | 3.577 | 206.848 | 0 | 0 | 0 | 1134.2593 | -391.8251 | -31.179 | 69.1142 | 15.9343 | 404.7906 | 0 | 2031 | 248
2032 | 978.3962 | 1065.18 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0.35497 | 1.6061 | 3.577 | 206.848 | 0 | 0 | 0 | 1133.7061 | -391.86 | -31.1813 | 68.5261 | 15.8739 | 404.7906 | 0 | 2032 | 248
2033 | 978.2687 | 1065.0411 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0.27978 | 1.1372 | 4.088 | 206.848 | 0 | 0 | 0 | 1133.673 | -391.7211 | -31.1723 | 68.6318 | 15.8856 | 404.7906 | 0 | 2033 | 248
2034 | 978.9426 | 1065.7748 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0.20561 | 0.83507 | 4.599 | 206.848 | 0 | 0 | 0 | 1133.8077 | -392.4548 | -31.2197 | 68.0328 | 15.8196 | 404.7906 | 0 | 2034 | 248
2035 | 979.3191 | 1066.1848 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0.14243 | 0.55625 | 4.599 | 206.848 | 0 | 0 | 0 | 1133.4657 | -392.8648 | -31.2461 | 67.2809 | 15.7402 | 404.7906 | 0 | 2035 | 248
2036 | 980.3504 | 1067.3075 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0.090078 | 0.34652 | 5.11 | 206.848 | 0 | 0 | 0 | 1133.7146 | -393.9875 | -31.3184 | 66.4071 | 15.6438 | 404.7906 | 0 | 2036 | 248
2037 | 980.0782 | 1067.0111 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0.049478 | 0.17881 | 5.11 | 206.848 | 0 | 0 | 0 | 1133.5063 | -393.6911 | -31.2994 | 66.4952 | 15.6547 | 404.7906 | 0 | 2037 | 248
2038 | 980.5898 | 1067.5681 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0.020478 | 0.076603 | 5.621 | 206.848 | 0 | 0 | 0 | 1133.8861 | -394.2481 | -31.3352 | 66.318 | 15.6331 | 404.7906 | 0 | 2038 | 248
2039 | 981.0352 | 1068.053 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0.0044529 | 0.016403 | 5.621 | 206.848 | 0 | 0 | 0 | 1133.8099 | -394.733 | -31.3664 | 65.7569 | 15.5728 | 404.7906 | 0 | 2039 | 248
2040 | 982.7065 | 1069.8726 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 6.132 | 232.704 | 0 | 0 | 0 | 1160.156 | -396.5526 | -31.4831 | 90.2834 | 18.0572 | 455.3894 | 0 | 2040 | 248
2041 | 982.8782 | 1070.0595 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 6.132 | 232.704 | 0 | 0 | 0 | 1160.156 | -396.7395 | -31.4951 | 90.0965 | 18.0366 | 455.3894 | 0 | 2041 | 248
2042 | 983.3314 | 1070.5529 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 6.643 | 232.704 | 0 | 0 | 0 | 1160.667 | -397.2329 | -31.5266 | 90.1141 | 18.0342 | 455.3894 | 0 | 2042 | 248
2043 | 983.5293 | 1070.7683 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 7.154 | 232.704 | 0 | 0 | 0 | 1161.178 | -397.4483 | -31.5404 | 90.4097 | 18.0624 | 455.3894 | 0 | 2043 | 248
2044 | 983.9902 | 1071.2701 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 7.154 | 232.704 | 0 | 0 | 0 | 1161.178 | -397.9501 | -31.5725 | 89.9079 | 18.0071 | 455.3894 | 0 | 2044 | 248
2045 | 984.6379 | 1071.9753 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 7.665 | 232.704 | 0 | 0 | 0 | 1161.689 | -398.6553 | -31.6175 | 89.7137 | 17.9813 | 455.3894 | 0 | 2045 | 248
2046 | 984.58 | 1071.9122 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 8.176 | 232.704 | 0 | 0 | 0 | 1162.2 | -398.5922 | -31.6135 | 90.2878 | 18.0402 | 455.3894 | 0 | 2046 | 248
2047 | 984.19 | 1071.4877 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 8.687 | 232.704 | 0 | 0 | 0 | 1162.711 | -398.1677 | -31.5864 | 91.2233 | 18.1389 | 455.3894 | 0 | 2047 | 248
2048 | 984.04 | 1071.3243 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 9.198 | 232.704 | 0 | 0 | 0 | 1163.222 | -398.0043 | -31.576 | 91.8977 | 18.2088 | 455.3894 | 0 | 2048 | 248
2049 | 983.28 | 1070.4969 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 9.198 | 232.704 | 0 | 0 | 0 | 1163.222 | -397.1769 | -31.5231 | 92.7251 | 18.3002 | 455.3894 | 0 | 2049 | 248
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31

## Solar + Wind-Low
DRAFT - PRELIMINARY
2019 KP IRP
2019H1 Low Band Commodity Pricing
KP Optimization Expansion Plan (Supply-side, Renewables, VVO, DR, EE) for Stakeholder 2023-2030 Wind and Solar Additions Scenario
| Planning Peak Load (MW) | Required Generation Capacity (MW) | Firm Generation Capacity without New Additions (MW) | 15 MW CHP Capacity (MW) | 216 MW RICE Firm Capacity (MW) | 256 MW (50% Share of 497 MW) GE 7F.05 Firm Capacity (MW) | 325 MW (25% Share of 1,603 MW) M 501 JAC Firm Capacity (MW) | 125 MW LM 6000 CT Firm Capacity (MW) | Big Sandy Site 216 MW RICE Firm Capacity (MW) | Big Sandy Site 256 MW (50% Share of 497 MW) GE 7F.05 Firm Capacity (MW) | Big Sandy Site 325 MW (25% Share of 1,603 MW) M 501 JAC Firm Capacity (MW) | Big Sandy Site Repower 443 MW Firm Capacity | Commercial DR Firm Capacity (MW) | Residential DR Firm Capacity (MW) | Commercial DSM Firm Capacity (MW) | Residential DSM Firm Capacity (MW) | Distributed Solar Firm Capacity (MW) | Utility Solar Firm Capacity (MW) | CVR Firm Capacity (MW) | Wind Firm Capacity (MW) | Short Term PPA Capacity (MW) | Firm Generation Capacity with New Additions (MW) | Capacity Reserves Above Required Generation without New Additions (MW) | Reserve Margin without New Capacity Additions (%) | Capacity Reserves Above Required Generation with New Capacity Additions (MW) | Reserve Margin with New Capacity Additions (%) | Nameplate Solar | Nameplate Wind |  | New Nat Gas
2020 | 978.4483 | 1065.5302 | 1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1302 | 236.4698 | 33.0678 | 236.4698 | 33.0678 | 0 | 0 | 2020 | 0
2021 | 982.7561 | 1069.6317 | 1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1302 | 232.3683 | 32.4846 | 232.3683 | 32.4846 | 0 | 0 | 2021 | 0
2022 | 988.7169 | 1076.4161 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155.136 | 0 | 0 | 0 | 1090.356 | -141.1961 | -5.4107 | 13.9399 | 10.2799 | 303.593 | 0 | 2022 | 0
2023 | 988.9349 | 1076.6534 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.022 | 155.136 | 0 | 0 | 0 | 1091.378 | -141.4334 | -5.4316 | 14.7246 | 10.3589 | 303.593 | 0 | 2023 | 0
2024 | 986.2338 | 1073.7128 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.533 | 155.136 | 0 | 0 | 0 | 1091.889 | -138.4928 | -5.1726 | 18.1762 | 10.713 | 303.593 | 0 | 2024 | 0
2025 | 983.648 | 1070.8976 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.533 | 155.136 | 0 | 0 | 0 | 1091.889 | -135.6776 | -4.9233 | 20.9914 | 11.004 | 303.593 | 0 | 2025 | 0
2026 | 981.351 | 1068.3969 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.533 | 155.136 | 0 | 0 | 0 | 1091.889 | -133.1769 | -4.7008 | 23.4921 | 11.2639 | 303.593 | 0 | 2026 | 0
2027 | 980.0358 | 1066.9649 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.044 | 155.136 | 0 | 0 | 0 | 1092.4 | -131.7449 | -4.5729 | 25.4351 | 11.4653 | 303.593 | 0 | 2027 | 0
2028 | 979.1785 | 1066.0316 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.044 | 155.136 | 0 | 0 | 0 | 1092.4 | -130.8116 | -4.4893 | 26.3684 | 11.5629 | 303.593 | 0 | 2028 | 0
2029 | 979.2926 | 1066.1559 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.555 | 155.136 | 0 | 0 | 0 | 1092.911 | -130.9359 | -4.5005 | 26.7551 | 11.6021 | 303.593 | 0 | 2029 | 0
2030 | 978.398 | 1065.1819 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.066 | 155.136 | 0 | 0 | 0 | 1093.422 | -129.9619 | -4.4131 | 28.2401 | 11.7564 | 303.593 | 0 | 2030 | 0
2031 | 978.3642 | 1065.1451 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 3.577 | 232.704 | 0 | 0 | 0 | 1157.601 | -391.8251 | -31.179 | 92.4559 | 18.3201 | 455.3894 | 0 | 2031 | 248
2032 | 978.3962 | 1065.18 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 3.577 | 232.704 | 0 | 0 | 0 | 1157.601 | -391.86 | -31.1813 | 92.421 | 18.3162 | 455.3894 | 0 | 2032 | 248
2033 | 978.2687 | 1065.0411 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 4.088 | 232.704 | 0 | 0 | 0 | 1158.112 | -391.7211 | -31.1723 | 93.0709 | 18.3838 | 455.3894 | 0 | 2033 | 248
2034 | 978.9426 | 1065.7748 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 4.599 | 232.704 | 0 | 0 | 0 | 1158.623 | -392.4548 | -31.2197 | 92.8482 | 18.3545 | 455.3894 | 0 | 2034 | 248
2035 | 979.3191 | 1066.1848 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 4.599 | 232.704 | 0 | 0 | 0 | 1158.623 | -392.8648 | -31.2461 | 92.4382 | 18.309 | 455.3894 | 0 | 2035 | 248
2036 | 980.3504 | 1067.3075 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 5.11 | 232.704 | 0 | 0 | 0 | 1159.134 | -393.9875 | -31.3184 | 91.8265 | 18.2367 | 455.3894 | 0 | 2036 | 248
2037 | 980.0782 | 1067.0111 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 5.11 | 232.704 | 0 | 0 | 0 | 1159.134 | -393.6911 | -31.2994 | 92.1229 | 18.2695 | 455.3894 | 0 | 2037 | 248
2038 | 980.5898 | 1067.5681 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 5.621 | 232.704 | 0 | 0 | 0 | 1159.645 | -394.2481 | -31.3352 | 92.0769 | 18.2599 | 455.3894 | 0 | 2038 | 248
2039 | 981.0352 | 1068.053 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 5.621 | 232.704 | 0 | 0 | 0 | 1159.645 | -394.733 | -31.3664 | 91.592 | 18.2063 | 455.3894 | 0 | 2039 | 248
2040 | 982.7065 | 1069.8726 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 6.132 | 232.704 | 0 | 0 | 0 | 1160.156 | -396.5526 | -31.4831 | 90.2834 | 18.0572 | 455.3894 | 0 | 2040 | 248
2041 | 982.8782 | 1070.0595 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 6.132 | 232.704 | 0 | 0 | 0 | 1160.156 | -396.7395 | -31.4951 | 90.0965 | 18.0366 | 455.3894 | 0 | 2041 | 248
2042 | 983.3314 | 1070.5529 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 6.643 | 232.704 | 0 | 0 | 0 | 1160.667 | -397.2329 | -31.5266 | 90.1141 | 18.0342 | 455.3894 | 0 | 2042 | 248
2043 | 983.5293 | 1070.7683 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 7.154 | 232.704 | 0 | 0 | 0 | 1161.178 | -397.4483 | -31.5404 | 90.4097 | 18.0624 | 455.3894 | 0 | 2043 | 248
2044 | 983.9902 | 1071.2701 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 7.154 | 232.704 | 0 | 0 | 0 | 1161.178 | -397.9501 | -31.5725 | 89.9079 | 18.0071 | 455.3894 | 0 | 2044 | 248
2045 | 984.6379 | 1071.9753 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 7.665 | 232.704 | 0 | 0 | 0 | 1161.689 | -398.6553 | -31.6175 | 89.7137 | 17.9813 | 455.3894 | 0 | 2045 | 248
2046 | 984.58 | 1071.9122 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 8.176 | 232.704 | 0 | 0 | 0 | 1162.2 | -398.5922 | -31.6135 | 90.2878 | 18.0402 | 455.3894 | 0 | 2046 | 248
2047 | 984.19 | 1071.4877 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 8.687 | 232.704 | 0 | 0 | 0 | 1162.711 | -398.1677 | -31.5864 | 91.2233 | 18.1389 | 455.3894 | 0 | 2047 | 248
2048 | 984.04 | 1071.3243 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 9.198 | 232.704 | 0 | 0 | 0 | 1163.222 | -398.0043 | -31.576 | 91.8977 | 18.2088 | 455.3894 | 0 | 2048 | 248
2049 | 983.28 | 1070.4969 | 673.32 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 9.198 | 232.704 | 0 | 0 | 0 | 1163.222 | -397.1769 | -31.5231 | 92.7251 | 18.3002 | 455.3894 | 0 | 2049 | 248
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31

## CT Only-Low
DRAFT - PRELIMINARY
2019 KP IRP
2019H1 Low Band Commodity Pricing
KP Optimization Expansion Plan (Supply-side, Renewables, VVO, DR, EE) for Stakeholder 2023 CT Addition Scenario
| Planning Peak Load (MW) | Required Generation Capacity (MW) | Firm Generation Capacity without New Additions (MW) | 15 MW CHP Capacity (MW) | 216 MW RICE Firm Capacity (MW) | 256 MW (50% Share of 497 MW) GE 7F.05 Firm Capacity (MW) | 325 MW (25% Share of 1,603 MW) M 501 JAC Firm Capacity (MW) | 125 MW LM 6000 CT Firm Capacity (MW) | Big Sandy Site 216 MW RICE Firm Capacity (MW) | Big Sandy Site 256 MW (50% Share of 497 MW) GE 7F.05 Firm Capacity (MW) | Big Sandy Site 325 MW (25% Share of 1,603 MW) M 501 JAC Firm Capacity (MW) | Big Sandy Site Repower 443 MW Firm Capacity | Commercial DR Firm Capacity (MW) | Residential DR Firm Capacity (MW) | Commercial DSM Firm Capacity (MW) | Residential DSM Firm Capacity (MW) | Distributed Solar Firm Capacity (MW) | Utility Solar Firm Capacity (MW) | CVR Firm Capacity (MW) | Wind Firm Capacity (MW) | Short Term PPA Capacity (MW) | Firm Generation Capacity with New Additions (MW) | Capacity Reserves Above Required Generation without New Additions (MW) | Reserve Margin without New Capacity Additions (%) | Capacity Reserves Above Required Generation with New Capacity Additions (MW) | Reserve Margin with New Capacity Additions (%) | Nameplate Solar | Nameplate Wind |  | New Nat Gas
2020 | 978.4483 | 1065.5302 | 1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1302 | 236.4698 | 33.0678 | 236.4698 | 33.0678 | 0 | 0 | 2020 | 0
2021 | 982.7561 | 1069.6317 | 1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1302 | 232.3683 | 32.4846 | 232.3683 | 32.4846 | 0 | 0 | 2021 | 0
2022 | 988.7169 | 1076.4161 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1085.22 | -141.1961 | -5.4107 | 8.8039 | 9.7604 | 0 | 0 | 2022 | 0
2023 | 988.9349 | 1076.6534 | 935.22 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.022 | 0 | 0 | 0 | 0 | 1184.242 | -141.4334 | -5.4316 | 107.5886 | 19.7492 | 0 | 0 | 2023 | 248
2024 | 986.2338 | 1073.7128 | 935.22 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.533 | 0 | 0 | 0 | 0 | 1184.753 | -138.4928 | -5.1726 | 111.0402 | 20.129 | 0 | 0 | 2024 | 248
2025 | 983.648 | 1070.8976 | 935.22 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.533 | 0 | 0 | 0 | 0 | 1184.753 | -135.6776 | -4.9233 | 113.8554 | 20.4448 | 0 | 0 | 2025 | 248
2026 | 981.351 | 1068.3969 | 935.22 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.533 | 0 | 0 | 0 | 0 | 1184.753 | -133.1769 | -4.7008 | 116.3561 | 20.7267 | 0 | 0 | 2026 | 248
2027 | 980.0358 | 1066.9649 | 935.22 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.044 | 0 | 0 | 0 | 0 | 1185.264 | -131.7449 | -4.5729 | 118.2991 | 20.9409 | 0 | 0 | 2027 | 248
2028 | 979.1785 | 1066.0316 | 935.22 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.044 | 0 | 0 | 0 | 0 | 1185.264 | -130.8116 | -4.4893 | 119.2324 | 21.0468 | 0 | 0 | 2028 | 248
2029 | 979.2926 | 1066.1559 | 935.22 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.555 | 0 | 0 | 0 | 0 | 1185.775 | -130.9359 | -4.5005 | 119.6191 | 21.0848 | 0 | 0 | 2029 | 248
2030 | 978.398 | 1065.1819 | 935.22 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.066 | 0 | 0 | 0 | 0 | 1186.286 | -129.9619 | -4.4131 | 121.1041 | 21.2478 | 0 | 0 | 2030 | 248
2031 | 978.3642 | 1065.1451 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.577 | 155.136 | 0 | 0 | 0 | 1080.033 | -391.8251 | -31.179 | 14.8879 | 10.3917 | 303.593 | 0 | 2031 | 248
2032 | 978.3962 | 1065.18 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.577 | 155.136 | 0 | 0 | 0 | 1080.033 | -391.86 | -31.1813 | 14.853 | 10.3881 | 303.593 | 0 | 2032 | 248
2033 | 978.2687 | 1065.0411 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.088 | 155.136 | 0 | 0 | 0 | 1080.544 | -391.7211 | -31.1723 | 15.5029 | 10.4547 | 303.593 | 0 | 2033 | 248
2034 | 978.9426 | 1065.7748 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.599 | 155.136 | 0 | 0 | 0 | 1081.055 | -392.4548 | -31.2197 | 15.2802 | 10.4309 | 303.593 | 0 | 2034 | 248
2035 | 979.3191 | 1066.1848 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.599 | 155.136 | 0 | 0 | 0 | 1081.055 | -392.8648 | -31.2461 | 14.8702 | 10.3884 | 303.593 | 0 | 2035 | 248
2036 | 980.3504 | 1067.3075 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.11 | 155.136 | 0 | 0 | 0 | 1081.566 | -393.9875 | -31.3184 | 14.2585 | 10.3244 | 303.593 | 0 | 2036 | 248
2037 | 980.0782 | 1067.0111 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.11 | 155.136 | 0 | 0 | 0 | 1081.566 | -393.6911 | -31.2994 | 14.5549 | 10.3551 | 303.593 | 0 | 2037 | 248
2038 | 980.5898 | 1067.5681 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.621 | 155.136 | 0 | 0 | 0 | 1082.077 | -394.2481 | -31.3352 | 14.5089 | 10.3496 | 303.593 | 0 | 2038 | 248
2039 | 981.0352 | 1068.053 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.621 | 155.136 | 0 | 0 | 0 | 1082.077 | -394.733 | -31.3664 | 14.024 | 10.2995 | 303.593 | 0 | 2039 | 248
2040 | 982.7065 | 1069.8726 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.132 | 232.704 | 0 | 0 | 0 | 1160.156 | -396.5526 | -31.4831 | 90.2834 | 18.0572 | 455.3894 | 0 | 2040 | 248
2041 | 982.8782 | 1070.0595 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.132 | 232.704 | 0 | 0 | 0 | 1160.156 | -396.7395 | -31.4951 | 90.0965 | 18.0366 | 455.3894 | 0 | 2041 | 248
2042 | 983.3314 | 1070.5529 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.643 | 232.704 | 0 | 0 | 0 | 1160.667 | -397.2329 | -31.5266 | 90.1141 | 18.0342 | 455.3894 | 0 | 2042 | 248
2043 | 983.5293 | 1070.7683 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.154 | 232.704 | 0 | 0 | 0 | 1161.178 | -397.4483 | -31.5404 | 90.4097 | 18.0624 | 455.3894 | 0 | 2043 | 248
2044 | 983.9902 | 1071.2701 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.154 | 232.704 | 0 | 0 | 0 | 1161.178 | -397.9501 | -31.5725 | 89.9079 | 18.0071 | 455.3894 | 0 | 2044 | 248
2045 | 984.6379 | 1071.9753 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.665 | 232.704 | 0 | 0 | 0 | 1161.689 | -398.6553 | -31.6175 | 89.7137 | 17.9813 | 455.3894 | 0 | 2045 | 248
2046 | 984.58 | 1071.9122 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.176 | 232.704 | 0 | 0 | 0 | 1162.2 | -398.5922 | -31.6135 | 90.2878 | 18.0402 | 455.3894 | 0 | 2046 | 248
2047 | 984.19 | 1071.4877 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.687 | 232.704 | 0 | 0 | 0 | 1162.711 | -398.1677 | -31.5864 | 91.2233 | 18.1389 | 455.3894 | 0 | 2047 | 248
2048 | 984.04 | 1071.3243 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.198 | 232.704 | 0 | 0 | 0 | 1163.222 | -398.0043 | -31.576 | 91.8977 | 18.2088 | 455.3894 | 0 | 2048 | 248
2049 | 983.28 | 1070.4969 | 673.32 | 0 | 0 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.198 | 232.704 | 0 | 0 | 0 | 1163.222 | -397.1769 | -31.5231 | 92.7251 | 18.3002 | 455.3894 | 0 | 2049 | 248
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31

## CC Only-Low
DRAFT - PRELIMINARY
2019 KP IRP
2019H1 Low Band Commodity Pricing
KP Optimization Expansion Plan (Supply-side, Renewables, VVO, DR, EE) for Stakeholder 2024 CC Addition Scenario
| Planning Peak Load (MW) | Required Generation Capacity (MW) | Firm Generation Capacity without New Additions (MW) | 15 MW CHP Capacity (MW) | 216 MW RICE Firm Capacity (MW) | 256 MW (50% Share of 497 MW) GE 7F.05 Firm Capacity (MW) | 325 MW (25% Share of 1,603 MW) M 501 JAC Firm Capacity (MW) | 125 MW LM 6000 CT Firm Capacity (MW) | Big Sandy Site 216 MW RICE Firm Capacity (MW) | Big Sandy Site 256 MW (50% Share of 497 MW) GE 7F.05 Firm Capacity (MW) | Big Sandy Site 325 MW (25% Share of 1,603 MW) M 501 JAC Firm Capacity (MW) | Big Sandy Site Repower 443 MW Firm Capacity | Commercial DR Firm Capacity (MW) | Residential DR Firm Capacity (MW) | Commercial DSM Firm Capacity (MW) | Residential DSM Firm Capacity (MW) | Distributed Solar Firm Capacity (MW) | Utility Solar Firm Capacity (MW) | CVR Firm Capacity (MW) | Wind Firm Capacity (MW) | Short Term PPA Capacity (MW) | Firm Generation Capacity with New Additions (MW) | Capacity Reserves Above Required Generation without New Additions (MW) | Reserve Margin without New Capacity Additions (%) | Capacity Reserves Above Required Generation with New Capacity Additions (MW) | Reserve Margin with New Capacity Additions (%) | Nameplate Solar | Nameplate Wind |  | New Nat Gas
2020 | 978.4483 | 1065.5302 | 1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1302 | 236.4698 | 33.0678 | 236.4698 | 33.0678 | 0 | 0 | 2020 | 0
2021 | 982.7561 | 1069.6317 | 1302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1302 | 232.3683 | 32.4846 | 232.3683 | 32.4846 | 0 | 0 | 2021 | 0
2022 | 988.7169 | 1076.4161 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 1085.22 | -141.1961 | -5.4107 | 8.8039 | 9.7604 | 0 | 0 | 2022 | 0
2023 | 988.9349 | 1076.6534 | 935.22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.022 | 0 | 0 | 0 | 150 | 1086.242 | -141.4334 | -5.4316 | 9.5886 | 9.8396 | 0 | 0 | 2023 | 0
2024 | 986.2338 | 1073.7128 | 935.22 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.533 | 0 | 0 | 0 | 0 | 1337.753 | -138.4928 | -5.1726 | 264.0402 | 35.6426 | 0 | 0 | 2024 | 401
2025 | 983.648 | 1070.8976 | 935.22 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.533 | 0 | 0 | 0 | 0 | 1337.753 | -135.6776 | -4.9233 | 266.8554 | 35.9992 | 0 | 0 | 2025 | 401
2026 | 981.351 | 1068.3969 | 935.22 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.533 | 0 | 0 | 0 | 0 | 1337.753 | -133.1769 | -4.7008 | 269.3561 | 36.3175 | 0 | 0 | 2026 | 401
2027 | 980.0358 | 1066.9649 | 935.22 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.044 | 0 | 0 | 0 | 0 | 1338.264 | -131.7449 | -4.5729 | 271.2991 | 36.5526 | 0 | 0 | 2027 | 401
2028 | 979.1785 | 1066.0316 | 935.22 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.044 | 0 | 0 | 0 | 0 | 1338.264 | -130.8116 | -4.4893 | 272.2324 | 36.6721 | 0 | 0 | 2028 | 401
2029 | 979.2926 | 1066.1559 | 935.22 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.555 | 0 | 0 | 0 | 0 | 1338.775 | -130.9359 | -4.5005 | 272.6191 | 36.7084 | 0 | 0 | 2029 | 401
2030 | 978.398 | 1065.1819 | 935.22 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.066 | 0 | 0 | 0 | 0 | 1339.286 | -129.9619 | -4.4131 | 274.1041 | 36.8856 | 0 | 0 | 2030 | 401
2031 | 978.3642 | 1065.1451 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.577 | 77.568 | 0 | 0 | 0 | 1155.465 | -391.8251 | -31.179 | 90.3199 | 18.1017 | 151.7965 | 0 | 2031 | 401
2032 | 978.3962 | 1065.18 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.577 | 77.568 | 0 | 0 | 0 | 1155.465 | -391.86 | -31.1813 | 90.285 | 18.0979 | 151.7965 | 0 | 2032 | 401
2033 | 978.2687 | 1065.0411 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.088 | 77.568 | 0 | 0 | 0 | 1155.976 | -391.7211 | -31.1723 | 90.9349 | 18.1655 | 151.7965 | 0 | 2033 | 401
2034 | 978.9426 | 1065.7748 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.599 | 77.568 | 0 | 0 | 0 | 1156.487 | -392.4548 | -31.2197 | 90.7122 | 18.1363 | 151.7965 | 0 | 2034 | 401
2035 | 979.3191 | 1066.1848 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.599 | 77.568 | 0 | 0 | 0 | 1156.487 | -392.8648 | -31.2461 | 90.3022 | 18.0909 | 151.7965 | 0 | 2035 | 401
2036 | 980.3504 | 1067.3075 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.11 | 77.568 | 0 | 0 | 0 | 1156.998 | -393.9875 | -31.3184 | 89.6905 | 18.0188 | 151.7965 | 0 | 2036 | 401
2037 | 980.0782 | 1067.0111 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.11 | 77.568 | 0 | 0 | 0 | 1156.998 | -393.6911 | -31.2994 | 89.9869 | 18.0516 | 151.7965 | 0 | 2037 | 401
2038 | 980.5898 | 1067.5681 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.621 | 77.568 | 0 | 0 | 0 | 1157.509 | -394.2481 | -31.3352 | 89.9409 | 18.0421 | 151.7965 | 0 | 2038 | 401
2039 | 981.0352 | 1068.053 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.621 | 77.568 | 0 | 0 | 0 | 1157.509 | -394.733 | -31.3664 | 89.456 | 17.9885 | 151.7965 | 0 | 2039 | 401
2040 | 982.7065 | 1069.8726 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.132 | 155.136 | 0 | 0 | 0 | 1235.588 | -396.5526 | -31.4831 | 165.7154 | 25.7332 | 303.593 | 0 | 2040 | 401
2041 | 982.8782 | 1070.0595 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.132 | 232.704 | 0 | 0 | 0 | 1313.156 | -396.7395 | -31.4951 | 243.0965 | 33.6031 | 455.3894 | 0 | 2041 | 401
2042 | 983.3314 | 1070.5529 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.643 | 232.704 | 0 | 0 | 0 | 1313.667 | -397.2329 | -31.5266 | 243.1141 | 33.5935 | 455.3894 | 0 | 2042 | 401
2043 | 983.5293 | 1070.7683 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.154 | 232.704 | 0 | 0 | 0 | 1314.178 | -397.4483 | -31.5404 | 243.4097 | 33.6186 | 455.3894 | 0 | 2043 | 401
2044 | 983.9902 | 1071.2701 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.154 | 232.704 | 0 | 0 | 0 | 1314.178 | -397.9501 | -31.5725 | 242.9079 | 33.556 | 455.3894 | 0 | 2044 | 401
2045 | 984.6379 | 1071.9753 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.665 | 232.704 | 0 | 0 | 0 | 1314.689 | -398.6553 | -31.6175 | 242.7137 | 33.52 | 455.3894 | 0 | 2045 | 401
2046 | 984.58 | 1071.9122 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.176 | 232.704 | 0 | 0 | 0 | 1315.2 | -398.5922 | -31.6135 | 243.2878 | 33.5798 | 455.3894 | 0 | 2046 | 401
2047 | 984.19 | 1071.4877 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.687 | 232.704 | 0 | 0 | 0 | 1315.711 | -398.1677 | -31.5864 | 244.2233 | 33.6847 | 455.3894 | 0 | 2047 | 401
2048 | 984.04 | 1071.3243 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.198 | 232.704 | 0 | 0 | 0 | 1316.222 | -398.0043 | -31.576 | 244.8977 | 33.757 | 455.3894 | 0 | 2048 | 401
2049 | 983.28 | 1070.4969 | 673.32 | 0 | 0 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.198 | 232.704 | 0 | 0 | 0 | 1316.222 | -397.1769 | -31.5231 | 245.7251 | 33.8603 | 455.3894 | 0 | 2049 | 401
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31

## Comparison
DRAFT - PRELIMINARY
2019 KPCo IRP | [10 empty] | Alternate Title Text:
| Base | Market | Solar + Wind | CT Only | CC Only | Base | Market | Solar + Wind | CT Only | CC Only | Nameplate Solar
2020 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 0 | 0 | 303.593 | 0 | 0 | 0 | 0 | 303.593 | 0 | 0
2023 | 50.5988 | 0 | 303.593 | 0 | 0 | 50.5988 | 0 | 303.593 | 0 | 0
2024 | 202.3953 | 0 | 303.593 | 0 | 0 | 202.3953 | 0 | 303.593 | 0 | 0
2025 | 202.3953 | 252.9941 | 303.593 | 0 | 0 | -50.5988 | 0 | 50.5988 | -252.9941 | -252.9941
2026 | 202.3953 | 252.9941 | 303.593 | 0 | 0 | -50.5988 | 0 | 50.5988 | -252.9941 | -252.9941
2027 | 202.3953 | 252.9941 | 303.593 | 0 | 0 | -50.5988 | 0 | 50.5988 | -252.9941 | -252.9941
2028 | 202.3953 | 252.9941 | 303.593 | 0 | 0 | -50.5988 | 0 | 50.5988 | -252.9941 | -252.9941
2029 | 202.3953 | 252.9941 | 303.593 | 0 | 0 | -50.5988 | 0 | 50.5988 | -252.9941 | -252.9941
2030 | 303.593 | 252.9941 | 303.593 | 0 | 0 | 50.5988 | 0 | 50.5988 | -252.9941 | -252.9941
2031 | 455.3894 | 404.7906 | 455.3894 | 303.593 | 151.7965 | 50.5988 | 0 | 50.5988 | -101.1977 | -252.9941
2032 | 455.3894 | 404.7906 | 455.3894 | 303.593 | 151.7965 | 50.5988 | 0 | 50.5988 | -101.1977 | -252.9941
2033 | 455.3894 | 404.7906 | 455.3894 | 303.593 | 151.7965 | 50.5988 | 0 | 50.5988 | -101.1977 | -252.9941
2034 | 455.3894 | 404.7906 | 455.3894 | 303.593 | 151.7965 | 50.5988 | 0 | 50.5988 | -101.1977 | -252.9941
2035 | 455.3894 | 404.7906 | 455.3894 | 303.593 | 151.7965 | 50.5988 | 0 | 50.5988 | -101.1977 | -252.9941
2036 | 455.3894 | 404.7906 | 455.3894 | 303.593 | 151.7965 | 50.5988 | 0 | 50.5988 | -101.1977 | -252.9941
2037 | 455.3894 | 404.7906 | 455.3894 | 303.593 | 151.7965 | 50.5988 | 0 | 50.5988 | -101.1977 | -252.9941
2038 | 455.3894 | 404.7906 | 455.3894 | 303.593 | 151.7965 | 50.5988 | 0 | 50.5988 | -101.1977 | -252.9941
2039 | 455.3894 | 404.7906 | 455.3894 | 303.593 | 151.7965 | 50.5988 | 0 | 50.5988 | -101.1977 | -252.9941
2040 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 303.593 | 0 | 0 | 0 | 0 | -151.7965
2041 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 0 | 0 | 0 | 0 | 0
2042 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 0 | 0 | 0 | 0 | 0
2043 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 0 | 0 | 0 | 0 | 0
2044 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 0 | 0 | 0 | 0 | 0
2045 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 0 | 0 | 0 | 0 | 0
2046 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 0 | 0 | 0 | 0 | 0
2047 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 0 | 0 | 0 | 0 | 0
2048 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 0 | 0 | 0 | 0 | 0
2049 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 0 | 0 | 0 | 0 | 0

## CumCapAdd Summary
Stakeholder Low Commodity Pricing Scenario |  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039
Case 3 | New Nat. Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
| New Solar (Nameplate) | 0 | 0 | 0 | 50.5988 | 202.3953 | 202.3953 | 202.3953 | 202.3953 | 202.3953 | 202.3953 | 303.593 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894
| New Solar (Firm) | 0 | 0 | 0 | 25.856 | 103.424 | 103.424 | 103.424 | 103.424 | 103.424 | 103.424 | 155.136 | 232.704 | 232.704 | 232.704 | 232.704 | 232.704 | 232.704 | 232.704 | 232.704 | 232.704
| New Wind (Nameplate) | 0 | 0 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| New Wind (Firm) | 0 | 0 | 0 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6
| New EE | 0 | 0 | 5.4533 | 10.7658 | 13.9293 | 12.6762 | 11.3298 | 10.0127 | 8.5597 | 6.9716 | 7.7179 | 9.1341 | 8.9889 | 8.332 | 6.8071 | 5.2743 | 3.9808 | 2.8581 | 2.2884 | 1.5044
| New VVO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7798 | 7.0496 | 7.0496 | 7.0496 | 7.0496 | 10.3337
| New DG | 0 | 0 | 0 | 1.022 | 1.533 | 1.533 | 1.533 | 2.044 | 2.044 | 2.555 | 3.066 | 3.577 | 3.577 | 4.088 | 4.599 | 4.599 | 5.11 | 5.11 | 5.621 | 5.621
| STMP | 0 | 0 | 150 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Reserves (MW) without new additions |  | 236.4698 | 232.3683 | -141.1961 | -141.4334 | -138.4928 | -135.6776 | -133.1769 | -131.7449 | -130.8116 | -130.9359 | -129.9619 | -391.8251 | -391.86 | -391.7211 | -392.4548 | -392.8648 | -393.9875 | -393.6911 | -394.2481 | -394.733
Capacity Reserves (MW) with new additions |  | 236.4698 | 232.3683 | 14.2572 | 20.8104 | 4.9935 | 6.5556 | 7.7099 | 8.3357 | 7.8161 | 6.6148 | 60.558 | 0.19006 | 0.0098577 | 0.0028857 | 1.0351 | 3.3622 | 1.4569 | 0.63061 | 0.014873 | 2.0301
Market Only-Low | New Nat. Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248
| New Solar (Nameplate) | 0 | 0 | 0 | 0 | 0 | 252.9941 | 252.9941 | 252.9941 | 252.9941 | 252.9941 | 252.9941 | 404.7906 | 404.7906 | 404.7906 | 404.7906 | 404.7906 | 404.7906 | 404.7906 | 404.7906 | 404.7906
| New Solar (Firm) | 0 | 0 | 0 | 0 | 0 | 129.28 | 129.28 | 129.28 | 129.28 | 129.28 | 129.28 | 206.848 | 206.848 | 206.848 | 206.848 | 206.848 | 206.848 | 206.848 | 206.848 | 206.848
| New Wind (Nameplate) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New Wind (Firm) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New EE | 0 | 0 | 0 | 0 | 0 | 4.9568 | 4.7759 | 4.2964 | 3.973 | 2.9898 | 3.1086 | 2.5143 | 1.9611 | 1.417 | 1.0407 | 0.69867 | 0.4366 | 0.22828 | 0.097081 | 0.020856
| New VVO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New DG | 0 | 0 | 0 | 1.022 | 1.533 | 1.533 | 1.533 | 2.044 | 2.044 | 2.555 | 3.066 | 3.577 | 3.577 | 4.088 | 4.599 | 4.599 | 5.11 | 5.11 | 5.621 | 5.621
| STMP | 0 | 0 | 150 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Reserves (MW) without new additions |  | 236.4698 | 232.3683 | -141.1961 | -141.4334 | -138.4928 | -135.6776 | -133.1769 | -131.7449 | -130.8116 | -130.9359 | -129.9619 | -391.8251 | -391.86 | -391.7211 | -392.4548 | -392.8648 | -393.9875 | -393.6911 | -394.2481 | -394.733
Capacity Reserves (MW) with new additions |  | 236.4698 | 232.3683 | 8.8039 | 9.5886 | 13.0402 | 0.092218 | 2.412 | 3.8755 | 4.4854 | 3.8889 | 5.4927 | 69.1142 | 68.5261 | 68.6318 | 68.0328 | 67.2809 | 66.4071 | 66.4952 | 66.318 | 65.7569
Solar + Wind-Low | New Nat. Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248
| New Solar (Nameplate) | 0 | 0 | 303.593 | 303.593 | 303.593 | 303.593 | 303.593 | 303.593 | 303.593 | 303.593 | 303.593 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894 | 455.3894
| New Solar (Firm) | 0 | 0 | 155.136 | 155.136 | 155.136 | 155.136 | 155.136 | 155.136 | 155.136 | 155.136 | 155.136 | 232.704 | 232.704 | 232.704 | 232.704 | 232.704 | 232.704 | 232.704 | 232.704 | 232.704
| New Wind (Nameplate) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New Wind (Firm) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New EE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New VVO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New DG | 0 | 0 | 0 | 1.022 | 1.533 | 1.533 | 1.533 | 2.044 | 2.044 | 2.555 | 3.066 | 3.577 | 3.577 | 4.088 | 4.599 | 4.599 | 5.11 | 5.11 | 5.621 | 5.621
| STMP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Reserves (MW) without new additions |  | 236.4698 | 232.3683 | -141.1961 | -141.4334 | -138.4928 | -135.6776 | -133.1769 | -131.7449 | -130.8116 | -130.9359 | -129.9619 | -391.8251 | -391.86 | -391.7211 | -392.4548 | -392.8648 | -393.9875 | -393.6911 | -394.2481 | -394.733
Capacity Reserves (MW) with new additions |  | 236.4698 | 232.3683 | 13.9399 | 14.7246 | 18.1762 | 20.9914 | 23.4921 | 25.4351 | 26.3684 | 26.7551 | 28.2401 | 92.4559 | 92.421 | 93.0709 | 92.8482 | 92.4382 | 91.8265 | 92.1229 | 92.0769 | 91.592
CT Only-Low | New Nat. Gas | 0 | 0 | 0 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248
| New Solar (Nameplate) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303.593 | 303.593 | 303.593 | 303.593 | 303.593 | 303.593 | 303.593 | 303.593 | 303.593
| New Solar (Firm) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155.136 | 155.136 | 155.136 | 155.136 | 155.136 | 155.136 | 155.136 | 155.136 | 155.136
| New Wind (Nameplate) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New Wind (Firm) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New EE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New VVO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New DG | 0 | 0 | 0 | 1.022 | 1.533 | 1.533 | 1.533 | 2.044 | 2.044 | 2.555 | 3.066 | 3.577 | 3.577 | 4.088 | 4.599 | 4.599 | 5.11 | 5.11 | 5.621 | 5.621
| STMP | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Reserves (MW) without new additions |  | 236.4698 | 232.3683 | -141.1961 | -141.4334 | -138.4928 | -135.6776 | -133.1769 | -131.7449 | -130.8116 | -130.9359 | -129.9619 | -391.8251 | -391.86 | -391.7211 | -392.4548 | -392.8648 | -393.9875 | -393.6911 | -394.2481 | -394.733
Capacity Reserves (MW) with new additions |  | 236.4698 | 232.3683 | 8.8039 | 107.5886 | 111.0402 | 113.8554 | 116.3561 | 118.2991 | 119.2324 | 119.6191 | 121.1041 | 14.8879 | 14.853 | 15.5029 | 15.2802 | 14.8702 | 14.2585 | 14.5549 | 14.5089 | 14.024
CC Only-Low | New Nat. Gas | 0 | 0 | 0 | 0 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401 | 401
| New Solar (Nameplate) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.7965 | 151.7965 | 151.7965 | 151.7965 | 151.7965 | 151.7965 | 151.7965 | 151.7965 | 151.7965
| New Solar (Firm) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.568 | 77.568 | 77.568 | 77.568 | 77.568 | 77.568 | 77.568 | 77.568 | 77.568
| New Wind (Nameplate) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New Wind (Firm) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New EE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New VVO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| New DG | 0 | 0 | 0 | 1.022 | 1.533 | 1.533 | 1.533 | 2.044 | 2.044 | 2.555 | 3.066 | 3.577 | 3.577 | 4.088 | 4.599 | 4.599 | 5.11 | 5.11 | 5.621 | 5.621
| STMP | 0 | 0 | 150 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Capacity Reserves (MW) without new additions |  | 236.4698 | 232.3683 | -141.1961 | -141.4334 | -138.4928 | -135.6776 | -133.1769 | -131.7449 | -130.8116 | -130.9359 | -129.9619 | -391.8251 | -391.86 | -391.7211 | -392.4548 | -392.8648 | -393.9875 | -393.6911 | -394.2481 | -394.733
Capacity Reserves (MW) with new additions |  | 236.4698 | 232.3683 | 8.8039 | 9.5886 | 264.0402 | 266.8554 | 269.3561 | 271.2991 | 272.2324 | 272.6191 | 274.1041 | 90.3199 | 90.285 | 90.9349 | 90.7122 | 90.3022 | 89.6905 | 89.9869 | 89.9409 | 89.456

## source (hidden)
27 | Nameplate Solar
Planning Peak Load (MW)
Required Generation Capacity (MW)
Firm Generation Capacity without New Additions (MW)
15 MW CHP Capacity (MW)
216 MW RICE Firm Capacity (MW)
256 MW (50% Share of 497 MW) GE 7F.05 Firm Capacity (MW)
325 MW (25% Share of 1,603 MW) M 501 JAC Firm Capacity (MW)
125 MW LM 6000 CT Firm Capacity (MW)
Big Sandy Site 216 MW RICE Firm Capacity (MW)
Big Sandy Site 256 MW (50% Share of 497 MW) GE 7F.05 Firm Capacity (MW)
Big Sandy Site 325 MW (25% Share of 1,603 MW) M 501 JAC Firm Capacity (MW)
Big Sandy Site Repower 443 MW Firm Capacity
Commercial DR Firm Capacity (MW)
Residential DR Firm Capacity (MW)
Commercial DSM Firm Capacity (MW)
Residential DSM Firm Capacity (MW)
Distributed Solar Firm Capacity (MW)
Utility Solar Firm Capacity (MW)
CVR Firm Capacity (MW)
Wind Firm Capacity (MW)
Short Term PPA Capacity (MW)
Firm Generation Capacity with New Additions (MW)
Capacity Reserves Above Required Generation without New Additions (MW)
Reserve Margin without New Capacity Additions (%)
Capacity Reserves Above Required Generation with New Capacity Additions (MW)
Reserve Margin with New Capacity Additions (%)
Nameplate Solar
Nameplate Wind