## Data
KY FAC Request
May 2019 - October 2019
Unit Name | Event Type | Month | Scheduled Hours | Forced Hours | Actual Hours | Event Duration | Event Start | Event End | Description
East Bend 2 | U1 | 2019-05-31 16:29 |  | 16.8833 | 16.8833 | 16.8833 | 2019-05-31 16:29 | 2019-06-01 09:22 | #4 Throttle Valve Actuator Failure
East Bend 2 | U1 | 2019-10-01 15:10 |  | 54.8333 | 54.8333 | 54.8333 | 2019-10-01 15:10 | 2019-10-03 22:00 | Condenser leak - chemistry issues
East Bend 2 | MO | 2019-10-03 22:00 | 938 |  | 938 | 938 | 2019-10-03 22:00 | 2019-11-12 | Turbine repairs
Woodsdale CT1 | U1 | 2019-05-29 14:57 |  | 4.25 | 4.25 | 4.25 | 2019-05-29 14:57 | 2019-05-29 19:12 | Automatic trip due to oil leak
Woodsdale CT1 | MO | 2019-06-14 06:00 | 8.95 |  | 8.95 | 8.95 | 2019-06-14 06:00 | 2019-06-14 14:57 | Install isolation valve & relocate Fuel Oil orafice
Woodsdale CT1 | PO | 2019-09-18 06:00 | 1492.95 |  | 1492.95 | 1492.95 | 2019-09-18 06:00 | 2019-11-19 10:57 | Generator upgrade
Woodsdale CT2 | PO | 2019-05-08 15:33 | 17.1333 |  | 17.1333 | 17.1333 | 2019-05-08 15:33 | 2019-05-09 08:41 | During burner inspection found damaged turbine blades
Woodsdale CT2 | PO | 2019-05-09 12:03 | 115.3 |  | 115.3 | 115.3 | 2019-05-09 12:03 | 2019-05-14 07:21 | During burner inspection found damaged turbine blades
Woodsdale CT2 | PO | 2019-05-14 16:21 | 89.5333 |  | 89.5333 | 89.5333 | 2019-05-14 16:21 | 2019-05-18 09:53 | During burner inspection found damaged turbine blades
Woodsdale CT2 | PO | 2019-05-18 11:09 | 74.3667 |  | 74.3667 | 74.3667 | 2019-05-18 11:09 | 2019-05-21 13:31 | During burner inspection found damaged turbine blades
Woodsdale CT2 | PO | 2019-05-21 14:06 | 44.2 |  | 44.2 | 44.2 | 2019-05-21 14:06 | 2019-05-23 10:18 | During burner inspection found damaged turbine blades
Woodsdale CT2 | PO | 2019-05-23 14:14 | 18.0167 |  | 18.0167 | 18.0167 | 2019-05-23 14:14 | 2019-05-24 08:15 | During burner inspection found damaged turbine blades
Woodsdale CT2 | MO | 2019-06-14 06:00 | 8.95 |  | 8.95 | 8.95 | 2019-06-14 06:00 | 2019-06-14 14:57 | Install isolation valve & relocate Fuel Oil orafice
Woodsdale CT3 | PO | 2019-05-26 14:54 | 14.15 |  | 14.15 | 14.15 | 2019-05-26 14:54 | 2019-05-27 05:03 | Fuel Oil Outage
Woodsdale CT3 | PO | 2019-05-27 08:57 | 5.4167 |  | 5.4167 | 5.4167 | 2019-05-27 08:57 | 2019-05-27 14:22 | Fuel Oil Outage
Woodsdale CT3 | PO | 2019-05-27 17:49 | 16.8833 |  | 16.8833 | 16.8833 | 2019-05-27 17:49 | 2019-05-28 10:42 | Fuel Oil Outage
Woodsdale CT3 | PO | 2019-05-28 19:06 | 36.5833 |  | 36.5833 | 36.5833 | 2019-05-28 19:06 | 2019-05-30 07:41 | Fuel Oil Outage
Woodsdale CT3 | PO | 2019-05-30 15:57 | 2.25 |  | 2.25 | 2.25 | 2019-05-30 15:57 | 2019-05-30 18:12 | Fuel Oil Outage
Woodsdale CT3 | MO | 2019-06-14 06:00 | 8.95 |  | 8.95 | 8.95 | 2019-06-14 06:00 | 2019-06-14 14:57 | Install isolation valve & relocate Fuel Oil orafice
Woodsdale CT3 | U1 | 2019-08-21 08:55 |  | 7.2667 | 7.2667 | 7.2667 | 2019-08-21 08:55 | 2019-08-21 16:11 | Fuel Oil Drain Valve Trouble
Woodsdale CT3 | PO | 2019-10-12 06:00 | 434.15 |  | 434.15 | 434.15 | 2019-10-12 06:00 | 2019-10-30 08:09 | SFC outage
Woodsdale CT4 | PO | 2019-05-20 16:32 | 163 |  | 163 | 163 | 2019-05-20 16:32 | 2019-05-27 11:32 | Fuel Oil Outage
Woodsdale CT4 | PO | 2019-05-27 11:46 | 78.0833 |  | 78.0833 | 78.0833 | 2019-05-27 11:46 | 2019-05-30 17:51 | Fuel Oil Outage
Woodsdale CT4 | PO | 2019-05-30 19:55 | 9.2667 |  | 9.2667 | 9.2667 | 2019-05-30 19:55 | 2019-05-31 05:11 | Fuel Oil Outage
Woodsdale CT4 | MO | 2019-06-13 06:00 | 5.0833 |  | 5.0833 | 5.0833 | 2019-06-13 06:00 | 2019-06-13 11:05 | Install isolation valve & relocate Fuel Oil orafice
Woodsdale CT4 | U1 | 2019-06-26 15:46 |  | 1.5667 | 1.5667 | 1.5667 | 2019-06-26 15:46 | 2019-06-26 17:20 | Operator Error
Woodsdale CT4 | U1 | 2019-07-02 11:30 |  | 5.25 | 5.25 | 5.25 | 2019-07-02 11:30 | 2019-07-02 16:45 | Took unit offline due to oil leak at fuel oil valve on top of combuster
Woodsdale CT4 | MO | 2019-08-22 10:22 | 31.6333 |  | 31.6333 | 31.6333 | 2019-08-22 10:22 | 2019-08-23 18:00 | Working on Moog Fuel Valves
Woodsdale CT4 | MO | 2019-09-08 06:00 | 8 |  | 8 | 8 | 2019-09-08 06:00 | 2019-09-08 14:00 | Change out Inlet Filters
Woodsdale CT4 | PO | 2019-09-21 06:00 | 1397.8833 |  | 1397.8833 | 1397.8833 | 2019-09-21 06:00 | 2019-11-18 11:53 | Begin U4 Compressor Outage
Woodsdale CT5 | PO | 2019-05-01 15:38 | 50.3333 |  | 50.3333 | 50.3333 | 2019-05-01 15:38 | 2019-05-03 17:58 | Fuel Oil Outage
Woodsdale CT5 | PO | 2019-05-03 18:06 | 20.7167 |  | 20.7167 | 20.7167 | 2019-05-03 18:06 | 2019-05-04 14:49 | Fuel Oil Outage
Woodsdale CT5 | PO | 2019-05-04 14:53 | 240.1833 |  | 240.1833 | 240.1833 | 2019-05-04 14:53 | 2019-05-14 15:04 | Fuel Oil Outage
Woodsdale CT5 | PO | 2019-05-14 16:00 | 15.4167 |  | 15.4167 | 15.4167 | 2019-05-14 16:00 | 2019-05-15 07:25 | Fuel Oil Outage
Woodsdale CT5 | PO | 2019-05-15 13:23 | 18.8333 |  | 18.8333 | 18.8333 | 2019-05-15 13:23 | 2019-05-16 08:13 | Fuel Oil Outage
Woodsdale CT5 | PO | 2019-05-16 16:52 | 21.4667 |  | 21.4667 | 21.4667 | 2019-05-16 16:52 | 2019-05-17 14:20 | Fuel Oil Outage
Woodsdale CT5 | PO | 2019-05-17 18:26 | 26.2333 |  | 26.2333 | 26.2333 | 2019-05-17 18:26 | 2019-05-18 20:40 | Fuel Oil Outage
Woodsdale CT5 | PO | 2019-05-18 22:08 | 58.1167 |  | 58.1167 | 58.1167 | 2019-05-18 22:08 | 2019-05-21 08:15 | Fuel Oil Outage
Woodsdale CT5 | PO | 2019-05-21 12:10 | 20.0167 |  | 20.0167 | 20.0167 | 2019-05-21 12:10 | 2019-05-22 08:11 | Fuel Oil Outage
Woodsdale CT5 | PO | 2019-05-22 08:13 | 9.05 |  | 9.05 | 9.05 | 2019-05-22 08:13 | 2019-05-22 17:16 | Fuel Oil Outage
Woodsdale CT5 | PO | 2019-05-22 17:55 | 13.3667 |  | 13.3667 | 13.3667 | 2019-05-22 17:55 | 2019-05-23 07:17 | Fuel Oil Outage
Woodsdale CT5 | MO | 2019-06-13 06:00 | 7.0667 |  | 7.0667 | 7.0667 | 2019-06-13 06:00 | 2019-06-13 13:04 | Install isolation valve & relocate Fuel Oil orafice
Woodsdale CT5 | MO | 2019-07-06 09:00 | 153.25 |  | 153.25 | 153.25 | 2019-07-06 09:00 | 2019-07-12 18:15 | Tagged TB41 to work on Unit 6
Woodsdale CT5 | MO | 2019-07-17 07:15 | 6.8333 |  | 6.8333 | 6.8333 | 2019-07-17 07:15 | 2019-07-17 14:05 | Tagged TB41 to work on Unit 6
Woodsdale CT5 | MO | 2019-08-22 10:22 | 9.2 |  | 9.2 | 9.2 | 2019-08-22 10:22 | 2019-08-22 19:34 | Working on Moog Fuel Valves
Woodsdale CT5 | MO | 2019-09-08 06:00 | 8 |  | 8 | 8 | 2019-09-08 06:00 | 2019-09-08 14:00 | Change out Inlet Filters
Woodsdale CT5 | PO | 2019-09-21 06:00 | 674 |  | 674 | 674 | 2019-09-21 06:00 | 2019-10-19 08:00 | SFC Outage
Woodsdale CT6 | PO | 2019-05-01 12:18 | 42.9667 |  | 42.9667 | 42.9667 | 2019-05-01 12:18 | 2019-05-03 07:16 | Fuel Oil Outage
Woodsdale CT6 | PO | 2019-05-03 17:08 | 19.5833 |  | 19.5833 | 19.5833 | 2019-05-03 17:08 | 2019-05-04 12:43 | Fuel Oil Outage
Woodsdale CT6 | PO | 2019-05-04 15:25 | 241.0833 |  | 241.0833 | 241.0833 | 2019-05-04 15:25 | 2019-05-14 16:30 | Fuel Oil Outage
Woodsdale CT6 | PO | 2019-05-14 17:17 | 18.1333 |  | 18.1333 | 18.1333 | 2019-05-14 17:17 | 2019-05-15 11:25 | Fuel Oil Outage
Woodsdale CT6 | PO | 2019-05-15 16:16 | 39.6333 |  | 39.6333 | 39.6333 | 2019-05-15 16:16 | 2019-05-17 07:54 | Fuel Oil Outage
Woodsdale CT6 | PO | 2019-05-17 16:39 | 64.85 |  | 64.85 | 64.85 | 2019-05-17 16:39 | 2019-05-20 09:30 | Fuel Oil Outage
Woodsdale CT6 | PO | 2019-05-20 13:31 | 42.25 |  | 42.25 | 42.25 | 2019-05-20 13:31 | 2019-05-22 07:46 | Fuel Oil Outage
Woodsdale CT6 | MO | 2019-06-13 06:00 | 7.0667 |  | 7.0667 | 7.0667 | 2019-06-13 06:00 | 2019-06-13 13:04 | Install isolation valve & relocate Fuel Oil orafice
Woodsdale CT6 | SF | 2019-06-19 08:27 |  | 4.95 | 4.95 | 4.95 | 2019-06-19 08:27 | 2019-06-19 13:24 | FLAME OUT
Woodsdale CT6 | U1 | 2019-07-02 13:12 |  | 360.8833 | 360.8833 | 360.8833 | 2019-07-02 13:12 | 2019-07-17 14:05 | Bus duct work failure, repaired
Woodsdale CT6 | MO | 2019-09-08 06:00 | 8 |  | 8 | 8 | 2019-09-08 06:00 | 2019-09-08 14:00 | Change out Inlet Filters
Woodsdale CT6 | U1 | 2019-09-10 22:09 |  | 2.7333 | 2.7333 | 2.7333 | 2019-09-10 22:09 | 2019-09-11 00:53 | 2nd stage NG reg problem
Woodsdale CT6 | PO | 2019-09-21 06:00 | 673.9333 |  | 673.9333 | 673.9333 | 2019-09-21 06:00 | 2019-10-19 07:56 | SFC outage
Event Type Legend:
PO | Planned Outage
PE | Planned Outage Extension
MO | Maintenance Outage
ME | Maintenance Outage Extension
U1 | Unplanned (Forced) Outage – Immediate
U2 | Unplanned (Forced) Outage – Delayed
U3 | Unplanned (Forced) Outage – Postponed
SF | Startup Failure