## Data
KY FAC Request
November 2019 - April 2020
Unit Name | Event Type | Month | Scheduled Hours | Forced Hours | Actual Hours | Event Duration | Event Start | Event End | Description
East Bend 2 | MO | 2019-11-12 | 240 |  | 240 | 240 | 2019-11-12 | 2019-11-22 | Additional LPT repairs - Added L-0 Blade Replacement
East Bend 2 | ME | 2019-11-22 | 64.7 |  | 64.7 | 64.7 | 2019-11-22 | 2019-11-24 16:42 | Replacement of L-0 Blades
East Bend 2 | U1 | 2019-11-24 17:12 |  | 9.567 | 9.567 | 9.567 | 2019-11-24 17:12 | 2019-11-25 02:46 | Unit trip due to vibration indication
East Bend 2 | U1 | 2019-11-26 09:50 |  | 3.833 | 3.833 | 3.833 | 2019-11-26 09:50 | 2019-11-26 13:40 | #1 Bearing vibration indication
East Bend 2 | U1 | 2020-03-02 10:20 |  | 15.7 | 15.7 | 15.7 | 2020-03-02 10:20 | 2020-03-03 02:02 | 2-1 BFP Recirc. Flange Leak
Woodsdale CT1 | MO | 2019-12-11 06:00 | 62 |  | 62 | 62 | 2019-12-11 06:00 | 2019-12-13 20:00 | Outage to install balance weights
Woodsdale CT1 | U1 | 2019-12-13 20:00 |  | 14.5 | 14.5 | 14.5 | 2019-12-13 20:00 | 2019-12-14 10:30 | Found ignition blowoff valve prox switch loose.
Woodsdale CT1 | PO | 2020-03-07 00:01 | 331.983 |  | 331.983 | 331.983 | 2020-03-07 00:01 | 2020-03-20 21:00 | Spring Prep and Boroscope Inspection
Woodsdale CT1 | U1 | 2020-03-26 14:55 |  | 2.25 | 2.25 | 2.25 | 2020-03-26 14:55 | 2020-03-26 17:10 | Emergency Sanitation at Station Covid 19
Woodsdale CT1 | PO | 2020-04-25 06:00 | 9.417 |  | 9.417 | 9.417 | 2020-04-25 06:00 | 2020-04-25 15:25 | Plant Blackstart; disconnected from grid
Woodsdale CT2 | PO | 2019-11-02 06:00 | 415.617 |  | 415.617 | 415.617 | 2019-11-02 06:00 | 2019-11-19 12:37 | SFC and synchronizer outage
Woodsdale CT2 | SF | 2019-12-12 06:40 |  | 1.867 | 1.867 | 1.867 | 2019-12-12 06:40 | 2019-12-12 08:32 | Main NG regulator failed
Woodsdale CT2 | PO | 2020-03-07 00:01 | 331.983 |  | 331.983 | 331.983 | 2020-03-07 00:01 | 2020-03-20 21:00 | Spring Prep and Boroscope Inspection
Woodsdale CT2 | U1 | 2020-03-26 14:55 |  | 2.25 | 2.25 | 2.25 | 2020-03-26 14:55 | 2020-03-26 17:10 | Emergency Sanitation at Station Covid 19
Woodsdale CT2 | PO | 2020-04-25 06:00 | 9.417 |  | 9.417 | 9.417 | 2020-04-25 06:00 | 2020-04-25 15:25 | Plant Blackstart; disconnected from grid
Woodsdale CT3 | U1 | 2019-11-12 06:08 |  | 5.867 | 5.867 | 5.867 | 2019-11-12 06:08 | 2019-11-12 12:00 | Gas pressure from Texas Eastern low
Woodsdale CT3 | U1 | 2019-11-13 06:55 |  | 7.083 | 7.083 | 7.083 | 2019-11-13 06:55 | 2019-11-13 14:00 | Gas pressure from Texas Eastern low
Woodsdale CT3 | SF | 2019-12-12 06:38 |  | 1.9 | 1.9 | 1.9 | 2019-12-12 06:38 | 2019-12-12 08:32 | Shut down 0648, gas reg not working
Woodsdale CT3 | PO | 2020-03-14 00:59 | 164.017 |  | 164.017 | 164.017 | 2020-03-14 00:59 | 2020-03-20 21:00 | Spring Prep and Boroscope Inspection
Woodsdale CT3 | U1 | 2020-03-26 14:55 |  | 2.25 | 2.25 | 2.25 | 2020-03-26 14:55 | 2020-03-26 17:10 | Emergency Sanitation at Station Covid 19
Woodsdale CT3 | PO | 2020-04-25 06:00 | 9.417 |  | 9.417 | 9.417 | 2020-04-25 06:00 | 2020-04-25 15:25 | Plant Blackstart; disconnected from grid
Woodsdale CT4 | U1 | 2019-11-18 12:08 |  | 2.35 | 2.35 | 2.35 | 2019-11-18 12:08 | 2019-11-18 14:29 | Gas pressure from Texas Eastern low
Woodsdale CT4 | U1 | 2019-12-12 06:48 |  | 1.733 | 1.733 | 1.733 | 2019-12-12 06:48 | 2019-12-12 08:32 | Tripped at 0648, gas reg not working
Woodsdale CT4 | PO | 2020-03-14 00:59 | 163.8 |  | 163.8 | 163.8 | 2020-03-14 00:59 | 2020-03-20 20:47 | Spring Prep and Boroscope Inspection
Woodsdale CT4 | U1 | 2020-03-26 14:55 |  | 2.25 | 2.25 | 2.25 | 2020-03-26 14:55 | 2020-03-26 17:10 | Emergency Sanitation at Station Covid 19
Woodsdale CT4 | PO | 2020-04-25 06:00 | 9.417 |  | 9.417 | 9.417 | 2020-04-25 06:00 | 2020-04-25 15:25 | Plant Blackstart; disconnected from grid
Woodsdale CT5 | U1 | 2019-11-12 06:18 |  | 5.7 | 5.7 | 5.7 | 2019-11-12 06:18 | 2019-11-12 12:00 | Gas pressure from Texas Eastern low
Woodsdale CT5 | SF | 2019-11-13 08:44 |  | 56.967 | 56.967 | 56.967 | 2019-11-13 08:44 | 2019-11-15 17:42 | SF6 Gas in Gen Breaker low
Woodsdale CT5 | PO | 2020-03-21 06:00 | 156.333 |  | 156.333 | 156.333 | 2020-03-21 06:00 | 2020-03-27 18:20 | Spring prep outage
Woodsdale CT5 | PO | 2020-04-25 06:00 | 9.417 |  | 9.417 | 9.417 | 2020-04-25 06:00 | 2020-04-25 15:25 | Plant Blackstart; disconnected from grid
Woodsdale CT6 | U1 | 2019-11-12 06:18 |  | 5.7 | 5.7 | 5.7 | 2019-11-12 06:18 | 2019-11-12 12:00 | Gas pressure from Texas Eastern low
Woodsdale CT6 | U1 | 2019-11-13 08:06 |  | 1 | 1 | 1 | 2019-11-13 08:06 | 2019-11-13 09:06 | Trip during transfer from NG to FO
Woodsdale CT6 | SF | 2019-12-12 06:33 |  | 1.983 | 1.983 | 1.983 | 2019-12-12 06:33 | 2019-12-12 08:32 | Main gas reg. not working
Woodsdale CT6 | SF | 2019-12-20 07:44 |  | 1 | 1 | 1 | 2019-12-20 07:44 | 2019-12-20 08:44 | High level in fuel/water pump
Woodsdale CT6 | PO | 2020-03-21 06:00 | 156.017 |  | 156.017 | 156.017 | 2020-03-21 06:00 | 2020-03-27 18:01 | Spring prep outage
Woodsdale CT6 | U1 | 2020-04-07 06:00 |  | 76.767 | 76.767 | 76.767 | 2020-04-07 06:00 | 2020-04-10 10:46 | Automatic Voltage Regulator Failure
Woodsdale CT6 | PO | 2020-04-25 06:00 | 9.417 |  | 9.417 | 9.417 | 2020-04-25 06:00 | 2020-04-25 15:25 | Plant Blackstart; disconnected from grid
Event Type Legend:
PO | Planned Outage
PE | Planned Outage Extension
MO | Maintenance Outage
ME | Maintenance Outage Extension
U1 | Unplanned (Forced) Outage – Immediate
U2 | Unplanned (Forced) Outage – Delayed
U3 | Unplanned (Forced) Outage – Postponed
SF | Startup Failure