## Sheet1
Company | Facility Name | County | Type | Permit/PWS # | Recent DMR Compliance | Issue | Construction Permit Pending | Construction Permit Improvements | Additional Improvments Pending | Should AOC Coverage continue
Airview | Airview | Hardin | wastewater | KY0045390 | Some continued exceedance | ammonia and TSS (brought down with resample) | yes | Convert lagoon to wet weather storage | Clearing berms of lagoon, installing pumping equipment for wet weather storage in lagoon | yes
Brocklyn | Brocklyn | Madison | wastewater | KY0081299 | Meeting limits | plant deteriorating beyond repair, plant replacement in permitting, exploring municiple connection option for permit approval | yes | plant replacement | The State required us to coordinate with municipality for connecting and taking plant offline. We are currently flow monitoring per municipality request in order for municipality to see if they can take flow and improvements necessary. | yes
Fox Run | Fox Run | Franklin | wastewater | KY0086967 | Meeting limits |  | yes | Flow eq and digestor |  | yes
Marshall Co. Env. | Golden Acres | Marshall | wastewater | KY0044164 | Some continued exceedance | Issues with TRC and DO, air to be added to Effluent Chamber, and add peracetic acid disinfection | yes | rebuild effluent pipe (larger size eliminate turns), add peracetic acid disinfection |  | yes
Marshall Co. Env. | Great Oaks | McCracken | wastewater | KY0080845 | Some continued exceedance | TRC, BOD. Dosing being adjusted | yes | digestor and flow eq |  | yes
Kingswood | Kingswood | Bullitt | wastewater | KY0101419 | Meeting limits |  | No |  |  | Probably can remove | This UV unit is operating at 2/3 capacity. Parts are no longer available since the unit has been discontinued. We decided to not include in the budget a replacement unit but we might have issues when I and I becomes an issue in the spring.
Lake Columbia | Lake Columbia | Bullitt | wastewater | KY0077674 | Meeting limits |  | yes | digestor flow eq |  | Yes
LH Treatment | LH | Scott | wastewater | KY0081591 | Some continued exceedance | E.Coli, pin floc issue, working to resolve | No |  |  | Probably can remove | We don't have much in budget for I and I. But, I and I is really our only problem. Slams the plant when it rains, but otherwise we meet limits.
Persimmon Ridge | Persimmon Ridge | Shelby | wastewater | KY0090956 | Meeting limits | Ammonia in winter. Have repaired baffle and aeration system. Has improved effluent but neet to evaluate through the winter. | No |  |  | yes | Ammonia levels have improved but I feel like we are going to have an issue in January through March on meeting limits. I'd like to leave on through first winter
Center Ridge WD | Water System | Calloway | water | KY0180549
Center Ridge WD | District #2 | Calloway | water | KY0180509
Center Ridge WD | District #3 | Calloway | water | KY0180502
Center Ridge WD | District #4 | Calloway | water | KY0183106
River Bluffs | River Bluffs | Oldham | wastewater | KY0043150 | Mostly meeting limits | exceedances have realated to improvments work, aeration system replacement. Mostly still meeting limits |  |  | Continued Aeration system repair and steel repair | Yes
Joann Estates | Timberland | McCracken | wastewater | KY0083755 | Some continued exceedance | TRC, DO, and Ammonia exceedances, continued rehab work: berms have been cleared of vegetation and repaired, regrading and reworked yard piping to improve, lift station repairs | Yes | Convert old plant to MBBR, convert lagoon to flow eq, add peracetic acid disinfection |  | Yes
Delaplain Disposal | Delaplain Disposal | Scott | wastewater | KY0079049 | Not closed
Herrington Haven | Herrington Haven | Garrard | wastewater | KY0053431 | Not closed
Woodland Acres | Woodland Acres | Bullitt | wastewater | KY0091600 | Not closed

## BG-Airview
BG - Airview - NPDES KY0045390 | [9 empty] | BG - Airview - NPDES KY0045390 |  |  | OH - Oak Tree - NPDES AR0050792
Testing Documentation | [9 empty] | Permit Limits |  |  | Regulatory Compliance
Test Type | Test Period Start Date | Test Period End Date | Sample Date | Date Received | Result | Limit | Compliance | Notes | Enforcement Status | Paramater | Limit | Frequency | Type | Date | Parameter | Test Result | Limit | Corrective Action | Notes | Compliance Deadline | Date Resolved | File Name
Flow | 2019-09-23 | 2019-09-27 | 2019-09-27 |  |  | Monitor Only |  |  |  | Flow | Monitor Only | 1/Week | KY EEC AO 09/03/19
pH | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | 5.8 | 6.0-9.0 | No |  | Under AO. | pH | 6.0-9.0 | 1/Week | CAP 01/28/20
CBOD5 (Monthly Avg lbs./Day) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | N/A | <11.5 lbs/day |  |  |  | CBOD5 (Monthly Avg lbs./Day) | <11.5 lbs/day | 1/Week | CAP NFA submitted 06/30/20
CBOD5 (Daily Max lbs/day) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | N/A | <17.25 lbs/day |  |  |  | CBOD5 (Daily Max lbs/day) | <17.25 lbs/day | 1/Week
CBOD5 (Monthly Avg mg/L) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | 18 | <25 mg/L | Yes |  |  | CBOD5 (Monthly Avg mg/L) | <25 mg/L | 1/Week
CBOD5 (Daily Max mg/L) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | 18 | <37.5 mg/L | Yes |  |  | CBOD5 (Daily Max mg/L) | <37.5 mg/L | 1/Week
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | N/A | <13.8 lbs/day |  |  |  | Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | <13.8 lbs/day | 1/Week
Total Suspened Solids(TSS) (Daily Max lbs/day) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | N/A | <20.7 lbs/day |  |  |  | Total Suspened Solids(TSS) (Daily Max lbs/day) | <20.7 lbs/day | 1/Week
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | 20 | <30 mg/L | Yes |  |  | Total Suspened Solids(TSS) (Monthly Avg mg/L) | <30 mg/L | 1/Week
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | 20 | <45 mg/L | Yes |  |  | Total Suspened Solids(TSS) (Daily Max mg/L) | <45 mg/L | 1/Week
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | N/A | <1.84 lbs/day |  |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | <1.84 lbs/day | 1/Week
Ammonia (as mg/L NH3N) May1-Oct 31 (Daily Max lbs/day) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | N/A | <2.76 lbs/day |  |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Daily Max lbs/day) | <2.76 lbs/day | 1/Week
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | 0.9 | <4.0 mg/L | Yes |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | <4.0 mg/L | 1/Week
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | 0.9 | <6.0 mg/L | Yes |  |  | Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | <6.0 mg/L | 1/Week
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | N/A | <4.6 lbs/day |  |  |  | Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | <4.6 lbs/day | 1/Week
Ammonia Nov 1-April 30 (Daily Max lbs/day) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | N/A | <6.9 lbs/day |  |  |  | Ammonia Nov 1-April 30 (Daily Max lbs/day) | <6.9 lbs/day | 1/Week
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | N/A | <10.0 mg/L |  |  |  | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | <10.0 mg/L | 1/Week
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | N/A | <15.0 mg/L |  |  |  | Ammonia Nov 1-April 30 (Daily Max mg/L) | <15.0 mg/L | 1/Week
Dissolved Oxygen (DO) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | 6.2 | >7.0 | No |  | Under AO. | Dissolved Oxygen (DO) | >7.0 | 1/Week
E. Coli (Monthly Avg) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | 60000 | <130 #/100mL | No |  | Under AO. | E. Coli (Monthly Avg) | <130 #/100mL | 1/Week
E. Coli (Weekly Avg) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | 60000 | <240 #100mL | No |  | Under AO. | E. Coli (Weekly Avg) | <240 #100mL | 1/Week
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | 0.07 | <0.011mg/L | No |  | Under AO. | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | <0.011mg/L | 1/Week
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-09-23 | 2019-09-27 | 2019-09-27 |  | 0.07 | <0.019 mg/L | No |  | Under AO. | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | <0.019 mg/L | 1/Week
Flow | 2019-10-01 | 2019-10-04 | 2019-10-04 |  |  | Monitor Only
pH | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | 7.4 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | 9 | <25 mg/L | Yes |  |  | Permit change: Monthly - effective May 1, 2020
CBOD5 (Daily Max mg/L) | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | 9 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | 29 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | 29 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | 1.8 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | 1.8 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | N/A | <10.0 mg/L
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | N/A | <15.0 mg/L
Dissolved Oxygen (DO) | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | 7.2 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | 16 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | 16 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-04 | 2019-10-04 |  | 0.01 | <0.019 mg/L | Yes
Flow | 2019-10-05 | 2019-10-11 | 2019-10-11 |  |  | Monitor Only
pH | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | 7.55 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | 15 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | 15 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | N/A | <13.8 lbs/day
Total Suspened Solids(TSS) (Daily Max lbs/day) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | N/A | <20.7 lbs/day
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | 60 | <30 mg/L | No |  | Under AO.
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | 60 | <45 mg/L | No |  | Under AO.
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | 1.4 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | 1.4 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | N/A | <10.0 mg/L
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | N/A | <15.0 mg/L
Dissolved Oxygen (DO) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | 8.9 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | 60000 | <130 #/100mL | No |  | Under AO.
E. Coli (Weekly Avg) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | 60000 | <240 #100mL | No |  | Under AO.
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | 0.13 | <0.011mg/L | No |  | Under AO.
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-05 | 2019-10-11 | 2019-10-11 |  | 0.13 | <0.019 mg/L | No |  | Under AO.
Flow | 2019-10-12 | 2019-10-18 | 2019-10-18 |  |  | Monitor Only
pH | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | 7.64 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | 8 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | 8 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | 18 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | 18 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | 0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | 0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | N/A | <10.0 mg/L
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | N/A | <15.0 mg/L
Dissolved Oxygen (DO) | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | 8.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | 69 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | 69 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | 1.78 | <0.011mg/L | No |  | Under AO.
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-12 | 2019-10-18 | 2019-10-18 |  | 1.78 | <0.019 mg/L | No |  | Under AO.
Flow | 2019-10-19 | 2019-10-25 | 2019-10-25 |  |  | Monitor Only
pH | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | 7.53 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | 13 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | 13 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | 47 | <30 mg/L | No |  | Under AO.
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | 47 | <45 mg/L | No |  | Under AO.
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | 0.4 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | 0.4 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | N/A | <10.0 mg/L
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | N/A | <15.0 mg/L
Dissolved Oxygen (DO) | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | 7.6 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | 1414 | <130 #/100mL | No |  | Under AO.
E. Coli (Weekly Avg) | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | 1414 | <240 #100mL | No |  | Under AO.
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-19 | 2019-10-25 | 2019-10-25 |  | 0.01 | <0.019 mg/L | Yes
Flow | 2019-10-26 | 2019-11-01 | 2019-11-01 |  |  | Monitor Only
pH | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 8.1 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 6 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 6 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 48 | <30 mg/L | No |  | Under AO.
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 48 | <45 mg/L | No |  | Under AO.
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 8.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 1987 | <130 #/100mL | No |  | Under AO.
E. Coli (Weekly Avg) | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 1987 | <240 #100mL | No |  | Under AO.
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-26 | 2019-11-01 | 2019-11-01 |  | 0.01 | <0.019 mg/L | Yes
Flow | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | 0.068 | Monitor Only
pH | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | 7.97 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | 5 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | 5 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | 0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | 0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | 8.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | 37 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | 37 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-11-02 | 2019-11-08 | 2019-11-08 |  | 0.01 | <0.019 mg/L | Yes
Flow | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | 0.068 | Monitor Only
pH | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | 8.11 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | 14 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | 14 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | 19 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | 19 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | 0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | 0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | 9.8 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | 118 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | 118 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-11-09 | 2019-11-15 | 2019-11-15 |  | 0.01 | <0.019 mg/L | yes
Flow | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | 0.068 | Monitor Only
pH | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | 8.1 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | 5 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | 5 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | 1 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | 1 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | 12.6 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | 24 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | 24 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-11-16 | 2019-11-22 | 2019-11-20 | 2019-12-02 | 0.01 | <0.019 mg/L | Yes
Flow | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | 0.068 | Monitor Only
pH | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | 7.81 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | 4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | 4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | 0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | 0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | 10.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | 33 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | 33 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-11-23 | 2019-11-29 | 2019-11-26 | 2019-12-04 | 0.01 | <0.019 mg/L | Yes
Flow | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | 0.048 | Monitor Only
pH | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | 7.34 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | 13 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | 13 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | 19 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | 19 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | 0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | 0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | 10.5 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | 1203 | <130 #/100mL | No |  | Under AO.
E. Coli (Weekly Avg) | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | 1203 | <240 #100mL | No |  | Under AO.
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-11-30 | 2019-12-06 | 2019-12-06 | 2019-12-13 | 0.01 | <0.019 mg/L | Yes
Flow | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | 0.048 | Monitor Only
pH | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | 8.1 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | 31 | <25 mg/L | No |  | Under AO.
CBOD5 (Daily Max mg/L) | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | 31 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | 0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | 0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | 11.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | 1414 | <130 #/100mL | No |  | Under AO.
E. Coli (Weekly Avg) | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | 1414 | <240 #100mL | No |  | Under AO.
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-12-07 | 2019-12-13 | 2019-12-13 | 2019-12-20 | 0.01 | <0.019 mg/L | Yes
Flow | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | 0.048 | Monitor Only
pH | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | 7.56 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | 15 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | 15 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | 41 | <30 mg/L | No |  | Under AO.
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | 41 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | 0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | 0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | 11.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | 60000 | <130 #/100mL | No |  | Under AO.
E. Coli (Weekly Avg) | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | 60000 | <240 #100mL | No |  | Under AO.
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-12-14 | 2019-12-20 | 2019-12-20 | 2019-01-03 | 0.01 | <0.019 mg/L | Yes
Flow | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | 0.048 | Monitor Only
pH | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | 7.56 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | 4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | 4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | 0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | 0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | 10.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | 3 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | 3 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-12-21 | 2019-12-27 | 2019-12-27 | 2020-01-03 | 0.01 | <0.019 mg/L | Yes
Flow | 2019-12-28 | 2020-01-03 |  |  |  | Monitor Only
pH | 2019-12-28 | 2020-01-03 |  |  |  | 6.0-9.0
CBOD5 (Monthly Avg mg/L) | 2019-12-28 | 2020-01-03 |  |  |  | <25 mg/L
CBOD5 (Daily Max mg/L) | 2019-12-28 | 2020-01-03 |  |  |  | <37.5 mg/L
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-12-28 | 2020-01-03 |  |  |  | <30 mg/L
Total Suspened Solids(TSS) (Daily Max mg/L) | 2019-12-28 | 2020-01-03 |  |  |  | <45 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-12-28 | 2020-01-03 |  |  | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2019-12-28 | 2020-01-03 |  |  | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-12-28 | 2020-01-03 |  |  |  | <10.0 mg/L
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2019-12-28 | 2020-01-03 |  |  |  | <15.0 mg/L
Dissolved Oxygen (DO) | 2019-12-28 | 2020-01-03 |  |  |  | >7.0
E. Coli (Monthly Avg) | 2019-12-28 | 2020-01-03 |  |  |  | <130 #/100mL
E. Coli (Weekly Avg) | 2019-12-28 | 2020-01-03 |  |  |  | <240 #100mL
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-12-28 | 2020-01-03 |  |  |  | <0.011mg/L
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-12-28 | 2020-01-03 |  |  |  | <0.019 mg/L
Flow | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.048 | Monitor Only
pH | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 8.43 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 8 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 0.048 | Monitor Only
pH | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 7.53 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 8.7 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 3 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 3 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | 0.048 | Monitor Only
pH | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | 7.26 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | 9 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | 9 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | 1.6 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | 1.6 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | 10.9 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | 1120 | <130 #/100mL | No |  | Under AO.
E. Coli (Weekly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | 1120 | <240 #100mL | No |  | Under AO.
E. Coli (Monthly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-28 | 2020-02-05 | 12 | <130 #/100mL | Yes | Resample for above for AO
E. Coli (Weekly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-28 | 2020-02-05 | 12 | <240 #100mL | Yes | Resample for above for AO
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-24 | 2020-02-05 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | 0.048 | Monitor Only
pH | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | 7.5 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | 7 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | 7 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | 0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | 0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | 9.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-31 | 2020-02-07 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-02-01 | 2020-02-29 | 2020-02-04 | 2020-02-13 | 0.047 | Monitor Only
pH | 2020-02-01 | 2020-02-29 | 2020-02-04 | 2020-02-13 | 7.37 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-04 | 2020-02-13 | 6 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-04 | 2020-02-13 | 6 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-04 | 2020-02-13 | 9 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-04 | 2020-02-13 | 9 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-04 | 2020-02-13 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-04 | 2020-02-13 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-04 | 2020-02-13 | <0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-04 | 2020-02-13 | <0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-02-01 | 2020-02-29 | 2020-02-04 | 2020-02-13 | 8.9 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-03 | 2020-02-13 | 17 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-03 | 2020-02-13 | 17 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-04 | 2020-02-13 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-04 | 2020-02-13 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | 0.047 | Monitor Only
pH | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | 7.92 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | <0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | <0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | 10.7 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | 6 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | 6 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-09 | 2020-02-18 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 0.047 | Monitor Only
pH | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 8.33 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | <0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | <0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 10.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 3 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 3 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | 0.047 | Monitor Only
pH | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | 7.87 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | 9 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | 9 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | 17 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | 17 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | <0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | <0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | 12.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | 57 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | 57 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-09 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | 0.048 | Monitor Only
pH | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | 7.81 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | 10 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | 10 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | 65 | <30 mg/L | No |  | Under AO.
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | 65 | <45 mg/L | No |  | Under AO.
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | 1 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | 1 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | 9.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | 60000 | <130 #/100mL | No |  | Under AO.
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | 60000 | <240 #100mL | No |  | Under AO.
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-11 | 22 | <130 #/100mL | Yes | Resample for above for AO
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-11 | 22 | <240 #100mL | Yes | Resample for above for AO
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-02 | 2020-03-11 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 0.048 | Monitor Only
pH | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 6.87 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 11 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 11 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 39 | <30 mg/L | No
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 39 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | <0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | <0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 8 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 238 | <130 #/100mL | No | Contact chamber began to float sludge from the bottom of the tank. Trash pump was used to clean it and aeration line was added. | Under AO.
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 238 | <240 #100mL | Yes
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-12 | 2020-03-19 | 11 | <130 #/100mL | Yes | Resample for above
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-12 | 2020-03-19 | 11 | <240 #100mL | Yes | Resample for above
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 0.048 | Monitor Only
pH | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 7.19 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | <0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | <0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 9.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | 0.048 | Monitor Only
pH | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | 7.01 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | 11 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | 11 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | <0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | <0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | 10.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | 60000 | <130 #/100mL | No |  | Under AO.
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | 60000 | <240 #100mL | No |  | Under AO.
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-26 | 2020-03-31 | 167 | <130 #/100mL | No | Resample for above for AO | Under AO.
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-26 | 2020-03-31 | 167 | <240 #100mL | Yes | Resample for above for AO
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-26 | 2020-03-31 | 143 | <130 #/100mL | No | Resample for above for AO | Under AO.
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-26 | 2020-03-31 | 143 | <240 #100mL | Yes | Resample for above for AO
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-27 | 2020-03-31 | <1 | <130 #/100mL | Yes | Resample for above for AO
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-27 | 2020-03-31 | <1 | <240 #100mL | Yes | Resample for above for AO
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-24 | 2020-03-31 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 0.048 | Monitor Only
pH | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 7.12 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 5 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 5 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 7 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 7 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 0.3 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 0.3 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 10.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 117 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 117 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 0.048 | Monitor Only
pH | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 7.12 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 13 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 13 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 22 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 22 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | <0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | <0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 8.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 43 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 43 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 0.048 | Monitor Only
pH | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 7.81 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | <0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | <0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 11.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 5 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 5 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | 0.048 | Monitor Only
pH | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | 6.92 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | 4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | 4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | 6.9 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | 6.9 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | 9.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | 11 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | 11 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-24 | 2020-04-30 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | 0.171 | Monitor Only
pH | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | 7.6 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | 7 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | 7 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | 34 | <30 mg/L | No | Facility was off several times for maintenance and repairs. | Under AO.
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | 34 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | 0.3 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | 0.3 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | 9.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | 60000 | <130 #/100mL | No |  | Under AO.
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | 60000 | <240 #100mL | No |  | Under AO.
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-07 | 2020-05-11 | 2 | <130 #/100mL | Yes | Resample for above for AO
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-07 | 2020-05-11 | 2 | <240 #100mL | Yes | Resample for above for AO
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-05 | 2020-05-12 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | 0.171 | Monitor Only
pH | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | 8 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | 10.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | 3 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | 3 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-20 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | 0.171 | Monitor Only
pH | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | 7.21 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | 10.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | 21 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | 21 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-19 | 2020-05-27 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 0.171 | Monitor Only
pH | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 7.14 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 8.42 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 30 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 30 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | <0.01 | <0.019 mg/L | Yes
Flow | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 |  | Monitor Only
pH | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | 7.61 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | 7.9 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | 3 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | 3 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-03 | 2020-06-09 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 |  | Monitor Only
pH | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | 7.81 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | 10 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | 10 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | 9.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | 13 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | 13 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-16 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 |  | Monitor Only
pH | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | 7.28 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | 8 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | 8 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | 16 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | 16 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | 7.2 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | 276 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | 276 | <240 #100mL | No | The plant was experiencing a little bit of bulking in the clarifier. The cl2, although adequate under normal circumstances, may not have been enough to account for the elevated suspended solids. Additional sample was taken. See below. | Under AO. AO/CAP NFA LTR Submitted 06/30/20.
E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-23 | 32 | <130 #/100mL | Yes | Resample for above
E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-23 | 32 | <240 #100mL | Yes | Resample for above
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-16 | 2020-06-23 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | 0.039 | Monitor Only
pH | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | 7.27 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | 9 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | 9 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | 21 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | 21 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | 9.2 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | 42 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | 42 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-06-30 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 |  | Monitor Only
pH | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | 7.61 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | 9.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | 2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | 2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-02 | 2020-07-13 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 |  | Monitor Only
pH | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 7.14 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 5 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 5 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 9 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 9 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 6.6 | <4.0 mg/L | No | Airveiw was off due to hight flow on 7/12 and was just recovering when the blower motor quit working on 7/14. It was repaired on 7/15 but did not have enough recovery time when the sample was taken on 7/16. High ammonia was likely due to low DO and washing. The blowers and motors are old and in need of rebuild or replacement. They are on the schedule for rebuild or replacement ASAP.
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 6.6 | <6.0 mg/L | No | Airveiw was off due to hight flow on 7/12 and was just recovering when the blower motor quit working on 7/14. It was repaired on 7/15 but did not have enough recovery time when the sample was taken on 7/16. High ammonia was likely due to low DO and washing. The blowers and motors are old and in need of rebuild or replacement. They are on the schedule for rebuild or replacement ASAP.
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 9.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | 0.044 | Monitor Only
pH | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | 7.48 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | 8.2 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-23 | 2020-07-30 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | 0.348 | Monitor Only
pH | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | 7.28 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | 7.04 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | 2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | 2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-04 | 2020-08-11 | <0.01 | <0.019 mg/L | Yes
Flow | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | 0.041 | Monitor Only
pH | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | 7.91 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | 8.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | 3 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | 3 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-08 | 2020-09-22 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 0.025 | Monitor Only
pH | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 7.76 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 12 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 12 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 1.1 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 1.1 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 9.2 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-28 | 2020-10-30 | 6 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-28 | 2020-10-30 | 6 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 |  | Monitor Only
pH | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | 6.81 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | <4 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | <4 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | 16.1 | <10.0 mg/L | No | High ammonia was due to low DO at the plant. The DO was low because the plant was running on only one blower due to mechanical failure. The ammonia level returned to acceptable range within 24 hours after the repairs were completed.
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | 16.1 | <15.0 mg/L | No | High ammonia was due to low DO at the plant. The DO was low because the plant was running on only one blower due to mechanical failure. The ammonia level returned to acceptable range within 24 hours after the repairs were completed.
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-17 |  | <0.2 | <10.0 mg/L | Yes | Resample for above
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-17 |  | <0.2 | <15.0 mg/L | Yes | Resample for above
Dissolved Oxygen (DO) | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | 7.31 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | 6 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | 6 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-10 | 2020-11-18 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 |  | Monitor Only
pH | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | 6.91 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | 20 | <25 mg/L | Yes
CBOD5 (Daily Max mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | 20 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | 44 | <30 mg/L | No | Had a 1 3/4" rain event that caused high flow with some washout and elevated pH. the contact chamber has been cleaned and all though the TSS is outside the monthly limit, it is within the weekly limit. The operator has contacted the lab about taking additional samples to lower the monthly average.
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | 44 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-22 | 2021-01-05 | 12 | <30 mg/L | Yes | Resample for above
Total Suspened Solids(TSS) (Daily Max mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-22 | 2021-01-05 | 12 | <45 mg/L | Yes | Resample for above
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Daily Max mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | 0.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Daily Max mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | 0.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | 8.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | 47 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | 47 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-15 | 0.01 | <0.019 mg/L | Yes

## BG-Brocklyn
BG - Brocklyn - NPDES KY0081299 | [8 empty] | BG - Brocklyn - NPDES KY0081299 |  |  | BG - Brocklyn - NPDES KY0081299
Testing Documentation | [8 empty] | Permit Limits |  |  | Regulatory Compliance
Test Type | Test Period Start Date | Test Period End Date | Sample Date | Date Received | Result | Limit | Compliance | Notes | Paramater | Limit | Frequency | Type | Date | Parameter | Test Result | Limit | Corrective Action | Notes | Compliance Deadline | Date Resolved | File Name
Flow | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 0.019 | Monitor Only |  |  | Flow | Monitor Only | 1/Month | KY EEC AO dated 9/3/19
pH | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 7.25 | 6.0-9.0 | Yes |  | pH | 6.0-9.0 | 1/Month | KY EEC CAP dated 12/13/19
CBOD5 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <3.34 lbs/day |  |  | CBOD5 (Monthly Avg lbs./Day) | <3.34 lbs/day | 1/Month
CBOD5 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <5.0 lbs/day |  |  | CBOD5 (Weekly Avg lbs/day) | <5.0 lbs/day | 1/Month
CBOD5 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 11 | <10 mg/L | No |  | CBOD5 (Monthly Avg mg/L) | <10 mg/L | 1/Month
CBOD5 (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 11 | <15 mg/L | Yes |  | CBOD5 (Weekly Avg mg/L) | <15 mg/L | 1/Month | yes
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <10.0 lbs/day |  |  | Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | <10.0 lbs/day | 1/Month
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <15.0 lbs/day |  |  | Total Suspened Solids(TSS) (Weekly Avg lbs/day) | <15.0 lbs/day | 1/Month
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 8 | <30 mg/L | Yes |  | Total Suspened Solids(TSS) (Monthly Avg mg/L) | <30 mg/L | 1/Month
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 8 | <45 mg/L | Yes |  | Total Suspened Solids(TSS) (Weekly Avg mg/L) | <45 mg/L | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <0.67 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | <0.67 lbs/day | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <1.0 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | <1.0 lbs/day | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 2.7 | <2.0 mg/L | No |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | <2.0 mg/L | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 2.7 | <3.0 mg/L | Yes |  | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | <3.0 mg/L | 1/Month
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <1.67 lbs/day |  |  | Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | <1.67 lbs/day | 1/Month
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <2.5 lbs/day |  |  | Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | <2.5 lbs/day | 1/Month
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <5.0 mg/L |  |  | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | <5.0 mg/L | 1/Month
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <7.5 mg/L |  |  | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | <7.5 mg/L | 1/Month
Dissolved Oxygen (DO) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 7 | >7.0 | Y/N |  | Dissolved Oxygen (DO) | >7.0 | 1/Month
E. Coli (Monthly Avg) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 60000 | <130 #/100mL | No |  | E. Coli (Monthly Avg) | <130 #/100mL | 1/Month
E. Coli (Weekly Avg) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 60000 | <240 #100mL | No |  | E. Coli (Weekly Avg) | <240 #100mL | 1/Month
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 0.01 | <0.011mg/L | Yes |  | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | <0.011mg/L | 1/Month
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 0.01 | <0.019 mg/L | Yes |  | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | <0.019 mg/L | 1/Month
Flow | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.046 | Monitor Only
pH | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 7.14 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <3.34 lbs/day
CBOD5 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <5.0 lbs/day
CBOD5 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 6 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 6 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <10.0 lbs/day
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <15.0 lbs/day
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 19 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 19 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <0.67 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <1.0 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.2 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.2 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <1.67 lbs/day
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <2.5 lbs/day
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <5.0 mg/L
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <7.5 mg/L
Dissolved Oxygen (DO) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 6.75 | >7.0 | No
E. Coli (Monthly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 291 | <130 #/100mL | No
E. Coli (Weekly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 291 | <240 #100mL | No
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.01 | <0.019 mg/L | Yes
Flow | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 0.043 | Monitor Only
pH | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 7.86 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <3.34 lbs/day
CBOD5 (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <5.0 lbs/day
CBOD5 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <10.0 lbs/day
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <15.0 lbs/day
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <0.67 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <1.0 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <2.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <3.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <1.67 lbs/day
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <2.5 lbs/day
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 1.3 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 1.3 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 9.7 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 0.01 | <0.019 mg/L | Yes
Flow | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.043 | Monitor Only
pH | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 7.73 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 8 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 8 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 16 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 16 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.4 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.4 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 7.76 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 4 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 4 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-02-17 | 0.036 | Monitor Only
pH | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 7.64 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.2 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.2 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 7.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 0.043 | Monitor Only
pH | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 7.79 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <6.00 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <6.00 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <0.2 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <0.2 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 8.59 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 0.036 | Monitor Only
pH | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 7.83 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 12 | <10 mg/L | No | I&I - rain event causes the plant to lose the proper F to M ratio which in turn causes bad test results
CBOD5 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 12 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 34 | <30 mg/L | No | I&I - rain event causes the plant to lose the proper F to M ratio which in turn causes bad test results
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 34 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 0.2 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 0.2 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | 8.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 |  | <130 #/100mL
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 |  | <240 #100mL
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-17 | 2020-03-26 | <0.01 | <0.019 mg/L | Yes
Flow | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 0.036 | Monitor Only
pH | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 7.93 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 12 | <10 mg/L | No | I&I - rain event causes the plant to lose the proper F to M ratio which in turn causes bad test results
CBOD5 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 12 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 108 | <30 mg/L | No | I&I - rain event causes the plant to lose the proper F to M ratio which in turn causes bad test results
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 108 | <45 mg/L | No | I&I - rain event causes the plant to lose the proper F to M ratio which in turn causes bad test results
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 3 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 3 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 7.8 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 17 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 17 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 0.048 | Monitor Only
pH | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 7.78 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 16 | <10 mg/L | No | Excessive rainfall caused high flows which in turn discharged solids.
CBOD5 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 16 | <15 mg/L | No | Excessive rainfall caused high flows which in turn discharged solids.
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 45 | <30 mg/L | No | Excessive rainfall caused high flows which in turn discharged solids.
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 45 | <45 mg/L | Y/N
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 8.3 | <2.0 mg/L | No | Excessive rainfall caused high flows which in turn discharged solids.
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 8.3 | <3.0 mg/L | No | Excessive rainfall caused high flows which in turn discharged solids.
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 7.5 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | <0.01 | <0.019 mg/L | Yes
Flow | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.029 | Monitor Only
pH | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 7.87 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 11 | <10 mg/L | No | I&I - rain event causes the plant to lose the proper F to M ratio which in turn causes bad test results
CBOD5 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 11 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 13 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 13 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 8 | <2.0 mg/L | No | I&I - rain event causes the plant to lose the proper F to M ratio which in turn causes bad test results
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 8 | <3.0 mg/L | No | I&I - rain event causes the plant to lose the proper F to M ratio which in turn causes bad test results |  |  |  | KY EEC CAP dated 12/13/19
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 7.14 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 0.036 | Monitor Only
pH | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 8.18 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 15 | <10 mg/L | No | Install new blower motor on #2 blower to increase aeration and wil schedule to have sludge pumped from clarifier. We have plans to build a new plant at this sight.
CBOD5 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 15 | <15 mg/L | Y/N
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 17 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 17 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 17.9 | <2.0 mg/L | No | Install new blower motor on #2 blower to increase aeration and wil schedule to have sludge pumped from clarifier. We have plans to build a new plant at this sight.
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 17.9 | <3.0 mg/L | No | Install new blower motor on #2 blower to increase aeration and wil schedule to have sludge pumped from clarifier. We have plans to build a new plant at this sight.
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 7.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 0.043 | Monitor Only
pH | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 7.67 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 23 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 23 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 14.4 | <2.0 mg/L | No | DO too low in ditches, will be installing new blower.
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 14.4 | <3.0 mg/L | No | DO too low in ditches, will be installing new blower.
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 7.35 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | <0.01 | <0.019 mg/L | Yes
Flow | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 0.039 | Monitor Only
pH | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 7.86 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <0.2 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <0.2 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 7.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <0.01 | <0.019 mg/L | Yes
Flow | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 0.033 | Monitor Only
pH | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 7.75 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 8 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 8 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 7 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 7 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 4.2 | <2.0 mg/L | No | DO levels are constantly below 0.50 mg/L in the ditch, which is causing the high ammonia levels.
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 4.2 | <3.0 mg/L | No | DO levels are constantly below 0.50 mg/L in the ditch, which is causing the high ammonia levels.
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 7.08 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 |  | Monitor Only
pH | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 7.43 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 3.1 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 3.1 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 8.25 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 5 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 5 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <0.01 | <0.019 mg/L | Yes
Flow | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 |  | Monitor Only
pH | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 7.3 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 8 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 8 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | <0.2 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | <0.2 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 7.47 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 0.01 | <0.019 mg/L | Yes

## BG-Fox Run
BG - Fox Run - NPDES KY0086967 | [8 empty] | BG - Fox Run - NPDES KY0086967 |  |  | BG - Fox Run - NPDES KY0086967
Testing Documentation | [8 empty] | Permit Limits |  |  | Regulatory Compliance
Test Type | Test Period Start Date | Test Period End Date | Sample Date | Date Received | Result | Limit | Compliance | Notes | Paramater | Limit | Frequency | Type | Date | Parameter | Test Result | Limit | Corrective Action | Notes | Compliance Deadline | Date Resolved | File Name
Flow | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 0.004 | Monitor Only |  |  | Flow | Monitor Only | 1/Month
pH | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 6.63 | 6.0-9.0 | Yes |  | pH | 6.0-9.0 | 1/Month
CBOD5 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <5.0 lbs/day |  |  | CBOD5 (Monthly Avg lbs./Day) | <5.0 lbs/day | 1/Month
CBOD5 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <7.5 lbs/day |  |  | CBOD5 (Weekly Avg lbs/day) | <7.5 lbs/day | 1/Month
CBOD5 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 9 | <30 mg/L | Yes |  | CBOD5 (Monthly Avg mg/L) | <30 mg/L | 1/Month
CBOD5 (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 9 | <45 mg/L | Yes |  | CBOD5 (Weekly Avg mg/L) | <45 mg/L | 1/Month
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <5.00 lbs/day |  |  | Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | <5.00 lbs/day | 1/Month
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <7.50 lbs/day |  |  | Total Suspened Solids(TSS) (Weekly Avg lbs/day) | <7.50 lbs/day | 1/Month
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 16 | <30 mg/L | Yes |  | Total Suspened Solids(TSS) (Monthly Avg mg/L) | <30 mg/L | 1/Month
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 16 | <45 mg/L | Yes |  | Total Suspened Solids(TSS) (Weekly Avg mg/L) | <45 mg/L | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <0.67 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | <0.67 lbs/day | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <1.0 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | <1.0 lbs/day | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 3.7 | <4.0 mg/L | Yes |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | <4.0 mg/L | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 3.7 | <6.0 mg/L | Yes |  | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | <6.0 mg/L | 1/Month
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <1.67 lbs/day |  |  | Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | <1.67 lbs/day | 1/Month
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <2.5 lbs/day |  |  | Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | <2.5 lbs/day | 1/Month
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <10 mg/L |  |  | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | <10 mg/L | 1/Month
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <15 mg/L |  |  | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | <15 mg/L | 1/Month
Dissolved Oxygen (DO) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 8.24 | >7.0 | Yes |  | Dissolved Oxygen (DO) | >7.0 | 1/Month
E. Coli (Monthly Avg) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 60000 | <130 #/100mL | No |  | E. Coli (Monthly Avg) | <130 #/100mL | 1/Month
E. Coli (Weekly Avg) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 60000 | <240 #100mL | No |  | E. Coli (Weekly Avg) | <240 #100mL | 1/Month
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 0.01 | <0.011mg/L | Yes |  | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | <0.011mg/L | 1/Month
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 0.01 | <0.019 mg/L | Yes |  | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | <0.019 mg/L | 1/Month
Flow | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.005 | Monitor Only
pH | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 6 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <5.0 lbs/day
CBOD5 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <7.5 lbs/day
CBOD5 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 23 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 23 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <5.00 lbs/day
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <7.50 lbs/day
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 21 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 21 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <0.67 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <1.0 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.5 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.5 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <1.67 lbs/day
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <2.5 lbs/day
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <10 mg/L
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <15 mg/L
Dissolved Oxygen (DO) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 9 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.01 | <0.019 mg/L | Yes
Flow | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 0.017 | Monitor Only
pH | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 7.74 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <5.0 lbs/day
CBOD5 (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <7.5 lbs/day
CBOD5 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 12 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 12 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <5.00 lbs/day
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <7.50 lbs/day
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 22 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 22 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <0.67 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <1.0 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <1.67 lbs/day
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <2.5 lbs/day
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 4.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 4.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 12.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 921 | <130 #/100mL | No
E. Coli (Weekly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 921 | <240 #100mL | No
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 0.01 | <0.019 mg/L | Yes
Flow | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.007 | Monitor Only
pH | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 7.76 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 12 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 12 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 1.1 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 1.1 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 10.62 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-02-17 | 0.225 | Monitor Only
pH | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 6.75 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 6 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 6 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 9.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 0.004 | Monitor Only
pH | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 8.43 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 39 | <30 mg/L | No | Sludge needed pumped - Staff has been working with local contractors and CSWR to get approved sludge haulers. There is a hauler scheduled June 1st to start removing sludge.
CBOD5 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 39 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 32 | <30 mg/L | No | Sludge needed pumped - Staff has been working with local contractors and CSWR to get approved sludge haulers. There is a hauler scheduled June 1st to start removing sludge.
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 32 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 9.2 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <1.00 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <1.00 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <0.010 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <0.010 | <0.019 mg/L | Yes
Flow | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 0.033 | Monitor Only
pH | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 7.26 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 45 | <30 mg/L | No | Sludge needed to be pumped
CBOD5 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 45 | <45 mg/L | Y/N
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 16 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 16 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 0.3 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 0.3 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 10.6 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | <0.010 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | <0.010 | <0.019 mg/L | Yes
Flow | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 0.006 | Monitor Only
pH | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 6.87 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 9 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 9 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | <0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | <0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 9.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 0.007 | Monitor Only
pH | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 7.14 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 12 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 12 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 8.2 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | <0.01 | <0.019 mg/L | Yes
Flow | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.004 | Monitor Only
pH | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 6.5 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 12 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 12 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.4 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.4 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 7.47 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 0.003 | Monitor Only
pH | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 7.02 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 7 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 7 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 11 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 11 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | <0.2 | <4.0 mg/L | yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | <0.2 | <6.0 mg/L | yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 8.35 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 6 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 6 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 0.01 | <0.019 mg/L | Yes
Flow | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 0.018 | Monitor Only
pH | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 7.23 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 12 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 12 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 4.6 | <4.0 mg/L | No | Due to sludge bulking in the chlorine chamber. Corrective action: contacting chemical company for polymer to prevent build up of pinfloc in chlorine contact.
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 4.6 | <6.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-28 | 2020-09-11 | 0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-28 | 2020-09-11 | 0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | 8 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-21 | <0.01 | <0.019 mg/L | Yes
Flow | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 0.005 | Monitor Only
pH | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 6.9 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 11 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 11 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 0.3 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 0.3 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 8.5 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <0.01 | <0.019 mg/L | Yes
Flow | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 0.007 | Monitor Only
pH | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 6.06 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 10 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 10 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | 9.34 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-06 | 2020-10-20 | <0.01 | <0.019 mg/L | Yes
Flow | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 |  | Monitor Only
pH | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 6.84 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 14 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 14 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 0.3 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 0.3 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 10.5 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <0.01 | <0.019 mg/L | Yes
Flow | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 |  | Monitor Only
pH | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 7.88 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | <4 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | <4 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | <0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | <0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 11.18 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 0.01 | <0.019 mg/L | Yes

## BG-Golden Acres
BG - Golden Acres - NPDES KY0044164 | [8 empty] | BG - Golden Acres - NPDES KY0044164 |  |  | BG - Golden Acres - NPDES KY0044164
Testing Documentation | [8 empty] | Permit Limits |  |  | Regulatory Compliance
Test Type | Test Period Start Date | Test Period End Date | Sample Date | Date Received | Result | Limit | Compliance | Notes | Paramater | Limit | Frequency | Type | Date | Parameter | Test Result | Limit | Corrective Action | Notes | Compliance Deadline | Date Resolved | File Name
Flow | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | 0.03 | Monitor Only |  |  | Flow | Monitor Only | Quarterly | KY EEC CAP dated 12/26/2019
pH | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | 6.76 | 6.0-9.0 | Yes |  | pH | 6.0-9.0 | Quarterly
CBOD5 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | N/A | <5.22 lbs/day |  |  | CBOD5 (Monthly Avg lbs./Day) | <5.22 lbs/day | Quarterly
CBOD5 (Weekly Avg lbs/day) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | N/A | <7.82 lbs/day |  |  | CBOD5 (Weekly Avg lbs/day) | <7.82 lbs/day | Quarterly
CBOD5 (Monthly Avg mg/L) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | 110 | <25 mg/L | No |  | CBOD5 (Monthly Avg mg/L) | <25 mg/L | Quarterly
CBOD5 (Weekly Avg mg/L) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | 110 | <37.5 mg/L | No |  | CBOD5 (Weekly Avg mg/L) | <37.5 mg/L | Quarterly
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | N/A | <6.26 lbs/day |  |  | Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | <6.26 lbs/day | Quarterly
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | N/A | <9.39 lbs/day |  |  | Total Suspened Solids(TSS) (Weekly Avg lbs/day) | <9.39 lbs/day | Quarterly
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | 72 | <30 mg/L | No |  | Total Suspened Solids(TSS) (Monthly Avg mg/L) | <30 mg/L | Quarterly
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | 72 | <45 mg/L | No |  | Total Suspened Solids(TSS) (Weekly Avg mg/L) | <45 mg/L | Quarterly
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | N/A | <0.83 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | <0.83 lbs/day | Quarterly
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | N/A | <1.25 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | <1.25 lbs/day | Quarterly
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | 32 | <4.0 mg/L | No |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | <4.0 mg/L | Quarterly
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | 32 | <6.0 mg/L | No |  | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | <6.0 mg/L | Quarterly
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | N/A | <2.09 lbs/day |  |  | Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | <2.09 lbs/day | Quarterly
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | N/A | <3.13 lbs/day |  |  | Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | <3.13 lbs/day | Quarterly
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | N/A | <10.0 mg/L |  |  | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | <10.0 mg/L | Quarterly
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | N/A | <15.0 mg/L |  |  | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | <15.0 mg/L | Quarterly
Dissolved Oxygen (DO) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | 1.8 | >7.0 | No |  | Dissolved Oxygen (DO) | >7.0 | Quarterly
E. Coli (Monthly Avg) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | >2419.6 | <130 #/100mL |  |  | E. Coli (Monthly Avg) | <130 #/100mL | Quarterly
E. Coli (Weekly Avg) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | >2419.6 | <240 #100mL |  |  | E. Coli (Weekly Avg) | <240 #100mL | Quarterly
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | <0.02 | <0.011mg/L | No |  | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | <0.011mg/L | Quarterly
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-01 | 2019-12-31 | 2019-10-01 | 2019-11-19 | <0.02 | <0.019 mg/L | No |  | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | <0.019 mg/L | Quarterly
Flow | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | 0.025 | Monitor Only
pH | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | 7.15 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | 14 | <25 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | 14 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | 22 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | 22 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | 11 | <10.0 mg/L | No | Had an undersized blower, returns would not operate correctly to keep plant funning efficiently to remove ammonia. Have since replaced with new blower. Also pumped down and cleaned the clairfier.
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | 11 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | 8.65 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | >2419.6 | <130 #/100mL | No | The integrity of the treatment process was affected by the infiltration into the plant and will affect contact time for chlorine and dechlorination.
E. Coli (Weekly Avg) | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | >2419.6 | <240 #100mL | No | The integrity of the treatment process was affected by the infiltration into the plant and will affect contact time for chlorine and dechlorination.
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | 0.02 | <0.011mg/L | No | Too much flow through due to infiltration
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-01-01 | 2019-03-31 | 2020-01-17 | 2020-01-28 | 0.02 | <0.019 mg/L | No | Too much flow through due to infiltration
Flow | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | 0.025 | Monitor Only
pH | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | 6.99 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | 14 | <25 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | 14 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | 24 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | 24 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | 6.2 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | 6.2 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | 9.07 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | >2419.6 | <130 #/100mL | No | The integrity of the treatment process was affected by the infiltration into the plant and will affect contact time for chlorine and dechlorination.
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | >2419.6 | <240 #100mL | No | The integrity of the treatment process was affected by the infiltration into the plant and will affect contact time for chlorine and dechlorination.
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | 0.03 | <0.011mg/L | No | Too much flow through due to infiltration
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-28 | 2020-03-09 | 0.03 | <0.019 mg/L | No | Too much flow through due to infiltration
Flow | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | 0.025 | Monitor Only
pH | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | 6.82 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | 7.8 | <25 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | 7.8 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | 27 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | 27 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | 5.4 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | 5.4 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | 3.7 | >7.0 | No | Caused by substantial presense of low DO filamentous bacteria in the activated sludge. Also blower and motor on treatment plant was insufficient...has since been replaced.
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | >2419.6 | <130 #/100mL | No | The integrity of the treatment process was affected by the infiltration into the plant and will affect contact time for chlorine and dechlorination.
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | >2419.6 | <240 #100mL | No | The integrity of the treatment process was affected by the infiltration into the plant and will affect contact time for chlorine and dechlorination.
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | 0.16 | <0.011mg/L | No | Too much flow through due to infiltration after eval with new equipment consider moving up jetting of collection system and identification of I&I issues.
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-31 | 2020-04-08 | 0.16 | <0.019 mg/L | No | Too much flow through due to infiltration after eval with new equipment consider moving up jetting of collection system and identification of I&I issues.
Flow | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | 0.025 | Monitor Only
pH | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | 6.86 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | <5.0 | <25 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | <5.0 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | 5 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | 5 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | <0.50 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | <0.50 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | 6.42 | >7.0 | No | Will need to add more air to the effluent channel, DO will vary based on flow and temperatures.
E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | <1.0 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | <1.0 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | >2.20 | <0.011mg/L | No | Not enough time between dechlorination tablets and chlorine tablets. Will be adjusted.
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-25 | 2020-07-02 | >2.20 | <0.019 mg/L | No | Not enough time between dechlorination tablets and chlorine tablets. Will be adjusted.
Flow | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | 0.025 | Monitor Only
pH | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | 6.87 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | <5.0 | <25 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | <5.0 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | <0.50 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | <0.50 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | 6.55 | >7.0 | No | Will need to add more air to the effluent channel, DO will vary based on flow and temperatures.
E. Coli (Monthly Avg) | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | 13.4 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | 13.4 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | <0.02 | <0.011mg/L | No | Not enough time between dechlorination tablets and chlorine tablets. Will be adjusted.
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-07-01 | 2020-09-30 | 2020-07-10 | 2020-07-20 | <0.02 | <0.019 mg/L | No | Not enough time between dechlorination tablets and chlorine tablets. Will be adjusted.
Flow | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 |  | Monitor Only
pH | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | 6.96 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | 14 | <25 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | 14 | <37.5 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | 10 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | 10 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | <0.50 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | <0.50 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | 6 | >7.0 | No
E. Coli (Monthly Avg) | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | 27.2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | 27.2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | <0.02 | <0.011mg/L | No
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-10-01 | 2020-12-31 | 2020-11-10 | 2020-11-19 | <0.02 | <0.019 mg/L | No
Note on J75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: after eval with new equipment consider moving up jetting of collection system and identification of I&I issues.

## BG-Great Oaks
BG - Great Oaks - NPDES KY0080845 | [8 empty] | BG - Great Oaks - NPDES KY0080845 |  |  | BG - Great Oaks - NPDES KY0080845
Testing Documentation | [8 empty] | Permit Limits |  |  | Regulatory Compliance
Test Type | Test Period Start Date | Test Period End Date | Sample Date | Date Received | Result | Limit | Compliance | Notes | Paramater | Limit | Frequency | Type | Date | Parameter | Test Result | Limit | Corrective Action | Notes | Compliance Deadline | Date Resolved | File Name
Flow | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | 0.022827 | Monitor Only |  |  | Flow | Monitor Only | 1/Month | 6-30-2020 Great Oaks CAP Status Report Letter
pH | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | 7.44 | 6.0-9.0 | Yes |  | pH | 6.0-9.0 | 1/Month
CBOD5 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | N/A | <5.84 lbs/day |  |  | CBOD5 (Monthly Avg lbs./Day) | <5.84 lbs/day | 1/Month
CBOD5 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | N/A | <8.76 lbs/day |  |  | CBOD5 (Weekly Avg lbs/day) | <8.76 lbs/day | 1/Month
CBOD5 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | 35 | <10 mg/L | No |  | CBOD5 (Monthly Avg mg/L) | <10 mg/L | 1/Month
CBOD5 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | 35 | <15 mg/L | No |  | CBOD5 (Weekly Avg mg/L) | <15 mg/L | 1/Month
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | N/A | <17.5 lbs/day |  |  | Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | <17.5 lbs/day | 1/Month
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | N/A | <26.3 lbs/day |  |  | Total Suspened Solids(TSS) (Weekly Avg lbs/day) | <26.3 lbs/day | 1/Month
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | 6 | <30 mg/L | Yes |  | Total Suspened Solids(TSS) (Monthly Avg mg/L) | <30 mg/L | 1/Month
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | 6 | <45 mg/L | Yes |  | Total Suspened Solids(TSS) (Weekly Avg mg/L) | <45 mg/L | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | N/A | <2.34 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | <2.34 lbs/day | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | N/A | <3.50 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | <3.50 lbs/day | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | 14 | <4.0 mg/L | No |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | <4.0 mg/L | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | 14 | <6.0 mg/L | No |  | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | <6.0 mg/L | 1/Month
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | N/A | <5.84 lbs/day |  |  | Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | <5.84 lbs/day | 1/Month
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | N/A | <8.76 lbs/day |  |  | Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | <8.76 lbs/day | 1/Month
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | N/A | <10.0 mg/L |  |  | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | <10.0 mg/L | 1/Month
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | N/A | <15.0 mg/L |  |  | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | <15.0 mg/L | 1/Month
Dissolved Oxygen (DO) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | 7.1 | >7.0 | Yes |  | Dissolved Oxygen (DO) | >7.0 | 1/Month
E. Coli (Monthly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | >2419.6 | <130 #/100mL | Yes |  | E. Coli (Monthly Avg) | <130 #/100mL | 1/Month
E. Coli (Weekly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | >2419.6 | <240 #100mL |  |  | E. Coli (Weekly Avg) | <240 #100mL | 1/Month
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | 0.1 | <0.011mg/L | Yes |  | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | <0.011mg/L | 1/Month
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 | 2019-11-19 | 0.1 | <0.019 mg/L | Yes |  | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | <0.019 mg/L | 1/Month
Flow | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | 0.025 | Monitor Only
pH | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | 7.51 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | 5.7 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | 5.7 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | 5 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | 5 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | 0.26 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | 0.26 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | 10.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | 2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | 2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | 0.46 | <0.011mg/L | No
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-21 | 2019-12-04 | 0.46 | <0.019 mg/L | No
Flow | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | 0.025 | Monitor Only
pH | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | 7.02 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | 5 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | 5 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | 5 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | 5 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | 0.32 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | 0.32 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | 9.93 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | 86.2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | 86.2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | 0.011 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-02 | B* <0.02 | <0.019 mg/L | Y/N | B = DMR states below detection limit/No detection
Flow | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | 0.025 | Monitor Only
pH | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | 7.24 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | 5 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | 5 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | 5 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | 5 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | 0.25 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | 0.25 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | 8.62 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | >2419.6 | <130 #/100mL | No
E. Coli (Weekly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | >2419.6 | <240 #100mL | No
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | B* <0.02 | <0.011mg/L |  | B = DMR states below detection limit/No detection
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-27 | B* <0.02 | <0.019 mg/L |  | B = DMR states below detection limit/No detection
Flow | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 0.025 | Monitor Only
pH | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 6.9 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | <5.0 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | <5.0 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 8 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 8 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | <0.25 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | <0.25 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 9.07 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 24.3 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 24.3 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | B* <0.02 | <0.011mg/L |  | B = DMR states below detection limit/No detection
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | B* <0.02 | <0.019 mg/L |  | B = DMR states below detection limit/No detection
Flow | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | 0.025 | Monitor Only
pH | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | 6.88 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | <5.0 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | <5.0 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | <0.25 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | <0.25 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | 7.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | 5.1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | 5.1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | 0.06 | <0.011mg/L | No | Too much flow through due to infiltration, due excess outside of normal operations.
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-06 | 2020-03-16 | 0.06 | <0.019 mg/L | No | Too much flow through due to infiltration, due excess outside of normal operations.
Flow | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | 0.025 | Monitor Only
pH | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | 7.09 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | 19 | <10 mg/L | No | Dealing with excessive pin-floc after installation of new aeration system and making plant adjustments.
CBOD5 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | 19 | <15 mg/L | No | Dealing with excessive pin-floc after installation of new aeration system and making plant adjustments.
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | 65 | <30 mg/L | No | Dealing with excessive pin-floc after installation of new aeration system and making plant adjustments.
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | 65 | <45 mg/L | No | Dealing with excessive pin-floc after installation of new aeration system and making plant adjustments.
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | 0.75 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | 0.75 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | 4.9 | >7.0 | No | Dealing with excessive pin-floc after installation of new aeration system and making plant adjustments.
E. Coli (Monthly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | 72.9 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | 72.9 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | 0.02 | <0.011mg/L | No | Dealing with excessive pin-floc after installation of new aeration system and making plant adjustments.
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-28 | 2020-05-07 | 0.02 | <0.019 mg/L | No | Dealing with excessive pin-floc after installation of new aeration system and making plant adjustments.
Flow | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | 0.025 | Monitor Only
pH | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | 6.85 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | 22 | <10 mg/L | No | Digestor is leaking into the effluent. Plan is to clean, patch, and repair digestor.
CBOD5 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | 22 | <15 mg/L | No | Digestor is leaking into the effluent. Plan is to clean, patch, and repair digestor.
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | <5 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | <5 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | <0.50 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | <0.50 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | 7.8 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | 16.9 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | 16.9 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | 0.14 | <0.011mg/L | No | Digestor is leaking into the effluent. Plan is to clean, patch, and repair digestor.
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-22 | 2020-06-02 | 0.14 | <0.019 mg/L | No | Digestor is leaking into the effluent. Plan is to clean, patch, and repair digestor.
Flow | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | 0.025 | Monitor Only
pH | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | 7.22 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | <5.0 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | <5.0 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | <5 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | <5 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | <0.50 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | <0.50 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | 7.32 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | 33.6 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | 33.6 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | B* 0.02 | <0.011mg/L |  | B = DMR states below detection limit/No detection
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-02 | B* 0.02 | <0.019 mg/L |  | B = DMR states below detection limit/No detection
Flow | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 |  | Monitor Only
pH | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | 7.36 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | <5.0 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | <5.0 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | <5 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | <5 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | <0.50 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | <0.50 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | 7.67 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | 12 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | 12 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | 0.03 | <0.011mg/L | No | Bisulfate dosage was too low, will increase dosage rate.
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-14 | 2020-07-23 | 0.03 | <0.019 mg/L | No | Bisulfate dosage was too low, will increase dosage rate.
Flow | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | 0.025 | Monitor Only
pH | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | 7.28 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | <5.0 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | <5.0 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | <5 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | <5 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | <0.50 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | <0.50 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | 7.27 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | 27.2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | 27.2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | B* <0.02 | <0.011mg/L |  | B = DMR states below detection limit/No detection
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-20 | B* <0.02 | <0.019 mg/L |  | B = DMR states below detection limit/No detection
Flow | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | 0.025 | Monitor Only
pH | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | 6.9 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | <5.0 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | <5.0 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | 8 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | 8 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | <0.50 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | <0.50 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | 8.96 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | <1.0 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | <1.0 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | 1.04 | <0.011mg/L | No | Incorrect dosing of Cl2 and Sodium Bisulfate. Will adjust feeding rates.
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-22 | 2020-10-07 | 1.04 | <0.019 mg/L | No | Incorrect dosing of Cl2 and Sodium Bisulfate. Will adjust feeding rates.
Flow | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 |  | Monitor Only
pH | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | 6.96 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | <5.0 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | <5.0 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | <5 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | <5 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | <0.50 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | <0.50 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | N/A | <10.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | N/A | <15.0 mg/L | N/A
Dissolved Oxygen (DO) | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | 7.9 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | 6.3 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | 6.3 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | B*<0.02 | <0.011mg/L |  | B = DMR states below detection limit/No detection
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-15 | 2020-10-27 | B*<0.02 | <0.019 mg/L |  | B = DMR states below detection limit/No detection
Flow | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 |  | Monitor Only
pH | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | 7.43 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | 19 | <10 mg/L | No | The plant was sampled after recovering from a heavy rain event. Operations team will adjust chemical feeders.
CBOD5 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | 19 | <15 mg/L | No | The plant was sampled after recovering from a heavy rain event. Operations team will adjust chemical feeders.
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | 8 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | 8 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | 2.9 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | 2.9 | <15.0 mg/L | Yes
Dissolved Oxygen (DO) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | 8.52 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | <1.0 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | <1.0 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | >2.20 | <0.011mg/L | No | The plant was sampled after recovering from a heavy rain event. Operations team will adjust chemical feeders.
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-25 | >2.20 | <0.019 mg/L | No | The plant was sampled after recovering from a heavy rain event. Operations team will adjust chemical feeders.
Flow | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | 0.025 | Monitor Only
pH | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | 6.42 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | <5.0 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | <5.0 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | 11 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | 11 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | <0.50 | <10.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | <0.50 | <15.0 mg/L | yes
Dissolved Oxygen (DO) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | 9.5 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | 2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | 2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | 0.04 | <0.011mg/L | No | Will add more bisulfate tablets. Recommend swapping to parasitic acid.
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-21 | 0.04 | <0.019 mg/L | No | Will add more bisulfate tablets. Recommend swapping to parasitic acid.

## BG - JE - Timberland
Timberland - NPDES KY0183106 | [8 empty] | Timberland - NPDES KY0183106 |  |  | Timberland - NPDES KY0183106
Testing Documentation | [8 empty] | Permit Limits |  |  | Regulatory Compliance Schedules
Test Type | Test Period Start Date | Test Period End Date | Sample Date | Date Received | Result | Limit | Compliance | Notes | Paramater | Limit | Frequency | Type | Date | Parameter | Test Result | Limit | Corrective Action | Notes | Compliance Deadline | Date Resolved | File Name
Flow | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 0.025 | Report (gpd) | Yes |  | Flow | Report | Monthly
pH | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 6.96 | 6.0-9.0 | Yes |  | pH | 6.0-9.0 | Monthly
CBOD5 (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 |  | 3.1 lbs/Day |  |  | CBOD5 (Weekly Avg) | 3.1 lbs/Day | Monthly
CBOD5 (Monthly Average) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 |  | 2.1 lbs/day |  |  | CBOD5 (Monthly Average) | 2.1 lbs/day | Monthly
CBOD5 (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 11 | 15mg/L | Yes |  | CBOD5 (Weekly Avg) | 15mg/L | Monthly
CBOD5 (Monthly Average) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 11 | 10 mg/L | No | Under AO | CBOD5 (Monthly Average) | 10 mg/L | Monthly
TSS (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 |  | 9.4 lbs/Day |  |  | TSS (Weekly Avg) | 9.4 lbs/Day | Monthly
TSS (Monthly Average) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 |  | 6.3 lbs/day |  |  | TSS (Monthly Average) | 6.3 lbs/day | Monthly
TSS (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 21 | 45 mg/L | Yes |  | TSS (Weekly Avg) | 45 mg/L | Monthly
TSS (Monthly Average) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 21 | 30 mg/L | Yes |  | TSS (Monthly Average) | 30 mg/L | Monthly
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 |  | 0.6 lbs/Day |  |  | Ammonia (May 1 - Oct 31 Weekly Avg) | 0.6 lbs/Day | Monthly
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 |  | 0.4 lbs/day |  |  | Ammonia (May 1 - Oct 31 Monthly Avg) | 0.4 lbs/day | Monthly
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 16 | 3 mg/L | No | Under AO | Ammonia (May 1 - Oct 31 Weekly Avg) | 3 mg/L | Monthly
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 16 | 2 mg/L | No | Under AO | Ammonia (May 1 - Oct 31 Monthly Avg) | 2 mg/L | Monthly
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 |  | 2.8 lbs/Day |  |  | Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2.8 lbs/Day | Monthly
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 |  | 1.9 lbs/day |  |  | Ammonia (Nov 1 - Apr 30 Monthly Avg) | 1.9 lbs/day | Monthly
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 |  | 13.5 mg/L |  |  | Ammonia (Nov 1 - Apr 30 Weekly Avg) | 13.5 mg/L | Monthly
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 |  | 9 mg/L |  |  | Ammonia (Nov 1 - Apr 30 Monthly Avg) | 9 mg/L | Monthly
E Coli. (colonies/100mL) (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | >2,419.6 | 240 #/100 mL | No | Under AO | E Coli. (colonies/100mL) (Weekly Avg) | 240 | Monthly
E Coli. (colonies/100mL) (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 |  | 130 |  |  | E Coli. (colonies/100mL) (Monthly Avg) | 130 | Monthly
DO (Min) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 6.02 | 7.0 mg/L | Yes |  | DO (Min) | 7.0 mg/L | Monthly
TRC (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 0.05 | 0.019 mg/L | No | Under AO | TRC (Weekly Avg) | 0.019 mg/L | Monthly
TRC (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-29 | 2020-06-09 | 0.05 | 0.011 mg/L | No | Under AO | TRC (Monthly Avg) | 0.011 mg/L | Monthly
Flow | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | 0.025 | Report (gpd)
pH | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | 7.1 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | 7.4 | <15mg/L | Yes
CBOD5 (Monthly Average) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | 7.4 | <10 mg/L | Yes
TSS (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | 15 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | 15 | <30 mg/L | Yes
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | 16 | <3 mg/L | No | Lagoon aeration is inop. Repairing the blower that runs logoon aeration and contact chamber will be rebuilt. Under AO
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | 16 | <2 mg/L | No | Lagoon aeration is inop. Repairing the blower that runs logoon aeration and contact chamber will be rebuilt. Under AO
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | N/A | 13.5 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | N/A | 9 mg/L | N/A
E Coli. (colonies/100mL) (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | >2419.6 | <240 #/100 mL | No | Lagoon aeration is inop. Repairing the blower that runs logoon aeration and contact chamber will be rebuilt. Under AO
E Coli. (colonies/100mL) (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | >2419.6 | <130 #/100mL | No | Lagoon aeration is inop. Repairing the blower that runs logoon aeration and contact chamber will be rebuilt. Under AO
DO (Min) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | 6.8 | >7.0 mg/L | Yes
TRC (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | 0.03 | 0.019 mg/L | No | Lagoon aeration is inop. Repairing the blower that runs logoon aeration and contact chamber will be rebuilt. Under AO
TRC (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-24 | 2020-07-01 | 0.03 | 0.011 mg/L | No | Lagoon aeration is inop. Repairing the blower that runs logoon aeration and contact chamber will be rebuilt. Under AO
Flow | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | 0.025 | Report (gpd)
pH | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | 7.79 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | 7.6 | <15mg/L | Yes
CBOD5 (Monthly Average) | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | 7.6 | <10 mg/L | Yes
TSS (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | 18 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | 18 | <30 mg/L | Yes
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | 18 | <3 mg/L | No
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | 18 | <2 mg/L | No
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | N/A | 13.5 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | N/A | 9 mg/L | N/A
E Coli. (colonies/100mL) (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | 2 | <240 #/100 mL | Yes
E Coli. (colonies/100mL) (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | 2 | <130 #/100mL | Yes
DO (Min) | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | 6.3 | >7.0 mg/L | No | The 2nd blower was recently put back online to bring DO up.
TRC (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | 2.2 | 0.019 mg/L | No | Will adjust chemical feeds.
TRC (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-28 | 2020-08-04 | 2.2 | 0.011 mg/L | No | Will adjust chemical feeds.
Flow | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | 0.025 | Report (gpd)
pH | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | 7.73 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | 7.3 | <15mg/L | Yes
CBOD5 (Monthly Average) | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | 7.3 | <10 mg/L | Yes
TSS (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | 18 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | 18 | <30 mg/L | Yes
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | 16 | <3 mg/L | No | Had to much CL2 and not enought dechlorination. Will add more dechlorination next time. Just replaced blower motor but may time sometime to help plant and lagoon. Lagoon really needs a separate blower. Operator thinks that's in the works.
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | 16 | <2 mg/L | No | Had to much CL2 and not enought dechlorination. Will add more dechlorination next time. Just replaced blower motor but may time sometime to help plant and lagoon. Lagoon really needs a separate blower. Operator thinks that's in the works.
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | N/A | 13.5 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | N/A | 9 mg/L | N/A
E Coli. (colonies/100mL) (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | 7.5 | <240 #/100 mL | Yes
E Coli. (colonies/100mL) (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | 7.5 | <130 #/100mL | Yes
DO (Min) | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | 8 | >7.0 mg/L | Yes
TRC (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | 0.05 | <0.019 mg/L | No | Had to much CL2 and not enought dechlorination. Will add more dechlorination next time. Just replaced blower motor but may time sometime to help plant and lagoon. Lagoon really needs a separate blower. Operator thinks that's in the works.
TRC (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-05 | 2020-08-17 | 0.05 | <0.011 mg/L | No | Had to much CL2 and not enought dechlorination. Will add more dechlorination next time. Just replaced blower motor but may time sometime to help plant and lagoon. Lagoon really needs a separate blower. Operator thinks that's in the works.
Flow | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | 0.025 | Report (gpd)
pH | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | 7.33 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | 9.2 | <15mg/L | Yes
CBOD5 (Monthly Average) | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | 9.2 | <10 mg/L | Yes
TSS (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | 36 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | 36 | <30 mg/L | No | Per the operator: We need more air in the lagoon, plant to help remove ammonia nd to help with DO levels. This is a capital project to add new blowers and separate blower for the lagoon. We will need to add CL2 to contact chamber for E.coli.
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | 8.8 | <3 mg/L | No | Per the operator: We need more air in the lagoon, plant to help remove ammonia nd to help with DO levels. This is a capital project to add new blowers and separate blower for the lagoon. We will need to add CL2 to contact chamber for E.coli.
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | 8.8 | <2 mg/L | No | Per the operator: We need more air in the lagoon, plant to help remove ammonia nd to help with DO levels. This is a capital project to add new blowers and separate blower for the lagoon. We will need to add CL2 to contact chamber for E.coli.
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | N/A | 13.5 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | N/A | 9 mg/L | N/A
E Coli. (colonies/100mL) (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | 2419.6 | <240 #/100 mL | No | Per the operator: We need more air in the lagoon, plant to help remove ammonia nd to help with DO levels. This is a capital project to add new blowers and separate blower for the lagoon. We will need to add CL2 to contact chamber for E.coli.
E Coli. (colonies/100mL) (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | 2419.6 | <130 #/100mL | No | Per the operator: We need more air in the lagoon, plant to help remove ammonia nd to help with DO levels. This is a capital project to add new blowers and separate blower for the lagoon. We will need to add CL2 to contact chamber for E.coli.
DO (Min) | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | 6.26 | >7.0 mg/L | No | Per the operator: We need more air in the lagoon, plant to help remove ammonia nd to help with DO levels. This is a capital project to add new blowers and separate blower for the lagoon. We will need to add CL2 to contact chamber for E.coli.
TRC (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | <0.02 | <0.019 mg/L | No | Per the operator: We need more air in the lagoon, plant to help remove ammonia nd to help with DO levels. This is a capital project to add new blowers and separate blower for the lagoon. We will need to add CL2 to contact chamber for E.coli.
TRC (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-10 | 2020-09-25 | <0.02 | <0.011 mg/L | No | Per the operator: We need more air in the lagoon, plant to help remove ammonia nd to help with DO levels. This is a capital project to add new blowers and separate blower for the lagoon. We will need to add CL2 to contact chamber for E.coli.
Flow | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | 0.025 | Report (gpd)
pH | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | 6.98 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | <5.0 | <15mg/L | Yes
CBOD5 (Monthly Average) | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | <5.0 | <10 mg/L | Yes
TSS (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | 16 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | 16 | <30 mg/L | Yes
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | 4.9 | <3 mg/L | No | Need more air for treatment plant and lagoon to help remove ammonia. Will add more CL2 to kill E.coli and bisulfate to reduce residual chlorine.
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | 4.9 | <2 mg/L | No | Need more air for treatment plant and lagoon to help remove ammonia. Will add more CL2 to kill E.coli and bisulfate to reduce residual chlorine.
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | N/A | 13.5 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | N/A | 9 mg/L | N/A
E Coli. (colonies/100mL) (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | >2419.6 | <240 #/100 mL | No | Need more air for treatment plant and lagoon to help remove ammonia. Will add more CL2 to kill E.coli and bisulfate to reduce residual chlorine.
E Coli. (colonies/100mL) (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | >2419.6 | <130 #/100mL | No | Need more air for treatment plant and lagoon to help remove ammonia. Will add more CL2 to kill E.coli and bisulfate to reduce residual chlorine.
DO (Min) | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | 7.41 | >7.0 mg/L | Yes
TRC (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | 0.06 | <0.019 mg/L | No | Need more air for treatment plant and lagoon to help remove ammonia. Will add more CL2 to kill E.coli and bisulfate to reduce residual chlorine.
TRC (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-29 | 2020-11-13 | 0.06 | <0.011 mg/L | No | Need more air for treatment plant and lagoon to help remove ammonia. Will add more CL2 to kill E.coli and bisulfate to reduce residual chlorine.
Flow | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | 0 | Report (gpd)
pH | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | 7.11 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | 9.5 | <15mg/L | Yes
CBOD5 (Monthly Average) | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | 9.5 | <10 mg/L | Yes
TSS (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | 6 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | 6 | <30 mg/L | Yes
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | N/A | <3 mg/L | N/A
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | N/A | <2 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | 4.1 | <13.5 mg/L | Yes
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | 4.1 | <9 mg/L | Yes
E Coli. (colonies/100mL) (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | 69.8 | <240 #/100 mL | Yes
E Coli. (colonies/100mL) (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | 69.8 | <130 #/100mL | Yes
DO (Min) | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | 8.71 | >7.0 mg/L | Yes
TRC (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | 1.42 | <0.019 mg/L | No | The chlorine contact & bisulfate contact tank too small and is not allowing sufficient contact time.
TRC (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-12 | 2020-11-30 | 1.42 | <0.011 mg/L | No | The chlorine contact & bisulfate contact tank too small and is not allowing sufficient contact time.
Flow | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 |  | Report (gpd)
pH | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | 6.89 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | <5.0 | <15mg/L | Yes
CBOD5 (Monthly Average) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | <5.0 | <10 mg/L | Yes
TSS (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | <10 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | <10 | <30 mg/L | Yes
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | N/A | <3 mg/L | N/A
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | N/A | <2 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | 4.5 | <13.5 mg/L | Yes
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | 4.5 | <9 mg/L | Yes
E Coli. (colonies/100mL) (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | 1 | <240 #/100 mL | Yes
E Coli. (colonies/100mL) (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | 1 | <130 #/100mL | Yes
DO (Min) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | 6.1 | >7.0 mg/L | No | Chrlorine contact and bisulfate tank too small and not allowing sufficient contact time. DO low from air adjustments. Will adjust air valves.
TRC (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | 2.06 | <0.019 mg/L | No | Chrlorine contact and bisulfate tank too small and not allowing sufficient contact time. DO low from air adjustments. Will adjust air valves.
TRC (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-08 | 2020-12-16 | 2.06 | <0.011 mg/L | No | Chrlorine contact and bisulfate tank too small and not allowing sufficient contact time. DO low from air adjustments. Will adjust air valves.

## BG-Kingswood
BG - Kingswood - NPDES KY0101419 | [8 empty] | BG - Kingswood - NPDES KY0101419 |  |  | BG - Kingswood - NPDES KY0101419
Testing Documentation | [8 empty] | Permit Limits |  |  | Regulatory Compliance
Test Type | Test Period Start Date | Test Period End Date | Sample Date | Date Received | Result | Limit | Compliance | Notes | Paramater | Limit | Frequency | Type | Date | Parameter | Test Result | Limit | Corrective Action | Notes | Compliance Deadline | Date Resolved | File Name
Flow | 2019-09-01 | 2019-09-30 | 2019-09-27 |  |  | Monitor Only |  |  | Flow | Monitor Only | 1/Month
pH | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 7.11 | 6.0-9.0 | Yes |  | pH | 6.0-9.0 | 1/Month
CBOD5 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <2.67 lbs/day |  |  | CBOD5 (Monthly Avg lbs./Day) | <2.67 lbs/day | 1/Month
CBOD5 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <4.0 lbs/day |  |  | CBOD5 (Weekly Avg lbs/day) | <4.0 lbs/day | 1/Month
CBOD5 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 7 | <20 mg/L | Yes |  | CBOD5 (Monthly Avg mg/L) | <20 mg/L | 1/Month
CBOD5 (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 7 | <30 mg/L | Yes |  | CBOD5 (Weekly Avg mg/L) | <30 mg/L | 1/Month
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <10.00 lbs/day |  |  | Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | <10.00 lbs/day | 1/Month
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <15.0 lbs/day |  |  | Total Suspened Solids(TSS) (Weekly Avg lbs/day) | <15.0 lbs/day | 1/Month
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 17 | <30 mg/L | Yes |  | Total Suspened Solids(TSS) (Monthly Avg mg/L) | <30 mg/L | 1/Month
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 17 | <45 mg/L | Yes |  | Total Suspened Solids(TSS) (Weekly Avg mg/L) | <45 mg/L | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <0.67 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | <0.67 lbs/day | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <1.0 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | <1.0 lbs/day | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 4.1 | <4.0 mg/L | No |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | <4.0 mg/L | 1/Month
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 4.1 | <6.0 mg/L | Yes |  | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | <6.0 mg/L | 1/Month
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <1.33 lbs/day |  |  | Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | <1.33 lbs/day | 1/Month
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <2.0 lbs/day |  |  | Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | <2.0 lbs/day | 1/Month
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <10 mg/L |  |  | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | <10 mg/L | 1/Month
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <15 mg/L |  |  | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | <15 mg/L | 1/Month
Dissolved Oxygen (DO) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 7.9 | >7.0 | Yes |  | Dissolved Oxygen (DO) | >7.0 | 1/Month
E. Coli (Monthly Avg) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 28 | <130 #/100mL | Yes |  | E. Coli (Monthly Avg) | <130 #/100mL | 1/Month
E. Coli (Weekly Avg) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 28 | <240 #100mL | Yes |  | E. Coli (Weekly Avg) | <240 #100mL | 1/Month
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  |  | <0.011mg/L |  |  | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | <0.011mg/L | 1/Month
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  |  | <0.019 mg/L |  |  | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | <0.019 mg/L | 1/Month
Total Phosphorus | 2019-09-01 | 2019-09-30 | 2019-09-27 |  |  | Report |  |  | Total Phosphorus | Report | 1/Month
Total Nitrogen | 2019-09-01 | 2019-09-30 | 2019-09-27 |  |  | Report |  |  | Total Nitrogen | Report | 1/Month
Flow | 2019-10-01 | 2019-10-31 | 2019-10-11 |  |  | Monitor Only
pH | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 6.9 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <2.67 lbs/day
CBOD5 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <4.0 lbs/day
CBOD5 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 8 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 8 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <10.00 lbs/day
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <15.0 lbs/day
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 16 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 16 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <0.67 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <1.0 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 1.6 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 1.6 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <1.33 lbs/day
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <2.0 lbs/day
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <10 mg/L
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <15 mg/L
Dissolved Oxygen (DO) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 8.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 148 | <130 #/100mL | No
E. Coli (Weekly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 148 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  |  | <0.011mg/L
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  |  | <0.019 mg/L
Total Phosphorus | 2019-10-01 | 2019-10-31 | 2019-10-11 |  |  | Report
Total Nitrogen | 2019-10-01 | 2019-10-31 | 2019-10-11 |  |  | Report
Flow | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 0.039 | Monitor Only
pH | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 7.86 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 12 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 12 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 37 | <30 mg/L | No
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 37 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 10.9 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 613 | <130 #/100mL | No
E. Coli (Weekly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 613 | <240 #100mL | No
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  |  | <0.011mg/L
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  |  | <0.019 mg/L
Total Phosphorus | 2019-11-01 | 2019-11-30 | 2019-11-15 |  |  | Report
Total Nitrogen | 2019-11-01 | 2019-11-30 | 2019-11-15 |  |  | Report
Flow | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.036 | Monitor Only
pH | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 7.81 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 8 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 8 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.3 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.3 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 12.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 19 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 19 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 |  | <0.011mg/L
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 |  | <0.019 mg/L
Total Phosphorus | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 |  | Report
Total Nitrogen | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 |  | Report
Flow | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 0.167 | Monitor Only
pH | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 7.83 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 4 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 4 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 11 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 11 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 9.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 |  |  |  | <0.011mg/L
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 |  |  |  | <0.019 mg/L
Total Phosphorus | 2020-01-01 | 2020-01-31 |  |  |  | Report
Total Nitrogen | 2020-01-01 | 2020-01-31 |  |  |  | Report
Flow | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 0.298 | Monitor Only
pH | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 8.13 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 6 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 21 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 21 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | <0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | <0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 9.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 12 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 | 12 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 |  | <0.011mg/L
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 |  | <0.019 mg/L
Total Phosphorus | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 |  | Report
Total Nitrogen | 2020-02-01 | 2020-02-29 | 2020-02-17 | 2020-02-26 |  | Report
Flow | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 0.029 | Monitor Only
pH | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 6.72 | 6.0-9.0
CBOD5 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | <4 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | <4 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 0.4 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 0.4 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 8.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 |  | <0.011mg/L
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 |  | <0.019 mg/L
Total Phosphorus | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 |  | Report
Total Nitrogen | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 |  | Report
Flow | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 0.027 | Monitor Only
pH | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 |  | 6.0-9.0
CBOD5 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 5 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 5 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 0.5 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 0.5 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 7.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 23 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 | 23 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 |  | <0.011mg/L
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 |  | <0.019 mg/L
Total Phosphorus | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 |  | Report
Total Nitrogen | 2020-04-01 | 2020-04-30 | 2020-04-10 | 2020-04-15 |  | Report
Flow | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 0.013 | Monitor Only
pH | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 7.61 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | <4 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | <4 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 0.6 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 0.6 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 7 | >7.0 | Y/N
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 19 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 19 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 |  | <0.011mg/L
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 |  | <0.019 mg/L
Total Phosphorus | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 |  | Report
Total Nitrogen | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 |  | Report
Flow | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 0.025 | Monitor Only
pH | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 7.63 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 14 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 14 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 0.3 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 0.3 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 8.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 |  | <0.011mg/L
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 |  | <0.019 mg/L
Total Phosphorus | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 |  | Report
Total Nitrogen | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 |  | Report
Flow | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | 0.042 | Monitor Only
pH | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | 7.23 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | 5 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | 5 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | 7.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | 3 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | 3 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 |  | Report
Total Nitrogen | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-16 |  | Report
Flow | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | 0.164 | Monitor Only
pH | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | 6.81 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | <4 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | <4 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | 2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | 2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | 7.05 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | 2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | 2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 | <0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 |  | Report
Total Nitrogen | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-13 |  | Report
Flow | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 | 0.02 | Monitor Only
pH | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 | 7.91 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 | 5 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 | 5 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 | 8.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 | 4 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 | 4 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 |  | <0.011mg/L
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 |  | <0.019 mg/L
Total Phosphorus | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 |  | Report
Total Nitrogen | 2020-09-01 | 2020-09-30 | 2020-09-04 | 2020-09-11 |  | Report
Flow | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 0.026 | Monitor Only
pH | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 7.25 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 5 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 5 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 28 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 28 | <45 mg/L | No | The elevated TSS in combination with two of the UV lights not working are the most likely cause for the E.coli. The aeration system is in need of repairs to better earate the water. We are looking into having the UV lights repaired, if possible. Updating the aeration, wasting more often, possibly adding a skimmer to the contact chamber and looking at switching to a different polymer or adding histosol to help break the cycle.
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 0.3 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 0.3 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 8.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 461 | <130 #/100mL | No | The elevated TSS in combination with two of the UV lights not working are the most likely cause for the E.coli. The aeration system is in need of repairs to better earate the water. We are looking into having the UV lights repaired, if possible. Updating the aeration, wasting more often, possibly adding a skimmer to the contact chamber and looking at switching to a different polymer or adding histosol to help break the cycle.
E. Coli (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 461 | <240 #100mL | No | The elevated TSS in combination with two of the UV lights not working are the most likely cause for the E.coli. The aeration system is in need of repairs to better earate the water. We are looking into having the UV lights repaired, if possible. Updating the aeration, wasting more often, possibly adding a skimmer to the contact chamber and looking at switching to a different polymer or adding histosol to help break the cycle.
E. Coli (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 71 | <130 #/100mL | Yes | Resample for above
E. Coli (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 71 | <240 #100mL | Yes | Resample for above
E. Coli (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-30 | 2020-11-04 | 26 | <130 #/100mL | Yes | Resample for above
E. Coli (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-30 | 2020-11-04 | 26 | <240 #100mL | Yes | Resample for above
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 |  | <0.011mg/L
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 |  | <0.019 mg/L
Total Phosphorus | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 |  | Report
Total Nitrogen | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 |  | Report
Flow | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 |  | Monitor Only
pH | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 6.58 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | <4 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | <4 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 15 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 15 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | <0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | <0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 6 | >7.0 | No | The DO has been lower than optimal but the weight that keeps the air diffuser under the water, in the contact chamber, had slipped a couple of times this month. The operations team believes it is secured now as they haven't had any issues in the past week.
E. Coli (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 3 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 3 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 |  | <0.011mg/L
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 |  | <0.019 mg/L
Total Phosphorus | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 |  | Report
Total Nitrogen | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 |  | Report
Flow | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 |  | Monitor Only
pH | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 6.67 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 6 | <20 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 13 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 13 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | <0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | <0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 11.15 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 29 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 29 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | <0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 |  | Report
Total Nitrogen | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 |  | Report

## BG-Lake Columbia
BG - Lake Columbia - NPDES KY0077674 | [8 empty] | BG - Lake Columbia - NPDES KY0077674 |  |  | BG - Lake Columbia - NPDES KY0077674
Testing Documentation | [8 empty] | Permit Limits |  |  | Regulatory Compliance
Test Type | Test Period Start Date | Test Period End Date | Sample Date | Date Received | Result | Limit | Compliance | Notes | Paramater | Limit | Frequency | Type | Date | Parameter | Test Result | Limit | Corrective Action | Notes | Compliance Deadline | Date Resolved | File Name
Flow | 2019-09-01 | 2019-09-30 | 2019-09-27 |  |  | Monitor Only |  |  | Flow | Monitor Only | Monthly
pH | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 7.07 | 6.0-9.0 | Yes |  | pH | 6.0-9.0 | Monthly
CBOD5 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <3.00 lbs/day |  |  | CBOD5 (Monthly Avg lbs./Day) | <3.00 lbs/day | Monthly
CBOD5 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <4.50 lbs/day |  |  | CBOD5 (Weekly Avg lbs/day) | <4.50 lbs/day | Monthly
CBOD5 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 19 | <30 mg/L | Yes |  | CBOD5 (Monthly Avg mg/L) | <30 mg/L | Monthly
CBOD5 (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 19 | <45 mg/L | Yes |  | CBOD5 (Weekly Avg mg/L) | <45 mg/L | Monthly
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <3.00 lbs/day |  |  | Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | <3.00 lbs/day | Monthly
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <4.50 lbs/day |  |  | Total Suspened Solids(TSS) (Weekly Avg lbs/day) | <4.50 lbs/day | Monthly
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 19 | <30 mg/L | Yes |  | Total Suspened Solids(TSS) (Monthly Avg mg/L) | <30 mg/L | Monthly
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 19 | <45 mg/L | Yes |  | Total Suspened Solids(TSS) (Weekly Avg mg/L) | <45 mg/L | Monthly
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <0.40 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | <0.40 lbs/day | Monthly
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <0.60 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | <0.60 lbs/day | Monthly
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 0.8 | <4.0 mg/L | Yes |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | <4.0 mg/L | Monthly
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 0.8 | <6.0 mg/L | Yes |  | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | <6.0 mg/L | Monthly
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <1.00 lbs/day |  |  | Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | <1.00 lbs/day | Monthly
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <1.50 lbs/day |  |  | Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | <1.50 lbs/day | Monthly
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <10 mg/L |  |  | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | <10 mg/L | Monthly
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | N/A | <15 mg/L |  |  | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | <15 mg/L | Monthly
Dissolved Oxygen (DO) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 8.6 | >7.0 | Yes |  | Dissolved Oxygen (DO) | >7.0 | Monthly
E. Coli (Monthly Avg) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 60000 | <130 #/100mL | No |  | E. Coli (Monthly Avg) | <130 #/100mL | Monthly
E. Coli (Weekly Avg) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 60000 | <240 #100mL | No |  | E. Coli (Weekly Avg) | <240 #100mL | Monthly
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 0.01 | <0.011mg/L | Yes |  | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | <0.011mg/L | Monthly
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 0.01 | <0.019 mg/L | Yes |  | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | <0.019 mg/L | Monthly
Total Phosphorus | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 1.71 | Report |  |  | Total Phosphorus | Report | Monthly
Total Nitrogen | 2019-09-01 | 2019-09-30 | 2019-09-27 |  | 9.4 | Report |  |  | Total Nitrogen | Report | Monthly
Flow | 2019-10-01 | 2019-10-31 | 2019-10-11 |  |  | Monitor Only
pH | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 7.51 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <3.00 lbs/day
CBOD5 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <4.50 lbs/day
CBOD5 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 12 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 12 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <3.00 lbs/day
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <4.50 lbs/day
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 88 | <30 mg/L | No
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 88 | <45 mg/L | No
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <0.40 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <0.60 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 0.4 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 0.4 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <1.00 lbs/day
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <1.50 lbs/day
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <10 mg/L
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | N/A | <15 mg/L
Dissolved Oxygen (DO) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 7.2 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 27 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 27 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 2.09 | Report
Total Nitrogen | 2019-10-01 | 2019-10-31 | 2019-10-11 |  | 6.8 | Report
Flow | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 0.002 | Monitor Only
pH | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 7.41 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 16 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 16 | <45 mg/L | yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 14 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 14 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 11.7 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 1300 | <130 #/100mL | No
E. Coli (Weekly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 1300 | <240 #100mL | No
E. Coli (Monthly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-27 |  | 1 | <130 #/100mL | Yes | *Resample for above exceeded limit*
E. Coli (Weekly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-27 |  | 1 | <240 #100mL | Yes | *Resample for above exceeded limit*
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 2.21 | Report
Total Nitrogen | 2019-11-01 | 2019-11-30 | 2019-11-15 |  | 3.2 | Report
Flow | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.005 | Monitor Only
pH | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 8.01 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 15 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 15 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 19 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 19 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | N/A | <4.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | N/A | <6.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 8.6 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 1300 | <130 #/100mL | No
E. Coli (Weekly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 1300 | <240 #100mL | No
E. Coli (Monthly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-12 | 2019-12-26 | 16 | <130 #/100mL | Yes | *Resample for above exceeded limit*
E. Coli (Weekly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-12 | 2019-12-26 | 16 | <240 #100mL | Yes | *Resample for above exceeded limit*
E. Coli (Monthly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-13 | 2019-12-26 | 1 | <130 #/100mL | Yes | *Resample for above exceeded limit*
E. Coli (Weekly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-13 | 2019-12-26 | 1 | <240 #100mL | Yes | *Resample for above exceeded limit*
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 1.77 | Report
Total Nitrogen | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 2.4 | Report
Flow | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 0.058 | Monitor Only
pH | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 7.19 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 11 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 11 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 19 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 19 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 8.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 36 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 36 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 2.37 | Report
Total Nitrogen | 2020-01-01 | 2020-01-31 | 2020-01-17 | 2020-01-28 | 1.8 | Report
Flow | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | 0.154 | Monitor Only
pH | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | 7.48 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | 11 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | 11 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | 18 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | 18 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | <0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | <0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | 10.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | 1733 | <130 #/100mL | No | Under CAP
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | 1733 | <240 #100mL | No | Under CAP
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-02-26 | 1414 | <130 #/100mL | No | Resample for above
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-02-26 | 1414 | <240 #100mL | No | Resample for above
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-04 | 38 | <130 #/100mL | Yes | Resample for above
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-27 | 2020-03-04 | 38 | <240 #100mL | Yes | Resample for above
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | 1.21 | Report
Total Nitrogen | 2020-02-01 | 2020-02-29 | 2020-02-14 | 2020-02-26 | 2.3 | Report
Flow | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 0.074 | Monitor Only
pH | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 6.73 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 20 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 20 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 34 | <30 mg/L | No | Due to accumulated layers of sludge in the contact chamber. S;udge was not removed at this time because it just been hauled mid Feb but they did set up a protable pump to pump from the contact chamber back to the aeration tank.
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 34 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | <0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | <0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 10.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 5.02 | Report
Total Nitrogen | 2020-03-01 | 2020-03-31 | 2020-03-09 | 2020-03-19 | 3 | Report
Flow | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 0.005 | Monitor Only
pH | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 7.81 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 23 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 23 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 496 | <30 mg/L | No | Pin flock caused bulking of sludge in the contact tank which resulted in high TSS
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 496 | <45 mg/L | No | Pin flock caused bulking of sludge in the contact tank which resulted in high TSS
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 10.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 61 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 61 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 7.83 | Report
Total Nitrogen | 2020-04-01 | 2020-04-30 | 2020-04-17 | 2020-04-24 | 23.6 | Report
Flow | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 0.04 | Monitor Only
pH | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 7.81 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 12 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 12 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 0.4 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 0.4 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 8.37 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 649 | <130 #/100mL | No | Under CAP
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 649 | <240 #100mL | No | Under CAP
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-18 | 60000 | <130 #/100mL | No | Resample
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-11 | 2020-05-18 | 60000 | <240 #100mL | No | Resample
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-13 | 2020-05-18 | 26 | <130 #/100mL | Yes | Resample
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-13 | 2020-05-18 | 26 | <240 #100mL | Yes | Resample
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-13 | 2020-05-18 | 31 | <130 #/100mL | Yes | Resample
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-13 | 2020-05-18 | 31 | <240 #100mL | Yes | Resample
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-13 | 2020-05-18 | 921 | <130 #/100mL | No | Resample
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-13 | 2020-05-18 | 921 | <240 #100mL | No | Resample
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-15 | 2020-05-18 | <1 | <130 #/100mL | Yes | Resample
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-15 | 2020-05-18 | <1 | <240 #100mL | Yes | Resample
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-15 | 2020-05-18 | <1 | <130 #/100mL | Yes | Resample
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-15 | 2020-05-18 | <1 | <240 #100mL | Yes | Resample
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 5.07 | Report
Total Nitrogen | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-15 | 2.1 | Report
Flow | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.015 | Monitor Only
pH | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 7.88 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 8 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 8 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 11 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 11 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 9.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 4.32 | Report
Total Nitrogen | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 11.3 | Report
Flow | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | 0.018 | Monitor Only
pH | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | 7.87 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | 11 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | 11 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | 11 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | 11 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | 10 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | 5.86 | Report
Total Nitrogen | 2020-07-01 | 2020-07-31 | 2020-07-08 | 2020-07-27 | 26.5 | Report
Flow | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 0.068 | Monitor Only
pH | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 7.46 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | <4 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | <4 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | <0.2 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | <0.2 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 7.02 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | <0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 4.96 | Report
Total Nitrogen | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 32.2 | Report
Flow | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | 0.064 | Monitor Only
pH | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | 6.56 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | <4 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | <4 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | 2.6 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | 2.6 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | 7.86 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | 6.58 | Report
Total Nitrogen | 2020-09-01 | 2020-09-30 | 2020-09-14 | 2020-09-23 | 3.6 | Report
Flow | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 0.013 | Monitor Only
pH | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 6.71 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | <4 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | <4 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 12 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 12 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 1.7 | <4.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 1.7 | <6.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | N/A | <10 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | N/A | <15 mg/L | N/A
Dissolved Oxygen (DO) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 7.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 3.71 | Report
Total Nitrogen | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 31.4 | Report
Flow | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 |  | Monitor Only
pH | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 6.12 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | <4 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | <4 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 19 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 19 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | <0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | <0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 9.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 18 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 18 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 6.43 | Report
Total Nitrogen | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 35.1 | Report
Flow | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 |  | Monitor Only
pH | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | 6.63 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | <4 | <30 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | <4 | <45 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | 26 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | 26 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | N/A | <4.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | N/A | <6.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | <0.2 | <10 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | <0.2 | <15 mg/L | Yes
Dissolved Oxygen (DO) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | 9.35 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | <0.01 | <0.019 mg/L | Yes
Total Phosphorus | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | 3.83 | Report
Total Nitrogen | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21 | 34.6 | Report
| 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-21

## BG-LH
| BG - LH - NPDES KY0081591 | [8 empty] | BG - LH - NPDES KY0081591 |  |  | BG - LH - NPDES KY0081591
| Testing Documentation | [8 empty] | Permit Limits |  |  | Regulatory Compliance
# | Test Type | Test Period Start Date | Test Period End Date | Sample Date | Date Received | Result | Limit | Compliance | Notes | Paramater | Limit | Frequency | Type | Date | Parameter | Test Result | Limit | Corrective Action | Notes | Compliance Deadline | Date Resolved | File Name
1 | Flow | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.046 | Monitor Only |  |  | Flow | Monitor Only | 1/week
2 | pH | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 7.13 | 6.0-9.0 | Yes |  | pH | 6.0-9.0 | 1/week
3 | CBOD5 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <25.0 lbs/day |  |  | CBOD5 (Monthly Avg lbs./Day) | <25.0 lbs/day | 1/week
4 | CBOD5 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <37.53 lbs/day |  |  | CBOD5 (Weekly Avg lbs/day) | <37.53 lbs/day | 1/week
5 | CBOD5 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 8 | <30 mg/L | Yes |  | CBOD5 (Monthly Avg mg/L) | <30 mg/L | 1/week
6 | CBOD5 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 8 | <45 mg/L | Yes |  | CBOD5 (Weekly Avg mg/L) | <45 mg/L | 1/week
7 | Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <25.0 lbs/day |  |  | Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | <25.0 lbs/day | 1/week
8 | Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <37.53 lbs/day |  |  | Total Suspened Solids(TSS) (Weekly Avg lbs/day) | <37.53 lbs/day | 1/week
9 | Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 14 | <30 mg/L | Yes |  | Total Suspened Solids(TSS) (Monthly Avg mg/L) | <30 mg/L | 1/week
10 | Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 14 | <45 mg/L | Yes |  | Total Suspened Solids(TSS) (Weekly Avg mg/L) | <45 mg/L | 1/week
11 | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <3.34 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | <3.34 lbs/day | 1/week
12 | Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <5.0 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | <5.0 lbs/day | 1/week
13 | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.2 | <4.0 mg/L | Yes |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | <4.0 mg/L | 1/week
14 | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.2 | <6.0 mg/L | Yes |  | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | <6.0 mg/L | 1/week
15 | Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <8.34 lbs/day |  |  | Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | <8.34 lbs/day | 1/week
16 | Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <12.5 lbs/day |  |  | Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | <12.5 lbs/day | 1/week
17 | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <10 mg/L |  |  | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | <10 mg/L | 1/week
18 | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | N/A | <15 mg/L |  |  | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | <15 mg/L | 1/week
19 | Dissolved Oxygen (DO) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 8.72 | >7.0 | Yes |  | Dissolved Oxygen (DO) | >7.0 | 1/week
20 | E. Coli (Monthly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 6 | <130 #/100mL | Yes |  | E. Coli (Monthly Avg) | <130 #/100mL | 1/week
21 | E. Coli (Weekly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 6 | <240 #100mL | Yes |  | E. Coli (Weekly Avg) | <240 #100mL | 1/week
22 | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.01 | <0.011mg/L | Yes |  | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | <0.011mg/L | 1/week
23 | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-10 |  | 0.01 | <0.019 mg/L | Yes |  | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | <0.019 mg/L | 1/week
24
25 | Flow | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 0.107 | Monitor Only
26 | pH | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 7.9 | 6.0-9.0 | Yes
27 | CBOD5 (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <25.0 lbs/day |  |  | **Permit states monitoring frequency is Monthly**
28 | CBOD5 (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <37.53 lbs/day
29 | CBOD5 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 6 | <30 mg/L | Yes
30 | CBOD5 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 6 | <45 mg/L | Yes
31 | Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <25.0 lbs/day
32 | Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <37.53 lbs/day
33 | Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 6 | <30 mg/L | Yes
34 | Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 6 | <45 mg/L | Yes
35 | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <3.34 lbs/day
36 | Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <5.0 lbs/day
37 | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <4.0 mg/L
38 | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <6.0 mg/L
39 | Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <8.34 lbs/day
40 | Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | N/A | <12.5 lbs/day
41 | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 4.7 | <10 mg/L | Yes
42 | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 4.7 | <15 mg/L | Yes
43 | Dissolved Oxygen (DO) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 10.9 | >7.0 | Yes
44 | E. Coli (Monthly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 3 | <130 #/100mL | Yes
45 | E. Coli (Weekly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 3 | <240 #100mL | Yes
46 | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 0.01 | <0.011mg/L | Yes
47 | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-08 |  | 0.01 | <0.019 mg/L | Yes
48
49 | Flow | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.045 | Monitor Only
50 | pH | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 7.11 | 6.0-9.0 | Yes
51 | CBOD5 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 6 | <30 mg/L | Yes
52 | CBOD5 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 6 | <45 mg/L | Yes
53 | Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 6 | <30 mg/L | Yes
54 | Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 6 | <45 mg/L | Yes
55 | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | N/A | <4.0 mg/L
56 | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | N/A | <6.0 mg/L
57 | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.2 | <10 mg/L | Yes
58 | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.2 | <15 mg/L | Yes
59 | Dissolved Oxygen (DO) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 9.65 | >7.0 | Yes
60 | E. Coli (Monthly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 1 | <130 #/100mL | Yes
61 | E. Coli (Weekly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 1 | <240 #100mL | Yes
62 | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.01 | <0.011mg/L | Yes
63 | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-06 | 2019-12-13 | 0.01 | <0.019 mg/L | Yes
64
65 | Flow | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-02-17 | 0.043 | Monitor Only
66 | pH | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 6.77 | 6.0-9.0 | Yes
67 | CBOD5 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 4 | <30 mg/L | Yes
68 | CBOD5 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 4 | <45 mg/L | Yes
69 | Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 6 | <30 mg/L | Yes
70 | Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 6 | <45 mg/L | Yes
71 | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | N/A | <4.0 mg/L | N/A
72 | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | N/A | <6.0 mg/L | N/A
73 | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.2 | <10 mg/L | Yes
74 | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.2 | <15 mg/L | Yes
75 | Dissolved Oxygen (DO) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 9 | >7.0 | Yes
76 | E. Coli (Monthly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 1 | <130 #/100mL | Yes
77 | E. Coli (Weekly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 1 | <240 #100mL | Yes
78 | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.01 | <0.011mg/L | Yes
79 | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-10 | 2020-01-17 | 0.01 | <0.019 mg/L | Yes
80
81 | Flow | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 0.06 | Monitor Only
82 | pH | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 7.46 | 6.0-9.0 | Yes
83 | CBOD5 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 8 | <30 mg/L | Yes
84 | CBOD5 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 8 | <45 mg/L | Yes
85 | Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <6.00 | <30 mg/L | Yes
86 | Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <6.00 | <45 mg/L | Yes
87 | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | N/A | <4.0 mg/L | N/A
88 | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | N/A | <6.0 mg/L | N/A
89 | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 0.5 | <10 mg/L | Yes
90 | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 0.5 | <15 mg/L | Yes
91 | Dissolved Oxygen (DO) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 8.12 | >7.0 | Yes
92 | E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 2 | <130 #/100mL | Yes
93 | E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | 2 | <240 #100mL | Yes
94 | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <0.010 | <0.011mg/L | Yes
95 | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-21 | 2020-03-04 | <0.010 | <0.019 mg/L | Yes
96
97 | Flow | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 0.009 | Monitor Only
98 | pH | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 6.93 | 6.0-9.0 | Yes
99 | CBOD5 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 4 | <30 mg/L | Yes
100 | CBOD5 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 4 | <45 mg/L | Yes
101 | Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | <6 | <30 mg/L | Yes
102 | Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | <6 | <45 mg/L | Yes
103 | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | N/A | <4.0 mg/L | N/A
104 | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | N/A | <6.0 mg/L | N/A
105 | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 1 | <10 mg/L | Yes
106 | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 1 | <15 mg/L | Yes
107 | Dissolved Oxygen (DO) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 4 | >7.0 | No | Due to heavy rains and high flows, the blowers were cut off.
108 | E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 16 | <130 #/100mL | Yes
109 | E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 | 16 | <240 #100mL | Yes
110 | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 |  | <0.011mg/L
111 | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-13 | 2020-03-20 |  | <0.019 mg/L
112
113 | Flow | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 0.043 | Monitor Only
114 | pH | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 7.74 | 6.0-9.0 | Yes
115 | CBOD5 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | <4 | <30 mg/L | Yes
116 | CBOD5 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | <4 | <45 mg/L | Yes
117 | Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | <6 | <30 mg/L | Yes
118 | Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | <6 | <45 mg/L | Yes
119 | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | N/A | <4.0 mg/L | N/A
120 | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | N/A | <6.0 mg/L | N/A
121 | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 2 | <10 mg/L | Yes
122 | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 2 | <15 mg/L | Yes
123 | Dissolved Oxygen (DO) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 8.9 | >7.0 | Yes
124 | E. Coli (Monthly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 19 | <130 #/100mL | Yes
125 | E. Coli (Weekly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | 19 | <240 #100mL | Yes
126 | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | <0.01 | <0.011mg/L | Yes
127 | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-03 | 2020-04-13 | <0.01 | <0.019 mg/L | Yes
128
129 | Flow | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 0.142 | Monitor Only
130 | pH | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 7.67 | 6.0-9.0 | Yes
131 | CBOD5 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 5 | <30 mg/L | Yes
132 | CBOD5 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 5 | <45 mg/L | Yes
133 | Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | <6 | <30 mg/L | Yes
134 | Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | <6 | <45 mg/L | Yes
135 | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | <0.2 | <4.0 mg/L | Yes
136 | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | <0.2 | <6.0 mg/L | Yes
137 | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | N/A | <10 mg/L | N/A
138 | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | N/A | <15 mg/L | N/A
139 | Dissolved Oxygen (DO) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 8.7 | >7.0 | Yes
140 | E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 24 | <130 #/100mL | Yes
141 | E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | 24 | <240 #100mL | Yes
142 | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | <0.01 | <0.011mg/L | Yes
143 | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-08 | 2020-05-14 | <0.01 | <0.019 mg/L | Yes
| Flow | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.04 | Monitor Only
| pH | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 7.61 | 6.0-9.0 | Yes
| CBOD5 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 11 | <30 mg/L | Yes
| CBOD5 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 11 | <45 mg/L | Yes
| Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 9 | <30 mg/L | Yes
| Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 9 | <45 mg/L | Yes
| Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 11.3 | <4.0 mg/L | No | Line was partially blocked by grease, which caused the wastewater to turn septic. Beckmar set up composite sampler for 6/25/2020.
| Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 11.3 | <6.0 mg/L | No | Line was partially blocked by grease, which caused the wastewater to turn septic. Beckmar set up composite sampler for 6/25/2020.
| Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | N/A | <10 mg/L | N/A
| Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | N/A | <15 mg/L | N/A
| Dissolved Oxygen (DO) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 7.95 | >7.0 | Yes
| E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 14 | <130 #/100mL | Yes
| E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 14 | <240 #100mL | Yes
| Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.01 | <0.011mg/L | Yes
| Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-12 | 2020-06-19 | 0.01 | <0.019 mg/L | Yes
| Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-26 | 2020-06-30 | 0.7 | <4.0 mg/L | No | Second set of ammonia samples to meet monthly average. Need thrid set to be below limit.
| Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 |  |  |  | <4.0 mg/L |  | Third set of ammonia samples to meet monthly average.
| Flow | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 0.034 | Monitor Only
| pH | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 7.78 | 6.0-9.0 | Yes
| CBOD5 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 4 | <30 mg/L | Yes
| CBOD5 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 4 | <45 mg/L | Yes
| Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | <6 | <30 mg/L | Yes
| Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | <6 | <45 mg/L | Yes
| Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | <0.2 | <4.0 mg/L | Yes
| Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | <0.2 | <6.0 mg/L | Yes
| Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | N/A | <10 mg/L | N/A
| Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | N/A | <15 mg/L | N/A
| Dissolved Oxygen (DO) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 8.07 | >7.0 | Yes
| E. Coli (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 103 | <130 #/100mL | Yes
| E. Coli (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | 103 | <240 #100mL | Yes
| Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | <0.01 | <0.011mg/L | Yes
| Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-09 | 2020-07-20 | <0.01 | <0.019 mg/L | Yes
| Flow | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | 0.036 | Monitor Only
| pH | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | 7.42 | 6.0-9.0 | Yes
| CBOD5 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | <4 | <30 mg/L | Yes
| CBOD5 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | <4 | <45 mg/L | Yes
| Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | <6 | <30 mg/L | Yes
| Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | <6 | <45 mg/L | Yes
| Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | 1.2 | <4.0 mg/L | Yes
| Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | 1.2 | <6.0 mg/L | Yes
| Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | N/A | <10 mg/L | N/A
| Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | N/A | <15 mg/L | N/A
| Dissolved Oxygen (DO) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | 7.73 | >7.0 | Yes
| E. Coli (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | 65 | <130 #/100mL | Yes
| E. Coli (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | 65 | <240 #100mL | Yes
| Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | <0.01 | <0.011mg/L | Yes
| Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-14 | 2020-08-24 | <0.01 | <0.019 mg/L | Yes
| Flow | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 0.035 | Monitor Only
| pH | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 7.16 | 6.0-9.0 | Yes
| CBOD5 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 5 | <30 mg/L | Yes
| CBOD5 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 5 | <45 mg/L | Yes
| Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <6 | <30 mg/L | Yes
| Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <6 | <45 mg/L | Yes
| Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 0.3 | <4.0 mg/L | Yes
| Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 0.3 | <6.0 mg/L | Yes
| Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | N/A | <10 mg/L | N/A
| Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | N/A | <15 mg/L | N/A
| Dissolved Oxygen (DO) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 8.45 | >7.0 | Yes
| E. Coli (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 68 | <130 #/100mL | Yes
| E. Coli (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | 68 | <240 #100mL | Yes
| Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <0.01 | <0.011mg/L | Yes
| Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-11 | 2020-09-22 | <0.01 | <0.019 mg/L | Yes
| Flow | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | 0.036 | Monitor Only
| pH | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | 6.8 | 6.0-9.0 | Yes
| CBOD5 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | 6 | <30 mg/L | Yes
| CBOD5 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | 6 | <45 mg/L | Yes
| Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | 16 | <30 mg/L | Yes
| Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | 16 | <45 mg/L | Yes
| Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | 0.3 | <4.0 mg/L | Yes
| Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | 0.3 | <6.0 mg/L | Yes
| Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | N/A | <10 mg/L | N/A
| Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | N/A | <15 mg/L | N/A
| Dissolved Oxygen (DO) | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | 8.75 | >7.0 | Yes
| E. Coli (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | 22 | <130 #/100mL | Yes
| E. Coli (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | 22 | <240 #100mL | Yes
| Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | <0.01 | <0.011mg/L | Yes
| Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-16 | 2020-10-26 | <0.01 | <0.019 mg/L | Yes
| Flow | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 |  | Monitor Only
| pH | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 7.42 | 6.0-9.0 | Yes
| CBOD5 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 8 | <30 mg/L | Yes
| CBOD5 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 8 | <45 mg/L | Yes
| Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 9 | <30 mg/L | Yes
| Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 9 | <45 mg/L | Yes
| Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | N/A | <4.0 mg/L | N/A
| Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | N/A | <6.0 mg/L | N/A
| Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 0.4 | <10 mg/L | Yes
| Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 0.4 | <15 mg/L | Yes
| Dissolved Oxygen (DO) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 9.3 | >7.0 | Yes
| E. Coli (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 137 | <130 #/100mL | No | When the operations team demolished the old building to instal the new building, the chemical tanks and pumpls had to be moved. During that switch over, there wasn't enough bleach being fed.
| E. Coli (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | 137 | <240 #100mL | Yes
| E. Coli (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-17 | 2020-11-20 | 9 | <130 #/100mL | Yes
| E. Coli (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-17 | 2020-11-20 | 9 | <240 #100mL | Yes | Resample for above
| Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <0.01 | <0.011mg/L | Yes
| Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-06 | 2020-11-12 | <0.01 | <0.019 mg/L | Yes
| Flow | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 |  | Monitor Only
| pH | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 7.53 | 6.0-9.0 | Yes
| CBOD5 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 4 | <30 mg/L | Yes
| CBOD5 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 4 | <45 mg/L | Yes
| Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 15 | <30 mg/L | Yes
| Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 15 | <45 mg/L | Yes
| Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | N/A | <4.0 mg/L | N/A
| Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | N/A | <6.0 mg/L | N/A
| Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | <0.2 | <10 mg/L | Yes
| Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | <0.2 | <15 mg/L | Yes
| Dissolved Oxygen (DO) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 9.43 | >7.0 | Yes
| E. Coli (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 517 | <130 #/100mL | No | Nitrification in the clarifier causing pin flock & solids in the effluent. The operator is working with the chemical supplier to add a biological treatment to resolve the issue.
| E. Coli (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 517 | <240 #100mL | No | Nitrification in the clarifier causing pin flock & solids in the effluent. The operator is working with the chemical supplier to add a biological treatment to resolve the issue.
| E. Coli (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-15 | 34 | <130 #/100mL | Yes | Resample for above
| E. Coli (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-10 | 2020-12-15 | 34 | <240 #100mL | Yes | Resample for above
| Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 0.01 | <0.011mg/L | Yes
| Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-04 | 2020-12-11 | 0.01 | <0.019 mg/L | Yes

## BG-Persimmon Ridge
BG - Persimmon Ridge - NPDES KY0090956 | [8 empty] | BG - Persimmon Ridge - NPDES KY0090956 |  |  | BG - Persimmon Ridge - NPDES KY0090956
Testing Documentation | [8 empty] | Permit Limits |  |  | Regulatory Compliance
Test Type | Test Period Start Date | Test Period End Date | Sample Date | Date Received | Result | Limit | Compliance | Notes | Paramater | Limit | Frequency | Type | Date | Parameter | Test Result | Limit | Corrective Action | Notes | Compliance Deadline | Date Resolved | File Name
Flow | 2019-09-01 | 2019-09-30 | 2019-09-19 |  |  | Monitor Only |  |  | Flow | Monitor Only | 2/Monthly
pH | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | 7.43 | 6.0-9.0 | Yes |  | pH | 6.0-9.0 | 2/Monthly
CBOD5 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | N/A | <11.8 lbs/day |  |  | CBOD5 (Monthly Avg lbs./Day) | <11.8 lbs/day | 2/Monthly
CBOD5 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | N/A | <17.8 lbs/day |  |  | CBOD5 (Weekly Avg lbs/day) | <17.8 lbs/day | 2/Monthly
CBOD5 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | 4 | <10 mg/L | Yes |  | CBOD5 (Monthly Avg mg/L) | <10 mg/L | 2/Monthly
CBOD5 (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | 4 | <15 mg/L | Yes |  | CBOD5 (Weekly Avg mg/L) | <15 mg/L | 2/Monthly
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | N/A | <35.5 lbs/day |  |  | Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | <35.5 lbs/day | 2/Monthly
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | N/A | <53.3 lbs/day |  |  | Total Suspened Solids(TSS) (Weekly Avg lbs/day) | <53.3 lbs/day | 2/Monthly
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | 6 | <30 mg/L | Yes |  | Total Suspened Solids(TSS) (Monthly Avg mg/L) | <30 mg/L | 2/Monthly
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | 6 | <45 mg/L | Yes |  | Total Suspened Solids(TSS) (Weekly Avg mg/L) | <45 mg/L | 2/Monthly
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | N/A | <2.4 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | <2.4 lbs/day | 2/Monthly
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | N/A | <3.6 lbs/day |  |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | <3.6 lbs/day | 2/Monthly
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | 0.2 | <2.0 mg/L | Yes |  | Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | <2.0 mg/L | 2/Monthly
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | 0.2 | <3.0 mg/L | Yes |  | Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | <3.0 mg/L | 2/Monthly
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | N/A | <5.9 lbs/day |  |  | Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | <5.9 lbs/day | 2/Monthly
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | N/A | <8.9 lbs/day |  |  | Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | <8.9 lbs/day | 2/Monthly
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | N/A | <5.0 mg/L |  |  | Ammonia Nov 1-April 30 (Monthly Avg mg/L) | <5.0 mg/L | 2/Monthly
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | N/A | <7.5 mg/L |  |  | Ammonia Nov 1-April 30 (Weekly Avg mg/L) | <7.5 mg/L | 2/Monthly
Dissolved Oxygen (DO) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | 8 | >7.0 | Yes |  | Dissolved Oxygen (DO) | >7.0 | 2/Monthly
E. Coli (Monthly Avg) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | 1 | <130 #/100mL | Yes |  | E. Coli (Monthly Avg) | <130 #/100mL | 2/Monthly
E. Coli (Weekly Avg) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | 1 | <240 #100mL | Yes |  | E. Coli (Weekly Avg) | <240 #100mL | 2/Monthly
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | 0.01 | <0.011mg/L | Yes |  | Total Residual Chlorine (TRC) (Monthly Avg mg/L) | <0.011mg/L | 2/Monthly
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | 0.01 | <0.019 mg/L | Yes |  | Total Residual Chlorine (TRC) (Weekly Avg mg/L) | <0.019 mg/L | 2/Monthly
Total Phosphorus (TP) | 2019-09-01 | 2019-09-30 | 2019-09-19 |  | 3.6 | Report |  |  | Total Phosphorus (TP) | Report | 2/Monthly
Total Nitrogen | 2019-09-01 | 2019-09-30 |  |  | 2.9 | Report |  |  | Total Nitrogen | Report | 2/Monthly
Flow | 2019-10-01 | 2019-10-31 | 2019-10-03 |  |  | Monitor Only
pH | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 7.35 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | N/A | <11.8 lbs/day
CBOD5 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | N/A | <17.8 lbs/day
CBOD5 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 5 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 5 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | N/A | <35.5 lbs/day
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | N/A | <53.3 lbs/day
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | N/A | <2.4 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | N/A | <3.6 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 0.2 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 0.2 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | N/A | <5.9 lbs/day
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | N/A | <8.9 lbs/day
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | N/A | <5.0 mg/L
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | N/A | <7.5 mg/L
Dissolved Oxygen (DO) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 8.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 4.11 | Report
Total Nitrogen | 2019-10-01 | 2019-10-31 | 2019-10-03 |  | 2.7 | Report
Flow | 2019-10-01 | 2019-10-31 | 2019-10-17 |  |  | Monitor Only
pH | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 7.3 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | N/A | <11.8 lbs/day
CBOD5 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | N/A | <17.8 lbs/day
CBOD5 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | N/A | <35.5 lbs/day
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | N/A | <53.3 lbs/day
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | N/A | <2.4 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | N/A | <3.6 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 0.2 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 0.2 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | N/A | <5.9 lbs/day
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | N/A | <8.9 lbs/day
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | N/A | <5.0 mg/L
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | N/A | <7.5 mg/L
Dissolved Oxygen (DO) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 9.41 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 4.53 | Report
Total Nitrogen | 2019-10-01 | 2019-10-31 | 2019-10-17 |  | 2.6 | Report
Flow | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 0.07 | Monitor Only
pH | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 7.87 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | N/A | <11.8 lbs/day
CBOD5 (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | N/A | <17.8 lbs/day
CBOD5 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | N/A | <35.5 lbs/day
Total Suspened Solids(TSS) (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | N/A | <53.3 lbs/day
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | N/A | <2.4 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | N/A | <3.6 lbs/day
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | N/A | <2.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | N/A | <3.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg lbs./Day) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | N/A | <5.9 lbs/day
Ammonia Nov 1-April 30 (Weekly Avg lbs/day) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | N/A | <8.9 lbs/day
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 0.7 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 0.7 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 11.3 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 3.94 | Report
Total Nitrogen | 2019-11-01 | 2019-11-30 | 2019-11-07 |  | 1.9 | Report
Flow | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 0.068 | Monitor Only
pH | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 8.1 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 5 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 5 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 1 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 1 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 12.6 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 24 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 24 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 4.21 | Report
Total Nitrogen | 2019-11-01 | 2019-11-30 | 2019-11-20 | 2019-12-02 | 2.1 | Report
Flow | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 0.085 | Monitor Only
pH | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 8.13 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 6 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 6 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | N/A | <2.0 mg/L
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | N/A | <3.0 mg/L
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 3 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 3 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 12.55 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 308 | <130 #/100mL | No
E. Coli (Weekly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 308 | <240 #100mL | No
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 3.54 | Report
Total Nitrogen | 2019-12-01 | 2019-12-31 | 2019-12-05 | 2019-12-13 | 4.5 | Report
Flow | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 0.085 | Monitor Only
pH | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 8.28 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 6 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 6 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 13 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 13 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 4.4 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 4.4 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 11.54 | >7.0 | Yes
E. Coli (Monthly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 101 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 101 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 4.01 | Report
Total Nitrogen | 2019-12-01 | 2019-12-31 | 2019-12-19 | 2020-01-06 | 10.3 | Report
Flow | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 |  | Monitor Only
pH | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 7.57 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 10 | <10 mg/L
CBOD5 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 10 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 9 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 9 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 6.5 | <5.0 mg/L | No | Under CAP
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 6.5 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 10.9 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 18 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 18 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 3.79 | Report
Total Nitrogen | 2020-01-01 | 2020-01-31 | 2020-01-09 | 2020-01-21 | 10.9 | Report
Flow | 2020-01-01 | 2020-01-31 |  |  | 0.094 | Monitor Only
pH | 2020-01-01 | 2020-01-31 |  |  |  | 6.0-9.0 |  | Lab didn't take samples - See Email
CBOD5 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 |  |  | 7.805 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 |  |  | 7.805 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 |  |  | 7.025 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 |  |  | 7.025 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 |  |  | N/A | <2.0 mg/L |  | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 |  |  | N/A | <3.0 mg/L |  | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 |  |  | 5.073 | <5.0 mg/L | No | Under CAP
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 |  |  | 5.073 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2020-01-01 | 2020-01-31 |  |  |  | >7.0 |  | Lab didn't take samples - See Email
E. Coli (Monthly Avg) | 2020-01-01 | 2020-01-31 |  |  |  | <130 #/100mL |  | Lab didn't take samples - See Email
E. Coli (Weekly Avg) | 2020-01-01 | 2020-01-31 |  |  |  | <240 #100mL |  | Lab didn't take samples - See Email
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-01-01 | 2020-01-31 |  |  |  | <0.011mg/L |  | Lab didn't take samples - See Email
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-01-01 | 2020-01-31 |  |  |  | <0.019 mg/L |  | Lab didn't take samples - See Email
Total Phosphorus (TP) | 2020-01-01 | 2020-01-31 |  |  |  | Report |  | Lab didn't take samples - See Email
Total Nitrogen | 2020-01-01 | 2020-01-31 |  |  |  | Report |  | Lab didn't take samples - See Email
Flow | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-14 | 0.08 | Monitor Only
pH | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-15 | 7.42 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-16 | 10 | <10 mg/L | Y/N
CBOD5 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-17 | 10 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-18 | 20 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-19 | 20 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-20 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-21 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-22 | 7.5 | <5.0 mg/L | No | Under CAP
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-23 | 7.5 | <7.5 mg/L | Y/N
Dissolved Oxygen (DO) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-24 | 10.85 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-25 | 24 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-26 | 24 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-27 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-28 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-02-29 | 3.59 | Report
Total Nitrogen | 2020-02-01 | 2020-02-29 | 2020-02-06 | 2020-03-01 | 9.6 | Report
Flow | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 0.08 | Monitor Only
pH | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 8.14 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 7 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 7 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 11 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 11 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 10.5 | <5.0 mg/L | No | Under CAP
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 10.5 | <7.5 mg/L | No | Under CAP
Dissolved Oxygen (DO) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 11.7 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 3 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 3 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 3.59 | Report
Total Nitrogen | 2020-02-01 | 2020-02-29 | 2020-02-20 | 2020-03-03 | 11.2 | Report
Flow | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | 0.099 | Monitor Only
pH | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | 7.97 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | 14.6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | 14.6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | 9.6 | <5.0 mg/L | No | Operator initially thought the PH was low and affecting the efficiant removal but that isn't the case so she's getting guidance from compliance assistance.
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | 9.6 | <7.5 mg/L | No | Operator initially thought the PH was low and affecting the efficiant removal but that isn't the case so she's getting guidance from compliance assistance.
Dissolved Oxygen (DO) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | 10.8 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | >1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-03-01 | 2020-03-31 | 2020-03-05 | 2020-03-13 | 3.63 | Report
Total Nitrogen | 2020-03-01 | 2020-03-31 | 2020-03-05 |  | 10.8 | Report
Flow | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | 0.099 | Monitor Only
pH | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | 8.15 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | 4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | 4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | 13.4 | <5.0 mg/L | No | Operator started collecting process checks at the beginning and end of each lagoon in order to determine the amont of and where nitrification was occuring. Following the advice from compliance assistance, we also slightly raised the pH in the lagoons.
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | 13.4 | <7.5 mg/L | No | Operator started collecting process checks at the beginning and end of each lagoon in order to determine the amont of and where nitrification was occuring. Following the advice from compliance assistance, we also slightly raised the pH in the lagoons.
Dissolved Oxygen (DO) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | 10.2 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | 488 | <130 #/100mL | No | Operator was still using the old Extec cl2 meter but after E.coli issues, did side by side comparisons and is now using the Hatch at all facilities.
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | 488 | <240 #100mL | No | Operator was still using the old Extec cl2 meter but after E.coli issues, did side by side comparisons and is now using the Hatch at all facilities.
E. Coli (Monthly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-20 | 2020-03-27 | 19 | <130 #/100mL | Yes | Resample for above
E. Coli (Weekly Avg) | 2020-03-01 | 2020-03-31 | 2020-03-20 | 2020-03-27 | 19 | <240 #100mL | Yes | Resample for above
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | 3.26 | Report
Total Nitrogen | 2020-03-01 | 2020-03-31 | 2020-03-19 | 2020-03-27 | 14.7 | Report
Flow | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | 0.07 | Monitor Only
pH | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | 8.13 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | 7 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | 7 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | 15.6 | <5.0 mg/L | No | Operator was still using the old Extec cl2 meter but after E.coli issues, did side by side comparisons and is now using the Hatch at all facilities.
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | 15.6 | <7.5 mg/L | No | Operator was still using the old Extec cl2 meter but after E.coli issues, did side by side comparisons and is now using the Hatch at all facilities.
Dissolved Oxygen (DO) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | 8.5 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | 3.63 | Report
Total Nitrogen | 2020-04-01 | 2020-04-30 | 2020-04-02 | 2020-04-13 | 15.4 | Report
Flow | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | 0.07 | Monitor Only
pH | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | 8.35 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | 14.2 | <5.0 mg/L | No | **per the operator - investigating possible causes**
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | 14.2 | <7.5 mg/L | No | **per the operator - investigating possible causes**
Dissolved Oxygen (DO) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | 8.97 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | <0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | 3.89 | Report
Total Nitrogen | 2020-04-01 | 2020-04-30 | 2020-04-16 | 2020-04-24 | 14.3 | Report
Flow | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | 0.077 | Monitor Only
pH | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | 8.06 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | 15.7 | <2.0 mg/L | No | Combination of cold water temps, less productive bacteria, decaying duckweed, the loss of 1 aerator in the second lagoon, the baffle falling into the water, and oxygen depletion. Added nutrifying bacteria & purchased ammonia testing kit. Also have plans to build simple houseing to install in the second lagoon, start duckweed control, and securly attach baffle.
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | 15.7 | <3.0 mg/L | No | Combination of cold water temps, less productive bacteria, decaying duckweed, the loss of 1 aerator in the second lagoon, the baffle falling into the water, and oxygen depletion. Added nutrifying bacteria & purchased ammonia testing kit. Also have plans to build simple houseing to install in the second lagoon, start duckweed control, and securly attach baffle.
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | 9.41 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | 3.7 | Report
Total Nitrogen | 2020-05-01 | 2020-05-31 | 2020-05-14 | 2020-05-22 | 11.1 | Report
Flow | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | 0.077 | Monitor Only
pH | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | 7.64 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | 4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | 4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | 11.8 | <2.0 mg/L | No | Combination of cold water temps, less productive bacteria, decaying duckweed, the loss of 1 aerator in the second lagoon, the baffle falling into the water, and oxygen depletion. Added nutrifying bacteria & purchased ammonia testing kit. Also have plans to build simple houseing to install in the second lagoon, start duckweed control, and securly attach baffle.
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | 11.8 | <3.0 mg/L | No | Combination of cold water temps, less productive bacteria, decaying duckweed, the loss of 1 aerator in the second lagoon, the baffle falling into the water, and oxygen depletion. Added nutrifying bacteria & purchased ammonia testing kit. Also have plans to build simple houseing to install in the second lagoon, start duckweed control, and securly attach baffle.
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | 7.78 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | 1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | 1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | 5.27 | Report
Total Nitrogen | 2020-05-01 | 2020-05-31 | 2020-05-28 | 2020-06-09 | 10.6 | Report
Flow | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 |  | Monitor Only
pH | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | 7.73 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | 9 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | 9 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | 10 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | 10 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | <0.2 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | <0.2 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | 7.05 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | 2.82 | Report
Total Nitrogen | 2020-06-01 | 2020-06-30 | 2020-06-10 | 2020-06-18 | 9.9 | Report
Flow | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 0.045 | Monitor Only
pH | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 7.69 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | <0.2 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | <0.2 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 7.25 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | <.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | <.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 2.952 | Report
Total Nitrogen | 2020-06-01 | 2020-06-30 | 2020-06-18 | 2020-06-26 | 0.7 | Report
Flow | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 |  | Monitor Only
pH | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | 7.78 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | 4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | 4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | <0.2 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | <0.2 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | 7.43 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | <0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | 3.31 | Report
Total Nitrogen | 2020-07-01 | 2020-07-31 | 2020-07-03 | 2020-07-13 | 3.1 | Report
Flow | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 0.012 | Monitor Only
pH | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 7.95 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | <0.2 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | <0.2 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 7.14 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 4.08 | Report
Total Nitrogen | 2020-07-01 | 2020-07-31 | 2020-07-16 | 2020-07-27 | 2.3 | Report
Flow | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 |  | Monitor Only
pH | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | 7.61 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | <0.2 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | <0.2 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | 7.15 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | <0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | 4.55 | Report
Total Nitrogen | 2020-08-01 | 2020-08-31 | 2020-08-06 | 2020-09-03 | 4 | Report
Flow | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | 0.508 | Monitor Only
pH | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | 6.76 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | 0.4 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | 0.4 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | 7.1 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | 4.91 | Report
Total Nitrogen | 2020-08-01 | 2020-08-31 | 2020-08-20 | 2020-08-26 | 3.3 | Report
Flow | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 |  | Monitor Only
pH | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | 7.77 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | 0.4 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | 0.4 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | 7.9 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | 2 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | 2 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | <0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | 4.86 | Report
Total Nitrogen | 2020-09-01 | 2020-09-30 | 2020-09-03 | 2020-09-11 | 3.2 | Report
Flow | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | 0.054 | Monitor Only
pH | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | 7.7 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | <0.2 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | <0.2 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | 8.05 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | <0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | 6.52 | Report
Total Nitrogen | 2020-09-01 | 2020-09-30 | 2020-09-17 | 2020-09-25 | 3 | Report
Flow | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 |  | Monitor Only
pH | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | 7.85 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | <0.2 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | <0.2 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | 8.74 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | 0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | 0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | 2.98 | Report
Total Nitrogen | 2020-10-01 | 2020-10-31 | 2020-10-09 | 2020-10-22 | 2.4 | Report
Flow | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | 0.06 | Monitor Only
pH | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | 7.45 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | 0.6 | <2.0 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | 0.6 | <3.0 mg/L | Yes
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | N/A | <5.0 mg/L | N/A
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | N/A | <7.5 mg/L | N/A
Dissolved Oxygen (DO) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | 10.15 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | <0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | 2.81 | Report
Total Nitrogen | 2020-10-01 | 2020-10-31 | 2020-10-22 | 2020-10-30 | 3 | Report
Flow | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 |  | Monitor Only
pH | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | 7.48 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | <4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | <4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | <0.2 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | <0.2 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | 10.85 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | <0.010 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | <0.010 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | 1.76 | Report
Total Nitrogen | 2020-11-01 | 2020-11-30 | 2020-11-05 | 2020-11-13 | 3.2 | Report
Flow | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 |  | Monitor Only
pH | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | 9 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | 5 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | 5 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | <0.2 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | <0.2 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | 9.4 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | <0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | 1.7 | Report
Total Nitrogen | 2020-11-01 | 2020-11-30 | 2020-11-19 | 2020-12-01 | 1.4 | Report
Flow | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 |  | Monitor Only
pH | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | 8 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | 6 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | 6 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | 1.6 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | 1.6 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | 11.6 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | <1 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | <1 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | <0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | 1.77 | Report
Total Nitrogen | 2020-12-01 | 2020-12-31 | 2020-12-03 | 2020-12-11 | 5 | Report
Flow | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 |  | Monitor Only
pH | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | 8.16 | 6.0-9.0 | Yes
CBOD5 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | 4 | <10 mg/L | Yes
CBOD5 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | 4 | <15 mg/L | Yes
Total Suspened Solids(TSS) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | <6 | <30 mg/L | Yes
Total Suspened Solids(TSS) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | <6 | <45 mg/L | Yes
Ammonia (as mg/L NH3N) May1-Oct 31 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | N/A | <2.0 mg/L | N/A
Ammonia (as mg/L NH3N) May1-Oct 31(Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | N/A | <3.0 mg/L | N/A
Ammonia Nov 1-April 30 (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | 1.1 | <5.0 mg/L | Yes
Ammonia Nov 1-April 30 (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | 1.1 | <7.5 mg/L | Yes
Dissolved Oxygen (DO) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | 10.65 | >7.0 | Yes
E. Coli (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | 3 | <130 #/100mL | Yes
E. Coli (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | 3 | <240 #100mL | Yes
Total Residual Chlorine (TRC) (Monthly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | <0.01 | <0.011mg/L | Yes
Total Residual Chlorine (TRC) (Weekly Avg mg/L) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | <0.01 | <0.019 mg/L | Yes
Total Phosphorus (TP) | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | 1.77 | Report
Total Nitrogen | 2020-12-01 | 2020-12-31 | 2020-12-17 | 2020-01-05 | 5.7 | Report

## BG - River Bluffs
River Bluffs - NPDES KY0043150 | [8 empty] | River Bluffs - NPDES KY0043150 |  |  | River Bluffs - NPDES KY0043150
Testing Documentation | [8 empty] | Permit Limits |  |  | Regulatory Compliance Schedules
Test Type | Test Period Start Date | Test Period End Date | Sample Date | Date Received | Result | Limit | Compliance | Notes | Paramater | Limit | Frequency | Type | Date | Parameter | Test Result | Limit | Corrective Action | Notes | Compliance Deadline | Date Resolved | File Name
Flow | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 0.079 | Report |  |  | Flow | Report | Monthly
pH | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 7.68 | 6.0-9.0 | Yes |  | pH | 6.0-9.0 | Monthly
CBOD5 (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | N/A | 24.8 lbs/Day | N/A |  | CBOD5 (Weekly Avg) | 24.8 lbs/Day | Monthly
CBOD5 (Monthly Average) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | N/A | 16.5 lbs/day | N/A |  | CBOD5 (Monthly Average) | 16.5 lbs/day | Monthly
CBOD5 (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 7 | <45 mg/L | Yes |  | CBOD5 (Weekly Avg) | 45 mg/L | Monthly
CBOD5 (Monthly Average) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 7 | <30 mg/L | Yes |  | CBOD5 (Monthly Average) | 30 mg/L | Monthly
TSS (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | N/A | 24.8 lbs/Day | N/A |  | TSS (Weekly Avg) | 24.8 lbs/Day | Monthly
TSS (Monthly Average) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | N/A | 16.5 lbs/day | N/A |  | TSS (Monthly Average) | 16.5 lbs/day | Monthly
TSS (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 22 | <45 mg/L | Yes |  | TSS (Weekly Avg) | 45 mg/L | Monthly
TSS (Monthly Average) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 22 | <30 mg/L | Yes |  | TSS (Monthly Average) | 30 mg/L | Monthly
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | N/A | 3.30 lbs/Day | N/A |  | Ammonia (May 1 - Oct 31 Weekly Avg) | 3.30 lbs/Day | Monthly
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | N/A | 2.20 lbs/day | N/A |  | Ammonia (May 1 - Oct 31 Monthly Avg) | 2.20 lbs/day | Monthly
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 4.1 | <6 mg/L | Yes |  | Ammonia (May 1 - Oct 31 Weekly Avg) | 6 mg/L | Monthly
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 4.1 | <4 mg/L | No | Under AO, no NOV | Ammonia (May 1 - Oct 31 Monthly Avg) | 4 mg/L | Monthly
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | N/A | 8.26 lbs/Day | N/A |  | Ammonia (Nov 1 - Apr 30 Weekly Avg) | 8.26 lbs/Day | Monthly
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | N/A | 5.5 lbs/day | N/A |  | Ammonia (Nov 1 - Apr 30 Monthly Avg) | 5.5 lbs/day | Monthly
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | N/A | 15 mg/L | N/A |  | Ammonia (Nov 1 - Apr 30 Weekly Avg) | 15 mg/L | Monthly
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | N/A | 10 mg/L | N/A |  | Ammonia (Nov 1 - Apr 30 Monthly Avg) | 10 mg/L | Monthly
E Coli. (colonies/100mL) (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 98 | <240 #/100mL | Yes |  | E Coli. (colonies/100mL) (Weekly Avg) | 240 | Monthly
E Coli. (colonies/100mL) (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 98 | <130 #/100mL | Yes |  | E Coli. (colonies/100mL) (Monthly Avg) | 130 | Monthly
DO (Min) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 8.04 | >7.0 mg/L | Yes |  | DO (Min) | 7.0 mg/L | Monthly
TRC (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | <0.01 | <0.019 mg/L | Yes |  | TRC (Weekly Avg) | 0.019 mg/L | Monthly
TRC (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | <0.01 | <0.011 mg/L | Yes |  | TRC (Monthly Avg) | 0.011 mg/L | Monthly
Total Phosphorus (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 0.96 | 2.0 mb/L |  |  | Total Phosphorus (Weekly Avg) | 2.0 mb/L | Monthly
Total Phosphorus (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 0.96 | 1.0 mg/L |  |  | Total Phosphorus (Monthly Avg) | 1.0 mg/L | Monthly
Total Nitrogen (Weekly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 5.9 | Report |  |  | Total Nitrogen (Weekly Avg) | Report | Monthly
Total Nitrogen (Monthly Avg) | 2020-05-01 | 2020-05-31 | 2020-05-21 | 2020-05-29 | 5.9 | Report |  |  | Total Nitrogen (Monthly Avg) | Report | Monthly
Flow | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 0.059 | Report
pH | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 7.55 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 7 | <45 mg/L | Yes
CBOD5 (Monthly Average) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 7 | <30 mg/L | Yes
TSS (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 17 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 17 | <30 mg/L | Yes
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 7.5 | <6 mg/L | No | Under AO, no NOV
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 7.5 | <4 mg/L | No | Under AO, no NOV
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | N/A | 15 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | N/A | 10 mg/L | N/A
E Coli. (colonies/100mL) (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 12 | <240 #/100mL | Yes
E Coli. (colonies/100mL) (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 12 | <130 #/100mL | Yes
DO (Min) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 7.14 | >7.0 mg/L | Yes
TRC (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | <0.01 | <0.019 mg/L | Yes
TRC (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | <0.01 | <0.011 mg/L | Yes
Total Phosphorus (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 1.69 | 2.0 mb/L
Total Phosphorus (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 1.69 | 1.0 mg/L
Total Nitrogen (Weekly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 8.4 | Report
Total Nitrogen (Monthly Avg) | 2020-06-01 | 2020-06-30 | 2020-06-09 | 2020-06-18 | 8.4 | Report
Flow | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 0.024 | Report
pH | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 7.19 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 10 | <45 mg/L | Yes
CBOD5 (Monthly Average) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 10 | <30 mg/L | Yes
TSS (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 13 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 13 | <30 mg/L | Yes
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 4.9 | <6 mg/L | Yes
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 4.9 | <4 mg/L | No | Due to low DO. Started adding nutrifying bacteria in June and closed off the airlines with the worst leakage and wrapped some of the smaller holes in the pipes. Been checking weekly and results have consistently been below 5 so the lab is going to resample in hopes of getting the monthly average lower.
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-21 | 2020-07-27 | 2.8 | <4 mg/L | Yes | Resample for above
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | N/A | 15 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | N/A | 10 mg/L | N/A
E Coli. (colonies/100mL) (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 57 | <240 #/100mL | Yes
E Coli. (colonies/100mL) (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 57 | <130 #/100mL | Yes
DO (Min) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 7.27 | >7.0 mg/L | Yes
TRC (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | <0.01 | <0.019 mg/L | Yes
TRC (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | <0.01 | <0.011 mg/L | Yes
Total Phosphorus (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 0.7 | 2.0 mb/L |  | **Permit has this as Report Only**-le
Total Phosphorus (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 0.7 | 1.0 mg/L |  | **Permit has this as Report Only**-le
Total Nitrogen (Weekly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 7.9 | Report
Total Nitrogen (Monthly Avg) | 2020-07-01 | 2020-07-31 | 2020-07-07 | 2020-07-16 | 7.9 | Report
Flow | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 0.798 | Report
pH | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 7.72 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 6 | <45 mg/L | Yes
CBOD5 (Monthly Average) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 6 | <30 mg/L | Yes
TSS (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 10 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 10 | <30 mg/L | Yes
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 1.7 | <6 mg/L | Yes
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 1.7 | <4 mg/L | Yes
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | N/A | 15 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | N/A | 10 mg/L | N/A
E Coli. (colonies/100mL) (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 11 | <240 #/100mL | Yes
E Coli. (colonies/100mL) (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 11 | <130 #/100mL | Yes
DO (Min) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 7.85 | >7.0 mg/L | Yes
TRC (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | <0.01 | <0.019 mg/L | Yes
TRC (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | <0.01 | <0.011 mg/L | Yes
Total Phosphorus (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 0.39 | 2.0 mb/L |  | **Permit has this as Report Only**-le
Total Phosphorus (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 0.39 | 1.0 mg/L |  | **Permit has this as Report Only**-le
Total Nitrogen (Weekly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 3.8 | Report
Total Nitrogen (Monthly Avg) | 2020-08-01 | 2020-08-31 | 2020-08-07 | 2020-08-14 | 3.8 | Report
Flow | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | 1.76 | Report
pH | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | 7.36 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | 20 | <45 mg/L | Yes
CBOD5 (Monthly Average) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | 20 | <30 mg/L | Yes
TSS (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | <6 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | <6 | <30 mg/L | Yes
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | 23.6 | <6 mg/L | No | Operator believes these problems are due to hydraulic issues due to inadequate blower performance. Repair and updates to the facility are underway. Operator plans to more closely with more frequent monitoring of the ammonia and add sampling locations, IE: aeration and clarifier as well as the effluent.
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-25 | 2020-10-07 | 21.8 | <6 mg/L | No | Resample for above
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | 23.6 | <4 mg/L | No | Operator believes these problems are due to hydraulic issues due to inadequate blower performance. Repair and updates to the facility are underway. Operator plans to more closely with more frequent monitoring of the ammonia and add sampling locations, IE: aeration and clarifier as well as the effluent.
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-25 | 2020-10-07 | 21.8 | <4 mg/L | No | Resample for above
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | N/A | 15 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | N/A | 10 mg/L | N/A
E Coli. (colonies/100mL) (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | 60000 | <240 #/100mL | No | Operator believes these problems are due to hydraulic issues due to inadequate blower performance. Repair and updates to the facility are underway. Operator plans to more closely with more frequent monitoring of the ammonia and add sampling locations, IE: aeration and clarifier as well as the effluent.
E Coli. (colonies/100mL) (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-24 | 2020-10-07 | 68 | <240 #/100mL | Yes | Resample for above
E Coli. (colonies/100mL) (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-24 | 2020-10-07 | 64 | <240 #/100mL | Yes | Resample for above
E Coli. (colonies/100mL) (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-25 | 2020-10-07 | 32 | <240 #/100mL | Yes | Resample for above
E Coli. (colonies/100mL) (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | 60000 | <130 #/100mL | No | Operator believes these problems are due to hydraulic issues due to inadequate blower performance. Repair and updates to the facility are underway. Operator plans to more closely with more frequent monitoring of the ammonia and add sampling locations, IE: aeration and clarifier as well as the effluent.
E Coli. (colonies/100mL) (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-24 | 2020-10-07 | 64 | <130 #/100mL | Yes | Resample for above
E Coli. (colonies/100mL) (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-24 | 2020-10-07 | 68 | <130 #/100mL | Yes | Resample for above
E Coli. (colonies/100mL) (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-25 | 2020-10-07 | 45 | <240 #/100mL | Yes | Resample for above
DO (Min) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | 7.19 | >7.0 mg/L | Yes
TRC (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | <0.01 | <0.019 mg/L | Yes
TRC (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | <0.01 | <0.011 mg/L | Yes
Total Phosphorus (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | 0.19 | 2.0 mb/L |  | **Permit has this as Report Only**-le
Total Phosphorus (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | 0.19 | 1.0 mg/L |  | **Permit has this as Report Only**-le
Total Nitrogen (Weekly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | 24.5 | Report
Total Nitrogen (Monthly Avg) | 2020-09-01 | 2020-09-30 | 2020-09-18 | 2020-09-25 | 24.5 | Report
Flow | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 0.077 | Report
pH | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 7.5 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 5 | <45 mg/L | Yes
CBOD5 (Monthly Average) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 5 | <30 mg/L | Yes
TSS (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | <6 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | <6 | <30 mg/L | Yes
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 8 | 6 mg/L | No | River Bluffs is undergoing a lot of repairs. The operator has been adding nitrifying bacteria at a low dose to help control the ammonia and improve the effluent quality. Unfortunately, the bacteria that was being used, has a short shelf like and expired. After several attemps to reorder the product with no response from the seller, the operator found another supplier and anticipates having it under control this week. Long term goal is, that after improvments are completed, the nitrification process will improve as well.
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 8 | 4 mg/L | No | River Bluffs is undergoing a lot of repairs. The operator has been adding nitrifying bacteria at a low dose to help control the ammonia and improve the effluent quality. Unfortunately, the bacteria that was being used, has a short shelf like and expired. After several attemps to reorder the product with no response from the seller, the operator found another supplier and anticipates having it under control this week. Long term goal is, that after improvments are completed, the nitrification process will improve as well.
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | N/A | 15 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | N/A | 10 mg/L | N/A
E Coli. (colonies/100mL) (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 11 | <240 #/100mL | Yes
E Coli. (colonies/100mL) (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 11 | <240 #/100mL | Yes
DO (Min) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 7.27 | >7.0 mg/L | Yes
TRC (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 0.01 | <0.019 mg/L | Yes
TRC (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 0.01 | <0.011 mg/L | Yes
Total Phosphorus (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 1.41 | 2.0 mb/L | Yes
Total Phosphorus (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 1.41 | 1.0 mg/L | No | River Bluffs is undergoing a lot of repairs. The operator has been adding nitrifying bacteria at a low dose to help control the ammonia and improve the effluent quality. Unfortunately, the bacteria that was being used, has a short shelf like and expired. After several attemps to reorder the product with no response from the seller, the operator found another supplier and anticipates having it under control this week. Long term goal is, that after improvments are completed, the nitrification process will improve as well.
Total Nitrogen (Weekly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 10.3 | Report
Total Nitrogen (Monthly Avg) | 2020-10-01 | 2020-10-31 | 2020-10-02 | 2020-10-20 | 10.3 | Report
Flow | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 |  | Report
pH | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 7.66 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 6 | <45 mg/L | Yes
CBOD5 (Monthly Average) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 6 | <30 mg/L | Yes
TSS (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | <6 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | <6 | <30 mg/L | Yes
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | N/A | <6 mg/L | N/A
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | N/A | <4 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 1.5 | 15 mg/L | Yes
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 1.5 | 10 mg/L | Yes
E Coli. (colonies/100mL) (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 250 | <240 #/100mL | No | This exceedance was due to renovation work being done at the facility.
E Coli. (colonies/100mL) (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 250 | <130 #/100mL | No | This exceedance was due to renovation work being done at the facility.
E Coli. (colonies/100mL) (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-19 | 1 | <240 #/100mL | Yes | Resample for above
E Coli. (colonies/100mL) (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-19 | 1 | <130 #/100mL | Yes | Resample for above
DO (Min) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 7.4 | >7.0 mg/L | Yes
TRC (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | <0.01 | <0.019 mg/L | Yes
TRC (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | <0.01 | <0.011 mg/L | Yes
Total Phosphorus (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 0.42 | 2.0 mb/L |  | **Permit has this as Report Only**-le
Total Phosphorus (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 0.42 | 1.0 mg/L |  | **Permit has this as Report Only**-le
Total Nitrogen (Weekly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 25.3 | Report
Total Nitrogen (Monthly Avg) | 2020-11-01 | 2020-11-30 | 2020-11-13 | 2020-11-20 | 25.3 | Report
Flow | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 |  | Report
pH | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 7.54 | 6.0-9.0 | Yes
CBOD5 (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 10 | <45 mg/L | Yes
CBOD5 (Monthly Average) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 10 | <30 mg/L | Yes
TSS (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 6 | <45 mg/L | Yes
TSS (Monthly Average) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 6 | <30 mg/L | Yes
Ammonia (May 1 - Oct 31 Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | N/A | <6 mg/L | N/A
Ammonia (May 1 - Oct 31 Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | N/A | <4 mg/L | N/A
Ammonia (Nov 1 - Apr 30 Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 0.8 | 15 mg/L | Yes
Ammonia (Nov 1 - Apr 30 Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 0.8 | 10 mg/L | Yes
E Coli. (colonies/100mL) (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 34 | <240 #/100mL | Yes
E Coli. (colonies/100mL) (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 34 | <130 #/100mL | Yes
DO (Min) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 7.48 | >7.0 mg/L | Yes
TRC (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 0.01 | <0.019 mg/L | Yes
TRC (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 0.01 | <0.011 mg/L | Yes
Total Phosphorus (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 1.5 | 2.0 mb/L |  | **Permit has this as Report Only**-le
Total Phosphorus (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 1.5 | 1.0 mg/L |  | **Permit has this as Report Only**-le
Total Nitrogen (Weekly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 26.2 | Report
Total Nitrogen (Monthly Avg) | 2020-12-01 | 2020-12-31 | 2020-12-11 | 2020-12-18 | 26.2 | Report