## LE 50-50 Summer
LG&E Non-Conincidental Summer Peak Load Forecast - Distribution Substations
Units Projected to be Above 90% of kVA Capacity by 2031
S |  |  | 2019 |  | 2019 |  | 2020 |  | 2021 |  | 2022 |  | 2023 |  | 2024 |  | 2025 |  | 2026 |  | 2027 |  | 2028 |  | 2029 |  | 2030 |  | 2031 |  | 2032 |  | Interconnected NM | NM | NMS
Transformer | Number | kVA Capacity | Act kW | pf | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | (Name Plate KVA) | KW | Customers
CL TR3 | CL3 | 20000 | 17365 | 0.97 | 16761.5087 | 0.864 | 17421.9995 | 0.89804 | 18082.4904 | 0.93209 | 18742.9812 | 0.96613 | 19403.4721 | 1.0002 | 20063.9629 | 1.0342 | 20724.4538 | 1.0683 | 21384.9446 | 1.1023 | 22045.4355 | 1.1364 | 22705.9263 | 1.1704 | 23366.4172 | 1.2045 | 24026.908 | 1.2385 | 24687.3989 | 1.2725 | 25347.8897 | 130.7% | 0 | 0 | 0
FV TR3 | FV3 | 28000 | 23720 | 0.98959 | 23728.1699 | 0.95911 | 23728.1699 | 0.95911 | 23728.1699 | 0.95911 | 23728.1699 | 0.95911 | 23728.1699 | 0.95911 | 23728.1699 | 0.95911 | 23728.1699 | 0.95911 | 23728.1699 | 0.95911 | 23728.1699 | 0.95911 | 23728.1699 | 0.95911 | 23728.1699 | 0.95911 | 23728.1699 | 0.95911 | 23728.1699 | 0.95911 | 23728.1699 | 95.91% | 38.47 | 38.0694 | 6
FH TR2 | FH2 | 44800 | 28280 | 0.97954 | 33006.8003 | 0.75215 | 33606.8003 | 0.76582 | 34206.8003 | 0.77949 | 34806.8003 | 0.79316 | 35406.8003 | 0.80684 | 36006.8003 | 0.82051 | 36606.8003 | 0.83418 | 37206.8003 | 0.84785 | 37806.8003 | 0.86153 | 38406.8003 | 0.8752 | 39006.8003 | 0.88887 | 39606.8003 | 0.90255 | 40206.8003 | 0.91622 | 40806.8003 | 92.99% | 146.385 | 143.3902 | 17
WT TR4 | WT4 | 44800 | 36670 | 0.99537 | 36879.6 | 0.82703 | 37179.6 | 0.83376 | 37479.6 | 0.84049 | 37779.6 | 0.84722 | 38079.6 | 0.85394 | 38379.6 | 0.86067 | 38679.6 | 0.8674 | 38979.6 | 0.87413 | 39279.6 | 0.88085 | 39579.6 | 0.88758 | 39879.6 | 0.89431 | 40179.6 | 0.90104 | 40479.6 | 0.90776 | 40779.6 | 91.45% | 174.32 | 173.5134 | 24
LG&E Non-Conincidental Summer Peak Load Forecast - Distribution Substations (Adjusted to Add Load Masked by Connected Net Metering)
Units Projected to be Above 90% of kVA Capacity by 2031
S |  |  | 2019 |  | 2019 |  | 2020 |  | 2021 |  | 2022 |  | 2023 |  | 2024 |  | 2025 |  | 2026 |  | 2027 |  | 2028 |  | 2029 |  | 2030 |  | 2031 |  | 2032 |  | Interconnected NM | Adjusted | NMS | 23.26%
Transformer | Number | kVA Capacity | Act kW | pf | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | (Name Plate KVA) | KW | Customers
CL TR3 | CL3 | 20000 | 17365 | 0.97 | 16761.5087 | 0.864 | 17421.9995 | 0.89804 | 18082.4904 | 0.93209 | 18742.9812 | 0.96613 | 19403.4721 | 1.0002 | 20063.9629 | 1.0342 | 20724.4538 | 1.0683 | 21384.9446 | 1.1023 | 22045.4355 | 1.1364 | 22705.9263 | 1.1704 | 23366.4172 | 1.2045 | 24026.908 | 1.2385 | 24687.3989 | 1.2725 | 25347.8897 | 130.7% | 0 | 0 | 0
FV TR3 | FV3 | 28000 | 23720 | 0.98959 | 23737.0249 | 0.85667 | 23737.0249 | 0.85667 | 23739.0519 | 0.85674 | 23741.9456 | 0.85685 | 23746.0042 | 0.857 | 23751.5597 | 0.8572 | 23759.0079 | 0.85746 | 23768.8243 | 0.85782 | 23781.562 | 0.85828 | 23797.877 | 0.85887 | 23818.3655 | 0.85961 | 23843.9956 | 0.86053 | 23876.9086 | 0.86172 | 23728.1699 | 95.91% | 38.47 | 8.8549 | 6
FH TR2 | FH2 | 44800 | 28280 | 0.97954 | 33040.1528 | 0.75291 | 33640.1528 | 0.76658 | 34247.7878 | 0.78043 | 34858.6871 | 0.79435 | 35473.9739 | 0.80837 | 36094.8988 | 0.82252 | 36722.9527 | 0.83683 | 37359.9267 | 0.85134 | 38007.904 | 0.86611 | 38669.3549 | 0.88118 | 39346.526 | 0.89661 | 40043.0626 | 0.91249 | 40767.0311 | 0.92898 | 40806.8003 | 92.99% | 146.385 | 33.3526 | 17
WT TR4 | WT4 | 44800 | 36670 | 0.99537 | 36919.9592 | 0.82794 | 37219.9592 | 0.83466 | 37529.1981 | 0.8416 | 37842.3871 | 0.84862 | 38160.8854 | 0.85577 | 38486.2062 | 0.86306 | 38820.1536 | 0.87055 | 39164.895 | 0.87828 | 39522.9513 | 0.88631 | 39897.3117 | 0.89471 | 40290.6948 | 0.90353 | 40707.5117 | 0.91287 | 41157.5233 | 0.92297 | 40779.6 | 91.45% | 174.32 | 40.3592 | 24
Annual DER Growth | [8 empty] | 1.2289 |  | 1.5557 |  | 2.014 |  | 2.6414 |  | 3.4826 |  | 4.5911 |  | 6.0296 |  | 7.8721 |  | 10.1859 |  | 13.0803 |  | 16.7972

## KU 50-50 Summer
KU Non-Conincidental Summer Peak Load Forecast - Distribution Substations
Units Projected to be Above 90% of kVA Capacity by 2031
S |  |  | 2019 |  | 2019 |  | 2020 |  | 2021 |  | 2022 |  | 2023 |  | 2024 |  | 2025 |  | 2026 |  | 2027 |  | 2028 |  | 2029 |  | 2030 |  | 2031 |  | 2032 |  | Interconnected NM | Nameplate | NMS
Transformer | Number | kVA Capacity | Act kW | pf | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | (Name Plate KVA) | KVA | Customers
HORSE CAVE INDUSTRIAL 2 | 7992 | 22400 | 17302 | 0.835 | 18549.5091 | 0.99174 | 19221.4 | 1.0277 | 19893.2909 | 1.0636 | 20565.1818 | 1.0995 | 21237.0727 | 1.1354 | 21908.9636 | 1.1714 | 22580.8545 | 1.2073 | 23252.7455 | 1.2432 | 23924.6364 | 1.2791 | 24596.5273 | 1.315 | 25268.4182 | 1.351 | 25940.3091 | 1.3869 | 26612.2 | 1.4228 | 27284.0909 | 1.4587 | 62.36 | 52.0706 | 3
CORPORATE DRIVE 12 2 | 6632 | 22400 | 14884 | 0.901 | 16790.9091 | 0.83196 | 17580.4 | 0.87108 | 18369.8909 | 0.91019 | 19159.3818 | 0.94931 | 19948.8727 | 0.98843 | 20738.3636 | 1.0275 | 21527.8545 | 1.0667 | 22317.3455 | 1.1058 | 23106.8364 | 1.1449 | 23896.3273 | 1.184 | 24685.8182 | 1.2231 | 25475.3091 | 1.2623 | 26264.8 | 1.3014 | 27054.2909 | 1.3405 | 0 | 0 | 0
LA GRANGE E 12 KV 2 | 8972 | 14000 | 10979 | 0.959 | 11746.0727 | 0.87488 | 12082.4 | 0.89993 | 12418.7273 | 0.92498 | 12755.0545 | 0.95003 | 13091.3818 | 0.97508 | 13427.7091 | 1.0001 | 13764.0364 | 1.0252 | 14100.3636 | 1.0502 | 14436.6909 | 1.0753 | 14773.0182 | 1.1003 | 15109.3455 | 1.1254 | 15445.6727 | 1.1504 | 15782 | 1.1755 | 16118.3273 | 1.2005 | 30.1 | 28.8659 | 3
AISIN 12KV | 4111 | 14000 | 9896 | 0.966 | 10289 | 0.7608 | 10755.2667 | 0.79527 | 11221.5333 | 0.82975 | 11687.8 | 0.86423 | 12154.0667 | 0.8987 | 12620.3333 | 0.93318 | 13086.6 | 0.96766 | 13552.8667 | 1.0021 | 14019.1333 | 1.0366 | 14485.4 | 1.0711 | 14951.6667 | 1.1056 | 15417.9333 | 1.14 | 15884.2 | 1.1745 | 16350.4667 | 1.209 | 7.9 | 7.6314 | 1
GEORGETOWN 12KV | 6692 | 14000 | 13685 | 0.988 | 12893.0909 | 0.93212 | 13039.2667 | 0.94269 | 13185.4424 | 0.95326 | 13331.6182 | 0.96382 | 13477.7939 | 0.97439 | 13623.9697 | 0.98496 | 13770.1455 | 0.99553 | 13916.3212 | 1.0061 | 14062.497 | 1.0167 | 14208.6727 | 1.0272 | 14354.8485 | 1.0378 | 14501.0242 | 1.0484 | 14647.2 | 1.0589 | 14793.3758 | 1.0695 | 70.53 | 69.6836 | 9
FLORIDA TIL 12KV | 4001 | 14000 | 11849 | 0.944 | 11422.2182 | 0.86427 | 11601.2 | 0.87781 | 11780.1818 | 0.89136 | 11959.1636 | 0.9049 | 12138.1455 | 0.91844 | 12317.1273 | 0.93199 | 12496.1091 | 0.94553 | 12675.0909 | 0.95907 | 12854.0727 | 0.97261 | 13033.0545 | 0.98616 | 13212.0364 | 0.9997 | 13391.0182 | 1.0132 | 13570 | 1.0268 | 13748.9818 | 1.0403 | 19.2 | 18.1248 | 1
ETOWN 2 12KV | 7671 | 22400 | 18522 | 0.996 | 18965.7273 | 0.85008 | 19290.8667 | 0.86466 | 19616.0061 | 0.87923 | 19941.1455 | 0.8938 | 20266.2848 | 0.90838 | 20591.4242 | 0.92295 | 20916.5636 | 0.93753 | 21241.703 | 0.9521 | 21566.8424 | 0.96667 | 21891.9818 | 0.98125 | 22217.1212 | 0.99582 | 22542.2606 | 1.0104 | 22867.4 | 1.025 | 23192.5394 | 1.0395 | 82.56 | 82.2298 | 6
LEBANON SOUTH 12 KV | 4091 | 14000 | 11480 | 0.983 | 11919.1636 | 0.86609 | 12098.8 | 0.87915 | 12278.4364 | 0.8922 | 12458.0727 | 0.90525 | 12637.7091 | 0.9183 | 12817.3455 | 0.93136 | 12996.9818 | 0.94441 | 13176.6182 | 0.95746 | 13356.2545 | 0.97052 | 13535.8909 | 0.98357 | 13715.5273 | 0.99662 | 13895.1636 | 1.0097 | 14074.8 | 1.0227 | 14254.4364 | 1.0358 | 19.2 | 18.8736 | 1
CORBIN USS 12KV 1 | 7951 | 10500 | 7713 | 0.884 | 7907.8 | 0.85195 | 8032.8 | 0.86542 | 8157.8 | 0.87888 | 8282.8 | 0.89235 | 8407.8 | 0.90582 | 8532.8 | 0.91928 | 8657.8 | 0.93275 | 8782.8 | 0.94622 | 8907.8 | 0.95969 | 9032.8 | 0.97315 | 9157.8 | 0.98662 | 9282.8 | 1.0001 | 9407.8 | 1.0136 | 9532.8 | 1.027 | 0 | 0 | 0
DELAPLAIN 12KV | 6091 | 14000 | 10644 | 0.928 | 10493.5455 | 0.80769 | 10699.8667 | 0.82357 | 10906.1879 | 0.83945 | 11112.5091 | 0.85533 | 11318.8303 | 0.87122 | 11525.1515 | 0.8871 | 11731.4727 | 0.90298 | 11937.7939 | 0.91886 | 12144.1152 | 0.93474 | 12350.4364 | 0.95062 | 12556.7576 | 0.9665 | 12763.0788 | 0.98238 | 12969.4 | 0.99826 | 13175.7212 | 1.0141 | 72.54 | 67.3171 | 3
VINE ST 12KV 2 | 7392 | 14000 | 9216 | 0.9846 | 9536.6909 | 0.69185 | 9864.2667 | 0.71561 | 10191.8424 | 0.73937 | 10519.4182 | 0.76314 | 10846.9939 | 0.7869 | 11174.5697 | 0.81067 | 11502.1455 | 0.83443 | 11829.7212 | 0.8582 | 12157.297 | 0.88196 | 12484.8727 | 0.90572 | 12812.4485 | 0.92949 | 13140.0242 | 0.95325 | 13467.6 | 0.97702 | 13795.1758 | 1.0008 | 0 | 0 | 0
OXFORD 12KV | 6661 | 14000 | 8108 | 0.9958 | 7484 | 0.53683 | 7984 | 0.57269 | 8484 | 0.60856 | 8984 | 0.64442 | 9484 | 0.68029 | 9984 | 0.71615 | 10484 | 0.75202 | 10984 | 0.78788 | 11484 | 0.82375 | 11984 | 0.85961 | 12484 | 0.89548 | 12984 | 0.93134 | 13484 | 0.96721 | 13984 | 1.0031 | 121.495 | 120.9847 | 7
WEST HIGH 12KV | 5161 | 14000 | 5366 | 1 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 0 | 0 | 0
LEMONS MILL 12KV 2 | 7232 | 22400 | 19037 | 0.97245 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 0 | 0 | 0
CAMARGO 12KV | 8051 | 14000 | 11952 | 1 | 11394.1818 | 0.81387 | 11524.4667 | 0.82318 | 11654.7515 | 0.83248 | 11785.0364 | 0.84179 | 11915.3212 | 0.85109 | 12045.6061 | 0.8604 | 12175.8909 | 0.86971 | 12306.1758 | 0.87901 | 12436.4606 | 0.88832 | 12566.7455 | 0.89762 | 12697.0303 | 0.90693 | 12827.3152 | 0.91624 | 12957.6 | 0.92554 | 13087.8848 | 0.93485 | 50.95 | 50.95 | 6
LEMONS MILL 12KV | 7231 | 22400 | 16056 | 0.9548 | 15475.9 | 0.7236 | 15825.9 | 0.73996 | 16175.9 | 0.75633 | 16525.9 | 0.77269 | 16875.9 | 0.78906 | 17225.9 | 0.80542 | 17575.9 | 0.82179 | 17925.9 | 0.83815 | 18275.9 | 0.85452 | 18625.9 | 0.87088 | 18975.9 | 0.88725 | 19325.9 | 0.90361 | 19675.9 | 0.91998 | 20025.9 | 0.93634 | 58.065 | 55.4402 | 4
CORNING GLASS 4 KV #7463 | 7463 | 1610 | 608 | 0.7685 | 738.9455 | 0.59723 | 771.9333 | 0.62389 | 804.9212 | 0.65055 | 837.9091 | 0.67722 | 870.897 | 0.70388 | 903.8848 | 0.73054 | 936.8727 | 0.7572 | 969.8606 | 0.78386 | 1002.8485 | 0.81052 | 1035.8364 | 0.83718 | 1068.8242 | 0.86385 | 1101.8121 | 0.89051 | 1134.8 | 0.91717 | 1167.7879 | 0.94383 | 0 | 0 | 0
MT STERLING 12KV | 7371 | 14000 | 12483 | 0.991 | 12602.8 | 0.90838 | 12602.8 | 0.90838 | 12602.8 | 0.90838 | 12602.8 | 0.90838 | 12602.8 | 0.90838 | 12602.8 | 0.90838 | 12602.8 | 0.90838 | 12602.8 | 0.90838 | 12602.8 | 0.90838 | 12602.8 | 0.90838 | 12602.8 | 0.90838 | 12602.8 | 0.90838 | 12602.8 | 0.90838 | 12602.8 | 0.90838 | 8.96 | 8.8794 | 2
VERSAILLES B 2 12 | 8382 | 22400 | 18262 | 0.998 | 18076.2182 | 0.80859 | 18251.8667 | 0.81645 | 18427.5152 | 0.82431 | 18603.1636 | 0.83216 | 18778.8121 | 0.84002 | 18954.4606 | 0.84788 | 19130.1091 | 0.85573 | 19305.7576 | 0.86359 | 19481.4061 | 0.87145 | 19657.0545 | 0.87931 | 19832.703 | 0.88716 | 20008.3515 | 0.89502 | 20184 | 0.90288 | 20359.6485 | 0.91073 | 112.85 | 112.6243 | 7
KU Non-Conincidental Summer Peak Load Forecast - Distribution Substations (Adjusted to Add Load Masked by Connected Net Metering)
Units Projected to be Above 90% of kVA Capacity by 2031
|  |  | 2019 |  | 2019 |  | 2020 |  | 2021 |  | 2022 |  | 2023 |  | 2024 |  | 2025 |  | 2026 |  | 2027 |  | 2028 |  | 2029 |  | 2030 |  | 2031 |  |  |  | Interconnected NM | Adjusted | NMS | 23.26%
Transformer | Number | kVA Capacity | Act kW | pf | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | (Name Plate KVA) | KW | Customers
HORSE CAVE INDUSTRIAL 2 | 7992 | 22400 | 17314.1116 | 0.835 | 18561.6207 | 0.99239 | 19233.5116 | 1.0283 | 19908.1751 | 1.0644 | 20584.024 | 1.1005 | 21261.4661 | 1.1367 | 21940.9557 | 1.1731 | 22623.0341 | 1.2095 | 23308.3517 | 1.2462 | 23997.665 | 1.283 | 24691.8712 | 1.3201 | 25391.7859 | 1.3576 | 26098.7331 | 1.3954 | 26815.6418 | 1.4337 | 27296.2025 | 1.4587 | 62.36 | 12.1116 | 3
CORPORATE DRIVE 12 2 | 6632 | 22400 | 14884 | 0.901 | 16790.9091 | 0.83196 | 17580.4 | 0.87108 | 18369.8909 | 0.91019 | 19159.3818 | 0.94931 | 19948.8727 | 0.98843 | 20738.3636 | 1.0275 | 21527.8545 | 1.0667 | 22317.3455 | 1.1058 | 23106.8364 | 1.1449 | 23896.3273 | 1.184 | 24685.8182 | 1.2231 | 25475.3091 | 1.2623 | 26264.8 | 1.3014 | 27054.2909 | 1.3405 | 0 | 0 | 0
LA GRANGE E 12 KV 2 | 8972 | 14000 | 10985.7142 | 0.959 | 11752.7869 | 0.87538 | 12089.1142 | 0.90043 | 12426.9785 | 0.92559 | 12765.4999 | 0.9508 | 13104.9046 | 0.97608 | 13445.4442 | 1.0014 | 13787.419 | 1.0269 | 14131.1895 | 1.0525 | 14477.1751 | 1.0783 | 14825.8731 | 1.1043 | 15177.7357 | 1.1305 | 15533.4968 | 1.157 | 15894.7802 | 1.1839 | 16125.0415 | 1.2005 | 30.1 | 6.7142 | 3
AISIN 12KV | 4111 | 14000 | 9897.7751 | 0.966 | 10290.7751 | 0.76093 | 10757.0417 | 0.7954 | 11223.7147 | 0.82991 | 11690.5615 | 0.86443 | 12157.6417 | 0.89897 | 12625.022 | 0.93353 | 13092.7818 | 0.96811 | 13561.0162 | 1.0027 | 14029.8363 | 1.0374 | 14499.3735 | 1.0721 | 14969.7473 | 1.1069 | 15441.1517 | 1.1418 | 15914.0162 | 1.1767 | 16352.2417 | 1.209 | 7.9 | 1.7751 | 1
GEORGETOWN 12KV | 6692 | 14000 | 13701.2084 | 0.988 | 12909.2993 | 0.93329 | 13055.4751 | 0.94386 | 13205.3612 | 0.9547 | 13356.8337 | 0.96565 | 13510.4385 | 0.97675 | 13666.7831 | 0.98806 | 13826.5923 | 0.99961 | 13990.7364 | 1.0115 | 14160.2278 | 1.0237 | 14336.267 | 1.0365 | 14519.9458 | 1.0497 | 14713.0356 | 1.0637 | 14919.4566 | 1.0786 | 14809.5842 | 1.0695 | 70.53 | 16.2084 | 9
FLORIDA TIL 12KV | 4001 | 14000 | 11853.2158 | 0.944 | 11426.434 | 0.86459 | 11605.4158 | 0.87813 | 11785.3627 | 0.89175 | 11965.7222 | 0.9054 | 12146.6363 | 0.91909 | 12328.2631 | 0.93283 | 12510.791 | 0.94664 | 12694.4464 | 0.96054 | 12879.4926 | 0.97454 | 13066.242 | 0.98867 | 13254.9784 | 1.0029 | 13446.1626 | 1.0174 | 13640.8143 | 1.0321 | 13753.1976 | 1.0403 | 19.2 | 4.2158 | 1
ETOWN 2 12KV | 7671 | 22400 | 18541.1266 | 0.996 | 18984.8539 | 0.85094 | 19309.9933 | 0.86552 | 19639.5111 | 0.88029 | 19970.9009 | 0.89514 | 20304.8068 | 0.91011 | 20641.946 | 0.92522 | 20983.1734 | 0.94051 | 21329.5162 | 0.95603 | 21682.1691 | 0.97184 | 22042.5487 | 0.98799 | 22411.9433 | 1.0046 | 22792.4434 | 1.0216 | 23188.6748 | 1.0394 | 23211.666 | 1.0395 | 82.56 | 19.1266 | 6
LEBANON SOUTH 12 KV | 4091 | 14000 | 11484.39 | 0.983 | 11923.5536 | 0.86641 | 12103.19 | 0.87946 | 12283.8313 | 0.89259 | 12464.9023 | 0.90575 | 12646.5508 | 0.91895 | 12828.9413 | 0.9322 | 13012.2703 | 0.94552 | 13196.7733 | 0.95893 | 13382.7246 | 0.97244 | 13570.4494 | 0.98608 | 13760.2434 | 0.99987 | 13952.5863 | 1.0138 | 14148.5399 | 1.0281 | 14258.8264 | 1.0358 | 19.2 | 4.39 | 1
CORBIN USS 12KV 1 | 7951 | 10500 | 7713 | 0.884 | 7907.8 | 0.85195 | 8032.8 | 0.86542 | 8157.8 | 0.87888 | 8282.8 | 0.89235 | 8407.8 | 0.90582 | 8532.8 | 0.91928 | 8657.8 | 0.93275 | 8782.8 | 0.94622 | 8907.8 | 0.95969 | 9032.8 | 0.97315 | 9157.8 | 0.98662 | 9282.8 | 1.0001 | 9407.8 | 1.0136 | 9532.8 | 1.027 | 0 | 0 | 0
DELAPLAIN 12KV | 6091 | 14000 | 10659.658 | 0.928 | 10509.2034 | 0.8089 | 10715.5246 | 0.82478 | 10925.4302 | 0.84094 | 11136.8683 | 0.85721 | 11350.3662 | 0.87364 | 11566.511 | 0.89028 | 11786.0026 | 0.90717 | 12009.6819 | 0.92439 | 12238.5269 | 0.942 | 12473.6974 | 0.96011 | 12716.248 | 0.97878 | 12967.8901 | 0.99814 | 13232.4105 | 1.0185 | 13191.3792 | 1.0141 | 72.54 | 15.658 | 3
VINE ST 12KV 2 | 7392 | 14000 | 9216 | 0.9846 | 9536.6909 | 0.69185 | 9864.2667 | 0.71561 | 10191.8424 | 0.73937 | 10519.4182 | 0.76314 | 10846.9939 | 0.7869 | 11174.5697 | 0.81067 | 11502.1455 | 0.83443 | 11829.7212 | 0.8582 | 12157.297 | 0.88196 | 12484.8727 | 0.90572 | 12812.4485 | 0.92949 | 13140.0242 | 0.95325 | 13467.6 | 0.97702 | 13795.1758 | 1.0008 | 0 | 0 | 0
OXFORD 12KV | 6661 | 14000 | 8136.141 | 0.9958 | 7512.141 | 0.53884 | 8012.141 | 0.57471 | 8518.583 | 0.61104 | 9027.7793 | 0.64756 | 9540.6774 | 0.68435 | 10058.3327 | 0.72148 | 10582.003 | 0.75905 | 11113.1996 | 0.79715 | 11653.6802 | 0.83592 | 12205.5291 | 0.8755 | 12770.6419 | 0.91604 | 13352.0941 | 0.95774 | 13956.6919 | 1.0011 | 14012.141 | 1.0031 | 121.495 | 28.141 | 7
WEST HIGH 12KV | 5161 | 14000 | 5366 | 1 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 13254.5 | 0.94675 | 0 | 0 | 0
LEMONS MILL 12KV 2 | 7232 | 22400 | 19037 | 0.97245 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 20234.7 | 0.92892 | 0 | 0 | 0
CAMARGO 12KV | 8051 | 14000 | 11963.851 | 1 | 11406.0328 | 0.81472 | 11536.3176 | 0.82402 | 11669.3154 | 0.83352 | 11803.473 | 0.84311 | 11939.1896 | 0.8528 | 12076.9096 | 0.86264 | 12217.1627 | 0.87265 | 12360.5853 | 0.8829 | 12507.9176 | 0.89342 | 12660.0375 | 0.90429 | 12817.7431 | 0.91555 | 12982.3297 | 0.92731 | 13156.6636 | 0.93976 | 13099.7358 | 0.93485 | 50.95 | 11.851 | 6
LEMONS MILL 12KV | 7231 | 22400 | 16068.8954 | 0.9548 | 15488.7954 | 0.7242 | 15838.7954 | 0.74057 | 16191.7474 | 0.75707 | 16545.9615 | 0.77363 | 16901.8719 | 0.79027 | 17259.9623 | 0.80702 | 17620.809 | 0.82389 | 17985.1046 | 0.84092 | 18353.6545 | 0.85815 | 18727.4138 | 0.87563 | 19107.2511 | 0.89339 | 19494.5759 | 0.9115 | 19892.5069 | 0.9301 | 20038.7954 | 0.93634 | 58.065 | 12.8954 | 4
CORNING GLASS 4 KV #7463 | 7463 | 1610 | 608 | 0.7685 | 738.9455 | 0.59723 | 771.9333 | 0.62389 | 804.9212 | 0.65055 | 837.9091 | 0.67722 | 870.897 | 0.70388 | 903.8848 | 0.73054 | 936.8727 | 0.7572 | 969.8606 | 0.78386 | 1002.8485 | 0.81052 | 1035.8364 | 0.83718 | 1068.8242 | 0.86385 | 1101.8121 | 0.89051 | 1134.8 | 0.91717 | 1167.7879 | 0.94383 | 0 | 0 | 0
MT STERLING 12KV | 7371 | 14000 | 12485.0653 | 0.991 | 12604.8653 | 0.90852 | 12604.8653 | 0.90852 | 12605.3381 | 0.90856 | 12606.0131 | 0.90861 | 12606.9597 | 0.90868 | 12608.2555 | 0.90877 | 12609.9927 | 0.90889 | 12612.2823 | 0.90906 | 12615.2532 | 0.90927 | 12619.0586 | 0.90955 | 12623.8373 | 0.90989 | 12629.8153 | 0.91032 | 12637.492 | 0.91088 | 12604.8653 | 0.90838 | 8.96 | 2.0653 | 2
VERSAILLES B 2 12 | 8382 | 22400 | 18288.1964 | 0.998 | 18102.4146 | 0.80976 | 18278.0631 | 0.81762 | 18459.7084 | 0.82575 | 18643.9176 | 0.83399 | 18831.573 | 0.84238 | 19023.6567 | 0.85097 | 19221.3398 | 0.85982 | 19426.0291 | 0.86897 | 19639.3608 | 0.87851 | 19863.2753 | 0.88853 | 20099.537 | 0.8991 | 20351.0092 | 0.91035 | 20624.0274 | 0.92256 | 20385.8449 | 0.91073 | 112.85 | 26.1964 | 7
Annual DER Growth | [8 empty] | 1.2289 |  | 1.5557 |  | 2.014 |  | 2.6414 |  | 3.4826 |  | 4.5911 |  | 6.0296 |  | 7.8721 |  | 10.1859 |  | 13.0803 |  | 16.7972
[31 empty] | #N/A | #N/A

## KU 50-50 Winter
KU Non-Conincidental Winter Peak Load Forecast - Distribution Substations
Units Projected to be Above 90% of kVA Capacity by 2031
W |  |  | 2020 |  | 2020 |  | 2021 |  | 2022 |  | 2023 |  | 2024 |  | 2025 |  | 2026 |  | 2027 |  | 2028 |  | 2029 |  | 2030 |  | 2031 |  | 2032 |  | Interconnected NM |  | NMS
Transformer | Number | kVA Capacity | Act kW | pf | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | (Name Plate KVA) | KW | Customers
SALT LICK 12KV | 7271 | 1440 | 3452 | 0.999 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 0 | 0 | 0
LEMONS MILL 12KV | 7231 | 22400 | 18835 | 0.98511 | 23248.3 | 1.0536 | 23998.3 | 1.0536 | 24748.3 | 1.1215 | 25498.3 | 1.1555 | 26248.3 | 1.1895 | 26998.3 | 1.2235 | 27748.3 | 1.2575 | 28498.3 | 1.2915 | 29248.3 | 1.3255 | 29998.3 | 1.3595 | 30748.3 | 1.3934 | 31498.3 | 1.4274 | 32248.3 | 1.4614 | 33.53 | 33.0308 | 6
OXFORD 12KV | 6661 | 14000 | 11539 | 1 | 13050.3 | 0.93216 | 13651.3 | 0.93216 | 14252.3 | 1.018 | 14853.3 | 1.061 | 15454.3 | 1.1039 | 16055.3 | 1.1468 | 16656.3 | 1.1897 | 17257.3 | 1.2327 | 17858.3 | 1.2756 | 18459.3 | 1.3185 | 19060.3 | 1.3615 | 19661.3 | 1.4044 | 20262.3 | 1.4473 | 121.495 | 121.495 | 7 | 0.0086782
CAMARGO 12KV | 8051 | 14000 | 12977 | 0.985 | 14921.9455 | 1.0821 | 15218.8 | 1.0821 | 15515.6545 | 1.1251 | 15812.5091 | 1.1467 | 16109.3636 | 1.1682 | 16406.2182 | 1.1897 | 16703.0727 | 1.2112 | 16999.9273 | 1.2328 | 17296.7818 | 1.2543 | 17593.6364 | 1.2758 | 17890.4909 | 1.2974 | 18187.3455 | 1.3189 | 18484.2 | 1.3404 | 50.95 | 50.1857 | 6
FARISTON 12KV | 8431 | 7000 | 6192 | 1 | 7023.1273 | 1.0033 | 7191.6 | 1.0033 | 7360.0727 | 1.0514 | 7528.5455 | 1.0755 | 7697.0182 | 1.0996 | 7865.4909 | 1.1236 | 8033.9636 | 1.1477 | 8202.4364 | 1.1718 | 8370.9091 | 1.1958 | 8539.3818 | 1.2199 | 8707.8545 | 1.244 | 8876.3273 | 1.268 | 9044.8 | 1.2921 | 0 | 0 | 0
SHUN PIKE 12KV | 4491 | 14000 | 10668 | 0.9961 | 11603.0182 | 0.83203 | 12153.0667 | 0.83203 | 12703.1152 | 0.91092 | 13253.1636 | 0.95036 | 13803.2121 | 0.9898 | 14353.2606 | 1.0292 | 14903.3091 | 1.0687 | 15453.3576 | 1.1081 | 16003.4061 | 1.1476 | 16553.4545 | 1.187 | 17103.503 | 1.2265 | 17653.5515 | 1.2659 | 18203.6 | 1.3053 | 10.14 | 10.1005 | 3
HORSE CAVE INDUSTRIAL 2 | 7992 | 22400 | 17345 | 0.847 | 18291.6182 | 0.9641 | 18793.6 | 0.9641 | 19295.5818 | 1.017 | 19797.5636 | 1.0435 | 20299.5455 | 1.0699 | 20801.5273 | 1.0964 | 21303.5091 | 1.1228 | 21805.4909 | 1.1493 | 22307.4727 | 1.1758 | 22809.4545 | 1.2022 | 23311.4364 | 1.2287 | 23813.4182 | 1.2551 | 24315.4 | 1.2816 | 62.36 | 52.8189 | 3
GEORGETOWN 12KV | 6692 | 14000 | 11136 | 0.998 | 13205.4 | 0.94513 | 13502.3333 | 0.94513 | 13799.2667 | 0.98764 | 14096.2 | 1.0089 | 14393.1333 | 1.0301 | 14690.0667 | 1.0514 | 14987 | 1.0726 | 15283.9333 | 1.0939 | 15580.8667 | 1.1151 | 15877.8 | 1.1364 | 16174.7333 | 1.1577 | 16471.6667 | 1.1789 | 16768.6 | 1.2002 | 70.53 | 70.3889 | 9
ADAMS 12KV | 1085 | 22400 | 16506 | 0.99998 | 21495.9 | 0.95966 | 21928.9 | 0.95966 | 22361.9 | 0.99832 | 22794.9 | 1.0176 | 23227.9 | 1.037 | 23660.9 | 1.0563 | 24093.9 | 1.0756 | 24526.9 | 1.095 | 24959.9 | 1.1143 | 25392.9 | 1.1336 | 25825.9 | 1.153 | 26258.9 | 1.1723 | 26691.9 | 1.1916 | 62.16 | 62.1589 | 5
BRODHEAD 12KV | 8491 | 5250 | 5380 | 0.999 | 5182.2545 | 0.98808 | 5268.5333 | 0.98808 | 5354.8121 | 1.021 | 5441.0909 | 1.0374 | 5527.3697 | 1.0539 | 5613.6485 | 1.0703 | 5699.9273 | 1.0868 | 5786.2061 | 1.1032 | 5872.4848 | 1.1197 | 5958.7636 | 1.1361 | 6045.0424 | 1.1526 | 6131.3212 | 1.169 | 6217.6 | 1.1855 | 16.7 | 16.6833 | 1
LEMONS MILL 12KV 2 | 7232 | 22400 | 17094 | 0.97907 | 19894.4 | 0.90713 | 20394.4 | 0.90713 | 20894.4 | 0.95272 | 21394.4 | 0.97552 | 21894.4 | 0.99832 | 22394.4 | 1.0211 | 22894.4 | 1.0439 | 23394.4 | 1.0667 | 23894.4 | 1.0895 | 24394.4 | 1.1123 | 24894.4 | 1.1351 | 25394.4 | 1.1579 | 25894.4 | 1.1807 | 0 | 0 | 0
KU Non-Conincidental Winter Peak Load Forecast - Distribution Substations (Adjusted to Add Load Masked by Connected Net Metering)
Units Projected to be Above 90% of kVA Capacity by 2031
W |  |  | 2020 |  | 2020 |  | 2021 |  | 2022 |  | 2023 |  | 2024 |  | 2025 |  | 2026 |  | 2027 |  | 2028 |  | 2029 |  | 2030 |  | 2031 |  | 2032 |  | Interconnected NM | Adjusted | NMS | 23.26%
Transformer | Number | kVA Capacity | Act kW | pf | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | kW | Pct | (Name Plate KVA) | KW | Customers
SALT LICK 12KV | 7271 | 1440 | 3452 | 0.999 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 4292.5 | 2.9839 | 0 | 0 | 0
LEMONS MILL 12KV | 7231 | 22400 | 18835 | 0.98511 | 23255.983 | 1.0539 | 24007.7417 | 1.088 | 24760.2524 | 1.1221 | 25513.7738 | 1.1562 | 26268.594 | 1.1904 | 27025.0564 | 1.2247 | 27783.5736 | 1.2591 | 28544.6254 | 1.2936 | 29308.781 | 1.3282 | 30076.5578 | 1.363 | 30848.7956 | 1.398 | 31627.3524 | 1.4333 | 32255.983 | 1.4618 | 33.53 | 7.683 | 6
OXFORD 12KV | 6661 | 14000 | 11539 | 1 | 13078.5597 | 0.93418 | 13686.0289 | 0.97757 | 14296.2639 | 1.0212 | 14910.2165 | 1.065 | 15528.9462 | 1.1092 | 16153.7164 | 1.1538 | 16786.0445 | 1.199 | 17427.6959 | 1.2448 | 18080.7635 | 1.2915 | 18747.1508 | 1.3391 | 19429.9466 | 1.3879 | 20135.9856 | 1.4383 | 20290.5597 | 1.4493 | 121.495 | 28.2597 | 7
CAMARGO 12KV | 8051 | 14000 | 12977 | 0.985 | 14933.6187 | 1.0829 | 15233.1454 | 1.1047 | 15533.8146 | 1.1265 | 15836.0195 | 1.1484 | 16140.1976 | 1.1704 | 16446.8709 | 1.1927 | 16756.6661 | 1.2151 | 17070.3124 | 1.2379 | 17388.6745 | 1.261 | 17712.5385 | 1.2844 | 18043.1803 | 1.3084 | 18383.4231 | 1.3331 | 18495.8732 | 1.3413 | 50.95 | 11.6732 | 6
FARISTON 12KV | 8431 | 7000 | 6192 | 1 | 7023.1273 | 1.0033 | 7191.6 | 1.0274 | 7360.0727 | 1.0514 | 7528.5455 | 1.0755 | 7697.0182 | 1.0996 | 7865.4909 | 1.1236 | 8033.9636 | 1.1477 | 8202.4364 | 1.1718 | 8370.9091 | 1.1958 | 8539.3818 | 1.2199 | 8707.8545 | 1.244 | 8876.3273 | 1.268 | 9044.8 | 1.2921 | 0 | 0 | 0
SHUN PIKE 12KV | 4491 | 14000 | 10668 | 0.9961 | 11605.3675 | 0.8322 | 12155.9538 | 0.87168 | 12706.7701 | 0.91118 | 13257.8954 | 0.9507 | 13809.4178 | 0.99025 | 14361.4424 | 1.0298 | 14914.0954 | 1.0695 | 15467.5234 | 1.1091 | 16021.9005 | 1.1489 | 16577.3849 | 1.1887 | 17134.2335 | 1.2287 | 17693.0144 | 1.2687 | 18205.9494 | 1.3055 | 10.14 | 2.3494 | 3
HORSE CAVE INDUSTRIAL 2 | 7992 | 22400 | 17345 | 0.847 | 18303.9039 | 0.96474 | 18808.6981 | 0.99135 | 19314.6948 | 1.018 | 19822.3076 | 1.0448 | 20331.9973 | 1.0716 | 20844.313 | 1.0986 | 21359.9144 | 1.1258 | 21879.5691 | 1.1532 | 22404.1868 | 1.1809 | 22934.5952 | 1.2088 | 23472.1371 | 1.2371 | 24019.7837 | 1.266 | 24327.6857 | 1.2822 | 62.36 | 12.2857 | 3
GEORGETOWN 12KV | 6692 | 14000 | 11136 | 0.998 | 13221.7725 | 0.9463 | 13522.4537 | 0.96783 | 13824.7374 | 0.98946 | 14129.1749 | 1.0112 | 14436.3801 | 1.0332 | 14747.0849 | 1.0555 | 15062.1684 | 1.078 | 15382.6533 | 1.101 | 15709.7524 | 1.1244 | 16044.5683 | 1.1483 | 16388.8906 | 1.173 | 16746.6789 | 1.1986 | 16784.9725 | 1.2013 | 70.53 | 16.3725 | 9
ADAMS 12KV | 1085 | 22400 | 16506 | 0.99998 | 21510.3582 | 0.9603 | 21946.6679 | 0.97978 | 22384.3927 | 0.99932 | 22824.0194 | 1.0189 | 23266.0903 | 1.0387 | 23711.2515 | 1.0586 | 24160.2795 | 1.0786 | 24614.0774 | 1.0989 | 25073.7161 | 1.1194 | 25540.1694 | 1.1402 | 26015.0175 | 1.1614 | 26501.7572 | 1.1831 | 26706.3582 | 1.1923 | 62.16 | 14.4582 | 5
BRODHEAD 12KV | 8491 | 5250 | 5380 | 0.999 | 5186.1351 | 0.98882 | 5273.3022 | 1.0054 | 5360.8491 | 1.0221 | 5448.9065 | 1.0389 | 5537.6199 | 1.0558 | 5627.1627 | 1.0729 | 5717.7434 | 1.0902 | 5809.6043 | 1.1077 | 5903.0328 | 1.1255 | 5998.2904 | 1.1437 | 6095.8011 | 1.1623 | 6196.5035 | 1.1815 | 6221.4805 | 1.1862 | 16.7 | 3.8805 | 1
LEMONS MILL 12KV 2 | 7232 | 22400 | 17094 | 0.97907 | 19894.4 | 0.90713 | 20394.4 | 0.92993 | 20894.4 | 0.95272 | 21394.4 | 0.97552 | 21894.4 | 0.99832 | 22394.4 | 1.0211 | 22894.4 | 1.0439 | 23394.4 | 1.0667 | 23894.4 | 1.0895 | 24394.4 | 1.1123 | 24894.4 | 1.1351 | 25394.4 | 1.1579 | 25894.4 | 1.1807 | 0 | 0 | 0
Annual DER Growth | [6 empty] | 1.2289 |  | 1.5557 |  | 2.014 |  | 2.6414 |  | 3.4826 |  | 4.5911 |  | 6.0296 |  | 7.8721 |  | 10.1859 |  | 13.0803 |  | 16.7972