## Sheet1
Starting assumptions | [8 empty] | Project Scope and costing assumptions
| Curent # burners | Current MCR, MW | Possible Conversion Derate, MW (see note 1&3) | Current Heat Rate BTU/kWhr | Post Conversion Heat Rate, BTU/kWhr (see note 2&3) | Post Full Load Fuel Consumption, MSCF/hr | Post Full Load Fuel Consumption, mmBTU/hr | Commisioning Start Up Fuel, MSCF | Gas Conditioning System | Plant Heating and Vent. System Upgrade | Electrical | Controls Changes | Burners | aux boiler | New Gas Line Distance to Plant, Miles | Gas Line Costs | Total - 2016 Dollars | Today's Dollars | $/kW | Start Up Times
Mitchell 1 | 36 | 800 | 320 | 9785 | 10355.4655 | 8.2844 | 7828 | 1184 | 2964540.3028 | 1545436 | 410900 | 1365427 | 20021588 | 13000000 | 1 | 4500000 | 43807891.3028 | 47640410.7049 | 59.5505 | 30
Notes:
| 1. | Derate shown is a potentenial, not used in this estimate
| 2. | Worse case heat rate multiplier (1.058) is an estimate. Potentially no change in heat rate
| 3. | Better defination to changes in load, heat rate and costs require an additional study, approx $200,000 per plant
| 4. | Costs are from Big Sandy and Clinch River conversion projects
| 5. | Cumulative inflation rate from 2016 to 2020…9.75%, Gas Line Costs is a rule of thumb and not escalated
| 6. | Start up time estimate from ComOps.
| 7. | Class V (+100 / -50%) estimate.