## EIA EastBitCoal_EAST
ULTRA-SUPERCRITICAL COAL WITH 90% CO2 CAPTURE, 650 MW | [19 empty] | CALCULATION OF CONSTRUCTION EXPENDITURES
Input Parameters | [19 empty] | Summer Capacity: | 630.5 | MW
(A) | Year of Cost Estimates |  |  | 2021 |  | (E) | New Capacity Cost ($/kW) |  |  |  | 6707.9246 |  | (I) | Heat Rate (MBtu/MWh) |  |  |  | 12.507 |  | Overnight Cost: | 3959.3098 | $M
(B) | First Year of Analysis |  |  | 2021 |  | (F) | Fixed O&M ($/kW-Yr) |  |  |  | 60.6984 |  | (J) | SO2 Emission Rate (lb./MBtu) |  |  |  | 0.09 |  | Overnight Cost: | 6279.6349 | $/kW (Summer, Excludes AFDC)
(C) | Discount Rate (%) |  |  | 7.52 |  | (G) | Variable O&M ($/MWh) |  |  |  | 11.1936 |  | (K) | NOx Emission Rate (lb./MBtu) |  |  |  | 0.06 |  | Base Year | 2021
(D) | Carrying Charge Rate (%) |  |  | 11.1764 |  | (H) | Capacity Factor (%) |  |  |  | 80 |  | (L) | CO2 Emission Rate (lb./MBtu) |  |  |  | 20.6 |  | AFDC Rate: | 6.3653 | %
[20 empty] | In-service Date: | 2021
[20 empty] | Average Infl Rate: | 1.8582
[22 empty] | Percent | Direct | Direct
|  |  |  | Fixed Costs |  |  |  | Variable Costs | [7 empty] | Total | [5 empty] | of Total | Expen. | Expen.
|  | O&M | Present |  | Fixed |  |  | Fuel | SO2 | NOx | CO2 | Variable |  |  |  | Annual |  |  |  | Year | Deflator | Expen. | 2,021$ | As Spent | AFDC | Total Expen.
| Fuel Cost | Escalation | Value | Generation | O&M | Total |  | Cost | Cost | Cost | Cost | O&M | Total | Total |  | Costs | Allowance Costs - $/Ton | [5 empty] | ($M) | ($M) | ($M) | ($M)
Year | ($/MBtu) | Factor | Factor | ($/kW) | ($/kW) | ($/kW) |  | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW) |  | ($/kW) | SO2 | NOx | CO2 | 2015 | 0.89541 | 0% | 0 | 0 | 0 | 0
2021 | 2.0997 | 1.0175 | 0.93006 | 762.8471 | 61.7622 | 824.6093 |  | 26.2605 | 0 | 0 | 0 | 11.3898 | 37.6503 | 263.8536 |  | 1088.4629 | 0 | 0 | 0 | 2016 | 0.91205 | 5% | 197.9655 | 180.5549 | 5.7465 | 186.3014
2022 | 2.2183 | 1.0168 | 0.86501 | 762.8471 | 62.7972 | 825.6442 |  | 27.7447 | 0 | 0 | 0 | 11.5807 | 39.3254 | 275.5921 |  | 1101.2364 | 0 | 0 | 0 | 2017 | 0.929 | 5% | 197.9655 | 183.91 | 17.712 | 201.622
2023 | 2.2913 | 1.0143 | 0.80451 | 762.8471 | 63.6951 | 826.5421 |  | 28.6577 | 0 | 0 | 0 | 11.7463 | 40.404 | 283.151 |  | 1109.6931 | 0 | 0 | 0 | 2018 | 0.94626 | 25% | 989.8275 | 936.6373 | 54.5027 | 991.14
2024 | 2.392 | 1.0181 | 0.74824 | 762.8471 | 64.8502 | 827.6972 |  | 29.9167 | 0 | 0 | 0 | 11.9593 | 41.876 | 293.4671 |  | 1121.1643 | 0 | 0 | 0 | 2019 | 0.96385 | 35% | 1385.7584 | 1335.6587 | 130.2917 | 1465.9504
2025 | 2.535 | 1.0199 | 0.69591 | 762.8471 | 66.1381 | 828.9851 |  | 31.7052 | 0 | 0 | 0 | 12.1968 | 43.902 | 307.6653 |  | 1136.6505 | 0 | 0 | 0 | 2020 | 0.98176 | 30% | 1187.793 | 1166.124 | 218.2087 | 1384.3327
2026 | 2.4761 | 1.0198 | 0.64724 | 762.8471 | 67.4472 | 830.2942 |  | 30.9684 | 0 | 0 | 0 | 12.4382 | 43.4066 | 304.1932 |  | 1134.4874 | 0 | 0 | 0 | Total Plant: |  | 100% | 3959.3098 | 3802.8849 | 426.4616 | 4229.3465
2027 | 2.4643 | 1.0204 | 0.60197 | 762.8471 | 68.8198 | 831.6668 |  | 30.8204 | 0 | 0 | 0 | 12.6913 | 43.5117 | 304.93 |  | 1136.5968 | 0 | 0 | 0 | [5 empty] | summer $/kw | 6707.9246
2028 | 2.5175 | 1.0212 | 0.55987 | 762.8471 | 70.2765 | 833.1236 |  | 31.4859 | 0 | 0 | 0 | 12.96 | 44.4459 | 311.4769 |  | 1144.6005 | 0 | 0 | 0
2029 | 2.5694 | 1.0217 | 0.52071 | 762.8471 | 71.8006 | 834.6477 |  | 32.1353 | 0 | 0 | 0 | 13.241 | 45.3764 | 317.9975 |  | 1152.6452 | 0 | 0 | 0
2030 | 2.6209 | 1.0216 | 0.48429 | 762.8471 | 73.3511 | 836.1982 |  | 32.7797 | 0 | 0 | 0 | 13.527 | 46.3067 | 324.5173 |  | 1160.7155 | 0 | 0 | 0
2031 | 2.6706 | 1.0206 | 0.45042 | 762.8471 | 74.864 | 837.711 |  | 33.4007 | 0 | 0 | 0 | 13.806 | 47.2067 | 330.8242 |  | 1168.5353 | 0 | 0 | 0
2032 | 2.7197 | 1.0201 | 0.41892 | 762.8471 | 76.3652 | 839.2123 |  | 34.0155 | 0 | 0 | 0 | 14.0828 | 48.0983 | 337.0726 |  | 1176.2849 | 0 | 0 | 0
2033 | 2.7676 | 1.0189 | 0.38962 | 762.8471 | 77.8118 | 840.6589 |  | 34.6138 | 0 | 0 | 0 | 14.3496 | 48.9634 | 343.1354 |  | 1183.7943 | 0 | 0 | 0
2034 | 2.8154 | 1.0184 | 0.36237 | 762.8471 | 79.244 | 842.0911 |  | 35.2124 | 0 | 0 | 0 | 14.6137 | 49.8261 | 349.1811 |  | 1191.2722 | 0 | 0 | 0
2035 | 2.864 | 1.0176 | 0.33702 | 762.8471 | 80.6379 | 843.485 |  | 35.8205 | 0 | 0 | 0 | 14.8708 | 50.6912 | 355.2441 |  | 1198.7291 | 0 | 0 | 0
2036 | 2.9132 | 1.0173 | 0.31345 | 762.8471 | 82.0324 | 844.8795 |  | 36.4358 | 0 | 0 | 0 | 15.1279 | 51.5637 | 361.3584 |  | 1206.2379 | 0 | 0 | 0
2037 | 2.9643 | 1.0173 | 0.29153 | 762.8471 | 83.449 | 846.2961 |  | 37.0748 | 0 | 0 | 0 | 15.3892 | 52.4639 | 367.6671 |  | 1213.9632 | 0 | 0 | 0
2038 | 3.0192 | 1.0172 | 0.27114 | 762.8471 | 84.8825 | 847.7296 |  | 37.7609 | 0 | 0 | 0 | 15.6535 | 53.4144 | 374.3282 |  | 1222.0578 | 0 | 0 | 0
2039 | 3.0752 | 1.0175 | 0.25218 | 762.8471 | 86.3711 | 849.2182 |  | 38.4611 | 0 | 0 | 0 | 15.928 | 54.3892 | 381.1593 |  | 1230.3775 | 0 | 0 | 0
2040 | 3.1321 | 1.0185 | 0.23454 | 762.8471 | 87.9696 | 850.8166 |  | 39.1737 | 0 | 0 | 0 | 16.2228 | 55.3965 | 388.2188 |  | 1239.0354 | 0 | 0 | 0
2041 | 3.1914 | 1.0185 | 0.21814 | 762.8471 | 89.6009 | 852.4479 |  | 39.9149 | 0 | 0 | 0 | 16.5236 | 56.4385 | 395.521 |  | 1247.969 | 0 | 0 | 0
2042 | 3.2503 | 1.0185 | 0.20288 | 762.8471 | 91.2609 | 854.108 |  | 40.6517 | 0 | 0 | 0 | 16.8298 | 57.4815 | 402.8304 |  | 1256.9384 | 0 | 0 | 0
2043 | 3.3101 | 1.0189 | 0.18869 | 762.8471 | 92.9875 | 855.8346 |  | 41.3994 | 0 | 0 | 0 | 17.1482 | 58.5475 | 410.3012 |  | 1266.1358 | 0 | 0 | 0
2044 | 3.3704 | 1.0185 | 0.17549 | 762.8471 | 94.7042 | 857.5512 |  | 42.1533 | 0 | 0 | 0 | 17.4648 | 59.618 | 417.8031 |  | 1275.3544 | 0 | 0 | 0
2045 | 3.4322 | 1.0184 | 0.16322 | 762.8471 | 96.4459 | 859.293 |  | 42.9262 | 0 | 0 | 0 | 17.786 | 60.7122 | 425.471 |  | 1284.7639 | 0 | 0 | 0
2046 | 3.4944 | 1.0182 | 0.1518 | 762.8471 | 98.2022 | 861.0493 |  | 43.7039 | 0 | 0 | 0 | 18.1098 | 61.8137 | 433.1907 |  | 1294.24 | 0 | 0 | 0
2047 | 3.5572 | 1.0183 | 0.14119 | 762.8471 | 100.003 | 862.85 |  | 44.4905 | 0 | 0 | 0 | 18.4419 | 62.9324 | 441.0306 |  | 1303.8806 | 0 | 0 | 0
2048 | 3.6191 | 1.0181 | 0.13131 | 762.8471 | 101.8146 | 864.6617 |  | 45.264 | 0 | 0 | 0 | 18.776 | 64.04 | 448.7924 |  | 1313.4541 | 0 | 0 | 0
2049 | 3.6813 | 1.018 | 0.12213 | 762.8471 | 103.6472 | 866.4943 |  | 46.0421 | 0 | 0 | 0 | 19.114 | 65.1561 | 456.6136 |  | 1323.1079 | 0 | 0 | 0
2050 | 3.7439 | 1.0174 | 0.11359 | 762.8471 | 105.4491 | 868.2961 |  | 46.8247 | 0 | 0 | 0 | 19.4463 | 66.271 | 464.4269 |  | 1332.723 | 0 | 0 | 0
|  | Present Worth | 11.7874 | 8992.0054 | 877.2826 | 9869.288 |  | 392.6986 | 0 | 0 | 0 | 161.7831 | 554.4816 | 3885.8072 | 0 | 13755.0952 |  |  |  | CF | $/kW-yr
|  | Levelized |  | 762.8471 | 74.4253 | 837.2723 |  | 33.315 | 0 | 0 | 0 | 13.7251 | 47.0401 | 329.6569 | 0 | 1166.9292 |  |  |  | 0 | 837.2723
[20 empty] | #REF! | 1166.9292
[11 empty] | Total Fixed Costs ($/kW) |  | 837.2723
[11 empty] | Total Variable Costs ($/MWh) |  | 47.0401
CF
[11 empty] | 1 |  | 9604.9434
[11 empty] | 2 |  | 4825.9917
[11 empty] | 3 |  | 3233.0078
[11 empty] | 4 |  | 2436.5159
[11 empty] | 5 |  | 1958.6207
[11 empty] | 6 |  | 1640.024
[11 empty] | 7 |  | 1412.4548
[11 empty] | 8 |  | 1241.778
[11 empty] | 9 |  | 1109.0293
[11 empty] | 10 |  | 1002.8304
[11 empty] | 11 |  | 915.9404
[11 empty] | 12 |  | 843.532
[11 empty] | 13 |  | 782.2634
[11 empty] | 14 |  | 729.7475
[11 empty] | 15 |  | 684.2336
[11 empty] | 16 |  | 644.409
[11 empty] | 17 |  | 609.2697
[11 empty] | 18 |  | 578.0347
[11 empty] | 19 |  | 550.0876
[11 empty] | 20 |  | 524.9352
[11 empty] | 21 |  | 502.1783
[11 empty] | 22 |  | 481.4902
[11 empty] | 23 |  | 462.6011
[11 empty] | 24 |  | 445.2861
[11 empty] | 25 |  | 429.3562
[11 empty] | 26 |  | 414.6517
[11 empty] | 27 |  | 401.0365
[11 empty] | 28 |  | 388.3938
[11 empty] | 29 |  | 376.623
[11 empty] | 30 |  | 365.6369
[11 empty] | 35 |  | 320.123
[11 empty] | 40 |  | 285.9877
[11 empty] | 45 |  | 259.4379
[11 empty] | 50 |  | 238.1981
[11 empty] | 55 |  | 220.8201
[11 empty] | 60 |  | 206.3385
[11 empty] | 65 |  | 194.0847
[11 empty] | 70 |  | 183.5816
[11 empty] | 75 |  | 174.4788
[11 empty] | 80 |  | 166.5139
[11 empty] | 85 |  | 159.486
[11 empty] | 90 |  | 153.239
[11 empty] | 95 |  | 147.6496
[11 empty] | 100 |  | 142.6191

## EIA_CC_2x1_H
COMB TURBINE H CLASS, 1100-MW COMBINED CYCLE | [19 empty] | CALCULATION OF CONSTRUCTION EXPENDITURES
Input Parameters | [19 empty] | Summer Capacity: | 1055.5424 | MW
(A) | Year of Cost Estimates |  |  | 2021 |  | (E) | New Capacity Cost ($/kW) |  |  |  | 1086.2998 |  | (I) | Heat Rate (MBtu/MWh) |  |  |  | 6.3636 |  | Overnight Cost: | 1027.8893 | $M
(B) | First Year of Analysis |  |  | 2021 |  | (F) | Fixed O&M ($/kW-Yr) |  |  |  | 12.4374 |  | (J) | SO2 Emission Rate (lb./MBtu) |  |  |  | 0.001 |  | Overnight Cost: | 973.8021 | $/kW (Summer, Excludes AFDC)
(C) | Discount Rate (%) |  |  | 7.52 |  | (G) | Variable O&M ($/MWh) |  |  |  | 1.9064 |  | (K) | NOx Emission Rate (lb./MBtu) |  |  |  | 0.0075 |  | Base Year | 2021
(D) | Carrying Charge Rate (%) |  |  | 11.1764 |  | (H) | Capacity Factor (%) |  |  |  | 80 |  | (L) | CO2 Emission Rate (lb./MBtu) |  |  |  | 117 |  | AFDC Rate: | 6.3653 | %
[20 empty] | In-service Date: | 2021
[20 empty] | Average Infl Rate: | 1.8582
[22 empty] | Percent | Direct | Direct
|  |  |  | Fixed Costs |  |  |  | Variable Costs | [7 empty] | Total | [5 empty] | of Total | Expen. | Expen.
|  | O&M | Present |  | Fixed |  |  | Fuel | SO2 | NOx | CO2 | Variable |  |  |  | Annual |  |  |  | Year | Deflator | Expen. | 2,021$ | As Spent | AFDC | Total Expen.
| Fuel Cost | Escalation | Value | Generation | O&M | Total |  | Cost | Cost | Cost | Cost | O&M | Total | Total |  | Costs | Allowance Costs - $/Ton | [5 empty] | ($M) | ($M) | ($M) | ($M)
Year | ($/MBtu) | Factor | Factor | ($/kW) | ($/kW) | ($/kW) |  | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW) |  | ($/kW) | SO2 | NOx | CO2 | 2015 | 0.89541 | 0% | 0 | 0 | 0 | 0
2021 | 3.0424 | 1.0175 | 0.93006 | 123.5376 | 12.6553 | 136.1929 |  | 19.3607 | 0 | 0 | 0 | 1.9398 | 21.3005 | 149.2736 |  | 285.4665 | 0 | 0 | 0 | 2016 | 0.91205 | 6% | 61.6734 | 56.2493 | 1.7902 | 58.0396
2022 | 3.1764 | 1.0168 | 0.86501 | 123.5376 | 12.8674 | 136.405 |  | 20.2133 | 0 | 0 | 0 | 1.9723 | 22.1856 | 155.4769 |  | 291.8819 | 0 | 0 | 0 | 2017 | 0.929 | 30% | 308.3668 | 286.4729 | 12.8119 | 299.2848
2023 | 3.5222 | 1.0143 | 0.80451 | 123.5376 | 13.0514 | 136.589 |  | 22.4141 | 0 | 0 | 0 | 2.0005 | 24.4146 | 171.0973 |  | 307.6863 | 0 | 0 | 0 | 2018 | 0.94626 | 46% | 472.8291 | 447.4208 | 36.9848 | 484.4056
2024 | 3.8599 | 1.0181 | 0.74824 | 123.5376 | 13.2881 | 136.8256 |  | 24.5628 | 0 | 0 | 0 | 2.0368 | 26.5996 | 186.4101 |  | 323.2357 | 0 | 0 | 0 | 2019 | 0.96385 | 15% | 154.1834 | 148.6092 | 58.3087 | 206.9179
2025 | 4.0826 | 1.0199 | 0.69591 | 123.5376 | 13.552 | 137.0895 |  | 25.9804 | 0 | 0 | 0 | 2.0772 | 28.0577 | 196.6281 |  | 333.7177 | 0 | 0 | 0 | 2020 | 0.98176 | 3% | 30.8367 | 30.2741 | 67.7135 | 97.9877
2026 | 4.2296 | 1.0198 | 0.64724 | 123.5376 | 13.8202 | 137.3578 |  | 26.9156 | 0 | 0 | 0 | 2.1183 | 29.0339 | 203.4697 |  | 340.8275 | 0 | 0 | 0 | Total Plant: |  | 100% | 1027.8893 | 969.0263 | 177.6092 | 1146.6355
2027 | 4.2825 | 1.0204 | 0.60197 | 123.5376 | 14.1015 | 137.639 |  | 27.2523 | 0 | 0 | 0 | 2.1615 | 29.4138 | 206.1319 |  | 343.7709 | 0 | 0 | 0 | [5 empty] | summer $/kw | 1086.2998
2028 | 4.2531 | 1.0212 | 0.55987 | 123.5376 | 14.4 | 137.9375 |  | 27.0652 | 0 | 0 | 0 | 2.2072 | 29.2724 | 205.1409 |  | 343.0784 | 0 | 0 | 0
2029 | 4.2829 | 1.0217 | 0.52071 | 123.5376 | 14.7122 | 138.2498 |  | 27.2545 | 0 | 0 | 0 | 2.2551 | 29.5095 | 206.8029 |  | 345.0527 | 0 | 0 | 0
2030 | 4.3993 | 1.0216 | 0.48429 | 123.5376 | 15.03 | 138.5675 |  | 27.9956 | 0 | 0 | 0 | 2.3038 | 30.2994 | 212.338 |  | 350.9056 | 0 | 0 | 0
2031 | 4.5783 | 1.0206 | 0.45042 | 123.5376 | 15.34 | 138.8775 |  | 29.1347 | 0 | 0 | 0 | 2.3513 | 31.486 | 220.6537 |  | 359.5312 | 0 | 0 | 0
2032 | 4.7416 | 1.0201 | 0.41892 | 123.5376 | 15.6476 | 139.1851 |  | 30.1741 | 0 | 0 | 0 | 2.3984 | 32.5725 | 228.2682 |  | 367.4533 | 0 | 0 | 0
2033 | 4.8325 | 1.0189 | 0.38962 | 123.5376 | 15.944 | 139.4815 |  | 30.7523 | 0 | 0 | 0 | 2.4439 | 33.1962 | 232.6388 |  | 372.1203 | 0 | 0 | 0
2034 | 4.9285 | 1.0184 | 0.36237 | 123.5376 | 16.2374 | 139.775 |  | 31.3634 | 0 | 0 | 0 | 2.4889 | 33.8522 | 237.2365 |  | 377.0115 | 0 | 0 | 0
2035 | 5.1047 | 1.0176 | 0.33702 | 123.5376 | 16.5231 | 140.0606 |  | 32.4845 | 0 | 0 | 0 | 2.5326 | 35.0171 | 245.4001 |  | 385.4608 | 0 | 0 | 0
2036 | 5.2561 | 1.0173 | 0.31345 | 123.5376 | 16.8088 | 140.3463 |  | 33.4479 | 0 | 0 | 0 | 2.5764 | 36.0243 | 252.4584 |  | 392.8048 | 0 | 0 | 0
2037 | 5.3853 | 1.0173 | 0.29153 | 123.5376 | 17.0991 | 140.6366 |  | 34.2699 | 0 | 0 | 0 | 2.6209 | 36.8908 | 258.5309 |  | 399.1676 | 0 | 0 | 0
2038 | 5.5096 | 1.0172 | 0.27114 | 123.5376 | 17.3928 | 140.9304 |  | 35.0611 | 0 | 0 | 0 | 2.6659 | 37.727 | 264.3912 |  | 405.3215 | 0 | 0 | 0
2039 | 5.625 | 1.0175 | 0.25218 | 123.5376 | 17.6978 | 141.2354 |  | 35.7952 | 0 | 0 | 0 | 2.7127 | 38.5079 | 269.8631 |  | 411.0985 | 0 | 0 | 0
2040 | 5.7904 | 1.0185 | 0.23454 | 123.5376 | 18.0253 | 141.5629 |  | 36.8479 | 0 | 0 | 0 | 2.7629 | 39.6108 | 277.5928 |  | 419.1557 | 0 | 0 | 0
2041 | 5.9483 | 1.0185 | 0.21814 | 123.5376 | 18.3596 | 141.8972 |  | 37.853 | 0 | 0 | 0 | 2.8141 | 40.6671 | 284.995 |  | 426.8922 | 0 | 0 | 0
2042 | 6.1064 | 1.0185 | 0.20288 | 123.5376 | 18.6998 | 142.2373 |  | 38.8591 | 0 | 0 | 0 | 2.8663 | 41.7254 | 292.4114 |  | 434.6487 | 0 | 0 | 0
2043 | 6.2854 | 1.0189 | 0.18869 | 123.5376 | 19.0535 | 142.5911 |  | 39.998 | 0 | 0 | 0 | 2.9205 | 42.9185 | 300.7728 |  | 443.3639 | 0 | 0 | 0
2044 | 6.4984 | 1.0185 | 0.17549 | 123.5376 | 19.4053 | 142.9429 |  | 41.3536 | 0 | 0 | 0 | 2.9744 | 44.328 | 310.6509 |  | 453.5937 | 0 | 0 | 0
2045 | 6.7357 | 1.0184 | 0.16322 | 123.5376 | 19.7622 | 143.2997 |  | 42.8632 | 0 | 0 | 0 | 3.0291 | 45.8924 | 321.6137 |  | 464.9134 | 0 | 0 | 0
2046 | 6.9572 | 1.0182 | 0.1518 | 123.5376 | 20.1221 | 143.6596 |  | 44.273 | 0 | 0 | 0 | 3.0843 | 47.3573 | 331.8801 |  | 475.5397 | 0 | 0 | 0
2047 | 7.1681 | 1.0183 | 0.14119 | 123.5376 | 20.491 | 144.0286 |  | 45.6148 | 0 | 0 | 0 | 3.1408 | 48.7557 | 341.6798 |  | 485.7084 | 0 | 0 | 0
2048 | 7.4389 | 1.0181 | 0.13131 | 123.5376 | 20.8623 | 144.3998 |  | 47.3383 | 0 | 0 | 0 | 3.1977 | 50.5361 | 354.1567 |  | 498.5566 | 0 | 0 | 0
2049 | 7.5668 | 1.018 | 0.12213 | 123.5376 | 21.2378 | 144.7753 |  | 48.1521 | 0 | 0 | 0 | 3.2553 | 51.4074 | 360.2629 |  | 505.0382 | 0 | 0 | 0
2050 | 7.6954 | 1.0174 | 0.11359 | 123.5376 | 21.607 | 145.1445 |  | 48.9706 | 0 | 0 | 0 | 3.3119 | 52.2824 | 366.3954 |  | 511.5399 | 0 | 0 | 0
|  | Present Worth | 11.7874 | 1456.1902 | 179.7589 | 1635.9491 |  | 343.1812 | 0 | 0 | 0 | 27.5532 | 370.7344 | 2598.1066 | 0 | 4234.0557 |  |  |  | CF | $/kW-yr
|  | Levelized |  | 123.5376 | 15.2501 | 138.7876 |  | 29.1142 | 0 | 0 | 0 | 2.3375 | 31.4517 | 220.4133 | 0 | 359.201 |  |  |  | 0 | 138.7876
[20 empty] | 80 | 359.201
[11 empty] | Total Fixed Costs ($/kW) |  | 138.7876
[11 empty] | Total Variable Costs ($/MWh) |  | 31.4517
CF
[11 empty] | 1 |  | 1615.7852
[11 empty] | 2 |  | 823.6184
[11 empty] | 3 |  | 559.5628
[11 empty] | 4 |  | 427.5351
[11 empty] | 5 |  | 348.3184
[11 empty] | 6 |  | 295.5073
[11 empty] | 7 |  | 257.785
[11 empty] | 8 |  | 229.4934
[11 empty] | 9 |  | 207.4887
[11 empty] | 10 |  | 189.885
[11 empty] | 11 |  | 175.482
[11 empty] | 12 |  | 163.4795
[11 empty] | 13 |  | 153.3235
[11 empty] | 14 |  | 144.6184
[11 empty] | 15 |  | 137.0739
[11 empty] | 16 |  | 130.4725
[11 empty] | 17 |  | 124.6478
[11 empty] | 18 |  | 119.4702
[11 empty] | 19 |  | 114.8376
[11 empty] | 20 |  | 110.6684
[11 empty] | 21 |  | 106.8961
[11 empty] | 22 |  | 103.4668
[11 empty] | 23 |  | 100.3357
[11 empty] | 24 |  | 97.4656
[11 empty] | 25 |  | 94.825
[11 empty] | 26 |  | 92.3876
[11 empty] | 27 |  | 90.1307
[11 empty] | 28 |  | 88.035
[11 empty] | 29 |  | 86.0839
[11 empty] | 30 |  | 84.2628
[11 empty] | 35 |  | 76.7183
[11 empty] | 40 |  | 71.06
[11 empty] | 45 |  | 66.6591
[11 empty] | 50 |  | 63.1383
[11 empty] | 55 |  | 60.2577
[11 empty] | 60 |  | 57.8572
[11 empty] | 65 |  | 55.826
[11 empty] | 70 |  | 54.085
[11 empty] | 75 |  | 52.5761
[11 empty] | 80 |  | 51.2558
[11 empty] | 85 |  | 50.0909
[11 empty] | 90 |  | 49.0554
[11 empty] | 95 |  | 48.1289
[11 empty] | 100 |  | 47.295

## EIA_CC_1x1_H
COMB TURBINE H CLASS, COMBINED-CYCLE SINGLE SHAFT, 430 MW | [19 empty] | CALCULATION OF CONSTRUCTION EXPENDITURES
Input Parameters | [19 empty] | Summer Capacity: | 407.4023 | MW
(A) | Year of Cost Estimates |  |  | 2021 |  | (E) | New Capacity Cost ($/kW) |  |  |  | 1254.3204 |  | (I) | Heat Rate (MBtu/MWh) |  |  |  | 7.1169 |  | Overnight Cost: | 458.0923 | $M
(B) | First Year of Analysis |  |  | 2021 |  | (F) | Fixed O&M ($/kW-Yr) |  |  |  | 28.137 |  | (J) | SO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | Overnight Cost: | 1124.4224 | $/kW (Summer, Excludes AFDC)
(C) | Discount Rate (%) |  |  | 7.52 |  | (G) | Variable O&M ($/MWh) |  |  |  | 0 |  | (K) | NOx Emission Rate (lb./MBtu) |  |  |  | 0.0075 |  | Base Year | 2021
(D) | Carrying Charge Rate (%) |  |  | 11.1764 |  | (H) | Capacity Factor (%) |  |  |  | 80 |  | (L) | CO2 Emission Rate (lb./MBtu) |  |  |  | 117 |  | AFDC Rate: | 6.3653 | %
[20 empty] | In-service Date: | 2021
[20 empty] | Average Infl Rate: | 1.8582
[22 empty] | Percent | Direct | Direct
|  |  |  | Fixed Costs |  |  |  | Variable Costs | [7 empty] | Total | [5 empty] | of Total | Expen. | Expen.
|  | O&M | Present |  | Fixed |  |  | Fuel | SO2 | NOx | CO2 | Variable |  |  |  | Annual |  |  |  | Year | Deflator | Expen. | 2,021$ | As Spent | AFDC | Total Expen.
| Fuel Cost | Escalation | Value | Generation | O&M | Total |  | Cost | Cost | Cost | Cost | O&M | Total | Total |  | Costs | Allowance Costs - $/Ton | [5 empty] | ($M) | ($M) | ($M) | ($M)
Year | ($/MBtu) | Factor | Factor | ($/kW) | ($/kW) | ($/kW) |  | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW) |  | ($/kW) | SO2 | NOx | CO2 | 2015 | 0.89541 | 0% | 0 | 0 | 0 | 0
2021 | 3.0424 | 1.0175 | 0.93006 | 142.6454 | 28.6301 | 171.2755 |  | 21.6523 | 0 | 0 | 0 | 0 | 21.6523 | 151.7396 |  | 323.0151 | 0 | 0 | 0 | 2016 | 0.91205 | 6% | 27.4855 | 25.0683 | 0.79784 | 25.8661
2022 | 3.1764 | 1.0168 | 0.86501 | 142.6454 | 29.1099 | 171.7553 |  | 22.6059 | 0 | 0 | 0 | 0 | 22.6059 | 158.4224 |  | 330.1777 | 0 | 0 | 0 | 2017 | 0.929 | 30% | 137.4277 | 127.6704 | 5.7098 | 133.3802
2023 | 3.5222 | 1.0143 | 0.80451 | 142.6454 | 29.5261 | 172.1715 |  | 25.0672 | 0 | 0 | 0 | 0 | 25.0672 | 175.6707 |  | 347.8422 | 0 | 0 | 0 | 2018 | 0.94626 | 46% | 210.7224 | 199.3989 | 16.4828 | 215.8817
2024 | 3.8599 | 1.0181 | 0.74824 | 142.6454 | 30.0615 | 172.707 |  | 27.4703 | 0 | 0 | 0 | 0 | 27.4703 | 192.5116 |  | 365.2186 | 0 | 0 | 0 | 2019 | 0.96385 | 15% | 68.7138 | 66.2296 | 25.986 | 92.2156
2025 | 4.0826 | 1.0199 | 0.69591 | 142.6454 | 30.6586 | 173.304 |  | 29.0557 | 0 | 0 | 0 | 0 | 29.0557 | 203.6222 |  | 376.9261 | 0 | 0 | 0 | 2020 | 0.98176 | 3% | 13.7428 | 13.4921 | 30.1774 | 43.6695
2026 | 4.2296 | 1.0198 | 0.64724 | 142.6454 | 31.2654 | 173.9108 |  | 30.1015 | 0 | 0 | 0 | 0 | 30.1015 | 210.9513 |  | 384.8621 | 0 | 0 | 0 | Total Plant: |  | 100% | 458.0923 | 431.8592 | 79.1539 | 511.0131
2027 | 4.2825 | 1.0204 | 0.60197 | 142.6454 | 31.9017 | 174.5471 |  | 30.4781 | 0 | 0 | 0 | 0 | 30.4781 | 213.5908 |  | 388.1379 | 0 | 0 | 0 | [5 empty] | summer $/kw | 1254.3204
2028 | 4.2531 | 1.0212 | 0.55987 | 142.6454 | 32.5769 | 175.2224 |  | 30.2688 | 0 | 0 | 0 | 0 | 30.2688 | 212.1238 |  | 387.3462 | 0 | 0 | 0
2029 | 4.2829 | 1.0217 | 0.52071 | 142.6454 | 33.2834 | 175.9289 |  | 30.4805 | 0 | 0 | 0 | 0 | 30.4805 | 213.6075 |  | 389.5363 | 0 | 0 | 0
2030 | 4.3993 | 1.0216 | 0.48429 | 142.6454 | 34.0022 | 176.6476 |  | 31.3094 | 0 | 0 | 0 | 0 | 31.3094 | 219.4161 |  | 396.0637 | 0 | 0 | 0
2031 | 4.5783 | 1.0206 | 0.45042 | 142.6454 | 34.7035 | 177.3489 |  | 32.5833 | 0 | 0 | 0 | 0 | 32.5833 | 228.3436 |  | 405.6925 | 0 | 0 | 0
2032 | 4.7416 | 1.0201 | 0.41892 | 142.6454 | 35.3994 | 178.0448 |  | 33.7457 | 0 | 0 | 0 | 0 | 33.7457 | 236.4899 |  | 414.5347 | 0 | 0 | 0
2033 | 4.8325 | 1.0189 | 0.38962 | 142.6454 | 36.07 | 178.7154 |  | 34.3924 | 0 | 0 | 0 | 0 | 34.3924 | 241.0217 |  | 419.7371 | 0 | 0 | 0
2034 | 4.9285 | 1.0184 | 0.36237 | 142.6454 | 36.7339 | 179.3793 |  | 35.0758 | 0 | 0 | 0 | 0 | 35.0758 | 245.8111 |  | 425.1904 | 0 | 0 | 0
2035 | 5.1047 | 1.0176 | 0.33702 | 142.6454 | 37.38 | 180.0254 |  | 36.3296 | 0 | 0 | 0 | 0 | 36.3296 | 254.5979 |  | 434.6234 | 0 | 0 | 0
2036 | 5.2561 | 1.0173 | 0.31345 | 142.6454 | 38.0264 | 180.6719 |  | 37.407 | 0 | 0 | 0 | 0 | 37.407 | 262.1485 |  | 442.8203 | 0 | 0 | 0
2037 | 5.3853 | 1.0173 | 0.29153 | 142.6454 | 38.6831 | 181.3285 |  | 38.3263 | 0 | 0 | 0 | 0 | 38.3263 | 268.591 |  | 449.9196 | 0 | 0 | 0
2038 | 5.5096 | 1.0172 | 0.27114 | 142.6454 | 39.3476 | 181.993 |  | 39.2112 | 0 | 0 | 0 | 0 | 39.2112 | 274.792 |  | 456.7851 | 0 | 0 | 0
2039 | 5.625 | 1.0175 | 0.25218 | 142.6454 | 40.0377 | 182.6831 |  | 40.0321 | 0 | 0 | 0 | 0 | 40.0321 | 280.5453 |  | 463.2283 | 0 | 0 | 0
2040 | 5.7904 | 1.0185 | 0.23454 | 142.6454 | 40.7786 | 183.424 |  | 41.2095 | 0 | 0 | 0 | 0 | 41.2095 | 288.7965 |  | 472.2205 | 0 | 0 | 0
2041 | 5.9483 | 1.0185 | 0.21814 | 142.6454 | 41.5348 | 184.1803 |  | 42.3335 | 0 | 0 | 0 | 0 | 42.3335 | 296.6733 |  | 480.8535 | 0 | 0 | 0
2042 | 6.1064 | 1.0185 | 0.20288 | 142.6454 | 42.3044 | 184.9498 |  | 43.4587 | 0 | 0 | 0 | 0 | 43.4587 | 304.5589 |  | 489.5086 | 0 | 0 | 0
2043 | 6.2854 | 1.0189 | 0.18869 | 142.6454 | 43.1047 | 185.7501 |  | 44.7325 | 0 | 0 | 0 | 0 | 44.7325 | 313.485 |  | 499.2352 | 0 | 0 | 0
2044 | 6.4984 | 1.0185 | 0.17549 | 142.6454 | 43.9005 | 186.5459 |  | 46.2485 | 0 | 0 | 0 | 0 | 46.2485 | 324.1097 |  | 510.6556 | 0 | 0 | 0
2045 | 6.7357 | 1.0184 | 0.16322 | 142.6454 | 44.7079 | 187.3533 |  | 47.9369 | 0 | 0 | 0 | 0 | 47.9369 | 335.9414 |  | 523.2947 | 0 | 0 | 0
2046 | 6.9572 | 1.0182 | 0.1518 | 142.6454 | 45.522 | 188.1674 |  | 49.5135 | 0 | 0 | 0 | 0 | 49.5135 | 346.9908 |  | 535.1582 | 0 | 0 | 0
2047 | 7.1681 | 1.0183 | 0.14119 | 142.6454 | 46.3568 | 189.0022 |  | 51.0142 | 0 | 0 | 0 | 0 | 51.0142 | 357.5072 |  | 546.5093 | 0 | 0 | 0
2048 | 7.4389 | 1.0181 | 0.13131 | 142.6454 | 47.1966 | 189.842 |  | 52.9416 | 0 | 0 | 0 | 0 | 52.9416 | 371.015 |  | 560.857 | 0 | 0 | 0
2049 | 7.5668 | 1.018 | 0.12213 | 142.6454 | 48.0461 | 190.6915 |  | 53.8517 | 0 | 0 | 0 | 0 | 53.8517 | 377.3928 |  | 568.0843 | 0 | 0 | 0
2050 | 7.6954 | 1.0174 | 0.11359 | 142.6454 | 48.8813 | 191.5267 |  | 54.7671 | 0 | 0 | 0 | 0 | 54.7671 | 383.8076 |  | 575.3344 | 0 | 0 | 0
|  | Present Worth | 11.7874 | 1681.4226 | 406.6678 | 2088.0904 |  | 383.8026 | 0 | 0 | 0 | 0 | 383.8026 | 2689.6887 | 0 | 4777.7791 |  |  |  | CF | $/kW-yr
|  | Levelized |  | 142.6454 | 34.5001 | 177.1455 |  | 32.5603 | 0 | 0 | 0 | 0 | 32.5603 | 228.1828 | 0 | 405.3284 |  |  |  | 0 | 177.1455
[20 empty] | #REF! | 405.3284
[11 empty] | Total Fixed Costs ($/kW) |  | 177.1455
[11 empty] | Total Variable Costs ($/MWh) |  | 32.5603
CF
[11 empty] | 1 |  | 2054.7697
[11 empty] | 2 |  | 1043.665
[11 empty] | 3 |  | 706.6301
[11 empty] | 4 |  | 538.1127
[11 empty] | 5 |  | 437.0022
[11 empty] | 6 |  | 369.5952
[11 empty] | 7 |  | 321.4474
[11 empty] | 8 |  | 285.3365
[11 empty] | 9 |  | 257.2503
[11 empty] | 10 |  | 234.7813
[11 empty] | 11 |  | 216.3975
[11 empty] | 12 |  | 201.0778
[11 empty] | 13 |  | 188.1149
[11 empty] | 14 |  | 177.0039
[11 empty] | 15 |  | 167.3743
[11 empty] | 16 |  | 158.9484
[11 empty] | 17 |  | 151.5138
[11 empty] | 18 |  | 144.9053
[11 empty] | 19 |  | 138.9924
[11 empty] | 20 |  | 133.6708
[11 empty] | 21 |  | 128.856
[11 empty] | 22 |  | 124.4789
[11 empty] | 23 |  | 120.4825
[11 empty] | 24 |  | 116.8191
[11 empty] | 25 |  | 113.4487
[11 empty] | 26 |  | 110.3376
[11 empty] | 27 |  | 107.457
[11 empty] | 28 |  | 104.7821
[11 empty] | 29 |  | 102.2917
[11 empty] | 30 |  | 99.9673
[11 empty] | 35 |  | 90.3377
[11 empty] | 40 |  | 83.1156
[11 empty] | 45 |  | 77.4983
[11 empty] | 50 |  | 73.0045
[11 empty] | 55 |  | 69.3278
[11 empty] | 60 |  | 66.2638
[11 empty] | 65 |  | 63.6712
[11 empty] | 70 |  | 61.449
[11 empty] | 75 |  | 59.5231
[11 empty] | 80 |  | 57.8379
[11 empty] | 85 |  | 56.351
[11 empty] | 90 |  | 55.0293
[11 empty] | 95 |  | 53.8467
[11 empty] | 100 |  | 52.7824

## EIA_CC_1x1_H_90pct
COMB TURBINE H CLASS, COMB-CYCLE SINGLE SHAFT W/90% CO2 CAPTURE, 430 MW | [19 empty] | CALCULATION OF CONSTRUCTION EXPENDITURES
Input Parameters | [19 empty] | Summer Capacity: | 367.4418 | MW
(A) | Year of Cost Estimates |  |  | 2021 |  | (E) | New Capacity Cost ($/kW) |  |  |  | 2827.6877 |  | (I) | Heat Rate (MBtu/MWh) |  |  |  | 7.1169 |  | Overnight Cost: | 931.4102 | $M
(B) | First Year of Analysis |  |  | 2021 |  | (F) | Fixed O&M ($/kW-Yr) |  |  |  | 28.137 |  | (J) | SO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | Overnight Cost: | 2534.8508 | $/kW (Summer, Excludes AFDC)
(C) | Discount Rate (%) |  |  | 7.52 |  | (G) | Variable O&M ($/MWh) |  |  |  | 5.9536 |  | (K) | NOx Emission Rate (lb./MBtu) |  |  |  | 0.0075 |  | Base Year | 2021
(D) | Carrying Charge Rate (%) |  |  | 11.1764 |  | (H) | Capacity Factor (%) |  |  |  | 80 |  | (L) | CO2 Emission Rate (lb./MBtu) |  |  |  | 12 |  | AFDC Rate: | 6.3653 | %
[20 empty] | In-service Date: | 2021
[20 empty] | Average Infl Rate: | 1.8582
[22 empty] | Percent | Direct | Direct
|  |  |  | Fixed Costs |  |  |  | Variable Costs | [7 empty] | Total | [5 empty] | of Total | Expen. | Expen.
|  | O&M | Present |  | Fixed |  |  | Fuel | SO2 | NOx | CO2 | Variable |  |  |  | Annual |  |  |  | Year | Deflator | Expen. | 2,021$ | As Spent | AFDC | Total Expen.
| Fuel Cost | Escalation | Value | Generation | O&M | Total |  | Cost | Cost | Cost | Cost | O&M | Total | Total |  | Costs | Allowance Costs - $/Ton | [5 empty] | ($M) | ($M) | ($M) | ($M)
Year | ($/MBtu) | Factor | Factor | ($/kW) | ($/kW) | ($/kW) |  | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW) |  | ($/kW) | SO2 | NOx | CO2 | 2015 | 0.89541 | 0% | 0 | 0 | 0 | 0
2021 | 3.0424 | 1.0175 | 0.93006 | 321.5739 | 28.6301 | 350.204 |  | 21.6523 | 0 | 0 | 0 | 6.058 | 27.7103 | 194.1938 |  | 544.3978 | 0 | 0 | 0 | 2016 | 0.91205 | 6% | 55.8846 | 50.9697 | 1.6222 | 52.5919
2022 | 3.1764 | 1.0168 | 0.86501 | 321.5739 | 29.1099 | 350.6837 |  | 22.6059 | 0 | 0 | 0 | 6.1595 | 28.7654 | 201.588 |  | 552.2718 | 0 | 0 | 0 | 2017 | 0.929 | 30% | 279.4231 | 259.5841 | 11.6094 | 271.1935
2023 | 3.5222 | 1.0143 | 0.80451 | 321.5739 | 29.5261 | 351.1 |  | 25.0672 | 0 | 0 | 0 | 6.2476 | 31.3147 | 219.4535 |  | 570.5535 | 0 | 0 | 0 | 2018 | 0.94626 | 46% | 428.4487 | 405.4252 | 33.5134 | 438.9386
2024 | 3.8599 | 1.0181 | 0.74824 | 321.5739 | 30.0615 | 351.6354 |  | 27.4703 | 0 | 0 | 0 | 6.3608 | 33.8311 | 237.0885 |  | 588.7239 | 0 | 0 | 0 | 2019 | 0.96385 | 15% | 139.7115 | 134.6605 | 52.8358 | 187.4963
2025 | 4.0826 | 1.0199 | 0.69591 | 321.5739 | 30.6586 | 352.2324 |  | 29.0557 | 0 | 0 | 0 | 6.4872 | 35.5428 | 249.0843 |  | 601.3167 | 0 | 0 | 0 | 2020 | 0.98176 | 3% | 27.9423 | 27.4326 | 61.3578 | 88.7904
2026 | 4.2296 | 1.0198 | 0.64724 | 321.5739 | 31.2654 | 352.8393 |  | 30.1015 | 0 | 0 | 0 | 6.6156 | 36.7171 | 257.3133 |  | 610.1525 | 0 | 0 | 0 | Total Plant: |  | 100% | 931.4102 | 878.0721 | 160.9386 | 1039.0107
2027 | 4.2825 | 1.0204 | 0.60197 | 321.5739 | 31.9017 | 353.4755 |  | 30.4781 | 0 | 0 | 0 | 6.7502 | 37.2283 | 260.8962 |  | 614.3718 | 0 | 0 | 0 | [5 empty] | summer $/kw | 2827.6877
2028 | 4.2531 | 1.0212 | 0.55987 | 321.5739 | 32.5769 | 354.1508 |  | 30.2688 | 0 | 0 | 0 | 6.8931 | 37.1619 | 260.4306 |  | 614.5814 | 0 | 0 | 0
2029 | 4.2829 | 1.0217 | 0.52071 | 321.5739 | 33.2834 | 354.8573 |  | 30.4805 | 0 | 0 | 0 | 7.0426 | 37.5231 | 262.9619 |  | 617.8192 | 0 | 0 | 0
2030 | 4.3993 | 1.0216 | 0.48429 | 321.5739 | 34.0022 | 355.5761 |  | 31.3094 | 0 | 0 | 0 | 7.1947 | 38.504 | 269.8363 |  | 625.4124 | 0 | 0 | 0
2031 | 4.5783 | 1.0206 | 0.45042 | 321.5739 | 34.7035 | 356.2774 |  | 32.5833 | 0 | 0 | 0 | 7.3431 | 39.9263 | 279.8038 |  | 636.0811 | 0 | 0 | 0
2032 | 4.7416 | 1.0201 | 0.41892 | 321.5739 | 35.3994 | 356.9732 |  | 33.7457 | 0 | 0 | 0 | 7.4903 | 41.236 | 288.982 |  | 645.9552 | 0 | 0 | 0
2033 | 4.8325 | 1.0189 | 0.38962 | 321.5739 | 36.07 | 357.6438 |  | 34.3924 | 0 | 0 | 0 | 7.6322 | 42.0246 | 294.5082 |  | 652.152 | 0 | 0 | 0
2034 | 4.9285 | 1.0184 | 0.36237 | 321.5739 | 36.7339 | 358.3077 |  | 35.0758 | 0 | 0 | 0 | 7.7727 | 42.8485 | 300.282 |  | 658.5897 | 0 | 0 | 0
2035 | 5.1047 | 1.0176 | 0.33702 | 321.5739 | 37.38 | 358.9539 |  | 36.3296 | 0 | 0 | 0 | 7.9094 | 44.239 | 310.027 |  | 668.9809 | 0 | 0 | 0
2036 | 5.2561 | 1.0173 | 0.31345 | 321.5739 | 38.0264 | 359.6003 |  | 37.407 | 0 | 0 | 0 | 8.0462 | 45.4532 | 318.5361 |  | 678.1364 | 0 | 0 | 0
2037 | 5.3853 | 1.0173 | 0.29153 | 321.5739 | 38.6831 | 360.257 |  | 38.3263 | 0 | 0 | 0 | 8.1851 | 46.5115 | 325.9524 |  | 686.2094 | 0 | 0 | 0
2038 | 5.5096 | 1.0172 | 0.27114 | 321.5739 | 39.3476 | 360.9215 |  | 39.2112 | 0 | 0 | 0 | 8.3257 | 47.5369 | 333.1388 |  | 694.0603 | 0 | 0 | 0
2039 | 5.625 | 1.0175 | 0.25218 | 321.5739 | 40.0377 | 361.6115 |  | 40.0321 | 0 | 0 | 0 | 8.4717 | 48.5039 | 339.9152 |  | 701.5267 | 0 | 0 | 0
2040 | 5.7904 | 1.0185 | 0.23454 | 321.5739 | 40.7786 | 362.3525 |  | 41.2095 | 0 | 0 | 0 | 8.6285 | 49.8381 | 349.2652 |  | 711.6177 | 0 | 0 | 0
2041 | 5.9483 | 1.0185 | 0.21814 | 321.5739 | 41.5348 | 363.1087 |  | 42.3335 | 0 | 0 | 0 | 8.7885 | 51.122 | 358.2633 |  | 721.372 | 0 | 0 | 0
2042 | 6.1064 | 1.0185 | 0.20288 | 321.5739 | 42.3044 | 363.8782 |  | 43.4587 | 0 | 0 | 0 | 8.9514 | 52.4101 | 367.29 |  | 731.1682 | 0 | 0 | 0
2043 | 6.2854 | 1.0189 | 0.18869 | 321.5739 | 43.1047 | 364.6786 |  | 44.7325 | 0 | 0 | 0 | 9.1207 | 53.8532 | 377.403 |  | 742.0816 | 0 | 0 | 0
2044 | 6.4984 | 1.0185 | 0.17549 | 321.5739 | 43.9005 | 365.4744 |  | 46.2485 | 0 | 0 | 0 | 9.2891 | 55.5376 | 389.2077 |  | 754.682 | 0 | 0 | 0
2045 | 6.7357 | 1.0184 | 0.16322 | 321.5739 | 44.7079 | 366.2817 |  | 47.9369 | 0 | 0 | 0 | 9.4599 | 57.3968 | 402.2366 |  | 768.5183 | 0 | 0 | 0
2046 | 6.9572 | 1.0182 | 0.1518 | 321.5739 | 45.522 | 367.0959 |  | 49.5135 | 0 | 0 | 0 | 9.6322 | 59.1457 | 414.4932 |  | 781.5891 | 0 | 0 | 0
2047 | 7.1681 | 1.0183 | 0.14119 | 321.5739 | 46.3568 | 367.9306 |  | 51.0142 | 0 | 0 | 0 | 9.8088 | 60.823 | 426.2474 |  | 794.178 | 0 | 0 | 0
2048 | 7.4389 | 1.0181 | 0.13131 | 321.5739 | 47.1966 | 368.7704 |  | 52.9416 | 0 | 0 | 0 | 9.9865 | 62.9282 | 441.0005 |  | 809.771 | 0 | 0 | 0
2049 | 7.5668 | 1.018 | 0.12213 | 321.5739 | 48.0461 | 369.6199 |  | 53.8517 | 0 | 0 | 0 | 10.1663 | 64.018 | 448.638 |  | 818.258 | 0 | 0 | 0
2050 | 7.6954 | 1.0174 | 0.11359 | 321.5739 | 48.8813 | 370.4552 |  | 54.7671 | 0 | 0 | 0 | 10.343 | 65.1101 | 456.2914 |  | 826.7466 | 0 | 0 | 0
|  | Present Worth | 11.7874 | 3790.529 | 406.6678 | 4197.1968 |  | 383.8026 | 0 | 0 | 0 | 86.0485 | 469.8512 | 3292.7169 | 0 | 7489.9137 |  |  |  | CF | $/kW-yr
|  | Levelized |  | 321.5739 | 34.5001 | 356.074 |  | 32.5603 | 0 | 0 | 0 | 7.3 | 39.8604 | 279.3414 | 0 | 635.4154 |  |  |  | 0 | 356.074
[20 empty] | #REF! | 635.4154
[11 empty] | Total Fixed Costs ($/kW) |  | 356.074
[11 empty] | Total Variable Costs ($/MWh) |  | 39.8604
CF
[11 empty] | 1 |  | 4104.6319
[11 empty] | 2 |  | 2072.2461
[11 empty] | 3 |  | 1394.7842
[11 empty] | 4 |  | 1056.0532
[11 empty] | 5 |  | 852.8147
[11 empty] | 6 |  | 717.3223
[11 empty] | 7 |  | 620.542
[11 empty] | 8 |  | 547.9568
[11 empty] | 9 |  | 491.5016
[11 empty] | 10 |  | 446.3375
[11 empty] | 11 |  | 409.385
[11 empty] | 12 |  | 378.5913
[11 empty] | 13 |  | 352.5351
[11 empty] | 14 |  | 330.2012
[11 empty] | 15 |  | 310.8451
[11 empty] | 16 |  | 293.9086
[11 empty] | 17 |  | 278.9646
[11 empty] | 18 |  | 265.681
[11 empty] | 19 |  | 253.7957
[11 empty] | 20 |  | 243.0989
[11 empty] | 21 |  | 233.4209
[11 empty] | 22 |  | 224.6227
[11 empty] | 23 |  | 216.5896
[11 empty] | 24 |  | 209.2258
[11 empty] | 25 |  | 202.4512
[11 empty] | 26 |  | 196.1977
[11 empty] | 27 |  | 190.4075
[11 empty] | 28 |  | 185.0308
[11 empty] | 29 |  | 180.0249
[11 empty] | 30 |  | 175.3527
[11 empty] | 35 |  | 155.9967
[11 empty] | 40 |  | 141.4796
[11 empty] | 45 |  | 130.1886
[11 empty] | 50 |  | 121.1558
[11 empty] | 55 |  | 113.7653
[11 empty] | 60 |  | 107.6066
[11 empty] | 65 |  | 102.3953
[11 empty] | 70 |  | 97.9285
[11 empty] | 75 |  | 94.0573
[11 empty] | 80 |  | 90.67
[11 empty] | 85 |  | 87.6812
[11 empty] | 90 |  | 85.0245
[11 empty] | 95 |  | 82.6474
[11 empty] | 100 |  | 80.5081

## EIA_CTx1F
COMB TURBINE F CLASS, 240-MW SIMPLE CYCLE | [19 empty] | CALCULATION OF CONSTRUCTION EXPENDITURES
Input Parameters | [19 empty] | Summer Capacity: | 238.2021 | MW
(A) | Year of Cost Estimates |  |  | 2021 |  | (E) | New Capacity Cost ($/kW) |  |  |  | 725.5737 |  | (I) | Heat Rate (MBtu/MWh) |  |  |  | 9.8654 |  | Overnight Cost: | 161.5225 | $M
(B) | First Year of Analysis |  |  | 2021 |  | (F) | Fixed O&M ($/kW-Yr) |  |  |  | 7.1362 |  | (J) | SO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | Overnight Cost: | 678.0902 | $/kW (Summer, Excludes AFDC)
(C) | Discount Rate (%) |  |  | 7.52 |  | (G) | Variable O&M ($/MWh) |  |  |  | 4.5875 |  | (K) | NOx Emission Rate (lb./MBtu) |  |  |  | 0.03 |  | Base Year | 2021
(D) | Carrying Charge Rate (%) |  |  | 11.1764 |  | (H) | Capacity Factor (%) |  |  |  | 80 |  | (L) | CO2 Emission Rate (lb./MBtu) |  |  |  | 117 |  | AFDC Rate: | 6.3653 | %
[20 empty] | In-service Date: | 2021
[20 empty] | Average Infl Rate: | 1.8582
[22 empty] | Percent | Direct | Direct
|  |  |  | Fixed Costs |  |  |  | Variable Costs | [7 empty] | Total | [5 empty] | of Total | Expen. | Expen.
|  | O&M | Present |  | Fixed |  |  | Fuel | SO2 | NOx | CO2 | Variable |  |  |  | Annual |  |  |  | Year | Deflator | Expen. | 2,021$ | As Spent | AFDC | Total Expen.
| Fuel Cost | Escalation | Value | Generation | O&M | Total |  | Cost | Cost | Cost | Cost | O&M | Total | Total |  | Costs | Allowance Costs - $/Ton | [5 empty] | ($M) | ($M) | ($M) | ($M)
Year | ($/MBtu) | Factor | Factor | ($/kW) | ($/kW) | ($/kW) |  | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW) |  | ($/kW) | SO2 | NOx | CO2 | 2015 | 0.89541 | 0% | 0 | 0 | 0 | 0
2021 | 3.0424 | 1.0175 | 0.93006 | 82.5146 | 7.2613 | 89.7759 |  | 30.0144 | 0 | 0 | 0 | 4.668 | 34.6823 | 243.0537 |  | 332.8296 | 0 | 0 | 0 | 2016 | 0.91205 | 0% | 0 | 0 | 0 | 0
2022 | 3.1764 | 1.0168 | 0.86501 | 82.5146 | 7.3829 | 89.8975 |  | 31.3362 | 0 | 0 | 0 | 4.7462 | 36.0824 | 252.8656 |  | 342.7631 | 0 | 0 | 0 | 2017 | 0.929 | 0% | 0 | 0 | 0 | 0
2023 | 3.5222 | 1.0143 | 0.80451 | 82.5146 | 7.4885 | 90.0031 |  | 34.748 | 0 | 0 | 0 | 4.814 | 39.562 | 277.2507 |  | 367.2538 | 0 | 0 | 0 | 2018 | 0.94626 | 50% | 80.7613 | 76.4214 | 2.4322 | 78.8536
2024 | 3.8599 | 1.0181 | 0.74824 | 82.5146 | 7.6243 | 90.1389 |  | 38.0792 | 0 | 0 | 0 | 4.9013 | 42.9805 | 301.2073 |  | 391.3462 | 0 | 0 | 0 | 2019 | 0.96385 | 25% | 40.3806 | 38.9207 | 6.258 | 45.1788
2025 | 4.0826 | 1.0199 | 0.69591 | 82.5146 | 7.7757 | 90.2903 |  | 40.2768 | 0 | 0 | 0 | 4.9987 | 45.2755 | 317.2908 |  | 407.5811 | 0 | 0 | 0 | 2020 | 0.98176 | 25% | 40.3806 | 39.644 | 9.1568 | 48.8008
2026 | 4.2296 | 1.0198 | 0.64724 | 82.5146 | 7.9296 | 90.4442 |  | 41.7266 | 0 | 0 | 0 | 5.0976 | 46.8242 | 328.1439 |  | 418.5881 | 0 | 0 | 0 | Total Plant: |  | 100% | 161.5225 | 154.9861 | 17.8471 | 172.8332
2027 | 4.2825 | 1.0204 | 0.60197 | 82.5146 | 8.091 | 90.6056 |  | 42.2486 | 0 | 0 | 0 | 5.2014 | 47.45 | 332.5296 |  | 423.1353 | 0 | 0 | 0 | [5 empty] | summer $/kw | 725.5737
2028 | 4.2531 | 1.0212 | 0.55987 | 82.5146 | 8.2623 | 90.7769 |  | 41.9585 | 0 | 0 | 0 | 5.3115 | 47.2699 | 331.2678 |  | 422.0446 | 0 | 0 | 0
2029 | 4.2829 | 1.0217 | 0.52071 | 82.5146 | 8.4415 | 90.9561 |  | 42.2519 | 0 | 0 | 0 | 5.4266 | 47.6786 | 334.1316 |  | 425.0877 | 0 | 0 | 0
2030 | 4.3993 | 1.0216 | 0.48429 | 82.5146 | 8.6237 | 91.1384 |  | 43.4009 | 0 | 0 | 0 | 5.5438 | 48.9447 | 343.0047 |  | 434.1431 | 0 | 0 | 0
2031 | 4.5783 | 1.0206 | 0.45042 | 82.5146 | 8.8016 | 91.3162 |  | 45.1668 | 0 | 0 | 0 | 5.6582 | 50.825 | 356.1814 |  | 447.4976 | 0 | 0 | 0
2032 | 4.7416 | 1.0201 | 0.41892 | 82.5146 | 8.9781 | 91.4927 |  | 46.7781 | 0 | 0 | 0 | 5.7716 | 52.5498 | 368.2688 |  | 459.7615 | 0 | 0 | 0
2033 | 4.8325 | 1.0189 | 0.38962 | 82.5146 | 9.1482 | 91.6628 |  | 47.6745 | 0 | 0 | 0 | 5.881 | 53.5555 | 375.317 |  | 466.9798 | 0 | 0 | 0
2034 | 4.9285 | 1.0184 | 0.36237 | 82.5146 | 9.3166 | 91.8312 |  | 48.6219 | 0 | 0 | 0 | 5.9892 | 54.6111 | 382.7146 |  | 474.5458 | 0 | 0 | 0
2035 | 5.1047 | 1.0176 | 0.33702 | 82.5146 | 9.4804 | 91.995 |  | 50.3599 | 0 | 0 | 0 | 6.0946 | 56.4545 | 395.6332 |  | 487.6283 | 0 | 0 | 0
2036 | 5.2561 | 1.0173 | 0.31345 | 82.5146 | 9.6444 | 92.159 |  | 51.8534 | 0 | 0 | 0 | 6.2 | 58.0534 | 406.8383 |  | 498.9973 | 0 | 0 | 0
2037 | 5.3853 | 1.0173 | 0.29153 | 82.5146 | 9.8109 | 92.3255 |  | 53.1278 | 0 | 0 | 0 | 6.307 | 59.4348 | 416.5193 |  | 508.8449 | 0 | 0 | 0
2038 | 5.5096 | 1.0172 | 0.27114 | 82.5146 | 9.9795 | 92.4941 |  | 54.3544 | 0 | 0 | 0 | 6.4154 | 60.7697 | 425.8744 |  | 518.3685 | 0 | 0 | 0
2039 | 5.625 | 1.0175 | 0.25218 | 82.5146 | 10.1545 | 92.6691 |  | 55.4924 | 0 | 0 | 0 | 6.5279 | 62.0202 | 434.6379 |  | 527.307 | 0 | 0 | 0
2040 | 5.7904 | 1.0185 | 0.23454 | 82.5146 | 10.3424 | 92.857 |  | 57.1245 | 0 | 0 | 0 | 6.6487 | 63.7732 | 446.9223 |  | 539.7793 | 0 | 0 | 0
2041 | 5.9483 | 1.0185 | 0.21814 | 82.5146 | 10.5342 | 93.0488 |  | 58.6825 | 0 | 0 | 0 | 6.772 | 65.4545 | 458.7052 |  | 551.754 | 0 | 0 | 0
2042 | 6.1064 | 1.0185 | 0.20288 | 82.5146 | 10.7294 | 93.244 |  | 60.2423 | 0 | 0 | 0 | 6.8974 | 67.1398 | 470.5154 |  | 563.7593 | 0 | 0 | 0
2043 | 6.2854 | 1.0189 | 0.18869 | 82.5146 | 10.9324 | 93.447 |  | 62.0079 | 0 | 0 | 0 | 7.0279 | 69.0359 | 483.8033 |  | 577.2503 | 0 | 0 | 0
2044 | 6.4984 | 1.0185 | 0.17549 | 82.5146 | 11.1342 | 93.6488 |  | 64.1095 | 0 | 0 | 0 | 7.1577 | 71.2672 | 499.4405 |  | 593.0893 | 0 | 0 | 0
2045 | 6.7357 | 1.0184 | 0.16322 | 82.5146 | 11.339 | 93.8536 |  | 66.4498 | 0 | 0 | 0 | 7.2893 | 73.7392 | 516.7641 |  | 610.6176 | 0 | 0 | 0
2046 | 6.9572 | 1.0182 | 0.1518 | 82.5146 | 11.5454 | 94.06 |  | 68.6354 | 0 | 0 | 0 | 7.4221 | 76.0575 | 533.0108 |  | 627.0709 | 0 | 0 | 0
2047 | 7.1681 | 1.0183 | 0.14119 | 82.5146 | 11.7572 | 94.2718 |  | 70.7156 | 0 | 0 | 0 | 7.5582 | 78.2737 | 548.5424 |  | 642.8141 | 0 | 0 | 0
2048 | 7.4389 | 1.0181 | 0.13131 | 82.5146 | 11.9701 | 94.4848 |  | 73.3874 | 0 | 0 | 0 | 7.6951 | 81.0825 | 568.2265 |  | 662.7112 | 0 | 0 | 0
2049 | 7.5668 | 1.018 | 0.12213 | 82.5146 | 12.1856 | 94.7002 |  | 74.649 | 0 | 0 | 0 | 7.8336 | 82.4826 | 578.038 |  | 672.7382 | 0 | 0 | 0
2050 | 7.6954 | 1.0174 | 0.11359 | 82.5146 | 12.3974 | 94.912 |  | 75.9179 | 0 | 0 | 0 | 7.9698 | 83.8876 | 587.8846 |  | 682.7966 | 0 | 0 | 0
[20 empty] | CF | $/kW-yr
|  | Present Worth | 11.7874 | 972.635 | 103.1404 | 1075.7754 |  | 532.0254 | 0 | 0 | 0 | 66.3045 | 598.3299 | 4193.096 | 0 | 5268.8714
|  | Levelized |  | 82.5146 | 8.75 | 91.2646 |  | 45.135 | 0 | 0 | 0 | 5.625 | 50.76 | 355.7261 | 0 | 446.9907 |  |  |  | 0 | 91.2646
[20 empty] | 80 | 446.9907
53.9285
[11 empty] | Total Fixed Costs ($/kW) |  | 91.2646
| 4.5751 | [9 empty] | Total Variable Costs ($/MWh) |  | 50.76
CF
[11 empty] | 1 |  | 1092.5938
[11 empty] | 2 |  | 571.6769
[11 empty] | 3 |  | 398.0379
[11 empty] | 4 |  | 311.2184
[11 empty] | 5 |  | 259.1268
[11 empty] | 6 |  | 224.399
[11 empty] | 7 |  | 199.5934
[11 empty] | 8 |  | 180.9892
[11 empty] | 9 |  | 166.5193
[11 empty] | 10 |  | 154.9434
[11 empty] | 11 |  | 145.4722
[11 empty] | 12 |  | 137.5795
[11 empty] | 13 |  | 130.9011
[11 empty] | 14 |  | 125.1767
[11 empty] | 15 |  | 120.2156
[11 empty] | 16 |  | 115.8746
[11 empty] | 17 |  | 112.0443
[11 empty] | 18 |  | 108.6397
[11 empty] | 19 |  | 105.5934
[11 empty] | 20 |  | 102.8517
[11 empty] | 21 |  | 100.3711
[11 empty] | 22 |  | 98.1161
[11 empty] | 23 |  | 96.0571
[11 empty] | 24 |  | 94.1697
[11 empty] | 25 |  | 92.4334
[11 empty] | 26 |  | 90.8305
[11 empty] | 27 |  | 89.3464
[11 empty] | 28 |  | 87.9683
[11 empty] | 29 |  | 86.6853
[11 empty] | 30 |  | 85.4878
[11 empty] | 35 |  | 80.5267
[11 empty] | 40 |  | 76.8058
[11 empty] | 45 |  | 73.9119
[11 empty] | 50 |  | 71.5967
[11 empty] | 55 |  | 69.7024
[11 empty] | 60 |  | 68.1239
[11 empty] | 65 |  | 66.7882
[11 empty] | 70 |  | 65.6433
[11 empty] | 75 |  | 64.6511
[11 empty] | 80 |  | 63.7829
[11 empty] | 85 |  | 63.0169
[11 empty] | 90 |  | 62.3359
[11 empty] | 95 |  | 61.7267
[11 empty] | 100 |  | 61.1783

## EIA_ADx1
#REF! | [19 empty] | CALCULATION OF CONSTRUCTION EXPENDITURES
Input Parameters | [19 empty] | Summer Capacity: | 107.3443 | MW
(A) | Year of Cost Estimates |  |  | 2021 |  | (E) | New Capacity Cost ($/kW) |  |  |  | 1197.1966 |  | (I) | Heat Rate (MBtu/MWh) |  |  |  | 9.0875 |  | Overnight Cost: | 120.102 | $M
(B) | First Year of Analysis |  |  | 2021 |  | (F) | Fixed O&M ($/kW-Yr) |  |  |  | 16.6171 |  | (J) | SO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | Overnight Cost: | 1118.8488 | $/kW (Summer, Excludes AFDC)
(C) | Discount Rate (%) |  |  | 7.52 |  | (G) | Variable O&M ($/MWh) |  |  |  | 4.7914 |  | (K) | NOx Emission Rate (lb./MBtu) |  |  |  | 0.09 |  | Base Year | 2021
(D) | Carrying Charge Rate (%) |  |  | 11.1764 |  | (H) | Capacity Factor (%) |  |  |  | 80 |  | (L) | CO2 Emission Rate (lb./MBtu) |  |  |  | 117 |  | AFDC Rate: | 6.3653 | %
[20 empty] | In-service Date: | 2021
[20 empty] | Average Infl Rate: | 1.8582
[22 empty] | Percent | Direct | Direct
|  |  |  | Fixed Costs |  |  |  | Variable Costs | [7 empty] | Total | [5 empty] | of Total | Expen. | Expen.
|  | O&M | Present |  | Fixed |  |  | Fuel | SO2 | NOx | CO2 | Variable |  |  |  | Annual |  |  |  | Year | Deflator | Expen. | 2,021$ | As Spent | AFDC | Total Expen.
| Fuel Cost | Escalation | Value | Generation | O&M | Total |  | Cost | Cost | Cost | Cost | O&M | Total | Total |  | Costs | Allowance Costs - $/Ton | [5 empty] | ($M) | ($M) | ($M) | ($M)
Year | ($/MBtu) | Factor | Factor | ($/kW) | ($/kW) | ($/kW) |  | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW) |  | ($/kW) | SO2 | NOx | CO2 | 2015 | 0.89541 | 0% | 0 | 0 | 0 | 0
2021 | 3.0424 | 1.0175 | 0.93006 | 136.1491 | 16.9084 | 153.0575 |  | 27.6478 | 0 | 0 | 0 | 4.8754 | 32.5232 | 227.9225 |  | 380.9799 | 0 | 0 | 0 | 2016 | 0.91205 | 0% | 0 | 0 | 0 | 0
2022 | 3.1764 | 1.0168 | 0.86501 | 136.1491 | 17.1917 | 153.3408 |  | 28.8654 | 0 | 0 | 0 | 4.9571 | 33.8225 | 237.0282 |  | 390.369 | 0 | 0 | 0 | 2017 | 0.929 | 0% | 0 | 0 | 0 | 0
2023 | 3.5222 | 1.0143 | 0.80451 | 136.1491 | 17.4375 | 153.5866 |  | 32.0081 | 0 | 0 | 0 | 5.028 | 37.0361 | 259.5492 |  | 413.1359 | 0 | 0 | 0 | 2018 | 0.94626 | 50% | 60.051 | 56.8241 | 1.8085 | 58.6326
2024 | 3.8599 | 1.0181 | 0.74824 | 136.1491 | 17.7537 | 153.9028 |  | 35.0767 | 0 | 0 | 0 | 5.1192 | 40.1958 | 281.6924 |  | 435.5952 | 0 | 0 | 0 | 2019 | 0.96385 | 25% | 30.0255 | 28.94 | 4.6532 | 33.5932
2025 | 4.0826 | 1.0199 | 0.69591 | 136.1491 | 18.1063 | 154.2554 |  | 37.101 | 0 | 0 | 0 | 5.2208 | 42.3219 | 296.5918 |  | 450.8472 | 0 | 0 | 0 | 2020 | 0.98176 | 25% | 30.0255 | 29.4778 | 6.8087 | 36.2864
2026 | 4.2296 | 1.0198 | 0.64724 | 136.1491 | 18.4647 | 154.6138 |  | 38.4365 | 0 | 0 | 0 | 5.3242 | 43.7606 | 306.6746 |  | 461.2884 | 0 | 0 | 0 | Total Plant: |  | 100% | 120.102 | 115.2418 | 13.2704 | 128.5122
2027 | 4.2825 | 1.0204 | 0.60197 | 136.1491 | 18.8405 | 154.9896 |  | 38.9174 | 0 | 0 | 0 | 5.4325 | 44.3499 | 310.8042 |  | 465.7938 | 0 | 0 | 0 | [5 empty] | summer $/kw | 1197.1966
2028 | 4.2531 | 1.0212 | 0.55987 | 136.1491 | 19.2393 | 155.3884 |  | 38.6501 | 0 | 0 | 0 | 5.5475 | 44.1976 | 309.7369 |  | 465.1253 | 0 | 0 | 0
2029 | 4.2829 | 1.0217 | 0.52071 | 136.1491 | 19.6565 | 155.8056 |  | 38.9204 | 0 | 0 | 0 | 5.6678 | 44.5883 | 312.4745 |  | 468.2801 | 0 | 0 | 0
2030 | 4.3993 | 1.0216 | 0.48429 | 136.1491 | 20.081 | 156.2301 |  | 39.9788 | 0 | 0 | 0 | 5.7902 | 45.769 | 320.7492 |  | 476.9793 | 0 | 0 | 0
2031 | 4.5783 | 1.0206 | 0.45042 | 136.1491 | 20.4952 | 156.6443 |  | 41.6054 | 0 | 0 | 0 | 5.9097 | 47.5151 | 332.9857 |  | 489.63 | 0 | 0 | 0
2032 | 4.7416 | 1.0201 | 0.41892 | 136.1491 | 20.9062 | 157.0553 |  | 43.0897 | 0 | 0 | 0 | 6.0282 | 49.1179 | 344.2181 |  | 501.2734 | 0 | 0 | 0
2033 | 4.8325 | 1.0189 | 0.38962 | 136.1491 | 21.3022 | 157.4513 |  | 43.9154 | 0 | 0 | 0 | 6.1424 | 50.0578 | 350.805 |  | 508.2563 | 0 | 0 | 0
2034 | 4.9285 | 1.0184 | 0.36237 | 136.1491 | 21.6943 | 157.8434 |  | 44.7881 | 0 | 0 | 0 | 6.2554 | 51.0435 | 357.7128 |  | 515.5562 | 0 | 0 | 0
2035 | 5.1047 | 1.0176 | 0.33702 | 136.1491 | 22.0759 | 158.225 |  | 46.3891 | 0 | 0 | 0 | 6.3654 | 52.7545 | 369.7039 |  | 527.9289 | 0 | 0 | 0
2036 | 5.2561 | 1.0173 | 0.31345 | 136.1491 | 22.4576 | 158.6067 |  | 47.7649 | 0 | 0 | 0 | 6.4755 | 54.2404 | 380.1165 |  | 538.7232 | 0 | 0 | 0
2037 | 5.3853 | 1.0173 | 0.29153 | 136.1491 | 22.8455 | 158.9946 |  | 48.9387 | 0 | 0 | 0 | 6.5873 | 55.5261 | 389.1267 |  | 548.1213 | 0 | 0 | 0
2038 | 5.5096 | 1.0172 | 0.27114 | 136.1491 | 23.2379 | 159.387 |  | 50.0686 | 0 | 0 | 0 | 6.7005 | 56.7691 | 397.8377 |  | 557.2247 | 0 | 0 | 0
2039 | 5.625 | 1.0175 | 0.25218 | 136.1491 | 23.6454 | 159.7945 |  | 51.1168 | 0 | 0 | 0 | 6.818 | 57.9349 | 406.0075 |  | 565.802 | 0 | 0 | 0
2040 | 5.7904 | 1.0185 | 0.23454 | 136.1491 | 24.083 | 160.2321 |  | 52.6203 | 0 | 0 | 0 | 6.9442 | 59.5644 | 417.4277 |  | 577.6598 | 0 | 0 | 0
2041 | 5.9483 | 1.0185 | 0.21814 | 136.1491 | 24.5296 | 160.6787 |  | 54.0555 | 0 | 0 | 0 | 7.073 | 61.1284 | 428.388 |  | 589.0667 | 0 | 0 | 0
2042 | 6.1064 | 1.0185 | 0.20288 | 136.1491 | 24.9841 | 161.1332 |  | 55.4923 | 0 | 0 | 0 | 7.204 | 62.6963 | 439.3754 |  | 600.5085 | 0 | 0 | 0
2043 | 6.2854 | 1.0189 | 0.18869 | 136.1491 | 25.4568 | 161.6059 |  | 57.1187 | 0 | 0 | 0 | 7.3403 | 64.459 | 451.7283 |  | 613.3342 | 0 | 0 | 0
2044 | 6.4984 | 1.0185 | 0.17549 | 136.1491 | 25.9267 | 162.0758 |  | 59.0545 | 0 | 0 | 0 | 7.4758 | 66.5303 | 466.2446 |  | 628.3204 | 0 | 0 | 0
2045 | 6.7357 | 1.0184 | 0.16322 | 136.1491 | 26.4036 | 162.5527 |  | 61.2103 | 0 | 0 | 0 | 7.6133 | 68.8236 | 482.316 |  | 644.8686 | 0 | 0 | 0
2046 | 6.9572 | 1.0182 | 0.1518 | 136.1491 | 26.8844 | 163.0335 |  | 63.2236 | 0 | 0 | 0 | 7.7519 | 70.9755 | 497.3964 |  | 660.4299 | 0 | 0 | 0
2047 | 7.1681 | 1.0183 | 0.14119 | 136.1491 | 27.3774 | 163.5265 |  | 65.1397 | 0 | 0 | 0 | 7.8941 | 73.0338 | 511.8209 |  | 675.3474 | 0 | 0 | 0
2048 | 7.4389 | 1.0181 | 0.13131 | 136.1491 | 27.8733 | 164.0224 |  | 67.6009 | 0 | 0 | 0 | 8.0371 | 75.638 | 530.0712 |  | 694.0936 | 0 | 0 | 0
2049 | 7.5668 | 1.018 | 0.12213 | 136.1491 | 28.375 | 164.5241 |  | 68.763 | 0 | 0 | 0 | 8.1818 | 76.9447 | 539.2288 |  | 703.7529 | 0 | 0 | 0
2050 | 7.6954 | 1.0174 | 0.11359 | 136.1491 | 28.8683 | 165.0174 |  | 69.9318 | 0 | 0 | 0 | 8.324 | 78.2558 | 548.4167 |  | 713.4341 | 0 | 0 | 0
|  | Present Worth | 11.7874 | 1604.8478 | 240.1697 | 1845.0175 |  | 490.0757 | 0 | 0 | 0 | 69.2514 | 559.3271 | 3919.7641 | 0 | 5764.7816
| 30 years | Levelized |  | 136.1491 | 20.3751 | 156.5242 |  | 41.5761 | 0 | 0 | 0 | 5.875 | 47.4512 | 332.5377 | 0 | 489.0618 |  |  |  | 0 | 156.5242
[20 empty] | 80 | 489.0618
[11 empty] | Total Fixed Costs ($/kW) |  | 156.5242
[11 empty] | Total Variable Costs ($/MWh) |  | 47.4512
30 years
CF
[11 empty] | 1 |  | 1834.2568
[11 empty] | 2 |  | 940.854
[11 empty] | 3 |  | 643.053
[11 empty] | 4 |  | 494.1526
[11 empty] | 5 |  | 404.8123
[11 empty] | 6 |  | 345.2521
[11 empty] | 7 |  | 302.7091
[11 empty] | 8 |  | 270.8019
[11 empty] | 9 |  | 245.9851
[11 empty] | 10 |  | 226.1317
[11 empty] | 11 |  | 209.888
[11 empty] | 12 |  | 196.3516
[11 empty] | 13 |  | 184.8977
[11 empty] | 14 |  | 175.0801
[11 empty] | 15 |  | 166.5715
[11 empty] | 16 |  | 159.1265
[11 empty] | 17 |  | 152.5574
[11 empty] | 18 |  | 146.7181
[11 empty] | 19 |  | 141.4936
[11 empty] | 20 |  | 136.7914
[11 empty] | 21 |  | 132.5371
[11 empty] | 22 |  | 128.6696
[11 empty] | 23 |  | 125.1384
[11 empty] | 24 |  | 121.9014
[11 empty] | 25 |  | 118.9234
[11 empty] | 26 |  | 116.1744
[11 empty] | 27 |  | 113.6291
[11 empty] | 28 |  | 111.2656
[11 empty] | 29 |  | 109.0651
[11 empty] | 30 |  | 107.0113
[11 empty] | 35 |  | 98.5027
[11 empty] | 40 |  | 92.1213
[11 empty] | 45 |  | 87.1579
[11 empty] | 50 |  | 83.1873
[11 empty] | 55 |  | 79.9385
[11 empty] | 60 |  | 77.2312
[11 empty] | 65 |  | 74.9405
[11 empty] | 70 |  | 72.9769
[11 empty] | 75 |  | 71.2752
[11 empty] | 80 |  | 69.7862
[11 empty] | 85 |  | 68.4724
[11 empty] | 90 |  | 67.3045
[11 empty] | 95 |  | 66.2596
[11 empty] | 100 |  | 65.3192

## EIA_Recip
#REF! | [19 empty] | CALCULATION OF CONSTRUCTION EXPENDITURES
Input Parameters | [19 empty] | Summer Capacity: | 20.758 | MW
(A) | Year of Cost Estimates |  |  | 2021 |  | (E) | New Capacity Cost ($/kW) |  |  |  | 1966.6987 |  | (I) | Heat Rate (MBtu/MWh) |  |  |  | 8.295 |  | Overnight Cost: | 38.5713 | $M
(B) | First Year of Analysis |  |  | 2021 |  | (F) | Fixed O&M ($/kW-Yr) |  |  |  | 35.8441 |  | (J) | SO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | Overnight Cost: | 1858.1414 | $/kW (Summer, Excludes AFDC)
(C) | Discount Rate (%) |  |  | 7.52 |  | (G) | Variable O&M ($/MWh) |  |  |  | 5.8007 |  | (K) | NOx Emission Rate (lb./MBtu) |  |  |  | 0.02 |  | Base Year | 2021
(D) | Carrying Charge Rate (%) |  |  | 11.1764 |  | (H) | Capacity Factor (%) |  |  |  | 80 |  | (L) | CO2 Emission Rate (lb./MBtu) |  |  |  | 117 |  | AFDC Rate: | 6.3653 | %
[20 empty] | In-service Date: | 2021
[20 empty] | Average Infl Rate: | 1.8582
[22 empty] | Percent | Direct | Direct
|  |  |  | Fixed Costs |  |  |  | Variable Costs | [7 empty] | Total | [5 empty] | of Total | Expen. | Expen.
|  | O&M | Present |  | Fixed |  |  | Fuel | SO2 | NOx | CO2 | Variable |  |  |  | Annual |  |  |  | Year | Deflator | Expen. | 2,021$ | As Spent | AFDC | Total Expen.
| Fuel Cost | Escalation | Value | Generation | O&M | Total |  | Cost | Cost | Cost | Cost | O&M | Total | Total |  | Costs | Allowance Costs - $/Ton | [5 empty] | ($M) | ($M) | ($M) | ($M)
Year | ($/MBtu) | Factor | Factor | ($/kW) | ($/kW) | ($/kW) |  | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW) |  | ($/kW) | SO2 | NOx | CO2 | 2015 | 0.89541 | 0% | 0 | 0 | 0 | 0
2021 | 3.0424 | 1.0175 | 0.93006 | 223.6594 | 36.4723 | 260.1317 |  | 25.2367 | 0 | 0 | 0 | 5.9024 | 31.139 | 218.2223 |  | 478.3539 | 0 | 0 | 0 | 2016 | 0.91205 | 0% | 0 | 0 | 0 | 0
2022 | 3.1764 | 1.0168 | 0.86501 | 223.6594 | 37.0835 | 260.7428 |  | 26.3481 | 0 | 0 | 0 | 6.0013 | 32.3494 | 226.7045 |  | 487.4473 | 0 | 0 | 0 | 2017 | 0.929 | 0% | 0 | 0 | 0 | 0
2023 | 3.5222 | 1.0143 | 0.80451 | 223.6594 | 37.6137 | 261.2731 |  | 29.2168 | 0 | 0 | 0 | 6.0871 | 35.3039 | 247.4094 |  | 508.6825 | 0 | 0 | 0 | 2018 | 0.94626 | 30% | 11.5714 | 10.9496 | 0.34849 | 11.2981
2024 | 3.8599 | 1.0181 | 0.74824 | 223.6594 | 38.2958 | 261.9552 |  | 32.0177 | 0 | 0 | 0 | 6.1975 | 38.2152 | 267.8118 |  | 529.767 | 0 | 0 | 0 | 2019 | 0.96385 | 40% | 15.4285 | 14.8707 | 1.1924 | 16.0632
2025 | 4.0826 | 1.0199 | 0.69591 | 223.6594 | 39.0563 | 262.7157 |  | 33.8655 | 0 | 0 | 0 | 6.3206 | 40.1861 | 281.6241 |  | 544.3398 | 0 | 0 | 0 | 2020 | 0.98176 | 30% | 11.5714 | 11.3603 | 2.1032 | 13.4635
2026 | 4.2296 | 1.0198 | 0.64724 | 223.6594 | 39.8294 | 263.4888 |  | 35.0845 | 0 | 0 | 0 | 6.4457 | 41.5301 | 291.0433 |  | 554.532 | 0 | 0 | 0 | Total Plant: |  | 100% | 38.5713 | 37.1806 | 3.6441 | 40.8247
2027 | 4.2825 | 1.0204 | 0.60197 | 223.6594 | 40.64 | 264.2994 |  | 35.5235 | 0 | 0 | 0 | 6.5768 | 42.1003 | 295.0389 |  | 559.3383 | 0 | 0 | 0 | [5 empty] | summer $/kw | 1966.6987
2028 | 4.2531 | 1.0212 | 0.55987 | 223.6594 | 41.5002 | 265.1596 |  | 35.2795 | 0 | 0 | 0 | 6.716 | 41.9955 | 294.3048 |  | 559.4643 | 0 | 0 | 0
2029 | 4.2829 | 1.0217 | 0.52071 | 223.6594 | 42.4002 | 266.0596 |  | 35.5262 | 0 | 0 | 0 | 6.8617 | 42.3879 | 297.0547 |  | 563.1143 | 0 | 0 | 0
2030 | 4.3993 | 1.0216 | 0.48429 | 223.6594 | 43.3159 | 266.9752 |  | 36.4923 | 0 | 0 | 0 | 7.0099 | 43.5022 | 304.8633 |  | 571.8385 | 0 | 0 | 0
2031 | 4.5783 | 1.0206 | 0.45042 | 223.6594 | 44.2092 | 267.8686 |  | 37.9771 | 0 | 0 | 0 | 7.1545 | 45.1316 | 316.2819 |  | 584.1505 | 0 | 0 | 0
2032 | 4.7416 | 1.0201 | 0.41892 | 223.6594 | 45.0957 | 268.7551 |  | 39.332 | 0 | 0 | 0 | 7.2979 | 46.6299 | 326.7821 |  | 595.5372 | 0 | 0 | 0
2033 | 4.8325 | 1.0189 | 0.38962 | 223.6594 | 45.95 | 269.6094 |  | 40.0857 | 0 | 0 | 0 | 7.4362 | 47.5218 | 333.033 |  | 602.6424 | 0 | 0 | 0
2034 | 4.9285 | 1.0184 | 0.36237 | 223.6594 | 46.7958 | 270.4551 |  | 40.8822 | 0 | 0 | 0 | 7.573 | 48.4552 | 339.5743 |  | 610.0295 | 0 | 0 | 0
2035 | 5.1047 | 1.0176 | 0.33702 | 223.6594 | 47.6189 | 271.2783 |  | 42.3436 | 0 | 0 | 0 | 7.7062 | 50.0498 | 350.7493 |  | 622.0276 | 0 | 0 | 0
2036 | 5.2561 | 1.0173 | 0.31345 | 223.6594 | 48.4424 | 272.1018 |  | 43.5994 | 0 | 0 | 0 | 7.8395 | 51.4389 | 360.4837 |  | 632.5854 | 0 | 0 | 0
2037 | 5.3853 | 1.0173 | 0.29153 | 223.6594 | 49.2789 | 272.9383 |  | 44.6709 | 0 | 0 | 0 | 7.9749 | 52.6458 | 368.9415 |  | 641.8798 | 0 | 0 | 0
2038 | 5.5096 | 1.0172 | 0.27114 | 223.6594 | 50.1255 | 273.7848 |  | 45.7022 | 0 | 0 | 0 | 8.1119 | 53.8141 | 377.1291 |  | 650.9139 | 0 | 0 | 0
2039 | 5.625 | 1.0175 | 0.25218 | 223.6594 | 51.0045 | 274.6639 |  | 46.659 | 0 | 0 | 0 | 8.2541 | 54.9132 | 384.8316 |  | 659.4955 | 0 | 0 | 0
2040 | 5.7904 | 1.0185 | 0.23454 | 223.6594 | 51.9484 | 275.6078 |  | 48.0313 | 0 | 0 | 0 | 8.4069 | 56.4382 | 395.5192 |  | 671.1271 | 0 | 0 | 0
2041 | 5.9483 | 1.0185 | 0.21814 | 223.6594 | 52.9118 | 276.5712 |  | 49.3414 | 0 | 0 | 0 | 8.5628 | 57.9042 | 405.7925 |  | 682.3637 | 0 | 0 | 0
2042 | 6.1064 | 1.0185 | 0.20288 | 223.6594 | 53.8921 | 277.5515 |  | 50.6529 | 0 | 0 | 0 | 8.7214 | 59.3743 | 416.0952 |  | 693.6467 | 0 | 0 | 0
2043 | 6.2854 | 1.0189 | 0.18869 | 223.6594 | 54.9117 | 278.5711 |  | 52.1374 | 0 | 0 | 0 | 8.8864 | 61.0239 | 427.6554 |  | 706.2265 | 0 | 0 | 0
2044 | 6.4984 | 1.0185 | 0.17549 | 223.6594 | 55.9254 | 279.5848 |  | 53.9045 | 0 | 0 | 0 | 9.0505 | 62.955 | 441.1886 |  | 720.7734 | 0 | 0 | 0
2045 | 6.7357 | 1.0184 | 0.16322 | 223.6594 | 56.9539 | 280.6133 |  | 55.8723 | 0 | 0 | 0 | 9.2169 | 65.0892 | 456.1454 |  | 736.7587 | 0 | 0 | 0
2046 | 6.9572 | 1.0182 | 0.1518 | 223.6594 | 57.9911 | 281.6505 |  | 57.71 | 0 | 0 | 0 | 9.3848 | 67.0948 | 470.2001 |  | 751.8506 | 0 | 0 | 0
2047 | 7.1681 | 1.0183 | 0.14119 | 223.6594 | 59.0545 | 282.7139 |  | 59.459 | 0 | 0 | 0 | 9.5569 | 69.0159 | 483.6634 |  | 766.3772 | 0 | 0 | 0
2048 | 7.4389 | 1.0181 | 0.13131 | 223.6594 | 60.1243 | 283.7837 |  | 61.7056 | 0 | 0 | 0 | 9.73 | 71.4356 | 500.6206 |  | 784.4043 | 0 | 0 | 0
2049 | 7.5668 | 1.018 | 0.12213 | 223.6594 | 61.2065 | 284.8659 |  | 62.7663 | 0 | 0 | 0 | 9.9051 | 72.6714 | 509.2815 |  | 794.1474 | 0 | 0 | 0
2050 | 7.6954 | 1.0174 | 0.11359 | 223.6594 | 62.2706 | 285.93 |  | 63.8332 | 0 | 0 | 0 | 10.0773 | 73.9105 | 517.965 |  | 803.895 | 0 | 0 | 0
|  | Present Worth | 11.7874 | 2636.3691 | 518.0594 | 3154.4285 |  | 447.3371 | 0 | 0 | 0 | 83.8384 | 531.1755 | 3722.4779 | 0 | 6876.9064 |  |  |  | CF | $/kW-yr
|  | Levelized |  | 223.6594 | 43.9502 | 267.6095 |  | 37.9504 | 0 | 0 | 0 | 7.1125 | 45.0629 | 315.8007 | 0 | 583.4102 |  |  |  | 0 | 267.6095
[20 empty] | 80 | 583.4102
53.9285
[11 empty] | Total Fixed Costs ($/kW) |  | 267.6095
| 4.5751 | [9 empty] | Total Variable Costs ($/MWh) |  | 45.0629
CF
[11 empty] | 1 |  | 3099.9664
[11 empty] | 2 |  | 1572.5146
[11 empty] | 3 |  | 1063.3641
[11 empty] | 4 |  | 808.7888
[11 empty] | 5 |  | 656.0436
[11 empty] | 6 |  | 554.2135
[11 empty] | 7 |  | 481.4777
[11 empty] | 8 |  | 426.9258
[11 empty] | 9 |  | 384.4966
[11 empty] | 10 |  | 350.5532
[11 empty] | 11 |  | 322.7814
[11 empty] | 12 |  | 299.6382
[11 empty] | 13 |  | 280.0555
[11 empty] | 14 |  | 263.2703
[11 empty] | 15 |  | 248.7231
[11 empty] | 16 |  | 235.9944
[11 empty] | 17 |  | 224.7631
[11 empty] | 18 |  | 214.7797
[11 empty] | 19 |  | 205.8473
[11 empty] | 20 |  | 197.8081
[11 empty] | 21 |  | 190.5345
[11 empty] | 22 |  | 183.9221
[11 empty] | 23 |  | 177.8848
[11 empty] | 24 |  | 172.3505
[11 empty] | 25 |  | 167.259
[11 empty] | 26 |  | 162.5592
[11 empty] | 27 |  | 158.2075
[11 empty] | 28 |  | 154.1666
[11 empty] | 29 |  | 150.4044
[11 empty] | 30 |  | 146.893
[11 empty] | 35 |  | 132.3458
[11 empty] | 40 |  | 121.4355
[11 empty] | 45 |  | 112.9496
[11 empty] | 50 |  | 106.161
[11 empty] | 55 |  | 100.6066
[11 empty] | 60 |  | 95.9779
[11 empty] | 65 |  | 92.0614
[11 empty] | 70 |  | 88.7044
[11 empty] | 75 |  | 85.7949
[11 empty] | 80 |  | 83.2492
[11 empty] | 85 |  | 81.0029
[11 empty] | 90 |  | 79.0063
[11 empty] | 95 |  | 77.2198
[11 empty] | 100 |  | 75.6119

## EIA_Small Nuclear
#REF! | [20 empty] | CALCULATION OF CONSTRUCTION EXPENDITURES
Input Parameters | [19 empty] | Summer Capacity: | 582 | MW
(A) | Year of Cost Estimates |  |  | 2021 |  | (E) | New Capacity Cost ($/kW) |  |  |  | 7263.5928 |  | (I) | Heat Rate (MBtu/MWh) |  |  |  | 10.046 |  | Overnight Cost: | 3800.0708 | $M
(B) | First Year of Analysis |  |  | 2021 |  | (F) | Fixed O&M ($/kW-Yr) |  |  |  | 97.9381 |  | (J) | SO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | Overnight Cost: | 6529.3314 | $/kW (Summer, Excludes AFDC)
(C) | Discount Rate (%) |  |  | 7.52 |  | (G) | Variable O&M ($/MWh) |  |  |  | 3 |  | (K) | NOx Emission Rate (lb./MBtu) |  |  |  | 0 |  | Base Year | 2021
(D) | Carrying Charge Rate (%) |  |  | 11.1764 |  | (H) | Capacity Factor (%) |  |  |  | 90 |  | (L) | CO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | AFDC Rate: | 6.3653 | %
[20 empty] | In-service Date: | 2021
[20 empty] | Average Infl Rate: | 1.8582
[22 empty] | Percent | Direct | Direct
|  |  |  | Fixed Costs |  |  |  | Variable Costs | [7 empty] | Total | [5 empty] | of Total | Expen. | Expen.
|  | O&M | Present |  | Fixed |  |  | Fuel | SO2 | NOx | CO2 | Variable |  |  |  | Annual |  |  |  | Year | Deflator | Expen. | 2,021$ | As Spent | AFDC | Total Expen.
| Fuel Cost | Escalation | Value | Generation | O&M | Total |  | Cost | Cost | Cost | Cost | O&M | Total | Total |  | Costs | Allowance Costs - $/Ton | [5 empty] | ($M) | ($M) | ($M) | ($M)
Year | ($/MBtu) | Factor | Factor | ($/kW) | ($/kW) | ($/kW) |  | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW) |  | ($/kW) | SO2 | NOx | CO2 | 2015 | 0.89541 | 0% | 0 | 0 | 0 | 0
2021 | 1.003 | 1.0175 | 0.93006 | 826.0395 | 99.6547 | 925.6942 |  | 10.0758 | 0 | 0 | 0 | 3.0526 | 13.1284 | 103.5043 |  | 1029.1984 | 0 | 0 | 0 | 2016 | 0.91205 | 9% | 342.0064 | 311.9278 | 9.9276 | 321.8554
2022 | 1.0253 | 1.0168 | 0.86501 | 826.0395 | 101.3246 | 927.3641 |  | 10.3003 | 0 | 0 | 0 | 3.1037 | 13.404 | 105.677 |  | 1033.0411 | 0 | 0 | 0 | 2017 | 0.929 | 29% | 1102.0205 | 1023.7776 | 53.0707 | 1076.8482
2023 | 1.0466 | 1.0143 | 0.80451 | 826.0395 | 102.7734 | 928.8129 |  | 10.514 | 0 | 0 | 0 | 3.1481 | 13.6621 | 107.7121 |  | 1036.5249 | 0 | 0 | 0 | 2018 | 0.94626 | 34% | 1292.0241 | 1222.5948 | 127.9434 | 1350.5382
2024 | 1.0673 | 1.0181 | 0.74824 | 826.0395 | 104.6371 | 930.6766 |  | 10.7223 | 0 | 0 | 0 | 3.2052 | 13.9275 | 109.8044 |  | 1040.481 | 0 | 0 | 0 | 2019 | 0.96385 | 23% | 874.0163 | 842.4177 | 201.81 | 1044.2277
2025 | 1.0886 | 1.0199 | 0.69591 | 826.0395 | 106.7152 | 932.7547 |  | 10.9363 | 0 | 0 | 0 | 3.2689 | 14.2052 | 111.9934 |  | 1044.7481 | 0 | 0 | 0 | 2020 | 0.98176 | 5% | 190.0035 | 186.5373 | 247.4041 | 433.9414
2026 | 1.1104 | 1.0198 | 0.64724 | 826.0395 | 108.8274 | 934.8669 |  | 11.1546 | 0 | 0 | 0 | 3.3336 | 14.4882 | 114.225 |  | 1049.0919 | 0 | 0 | 0 | Total Plant: |  | 100% | 3800.0708 | 3587.2552 | 640.1558 | 4227.411
2027 | 1.1326 | 1.0204 | 0.60197 | 826.0395 | 111.0422 | 937.0817 |  | 11.3785 | 0 | 0 | 0 | 3.4014 | 14.7799 | 116.5245 |  | 1053.6062 | 0 | 0 | 0 | [5 empty] | summer $/kw | 7263.5928
2028 | 1.1552 | 1.0212 | 0.55987 | 826.0395 | 113.3927 | 939.4321 |  | 11.6056 | 0 | 0 | 0 | 3.4734 | 15.079 | 118.8827 |  | 1058.3149 | 0 | 0 | 0
2029 | 1.178 | 1.0217 | 0.52071 | 826.0395 | 115.8518 | 941.8913 |  | 11.8342 | 0 | 0 | 0 | 3.5487 | 15.383 | 121.2793 |  | 1063.1706 | 0 | 0 | 0
2030 | 1.2009 | 1.0216 | 0.48429 | 826.0395 | 118.3537 | 944.3931 |  | 12.0645 | 0 | 0 | 0 | 3.6254 | 15.6899 | 123.6989 |  | 1068.092 | 0 | 0 | 0
2031 | 1.2243 | 1.0206 | 0.45042 | 826.0395 | 120.7947 | 946.8341 |  | 12.2989 | 0 | 0 | 0 | 3.7001 | 15.9991 | 126.1365 |  | 1072.9707 | 0 | 0 | 0
2032 | 1.2478 | 1.0201 | 0.41892 | 826.0395 | 123.2169 | 949.2564 |  | 12.5349 | 0 | 0 | 0 | 3.7743 | 16.3092 | 128.5821 |  | 1077.8384 | 0 | 0 | 0
2033 | 1.2714 | 1.0189 | 0.38962 | 826.0395 | 125.5511 | 951.5906 |  | 12.7726 | 0 | 0 | 0 | 3.8458 | 16.6184 | 131.0194 |  | 1082.6099 | 0 | 0 | 0
2034 | 1.2952 | 1.0184 | 0.36237 | 826.0395 | 127.8619 | 953.9014 |  | 13.0113 | 0 | 0 | 0 | 3.9166 | 16.9279 | 133.4598 |  | 1087.3612 | 0 | 0 | 0
2035 | 1.3192 | 1.0176 | 0.33702 | 826.0395 | 130.1111 | 956.1505 |  | 13.2524 | 0 | 0 | 0 | 3.9855 | 17.2379 | 135.9036 |  | 1092.0541 | 0 | 0 | 0
2036 | 1.3434 | 1.0173 | 0.31345 | 826.0395 | 132.3611 | 958.4005 |  | 13.4955 | 0 | 0 | 0 | 4.0544 | 17.5499 | 138.3637 |  | 1096.7643 | 0 | 0 | 0
2037 | 1.3675 | 1.0173 | 0.29153 | 826.0395 | 134.6468 | 960.6863 |  | 13.7376 | 0 | 0 | 0 | 4.1244 | 17.8621 | 140.8247 |  | 1101.511 | 0 | 0 | 0
2038 | 1.3917 | 1.0172 | 0.27114 | 826.0395 | 136.9598 | 962.9993 |  | 13.9811 | 0 | 0 | 0 | 4.1953 | 18.1764 | 143.303 |  | 1106.3022 | 0 | 0 | 0
2039 | 1.416 | 1.0175 | 0.25218 | 826.0395 | 139.3617 | 965.4011 |  | 14.2256 | 0 | 0 | 0 | 4.2689 | 18.4945 | 145.8104 |  | 1111.2115 | 0 | 0 | 0
2040 | 1.4404 | 1.0185 | 0.23454 | 826.0395 | 141.9408 | 967.9803 |  | 14.4699 | 0 | 0 | 0 | 4.3479 | 18.8177 | 148.359 |  | 1116.3392 | 0 | 0 | 0
2041 | 1.4645 | 1.0185 | 0.21814 | 826.0395 | 144.573 | 970.6124 |  | 14.7123 | 0 | 0 | 0 | 4.4285 | 19.1408 | 150.9061 |  | 1121.5185 | 0 | 0 | 0
2042 | 1.4885 | 1.0185 | 0.20288 | 826.0395 | 147.2515 | 973.2909 |  | 14.9534 | 0 | 0 | 0 | 4.5105 | 19.4639 | 153.4538 |  | 1126.7447 | 0 | 0 | 0
2043 | 1.5125 | 1.0189 | 0.18869 | 826.0395 | 150.0374 | 976.0769 |  | 15.1947 | 0 | 0 | 0 | 4.5959 | 19.7906 | 156.0293 |  | 1132.1061 | 0 | 0 | 0
2044 | 1.5365 | 1.0185 | 0.17549 | 826.0395 | 152.8073 | 978.8467 |  | 15.4355 | 0 | 0 | 0 | 4.6807 | 20.1162 | 158.5961 |  | 1137.4428 | 0 | 0 | 0
2045 | 1.5608 | 1.0184 | 0.16322 | 826.0395 | 155.6176 | 981.657 |  | 15.6798 | 0 | 0 | 0 | 4.7668 | 20.4466 | 161.2014 |  | 1142.8584 | 0 | 0 | 0
2046 | 1.5855 | 1.0182 | 0.1518 | 826.0395 | 158.4514 | 984.4909 |  | 15.928 | 0 | 0 | 0 | 4.8536 | 20.7817 | 163.8426 |  | 1148.3335 | 0 | 0 | 0
2047 | 1.6106 | 1.0183 | 0.14119 | 826.0395 | 161.3569 | 987.3964 |  | 16.1804 | 0 | 0 | 0 | 4.9426 | 21.123 | 166.5337 |  | 1153.9301 | 0 | 0 | 0
2048 | 1.636 | 1.0181 | 0.13131 | 826.0395 | 164.2801 | 990.3196 |  | 16.4349 | 0 | 0 | 0 | 5.0322 | 21.467 | 169.2461 |  | 1159.5657 | 0 | 0 | 0
2049 | 1.6641 | 1.018 | 0.12213 | 826.0395 | 167.237 | 993.2765 |  | 16.7174 | 0 | 0 | 0 | 5.1227 | 21.8401 | 172.1876 |  | 1165.4641 | 0 | 0 | 0
2050 | 1.6924 | 1.0174 | 0.11359 | 826.0395 | 170.1444 | 996.1839 |  | 17.0016 | 0 | 0 | 0 | 5.2118 | 22.2133 | 175.13 |  | 1171.3139 | 0 | 0 | 0
|  | Present Worth | 11.7874 | 9736.8813 | 1415.5145 | 11152.3959 |  | 144.1118 | 0 | 0 | 0 | 43.3594 | 187.4713 | 1478.0235 | 0 | 12630.4193 |  |  |  | CF | $/kW-yr
|  | Levelized |  | 826.0395 | 120.0868 | 946.1263 |  | 12.2259 | 0 | 0 | 0 | 3.6784 | 15.9043 | 125.3898 | 0 | 1071.5161 |  |  |  | 0 | 946.1263
[20 empty] | 90 | 1071.5161
[11 empty] | Total Fixed Costs ($/kW) |  | 946.1263
[11 empty] | Total Variable Costs ($/MWh) |  | 15.9043
CF
[11 empty] | 1 |  | 10816.4323
[11 empty] | 2 |  | 5416.1683
[11 empty] | 3 |  | 3616.0803
[11 empty] | 4 |  | 2716.0363
[11 empty] | 5 |  | 2176.0099
[11 empty] | 6 |  | 1815.9923
[11 empty] | 7 |  | 1558.8369
[11 empty] | 8 |  | 1365.9703
[11 empty] | 9 |  | 1215.963
[11 empty] | 10 |  | 1095.9571
[11 empty] | 11 |  | 997.7705
[11 empty] | 12 |  | 915.9483
[11 empty] | 13 |  | 846.7142
[11 empty] | 14 |  | 787.3706
[11 empty] | 15 |  | 735.9395
[11 empty] | 16 |  | 690.9373
[11 empty] | 17 |  | 651.2295
[11 empty] | 18 |  | 615.9337
[11 empty] | 19 |  | 584.3532
[11 empty] | 20 |  | 555.9307
[11 empty] | 21 |  | 530.2152
[11 empty] | 22 |  | 506.8374
[11 empty] | 23 |  | 485.4925
[11 empty] | 24 |  | 465.9263
[11 empty] | 25 |  | 447.9255
[11 empty] | 26 |  | 431.3093
[11 empty] | 27 |  | 415.9239
[11 empty] | 28 |  | 401.6375
[11 empty] | 29 |  | 388.3363
[11 empty] | 30 |  | 375.9219
[11 empty] | 35 |  | 324.4909
[11 empty] | 40 |  | 285.9175
[11 empty] | 45 |  | 255.9161
[11 empty] | 50 |  | 231.9149
[11 empty] | 55 |  | 212.2776
[11 empty] | 60 |  | 195.9131
[11 empty] | 65 |  | 182.0663
[11 empty] | 70 |  | 170.1976
[11 empty] | 75 |  | 159.9114
[11 empty] | 80 |  | 150.9109
[11 empty] | 85 |  | 142.9694
[11 empty] | 90 |  | 135.9102
[11 empty] | 95 |  | 129.5941
[11 empty] | 100 |  | 123.9096

## EIA_Battery
BATTERY ENERGY STORAGE SYSTEM, 50 MW / 200 MWH | [19 empty] | CALCULATION OF CONSTRUCTION EXPENDITURES
Input Parameters | [19 empty] | Summer Capacity: | 50 | MW
(A) | Year of Cost Estimates |  |  | 2021 |  | (E) | New Capacity Cost ($/kW) |  |  |  | 1470.9987 |  | (I) | Efficiency (%) |  |  |  | 0.87 |  | Overnight Cost: | 70.2914 | $M
(B) | First Year of Analysis |  |  | 2021 |  | (F) | Fixed O&M ($/kW-Yr) |  |  |  | 25.2825 |  | (J) | SO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | Overnight Cost: | 1405.829 | $/kW (Summer, Excludes AFDC)
(C) | Discount Rate (%) |  |  | 7.52 |  | (G) | Variable O&M ($/MWh) |  |  |  | 0 |  | (K) | NOx Emission Rate (lb./MBtu) |  |  |  | 0 |  | Base Year | 2021
(D) | Carrying Charge Rate (%) |  |  | 11.1764 |  | (H) | Capacity Factor (%) |  |  |  | 25 |  | (L) | CO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | AFDC Rate: | 6.3653 | %
[20 empty] | In-service Date: | 2021
[20 empty] | Average Infl Rate: | 1.8729
[22 empty] | Percent | Direct | Direct
|  |  |  | Fixed Costs |  |  |  | Variable Costs | [7 empty] | Total | [5 empty] | of Total | Expen. | Expen.
| Off Peak | O&M | Present |  | Fixed |  |  | Fuel | SO2 | NOx | CO2 | Variable |  |  |  | Annual |  |  |  | Year | Deflator | Expen. | 2,021$ | As Spent | AFDC | Total Expen. | Energy Prices
| Power Price | Escalation | Value | Generation | O&M | Total |  | Cost | Cost | Cost | Cost | O&M | Total | Total |  | Costs | Allowance Costs - $/Ton | [5 empty] | ($M) | ($M) | ($M) | ($M) | Region: | PJM
Year | ($/MWh) | Factor | Factor | ($/kW) | ($/kW) | ($/kW) |  | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW) |  | ($/kW) | SO2 | NOx | CO2 | 2015 | 0.89464 | 0% | 0 | 0 | 0 | 0 | Year | PJM | SPP
2021 | 20.2833 | 1.0175 | 0.93006 | 167.2868 | 25.7256 | 193.0124 |  | 23.3142 | 0 | 0 | 0 | 0 | 23.3142 | 51.058 |  | 244.0704 | 0 | 0 | 0 | 2016 | 0.9114 | 0% | 0 | 0 | 0 | 0 | 2021 | 20.2833 | 16.855
2022 | 20.4517 | 1.0168 | 0.86501 | 167.2868 | 26.1567 | 193.4435 |  | 23.5077 | 0 | 0 | 0 | 0 | 23.5077 | 51.4818 |  | 244.9252 | 0 | 0 | 0 | 2017 | 0.92847 | 0% | 0 | 0 | 0 | 0 | 2022 | 20.4517 | 16.9442
2023 | 21.6175 | 1.0143 | 0.80451 | 167.2868 | 26.5307 | 193.8175 |  | 24.8477 | 0 | 0 | 0 | 0 | 24.8477 | 54.4165 |  | 248.2339 | 0 | 0 | 0 | 2018 | 0.94585 | 0% | 0 | 0 | 0 | 0 | 2023 | 21.6175 | 18.3533
2024 | 22.4067 | 1.0181 | 0.74824 | 167.2868 | 27.0118 | 194.2986 |  | 25.7548 | 0 | 0 | 0 | 0 | 25.7548 | 56.403 |  | 250.7016 | 0 | 0 | 0 | 2019 | 0.96357 | 75% | 52.7186 | 50.798 | 1.6167 | 52.4148 | 2024 | 22.4067 | 19.0817
2025 | 23.8408 | 1.0199 | 0.69591 | 167.2868 | 27.5483 | 194.835 |  | 27.4033 | 0 | 0 | 0 | 0 | 27.4033 | 60.0131 |  | 254.8482 | 0 | 0 | 0 | 2020 | 0.98162 | 25% | 17.5729 | 17.2498 | 3.8854 | 21.1352 | 2025 | 23.8408 | 20.0792
2026 | 24.9975 | 1.0198 | 0.64724 | 167.2868 | 28.0935 | 195.3803 |  | 28.7328 | 0 | 0 | 0 | 0 | 28.7328 | 62.9247 |  | 258.305 | 0 | 0 | 0 | Total Plant: |  | 100% | 70.2914 | 68.0478 | 5.5021 | 73.5499 | 2026 | 24.9975 | 20.8858
2027 | 26.0575 | 1.0204 | 0.60197 | 167.2868 | 28.6653 | 195.952 |  | 29.9511 | 0 | 0 | 0 | 0 | 29.9511 | 65.593 |  | 261.5451 | 0 | 0 | 0 | [5 empty] | summer $/kw | 1470.9987 | 2027 | 26.0575 | 21.9692
2028 | 26.56 | 1.0212 | 0.55987 | 167.2868 | 29.272 | 196.5588 |  | 30.5287 | 0 | 0 | 0 | 0 | 30.5287 | 66.8579 |  | 263.4167 | 0 | 0 | 0 | [7 empty] | 2028 | 26.56 | 22.77
2029 | 26.6142 | 1.0217 | 0.52071 | 167.2868 | 29.9069 | 197.1936 |  | 30.591 | 0 | 0 | 0 | 0 | 30.591 | 66.9943 |  | 264.1879 | 0 | 0 | 0 | [7 empty] | 2029 | 26.6142 | 22.8408
2030 | 26.3658 | 1.0216 | 0.48429 | 167.2868 | 30.5527 | 197.8395 |  | 30.3056 | 0 | 0 | 0 | 0 | 30.3056 | 66.3692 |  | 264.2086 | 0 | 0 | 0 | [7 empty] | 2030 | 26.3658 | 22.3192
2031 | 26.0208 | 1.0206 | 0.45042 | 167.2868 | 31.1829 | 198.4696 |  | 29.909 | 0 | 0 | 0 | 0 | 29.909 | 65.5007 |  | 263.9703 | 0 | 0 | 0 | [7 empty] | 2031 | 26.0208 | 21.8558
2032 | 26.3458 | 1.0201 | 0.41892 | 167.2868 | 31.8081 | 199.0949 |  | 30.2826 | 0 | 0 | 0 | 0 | 30.2826 | 66.3188 |  | 265.4137 | 0 | 0 | 0 | [7 empty] | 2032 | 26.3458 | 21.9617
2033 | 27.3467 | 1.0189 | 0.38962 | 167.2868 | 32.4107 | 199.6975 |  | 31.433 | 0 | 0 | 0 | 0 | 31.433 | 68.8382 |  | 268.5356 | 0 | 0 | 0 | [7 empty] | 2033 | 27.3467 | 22.7675
2034 | 28.4383 | 1.0184 | 0.36237 | 167.2868 | 33.0072 | 200.294 |  | 32.6877 | 0 | 0 | 0 | 0 | 32.6877 | 71.5861 |  | 271.8802 | 0 | 0 | 0 | [7 empty] | 2034 | 28.4383 | 24.2658
2035 | 29.5867 | 1.0176 | 0.33702 | 167.2868 | 33.5879 | 200.8746 |  | 34.0077 | 0 | 0 | 0 | 0 | 34.0077 | 74.4768 |  | 275.3514 | 0 | 0 | 0 | [7 empty] | 2035 | 29.5867 | 24.695
2036 | 29.9675 | 1.0173 | 0.31345 | 167.2868 | 34.1687 | 201.4555 |  | 34.4454 | 0 | 0 | 0 | 0 | 34.4454 | 75.4354 |  | 276.8909 | 0 | 0 | 0 | [7 empty] | 2036 | 29.9675 | 25.175
2037 | 31.53 | 1.0173 | 0.29153 | 167.2868 | 34.7588 | 202.0455 |  | 36.2414 | 0 | 0 | 0 | 0 | 36.2414 | 79.3686 |  | 281.4141 | 0 | 0 | 0 | [7 empty] | 2037 | 31.53 | 26.5983
2038 | 33.3583 | 1.0172 | 0.27114 | 167.2868 | 35.3558 | 202.6426 |  | 38.3429 | 0 | 0 | 0 | 0 | 38.3429 | 83.971 |  | 286.6136 | 0 | 0 | 0 | [7 empty] | 2038 | 33.3583 | 27.885
2039 | 34.1575 | 1.0175 | 0.25218 | 167.2868 | 35.9759 | 203.2626 |  | 39.2615 | 0 | 0 | 0 | 0 | 39.2615 | 85.9827 |  | 289.2453 | 0 | 0 | 0 | [7 empty] | 2039 | 34.1575 | 28.5108
2040 | 35.4858 | 1.0185 | 0.23454 | 167.2868 | 36.6417 | 203.9284 |  | 40.7883 | 0 | 0 | 0 | 0 | 40.7883 | 89.3264 |  | 293.2548 | 0 | 0 | 0 | [7 empty] | 2040 | 35.4858 | 29.7117
|  | Present Worth | 10.179 | 1702.8127 | 300.8506 | 2003.6632 |  | 297.6106 | 0 | 0 | 0 | 0 | 297.6106 | 651.7673 | 0 | 2655.4306 |  |  |  | CF | $/kW-yr
|  | Levelized |  | 167.2868 | 29.556 | 196.8428 |  | 29.2377 | 0 | 0 | 0 | 0 | 29.2377 | 64.0306 | 0 | 260.8733 |  |  |  | 0 | 196.8428
[20 empty] | 25 | 260.8733
258.9213
[11 empty] | Total Fixed Costs ($/kW) |  | 196.8428
| 25.4368 | [9 empty] | Total Variable Costs ($/MWh) |  | 29.2377
CF
[11 empty] | 1 |  | 2276.3012
[11 empty] | 2 |  | 1152.7694
[11 empty] | 3 |  | 778.2589
[11 empty] | 4 |  | 591.0036
[11 empty] | 5 |  | 478.6504
[11 empty] | 6 |  | 403.7483
[11 empty] | 7 |  | 350.2468
[11 empty] | 8 |  | 310.1206
[11 empty] | 9 |  | 278.9114
[11 empty] | 10 |  | 253.944
[11 empty] | 11 |  | 233.5162
[11 empty] | 12 |  | 216.493
[11 empty] | 13 |  | 202.0887
[11 empty] | 14 |  | 189.7422
[11 empty] | 15 |  | 179.0419
[11 empty] | 16 |  | 169.6792
[11 empty] | 17 |  | 161.4179
[11 empty] | 18 |  | 154.0746
[11 empty] | 19 |  | 147.5042
[11 empty] | 20 |  | 141.5909
[11 empty] | 21 |  | 136.2407
[11 empty] | 22 |  | 131.3769
[11 empty] | 23 |  | 126.9361
[11 empty] | 24 |  | 122.8653
[11 empty] | 25 |  | 119.1202
[11 empty] | 26 |  | 115.6632
[11 empty] | 27 |  | 112.4623
[11 empty] | 28 |  | 109.49
[11 empty] | 29 |  | 106.7226
[11 empty] | 30 |  | 104.1398
[11 empty] | 35 |  | 93.4395
[11 empty] | 40 |  | 85.4143
[11 empty] | 45 |  | 79.1724
[11 empty] | 50 |  | 74.179
[11 empty] | 55 |  | 70.0934
[11 empty] | 60 |  | 66.6888
[11 empty] | 65 |  | 63.8079
[11 empty] | 70 |  | 61.3386
[11 empty] | 75 |  | 59.1985
[11 empty] | 80 |  | 57.326
[11 empty] | 85 |  | 55.6737
[11 empty] | 90 |  | 54.2051
[11 empty] | 95 |  | 52.891
[11 empty] | 100 |  | 51.7083

## EIA_Solar+Battery
SOLAR PHOTOVOLTAIC WITH BATTERY ENERGY STORAGE SYSTEM, 150 MWx200 MWh | [19 empty] | CALCULATION OF CONSTRUCTION EXPENDITURES
Input Parameters | [19 empty] | Summer Capacity: | 150 | MW
(A) | Year of Cost Estimates |  |  | 2021 |  | (E) | New Capacity Cost ($/kW) |  |  |  | 2003.289 |  | (I) | Efficiency (%) |  |  |  | 0.87 |  | Overnight Cost: | 287.1806 | $M | 287.1806
(B) | First Year of Analysis |  |  | 2021 |  | (F) | Fixed O&M ($/kW-Yr) |  |  |  | 32.7959 |  | (J) | SO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | Overnight Cost: | 1914.5372 | $/kW (Summer, Excludes AFDC)
(C) | Discount Rate (%) |  |  | 7.52 |  | (G) | Variable O&M ($/MWh) |  |  |  | 0 |  | (K) | NOx Emission Rate (lb./MBtu) |  |  |  | 0 |  | Base Year | 2021
(D) | Carrying Charge Rate (%) |  |  | 11.1764 |  | (H) | Capacity Factor (%) |  |  |  | 25 |  | (L) | CO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | AFDC Rate: | 6.3653 | %
[20 empty] | In-service Date: | 2021
[20 empty] | Average Infl Rate: | 1.8729
[22 empty] | Percent | Direct | Direct
|  |  |  | Fixed Costs |  |  |  | Variable Costs | [7 empty] | Total | [5 empty] | of Total | Expen. | Expen.
| Off Peak | O&M | Present |  | Fixed |  |  | Fuel | SO2 | NOx | CO2 | Variable |  |  |  | Annual |  |  |  | Year | Deflator | Expen. | 2,021$ | As Spent | AFDC | Total Expen. | Energy Prices
| Power Price | Escalation | Value | Generation | O&M | Total |  | Cost | Cost | Cost | Cost | O&M | Total | Total |  | Costs | Allowance Costs - $/Ton | [5 empty] | ($M) | ($M) | ($M) | ($M) | Region: | PJM
Year | ($/MWh) | Factor | Factor | ($/kW) | ($/kW) | ($/kW) |  | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW) |  | ($/kW) | SO2 | NOx | CO2 | 2015 | 0.89464 | 0% | 0 | 0 | 0 | 0 | Year | PJM | SPP
2021 | 20.2833 | 1.0175 | 0.93006 | [16 empty] | 2016 | 0.9114 | 0% | 0 | 0 | 0 | 0 | 2021 | 20.2833 | 16.855
2022 | 20.4517 | 1.0168 | 0.86501 | [16 empty] | 2017 | 0.92847 | 0% | 0 | 0 | 0 | 0 | 2022 | 20.4517 | 16.9442
2023 | 21.6175 | 1.0143 | 0.80451 | [16 empty] | 2018 | 0.94585 | 0% | 0 | 0 | 0 | 0 | 2023 | 21.6175 | 18.3533
2024 | 22.4067 | 1.0181 | 0.74824 | [16 empty] | 2019 | 0.96357 | 75% | 215.3854 | 207.5388 | 6.6053 | 214.1441 | 2024 | 22.4067 | 19.0817
2025 | 23.8408 | 1.0199 | 0.69591 | [16 empty] | 2020 | 0.98162 | 25% | 71.7951 | 70.4752 | 15.874 | 86.3492 | 2025 | 23.8408 | 20.0792
2026 | 24.9975 | 1.0198 | 0.64724 | [16 empty] | Total Plant: |  | 100% | 287.1806 | 278.0141 | 22.4793 | 300.4934 | 2026 | 24.9975 | 20.8858
2027 | 26.0575 | 1.0204 | 0.60197 | [21 empty] | summer $/kw | 2003.289 | 2027 | 26.0575 | 21.9692
2028 | 26.56 | 1.0212 | 0.55987 | [23 empty] | 2028 | 26.56 | 22.77
2029 | 26.6142 | 1.0217 | 0.52071 | [23 empty] | 2029 | 26.6142 | 22.8408
2030 | 26.3658 | 1.0216 | 0.48429 | [23 empty] | 2030 | 26.3658 | 22.3192
2031 | 26.0208 | 1.0206 | 0.45042 | [23 empty] | 2031 | 26.0208 | 21.8558
2032 | 26.3458 | 1.0201 | 0.41892 | [23 empty] | 2032 | 26.3458 | 21.9617
2033 | 27.3467 | 1.0189 | 0.38962 | [23 empty] | 2033 | 27.3467 | 22.7675
2034 | 28.4383 | 1.0184 | 0.36237 | [23 empty] | 2034 | 28.4383 | 24.2658
2035 | 29.5867 | 1.0176 | 0.33702 | [23 empty] | 2035 | 29.5867 | 24.695
2036 | 29.9675 | 1.0173 | 0.31345 | [23 empty] | 2036 | 29.9675 | 25.175
2037 | 31.53 | 1.0173 | 0.29153 | [23 empty] | 2037 | 31.53 | 26.5983
2038 | 33.3583 | 1.0172 | 0.27114 | [23 empty] | 2038 | 33.3583 | 27.885
2039 | 34.1575 | 1.0175 | 0.25218 | [23 empty] | 2039 | 34.1575 | 28.5108
2040 | 35.4858 | 1.0185 | 0.23454 | [23 empty] | 2040 | 35.4858 | 29.7117
|  | Present Worth | 10.179 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CF | $/kW-yr
|  | Levelized |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0
[20 empty] | 25 | 0
258.9213
[11 empty] | Total Fixed Costs ($/kW) |  | 0
| 25.4368 | [9 empty] | Total Variable Costs ($/MWh) |  | 0
CF
[11 empty] | 1 |  | 0
[11 empty] | 2 |  | 0
[11 empty] | 3 |  | 0
[11 empty] | 4 |  | 0
[11 empty] | 5 |  | 0
[11 empty] | 6 |  | 0
[11 empty] | 7 |  | 0
[11 empty] | 8 |  | 0
[11 empty] | 9 |  | 0
[11 empty] | 10 |  | 0
[11 empty] | 11 |  | 0
[11 empty] | 12 |  | 0
[11 empty] | 13 |  | 0
[11 empty] | 14 |  | 0
[11 empty] | 15 |  | 0
[11 empty] | 16 |  | 0
[11 empty] | 17 |  | 0
[11 empty] | 18 |  | 0
[11 empty] | 19 |  | 0
[11 empty] | 20 |  | 0
[11 empty] | 21 |  | 0
[11 empty] | 22 |  | 0
[11 empty] | 23 |  | 0
[11 empty] | 24 |  | 0
[11 empty] | 25 |  | 0
[11 empty] | 26 |  | 0
[11 empty] | 27 |  | 0
[11 empty] | 28 |  | 0
[11 empty] | 29 |  | 0
[11 empty] | 30 |  | 0
[11 empty] | 35 |  | 0
[11 empty] | 40 |  | 0
[11 empty] | 45 |  | 0
[11 empty] | 50 |  | 0
[11 empty] | 55 |  | 0
[11 empty] | 60 |  | 0
[11 empty] | 65 |  | 0
[11 empty] | 70 |  | 0
[11 empty] | 75 |  | 0
[11 empty] | 80 |  | 0
[11 empty] | 85 |  | 0
[11 empty] | 90 |  | 0
[11 empty] | 95 |  | 0
[11 empty] | 100 |  | 0

## EIA_Solar
SOLAR PHOTOVOLTAIC, 150 MWAC | [19 empty] | CALCULATION OF CONSTRUCTION EXPENDITURES
Input Parameters | [19 empty] | Summer Capacity: | 150 | MW
(A) | Year of Cost Estimates |  |  | 2021 |  | (E) | New Capacity Cost ($/kW) |  |  |  | 1417.0465 |  | (I) | Efficiency (%) |  |  |  | 1 |  | Overnight Cost: | 199.4055 | $M
(B) | First Year of Analysis |  |  | 2021 |  | (F) | Fixed O&M ($/kW-Yr) |  |  |  | 15.25 |  | (J) | SO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | Overnight Cost: | 1329.3698 | $/kW (Summer, Excludes AFDC)
(C) | Discount Rate (%) |  |  | 7.52 |  | (G) | Variable O&M ($/MWh) |  |  |  | 0 |  | (K) | NOx Emission Rate (lb./MBtu) |  |  |  | 0 |  | Base Year | 2021
(D) | Carrying Charge Rate (%) |  |  | 11.1764 |  | (H) | Capacity Factor (%) |  |  |  | 25 |  | (L) | CO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | AFDC Rate: | 6.3653 | %
[20 empty] | In-service Date: | 2022
[20 empty] | Average Infl Rate: | 1.8729
[22 empty] | Percent | Direct | Direct
|  |  |  | Fixed Costs |  |  |  | Variable Costs | [7 empty] | Total | [5 empty] | of Total | Expen. | Expen.
| Off Peak | O&M | Present |  | Fixed |  |  | Fuel | SO2 | NOx | CO2 | Variable |  |  |  | Annual |  |  |  | Year | Deflator | Expen. | 2,022$ | As Spent | AFDC | Total Expen. | Energy Prices
| Power Price | Escalation | Value | Generation | O&M | Total |  | Cost | Cost | Cost | Cost | O&M | Total | Total |  | Costs | Allowance Costs - $/Ton | [5 empty] | ($M) | ($M) | ($M) | ($M) | Region: | PJM
Year | ($/MWh) | Factor | Factor | ($/kW) | ($/kW) | ($/kW) |  | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW) |  | ($/kW) | SO2 | NOx | CO2 | 2016 | 0.89464 | 0% | 0 | 0 | 0 | 0 | Year | PJM | SPP
2021 | 20.2833 | 1.0175 | 0.93006 | [16 empty] | 2017 | 0.9114 | 0% | 0 | 0 | 0 | 0 | 2021 | 20.2833 | 16.855
2022 | 20.4517 | 1.0168 | 0.86501 | [16 empty] | 2018 | 0.92847 | 0% | 0 | 0 | 0 | 0 | 2022 | 20.4517 | 16.9442
2023 | 21.6175 | 1.0143 | 0.80451 | [16 empty] | 2019 | 0.94585 | 0% | 0 | 0 | 0 | 0 | 2023 | 21.6175 | 18.3533
2024 | 22.4067 | 1.0181 | 0.74824 | [16 empty] | 2020 | 0.96357 | 75% | 152.355 | 146.8047 | 4.6723 | 151.477 | 2024 | 22.4067 | 19.0817
2025 | 23.8408 | 1.0199 | 0.69591 | [16 empty] | 2021 | 0.98162 | 25% | 50.785 | 49.8514 | 11.2286 | 61.08 | 2025 | 23.8408 | 20.0792
2026 | 24.9975 | 1.0198 | 0.64724 | [16 empty] | Total Plant: |  | 100% | 203.14 | 196.656 | 15.9009 | 212.557 | 2026 | 24.9975 | 20.8858
2027 | 26.0575 | 1.0204 | 0.60197 | [21 empty] | summer $/kw | 1417.0465 | 2027 | 26.0575 | 21.9692
2028 | 26.56 | 1.0212 | 0.55987 | [23 empty] | 2028 | 26.56 | 22.77
2029 | 26.6142 | 1.0217 | 0.52071 | [23 empty] | 2029 | 26.6142 | 22.8408
2030 | 26.3658 | 1.0216 | 0.48429 | [23 empty] | 2030 | 26.3658 | 22.3192
2031 | 26.0208 | 1.0206 | 0.45042 | [23 empty] | 2031 | 26.0208 | 21.8558
2032 | 26.3458 | 1.0201 | 0.41892 | [23 empty] | 2032 | 26.3458 | 21.9617
2033 | 27.3467 | 1.0189 | 0.38962 | [23 empty] | 2033 | 27.3467 | 22.7675
2034 | 28.4383 | 1.0184 | 0.36237 | [23 empty] | 2034 | 28.4383 | 24.2658
2035 | 29.5867 | 1.0176 | 0.33702 | [23 empty] | 2035 | 29.5867 | 24.695
2036 | 29.9675 | 1.0173 | 0.31345 | [23 empty] | 2036 | 29.9675 | 25.175
2037 | 31.53 | 1.0173 | 0.29153 | [23 empty] | 2037 | 31.53 | 26.5983
2038 | 33.3583 | 1.0172 | 0.27114 | [23 empty] | 2038 | 33.3583 | 27.885
2039 | 34.1575 | 1.0175 | 0.25218 | [23 empty] | 2039 | 34.1575 | 28.5108
2040 | 35.4858 | 1.0185 | 0.23454 | [23 empty] | 2040 | 35.4858 | 29.7117
|  | Present Worth | 10.179 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CF | $/kW-yr
|  | Levelized |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0
[20 empty] | 25 | 0
258.9213
[11 empty] | Total Fixed Costs ($/kW) |  | 0
| 25.4368 | [9 empty] | Total Variable Costs ($/MWh) |  | 0
CF
[11 empty] | 1 |  | 0
[11 empty] | 2 |  | 0
[11 empty] | 3 |  | 0
[11 empty] | 4 |  | 0
[11 empty] | 5 |  | 0
[11 empty] | 6 |  | 0
[11 empty] | 7 |  | 0
[11 empty] | 8 |  | 0
[11 empty] | 9 |  | 0
[11 empty] | 10 |  | 0
[11 empty] | 11 |  | 0
[11 empty] | 12 |  | 0
[11 empty] | 13 |  | 0
[11 empty] | 14 |  | 0
[11 empty] | 15 |  | 0
[11 empty] | 16 |  | 0
[11 empty] | 17 |  | 0
[11 empty] | 18 |  | 0
[11 empty] | 19 |  | 0
[11 empty] | 20 |  | 0
[11 empty] | 21 |  | 0
[11 empty] | 22 |  | 0
[11 empty] | 23 |  | 0
[11 empty] | 24 |  | 0
[11 empty] | 25 |  | 0
[11 empty] | 26 |  | 0
[11 empty] | 27 |  | 0
[11 empty] | 28 |  | 0
[11 empty] | 29 |  | 0
[11 empty] | 30 |  | 0
[11 empty] | 35 |  | 0
[11 empty] | 40 |  | 0
[11 empty] | 45 |  | 0
[11 empty] | 50 |  | 0
[11 empty] | 55 |  | 0
[11 empty] | 60 |  | 0
[11 empty] | 65 |  | 0
[11 empty] | 70 |  | 0
[11 empty] | 75 |  | 0
[11 empty] | 80 |  | 0
[11 empty] | 85 |  | 0
[11 empty] | 90 |  | 0
[11 empty] | 95 |  | 0
[11 empty] | 100 |  | 0

## EIA_Wind
SOLAR PHOTOVOLTAIC, 150 MWAC | [19 empty] | CALCULATION OF CONSTRUCTION EXPENDITURES
Input Parameters | [19 empty] | Summer Capacity: | 200 | MW
(A) | Year of Cost Estimates |  |  | 2021 |  | (E) | New Capacity Cost ($/kW) |  |  |  | 1369.232 |  | (I) | Efficiency (%) |  |  |  | 1 |  | Overnight Cost: | 256.9028 | $M
(B) | First Year of Analysis |  |  | 2021 |  | (F) | Fixed O&M ($/kW-Yr) |  |  |  | 26.34 |  | (J) | SO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | Overnight Cost: | 1284.5138 | $/kW (Summer, Excludes AFDC)
(C) | Discount Rate (%) |  |  | 7.52 |  | (G) | Variable O&M ($/MWh) |  |  |  | 0 |  | (K) | NOx Emission Rate (lb./MBtu) |  |  |  | 0 |  | Base Year | 2021
(D) | Carrying Charge Rate (%) |  |  | 11.1764 |  | (H) | Capacity Factor (%) |  |  |  | 37 |  | (L) | CO2 Emission Rate (lb./MBtu) |  |  |  | 0 |  | AFDC Rate: | 6.3653 | %
[20 empty] | In-service Date: | 2022
[20 empty] | Average Infl Rate: | 1.8729
[22 empty] | Percent | Direct | Direct
|  |  |  | Fixed Costs |  |  |  | Variable Costs | [7 empty] | Total | [5 empty] | of Total | Expen. | Expen.
| Off Peak | O&M | Present |  | Fixed |  |  | Fuel | SO2 | NOx | CO2 | Variable |  |  |  | Annual |  |  |  | Year | Deflator | Expen. | 2,022$ | As Spent | AFDC | Total Expen. | Energy Prices
| Power Price | Escalation | Value | Generation | O&M | Total |  | Cost | Cost | Cost | Cost | O&M | Total | Total |  | Costs | Allowance Costs - $/Ton | [5 empty] | ($M) | ($M) | ($M) | ($M) | Region: | PJM
Year | ($/MWh) | Factor | Factor | ($/kW) | ($/kW) | ($/kW) |  | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/MWh) | ($/kW) |  | ($/kW) | SO2 | NOx | CO2 | 2016 | 0.89464 | 0% | 0 | 0 | 0 | 0 | Year | PJM | SPP
2021 | 20.2833 | 1.0175 | 0.93006 | [16 empty] | 2017 | 0.9114 | 0% | 0 | 0 | 0 | 0 | 2021 | 20.2833 | 16.855
2022 | 20.4517 | 1.0168 | 0.86501 | [16 empty] | 2018 | 0.92847 | 0% | 0 | 0 | 0 | 0 | 2022 | 20.4517 | 16.9442
2023 | 21.6175 | 1.0143 | 0.80451 | [16 empty] | 2019 | 0.94585 | 0% | 0 | 0 | 0 | 0 | 2023 | 21.6175 | 18.3533
2024 | 22.4067 | 1.0181 | 0.74824 | [16 empty] | 2020 | 0.96357 | 75% | 196.2856 | 189.1348 | 6.0195 | 195.1544 | 2024 | 22.4067 | 19.0817
2025 | 23.8408 | 1.0199 | 0.69591 | [16 empty] | 2021 | 0.98162 | 25% | 65.4285 | 64.2257 | 14.4663 | 78.692 | 2025 | 23.8408 | 20.0792
2026 | 24.9975 | 1.0198 | 0.64724 | [16 empty] | Total Plant: |  | 100% | 261.7142 | 253.3605 | 20.4859 | 273.8464 | 2026 | 24.9975 | 20.8858
2027 | 26.0575 | 1.0204 | 0.60197 | [21 empty] | summer $/kw | 1369.232 | 2027 | 26.0575 | 21.9692
2028 | 26.56 | 1.0212 | 0.55987 | [23 empty] | 2028 | 26.56 | 22.77
2029 | 26.6142 | 1.0217 | 0.52071 | [23 empty] | 2029 | 26.6142 | 22.8408
2030 | 26.3658 | 1.0216 | 0.48429 | [23 empty] | 2030 | 26.3658 | 22.3192
2031 | 26.0208 | 1.0206 | 0.45042 | [23 empty] | 2031 | 26.0208 | 21.8558
2032 | 26.3458 | 1.0201 | 0.41892 | [23 empty] | 2032 | 26.3458 | 21.9617
2033 | 27.3467 | 1.0189 | 0.38962 | [23 empty] | 2033 | 27.3467 | 22.7675
2034 | 28.4383 | 1.0184 | 0.36237 | [23 empty] | 2034 | 28.4383 | 24.2658
2035 | 29.5867 | 1.0176 | 0.33702 | [23 empty] | 2035 | 29.5867 | 24.695
2036 | 29.9675 | 1.0173 | 0.31345 | [23 empty] | 2036 | 29.9675 | 25.175
2037 | 31.53 | 1.0173 | 0.29153 | [23 empty] | 2037 | 31.53 | 26.5983
2038 | 33.3583 | 1.0172 | 0.27114 | [23 empty] | 2038 | 33.3583 | 27.885
2039 | 34.1575 | 1.0175 | 0.25218 | [23 empty] | 2039 | 34.1575 | 28.5108
2040 | 35.4858 | 1.0185 | 0.23454 | [23 empty] | 2040 | 35.4858 | 29.7117
|  | Present Worth | 10.179 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | CF | $/kW-yr
|  | Levelized |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0
[20 empty] | 37 | 0
258.9213
[11 empty] | Total Fixed Costs ($/kW) |  | 0
| 25.4368 | [9 empty] | Total Variable Costs ($/MWh) |  | 0
CF
[11 empty] | 1 |  | 0
[11 empty] | 2 |  | 0
[11 empty] | 3 |  | 0
[11 empty] | 4 |  | 0
[11 empty] | 5 |  | 0
[11 empty] | 6 |  | 0
[11 empty] | 7 |  | 0
[11 empty] | 8 |  | 0
[11 empty] | 9 |  | 0
[11 empty] | 10 |  | 0
[11 empty] | 11 |  | 0
[11 empty] | 12 |  | 0
[11 empty] | 13 |  | 0
[11 empty] | 14 |  | 0
[11 empty] | 15 |  | 0
[11 empty] | 16 |  | 0
[11 empty] | 17 |  | 0
[11 empty] | 18 |  | 0
[11 empty] | 19 |  | 0
[11 empty] | 20 |  | 0
[11 empty] | 21 |  | 0
[11 empty] | 22 |  | 0
[11 empty] | 23 |  | 0
[11 empty] | 24 |  | 0
[11 empty] | 25 |  | 0
[11 empty] | 26 |  | 0
[11 empty] | 27 |  | 0
[11 empty] | 28 |  | 0
[11 empty] | 29 |  | 0
[11 empty] | 30 |  | 0
[11 empty] | 35 |  | 0
[11 empty] | 40 |  | 0
[11 empty] | 45 |  | 0
[11 empty] | 50 |  | 0
[11 empty] | 55 |  | 0
[11 empty] | 60 |  | 0
[11 empty] | 65 |  | 0
[11 empty] | 70 |  | 0
[11 empty] | 75 |  | 0
[11 empty] | 80 |  | 0
[11 empty] | 85 |  | 0
[11 empty] | 90 |  | 0
[11 empty] | 95 |  | 0
[11 empty] | 100 |  | 0

## APCO Wind Cost
| Capacity Factor | 35%
LCOE
Tranche B - 35% CF
COD Year (December) | 1st Yr Rev | 35% CF | Wind Build Cost (EIA $/kW) (1) | PTC
2022 | 2023 | 40.7716 | 1296.2505 | 60%
2023 | 2024 | 45.7704 | 1305.8329 | 40%
2024 | 2025 | 41.4389 | 1317.415 | 60%
2025 | 2026 | 56.5197 | 1332.536 | 0%
2026 | 2027 | 57.2107 | 1346.0544 | 0%
2027 | 2028 | 57.8859 | 1359.1062 | 0%
2028 | 2029 | 58.5783 | 1371.9146 | 0%
2029 | 2030 | 59.2335 | 1384.1185 | 0%
2030 | 2031 | 59.9088 | 1396.9238 | 0%
2031 | 2032 | 60.5503 | 1408.7497 | 0%
2031 | 2032 | 61.208 | 1420.2748
2032 | 2033 | 61.8034 | 1430.3908
2033 | 2034 | 62.3504 | 1438.9053
2034 | 2035 | 62.8408 | 1445.662
2035 | 2036 | 63.3956 | 1453.5033
2036 | 2037 | 63.906 | 1460.4627
2037 | 2038 | 64.4087 | 1467.0457
2038 | 2039 | 64.9731 | 1475.54
2039 | 2040 | 65.6558 | 1486.8165
2040 | 2041 | 66.2801 | 1496.8597
2041 | 2042 | 66.9408 | 1507.9599
2042 | 2043 | 67.6109 | 1519.435
2043 | 2044 | 68.283 | 1530.0904
2044 | 2045 | 68.893 | 1539.4481
2045 | 2046 | 69.562 | 1550.5881
2046 | 2047 | 70.2124 | 1561.2597
2047 | 2048 | 70.8656 | 1571.1308
2048 | 2049 | 71.4785 | 1580.4308
2049 | 2050 | 72.4998 | 1602.3617
2050 | 2051 | 72.2028 | 1593.1526
2051 | 2052 | 72.7822 | 1601.4834
| Capital (2022) | 18.5116
| O&M (2022) | 22.26
| Total | 22.26
Source: |  | (1) AEP - Based on EIA 2020 AEO
Note on F4: dtso762: Per Yetzers 3/6/2020 IM Presentation DRAFT
Note on A5: com-ops says not possible to build this early

## APCO Solar Cost
|  | Tier 1 |  |  |  |  | Tier 2 |  |  | PPA T2
[5 empty] | Capacity Factor: | 24.6%
|  | ITC w/SH |  | Utility Cost PJM | ITC | ITC w/SH | ITC w/SH |  | Utility Cost PJM
COD | 1st Yr Rev | LCOE | EIA ($/kW) | ($/Watt) | (%) | (%) | LCOE | EIA ($/kW) | ($/Watt) | LCOE | Build Cost ($/kW)
2020 | 2021 |  |  |  | 22% | 30%
2021 | 2022 |  |  |  | 10% | 30% | 55.9657 | 1194.6773 | 1.1947 | 49.6986 | 1352.6695
2022 | 2023 |  |  |  |  | 30% | 54.3639 | 1148.9261 | 1.1489 | 48.3369 | 1257.2615
2023 | 2024 |  |  |  |  | 30% | 53.1627 | 1113.3372 | 1.1133 | 47.3256 | 1197.6818
2024 | 2025 |  |  |  | % | 10% | 58.9446 | 1107.5073 | 1.1075 | 56.1119 | 1152.627
2025 | 2026 |  |  |  |  | 0% | 61.7964 | 1102.3305 | 1.1023 | 60.4585 | 1121.9058
2026 | 2027 |  |  |  |  | 0% | 61.6363 | 1094.8385 | 1.0948 | 60.3074 | 1114.2192
2027 | 2028 |  |  |  |  | 0% | 61.704 | 1092.1791 | 1.0922 | 60.3821 | 1115.1867
2028 | 2029 |  |  |  |  | 0% | 61.8349 | 1090.5002 | 1.0905 | 60.5114 | 1111.624
2029 | 2030 |  |  |  |  | 0% | 61.9756 | 1089.3162 | 1.0893 | 60.6536 | 1110.2789
2030 | 2031 |  |  |  |  | 0% | 62.1736 | 1089.3675 | 1.0894 | 60.8513 | 1109.8515
2031 | 2032 | [5 empty] | 62.4936 | 1092.0077 | 1.092 | 61.1719 | 1108.6828
2032 | 2033 | [5 empty] | 62.8875 | 1095.8565 | 1.0959 | 61.5575 | 1107.8175
2033 | 2034 | [5 empty] | 63.2024 | 1098.2784 | 1.0983 | 61.8694 | 1108.5395
2034 | 2035 | [5 empty] | 63.4877 | 1100.044 | 1.1 | 62.1524 | 1109.2344
2035 | 2036 | [5 empty] | 63.6706 | 1099.5581 | 1.0996 | 62.3398 | 1109.3736
2036 | 2037 | [5 empty] | 63.9226 | 1100.138 | 1.1001 | 62.5874 | 1108.3231
2037 | 2038 | [5 empty] | 64.0979 | 1099.321 | 1.0993 | 62.7637 | 1106.6985
2038 | 2039 | [5 empty] | 64.2422 | 1097.8003 | 1.0978 | 62.9097 | 1105.967
2039 | 2040 | [5 empty] | 64.4424 | 1097.4158 | 1.0974 | 63.1141 | 1105.0023
2040 | 2041 | [5 empty] | 64.7195 | 1098.2879 | 1.0983 | 63.3866 | 1104.8809
2041 | 2042 | [5 empty] | 64.8949 | 1097.2569 | 1.0973 | 63.5632 | 1105.454
2042 | 2043 | [5 empty] | 65.1537 | 1098.0057 | 1.098 | 63.8209 | 1106.8789
2043 | 2044 | [5 empty] | 65.4228 | 1098.9501 | 1.099 | 64.0927 | 1107.6639
2044 | 2045 | [5 empty] | 65.6467 | 1098.5482 | 1.0985 | 64.3135 | 1108.4028
2045 | 2046 | [5 empty] | 65.87 | 1098.4243 | 1.0984 | 64.5369 | 1108.7553
2046 | 2047 | [5 empty] | 66.1101 | 1098.6664 | 1.0987 | 64.7766 | 1108.6509
2047 | 2048 | [5 empty] | 66.3497 | 1098.8806 | 1.0989 | 65.0197 | 1107.7973
2048 | 2049 | [5 empty] | 66.5615 | 1098.1283 | 1.0981 | 65.2287 | 1107.8365
2049 | 2050 | [5 empty] | 66.7641 | 1097.4896 | 1.0975 | 65.4321 | 1107.421
2050 | 2051 | [5 empty] | 67.3619 | 1105.3194 | 1.1053 | 66.0203 | 1106.0523
|  | Source: | (1)EIA Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies report (Feb 2020)
[6 empty] | Capital | 37.0857
[6 empty] | O&M | 18.88
[6 empty] | Total | 18.88

## Bar Chart $ per MWh
EIA COSTS

## Bar Chart Calculations
EIA LEVELIZED COSTS
Levelized Cost of Energy (2020$/MWh)
| Capital | O&M | Fuel + Variable O&M | Total
Natural Gas - CC H 2x2 (75% CF) | 18.8033 | 2.3212 | 31.4517 | 52.5761
Natural Gas - Frame GT (25% CF) | 37.6779 | 3.9954 | 50.76 | 92.4334
Natural Gas - Aero GT (25% CF) | 62.1685 | 9.3037 | 47.4512 | 118.9234
Natural Gas - RICE (25% CF) | 102.1276 | 20.0686 | 45.0629 | 167.259
Battery Storage - (25% CF) | 76.3867 | 13.4959 | 29.2377 | 119.1202
| Natural Gas - RICE (25% CF) | Battery Storage - (25% CF) | Natural Gas - Aero GT (25% CF) | Natural Gas - Frame GT (25% CF) | Natural Gas - CC H 2x2 (75% CF) | Intermittent Solar (25% CF) | Intermittent Wind (35% CF)
Capital | 102.1276 | 76.3867 | 62.1685 | 37.6779 | 18.8033 | 37.0857 | 18.5116
O&M | 20.0686 | 13.4959 | 9.3037 | 3.9954 | 2.3212 | 18.88 | 22.26
Fuel + Variable O&M | 45.0629 | 29.2377 | 47.4512 | 50.76 | 31.4517 | 0 | 0
| 167.259 | 119.1202 | 118.9234 | 92.4334 | 52.5761 | 55.9657 | 40.7716

## IRP Exhibit
AEP System
New Generation Technologies
Key Supply-Side Resource Option Assumptions (a)(b)(c)(d)
[7 empty] | Installed | Overnight | Full Load | Fuel | Variable | Fixed | Emission Rates |  |  | Capacity
|  |  |  | Capability (MW) (e) |  |  | Cost (d,f) | Cost (d,f) | Heat Rate | Cost | O&M | O&M | SO2 | NOx | CO2 | Factor | LCOE (g)
| Type |  |  | Std. ISO | Summer | Winter | ($/kW) | ($/kW) | (HHV,Btu/kWh) | ($/MBtu) | ($/MWh) | ($/kW-yr) | (Lb/mmBtu) | (Lb/mmBtu) | (Lb/mmBtu) | (%) | ($/MWh)
Base Load
EIA Case 12 | SMALL MODULAR REACTOR NUCLEAR POWER PLANT, 600 MW |  |  | 600 | 580 | 630 | 7000 | 6333.4514 | 10000 | 1.003 | 3 | 97.9381 | 0 | 0 | 0 | 90 | 135.9102
EIA Case 3 | ULTRA-SUPERCRITICAL COAL WITH 90% CO2 CAPTURE, 650 MW |  |  | 650 | 630 | 690 | 6700 | 5975 | 12500 | 2.0997 | 11.1936 | 60.6984 | 0.09 | 0.06 | 20.6 | 75 | 174.4788
EIA Case 9 | COMB TURBINE H CLASS, COMB-CYCLE SINGLE SHAFT W/90% CO2 CAPTURE, 430 MW |  |  | 370 | 370 | 390 | 2800 | 2488 | 7100 | 3.0424 | 5.9536 | 28.137 | 0 | 0.0075 | 12 | 75 | 94.0573
EIA Case 7 | COMB TURBINE H CLASS, 1100-MW COMBINED CYCLE |  |  | 1080 | 1060 | 1110 | 1100 | 931 | 6400 | 3.0424 | 1.9064 | 12.4374 | 0.001 | 0.0075 | 117 | 75 | 52.5761
EIA Case 8 | COMB TURBINE H CLASS, COMBINED-CYCLE SINGLE SHAFT, 430 MW |  |  | 420 | 410 | 430 | 1300 | 1075 | 7100 | 3.0424 | 0 | 28.137 | 0 | 0.0075 | 117 | 75 | 59.5231
Peaking
EIA Case 6 | COMB TURBINE F CLASS, 240-MW SIMPLE CYCLE |  |  | 230 | 240 | 250 | 700 | 680 | 9900 | 3.0424 | 4.5875 | 7.1362 | 0 | 0.03 | 117 | 25 | 92.4334
EIA Case 5 | COMB TURBINES AERODERIVATIVE, 100-MW SIMPLE CYCLE |  |  | 100 | 110 | 110 | 1200 | 1122 | 9100 | 3.0424 | 4.7914 | 16.6171 | 0 | 0.09 | 117 | 25 | 118.9234
EIA Case 4 | INTERNAL COMBUSTION ENGINES, 20 MW |  |  | 20 | 20 | 20 | 2000 | 1768 | 8300 | 3.0424 | 5.8007 | 35.8441 | 0 | 0.02 | 117 | 25 | 167.259
Intermittent
EIA Case 18 | BATTERY ENERGY STORAGE SYSTEM, 50 MW / 200 MWH |  |  | 50 | 50 | 50 | 1470 | 1379 |  |  | 0 | 25.2825 |  |  |  | 25 | 119.1202
EIA Case 20(j) | ONSHORE WIND, LARGE PLANT FOOTPRINT, 200 MW(j) |  |  | 200 | 200 | 200 | 1370 | 1260 |  |  | 0 | 26.34 |  |  |  | 35 | 45.7704
EIA Case 24(j) | SOLAR PHOTOVOLTAIC, 150 MWAC(j) |  |  | 150 | 150 | 150 | 1420 | 1304 |  |  | 0 | 15.25 |  |  |  | 25 | 55.9657
EIA Case 25(j) | SOLAR PHOTOVOLTAIC WITH BATTERY ENERGY STORAGE SYSTEM, 150 MWx200 MWh (j) |  |  | 150 | 150 | 150 | 2000 | 1878 |  |  | 0 | 32.7959 |  |  |  | 24 | 82.07
| Notes: | (a) | Costs and performance data informed by EIA report Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies (Feb 2020)
|  | (b) | Installed cost, capability and heat rate numbers have been rounded
|  | (c) | All costs in 2020 dollars, except as noted. Costs adjustments made based on EIA report Cost and Performance Characteristics of New Generating Technologies, Annual Energy Outlook 2020 (Region 11-PJMW)
|  | (d) | $/kW costs are based on summer capability
|  | (e) | All Capabilities adjusted by the Performance Adjustment Factors defined in the reference report (a)
|  | (f) | Total Plant Investment Cost w/AFUDC (AEP rate of 6.37%,site rating $/kW)
|  | (g) | Levelized cost of energy based on capacity factors shown in table
|  | (j) | System in service (COD) 2022

## Table 6
AEP System
New Generation Technologies
Key Supply-Side Resource Option Assumptions (a)(b)(c)(d)
[6 empty] | Installed | Full Load | Fuel | Variable | Fixed | Emission Rates |  |  | Capacity
|  |  | Capability (MW) (e) |  |  | Cost (d,f) | Heat Rate | Cost | O&M | O&M | SO2 | NOx | CO2 | Factor | LCOE (g)
Type |  |  | Std. ISO | Summer | Winter | ($/kW) | (HHV,Btu/kWh) | ($/MBtu) | ($/MWh) | ($/kW-yr) | (Lb/mmBtu) | (Lb/mmBtu) | (Lb/mmBtu) | (%) | ($/MWh)
Base Load
SMALL MODULAR REACTOR NUCLEAR POWER PLANT, 600 MW |  |  | 600 | 580 | 630 | 7000 | [7 empty] | 90 | 135.9102
ULTRA-SUPERCRITICAL COAL WITH 90% CO2 CAPTURE, 650 MW |  |  | 650 | 630 | 690 | 6700 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 75 | 174.4788
COMB TURBINE H CLASS, COMB-CYCLE SINGLE SHAFT W/90% CO2 CAPTURE, 430 MW |  |  | 370 | 370 | 390 | 2800 | [7 empty] | 75 | 94.0573
COMB TURBINE H CLASS, 1100-MW COMBINED CYCLE |  |  | 1080 | 1060 | 1110 | 1100 | [7 empty] | 75 | 52.5761
COMB TURBINE H CLASS, COMBINED-CYCLE SINGLE SHAFT, 430 MW |  |  | 420 | 410 | 430 | 1300 | [7 empty] | 75 | 59.5231
Peaking
COMB TURBINE F CLASS, 240-MW SIMPLE CYCLE |  |  | 230 | 240 | 250 | 700 | [7 empty] | 25 | 92.4334
COMB TURBINES AERODERIVATIVE, 100-MW SIMPLE CYCLE |  |  | 100 | 110 | 110 | 1200 | [7 empty] | 25 | 118.9234
INTERNAL COMBUSTION ENGINES, 20 MW |  |  | 20 | 20 | 20 | 2000 | [7 empty] | 25 | 167.259
Intermittent
BATTERY ENERGY STORAGE SYSTEM, 50 MW / 200 MWH |  |  | 50 | 50 | 50 | 1470.9987 | [7 empty] | 25 | 119.1202
SOLAR PHOTOVOLTAIC WITH BATTERY ENERGY STORAGE SYSTEM, 150 MWx200 MWh |  |  | 150 | 150 | 150 | 2003.289 | [7 empty] | 24 | 82.07
ONSHORE WIND, LARGE PLANT FOOTPRINT, 200 MW |  |  | 200 | 200 | 200 | 1370 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 35 | 45.7704
SOLAR PHOTOVOLTAIC, 150 MWAC |  |  | 150 | 150 | 150 | 1420 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 25 | 55.9657
Notes: | (a) | Costs and performance data informed by EIA report Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies (Feb 2020)
| (b) | Installed cost, capability and heat rate numbers have been rounded
| (c) | All costs in 2020 dollars, except as noted. Costs adjustments made based on EIA report Cost and Performance Characteristics of New Generating Technologies, Annual Energy Outlook 2020 - Region 11 (PJMW)
| (d) | $/kW costs are based on summer capability
| (e) | All Capabilities adjusted by the Performance Adjustment Factors defined in the reference report (a)
| (f) | Total Plant Investment Cost w/AFUDC (AEP rate of 6.37%,site rating $/kW)
| (g) | Levelized cost of energy based on capacity factors shown in table
| (g) | Includes Dual Fuel capability and SCR environmental installation
| (h) | Includes Black Start capability
| (i) | Denotes efficiency, (w/ power electronics)

## NEW Data Inputs from Summary
|  | OpCO: | APCO
|  | AFDC Rate (%): | 6.3653
|  | Discount Rate (%): | 7.52
|  | Carrying Charge Rate (%): | 11.1764
Used in Analysis
|  | Base Year | 2021
|  | In-service Date | 2021
|  | EIA Region | 11 (PJMW)
[6 empty] | Overnight | Capital Cost
|  |  | Capability (MW) |  |  | Cost | Calculated Values ($/kW) |  | Construction Expenditure Profile | [5 empty] | Life, Years
|  |  | Std. ISO | Summer | Winter | (Millions$) | Overnight | Installed | 1 | 2 | 3 | 4 | 5 | Total
| Base Load | Type
EIA Case 12 | SMALL MODULAR REACTOR NUCLEAR POWER PLANT, 600 MW | Small modular reactor | 600 | 582 | 633 | 3800.0708 | 6333.4514 | 7263.5928 | 20% | 25% | 25% | 30% | 0% | 100% | 40
Base Load (90% CO2 Capture New Unit)
EIA Case 3 | ULTRA-SUPERCRITICAL COAL WITH 90% CO2 CAPTURE, 650 MW | USC with 90% CCS | 650 | 630.5 | 685.75 | 3959.3098 | 5975 | 6707.9246 | 5% | 5% | 25% | 35% | 30% | 100% | 40
Intermediate
EIA Case 9 | COMBUSTION TURBINE H CLASS, COMBINED-CYCLE SINGLE SHAFT W/90% CO2 CAPTURE, 430 MW | CC with 90% CCS | 374.361 | 367.4418 | 387.0039 | 931.4102 | 2488 | 2827.6877 | 10% | 20% | 30% | 30% | 10% | 100% | 40
EIA Case 7 | COMBUSTION TURBINE H CLASS, 1100-MW COMBINED CYCLE | CC – multi shaft | 1075.419 | 1055.5424 | 1111.7381 | 1027.8893 | 931 | 1086.2998 | 10% | 35% | 35% | 20% | 0% | 100% | 40
EIA Case 8 | COMBUSTION TURBINE H CLASS, COMBINED-CYCLE SINGLE SHAFT, 430 MW | CC – single shaft | 415.074 | 407.4023 | 429.0919 | 458.0923 | 1075 | 1254.3204 | 10% | 35% | 35% | 20% | 0% | 100% | 25
Peaking
EIA Case 6 | COMBUSTION TURBINE F CLASS, 240-MW SIMPLE CYCLE | CT – industrial frame | 232.767 | 238.2021 | 245.5692 | 161.5225 | 680 | 725.5737 | 10% | 35% | 35% | 20% | 0% | 100% | 40
EIA Case 5 | COMBUSTION TURBINES AERODERIVATIVE, 100-MW SIMPLE CYCLE | CT – aeroderivative | 104.895 | 107.3443 | 110.6642 | 120.102 | 1122 | 1197.1966 | 10% | 35% | 35% | 20% | 0% | 100% | 40
EIA Case 4 | INTERNAL COMBUSTION ENGINES, 20 MW | Internal combustion engine | 21.4 | 20.758 | 22.577 | 38.5713 | 1768 | 1966.6987 | 20% | 50% | 30% | 0% | 0% | 100% | 30
Intermittent
EIA Case 18 | BATTERY ENERGY STORAGE SYSTEM, 50 MW / 200 MWH | Battery storage | 50 | 50 | 50 | 70.2914 | 1379 | 1470.9987 | 100% | 0% | 0% | 0% | 0% | 100% | 10
EIA Case 20 | ONSHORE WIND, LARGE PLANT FOOTPRINT, 200 MW | Wind | 200 | 200 | 200 | 256.9028 | 1260 | 1369.232 | 65% | 35% | 0% | 0% | 0% | 100% | 25
EIA Case 24 | SOLAR PHOTOVOLTAIC, 150 MWAC | Solar PV - tracking | 150 | 150 | 150 | 199.4055 | 1304 | 1417.0465 | 75% | 25% | 0% | 0% | 0% | 100% | 30
EIA Case 25 | SOLAR PHOTOVOLTAIC WITH BATTERY ENERGY STORAGE SYSTEM, 150 MWx200 MWh | Solar + Storage | 150 | 150 | 150 | 287.1806 | 1878 | 2003.289 | 75% | 25% | 0% | 0% | 0% | 100% | 30

## Key Assump
AEP SYSTEM
New Generation Technologies
Key Supply-Side Resource Option Assumptions (a)(b)(c)
[6 empty] | Installed | Full Load | Full Load | Variable | Fixed | Emission Rates
|  |  | Capability (MW) |  |  | Cost (e) | Heat Rate w/o DB | Heat Rate w/DB | O&M | O&M | SO2 | NOx | CO2
| Spec | Type | Std. ISO | Summer | Winter | ($/kW) | (HHV,Btu/kWh) | (HHV,Btu/kWh) | ($/MWh) | ($/kW-yr) | (Lb/mmBtu) | (Lb/mmBtu) | (Lb/mmBtu)
Base Load
EIA Case 12 | SMALL MODULAR REACTOR NUCLEAR POWER PLANT, 600 MW | Small modular reactor | 600 | 582 | 633 | 7045.6851 | 10046 | 10046 | 3 | 97.9381 | 0 | 0 | 0
EIA Case 3 | ULTRA-SUPERCRITICAL COAL WITH 90% CO2 CAPTURE, 650 MW | USC with 90% CCS | 650 | 630.5 | 685.75 | 6707.9246 | 12507 | 12507 | 11.1936 | 60.6984 | 0.09 | 0.06 | 20.6
EIA Case 9 | COMB TURBINE H CLASS, COMB-CYCLE SINGLE SHAFT W/90% CO2 CAPTURE, 430 MW | CC with 90% CCS | 374.361 | 367.4418 | 387.0039 | 2827.6877 | 7116.876 | 7116.876 | 5.9536 | 28.137 | 0 | 0.0075 | 12
EIA Case 7 | COMB TURBINE H CLASS, 1100-MW COMBINED CYCLE | CC – multi shaft | 1075.419 | 1055.5424 | 1111.7381 | 1086.2998 | 6363.63 | 6363.63 | 1.9064 | 12.4374 | 0.001 | 0.0075 | 117
EIA Case 8 | COMB TURBINE H CLASS, COMBINED-CYCLE SINGLE SHAFT, 430 MW | CC – single shaft | 415.074 | 407.4023 | 429.0919 | 1254.3204 | 7116.876 | 7116.876 | 0 | 28.137 | 0 | 0.0075 | 117
Peaking (h)
EIA Case 6 | COMB TURBINE F CLASS, 240-MW SIMPLE CYCLE | CT – industrial frame | 232.767 | 238.2021 | 245.5692 | 725.5737 | 9865.38 | 9865.38 | 4.5875 | 7.1362 | 0 | 0.03 | 117 | 0.35
EIA Case 5 | COMB TURBINES AERODERIVATIVE, 100-MW SIMPLE CYCLE | CT – aeroderivative | 104.895 | 107.3443 | 110.6642 | 1197.1966 | 9087.504 | 9087.504 | 4.7914 | 16.6171 | 0 | 0.09 | 117
EIA Case 4 | INTERNAL COMBUSTION ENGINES, 20 MW | Internal combustion engine | 21.4 | 20.758 | 22.577 | 1966.6987 | 8295 | 8295 | 5.8007 | 35.8441 | 0 | 0.02 | 117
Intermittent
EIA Case 18 | BATTERY ENERGY STORAGE SYSTEM, 50 MW / 200 MWH | Battery storage | 50 | 50 | 50 | 1470.9987 |  |  | 0 | 25.2825
EIA Case 20 | ONSHORE WIND, LARGE PLANT FOOTPRINT, 200 MW | Wind | 200 | 200 | 200 | 1369.232 |  |  | 0 | 26.34
EIA Case 24 | SOLAR PHOTOVOLTAIC, 150 MWAC | Solar PV - tracking | 150 | 150 | 150 | 1417.0465 |  |  | 0 | 15.25
EIA Case 25 | SOLAR PHOTOVOLTAIC WITH BATTERY ENERGY STORAGE SYSTEM, 150 MWx200 MWh | Solar + Storage | 150 | 150 | 150 | 2003.289 |  |  | 0 | 32.7959

## Table 1_jan31
Table 1. Updated estimates of power plant capital and operating costs
Plant Characteristics
|  | Nominal Capacity (MW) | Heat Rate(Btu/kWh) | Overnight Capital Cost ($/kW) | Fixed O&M ($/kW-yr) | Variable O&M ($/MWh) | NEMS Input | Type of Revision
S&L Case | Coal
1 | Ultra-Supercritical coal (USC) | 650 | 8638 | 3676 | 40.58 | 4.5 | Y | Updated
2 | USC with 30% carbon capture ad sequestration (CCS) | 650 | 9751 | 4558 | 54.3 | 7.08 | Y | Updated
3 | USC with 90% CCS | 650 | 12507 | 5876 | 59.54 | 10.98 | Y | Updated
Natural Gas
8 | Combined-cycle—single shaft | 418 | 6431 | 1084 | 14.1 | 2.55 | Y | Updated
7 | Combined-cycle—multi shaft | 1083 | 6370 | 958 | 12.2 | 1.87 | Y | Updated
9 | Combined-cycle with 90% CCS | 377 | 7124 | 2481 | 27.6 | 5.84 | N | New
5 | Combustion turbine—aeroderivative | 105 | 9124 | 1175 | 16.3 | 4.7 | Y | Updated
6 | Combustion turbine—industrial frame | 237 | 9905 | 713 | 7 | 4.5 | Y | Updated
10 | Fuel cells | 10 | 6469 | 6700 | 30.78 | 0.59 | Y | New
4 | Internal combustion engine | 21 | 8295 | 1810 | 35.16 | 5.69 | Y | Updated
Uranium
11 | Advanced nuclear | 2156 | 10608 | 6041 | 121.64 | 2.37 | Y | Updated
12 | Small modular reactor | 600 | 10046 | 6191 | 95 | 3 | N | New
Hydroelectric
17 | Conventional hydropower | 100 | N/A | 5316 | 29.86 | 0 | Y | New
Wind
21 | Wind (Coastal) | 50 | N/A | 1677 | 35.14 | 0 | N | New
20 | Wind (Great Plains) | 200 | N/A | 1265 | 26.34 | 0 | Y | Updated
22 | Wind offshore | 400 | N/A | 4375 | 110 | 0 | Y | New
Solar
| Solar thermal | 115 | N/A | 7221 | 85.4 | 0 | Y | New
24 | Solar photovoltaic—tracking | 150 | N/A | 1313 | 15.25 | 0 | Y | Updated
25 | Solar photovoltaic—tracking + battery storage | 150 | N/A | 1755 | 31.27 | 0 | N | New
Biomass
13 | Biomass | 50 | 13300 | 4097 | 125.72 | 4.83 | Y | Updated
Geothermal
15 | Geothermal | 50 | N/A | 2521 | 128.544 | 1.16 | Y | New
Municipal Solid Waste
16 | Municipal solid waste—landfill gas | 35.6 | 8513 | 1563 | 20.1 | 6.2 | Y | New
Battery Storage
19 | Battery storage (50 MW/100 MWh) | 50 | N/A | 845 | 12.9 | 0 | N | New
18 | Battery storage (50 MW/200 MWh) | 50 | N/A | 1389 | 24.8 | 0 | Y | New

## Table 3_jan31
Table 3. Total overnight capital costs of new electricity generating technologies by region
2019 $ per kilowatt
Base
Technology | BASE | 1 (TRE) | 2 (FRCC) | 3 (MISW) | 4 (MISC) | 5 (MISE) | 6 (MISS) | 7 (ISNE) | 8 (NYCW) | 9 (NYUP) | 10 (PJME) | 11 (PJMW) | 12 (PJMC) | 13 (PJMD) | 14 (SRCA) | 15 (SRSE) | 16 (SRCE) | 17 (SPPS) | 18 (SPPC) | 19 (SPPN) | 20 (SRSG) | 21 (CANO) | 22 (CASO) | 23 (NWPP) | 24 (RMRG) | 25 (BASN) | 1 (TRE)
Ultra-supercritical Coal (USC) | 3676 | 3402 | 3523 | 3892 | 3923 | 3973 | 3521 | 4242 | NA | 4146 | 4280 | 3651 | 4601 | 3940 | 3522 | 3615 | 3593 | 3546 | 3768 | 3586 | 3737 | NA | NA | 3959 | 3701 | 3861 | 2 (FRCC)
USC with 30% CCS | 4558 | 4362 | 4499 | 4906 | 4959 | 5004 | 4506 | 5338 | NA | 5231 | 5372 | 4651 | 5710 | 5000 | 4509 | 4610 | 4578 | 4522 | 4772 | 4564 | 4761 | NA | NA | 5004 | 4711 | 4888 | 3 (MISW)
USC with 90% CCS | 5876 | 5660 | 5826 | 6273 | 6395 | 6407 | 5860 | 6785 | NA | 6611 | 6796 | 5975 | 7236 | 6350 | 5871 | 5976 | 5951 | 5839 | 6136 | 5881 | 6117 | NA | NA | 6418 | 6027 | 6306 | 4 (MISC)
CC – single shaft | 1084 | 974 | 1011 | 1125 | 1119 | 1147 | 1003 | 1294 | 1717 | 1298 | 1296 | 1075 | 1299 | 1237 | 991 | 1003 | 1023 | 1001 | 1063 | 992 | 975 | 1451 | 1374 | 1135 | 919 | 994 | 5 (MISE)
CC – multi shaft | 958 | 848 | 886 | 1003 | 1004 | 1030 | 880 | 1131 | 1549 | 1112 | 1137 | 931 | 1192 | 1051 | 869 | 883 | 901 | 879 | 944 | 872 | 839 | 1278 | 1202 | 985 | 790 | 887 | 6 (MISS)
CC with 90% CCS | 2481 | 2409 | 2466 | 2614 | 2604 | 2644 | 2454 | 2728 | 3090 | 2666 | 2706 | 2488 | 2820 | 2592 | 2424 | 2425 | 2477 | 2427 | 2508 | 2390 | 2211 | 2802 | 2708 | 2558 | 2079 | 2335 | 7 (ISNE)
Internal combustion engine | 1810 | 1695 | 1744 | 1871 | 1924 | 1903 | 1756 | 1972 | 2472 | 1898 | 1973 | 1768 | 2150 | 1836 | 1765 | 1785 | 1785 | 1752 | 1847 | 1770 | 1787 | 2157 | 2098 | 1904 | 1764 | 1888 | 8 (NYCW)
CT – aeroderivative | 1175 | 1035 | 1087 | 1242 | 1227 | 1264 | 1078 | 1316 | 1685 | 1270 | 1309 | 1122 | 1438 | 1191 | 1072 | 1081 | 1109 | 1080 | 1156 | 1087 | 981 | 1406 | 1324 | 1212 | 950 | 1082 | 9 (NYUP)
CT – industrial frame | 713 | 626 | 658 | 754 | 746 | 769 | 653 | 801 | 1034 | 772 | 797 | 680 | 878 | 723 | 649 | 656 | 673 | 654 | 702 | 659 | 594 | 860 | 808 | 737 | 575 | 658 | 10 (PJME)
Fuel cells | 6700 | 7042 | 7191 | 7531 | 7793 | 7653 | 7272 | 7939 | 9346 | 7617 | 7871 | 7251 | 8392 | 7474 | 7325 | 7372 | 7368 | 7191 | 7492 | 7256 | 7357 | 8480 | 8305 | 7705 | 7216 | 7686 | 11 (PJMW)
Adv nuclear | 6041 | 5963 | 6120 | 6494 | 7008 | 6766 | 6290 | 7156 | NA | 6676 | 6992 | 6180 | 7688 | 6432 | 6371 | 6382 | 6438 | 6116 | 6468 | 6114 | 6342 | NA | NA | 6865 | 6143 | 6872 | 12 (PJMC)
Small modular reactor | 6191 | 6111.0632 | 6271.9616 | 6655.2481 | 7182.0109 | 6934.002 | 6446.1828 | 7333.6858 | NA | 6841.7673 | 7165.6136 | 6333.4514 | 7878.8955 | 6591.7087 | 6529.194 | 6540.4671 | 6597.8576 | 6267.8623 | 6628.6025 | 6265.8126 | 6499.4739 | NA | NA | 7035.4602 | 6295.5327 | 7042.634 | 13 (PJMD)
Dist. generation - base |  | 1384 | 1425 | 1536 | 1597 | 1581 | 1390 | 1778 | 2540 | 1799 | 1862 | 1596 | 1597 | 1358 | 1358 | 1418 | 1409 | 1460 | 1515 | 1521 | 1555 | 1933 | 1933 | 1569 | 1638 | 1569 | 14 (SRCA)
Dist. generation - peak |  | 1795 | 1864 | 1847 | 1905 | 1852 | 1818 | 1940 | 2631 | 1915 | 2055 | 1894 | 1899 | 1767 | 1767 | 1868 | 1786 | 1850 | 1888 | 1848 | 2157 | 2145 | 2145 | 1956 | 2246 | 1956 | 15 (SRSE)
Battery storage | 1389 | 1383 | 1385 | 1363 | 1431 | 1386 | 1415 | 1425 | 1420 | 1388 | 1392 | 1379 | 1397 | 1392 | 1428 | 1408 | 1419 | 1376 | 1385 | 1368 | 1400 | 1440 | 1441 | 1416 | 1371 | 1426 | 16 (SRCE)
Biomass | 4097 | 3808 | 3944 | 4292 | 4371 | 4385 | 3944 | 4873 | 6614 | 4888 | 4974 | 4182 | 4982 | 4766 | 3959 | 4033 | 4009 | 3962 | 4209 | 4045 | 4333 | 5616 | 5389 | 4480 | 4292 | 4292 | 17 (SPPS)
Geothermal | 2521 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | 2817 | 2794 | 2262 | 2734 | NA | 2680 | 18 (SPPC)
MSW - landfill gas | 1563 | 1467 | 1509 | 1613 | 1662 | 1642 | 1520 | 1702 | 2120 | 1637 | 1701 | 1528 | 1850 | 1587 | 1529 | 1545 | 1545 | 1515 | 1595 | 1529 | 1545 | 1859 | 1809 | 1645 | 1525 | 1632 | 19 (SPPN)
Conventional hydropower | 5316 | NA | 4905 | 1609 | NA | NA | NA | 1808 | NA | 3699 | 3843 | 3530 | 3349 | 3399 | 1892 | 4105 | 1297 | NA | 1711 | 1971 | 3262 | 3323 | 4478 | 2752 | 3286 | 3591 | 20 (SRSG)
Wind | 1265 | 1231 | NA | 1260 | 1259 | 1509 | 1260 | 1670 | NA | 2037 | 1670 | 1260 | 1668 | 1739 | 1503 | 1703 | 1260 | 1260 | 1260 | 1260 | 1260 | 2782 | 2185 | 1670 | 1260 | 1260 | 21 (CANO)
Wind offshore | 4375 | 5319 | 5446 | 5446 | NA | 6521 | NA | 5446 | 5478 | 6643 | 5446 | 5446 | 7210 | 5672 | 4901 | NA | NA | NA | NA | NA | NA | 7126 | 5446 | 5446 | NA | NA | 22 (CASO)
Solar thermal | 7221 | 6937 | 7049 | 7172 | 7896 | 7491 | 7324 | 7953 | 9165 | 7446 | 7682 | 7062 | 8143 | 7304 | 7440 | 7341 | 7448 | 7007 | 7279 | 6936 | 7268 | 8614 | 8430 | 7736 | 6984 | 7751 | 23 (NWPP)
Solar PV - tracking | 1313 | 1289 | 1265 | 1318 | 1355 | 1341 | 1275 | 1354 | 1593 | 1341 | 1381 | 1304 | 1423 | 1301 | 1327 | 1284 | 1282 | 1263 | 1313 | 1272 | 1285 | 1443 | 1409 | 1317 | 1300 | 1312 | 24 (RMRG)
Solar + Storage | 1755 | 1787 | 1755 | 1723 | 1794 | 1843 | 1825 | 1736 | 1842 | 2161 | 1825 | 1878 | 1775 | 1934 | 1771 | 1806 | 1748 | 1746 | 1720 | 1787 | 1732 | 1750 | 1961 | 1915 | 1792 | 1770 | 25 (BASN)
Notes: Costs include contingency factors and regional cost and ambient conditions multipliers. Interest charges are excluded. The costs are shown before investment tax credits are applied.
NA: Not available; plant type cannot be built in the region due to lack of resources, sites or specific state legislation.
USC = ultra-supercritical, CCS = carbon capture and sequestration, CC = combined cycle, CT = combustion turbine, PV = photovoltaic, MSW = municipal solid waste
Electricity Market Module region map: http://www.eia.gov/forecasts/aeo/pdf/nerc_map.pdf
Source: U.S. Energy Information Administration, Office of Electricity, Coal, Nuclear and Renewables Analysis.
Solar + Storage |  | 1.828% | 0% | -1.828% | 2.209% | 5.027% | 3.96% | -1.066% | 4.95% | 23.15% | 3.96% | 7.007% | 1.142% | 10.21% | 0.9139% | 2.894% | -0.3808% | -0.5331% | -1.98% | 1.828% | -1.295% | -0.3046% | 11.73% | 9.139% | 2.133% | 0.8378%

## AEO2020_AppdxB
Appendix B. Combustion Turbine Capacity Adjustments
Cost & Performance Estimates for New Utility-Scale Electric Power Generating Technologies Project 13651.005
Performance Adjustment Factors
Capital Cost Study Cost and Performance Estimates for New Utility-Scale Electric Power Generating Technologies
| Prepared by Sargent & Lundy | [12 empty] | Prepared for U.S. Energy Information Administration
FINAL Contract No. 89303019CEI00022 Project No. 13651-005
| 55 East Monroe ¦ Chicago, IL 60603 ¦ sargentlundy.com | [8 empty] | HR NET values are LHV! (HHV = LLV*1.11)
Gas Turbine Based Capacity and Heat Rate Adjustments
| LOCATION |  | Adjustment Basis |  |  | Simple Cycle |  | Combined Cyle |  | 2 x LM6000PF+ |  | 1 x 7F.05 |  | 1 x 7HA.01 WCT |  | 1 x 7HA.01 ACC |  | 2 x 7HA.02 WCT |  | 2 x 7HA.02 ACC
NERC Reg | State | City | ASHRAE Station | Alt (ft) | Ave T (F) | MW Adj SC | HR Adj SC | MW Adj CC | HR Adj CC | MW Net | HR Net | MW Net | HR Net | MW Net | HR Net | MW Net | HR Net | MW Net | HR Net | MW Net | HR Net | NERC Reg
Base | ISO | ISO | - | 0 | 59 | 100% | 100% | 100% | 100% | 105.1 | 8220 | 232.6 | 8923 | 418.3 | 5793 | 406.9 | 5955 | 1083.3 | 5739 | 1026.5 | 6056
| Alabama | Huntsville | 723230 | 624 | 61.7 | 96.8% | 100.3% | 97.2% | 100.3% | 101.7 | 8242 | 225.1 | 8947 | 406.4 | 5809 | 395.3 | 5971 | 1052.5 | 5754 | 997.4 | 6072 | 16 (SRCE)
| Alaska | Anchorage | 997381 | 10 | 37.4 | 108.6% | 97.8% | 105.4% | 98.9% | 114.1 | 8042 | 252.6 | 8730 | 440.7 | 5731 | 428.7 | 5891 | 1141.4 | 5677 | 1081.6 | 5991
| Alaska | Fairbanks | 702610 | 432 | 28 | 110.7% | 96.9% | 106.1% | 98.5% | 116.3 | 7965 | 257.5 | 8646 | 443.9 | 5709 | 431.8 | 5868 | 1149.6 | 5655 | 1089.4 | 5967
20 (SRSG) | Arizona | Phoenix | 722780 | 1107 | 75.2 | 89.9% | 101.6% | 92.2% | 101% | 94.5 | 8353 | 209.1 | 9068 | 385.8 | 5853 | 375.3 | 6017 | 999.1 | 5798 | 946.8 | 6118 | 20 (SRSG)
6 (MISS) | Arkansas | Little Rock | 723400 | 563 | 61.6 | 97% | 100.3% | 97.4% | 100.2% | 101.9 | 8241 | 225.7 | 8946 | 407.4 | 5808 | 396.3 | 5970 | 1055 | 5753 | 999.8 | 6071 | 6 (MISS)
| California | Los Angeles | 722950 | 97 | 63.2 | 98% | 100.4% | 98.6% | 100.2% | 103 | 8254 | 227.9 | 8961 | 412.5 | 5807 | 401.3 | 5969 | 1068.3 | 5752 | 1012.3 | 6070
| California | Redding | 725920 | 497 | 62.8 | 96.8% | 100.4% | 97.3% | 100.3% | 101.7 | 8251 | 225.1 | 8957 | 407.1 | 5810 | 396 | 5973 | 1054.3 | 5755 | 999.1 | 6073
22 (CASO) | California | Bakersfield | 723840 | 489 | 65.7 | 95.7% | 100.7% | 96.6% | 100.4% | 100.5 | 8275 | 222.5 | 8983 | 404.2 | 5819 | 393.2 | 5981 | 1046.9 | 5764 | 992.1 | 6082 | 22 (CASO)
| California | Modesto | 724926 | 73 | 63 | 98.1% | 100.4% | 98.7% | 100.2% | 103.1 | 8253 | 228.3 | 8959 | 413 | 5806 | 401.8 | 5968 | 1069.7 | 5751 | 1013.7 | 6069
21 (CANO) | California | Sacramento | 724839 | 23 | 61.9 | 98.8% | 100.3% | 99.2% | 100.1% | 103.8 | 8244 | 229.7 | 8949 | 414.9 | 5802 | 403.6 | 5964 | 1074.6 | 5747 | 1018.3 | 6065 | 21 (CANO)
| California | San Francisco | 724940 | 8 | 58.1 | 100.3% | 99.9% | 100.2% | 100% | 105.4 | 8212 | 233.4 | 8915 | 419.1 | 5791 | 407.7 | 5953 | 1085.4 | 5736 | 1028.6 | 6053
| Colorado | Denver | 725650 | 5414 | 51 | 83.6% | 99.2% | 82.7% | 100.7% | 87.9 | 8154 | 194.6 | 8852 | 345.8 | 5833 | 336.4 | 5996 | 895.6 | 5778 | 848.7 | 6097 | 24 (RMRG)
| Connecticut | Hartford | 725087 | 19 | 52.3 | 102.6% | 99.3% | 101.6% | 99.7% | 107.8 | 8165 | 238.7 | 8863 | 425 | 5774 | 413.4 | 5936 | 1100.7 | 5720 | 1043 | 6036
| DC | Washington | 745940 | 282 | 56.4 | 100% | 99.7% | 99.7% | 99.9% | 105.1 | 8199 | 232.7 | 8900 | 416.8 | 5789 | 405.5 | 5951 | 1079.6 | 5735 | 1023 | 6051
7 (ISNE) | Delaware | Dover | 724088 | 28 | 56.1 | 101.1% | 99.7% | 100.6% | 99.9% | 106.2 | 8196 | 235.1 | 8897 | 420.9 | 5785 | 409.4 | 5947 | 1090.1 | 5731 | 1033 | 6047 | 7 (ISNE)
| Florida | Tallahassee | 722140 | 55 | 68.2 | 96.1% | 100.9% | 97.5% | 100.5% | 101 | 8295 | 223.6 | 9005 | 407.9 | 5821 | 396.8 | 5983 | 1056.3 | 5766 | 1001 | 6084
2 (FRCC) | Florida | Tampa | 722110 | 19 | 73.5 | 94.1% | 101.5% | 96.3% | 100.7% | 98.9 | 8339 | 219 | 9052 | 402.8 | 5836 | 391.9 | 5999 | 1043.3 | 5781 | 988.7 | 6100 | 2 (FRCC)
15 (SRSE) | Georgia | Atlanta | 722190 | 1027 | 63 | 94.9% | 100.4% | 95.4% | 100.4% | 99.7 | 8253 | 220.7 | 8959 | 399.2 | 5817 | 388.3 | 5980 | 1033.9 | 5762 | 979.8 | 6080 | 15 (SRSE)
| Hawaii | Honolulu | 911820 | 7 | 77.8 | 92.5% | 101.9% | 95.3% | 100.9% | 97.2 | 8374 | 215.1 | 9091 | 398.5 | 5848 | 387.7 | 6012 | 1032.1 | 5793 | 978.1 | 6113
| Idaho | Boise | 726810 | 2814 | 52.9 | 92.4% | 99.4% | 91.5% | 100.3% | 97 | 8170 | 214.8 | 8869 | 382.8 | 5808 | 372.4 | 5971 | 991.5 | 5753 | 939.6 | 6071
12 (PJMC) | Illinois | Chicago | 997338 | 663 | 50 | 101.2% | 99.1% | 99.9% | 99.7% | 106.3 | 8146 | 235.4 | 8843 | 417.8 | 5775 | 406.4 | 5937 | 1081.9 | 5720 | 1025.3 | 6037 | 12 (PJMC)
4 (MISC) | Indiana | Indianapolis | 724380 | 790 | 53.6 | 99.3% | 99.5% | 98.5% | 99.9% | 104.4 | 8175 | 231.1 | 8875 | 412.2 | 5787 | 401 | 5949 | 1067.5 | 5732 | 1011.6 | 6049
| Iowa | Davenport | 725349 | 753 | 49.7 | 101% | 99.1% | 99.6% | 99.7% | 106.1 | 8143 | 234.9 | 8840 | 416.7 | 5775 | 405.4 | 5937 | 1079.2 | 5721 | 1022.7 | 6037
| Iowa | Waterloo | 725480 | 686 | 47.9 | 101.9% | 98.9% | 100.3% | 99.6% | 107.1 | 8129 | 237.1 | 8824 | 419.6 | 5769 | 408.1 | 5931 | 1086.6 | 5715 | 1029.7 | 6030
| Kansas | Wichita | 724500 | 1321 | 57.6 | 95.9% | 99.9% | 95.7% | 100.2% | 100.8 | 8208 | 223.1 | 8911 | 400.3 | 5805 | 389.4 | 5967 | 1036.8 | 5750 | 982.5 | 6068
| Kentucky | Louisville | 724230 | 488 | 58.3 | 98.6% | 99.9% | 98.5% | 100.1% | 103.6 | 8214 | 229.3 | 8917 | 411.8 | 5797 | 400.6 | 5959 | 1066.6 | 5742 | 1010.8 | 6060 | 16 (SRCE)
| Louisiana | New Orleans | 722316 | 2 | 68.7 | 96.1% | 101% | 97.6% | 100.5% | 101 | 8300 | 223.6 | 9010 | 408.1 | 5822 | 397 | 5984 | 1056.9 | 5767 | 1001.6 | 6085
| Maine | Portland | 726060 | 45 | 47.1 | 104.6% | 98.8% | 102.8% | 99.4% | 109.9 | 8122 | 243.3 | 8817 | 430 | 5760 | 418.3 | 5921 | 1113.7 | 5705 | 1055.4 | 6020 | 7 (ISNE)
7 (ISNE) | Maryland | Baltimore | 724060 | 56 | 56 | 101% | 99.7% | 100.6% | 99.9% | 106.1 | 8195 | 234.9 | 8896 | 420.6 | 5785 | 409.1 | 5947 | 1089.3 | 5731 | 1032.2 | 6047 | 13 (PJMD)
| Massachusetts | Boston | 725090 | 12 | 52 | 102.8% | 99.3% | 101.7% | 99.7% | 108 | 8162 | 239 | 8861 | 425.4 | 5773 | 413.8 | 5935 | 1101.8 | 5719 | 1044.1 | 6035 | 7 (ISNE)
| Michigan | Detroit | 725375 | 626 | 51 | 100.9% | 99.2% | 99.8% | 99.7% | 106.1 | 8154 | 234.8 | 8852 | 417.3 | 5778 | 405.9 | 5939 | 1080.7 | 5723 | 1024.1 | 6039 | 5 (MISE)
5 (MISE) | Michigan | Grand Rapids | 726350 | 803 | 48.9 | 101.1% | 99% | 99.6% | 99.7% | 106.3 | 8137 | 235.2 | 8833 | 416.8 | 5773 | 405.4 | 5935 | 1079.4 | 5719 | 1022.9 | 6035 | 5 (MISE)
3 (MISW) | Minnesota | Saint Paul | 726584 | 700 | 46.6 | 102.4% | 98.8% | 100.6% | 99.5% | 107.6 | 8118 | 238.2 | 8812 | 420.7 | 5766 | 409.2 | 5927 | 1089.5 | 5711 | 1032.4 | 6027 | 3 (MISW)
| Mississippi | Jackson | 722350 | 330 | 65.1 | 96.4% | 100.6% | 97.3% | 100.4% | 101.3 | 8270 | 224.3 | 8977 | 407.1 | 5815 | 396.1 | 5978 | 1054.4 | 5760 | 999.2 | 6078
| Missouri | St. Louis | 724340 | 531 | 57.5 | 98.7% | 99.9% | 98.5% | 100% | 103.8 | 8208 | 229.7 | 8910 | 412 | 5795 | 400.8 | 5957 | 1067.1 | 5741 | 1011.2 | 6058 | 4 (MISC)
| Missouri | Kansas City | 724463 | 742 | 57 | 98.2% | 99.8% | 97.9% | 100% | 103.2 | 8203 | 228.4 | 8905 | 409.4 | 5796 | 398.3 | 5958 | 1060.4 | 5742 | 1004.9 | 6059
| Montana | Great Falls | 727750 | 3364 | 45.2 | 93.1% | 98.6% | 91.3% | 100% | 97.8 | 8106 | 216.6 | 8800 | 381.8 | 5792 | 371.4 | 5954 | 988.7 | 5737 | 936.9 | 6055
18 (SPPC) | Nebraska | Omaha | 725530 | 1332 | 51.6 | 98.2% | 99.3% | 97.1% | 99.9% | 103.2 | 8159 | 228.3 | 8857 | 406.1 | 5787 | 395.1 | 5949 | 1051.9 | 5733 | 996.8 | 6050 | 18 (SPPC)
25 (BASN) | Nevada | Las Vegas | 724846 | 2203 | 69.1 | 88.6% | 101% | 90% | 100.9% | 93.1 | 8303 | 206 | 9013 | 376.3 | 5848 | 366 | 6012 | 974.5 | 5793 | 923.5 | 6113 | 25 (BASN)
| New Hampshire | Concord | 726050 | 346 | 47 | 103.5% | 98.8% | 101.8% | 99.5% | 108.8 | 8121 | 240.8 | 8816 | 425.6 | 5763 | 414 | 5924 | 1102.3 | 5708 | 1044.5 | 6024 | 7 (ISNE)
10 (PJME) | New Jersey | Newark | 725020 | 7 | 55.8 | 101.3% | 99.7% | 100.8% | 99.8% | 106.4 | 8194 | 235.5 | 8894 | 421.5 | 5784 | 410 | 5946 | 1091.7 | 5730 | 1034.5 | 6046 | 10 (PJME)
| New Mexico | Albuquerque | 723650 | 5310 | 58.1 | 81.7% | 99.9% | 81.6% | 101% | 85.9 | 8212 | 190.1 | 8915 | 341.3 | 5852 | 332 | 6016 | 883.9 | 5797 | 837.6 | 6117
8 (NYCW) | New York | New York | 725053 | 130 | 55.3 | 101% | 99.6% | 100.5% | 99.8% | 106.2 | 8189 | 235 | 8890 | 420.2 | 5784 | 408.8 | 5946 | 1088.3 | 5730 | 1031.3 | 6046 | 8 (NYCW)
9 (NYUP) | New York | Syracuse | 725190 | 413 | 48.9 | 102.5% | 99% | 101% | 99.6% | 107.8 | 8137 | 238.5 | 8833 | 422.6 | 5769 | 411.1 | 5930 | 1094.6 | 5714 | 1037.3 | 6030 | 9 (NYUP)
| North Carolina | Asheville | 723150 | 2117 | 56.2 | 93.6% | 99.7% | 93.2% | 100.3% | 98.4 | 8197 | 217.8 | 8898 | 390 | 5810 | 379.4 | 5972 | 1010 | 5755 | 957.1 | 6073 | 14 (SRCA)
14 (SRCA) | North Carolina | Charlotte | 723140 | 728 | 61.3 | 96.6% | 100.2% | 96.9% | 100.3% | 101.5 | 8239 | 224.6 | 8944 | 405.3 | 5809 | 394.2 | 5971 | 1049.6 | 5754 | 994.6 | 6072 | 14 (SRCA)
19 (SPPN) | North Dakota | Bismarck | 727640 | 1651 | 43.3 | 100.1% | 98.4% | 97.9% | 99.5% | 105.2 | 8091 | 232.9 | 8783 | 409.6 | 5767 | 398.4 | 5928 | 1060.7 | 5712 | 1005.2 | 6028 | 19 (SPPN)
11 (PJMW) | Ohio | Cincinnati | 724297 | 490 | 55 | 99.9% | 99.6% | 99.3% | 99.9% | 104.9 | 8187 | 232.3 | 8887 | 415.2 | 5788 | 403.9 | 5949 | 1075.3 | 5733 | 1019 | 6050 | 11 (PJMW)
| Oklahoma | Oklahoma City | 723530 | 1285 | 61.2 | 94.7% | 100.2% | 95% | 100.4% | 99.5 | 8238 | 220.2 | 8943 | 397.3 | 5815 | 386.5 | 5977 | 1028.9 | 5760 | 975 | 6078 | 17 (SPPS)
17 (SPPS) | Oklahoma | Tulsa | 723560 | 650 | 61.3 | 96.8% | 100.2% | 97.2% | 100.2% | 101.8 | 8239 | 225.2 | 8944 | 406.4 | 5808 | 395.3 | 5970 | 1052.5 | 5753 | 997.4 | 6071 | 17 (SPPS)
23 (NWPP) | Oregon | Portland | 726980 | 19 | 54.6 | 101.7% | 99.6% | 101% | 99.8% | 106.9 | 8184 | 236.6 | 8884 | 422.6 | 5781 | 411.1 | 5943 | 1094.5 | 5726 | 1037.2 | 6043 | 23 (NWPP)
| Pennsylvania | Philadelphia | 724080 | 10 | 56.6 | 100.9% | 99.8% | 100.6% | 99.9% | 106.1 | 8200 | 234.8 | 8902 | 420.6 | 5787 | 409.2 | 5948 | 1089.4 | 5732 | 1032.3 | 6049 | 10 (PJME)
| Pennsylvania | Wilkes-Barre | 725130 | 930 | 50.3 | 100.1% | 99.1% | 98.8% | 99.8% | 105.2 | 8148 | 232.9 | 8845 | 413.5 | 5779 | 402.2 | 5941 | 1070.8 | 5724 | 1014.7 | 6041 | 10 (PJME)
| Puerto Rico | San Juan | 994043 | 16 | 80.3 | 91.4% | 102.1% | 94.6% | 101.1% | 96.1 | 8395 | 212.7 | 9113 | 395.8 | 5855 | 385 | 6019 | 1025 | 5800 | 971.3 | 6121
| Rhode Island | Providence | 997278 | 33 | 53 | 102.3% | 99.4% | 101.4% | 99.7% | 107.5 | 8171 | 237.9 | 8870 | 424.1 | 5776 | 412.5 | 5938 | 1098.3 | 5722 | 1040.7 | 6038 | 7 (ISNE)
| South Carolina | Charleston | 722080 | 40 | 66.5 | 96.9% | 100.8% | 98% | 100.4% | 101.8 | 8282 | 225.3 | 8990 | 409.9 | 5816 | 398.7 | 5978 | 1061.5 | 5761 | 1005.9 | 6079 | 14 (SRCA)
| South Carolina | Spartanburg | 723120 | 943 | 61.2 | 95.8% | 100.2% | 96.2% | 100.3% | 100.7 | 8238 | 223 | 8943 | 402.2 | 5811 | 391.3 | 5973 | 1041.8 | 5756 | 987.2 | 6074 | 14 (SRCA)
24 (RMRG) | South Dakota | Rapid City | 726620 | 3160 | 47.4 | 93.1% | 98.8% | 91.5% | 100% | 97.8 | 8125 | 216.5 | 8820 | 382.8 | 5796 | 372.4 | 5958 | 991.4 | 5742 | 939.5 | 6059 | 24 (RMRG)
16 (SRCE) | Tennessee | Knoxville | 723260 | 962 | 59.5 | 96.4% | 100.1% | 96.5% | 100.2% | 101.3 | 8224 | 224.3 | 8928 | 403.7 | 5806 | 392.7 | 5968 | 1045.5 | 5751 | 990.7 | 6069 | 16 (SRCE)
| Tennessee | Nashville | 723270 | 600 | 60.2 | 97.4% | 100.1% | 97.6% | 100.2% | 102.4 | 8230 | 226.6 | 8934 | 408.3 | 5804 | 397.2 | 5966 | 1057.3 | 5749 | 1002 | 6067 | 16 (SRCE)
1 (TRE) | Texas | Houston | 722436 | 32 | 70.6 | 95.3% | 101.2% | 97% | 100.6% | 100.1 | 8315 | 221.6 | 9027 | 405.7 | 5827 | 394.6 | 5990 | 1050.7 | 5772 | 995.7 | 6091 | 1 (TRE)
| Utah | Salt Lake City | 725720 | 4225 | 53.5 | 87.1% | 99.5% | 86.4% | 100.6% | 91.5 | 8175 | 202.6 | 8874 | 361.3 | 5826 | 351.5 | 5989 | 935.8 | 5771 | 886.8 | 6090 | 25 (BASN)
| Vermont | Burlington | 726170 | 330 | 46.6 | 103.7% | 98.8% | 101.9% | 99.4% | 109 | 8118 | 241.3 | 8812 | 426.3 | 5761 | 414.7 | 5922 | 1104 | 5707 | 1046.1 | 6022 | 7 (ISNE)
| Virginia | Alexandria | 724050 | 10 | 58.7 | 100.1% | 100% | 100% | 100% | 105.2 | 8217 | 232.8 | 8920 | 418.4 | 5793 | 407.1 | 5955 | 1083.7 | 5738 | 1027 | 6055 | 13 (PJMD)
| Virginia | Lynchburg | 724100 | 940 | 56.6 | 97.6% | 99.8% | 97.3% | 100.1% | 102.6 | 8200 | 227.1 | 8902 | 406.9 | 5797 | 395.9 | 5959 | 1053.9 | 5743 | 998.7 | 6060 | 13 (PJMD)
| Washington | Seattle | 994014 | 7 | 53.2 | 102.3% | 99.4% | 101.4% | 99.7% | 107.5 | 8172 | 238 | 8871 | 424.2 | 5777 | 412.7 | 5938 | 1098.7 | 5722 | 1041.2 | 6038 | 23 (NWPP)
| Washington | Spokane | 727850 | 2353 | 48.1 | 95.8% | 98.9% | 94.3% | 99.9% | 100.6 | 8130 | 222.8 | 8826 | 394.3 | 5789 | 383.6 | 5951 | 1021.1 | 5734 | 967.7 | 6051 | 23 (NWPP)
| West Virginia | Charleston | 724140 | 910 | 55.9 | 98% | 99.7% | 97.6% | 100% | 103 | 8194 | 228 | 8895 | 408.1 | 5795 | 397 | 5957 | 1056.9 | 5740 | 1001.6 | 6057 | 11 (PJMW)
| Wisconsin | Green Bay | 726450 | 687 | 45.5 | 102.9% | 98.7% | 100.9% | 99.5% | 108.1 | 8109 | 239.3 | 8803 | 422 | 5762 | 410.5 | 5923 | 1092.9 | 5708 | 1035.7 | 6023 | 3 (MISW)
| Wyoming | Cheyenne | 725640 | 6130 | 46.6 | 82.4% | 98.8% | 81% | 100.6% | 86.6 | 8118 | 191.8 | 8812 | 338.7 | 5828 | 329.5 | 5991 | 877.2 | 5773 | 831.3 | 6092

## 2021 Wind
Data feeds to other sheets. Some data not used for all technologies/fuels.
CJB updated 8-24-2020 | Vendor Name | Wind
| Model | CASE 20. ONSHORE WIND, LARGE PLANT FOOTPRINT, 200 MW
New Generation Technology Cost and Performance Estimates | Arrangement
Number of (generating) Units
Shaded cells are not currently used. | Nominal MW net, plant | 200
CO2 Control % (up to 99.99%)
APCo, I&M, AEG, Kentucky Power, PSO, SWEPCO, AEP Generation Resources (AGR), BPCo (Buckeye), General | Location by Operating Company
Specific Location, if available | Text
PJM or SPP Regional Transmission Area? If neither, use None | Text - PJM, SPP, or None
Plant Configuration | Units / Inputs
Technology | Text
Technology - Combustion turbine or recip engine? See also Fuel Type | Text, CT or RICE (or other)
If (gas) turbine, Simple or Combined Cycle? | Text, Simple Cycle, Combined Cycle, or None
Black Start Capability, total MW (must type in number even if Zero) | MW
Does Land need to be purchased? Typical responses: No = existing property; wind = Lease; solar = Yes | Text, Yes, No, or Lease
Is this a typical "build" project or asset purchase (build, own, transfer) upon completion? | Text, Build or Buy. For Energy Storage, use Build.
Fuel Type | Solar
Fuel Characteristic | Text
Fuel Availability | Text
Fuel Price Stability | Text
Fuel Cost, $/mmBtu | $/mmBtu
Heating Value, Btu/lb HHV | Btu/Lb HHV
Sulfur, % | %
Ash, % | %
Moisture, % | %
Volatile Matter, VM, % | %
Carbon, % | %
H2, % | %
O2, % | %
N2, % | %
Hg, lb/Tbtu | lb/Tbtu
Annual Fuel Usage, equivalent million tons/year | Million Tons/yr
Annual Heat Input (not valid for all technologies, but used in calculations), mmBtu | Million Btu (mmBtu)
Total Fuel Costs, $/MW-hr | $/MW-hr
Total Fuel Costs, $ million per year | $ Million
General Plant Description | Text
Capacity
Standard ISO MW @ 1,000 ft. Gross | MW gross | 200
Parasitic Load, % | %
Standard ISO MW @1,000 feet, WITHOUT the steam turbine | Nominal MWac net
Standard ISO MW @ 1,000 feet WITH steam turbine | MW
Steam Turbine (used in calcs) MW | MW
Actual DC to AC ratio (default = 1.00) | Number
DC capacity for solar; for all others = Standard ISO at 1,000 ft, MWac | Nominal MWdc net, plant
Standard ISO MW thermal @ 1,000 ft | Nominal MW thermal
Energy Storage Duration, hours | Hours
Energy Storage Capability, MW-hr, AC | MW-hr | 0
Spare Row
Minimum MW net, either calculation or from vendor (aka Turn Down Capability) | MW net
Minimum, Turndown, % (minimum load with 1 machine for combustion turbines) | %
Inlet Chilling Type for Combustion Turbines (See Notes page) | Text - None, Evaporative Cooler, or Chiller
Inlet Chilling Addition (check heat rate impact) MW | MW
Inlet Chilling Heat Rate Impact | Btu/kWh
Power Augmentation ? (See Notes page) | Text - None, Steam Injection, or Water Injection
Power Augmentation Addition (check heat rate impact) MW | MW
Power Augmentation Heat Rate Impact | Btu/kWh
Is Fuel Oil included? Yes or No (Not applicable to Fuel Oil Only units) | Text - Yes or No
Fuel Oil Capacity (check heat rate impact) MW | MW
Fuel Oil Heat Rate Impact | Btu/kWh
HRSG Capability, if Equipped, Unfired MW | MW
Duct Burners included ? Yes or No | Text - Yes or No
Duct Burners (included for all combined cycle HRSGs) MW | MW
Duct Burner Heat Rate Impact | Btu/kWh
Total Potential HRSG + Duct Firing Capability, MW | MW
Spare Row
Spare Row
Winter (30F) MW net without fuel oil + steam turbine | MW net
Winter (30F) MW net + fuel oil (if fuel oil included) + steam turbine | MW net
Summer (90F) MW net by itself + steam turbine | MW net
Summer (90F) MW net + inlet cooling + duct firing + steam turbine | MW net
Summer (90F) MW net without inlet cooling + duct firing + steam turbine | MW net
Summer (90F) MW net + inlet cooling without duct firing + steam turbine | MW net
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. NO Steam Turbine Limit. | MW
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. May be steam turbine limited. USE THIS. | MW
Spare Row
Potential Steam Generation (CHP only, 150 psig, saturated, at capacity factor) lb/year. Not applicable if other technology. (B&McD July 2017; see Notes) | lb/year
Potential Hot Water Generation (CHP only, 150 psig, saturated, at capacity factor) mmBtu/year. Not applicable if other technology. (B&McD July 2017; see Notes) | mmBtu/year
Heat Rate (Higher Heating Value)
Full Load, HHV, net, with degradation (not applicable for all technologies, however, used in calculations) Btu/kW-hr | Btu/kWh
Full Load, HHV, net, with degradation and duct burner heat rate impact, Btu/kW-hr (if not combined cycle with duct burners, use the number above) | Btu/kWh
Full Load, HHV, net, with degradation and fuel oil (Winter) | Btu/kWh
Full Load, HHV, net, with degradation and inlet cooling, NO duct burners (Summer) | Btu/kWh
Full Load, HHV, net, with degradation, inlet cooling, and duct burner heat rate impact (Summer) | Btu/kWh
Full Load, HHV, net, with degradation and duct burners, NO inlet cooling heat rate impact | Btu/kWh
Full Load, HHV, net, with degradation, inlet cooling, power augmentation, HRSG, and duct firing. Does not include Fuel Oil Impact. | Btu/kWh
75% Load, Btu/kW-hr | Btu/kWh
50% Load, Btu/kW-hr | Btu/kWh
25% Load, Btu/kW-hr | Btu/kWh
Average Annual (without duct burners), Btu/kW-hr | Btu/kWh
Estimated efficiency, HHV, full load, degraded, % | %
Energy Storage Roundtrip efficiency (82.67% is average) | %
Capacity Factor, %, for all but energy storage, includes hybrid | %, ac
Capacity Factor, %, for energy storage only (not hybrid) | %
Annual Energy AC Generation from Net Rating, MW-hr (to grid) | MW-hr
Spare row for notes, other calculations
Capital Cost, $/kW based on nominal MW | 2020
Asset Purchase Price (not typical build) | $/kW
Steam generator | $/kW
Gasifier | $/kW
Air Separator | $/kW
Steam, Combustion, or Wind Turbines | $/kW
Black Start / Coping Power Combustion Turbines | $/kW
Solar Modules/Panels | $/kW
Inverters | $/kW
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $/kW (if hybrid, based on generation size)
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $/kW (if hybrid, based on generation size)
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $/kW (if hybrid, based on generation size)
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $/kW
Duct Burners | $/kW
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $/kW
Plant Water Treatment (Demin/RO system, tanks, piping) | $/kW
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $/kW
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $/kW
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $/kW
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $/kW
Misc. Pumps and Piping not otherwise included | $/kW
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $/kW
Balance of Plant, BOP (adds from below) | $/kW
IT, Telecomm, SCADA, Metering, Telemetry, Software | $/kW
Security (including cameras), Roads, and Fencing | $/kW
Control Room | $/kW
Other BOP, not otherwise classified | $/kW
Gas Compression | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Freight/Shipping, Importation Duty, Fees, and Taxes | $/kW
Construction Labor | $/kW
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | $/kW
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | $/kW
Owner's Project and Construction Mgmt | $/kW
Developer Margin and Overheads | $/kW
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $/kW
First of a kind and/or Plug Number | $/kW
SO2 Polishing (used with CO2 capture) | $/kW
(AEP) O&M Mobilization Fee for a Buy | $/kW
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | $/kW
Project Contingency for a Build | $/kW
Project Contingency for a Buy | $/kW
EPC Contractor's Fee | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Fee Subtotal for Build (not used in calculation) | $/kW
Fee Subtotal for Buy (not used in calculation) | $/kW
Total Plant Cost (Overnight EPC) for Build Option | $/kW
Asset Purchase = Buy | $/kW
Owner's Costs | $/kW
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | $/kW
Owner's Costs for a BUY project (excluding Land) | $/kW
Inventory Capital | $/kW
Development and Legal Fees | $/kW
Regulatory Support Fees | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUILD | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUY | $/kW
Interconnection Studies (e.g., Tom Fecho) | $/kW
Enviro and building permits for BUILD | $/kW
Enviro and building permits for BUY | $/kW
AEP-paid sales tax, based on location | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Initial catalyst and chemicals | $/kW
Land Costs (for Buying Land; if Lease = O&M cost) | $/kW
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $/kW
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $/kW
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $/kW
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $/kW
Total Interconnects and Infrastructure (adds from below) | $/kW
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $/kW
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $/kW
Water Supply (Intake) and Wastewater Treatment | $/kW
Site Infrastructure (includes railroad and barge access) | $/kW
Landfill development | $/kW
Initial fuel Inventory (30 days for solid or liquid fuels) | $/kW
Total Plant Cost + Owner's Cost + Interconnects for Build | $/kW
Transmission Upgrade - not currently used | $/kW
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $/kW
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $/kW | 1265
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $/kW
Capital Cost | 2020
Asset Purchase Price (not typical build) | $ million
Steam generator | $ million
Gasifier | $ million
Air Separator | $ million
Steam, Combustion, or Wind Turbines | $ million
Black Start / Coping Power Combustion Turbines | $ million
Solar Modules/Panels | $ million
Inverters | $ million
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $ million (if hybrid, storage only portion)
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $ million (if hybrid, storage only portion)
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $ million (if hybrid, storage only portion)
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $ million
Duct Burners | $ million
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $ million
Plant Water Treatment (Demin/RO system, tanks, piping) | $ million
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $ million
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $ million
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $ million
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $ million
Misc. Pumps and Piping not otherwise included | $ million
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $ million
Balance of Plant, BOP (adds from below) | $ million
IT, Telecomm, SCADA, Metering, Telemetry, Software | $ million
Security (including cameras), Roads, and Fencing | $ million
Control Room | $ million
Other BOP, not otherwise classified | $ million
Gas Compression | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Freight/Shipping, Importation Duty, Fees, and Taxes | 3%
Construction Labor | $ million
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | 12%
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | 5%
Owner's Project and Construction Mgmt | 5%
Developer Margin and Overheads | $ million
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $ million
First of a kind and/or Plug Number | $ million
SO2 Polishing (used with CO2 capture) | $ million
(AEP) O&M Mobilization Fee for a Buy | $ million
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | 1.25%
Project Contingency for a Build | 10%
Project Contingency for a Buy | $ million
EPC Contractor's Fee | 8%
Spare row
Spare row
Spare row
Fee Subtotal for Build (not used in calculation) | $ million
Fee Subtotal for Buy (not used in calculation) | $ million
Total Plant Cost (Overnight EPC) for Build Option | $ million
Asset Purchase = Buy | $ million
Owner's Costs
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | 5%
Owner's Costs for a BUY project (excluding Land) | $ million
Inventory Capital | 1%
Development and Legal Fees | 1.25%
Regulatory Support Fees | 1%
Civil Work (surveys, geotech, grading, site installation) for BUILD | $ million
Civil Work (surveys, geotech, grading, site installation) for BUY | $ million
Interconnection Studies (e.g., Tom Fecho) | $ million
Enviro and building permits for BUILD | $ million
Enviro and building permits for BUY | $ million
AEP-paid sales tax, based on location | $ million
Spare row - check formulas
Spare row - check formulas
Spare row - check formulas
Initial catalyst and chemicals | $ million
Land Costs (for Buying Land; if Lease = O&M cost) | $ million
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $ million
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $ million
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $ million
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $ million
Total Interconnects and Infrastructure (adds from below) | $ million
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $ million
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $ million
Water Supply (Intake) and Wastewater Treatment | $ million
Site Infrastructure (includes railroad and barge access) | $ million
Landfill development | $ million
Initial fuel Inventory (30 days for solid or liquid fuels) | $ million
Total Plant Cost + Owner's Cost + Interconnects for Build | $ million
Total Plant Cost + Owner's Cost + Interconnects for Buy | $ million
Transmission Upgrade - not currently used | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUY (Included in EPC) | $ million
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $ million | 256.9028
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $ million
Financial
AFUDC | $ million
Total Project Duration | months
AFUDC %, by operating company or equivalent, avg. annual rate | %
Financial Risk | Text (Low, Average, High)
Investment Life, years | Years (choose from 2, 3, 4, 5, 10, 15, 20, 25, 30, 33, 40, or 50 years) | 25
Economic Cost of Capital (AEP carrying cost, used in annual capital cost), % | %
Overhead / Allocation Rate for AEP operating company, % | %
Overhead / Allocation Costs, $ million for Build | $ million
Overhead / Allocation Costs, $ million for Buy | $ million
Annual Capital Cost, $ million for Build | $ million
Annual Capital Cost, $ million for Buy | $ million
Capital Cost $/kW - year for Build | $/kW-year
Capital Cost $/kW - year for Buy | $/kW-year
Nuclear Decommissioning Accrual, $ million/year | $ million / year
Nuclear Decommissioning Accrual, $ million | $ million
General Decommissioning Cost, $ | $ million
Assumes no salvage value
Remediation and/or Demolition Costs for Brownfield Site | $ million
Total Capital Costs, $/MW-hr | $/MW-hr
Operations & Maintenance (O&M)
Duty Cycle | Text
Capacity Factor | %
Annual Energy AC Generation from Net Rating, MW-hr (to grid) | MW-hr
Generating Facility Staff | Number (if part-time, use decimal)
Fixed O&M Costs
Fixed O&M as an input from data sources for comparison, $/kW-year | $/kW-year
Fixed O&M as an EPRI/resource planning calculation, $/kW-year | $/kW (if hybrid, based on generation size) | 26.34
Fixed O&M (adds from below), $ million | $ million
Plant Staff Payroll | $ million
General & Administrative Overheads (20% of Payroll) | $ million
Routine Maintenance, typically 1% of major equipment costs or input | $ million
Non-Natural Gas units Major Maintenance = 50% of the Variable O&M Major Maint. (per Resource Planning) | $ million
Utility (aux power and water) costs | $ million
Environmental and safety (monitoring, waste removal, etc.) | $ million
Buildings/grounds, SCADA, Communications, Software licensing, Other | $ million
Maint Expenses Not Otherwise Classified (Asset Management, collection system, substation work, wind turbine blade repairs, solar panel washing, energy storage potential cell upgrades, fuel cell stack replacement, misc. maint.) | $ million
O&M Service Agreement by 3rd party | $ million
Forecasting Services (hydro, wind, and solar) | $ million
Extended Warranties, per year | $ million
Land Lease Costs (not land purchase) | $ million
Natural Gas Major Maint. according to Resource Planning, using EPRI numbers. Calcs from below. | $ million
(EPRI) natural gas fixed O&M, $ million | $ million
(EPRI) natural gas scheduled Maintenance labor, $ million | $ million
(EPRI) gas CT scheduled Maintenance materials, $ million | $ million
(EPRI) natural gas variable O&M, $ million | $ million
(EPRI) CO2 Capture and Storage Fixed O&M, $ million, INCREMENTAL | $ million
Spare row not used | $ million
Spare row not used | $ million
Property, Taxes, and Insurance sum, $ million (adds from below) | $ million
Property costs (leases, royalties, etc.) (0.2% EPC) | $ million
Property Taxes (0.2% EPC) | $ million
Insurance costs (0.2% EPC) | $ million
Title Insurance | $ million
Property, Tax, and Insurance sum, $/MW-hr | $/MW-hr
Fixed O&M - $/MW-hr | $/MW-hr
Variable O&M Costs
Variable O&M (sums from below), $/MW-hr | $/MW-hr
Consumables and Reagents | $/MW-hr
Major Maintenance = the other 50% of Variable O&M (per Resource Planning). | $/MW-hr
Variable O&M, $ million/year | $ million/yr
EPRI CO2 Capture and Storage Variable O&M, $ million/year, INCREMENTAL | $ million/yr
Total Variable O&M, $ million/year | $ million/year
Total Fixed & Variable O&M, $ million/year | $ million/yr
Total Fixed & Variable O&M, $/MW-hr | $/MW-hr
Production cost (Fuel + VOM) | $/MW-hr
Environmental
Production of sulfuric acid for IGCC | Tons/yr
Sulfuric acid market value | $/Ton
Sulfuric acid value | $
Water Usage, gpm | gallons / minute / unit, gpm
Water Usage, gal/year | gallons / year, total plant
Water Usage, gal/MW-hr | gal/MW-hr
* Some data are input, some are calculations. * | Check each emissions line
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
NOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
SOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Hg, Uncontrolled at exhaust, lb/TBtu | lb/TBtu
CO, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
CO2, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, ppm | ppm
NOx, Uncontrolled at exhaust, ppm | ppm
SOx, Uncontrolled at exhaust, ppm | ppm
Hg, Uncontrolled at exhaust, ppm | ppm
CO, Uncontrolled at exhaust, ppm | ppm
CO2, Uncontrolled at exhaust, ppm | ppm
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/hour | lb/hour
NOx, Uncontrolled at exhaust, lb/hour | lb/hour
SOx, Uncontrolled at exhaust, lb/hour | lb/hour
Hg, Uncontrolled at exhaust, lb/hour | lb/hour
CO, Uncontrolled at exhaust, lb/hour | lb/hour
CO2, Uncontrolled at exhaust, lb/hour | lb/hour
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/mmBtu | lb/mmBtu
NOx, Controlled, lb/mmBtu | lb/mmBtu
SOx, Controlled, lb/mmBtu | lb/mmBtu
Hg, Controlled, lb/TBtu | lb/Tbtu
CO, Controlled, lb/mmBtu | lb/mmBtu
CO2, Controlled, lb/mmBtu | lb/mmBtu
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, ppm | ppm
NOx, Controlled, ppm | ppm
SOx, Controlled, ppm | ppm
Hg, Controlled, ppm | ppm
CO, Controlled, ppm | ppm
CO2, Controlled, ppm | ppm
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/MW-hr | lb/MW-hr
NOx, Controlled, lb/MW-hr | lb/MW-hr
SOx, Controlled, lb/MW-hr | lb/MW-hr
Hg, Controlled, lb/MW-hr | lb/MW-hr
CO, Controlled, lb/MW-hr | lb/MW-hr
CO2, Controlled, lb/MW-hr | lb/MW-hr
Control Efficiency Needed to meet Expected Permit Limit
Particulate Matter PM10 Control Efficiency % | %
NOx Control Efficiency % | %
SOx Control Efficiency % | %
Hg Control Efficiency % | %
CO Control Efficiency % | %
CO2 Control Efficiency % | %
Annual Emission Rate, Controlled
Particulate Matter PM10, Annual Emission Rate, Tons/year | Tons/yr
NOx, Annual Emission Rate, Tons/year | Tons/yr
SOx, Annual Emission Rate, Tons/year | Tons/yr
Hg, Annual Emission Rate, lb/year | lb/yr
CO, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Metric Tonnes/year | Tonnes/yr
Annual Captured Rate (what does not get emitted)
Particulate Matter PM10, Annual Captured Rate, Tons/year | Tons/yr
NOx, Annual Captured Rate, Tons/year | Tons/yr
SOx, Annual Captured Rate, Tons/year | Tons/yr
Hg, Annual Captured Rate, lb/year | lb/yr
CO, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Metric Tonnes/year | Tonnes/yr
Emission Fees (Title V)
Particulate Matter PM10 Emission Fee, $/Ton | $/Ton
NOx Emission Fee, $/Ton | $/Ton
SOx Emission Fee, $/Ton | $/Ton
Hg Emission Fee, $/lb | $/lb
CO Emission Fee, $/Ton | $/Ton
CO2 Emission Fee, $/Ton | $/Ton
Annual Emission Cost
Particulate Matter PM10 Annual Emission Cost, $ million | $ million
NOx Annual Emission Cost, $ million | $ million
SOx Annual Emission Cost, $ million | $ million
Hg Annual Emission Cost, $ million | $ million
CO Annual Emission Cost, $ million | $ million
CO2 Annual Emission Cost, $ million | $ million
Total Emission Cost $ million | $ million
Avoided CO2 Cost (Same Technology), $/Tonne | $ / Tonne
$/Tonne Captured and Sequestered | $ / Tonne
$/Tonne Captured and Sequestered with Capacity and Energy Payments | $ / Tonne
Total Emission Cost, $/MW-hr | $/MW-hr
Energy Storage Capital Cost, Simple $ / kW-hr | $/kW-hr
Levelized Cost of Storage Capital, $/MW-hr | $/MW-hr
Levelized Cost of Storage Fuel, $/MW-hr | $/MW-hr
Levelized Cost of Storage O&M, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/kW-hr | $/kW-hr
Emissions, $/MW-hr | $/MW-hr
LCOS, Total with Emissions, $/MW-hr | $/MW-hr
First Year Cost of Electricity COE WITHOUT Incentives or Subsidies. NOT applicable to energy storage.
Capital, $/MW-hr | $/MW-hr
Fuel, $/MW-hr | $/MW-hr
O&M, $/MW-hr | $/MW-hr
Total without Emissions, $/MW-hr | $/MW-hr
Emissions, $/MW-hr | $/MW-hr
Total with Emissions, $/MW-hr | $/MW-hr
Transportation and Storage Cost of CO2, $/Tonne | $ / Tonne
Annual Cost of CO2 Transportation and Storage, $ million | $ million
Annual Cost of CO2 Transportation and Storage, $/MW-hr | $/MW-hr
Total Cost of Electricity, with Emissions and CO2, $/MW-hr (NOT applicable to energy storage) | $/MW-hr
Soft Data
Equipment description | Text
Solar/wind/other equipment size | MW, kW, or watt, as applicable
Number of Generating Units (e.g., solar panels, wind turbines) | Number
Number of (Solar panels, wind turbines, etc.) | Number
Inverter Description | Text
Number of Inverters | Number
Energy Storage Volumetric Energy Density | watt-hour / liter
Energy Storage Specific Energy Density | watt-hour / kg
Energy Storage Specific Power Density | watts / kg
Energy Storage Cycles over 1 year | Number
Energy Storage Depth of Discharge, % (80% is typical) | Number
Energy Storage Roundtrip Efficiency, % (83% is typical) | %
Energy Storage Use (energy = storage; power = frequency response) | Text, Energy or Power
Energy Storage Use (e.g., Frequency response, arbitrage, peak shaving, etc.) | Text
Stack Height, meters or feet, as appropriate | Text
Spare row
Spare row
Unit Availability
Black Start Capable (equipment in place)? | Text, Yes or No
Black Start Capability, MW | MW
Dispatchable ? | Text, Yes or No
Volt - VAR Support ? | Text, Yes or No
Generation Reliability | Text, Good, Fair, or Poor
Flexibility of Operations | Text, Flexible or Inflexible
Operational Complexity | Text, Simple or Complex
Location Benefits? (e.g., saving transmission losses, etc.) | Text, Yes or No
Used for Asset Deferral? (e.g., delay distribution upgrade) | Text, Yes or No
Spare row
Spare row
Scheduled / Planned Outage Factor % | %
Planned Outage Hours | Hours
Planned Outage Days | Days
Forced Outage Factor % | %
Forced Outage Avg. Duration | Hours
Availability Factor % | %
Equivalent Availability Factor % | %
Standard Start Time to Full Speed / No Load (FSNL) | Minutes
Standard Start Time from FSNL to Base Load | Minutes
Time from Zero to FSNL, Cold Start, Cold > 48 hours shutdown | Minutes
Time from Zero to FSNL, Warm Start, Warm < 48 hours shutdown | Minutes
Time from Zero to FSNL, Hot Start, Hot < 8 hours shutdown | Minutes
Hours between Overhauls | Number
Equivalent Starts | Number
Typical Ramp Rate | MW / minute
Down Time (Minimum hrs) | Hours
Run Time (Minimum hrs) | Hours
Spare row
Spare row
Construction
Type of Site | Text
Footprint Needed, minimum acres | Acres
Required Gas Pressure, psig | psig
Fuel Mass Flow, lb/hour | lb/hour
Permitting Risk | Text, Low, Avg., or High
Technology Risk | Text, Low, Avg., or High
Social Acceptance | Text, Low, Avg., or High
Financial Risk (from above) | Text, Low, Avg., or High
Spare row
Spare row
Commercial Availability, years | Years
Permit, License, and Design, years | Years
EPC (Engineer, Procure, Construct), years | Years
Total Project Duration, years | Years
Construction Cash Flow (%) -Yr 1 | % | 65%
Yr 2 | % | 35%
Yr 3 | % | 0%
Yr 4 | % | 0%
Yr 5 | % | 0%
Total | %
Total, All-in US$ 2020 for this Project | $ / kW
Escalation | $ / kW
Total, All-in As-Spent $US | $ / kW
Total, All-in US$ 2020 for this Project | $ million
Escalation | $ million
Total, All-in As-Spent $US | $ million
Numbers will NOT add due to categorization
Power Block | $ million
Balance of Plant | $ million
CO2 Capture Equipment | $ million
Labor | $ million
Interconnects and Infrastructure | $ million
Owner's costs with Sales Tax and Land | $ million
Project Contingency | $ million
AEP Allocations | $ million
Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for the Project | $ million
Power Block | %
Balance of Plant | %
CO2 Capture Equipment | %
Labor | %
Interconnects and Infrastructure | %
Owner's costs with Sales Tax and Land | %
Project Contingency | %
AEP Allocations | %
Commercially Viable | Year
Start Construction | Year
Commercial Operation Date | Year
Graphs show % of costs for major items, NOT every item, without AEP allocations.
Shaded cells are not currently used.
Total All-in, As-spent, $/kW
Maximum across the worksheet = | 2807.1143
Average across the worksheet = | 2807.1143
Minimum across the worksheet = | 2807.1143
Risk/Insurance equipment + labor, $/kW =
Notes and Data Sources | Text

## 2021 Solar
Data feeds to other sheets. Some data not used for all technologies/fuels.
CJB updated 8-24-2020 | Vendor Name | Solar PV - tracking
| Model | CASE 24. SOLAR PHOTOVOLTAIC, 150 MWAC
New Generation Technology Cost and Performance Estimates | Arrangement
Number of (generating) Units
Shaded cells are not currently used. | Nominal MW net, plant | 150
CO2 Control % (up to 99.99%)
APCo, I&M, AEG, Kentucky Power, PSO, SWEPCO, AEP Generation Resources (AGR), BPCo (Buckeye), General | Location by Operating Company
Specific Location, if available | Text
PJM or SPP Regional Transmission Area? If neither, use None | Text - PJM, SPP, or None
Plant Configuration | Units / Inputs
Technology | Text
Technology - Combustion turbine or recip engine? See also Fuel Type | Text, CT or RICE (or other)
If (gas) turbine, Simple or Combined Cycle? | Text, Simple Cycle, Combined Cycle, or None
Black Start Capability, total MW (must type in number even if Zero) | MW
Does Land need to be purchased? Typical responses: No = existing property; wind = Lease; solar = Yes | Text, Yes, No, or Lease
Is this a typical "build" project or asset purchase (build, own, transfer) upon completion? | Text, Build or Buy. For Energy Storage, use Build.
Fuel Type | Solar
Fuel Characteristic | Text
Fuel Availability | Text
Fuel Price Stability | Text
Fuel Cost, $/mmBtu | $/mmBtu
Heating Value, Btu/lb HHV | Btu/Lb HHV
Sulfur, % | %
Ash, % | %
Moisture, % | %
Volatile Matter, VM, % | %
Carbon, % | %
H2, % | %
O2, % | %
N2, % | %
Hg, lb/Tbtu | lb/Tbtu
Annual Fuel Usage, equivalent million tons/year | Million Tons/yr
Annual Heat Input (not valid for all technologies, but used in calculations), mmBtu | Million Btu (mmBtu)
Total Fuel Costs, $/MW-hr | $/MW-hr
Total Fuel Costs, $ million per year | $ Million
General Plant Description | Text
Capacity
Standard ISO MW @ 1,000 ft. Gross | MW gross | 150
Parasitic Load, % | %
Standard ISO MW @1,000 feet, WITHOUT the steam turbine | Nominal MWac net
Standard ISO MW @ 1,000 feet WITH steam turbine | MW
Steam Turbine (used in calcs) MW | MW
Actual DC to AC ratio (default = 1.00) | Number
DC capacity for solar; for all others = Standard ISO at 1,000 ft, MWac | Nominal MWdc net, plant
Standard ISO MW thermal @ 1,000 ft | Nominal MW thermal
Energy Storage Duration, hours | Hours
Energy Storage Capability, MW-hr, AC | MW-hr | 0
Spare Row
Minimum MW net, either calculation or from vendor (aka Turn Down Capability) | MW net
Minimum, Turndown, % (minimum load with 1 machine for combustion turbines) | %
Inlet Chilling Type for Combustion Turbines (See Notes page) | Text - None, Evaporative Cooler, or Chiller
Inlet Chilling Addition (check heat rate impact) MW | MW
Inlet Chilling Heat Rate Impact | Btu/kWh
Power Augmentation ? (See Notes page) | Text - None, Steam Injection, or Water Injection
Power Augmentation Addition (check heat rate impact) MW | MW
Power Augmentation Heat Rate Impact | Btu/kWh
Is Fuel Oil included? Yes or No (Not applicable to Fuel Oil Only units) | Text - Yes or No
Fuel Oil Capacity (check heat rate impact) MW | MW
Fuel Oil Heat Rate Impact | Btu/kWh
HRSG Capability, if Equipped, Unfired MW | MW
Duct Burners included ? Yes or No | Text - Yes or No
Duct Burners (included for all combined cycle HRSGs) MW | MW
Duct Burner Heat Rate Impact | Btu/kWh
Total Potential HRSG + Duct Firing Capability, MW | MW
Spare Row
Spare Row
Winter (30F) MW net without fuel oil + steam turbine | MW net
Winter (30F) MW net + fuel oil (if fuel oil included) + steam turbine | MW net
Summer (90F) MW net by itself + steam turbine | MW net
Summer (90F) MW net + inlet cooling + duct firing + steam turbine | MW net
Summer (90F) MW net without inlet cooling + duct firing + steam turbine | MW net
Summer (90F) MW net + inlet cooling without duct firing + steam turbine | MW net
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. NO Steam Turbine Limit. | MW
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. May be steam turbine limited. USE THIS. | MW
Spare Row
Potential Steam Generation (CHP only, 150 psig, saturated, at capacity factor) lb/year. Not applicable if other technology. (B&McD July 2017; see Notes) | lb/year
Potential Hot Water Generation (CHP only, 150 psig, saturated, at capacity factor) mmBtu/year. Not applicable if other technology. (B&McD July 2017; see Notes) | mmBtu/year
Heat Rate (Higher Heating Value)
Full Load, HHV, net, with degradation (not applicable for all technologies, however, used in calculations) Btu/kW-hr | Btu/kWh
Full Load, HHV, net, with degradation and duct burner heat rate impact, Btu/kW-hr (if not combined cycle with duct burners, use the number above) | Btu/kWh
Full Load, HHV, net, with degradation and fuel oil (Winter) | Btu/kWh
Full Load, HHV, net, with degradation and inlet cooling, NO duct burners (Summer) | Btu/kWh
Full Load, HHV, net, with degradation, inlet cooling, and duct burner heat rate impact (Summer) | Btu/kWh
Full Load, HHV, net, with degradation and duct burners, NO inlet cooling heat rate impact | Btu/kWh
Full Load, HHV, net, with degradation, inlet cooling, power augmentation, HRSG, and duct firing. Does not include Fuel Oil Impact. | Btu/kWh
75% Load, Btu/kW-hr | Btu/kWh
50% Load, Btu/kW-hr | Btu/kWh
25% Load, Btu/kW-hr | Btu/kWh
Average Annual (without duct burners), Btu/kW-hr | Btu/kWh
Estimated efficiency, HHV, full load, degraded, % | %
Energy Storage Roundtrip efficiency (82.67% is average) | %
Capacity Factor, %, for all but energy storage, includes hybrid | %, ac
Capacity Factor, %, for energy storage only (not hybrid) | %
Annual Energy AC Generation from Net Rating, MW-hr (to grid) | MW-hr
Spare row for notes, other calculations
Capital Cost, $/kW based on nominal MW | 2020
Asset Purchase Price (not typical build) | $/kW
Steam generator | $/kW
Gasifier | $/kW
Air Separator | $/kW
Steam, Combustion, or Wind Turbines | $/kW
Black Start / Coping Power Combustion Turbines | $/kW
Solar Modules/Panels | $/kW
Inverters | $/kW
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $/kW (if hybrid, based on generation size)
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $/kW (if hybrid, based on generation size)
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $/kW (if hybrid, based on generation size)
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $/kW
Duct Burners | $/kW
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $/kW
Plant Water Treatment (Demin/RO system, tanks, piping) | $/kW
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $/kW
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $/kW
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $/kW
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $/kW
Misc. Pumps and Piping not otherwise included | $/kW
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $/kW
Balance of Plant, BOP (adds from below) | $/kW
IT, Telecomm, SCADA, Metering, Telemetry, Software | $/kW
Security (including cameras), Roads, and Fencing | $/kW
Control Room | $/kW
Other BOP, not otherwise classified | $/kW
Gas Compression | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Freight/Shipping, Importation Duty, Fees, and Taxes | $/kW
Construction Labor | $/kW
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | $/kW
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | $/kW
Owner's Project and Construction Mgmt | $/kW
Developer Margin and Overheads | $/kW
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $/kW
First of a kind and/or Plug Number | $/kW
SO2 Polishing (used with CO2 capture) | $/kW
(AEP) O&M Mobilization Fee for a Buy | $/kW
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | $/kW
Project Contingency for a Build | $/kW
Project Contingency for a Buy | $/kW
EPC Contractor's Fee | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Fee Subtotal for Build (not used in calculation) | $/kW
Fee Subtotal for Buy (not used in calculation) | $/kW
Total Plant Cost (Overnight EPC) for Build Option | $/kW
Asset Purchase = Buy | $/kW
Owner's Costs | $/kW
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | $/kW
Owner's Costs for a BUY project (excluding Land) | $/kW
Inventory Capital | $/kW
Development and Legal Fees | $/kW
Regulatory Support Fees | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUILD | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUY | $/kW
Interconnection Studies (e.g., Tom Fecho) | $/kW
Enviro and building permits for BUILD | $/kW
Enviro and building permits for BUY | $/kW
AEP-paid sales tax, based on location | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Initial catalyst and chemicals | $/kW
Land Costs (for Buying Land; if Lease = O&M cost) | $/kW
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $/kW
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $/kW
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $/kW
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $/kW
Total Interconnects and Infrastructure (adds from below) | $/kW
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $/kW
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $/kW
Water Supply (Intake) and Wastewater Treatment | $/kW
Site Infrastructure (includes railroad and barge access) | $/kW
Landfill development | $/kW
Initial fuel Inventory (30 days for solid or liquid fuels) | $/kW
Total Plant Cost + Owner's Cost + Interconnects for Build | $/kW
Transmission Upgrade - not currently used | $/kW
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $/kW
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $/kW | 1313
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $/kW
Capital Cost | 2020
Asset Purchase Price (not typical build) | $ million
Steam generator | $ million
Gasifier | $ million
Air Separator | $ million
Steam, Combustion, or Wind Turbines | $ million
Black Start / Coping Power Combustion Turbines | $ million
Solar Modules/Panels | $ million
Inverters | $ million
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $ million (if hybrid, storage only portion)
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $ million (if hybrid, storage only portion)
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $ million (if hybrid, storage only portion)
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $ million
Duct Burners | $ million
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $ million
Plant Water Treatment (Demin/RO system, tanks, piping) | $ million
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $ million
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $ million
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $ million
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $ million
Misc. Pumps and Piping not otherwise included | $ million
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $ million
Balance of Plant, BOP (adds from below) | $ million
IT, Telecomm, SCADA, Metering, Telemetry, Software | $ million
Security (including cameras), Roads, and Fencing | $ million
Control Room | $ million
Other BOP, not otherwise classified | $ million
Gas Compression | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Freight/Shipping, Importation Duty, Fees, and Taxes | 3%
Construction Labor | $ million
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | 12%
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | 5%
Owner's Project and Construction Mgmt | 5%
Developer Margin and Overheads | $ million
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $ million
First of a kind and/or Plug Number | $ million
SO2 Polishing (used with CO2 capture) | $ million
(AEP) O&M Mobilization Fee for a Buy | $ million
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | 1.25%
Project Contingency for a Build | 10%
Project Contingency for a Buy | $ million
EPC Contractor's Fee | 8%
Spare row
Spare row
Spare row
Fee Subtotal for Build (not used in calculation) | $ million
Fee Subtotal for Buy (not used in calculation) | $ million
Total Plant Cost (Overnight EPC) for Build Option | $ million
Asset Purchase = Buy | $ million
Owner's Costs
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | 5%
Owner's Costs for a BUY project (excluding Land) | $ million
Inventory Capital | 1%
Development and Legal Fees | 1.25%
Regulatory Support Fees | 1%
Civil Work (surveys, geotech, grading, site installation) for BUILD | $ million
Civil Work (surveys, geotech, grading, site installation) for BUY | $ million
Interconnection Studies (e.g., Tom Fecho) | $ million
Enviro and building permits for BUILD | $ million
Enviro and building permits for BUY | $ million
AEP-paid sales tax, based on location | $ million
Spare row - check formulas
Spare row - check formulas
Spare row - check formulas
Initial catalyst and chemicals | $ million
Land Costs (for Buying Land; if Lease = O&M cost) | $ million
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $ million
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $ million
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $ million
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $ million
Total Interconnects and Infrastructure (adds from below) | $ million
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $ million
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $ million
Water Supply (Intake) and Wastewater Treatment | $ million
Site Infrastructure (includes railroad and barge access) | $ million
Landfill development | $ million
Initial fuel Inventory (30 days for solid or liquid fuels) | $ million
Total Plant Cost + Owner's Cost + Interconnects for Build | $ million
Total Plant Cost + Owner's Cost + Interconnects for Buy | $ million
Transmission Upgrade - not currently used | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUY (Included in EPC) | $ million
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $ million | 199.4055
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $ million
Financial
AFUDC | $ million
Total Project Duration | months
AFUDC %, by operating company or equivalent, avg. annual rate | %
Financial Risk | Text (Low, Average, High)
Investment Life, years | Years (choose from 2, 3, 4, 5, 10, 15, 20, 25, 30, 33, 40, or 50 years) | 30
Economic Cost of Capital (AEP carrying cost, used in annual capital cost), % | %
Overhead / Allocation Rate for AEP operating company, % | %
Overhead / Allocation Costs, $ million for Build | $ million
Overhead / Allocation Costs, $ million for Buy | $ million
Annual Capital Cost, $ million for Build | $ million
Annual Capital Cost, $ million for Buy | $ million
Capital Cost $/kW - year for Build | $/kW-year
Capital Cost $/kW - year for Buy | $/kW-year
Nuclear Decommissioning Accrual, $ million/year | $ million / year
Nuclear Decommissioning Accrual, $ million | $ million
General Decommissioning Cost, $ | $ million
Assumes no salvage value
Remediation and/or Demolition Costs for Brownfield Site | $ million
Total Capital Costs, $/MW-hr | $/MW-hr
Operations & Maintenance (O&M)
Duty Cycle | Text
Capacity Factor | %
Annual Energy AC Generation from Net Rating, MW-hr (to grid) | MW-hr
Generating Facility Staff | Number (if part-time, use decimal)
Fixed O&M Costs
Fixed O&M as an input from data sources for comparison, $/kW-year | $/kW-year
Fixed O&M as an EPRI/resource planning calculation, $/kW-year | $/kW (if hybrid, based on generation size) | 15.25
Fixed O&M (adds from below), $ million | $ million
Plant Staff Payroll | $ million
General & Administrative Overheads (20% of Payroll) | $ million
Routine Maintenance, typically 1% of major equipment costs or input | $ million
Non-Natural Gas units Major Maintenance = 50% of the Variable O&M Major Maint. (per Resource Planning) | $ million
Utility (aux power and water) costs | $ million
Environmental and safety (monitoring, waste removal, etc.) | $ million
Buildings/grounds, SCADA, Communications, Software licensing, Other | $ million
Maint Expenses Not Otherwise Classified (Asset Management, collection system, substation work, wind turbine blade repairs, solar panel washing, energy storage potential cell upgrades, fuel cell stack replacement, misc. maint.) | $ million
O&M Service Agreement by 3rd party | $ million
Forecasting Services (hydro, wind, and solar) | $ million
Extended Warranties, per year | $ million
Land Lease Costs (not land purchase) | $ million
Natural Gas Major Maint. according to Resource Planning, using EPRI numbers. Calcs from below. | $ million
(EPRI) natural gas fixed O&M, $ million | $ million
(EPRI) natural gas scheduled Maintenance labor, $ million | $ million
(EPRI) gas CT scheduled Maintenance materials, $ million | $ million
(EPRI) natural gas variable O&M, $ million | $ million
(EPRI) CO2 Capture and Storage Fixed O&M, $ million, INCREMENTAL | $ million
Spare row not used | $ million
Spare row not used | $ million
Property, Taxes, and Insurance sum, $ million (adds from below) | $ million
Property costs (leases, royalties, etc.) (0.2% EPC) | $ million
Property Taxes (0.2% EPC) | $ million
Insurance costs (0.2% EPC) | $ million
Title Insurance | $ million
Property, Tax, and Insurance sum, $/MW-hr | $/MW-hr
Fixed O&M - $/MW-hr | $/MW-hr
Variable O&M Costs
Variable O&M (sums from below), $/MW-hr | $/MW-hr
Consumables and Reagents | $/MW-hr
Major Maintenance = the other 50% of Variable O&M (per Resource Planning). | $/MW-hr
Variable O&M, $ million/year | $ million/yr
EPRI CO2 Capture and Storage Variable O&M, $ million/year, INCREMENTAL | $ million/yr
Total Variable O&M, $ million/year | $ million/year
Total Fixed & Variable O&M, $ million/year | $ million/yr
Total Fixed & Variable O&M, $/MW-hr | $/MW-hr
Production cost (Fuel + VOM) | $/MW-hr
Environmental
Production of sulfuric acid for IGCC | Tons/yr
Sulfuric acid market value | $/Ton
Sulfuric acid value | $
Water Usage, gpm | gallons / minute / unit, gpm
Water Usage, gal/year | gallons / year, total plant
Water Usage, gal/MW-hr | gal/MW-hr
* Some data are input, some are calculations. * | Check each emissions line
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
NOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
SOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Hg, Uncontrolled at exhaust, lb/TBtu | lb/TBtu
CO, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
CO2, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, ppm | ppm
NOx, Uncontrolled at exhaust, ppm | ppm
SOx, Uncontrolled at exhaust, ppm | ppm
Hg, Uncontrolled at exhaust, ppm | ppm
CO, Uncontrolled at exhaust, ppm | ppm
CO2, Uncontrolled at exhaust, ppm | ppm
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/hour | lb/hour
NOx, Uncontrolled at exhaust, lb/hour | lb/hour
SOx, Uncontrolled at exhaust, lb/hour | lb/hour
Hg, Uncontrolled at exhaust, lb/hour | lb/hour
CO, Uncontrolled at exhaust, lb/hour | lb/hour
CO2, Uncontrolled at exhaust, lb/hour | lb/hour
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/mmBtu | lb/mmBtu
NOx, Controlled, lb/mmBtu | lb/mmBtu
SOx, Controlled, lb/mmBtu | lb/mmBtu
Hg, Controlled, lb/TBtu | lb/Tbtu
CO, Controlled, lb/mmBtu | lb/mmBtu
CO2, Controlled, lb/mmBtu | lb/mmBtu
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, ppm | ppm
NOx, Controlled, ppm | ppm
SOx, Controlled, ppm | ppm
Hg, Controlled, ppm | ppm
CO, Controlled, ppm | ppm
CO2, Controlled, ppm | ppm
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/MW-hr | lb/MW-hr
NOx, Controlled, lb/MW-hr | lb/MW-hr
SOx, Controlled, lb/MW-hr | lb/MW-hr
Hg, Controlled, lb/MW-hr | lb/MW-hr
CO, Controlled, lb/MW-hr | lb/MW-hr
CO2, Controlled, lb/MW-hr | lb/MW-hr
Control Efficiency Needed to meet Expected Permit Limit
Particulate Matter PM10 Control Efficiency % | %
NOx Control Efficiency % | %
SOx Control Efficiency % | %
Hg Control Efficiency % | %
CO Control Efficiency % | %
CO2 Control Efficiency % | %
Annual Emission Rate, Controlled
Particulate Matter PM10, Annual Emission Rate, Tons/year | Tons/yr
NOx, Annual Emission Rate, Tons/year | Tons/yr
SOx, Annual Emission Rate, Tons/year | Tons/yr
Hg, Annual Emission Rate, lb/year | lb/yr
CO, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Metric Tonnes/year | Tonnes/yr
Annual Captured Rate (what does not get emitted)
Particulate Matter PM10, Annual Captured Rate, Tons/year | Tons/yr
NOx, Annual Captured Rate, Tons/year | Tons/yr
SOx, Annual Captured Rate, Tons/year | Tons/yr
Hg, Annual Captured Rate, lb/year | lb/yr
CO, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Metric Tonnes/year | Tonnes/yr
Emission Fees (Title V)
Particulate Matter PM10 Emission Fee, $/Ton | $/Ton
NOx Emission Fee, $/Ton | $/Ton
SOx Emission Fee, $/Ton | $/Ton
Hg Emission Fee, $/lb | $/lb
CO Emission Fee, $/Ton | $/Ton
CO2 Emission Fee, $/Ton | $/Ton
Annual Emission Cost
Particulate Matter PM10 Annual Emission Cost, $ million | $ million
NOx Annual Emission Cost, $ million | $ million
SOx Annual Emission Cost, $ million | $ million
Hg Annual Emission Cost, $ million | $ million
CO Annual Emission Cost, $ million | $ million
CO2 Annual Emission Cost, $ million | $ million
Total Emission Cost $ million | $ million
Avoided CO2 Cost (Same Technology), $/Tonne | $ / Tonne
$/Tonne Captured and Sequestered | $ / Tonne
$/Tonne Captured and Sequestered with Capacity and Energy Payments | $ / Tonne
Total Emission Cost, $/MW-hr | $/MW-hr
Energy Storage Capital Cost, Simple $ / kW-hr | $/kW-hr
Levelized Cost of Storage Capital, $/MW-hr | $/MW-hr
Levelized Cost of Storage Fuel, $/MW-hr | $/MW-hr
Levelized Cost of Storage O&M, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/kW-hr | $/kW-hr
Emissions, $/MW-hr | $/MW-hr
LCOS, Total with Emissions, $/MW-hr | $/MW-hr
First Year Cost of Electricity COE WITHOUT Incentives or Subsidies. NOT applicable to energy storage.
Capital, $/MW-hr | $/MW-hr
Fuel, $/MW-hr | $/MW-hr
O&M, $/MW-hr | $/MW-hr
Total without Emissions, $/MW-hr | $/MW-hr
Emissions, $/MW-hr | $/MW-hr
Total with Emissions, $/MW-hr | $/MW-hr
Transportation and Storage Cost of CO2, $/Tonne | $ / Tonne
Annual Cost of CO2 Transportation and Storage, $ million | $ million
Annual Cost of CO2 Transportation and Storage, $/MW-hr | $/MW-hr
Total Cost of Electricity, with Emissions and CO2, $/MW-hr (NOT applicable to energy storage) | $/MW-hr
Soft Data
Equipment description | Text
Solar/wind/other equipment size | MW, kW, or watt, as applicable
Number of Generating Units (e.g., solar panels, wind turbines) | Number
Number of (Solar panels, wind turbines, etc.) | Number
Inverter Description | Text
Number of Inverters | Number
Energy Storage Volumetric Energy Density | watt-hour / liter
Energy Storage Specific Energy Density | watt-hour / kg
Energy Storage Specific Power Density | watts / kg
Energy Storage Cycles over 1 year | Number
Energy Storage Depth of Discharge, % (80% is typical) | Number
Energy Storage Roundtrip Efficiency, % (83% is typical) | %
Energy Storage Use (energy = storage; power = frequency response) | Text, Energy or Power
Energy Storage Use (e.g., Frequency response, arbitrage, peak shaving, etc.) | Text
Stack Height, meters or feet, as appropriate | Text
Spare row
Spare row
Unit Availability
Black Start Capable (equipment in place)? | Text, Yes or No
Black Start Capability, MW | MW
Dispatchable ? | Text, Yes or No
Volt - VAR Support ? | Text, Yes or No
Generation Reliability | Text, Good, Fair, or Poor
Flexibility of Operations | Text, Flexible or Inflexible
Operational Complexity | Text, Simple or Complex
Location Benefits? (e.g., saving transmission losses, etc.) | Text, Yes or No
Used for Asset Deferral? (e.g., delay distribution upgrade) | Text, Yes or No
Spare row
Spare row
Scheduled / Planned Outage Factor % | %
Planned Outage Hours | Hours
Planned Outage Days | Days
Forced Outage Factor % | %
Forced Outage Avg. Duration | Hours
Availability Factor % | %
Equivalent Availability Factor % | %
Standard Start Time to Full Speed / No Load (FSNL) | Minutes
Standard Start Time from FSNL to Base Load | Minutes
Time from Zero to FSNL, Cold Start, Cold > 48 hours shutdown | Minutes
Time from Zero to FSNL, Warm Start, Warm < 48 hours shutdown | Minutes
Time from Zero to FSNL, Hot Start, Hot < 8 hours shutdown | Minutes
Hours between Overhauls | Number
Equivalent Starts | Number
Typical Ramp Rate | MW / minute
Down Time (Minimum hrs) | Hours
Run Time (Minimum hrs) | Hours
Spare row
Spare row
Construction
Type of Site | Text
Footprint Needed, minimum acres | Acres
Required Gas Pressure, psig | psig
Fuel Mass Flow, lb/hour | lb/hour
Permitting Risk | Text, Low, Avg., or High
Technology Risk | Text, Low, Avg., or High
Social Acceptance | Text, Low, Avg., or High
Financial Risk (from above) | Text, Low, Avg., or High
Spare row
Spare row
Commercial Availability, years | Years
Permit, License, and Design, years | Years
EPC (Engineer, Procure, Construct), years | Years
Total Project Duration, years | Years
Construction Cash Flow (%) -Yr 1 | % | 75%
Yr 2 | % | 25%
Yr 3 | % | 0%
Yr 4 | % | 0%
Yr 5 | % | 0%
Total | %
Total, All-in US$ 2020 for this Project | $ / kW
Escalation | $ / kW
Total, All-in As-Spent $US | $ / kW
Total, All-in US$ 2020 for this Project | $ million
Escalation | $ million
Total, All-in As-Spent $US | $ million
Numbers will NOT add due to categorization
Power Block | $ million
Balance of Plant | $ million
CO2 Capture Equipment | $ million
Labor | $ million
Interconnects and Infrastructure | $ million
Owner's costs with Sales Tax and Land | $ million
Project Contingency | $ million
AEP Allocations | $ million
Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for the Project | $ million
Power Block | %
Balance of Plant | %
CO2 Capture Equipment | %
Labor | %
Interconnects and Infrastructure | %
Owner's costs with Sales Tax and Land | %
Project Contingency | %
AEP Allocations | %
Commercially Viable | Year
Start Construction | Year
Commercial Operation Date | Year
Graphs show % of costs for major items, NOT every item, without AEP allocations.
Shaded cells are not currently used.
Total All-in, As-spent, $/kW
Maximum across the worksheet = | 2807.1143
Average across the worksheet = | 2807.1143
Minimum across the worksheet = | 2807.1143
Risk/Insurance equipment + labor, $/kW =
Notes and Data Sources | Text

## 2021 Solar + Storage
Data feeds to other sheets. Some data not used for all technologies/fuels.
CJB updated 8-24-2020 | Vendor Name | Solar + Storage
| Model | CASE 25. SOLAR PHOTOVOLTAIC WITH BATTERY ENERGY STORAGE SYSTEM, 150 MWx200 MWh
New Generation Technology Cost and Performance Estimates | Arrangement
Number of (generating) Units
Shaded cells are not currently used. | Nominal MW net, plant | 150
CO2 Control % (up to 99.99%)
APCo, I&M, AEG, Kentucky Power, PSO, SWEPCO, AEP Generation Resources (AGR), BPCo (Buckeye), General | Location by Operating Company
Specific Location, if available | Text
PJM or SPP Regional Transmission Area? If neither, use None | Text - PJM, SPP, or None
Plant Configuration | Units / Inputs
Technology | Text
Technology - Combustion turbine or recip engine? See also Fuel Type | Text, CT or RICE (or other)
If (gas) turbine, Simple or Combined Cycle? | Text, Simple Cycle, Combined Cycle, or None
Black Start Capability, total MW (must type in number even if Zero) | MW
Does Land need to be purchased? Typical responses: No = existing property; wind = Lease; solar = Yes | Text, Yes, No, or Lease
Is this a typical "build" project or asset purchase (build, own, transfer) upon completion? | Text, Build or Buy. For Energy Storage, use Build.
Fuel Type | Solar
Fuel Characteristic | Text
Fuel Availability | Text
Fuel Price Stability | Text
Fuel Cost, $/mmBtu | $/mmBtu
Heating Value, Btu/lb HHV | Btu/Lb HHV
Sulfur, % | %
Ash, % | %
Moisture, % | %
Volatile Matter, VM, % | %
Carbon, % | %
H2, % | %
O2, % | %
N2, % | %
Hg, lb/Tbtu | lb/Tbtu
Annual Fuel Usage, equivalent million tons/year | Million Tons/yr
Annual Heat Input (not valid for all technologies, but used in calculations), mmBtu | Million Btu (mmBtu)
Total Fuel Costs, $/MW-hr | $/MW-hr
Total Fuel Costs, $ million per year | $ Million
General Plant Description | Text
Capacity
Standard ISO MW @ 1,000 ft. Gross | MW gross | 150
Parasitic Load, % | %
Standard ISO MW @1,000 feet, WITHOUT the steam turbine | Nominal MWac net
Standard ISO MW @ 1,000 feet WITH steam turbine | MW
Steam Turbine (used in calcs) MW | MW
Actual DC to AC ratio (default = 1.00) | Number
DC capacity for solar; for all others = Standard ISO at 1,000 ft, MWac | Nominal MWdc net, plant
Standard ISO MW thermal @ 1,000 ft | Nominal MW thermal
Energy Storage Duration, hours | Hours | 4
Energy Storage Capability, MW-hr, AC | MW-hr | 200
Spare Row
Minimum MW net, either calculation or from vendor (aka Turn Down Capability) | MW net
Minimum, Turndown, % (minimum load with 1 machine for combustion turbines) | %
Inlet Chilling Type for Combustion Turbines (See Notes page) | Text - None, Evaporative Cooler, or Chiller
Inlet Chilling Addition (check heat rate impact) MW | MW
Inlet Chilling Heat Rate Impact | Btu/kWh
Power Augmentation ? (See Notes page) | Text - None, Steam Injection, or Water Injection
Power Augmentation Addition (check heat rate impact) MW | MW
Power Augmentation Heat Rate Impact | Btu/kWh
Is Fuel Oil included? Yes or No (Not applicable to Fuel Oil Only units) | Text - Yes or No
Fuel Oil Capacity (check heat rate impact) MW | MW
Fuel Oil Heat Rate Impact | Btu/kWh
HRSG Capability, if Equipped, Unfired MW | MW
Duct Burners included ? Yes or No | Text - Yes or No
Duct Burners (included for all combined cycle HRSGs) MW | MW
Duct Burner Heat Rate Impact | Btu/kWh
Total Potential HRSG + Duct Firing Capability, MW | MW
Spare Row
Spare Row
Winter (30F) MW net without fuel oil + steam turbine | MW net
Winter (30F) MW net + fuel oil (if fuel oil included) + steam turbine | MW net
Summer (90F) MW net by itself + steam turbine | MW net
Summer (90F) MW net + inlet cooling + duct firing + steam turbine | MW net
Summer (90F) MW net without inlet cooling + duct firing + steam turbine | MW net
Summer (90F) MW net + inlet cooling without duct firing + steam turbine | MW net
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. NO Steam Turbine Limit. | MW
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. May be steam turbine limited. USE THIS. | MW
Spare Row
Potential Steam Generation (CHP only, 150 psig, saturated, at capacity factor) lb/year. Not applicable if other technology. (B&McD July 2017; see Notes) | lb/year
Potential Hot Water Generation (CHP only, 150 psig, saturated, at capacity factor) mmBtu/year. Not applicable if other technology. (B&McD July 2017; see Notes) | mmBtu/year
Heat Rate (Higher Heating Value)
Full Load, HHV, net, with degradation (not applicable for all technologies, however, used in calculations) Btu/kW-hr | Btu/kWh
Full Load, HHV, net, with degradation and duct burner heat rate impact, Btu/kW-hr (if not combined cycle with duct burners, use the number above) | Btu/kWh
Full Load, HHV, net, with degradation and fuel oil (Winter) | Btu/kWh
Full Load, HHV, net, with degradation and inlet cooling, NO duct burners (Summer) | Btu/kWh
Full Load, HHV, net, with degradation, inlet cooling, and duct burner heat rate impact (Summer) | Btu/kWh
Full Load, HHV, net, with degradation and duct burners, NO inlet cooling heat rate impact | Btu/kWh
Full Load, HHV, net, with degradation, inlet cooling, power augmentation, HRSG, and duct firing. Does not include Fuel Oil Impact. | Btu/kWh
75% Load, Btu/kW-hr | Btu/kWh
50% Load, Btu/kW-hr | Btu/kWh
25% Load, Btu/kW-hr | Btu/kWh
Average Annual (without duct burners), Btu/kW-hr | Btu/kWh
Estimated efficiency, HHV, full load, degraded, % | %
Energy Storage Roundtrip efficiency (82.67% is average) | %
Capacity Factor, %, for all but energy storage, includes hybrid | %, ac
Capacity Factor, %, for energy storage only (not hybrid) | %
Annual Energy AC Generation from Net Rating, MW-hr (to grid) | MW-hr
Spare row for notes, other calculations
Capital Cost, $/kW based on nominal MW | 2020
Asset Purchase Price (not typical build) | $/kW
Steam generator | $/kW
Gasifier | $/kW
Air Separator | $/kW
Steam, Combustion, or Wind Turbines | $/kW
Black Start / Coping Power Combustion Turbines | $/kW
Solar Modules/Panels | $/kW
Inverters | $/kW
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $/kW (if hybrid, based on generation size)
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $/kW (if hybrid, based on generation size)
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $/kW (if hybrid, based on generation size)
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $/kW
Duct Burners | $/kW
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $/kW
Plant Water Treatment (Demin/RO system, tanks, piping) | $/kW
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $/kW
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $/kW
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $/kW
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $/kW
Misc. Pumps and Piping not otherwise included | $/kW
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $/kW
Balance of Plant, BOP (adds from below) | $/kW
IT, Telecomm, SCADA, Metering, Telemetry, Software | $/kW
Security (including cameras), Roads, and Fencing | $/kW
Control Room | $/kW
Other BOP, not otherwise classified | $/kW
Gas Compression | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Freight/Shipping, Importation Duty, Fees, and Taxes | $/kW
Construction Labor | $/kW
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | $/kW
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | $/kW
Owner's Project and Construction Mgmt | $/kW
Developer Margin and Overheads | $/kW
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $/kW
First of a kind and/or Plug Number | $/kW
SO2 Polishing (used with CO2 capture) | $/kW
(AEP) O&M Mobilization Fee for a Buy | $/kW
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | $/kW
Project Contingency for a Build | $/kW
Project Contingency for a Buy | $/kW
EPC Contractor's Fee | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Fee Subtotal for Build (not used in calculation) | $/kW
Fee Subtotal for Buy (not used in calculation) | $/kW
Total Plant Cost (Overnight EPC) for Build Option | $/kW
Asset Purchase = Buy | $/kW
Owner's Costs | $/kW
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | $/kW
Owner's Costs for a BUY project (excluding Land) | $/kW
Inventory Capital | $/kW
Development and Legal Fees | $/kW
Regulatory Support Fees | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUILD | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUY | $/kW
Interconnection Studies (e.g., Tom Fecho) | $/kW
Enviro and building permits for BUILD | $/kW
Enviro and building permits for BUY | $/kW
AEP-paid sales tax, based on location | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Initial catalyst and chemicals | $/kW
Land Costs (for Buying Land; if Lease = O&M cost) | $/kW
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $/kW
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $/kW
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $/kW
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $/kW
Total Interconnects and Infrastructure (adds from below) | $/kW
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $/kW
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $/kW
Water Supply (Intake) and Wastewater Treatment | $/kW
Site Infrastructure (includes railroad and barge access) | $/kW
Landfill development | $/kW
Initial fuel Inventory (30 days for solid or liquid fuels) | $/kW
Total Plant Cost + Owner's Cost + Interconnects for Build | $/kW
Transmission Upgrade - not currently used | $/kW
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $/kW
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $/kW | 1755
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $/kW
Capital Cost | 2020
Asset Purchase Price (not typical build) | $ million
Steam generator | $ million
Gasifier | $ million
Air Separator | $ million
Steam, Combustion, or Wind Turbines | $ million
Black Start / Coping Power Combustion Turbines | $ million
Solar Modules/Panels | $ million
Inverters | $ million
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $ million (if hybrid, storage only portion)
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $ million (if hybrid, storage only portion)
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $ million (if hybrid, storage only portion)
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $ million
Duct Burners | $ million
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $ million
Plant Water Treatment (Demin/RO system, tanks, piping) | $ million
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $ million
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $ million
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $ million
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $ million
Misc. Pumps and Piping not otherwise included | $ million
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $ million
Balance of Plant, BOP (adds from below) | $ million
IT, Telecomm, SCADA, Metering, Telemetry, Software | $ million
Security (including cameras), Roads, and Fencing | $ million
Control Room | $ million
Other BOP, not otherwise classified | $ million
Gas Compression | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Freight/Shipping, Importation Duty, Fees, and Taxes | 3%
Construction Labor | $ million
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | 12%
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | 5%
Owner's Project and Construction Mgmt | 5%
Developer Margin and Overheads | $ million
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $ million
First of a kind and/or Plug Number | $ million
SO2 Polishing (used with CO2 capture) | $ million
(AEP) O&M Mobilization Fee for a Buy | $ million
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | 1.25%
Project Contingency for a Build | 10%
Project Contingency for a Buy | $ million
EPC Contractor's Fee | 8%
Spare row
Spare row
Spare row
Fee Subtotal for Build (not used in calculation) | $ million
Fee Subtotal for Buy (not used in calculation) | $ million
Total Plant Cost (Overnight EPC) for Build Option | $ million
Asset Purchase = Buy | $ million
Owner's Costs
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | 5%
Owner's Costs for a BUY project (excluding Land) | $ million
Inventory Capital | 1%
Development and Legal Fees | 1.25%
Regulatory Support Fees | 1%
Civil Work (surveys, geotech, grading, site installation) for BUILD | $ million
Civil Work (surveys, geotech, grading, site installation) for BUY | $ million
Interconnection Studies (e.g., Tom Fecho) | $ million
Enviro and building permits for BUILD | $ million
Enviro and building permits for BUY | $ million
AEP-paid sales tax, based on location | $ million
Spare row - check formulas
Spare row - check formulas
Spare row - check formulas
Initial catalyst and chemicals | $ million
Land Costs (for Buying Land; if Lease = O&M cost) | $ million
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $ million
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $ million
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $ million
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $ million
Total Interconnects and Infrastructure (adds from below) | $ million
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $ million
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $ million
Water Supply (Intake) and Wastewater Treatment | $ million
Site Infrastructure (includes railroad and barge access) | $ million
Landfill development | $ million
Initial fuel Inventory (30 days for solid or liquid fuels) | $ million
Total Plant Cost + Owner's Cost + Interconnects for Build | $ million
Total Plant Cost + Owner's Cost + Interconnects for Buy | $ million
Transmission Upgrade - not currently used | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUY (Included in EPC) | $ million
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $ million | 287.1806
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $ million
Financial
AFUDC | $ million
Total Project Duration | months
AFUDC %, by operating company or equivalent, avg. annual rate | %
Financial Risk | Text (Low, Average, High)
Investment Life, years | Years (choose from 2, 3, 4, 5, 10, 15, 20, 25, 30, 33, 40, or 50 years) | 30
Economic Cost of Capital (AEP carrying cost, used in annual capital cost), % | %
Overhead / Allocation Rate for AEP operating company, % | %
Overhead / Allocation Costs, $ million for Build | $ million
Overhead / Allocation Costs, $ million for Buy | $ million
Annual Capital Cost, $ million for Build | $ million
Annual Capital Cost, $ million for Buy | $ million
Capital Cost $/kW - year for Build | $/kW-year
Capital Cost $/kW - year for Buy | $/kW-year
Nuclear Decommissioning Accrual, $ million/year | $ million / year
Nuclear Decommissioning Accrual, $ million | $ million
General Decommissioning Cost, $ | $ million
Assumes no salvage value
Remediation and/or Demolition Costs for Brownfield Site | $ million
Total Capital Costs, $/MW-hr | $/MW-hr
Operations & Maintenance (O&M)
Duty Cycle | Text
Capacity Factor | %
Annual Energy AC Generation from Net Rating, MW-hr (to grid) | MW-hr
Generating Facility Staff | Number (if part-time, use decimal)
Fixed O&M Costs
Fixed O&M as an input from data sources for comparison, $/kW-year | $/kW-year
Fixed O&M as an EPRI/resource planning calculation, $/kW-year | $/kW (if hybrid, based on generation size) | 32.7959
Fixed O&M (adds from below), $ million | $ million
Plant Staff Payroll | $ million
General & Administrative Overheads (20% of Payroll) | $ million
Routine Maintenance, typically 1% of major equipment costs or input | $ million
Non-Natural Gas units Major Maintenance = 50% of the Variable O&M Major Maint. (per Resource Planning) | $ million
Utility (aux power and water) costs | $ million
Environmental and safety (monitoring, waste removal, etc.) | $ million
Buildings/grounds, SCADA, Communications, Software licensing, Other | $ million
Maint Expenses Not Otherwise Classified (Asset Management, collection system, substation work, wind turbine blade repairs, solar panel washing, energy storage potential cell upgrades, fuel cell stack replacement, misc. maint.) | $ million
O&M Service Agreement by 3rd party | $ million
Forecasting Services (hydro, wind, and solar) | $ million
Extended Warranties, per year | $ million
Land Lease Costs (not land purchase) | $ million
Natural Gas Major Maint. according to Resource Planning, using EPRI numbers. Calcs from below. | $ million
(EPRI) natural gas fixed O&M, $ million | $ million
(EPRI) natural gas scheduled Maintenance labor, $ million | $ million
(EPRI) gas CT scheduled Maintenance materials, $ million | $ million
(EPRI) natural gas variable O&M, $ million | $ million
(EPRI) CO2 Capture and Storage Fixed O&M, $ million, INCREMENTAL | $ million
Spare row not used | $ million
Spare row not used | $ million
Property, Taxes, and Insurance sum, $ million (adds from below) | $ million
Property costs (leases, royalties, etc.) (0.2% EPC) | $ million
Property Taxes (0.2% EPC) | $ million
Insurance costs (0.2% EPC) | $ million
Title Insurance | $ million
Property, Tax, and Insurance sum, $/MW-hr | $/MW-hr
Fixed O&M - $/MW-hr | $/MW-hr
Variable O&M Costs
Variable O&M (sums from below), $/MW-hr | $/MW-hr
Consumables and Reagents | $/MW-hr
Major Maintenance = the other 50% of Variable O&M (per Resource Planning). | $/MW-hr
Variable O&M, $ million/year | $ million/yr
EPRI CO2 Capture and Storage Variable O&M, $ million/year, INCREMENTAL | $ million/yr
Total Variable O&M, $ million/year | $ million/year
Total Fixed & Variable O&M, $ million/year | $ million/yr
Total Fixed & Variable O&M, $/MW-hr | $/MW-hr
Production cost (Fuel + VOM) | $/MW-hr
Environmental
Production of sulfuric acid for IGCC | Tons/yr
Sulfuric acid market value | $/Ton
Sulfuric acid value | $
Water Usage, gpm | gallons / minute / unit, gpm
Water Usage, gal/year | gallons / year, total plant
Water Usage, gal/MW-hr | gal/MW-hr
* Some data are input, some are calculations. * | Check each emissions line
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
NOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
SOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Hg, Uncontrolled at exhaust, lb/TBtu | lb/TBtu
CO, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
CO2, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, ppm | ppm
NOx, Uncontrolled at exhaust, ppm | ppm
SOx, Uncontrolled at exhaust, ppm | ppm
Hg, Uncontrolled at exhaust, ppm | ppm
CO, Uncontrolled at exhaust, ppm | ppm
CO2, Uncontrolled at exhaust, ppm | ppm
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/hour | lb/hour
NOx, Uncontrolled at exhaust, lb/hour | lb/hour
SOx, Uncontrolled at exhaust, lb/hour | lb/hour
Hg, Uncontrolled at exhaust, lb/hour | lb/hour
CO, Uncontrolled at exhaust, lb/hour | lb/hour
CO2, Uncontrolled at exhaust, lb/hour | lb/hour
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/mmBtu | lb/mmBtu
NOx, Controlled, lb/mmBtu | lb/mmBtu
SOx, Controlled, lb/mmBtu | lb/mmBtu
Hg, Controlled, lb/TBtu | lb/Tbtu
CO, Controlled, lb/mmBtu | lb/mmBtu
CO2, Controlled, lb/mmBtu | lb/mmBtu
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, ppm | ppm
NOx, Controlled, ppm | ppm
SOx, Controlled, ppm | ppm
Hg, Controlled, ppm | ppm
CO, Controlled, ppm | ppm
CO2, Controlled, ppm | ppm
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/MW-hr | lb/MW-hr
NOx, Controlled, lb/MW-hr | lb/MW-hr
SOx, Controlled, lb/MW-hr | lb/MW-hr
Hg, Controlled, lb/MW-hr | lb/MW-hr
CO, Controlled, lb/MW-hr | lb/MW-hr
CO2, Controlled, lb/MW-hr | lb/MW-hr
Control Efficiency Needed to meet Expected Permit Limit
Particulate Matter PM10 Control Efficiency % | %
NOx Control Efficiency % | %
SOx Control Efficiency % | %
Hg Control Efficiency % | %
CO Control Efficiency % | %
CO2 Control Efficiency % | %
Annual Emission Rate, Controlled
Particulate Matter PM10, Annual Emission Rate, Tons/year | Tons/yr
NOx, Annual Emission Rate, Tons/year | Tons/yr
SOx, Annual Emission Rate, Tons/year | Tons/yr
Hg, Annual Emission Rate, lb/year | lb/yr
CO, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Metric Tonnes/year | Tonnes/yr
Annual Captured Rate (what does not get emitted)
Particulate Matter PM10, Annual Captured Rate, Tons/year | Tons/yr
NOx, Annual Captured Rate, Tons/year | Tons/yr
SOx, Annual Captured Rate, Tons/year | Tons/yr
Hg, Annual Captured Rate, lb/year | lb/yr
CO, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Metric Tonnes/year | Tonnes/yr
Emission Fees (Title V)
Particulate Matter PM10 Emission Fee, $/Ton | $/Ton
NOx Emission Fee, $/Ton | $/Ton
SOx Emission Fee, $/Ton | $/Ton
Hg Emission Fee, $/lb | $/lb
CO Emission Fee, $/Ton | $/Ton
CO2 Emission Fee, $/Ton | $/Ton
Annual Emission Cost
Particulate Matter PM10 Annual Emission Cost, $ million | $ million
NOx Annual Emission Cost, $ million | $ million
SOx Annual Emission Cost, $ million | $ million
Hg Annual Emission Cost, $ million | $ million
CO Annual Emission Cost, $ million | $ million
CO2 Annual Emission Cost, $ million | $ million
Total Emission Cost $ million | $ million
Avoided CO2 Cost (Same Technology), $/Tonne | $ / Tonne
$/Tonne Captured and Sequestered | $ / Tonne
$/Tonne Captured and Sequestered with Capacity and Energy Payments | $ / Tonne
Total Emission Cost, $/MW-hr | $/MW-hr
Energy Storage Capital Cost, Simple $ / kW-hr | $/kW-hr
Levelized Cost of Storage Capital, $/MW-hr | $/MW-hr
Levelized Cost of Storage Fuel, $/MW-hr | $/MW-hr
Levelized Cost of Storage O&M, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/kW-hr | $/kW-hr
Emissions, $/MW-hr | $/MW-hr
LCOS, Total with Emissions, $/MW-hr | $/MW-hr
First Year Cost of Electricity COE WITHOUT Incentives or Subsidies. NOT applicable to energy storage.
Capital, $/MW-hr | $/MW-hr
Fuel, $/MW-hr | $/MW-hr
O&M, $/MW-hr | $/MW-hr
Total without Emissions, $/MW-hr | $/MW-hr
Emissions, $/MW-hr | $/MW-hr
Total with Emissions, $/MW-hr | $/MW-hr
Transportation and Storage Cost of CO2, $/Tonne | $ / Tonne
Annual Cost of CO2 Transportation and Storage, $ million | $ million
Annual Cost of CO2 Transportation and Storage, $/MW-hr | $/MW-hr
Total Cost of Electricity, with Emissions and CO2, $/MW-hr (NOT applicable to energy storage) | $/MW-hr
Soft Data
Equipment description | Text
Solar/wind/other equipment size | MW, kW, or watt, as applicable
Number of Generating Units (e.g., solar panels, wind turbines) | Number
Number of (Solar panels, wind turbines, etc.) | Number
Inverter Description | Text
Number of Inverters | Number
Energy Storage Volumetric Energy Density | watt-hour / liter
Energy Storage Specific Energy Density | watt-hour / kg
Energy Storage Specific Power Density | watts / kg
Energy Storage Cycles over 1 year | Number
Energy Storage Depth of Discharge, % (80% is typical) | Number
Energy Storage Roundtrip Efficiency, % (83% is typical) | %
Energy Storage Use (energy = storage; power = frequency response) | Text, Energy or Power
Energy Storage Use (e.g., Frequency response, arbitrage, peak shaving, etc.) | Text
Stack Height, meters or feet, as appropriate | Text
Spare row
Spare row
Unit Availability
Black Start Capable (equipment in place)? | Text, Yes or No
Black Start Capability, MW | MW
Dispatchable ? | Text, Yes or No
Volt - VAR Support ? | Text, Yes or No
Generation Reliability | Text, Good, Fair, or Poor
Flexibility of Operations | Text, Flexible or Inflexible
Operational Complexity | Text, Simple or Complex
Location Benefits? (e.g., saving transmission losses, etc.) | Text, Yes or No
Used for Asset Deferral? (e.g., delay distribution upgrade) | Text, Yes or No
Spare row
Spare row
Scheduled / Planned Outage Factor % | %
Planned Outage Hours | Hours
Planned Outage Days | Days
Forced Outage Factor % | %
Forced Outage Avg. Duration | Hours
Availability Factor % | %
Equivalent Availability Factor % | %
Standard Start Time to Full Speed / No Load (FSNL) | Minutes
Standard Start Time from FSNL to Base Load | Minutes
Time from Zero to FSNL, Cold Start, Cold > 48 hours shutdown | Minutes
Time from Zero to FSNL, Warm Start, Warm < 48 hours shutdown | Minutes
Time from Zero to FSNL, Hot Start, Hot < 8 hours shutdown | Minutes
Hours between Overhauls | Number
Equivalent Starts | Number
Typical Ramp Rate | MW / minute
Down Time (Minimum hrs) | Hours
Run Time (Minimum hrs) | Hours
Spare row
Spare row
Construction
Type of Site | Text
Footprint Needed, minimum acres | Acres
Required Gas Pressure, psig | psig
Fuel Mass Flow, lb/hour | lb/hour
Permitting Risk | Text, Low, Avg., or High
Technology Risk | Text, Low, Avg., or High
Social Acceptance | Text, Low, Avg., or High
Financial Risk (from above) | Text, Low, Avg., or High
Spare row
Spare row
Commercial Availability, years | Years
Permit, License, and Design, years | Years
EPC (Engineer, Procure, Construct), years | Years
Total Project Duration, years | Years
Construction Cash Flow (%) -Yr 1 | % | 75%
Yr 2 | % | 25%
Yr 3 | % | 0%
Yr 4 | % | 0%
Yr 5 | % | 0%
Total | %
Total, All-in US$ 2020 for this Project | $ / kW
Escalation | $ / kW
Total, All-in As-Spent $US | $ / kW
Total, All-in US$ 2020 for this Project | $ million
Escalation | $ million
Total, All-in As-Spent $US | $ million
Numbers will NOT add due to categorization
Power Block | $ million
Balance of Plant | $ million
CO2 Capture Equipment | $ million
Labor | $ million
Interconnects and Infrastructure | $ million
Owner's costs with Sales Tax and Land | $ million
Project Contingency | $ million
AEP Allocations | $ million
Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for the Project | $ million
Power Block | %
Balance of Plant | %
CO2 Capture Equipment | %
Labor | %
Interconnects and Infrastructure | %
Owner's costs with Sales Tax and Land | %
Project Contingency | %
AEP Allocations | %
Commercially Viable | Year
Start Construction | Year
Commercial Operation Date | Year
Graphs show % of costs for major items, NOT every item, without AEP allocations.
Shaded cells are not currently used.
Total All-in, As-spent, $/kW
Maximum across the worksheet = | 2807.1143
Average across the worksheet = | 2807.1143
Minimum across the worksheet = | 2807.1143
Risk/Insurance equipment + labor, $/kW =
Notes and Data Sources | Text

## IRP Pull Data 2020 East Bit
Pulls from Master Sheets. Will feed Stop Light Grid sheet eventually. |  | 3 | <- this is the tech resource number from EIA Table 1
CJB updated 2-10-2020 | Vendor Name | USC with 90% CCS | Check NEW Data Inputs from Summary worksheet to verify a specific EIA region Capital Cost
| Model | 650 MW high sulfur bituminous coal (approximately 4 MMBtu/hour SO2), ultra-supercritical, 90% CO2 capture US EIA
New Generation Technology Cost and Performance Estimates | Arrangement | 650 MW pulverized coal, 1 unit
| Number of (generating) Units | 1
Shaded cells are not currently used. | Nominal MW net, plant | 650
| CO2 Control % (up to 99.99%) | 90%
APCo, I&M, AEG, Kentucky Power, PSO, SWEPCO, AEP Generation Resources (AGR), BPCo (Buckeye), General | Location by Operating Company | General
Specific Location, if available | Text | None
PJM or SPP Regional Transmission Area? If neither, use None | Text - PJM, SPP, or None | PJM
Plant Configuration | Units / Inputs
Technology | Text | 650 MW high sulfur bituminous coal (approximately 4 MMBtu/hour SO2), ultra-supercritical, 90% CO2 capture US EIA
Black Start Capability, total MW (must type in number even if Zero) | MW | 0
Does Land need to be purchased? Typical responses: No = existing property; wind = Lease; solar = Yes | Text, Yes, No, or Lease | No
Is this a typical "build" project or asset purchase (build, own, transfer) upon completion? | Text, Build or Buy. For Energy Storage, use Build. | Build
Fuel Type | East Bit | East Bit
Fuel Characteristic | Text | Solid
Fuel Availability | Text | Firm
Fuel Price Stability | Text | Stable
Fuel Cost, $/mmBtu | $/mmBtu
Heating Value, Btu/lb HHV | Btu/Lb HHV
Annual Fuel Usage, equivalent million tons/year | Million Tons/yr
Annual Heat Input (not valid for all technologies, but used in calculations), mmBtu | Million Btu (mmBtu)
Total Fuel Costs, $/MW-hr | $/MW-hr
Total Fuel Costs, $ million per year | $ Million
General Plant Description | Text
Capacity
Standard ISO MW @ 1,000 ft. Gross | MW gross | 831
Parasitic Load, % | % | 21.78%
Standard ISO MW @1,000 feet, WITHOUT the steam turbine | Nominal MWac net | 650
Standard ISO MW @ 1,000 feet WITH steam turbine | MW | 650
Steam Turbine (used in calcs) MW | MW
Actual DC to AC ratio (default = 1.00) | Number
DC capacity for solar; for all others = Standard ISO at 1,000 ft, MWac | Nominal MWdc net, plant
Energy Storage Duration, hours | Hours
Energy Storage Capability, MW-hr, AC | MW-hr
Minimum MW net, either calculation or from vendor (aka Turn Down Capability) | MW net
Minimum, Turndown, % (minimum load with 1 machine for combustion turbines) | % | 25
Inlet Chilling Type for Combustion Turbines (See Notes page) | Text - None, Evaporative Cooler, or Chiller
Inlet Chilling Addition (check heat rate impact) MW | MW
Inlet Chilling Heat Rate Impact | Btu/kWh
Is Fuel Oil included? Yes or No (Not applicable to Fuel Oil Only units) | Text - Yes or No
Fuel Oil Capacity (check heat rate impact) MW | MW
Fuel Oil Heat Rate Impact | Btu/kWh
HRSG Capability, if Equipped, Unfired MW | MW
Duct Burners included ? Yes or No | Text - Yes or No
Duct Burners (included for all combined cycle HRSGs) MW | MW
Duct Burner Heat Rate Impact | Btu/kWh
Total Potential HRSG + Duct Firing Capability, MW | MW
Spare Row | 0
Spare Row | 0
Winter (30F) MW net without fuel oil + steam turbine | MW net | 685.75
Winter (30F) MW net + fuel oil (if fuel oil included) + steam turbine | MW net
Summer (90F) MW net by itself + steam turbine | MW net
Summer (90F) MW net + inlet cooling + duct firing + steam turbine | MW net | 630.5
Summer (90F) MW net without inlet cooling + duct firing + steam turbine | MW net
Summer (90F) MW net + inlet cooling without duct firing + steam turbine | MW net | 630.5
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. NO Steam Turbine Limit. | MW
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. May be steam turbine limited. USE THIS. | MW
Heat Rate (Higher Heating Value)
Full Load, HHV, net, with degradation (not applicable for all technologies, however, used in calculations) Btu/kW-hr | Btu/kWh
Full Load, HHV, net, with degradation and duct burner heat rate impact, Btu/kW-hr (if not combined cycle with duct burners, use the number above) | Btu/kWh
Full Load, HHV, net, with degradation and fuel oil (Winter) | Btu/kWh
Full Load, HHV, net, with degradation and inlet cooling, NO duct burners (Summer) | Btu/kWh | 12507
Full Load, HHV, net, with degradation, inlet cooling, and duct burner heat rate impact (Summer) | Btu/kWh | 12507
Full Load, HHV, net, with degradation and duct burners, NO inlet cooling heat rate impact | Btu/kWh
Full Load, HHV, net, with degradation, inlet cooling, power augmentation, HRSG, and duct firing. Does not include Fuel Oil Impact. | Btu/kWh | 12507
75% Load, Btu/kW-hr | Btu/kWh | #REF!
50% Load, Btu/kW-hr | Btu/kWh | #REF!
25% Load, Btu/kW-hr | Btu/kWh | #REF!
Average Annual (without duct burners), Btu/kW-hr | Btu/kWh
Estimated efficiency, HHV, full load, degraded, % | %
Energy Storage Roundtrip efficiency (82.67% is average) | %
Capacity Factor, %, for all but energy storage | %
Capacity Factor, %, for energy storage only | %
Annual Generation from Net Rating, MW-hr | MW-hr
Capital Cost, $/kW based on nominal MW | 2020
Asset Purchase Price (not typical build) | $/kW
Steam generator | $/kW
Gasifier | $/kW
Air Separator | $/kW
Steam, Combustion, or Wind Turbines | $/kW
Black Start / Coping Power Combustion Turbines | $/kW
Solar Modules/Panels | $/kW
Inverters | $/kW
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $/kW
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $/kW
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $/kW
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $/kW
Duct Burners | $/kW
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $/kW
Plant Water Treatment (Demin/RO system, tanks, piping) | $/kW
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $/kW
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $/kW
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $/kW
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $/kW
Misc. Pumps and Piping not otherwise included | $/kW
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $/kW
Balance of Plant, BOP (adds from below) | $/kW
IT, Telecomm, SCADA, Metering, Telemetry, Software | $/kW
Security (including cameras), Roads, and Fencing | $/kW
Control Room | $/kW
Other BOP, not otherwise classified | $/kW
Gas Compression | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Freight/Shipping, Importation Duty, Fees, and Taxes | $/kW
Construction Labor | $/kW
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | $/kW
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | $/kW
Owner's Project and Construction Mgmt | $/kW
Developer Margin and Overheads | $/kW
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $/kW
First of a kind and/or Plug Number | $/kW
SO2 Polishing (used with CO2 capture) | $/kW
(AEP) O&M Mobilization Fee for a Buy | $/kW
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | $/kW
Project Contingency for a Build | $/kW
Project Contingency for a Buy | $/kW
EPC Contractor's Fee | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Fee Subtotal for Build (not used in calculation) | $/kW
Fee Subtotal for Buy (not used in calculation) | $/kW
Total Plant Cost (Overnight EPC) for Build Option | $/kW
Asset Purchase = Buy | $/kW
Owner's Costs | $/kW
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | $/kW
Owner's Costs for a BUY project (excluding Land) | $/kW
Inventory Capital | $/kW
Development and Legal Fees | $/kW
Regulatory Support Fees | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUILD | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUY | $/kW
Interconnection Studies (e.g., Tom Fecho) | $/kW
Enviro and building permits for BUILD | $/kW
Enviro and building permits for BUY | $/kW
AEP-paid sales tax, based on location | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Initial catalyst and chemicals | $/kW
Land Costs (for Buying Land; if Lease = O&M cost) | $/kW
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $/kW
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $/kW
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $/kW
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $/kW
Total Interconnects and Infrastructure (adds from below) | $/kW
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $/kW
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $/kW
Water Supply (Intake) and Wastewater Treatment | $/kW
Site Infrastructure (includes railroad and barge access) | $/kW
Landfill development | $/kW
Initial fuel Inventory (30 days for solid or liquid fuels) | $/kW
Total Plant Cost + Owner's Cost + Interconnects for Build | $/kW
Transmission Upgrade - not currently used | $/kW
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $/kW
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $/kW
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $/kW
Capital Cost | 2020
Asset Purchase Price (not typical build) | $ million
Steam generator | $ million
Gasifier | $ million
Air Separator | $ million
Steam, Combustion, or Wind Turbines | $ million
Black Start / Coping Power Combustion Turbines | $ million
Solar Modules/Panels | $ million
Inverters | $ million
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $ million
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $ million
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $ million
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $ million
Duct Burners | $ million
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $ million
Plant Water Treatment (Demin/RO system, tanks, piping) | $ million
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $ million
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $ million
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $ million
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $ million
Misc. Pumps and Piping not otherwise included | $ million
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $ million
Balance of Plant, BOP (adds from below) | $ million
IT, Telecomm, SCADA, Metering, Telemetry, Software | $ million
Security (including cameras), Roads, and Fencing | $ million
Control Room | $ million
Other BOP, not otherwise classified | $ million
Gas Compression | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Freight/Shipping, Importation Duty, Fees, and Taxes | 3%
Construction Labor | $ million
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | 12%
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | 5%
Owner's Project and Construction Mgmt | 5%
Developer Margin and Overheads | $ million
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $ million
First of a kind and/or Plug Number | $ million
SO2 Polishing (used with CO2 capture) | $ million
(AEP) O&M Mobilization Fee for a Buy | $ million
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | 1.25%
Project Contingency for a Build | 10%
Project Contingency for a Buy | $ million
EPC Contractor's Fee | 8%
Spare row | 0%
Spare row | 0%
Spare row | 0%
Fee Subtotal for Build (not used in calculation) | $ million
Fee Subtotal for Buy (not used in calculation) | $ million
Total Plant Cost (Overnight EPC) for Build Option | $ million
Asset Purchase = Buy | $ million
Owner's Costs | 0
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | 5%
Owner's Costs for a BUY project (excluding Land) | $ million
Inventory Capital | 1%
Development and Legal Fees | 1.25%
Regulatory Support Fees | 1%
Civil Work (surveys, geotech, grading, site installation) for BUILD | $ million
Civil Work (surveys, geotech, grading, site installation) for BUY | $ million
Interconnection Studies (e.g., Tom Fecho) | $ million
Enviro and building permits for BUILD | $ million
Enviro and building permits for BUY | $ million
AEP-paid sales tax, based on location | $ million
Spare row - check formulas | 0
Spare row - check formulas | 0
Spare row - check formulas | 0
Initial catalyst and chemicals | $ million
Land Costs (for Buying Land; if Lease = O&M cost) | $ million
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $ million
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $ million
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $ million
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $ million
Total Interconnects and Infrastructure (adds from below) | $ million
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $ million
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $ million
Water Supply (Intake) and Wastewater Treatment | $ million
Site Infrastructure (includes railroad and barge access) | $ million
Landfill development | $ million
Initial fuel Inventory (30 days for solid or liquid fuels) | $ million
Total Plant Cost + Owner's Cost + Interconnects for Build | $ million
Total Plant Cost + Owner's Cost + Interconnects for Buy | $ million
Transmission Upgrade - not currently used | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUY (Included in EPC) | $ million
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $ million | 3959.3098 | Set Cell C9 in worksheet NEW Data Inputs from Summary to EIA region for specific costs
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $ million
Financial
AFUDC | $ million
Total Project Duration | months
AFUDC %, by operating company or equivalent, avg. annual rate | %
Financial Risk | Text (Low, Average, High)
Investment Life, years | Years (choose from 2, 3, 4, 5, 10, 15, 20, 25, 30, 33, 40, or 50 years) | 40
Economic Cost of Capital (AEP carrying cost, used in annual capital cost), % | %
Overhead / Allocation Rate for AEP operating company, % | %
Annual Capital Cost, $ million for Build | $ million
Annual Capital Cost, $ million for Buy | $ million
Capital Cost $/kW - year for Build | $/kW-year
Capital Cost $/kW - year for Buy | $/kW-year
Total Capital Costs, $/MW-hr | $/MW-hr
Operations & Maintenance (O&M)
Duty Cycle | Text
Capacity Factor | %
Annual Generation | MW-hr
Generating Facility Staff | Number (if part-time, use decimal)
Fixed O&M Costs
Fixed O&M as an EPRI/resource planning calculation, $/kW-year | $/kW-year | 60.6984
Fixed O&M (adds from below), $ million | $ million
Plant Staff Payroll | $ million
General & Administrative Overheads (20% of Payroll) | $ million
Routine Maintenance, typically 1% of major equipment costs or input | $ million
Non-Natural Gas units Major Maintenance = 50% of the Variable O&M Major Maint. (per Resource Planning) | $ million
Utility (aux power and water) costs | $ million
Environmental and safety (monitoring, waste removal, etc.) | $ million
Buildings/grounds, SCADA, Communications, Software licensing, Other | $ million
Maint Expenses Not Otherwise Classified (Asset Management, collection system, substation work, wind turbine blade repairs, solar panel washing, energy storage potential cell upgrades, fuel cell stack replacement, misc. maint.) | $ million
O&M Service Agreement by 3rd party | $ million
Forecasting Services (hydro, wind, and solar) | $ million
Extended Warranties, per year | $ million
Land Lease Costs (not land purchase) | $ million
Natural Gas Major Maint. according to Resource Planning, using EPRI numbers. Calcs from below. | $ million
Property, Tax, and Insurance sum, $/MW-hr | $/MW-hr
Fixed O&M - $/MW-hr | $/MW-hr
Variable O&M Costs
Variable O&M (sums from below), $/MW-hr | $/MW-hr | 11.1936
Consumables and Reagents | $/MW-hr
Major Maintenance = the other 50% of Variable O&M (per Resource Planning). | $/MW-hr
Variable O&M, $ million/year | $ million/yr
EPRI CO2 Capture and Storage Variable O&M, $ million/year, INCREMENTAL | $ million/yr
Total Variable O&M, $ million/year | $ million/year
Total Fixed & Variable O&M, $ million/year | $ million/yr
Total Fixed & Variable O&M, $/MW-hr | $/MW-hr
Production cost (Fuel + VOM) | $/MW-hr
Environmental
Water Usage, gpm | gallons / minute / unit, gpm
Water Usage, gal/year | gallons / year, total plant
Water Usage, gal/MW-hr | gal/MW-hr
* Some data are input, some are calculations. * | Check each emissions line
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
NOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
SOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Hg, Uncontrolled at exhaust, lb/TBtu | lb/TBtu
CO, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
CO2, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, ppm | ppm
NOx, Uncontrolled at exhaust, ppm | ppm
SOx, Uncontrolled at exhaust, ppm | ppm
Hg, Uncontrolled at exhaust, ppm | ppm
CO, Uncontrolled at exhaust, ppm | ppm
CO2, Uncontrolled at exhaust, ppm | ppm
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/hour | lb/hour
NOx, Uncontrolled at exhaust, lb/hour | lb/hour
SOx, Uncontrolled at exhaust, lb/hour | lb/hour
Hg, Uncontrolled at exhaust, lb/hour | lb/hour
CO, Uncontrolled at exhaust, lb/hour | lb/hour
CO2, Uncontrolled at exhaust, lb/hour | lb/hour
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/mmBtu | lb/mmBtu
NOx, Controlled, lb/mmBtu | lb/mmBtu | 0.06
SOx, Controlled, lb/mmBtu | lb/mmBtu | 0.09
Hg, Controlled, lb/TBtu | lb/Tbtu
CO, Controlled, lb/mmBtu | lb/mmBtu
CO2, Controlled, lb/mmBtu | lb/mmBtu | 20.6
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, ppm | ppm
NOx, Controlled, ppm | ppm
SOx, Controlled, ppm | ppm
Hg, Controlled, ppm | ppm
CO, Controlled, ppm | ppm
CO2, Controlled, ppm | ppm
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/MW-hr | lb/MW-hr
NOx, Controlled, lb/MW-hr | lb/MW-hr
SOx, Controlled, lb/MW-hr | lb/MW-hr
Hg, Controlled, lb/MW-hr | lb/MW-hr
CO, Controlled, lb/MW-hr | lb/MW-hr
CO2, Controlled, lb/MW-hr | lb/MW-hr
Control Efficiency Needed to meet Expected Permit Limit
Particulate Matter PM10 Control Efficiency % | %
NOx Control Efficiency % | %
SOx Control Efficiency % | %
Hg Control Efficiency % | %
CO Control Efficiency % | %
CO2 Control Efficiency % | %
Annual Emission Rate, Controlled
Particulate Matter PM10, Annual Emission Rate, Tons/year | Tons/yr
NOx, Annual Emission Rate, Tons/year | Tons/yr
SOx, Annual Emission Rate, Tons/year | Tons/yr
Hg, Annual Emission Rate, lb/year | lb/yr
CO, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Metric Tonnes/year | Tonnes/yr
Annual Captured Rate (what does not get emitted)
Particulate Matter PM10, Annual Captured Rate, Tons/year | Tons/yr
NOx, Annual Captured Rate, Tons/year | Tons/yr
SOx, Annual Captured Rate, Tons/year | Tons/yr
Hg, Annual Captured Rate, lb/year | lb/yr
CO, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Metric Tonnes/year | Tonnes/yr
Emission Fees (Title V)
Particulate Matter PM10 Emission Fee, $/Ton | $/Ton
NOx Emission Fee, $/Ton | $/Ton
SOx Emission Fee, $/Ton | $/Ton
Hg Emission Fee, $/lb | $/lb
CO Emission Fee, $/Ton | $/Ton
CO2 Emission Fee, $/Ton | $/Ton
Annual Emission Cost
Particulate Matter PM10 Annual Emission Cost, $ million | $ million
NOx Annual Emission Cost, $ million | $ million
SOx Annual Emission Cost, $ million | $ million
Hg Annual Emission Cost, $ million | $ million
CO Annual Emission Cost, $ million | $ million
CO2 Annual Emission Cost, $ million | $ million
Total Emission Cost $ million | $ million
Total Emission Cost, $/MW-hr | $/MW-hr
Energy Storage Capital Cost, Simple $ / kW-hr | $/kW-hr
Levelized Cost of Storage Capital, $/MW-hr | $/MW-hr
Levelized Cost of Storage Fuel, $/MW-hr | $/MW-hr
Levelized Cost of Storage O&M, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/kW-hr | $/kW-hr
Emissions, $/MW-hr | $/MW-hr
LCOS, Total with Emissions, $/MW-hr | $/MW-hr
First Year Cost of Electricity COE WITHOUT Incentives or Subsidies. NOT applicable to energy storage.
Capital, $/MW-hr | $/MW-hr
Fuel, $/MW-hr | $/MW-hr
O&M, $/MW-hr | $/MW-hr
Total without Emissions, $/MW-hr | $/MW-hr
Emissions, $/MW-hr | $/MW-hr
Total with Emissions, $/MW-hr | $/MW-hr
Transportation and Storage Cost of CO2, $/Tonne | $ / Tonne
Annual Cost of CO2 Transportation and Storage, $ million | $ million
Annual Cost of CO2 Transportation and Storage, $/MW-hr | $/MW-hr
Total Cost of Electricity, with Emissions and CO2, $/MW-hr (NOT applicable to energy storage) | $/MW-hr
Energy Storage Cycles over 1 year | Number
Energy Storage Depth of Discharge, % (80% is typical) | Number
Scheduled / Planned Outage Factor % | %
Planned Outage Hours | Hours
Planned Outage Days | Days
Forced Outage Factor % | % | 5.4% | used value fro Column D
Forced Outage Avg. Duration | Hours
Availability Factor % | %
Equivalent Availability Factor % | %
Typical Ramp Rate | MW / minute
Down Time (Minimum hrs) | Hours
Run Time (Minimum hrs) | Hours
Construction
Type of Site | Text
Footprint Needed, minimum acres | Acres
Required Gas Pressure, psig | psig
Commercial Availability, years | Years
Permit, License, and Design, years | Years
EPC (Engineer, Procure, Construct), years | Years
Total Project Duration, years | Years
Construction Cash Flow (%) -Yr 1 | % | 5%
Yr 2 | % | 5%
Yr 3 | % | 25%
Yr 4 | % | 35%
Yr 5 | % | 30%
Total | %
Total, All-in US$ 2020 for this Project | $ / kW
Escalation | $ / kW
Total, All-in As-Spent $US | $ / kW
Total, All-in US$ 2020 for this Project | $ million
Escalation | $ million
Total, All-in As-Spent $US | $ million
Numbers will NOT add due to categorization
Power Block | $ million
Balance of Plant | $ million
CO2 Capture Equipment | $ million
Labor | $ million
Interconnects and Infrastructure | $ million
Owner's costs with Sales Tax and Land | $ million
Project Contingency | $ million
AEP Allocations | $ million
Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for the Project | $ million
Power Block | %
Balance of Plant | %
CO2 Capture Equipment | %
Labor | %
Interconnects and Infrastructure | %
Owner's costs with Sales Tax and Land | %
Project Contingency | %
AEP Allocations | %
Commercially Viable | Year
Start Construction | Year
Commercial Operation Date | Year
Notes and Data Sources | Text
Note on C31: S&L/EIA report describes 181MW loss from Gross Output
Note on C290: Slight Rounding error: BASE Cost in EIA report is $3,819,201M EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C314: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C333: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C337: s232253: missing ?

## IRP Pull Data 20 Comb Cycle
Pulls from Master Sheets. Will feed Stop Light Grid sheet eventually. |  | 9 | 7 | 8
CJB updated 3-6-2020 with Tom McCartney Thermoflow data, aep costs, PJM CONE labor. Discussion with IRP people. | Vendor Name | CC with 90% CCS | CC – multi shaft | CC – single shaft
| Model | Case 9, Combustion Turbine H-Class, 1 x 1 x 1 combined cycle, single shaft, with 90% CO2 capture. No duct firing. | S&L Case 7, COMBUSTION TURBINE H CLASS, 1100-MW COMBINED CYCLE | S&L Case 8, COMBUSTION TURBINE H CLASS, COMBINED-CYCLE SINGLE SHAFT, 430 MW
New Generation Technology Cost and Performance Estimates | Arrangement | 1 x 1 x 1 |  |  |  | 49
| Number of (generating) Units | 1
Shaded cells are not currently used. | Nominal MW net, plant | 377 | 1083 | 418 | Base value without adjusting for location
CO2 Control % (up to 99.99%)
APCo, I&M, AEG, Kentucky Power, PSO, SWEPCO, AEP Generation Resources (AGR), BPCo (Buckeye), General | Location by Operating Company
Specific Location, if available | Text
PJM or SPP Regional Transmission Area? If neither, use None | Text - PJM, SPP, or None
Plant Configuration | Units / Inputs
Technology | Text
Black Start Capability, total MW (must type in number even if Zero) | MW |  | 0 | 0
Does Land need to be purchased? Typical responses: No = existing property; wind = Lease; solar = Yes | Text, Yes, No, or Lease | Yes | Yes | Yes
Is this a typical "build" project or asset purchase (build, own, transfer) upon completion? | Text, Build or Buy. For Energy Storage, use Build. | Build | Build | Build
Fuel Type | Natural Gas CT | Natural Gas CT | Natural Gas CT | Natural Gas CT
Fuel Characteristic | Text | Gas | Gas | Gas
Fuel Availability | Text
Fuel Price Stability | Text
Fuel Cost, $/mmBtu | $/mmBtu
Heating Value, Btu/lb HHV | Btu/Lb HHV
Annual Fuel Usage, equivalent million tons/year | Million Tons/yr
Annual Heat Input (not valid for all technologies, but used in calculations), mmBtu | Million Btu (mmBtu)
Total Fuel Costs, $/MW-hr | $/MW-hr
Total Fuel Costs, $ million per year | $ Million
General Plant Description | Text
Capacity
Standard ISO MW @ 1,000 ft. Gross | MW gross | 297.1685
Parasitic Load, % | % | 10.82%
Standard ISO MW @1,000 feet, WITHOUT the steam turbine | Nominal MWac net | 265
Standard ISO MW @ 1,000 feet WITH steam turbine | MW | 374.361 | 1075.419 | 415.074 | Location adjusted value
Steam Turbine (used in calcs) MW | MW
Actual DC to AC ratio (default = 1.00) | Number
DC capacity for solar; for all others = Standard ISO at 1,000 ft, MWac | Nominal MWdc net, plant
Energy Storage Duration, hours | Hours
Energy Storage Capability, MW-hr, AC | MW-hr
Minimum MW net, either calculation or from vendor (aka Turn Down Capability) | MW net
Minimum, Turndown, % (minimum load with 1 machine for combustion turbines) | % | 20
Inlet Chilling Type for Combustion Turbines (See Notes page) | Text - None, Evaporative Cooler, or Chiller
Inlet Chilling Addition (check heat rate impact) MW | MW
Inlet Chilling Heat Rate Impact | Btu/kWh
Is Fuel Oil included? Yes or No (Not applicable to Fuel Oil Only units) | Text - Yes or No
Fuel Oil Capacity (check heat rate impact) MW | MW
Fuel Oil Heat Rate Impact | Btu/kWh
HRSG Capability, if Equipped, Unfired MW | MW
Duct Burners included ? Yes or No | Text - Yes or No
Duct Burners (included for all combined cycle HRSGs) MW | MW |  | 0 | 0
Duct Burner Heat Rate Impact | Btu/kWh
Total Potential HRSG + Duct Firing Capability, MW | MW
Spare Row | 0
Spare Row | 0
Winter (30F) MW net without fuel oil + steam turbine | MW net | 387.0039 | 1111.7381 | 429.0919
Winter (30F) MW net + fuel oil (if fuel oil included) + steam turbine | MW net | 391.575
Summer (90F) MW net by itself + steam turbine | MW net | 369.05
Summer (90F) MW net + inlet cooling + duct firing + steam turbine | MW net | 367.4418 | 1055.5424 | 407.4023
Summer (90F) MW net without inlet cooling + duct firing + steam turbine | MW net | 369.05
Summer (90F) MW net + inlet cooling without duct firing + steam turbine | MW net | 367.4418 | 1055.5424 | 407.4023
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. NO Steam Turbine Limit. | MW
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. May be steam turbine limited. USE THIS. | MW
Heat Rate (Higher Heating Value)
Full Load, HHV, net, with degradation (not applicable for all technologies, however, used in calculations) Btu/kW-hr | Btu/kWh
Full Load, HHV, net, with degradation and duct burner heat rate impact, Btu/kW-hr (if not combined cycle with duct burners, use the number above) | Btu/kWh
Full Load, HHV, net, with degradation and fuel oil (Winter) | Btu/kWh
Full Load, HHV, net, with degradation and inlet cooling, NO duct burners (Summer) | Btu/kWh | 7116.876 | 6363.63 | 6424.569 | Set Cell C9 in worksheet NEW Data Inputs from Summary to EIA region for specific regional HR
Full Load, HHV, net, with degradation, inlet cooling, and duct burner heat rate impact (Summer) | Btu/kWh | 7116.876 | 6363.63 | 6424.569
Full Load, HHV, net, with degradation and duct burners, NO inlet cooling heat rate impact | Btu/kWh | 7116.876 | 6363.63 | 6424.569
Full Load, HHV, net, with degradation, inlet cooling, power augmentation, HRSG, and duct firing. Does not include Fuel Oil Impact. | Btu/kWh | 7116.876 | 6363.63 | 6424.569
75% Load, Btu/kW-hr | Btu/kWh | 7275.0288 | 6505.044 | 6567.3372
50% Load, Btu/kW-hr | Btu/kWh | 8366.2831 | 7480.8006 | 7552.4378
25% Load, Btu/kW-hr | Btu/kWh | 9411.2319 | 8415.1526 | 8495.7373
Average Annual (without duct burners), Btu/kW-hr | Btu/kWh | 7216.612
Estimated efficiency, HHV, full load, degraded, % | %
Energy Storage Roundtrip efficiency (82.67% is average) | %
Capacity Factor, %, for all but energy storage | %
Capacity Factor, %, for energy storage only | %
Annual Generation from Net Rating, MW-hr | MW-hr
Capital Cost, $/kW based on nominal MW | 2020
Asset Purchase Price (not typical build) | $/kW
Steam generator | $/kW
Gasifier | $/kW
Air Separator | $/kW
Steam, Combustion, or Wind Turbines | $/kW
Black Start / Coping Power Combustion Turbines | $/kW
Solar Modules/Panels | $/kW
Inverters | $/kW
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $/kW
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $/kW
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $/kW
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $/kW
Duct Burners | $/kW
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $/kW
Plant Water Treatment (Demin/RO system, tanks, piping) | $/kW
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $/kW
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $/kW
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $/kW
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $/kW
Misc. Pumps and Piping not otherwise included | $/kW
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $/kW
Balance of Plant, BOP (adds from below) | $/kW
IT, Telecomm, SCADA, Metering, Telemetry, Software | $/kW
Security (including cameras), Roads, and Fencing | $/kW
Control Room | $/kW
Other BOP, not otherwise classified | $/kW
Gas Compression | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Freight/Shipping, Importation Duty, Fees, and Taxes | $/kW
Construction Labor | $/kW
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | $/kW
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | $/kW
Owner's Project and Construction Mgmt | $/kW
Developer Margin and Overheads | $/kW
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $/kW
First of a kind and/or Plug Number | $/kW
SO2 Polishing (used with CO2 capture) | $/kW
(AEP) O&M Mobilization Fee for a Buy | $/kW
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | $/kW
Project Contingency for a Build | $/kW
Project Contingency for a Buy | $/kW
EPC Contractor's Fee | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Fee Subtotal for Build (not used in calculation) | $/kW
Fee Subtotal for Buy (not used in calculation) | $/kW
Total Plant Cost (Overnight EPC) for Build Option | $/kW
Asset Purchase = Buy | $/kW
Owner's Costs | $/kW
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | $/kW
Owner's Costs for a BUY project (excluding Land) | $/kW
Inventory Capital | $/kW
Development and Legal Fees | $/kW
Regulatory Support Fees | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUILD | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUY | $/kW
Interconnection Studies (e.g., Tom Fecho) | $/kW
Enviro and building permits for BUILD | $/kW
Enviro and building permits for BUY | $/kW
AEP-paid sales tax, based on location | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Initial catalyst and chemicals | $/kW
Land Costs (for Buying Land; if Lease = O&M cost) | $/kW
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $/kW
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $/kW
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $/kW
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $/kW
Total Interconnects and Infrastructure (adds from below) | $/kW
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $/kW
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $/kW
Water Supply (Intake) and Wastewater Treatment | $/kW
Site Infrastructure (includes railroad and barge access) | $/kW
Landfill development | $/kW
Initial fuel Inventory (30 days for solid or liquid fuels) | $/kW
Total Plant Cost + Owner's Cost + Interconnects for Build | $/kW
Transmission Upgrade - not currently used | $/kW
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $/kW
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $/kW
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $/kW
Capital Cost | 2020
Asset Purchase Price (not typical build) | $ million
Steam generator | $ million
Gasifier | $ million
Air Separator | $ million
Steam, Combustion, or Wind Turbines | $ million
Black Start / Coping Power Combustion Turbines | $ million
Solar Modules/Panels | $ million
Inverters | $ million
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $ million
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $ million
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $ million
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $ million
Duct Burners | $ million
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $ million
Plant Water Treatment (Demin/RO system, tanks, piping) | $ million
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $ million
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $ million
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $ million
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $ million
Misc. Pumps and Piping not otherwise included | $ million
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $ million
Balance of Plant, BOP (adds from below) | $ million
IT, Telecomm, SCADA, Metering, Telemetry, Software | $ million
Security (including cameras), Roads, and Fencing | $ million
Control Room | $ million
Other BOP, not otherwise classified | $ million
Gas Compression | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Freight/Shipping, Importation Duty, Fees, and Taxes | 3%
Construction Labor | $ million
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | 12%
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | 5%
Owner's Project and Construction Mgmt | 5%
Developer Margin and Overheads | $ million
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $ million
First of a kind and/or Plug Number | $ million
SO2 Polishing (used with CO2 capture) | $ million
(AEP) O&M Mobilization Fee for a Buy | $ million
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | 1.25%
Project Contingency for a Build | 10%
Project Contingency for a Buy | $ million
EPC Contractor's Fee | 8%
Spare row | 0%
Spare row | 0%
Spare row | 0%
Fee Subtotal for Build (not used in calculation) | $ million
Fee Subtotal for Buy (not used in calculation) | $ million
Total Plant Cost (Overnight EPC) for Build Option | $ million
Asset Purchase = Buy | $ million
Owner's Costs | 0
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | 5%
Owner's Costs for a BUY project (excluding Land) | $ million
Inventory Capital | 1%
Development and Legal Fees | 1.25%
Regulatory Support Fees | 1%
Civil Work (surveys, geotech, grading, site installation) for BUILD | $ million
Civil Work (surveys, geotech, grading, site installation) for BUY | $ million
Interconnection Studies (e.g., Tom Fecho) | $ million
Enviro and building permits for BUILD | $ million
Enviro and building permits for BUY | $ million
AEP-paid sales tax, based on location | $ million
Spare row - check formulas | 0
Spare row - check formulas | 0
Spare row - check formulas | 0
Initial catalyst and chemicals | $ million
Land Costs (for Buying Land; if Lease = O&M cost) | $ million
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $ million
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $ million
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $ million
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $ million
Total Interconnects and Infrastructure (adds from below) | $ million
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $ million
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $ million
Water Supply (Intake) and Wastewater Treatment | $ million
Site Infrastructure (includes railroad and barge access) | $ million
Landfill development | $ million
Initial fuel Inventory (30 days for solid or liquid fuels) | $ million
Total Plant Cost + Owner's Cost + Interconnects for Build | $ million
Total Plant Cost + Owner's Cost + Interconnects for Buy | $ million
Transmission Upgrade - not currently used | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUY (Included in EPC) | $ million
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $ million | 956.2247 | 1027.8893 | 458.0923 | Set Cell C9 in worksheet NEW Data Inputs from Summary to EIA region for specific costs
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $ million
Financial
AFUDC | $ million
Total Project Duration | months
AFUDC %, by operating company or equivalent, avg. annual rate | %
Financial Risk | Text (Low, Average, High)
Investment Life, years | Years (choose from 2, 3, 4, 5, 10, 15, 20, 25, 30, 33, 40, or 50 years) | 40 | 40 | 25
Economic Cost of Capital (AEP carrying cost, used in annual capital cost), % | %
Overhead / Allocation Rate for AEP operating company, % | %
Annual Capital Cost, $ million for Build | $ million
Annual Capital Cost, $ million for Buy | $ million
Capital Cost $/kW - year for Build | $/kW-year
Capital Cost $/kW - year for Buy | $/kW-year
Total Capital Costs, $/MW-hr | $/MW-hr
Operations & Maintenance (O&M)
Duty Cycle | Text
Capacity Factor | %
Annual Generation | MW-hr
Generating Facility Staff | Number (if part-time, use decimal)
Fixed O&M Costs
Fixed O&M as an EPRI/resource planning calculation, $/kW-year | $/kW-year | 28.137 | 12.4374 | 14.3743
Fixed O&M (adds from below), $ million | $ million
Plant Staff Payroll | $ million
General & Administrative Overheads (20% of Payroll) | $ million
Routine Maintenance, typically 1% of major equipment costs or input | $ million
Non-Natural Gas units Major Maintenance = 50% of the Variable O&M Major Maint. (per Resource Planning) | $ million
Utility (aux power and water) costs | $ million
Environmental and safety (monitoring, waste removal, etc.) | $ million
Buildings/grounds, SCADA, Communications, Software licensing, Other | $ million
Maint Expenses Not Otherwise Classified (Asset Management, collection system, substation work, wind turbine blade repairs, solar panel washing, energy storage potential cell upgrades, fuel cell stack replacement, misc. maint.) | $ million
O&M Service Agreement by 3rd party | $ million
Forecasting Services (hydro, wind, and solar) | $ million
Extended Warranties, per year | $ million
Land Lease Costs (not land purchase) | $ million
Natural Gas Major Maint. according to Resource Planning, using EPRI numbers. Calcs from below. | $ million
Property, Tax, and Insurance sum, $/MW-hr | $/MW-hr
Fixed O&M - $/MW-hr | $/MW-hr
Variable O&M Costs
Variable O&M (sums from below), $/MW-hr | $/MW-hr | 5.9536 | 1.9064 | 2.5996
Consumables and Reagents | $/MW-hr
Major Maintenance = the other 50% of Variable O&M (per Resource Planning). | $/MW-hr
Variable O&M, $ million/year | $ million/yr
EPRI CO2 Capture and Storage Variable O&M, $ million/year, INCREMENTAL | $ million/yr
Total Variable O&M, $ million/year | $ million/year
Total Fixed & Variable O&M, $ million/year | $ million/yr
Total Fixed & Variable O&M, $/MW-hr | $/MW-hr
Production cost (Fuel + VOM) | $/MW-hr
Environmental
Water Usage, gpm | gallons / minute / unit, gpm
Water Usage, gal/year | gallons / year, total plant
Water Usage, gal/MW-hr | gal/MW-hr
* Some data are input, some are calculations. * | Check each emissions line
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
NOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
SOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Hg, Uncontrolled at exhaust, lb/TBtu | lb/TBtu
CO, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
CO2, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, ppm | ppm
NOx, Uncontrolled at exhaust, ppm | ppm
SOx, Uncontrolled at exhaust, ppm | ppm
Hg, Uncontrolled at exhaust, ppm | ppm
CO, Uncontrolled at exhaust, ppm | ppm
CO2, Uncontrolled at exhaust, ppm | ppm
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/hour | lb/hour
NOx, Uncontrolled at exhaust, lb/hour | lb/hour
SOx, Uncontrolled at exhaust, lb/hour | lb/hour
Hg, Uncontrolled at exhaust, lb/hour | lb/hour
CO, Uncontrolled at exhaust, lb/hour | lb/hour
CO2, Uncontrolled at exhaust, lb/hour | lb/hour
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/mmBtu | lb/mmBtu
NOx, Controlled, lb/mmBtu | lb/mmBtu | 0.0075 | 0.0075 | 0.0075
SOx, Controlled, lb/mmBtu | lb/mmBtu | 0 | 0.001 | 0
Hg, Controlled, lb/TBtu | lb/Tbtu
CO, Controlled, lb/mmBtu | lb/mmBtu
CO2, Controlled, lb/mmBtu | lb/mmBtu | 12 | 117 | 117
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, ppm | ppm
NOx, Controlled, ppm | ppm
SOx, Controlled, ppm | ppm
Hg, Controlled, ppm | ppm
CO, Controlled, ppm | ppm
CO2, Controlled, ppm | ppm
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/MW-hr | lb/MW-hr
NOx, Controlled, lb/MW-hr | lb/MW-hr
SOx, Controlled, lb/MW-hr | lb/MW-hr
Hg, Controlled, lb/MW-hr | lb/MW-hr
CO, Controlled, lb/MW-hr | lb/MW-hr
CO2, Controlled, lb/MW-hr | lb/MW-hr
Control Efficiency Needed to meet Expected Permit Limit
Particulate Matter PM10 Control Efficiency % | %
NOx Control Efficiency % | %
SOx Control Efficiency % | %
Hg Control Efficiency % | %
CO Control Efficiency % | %
CO2 Control Efficiency % | %
Annual Emission Rate, Controlled
Particulate Matter PM10, Annual Emission Rate, Tons/year | Tons/yr
NOx, Annual Emission Rate, Tons/year | Tons/yr
SOx, Annual Emission Rate, Tons/year | Tons/yr
Hg, Annual Emission Rate, lb/year | lb/yr
CO, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Metric Tonnes/year | Tonnes/yr
Annual Captured Rate (what does not get emitted)
Particulate Matter PM10, Annual Captured Rate, Tons/year | Tons/yr
NOx, Annual Captured Rate, Tons/year | Tons/yr
SOx, Annual Captured Rate, Tons/year | Tons/yr
Hg, Annual Captured Rate, lb/year | lb/yr
CO, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Metric Tonnes/year | Tonnes/yr
Emission Fees (Title V)
Particulate Matter PM10 Emission Fee, $/Ton | $/Ton
NOx Emission Fee, $/Ton | $/Ton
SOx Emission Fee, $/Ton | $/Ton
Hg Emission Fee, $/lb | $/lb
CO Emission Fee, $/Ton | $/Ton
CO2 Emission Fee, $/Ton | $/Ton
Annual Emission Cost
Particulate Matter PM10 Annual Emission Cost, $ million | $ million
NOx Annual Emission Cost, $ million | $ million
SOx Annual Emission Cost, $ million | $ million
Hg Annual Emission Cost, $ million | $ million
CO Annual Emission Cost, $ million | $ million
CO2 Annual Emission Cost, $ million | $ million
Total Emission Cost $ million | $ million
Total Emission Cost, $/MW-hr | $/MW-hr
Energy Storage Capital Cost, Simple $ / kW-hr | $/kW-hr
Levelized Cost of Storage Capital, $/MW-hr | $/MW-hr
Levelized Cost of Storage Fuel, $/MW-hr | $/MW-hr
Levelized Cost of Storage O&M, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/kW-hr | $/kW-hr
Emissions, $/MW-hr | $/MW-hr
LCOS, Total with Emissions, $/MW-hr | $/MW-hr
First Year Cost of Electricity COE WITHOUT Incentives or Subsidies. NOT applicable to energy storage.
Capital, $/MW-hr | $/MW-hr
Fuel, $/MW-hr | $/MW-hr
O&M, $/MW-hr | $/MW-hr
Total without Emissions, $/MW-hr | $/MW-hr
Emissions, $/MW-hr | $/MW-hr
Total with Emissions, $/MW-hr | $/MW-hr
Transportation and Storage Cost of CO2, $/Tonne | $ / Tonne
Annual Cost of CO2 Transportation and Storage, $ million | $ million
Annual Cost of CO2 Transportation and Storage, $/MW-hr | $/MW-hr
Total Cost of Electricity, with Emissions and CO2, $/MW-hr (NOT applicable to energy storage) | $/MW-hr
Energy Storage Cycles over 1 year | Number
Energy Storage Depth of Discharge, % (80% is typical) | Number
Scheduled / Planned Outage Factor % | %
Planned Outage Hours | Hours
Planned Outage Days | Days
Forced Outage Factor % | % | 5% | 5% | 5%
Forced Outage Avg. Duration | Hours
Availability Factor % | %
Equivalent Availability Factor % | %
Typical Ramp Rate | MW / minute
Down Time (Minimum hrs) | Hours
Run Time (Minimum hrs) | Hours
Construction
Type of Site | Text
Footprint Needed, minimum acres | Acres
Required Gas Pressure, psig | psig
Commercial Availability, years | Years
Permit, License, and Design, years | Years
EPC (Engineer, Procure, Construct), years | Years
Total Project Duration, years | Years
Construction Cash Flow (%) -Yr 1 | % | 10% | 10% | 10%
Yr 2 | % | 20% | 35% | 35%
Yr 3 | % | 30% | 35% | 35%
Yr 4 | % | 30% | 20% | 20%
Yr 5 | % | 10% | 0% | 0%
Total | %
Total, All-in US$ 2020 for this Project | $ / kW
Escalation | $ / kW
Total, All-in As-Spent $US | $ / kW
Total, All-in US$ 2020 for this Project | $ million
Escalation | $ million
Total, All-in As-Spent $US | $ million
Numbers will NOT add due to categorization
Power Block | $ million
Balance of Plant | $ million
CO2 Capture Equipment | $ million
Labor | $ million
Interconnects and Infrastructure | $ million
Owner's costs with Sales Tax and Land | $ million
Project Contingency | $ million
AEP Allocations | $ million
Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for the Project | $ million
Power Block | %
Balance of Plant | %
CO2 Capture Equipment | %
Labor | %
Interconnects and Infrastructure | %
Owner's costs with Sales Tax and Land | %
Project Contingency | %
AEP Allocations | %
Commercially Viable | Year
Start Construction | Year
Commercial Operation Date | Year
Notes and Data Sources | Text
Note on C290: Slight Rounding error: BASE Cost in EIA report is $935,262.6M EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on D290: Slight Rounding error: BASE Cost in EIA report is $1,037.939M EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on E290: Slight Rounding error: BASE Cost in EIA report is $453.237M EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C314: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on D314: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on E314: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C333: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on D333: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on E333: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C480: 54 Month Project 24M Development, permitting, Engineering 30M Plant Construciton
Note on D480: 42 Month construction: 18M Dev, Permit, Engineer 24M Plant Construction
Note on E480: 40 Month construction: 18M Dev, Permit, Engineer 22M Plant Construction

## IRP Pull Data 2020 Simple CHP
Pulls from Master Sheets. Will feed Stop Light Grid sheet eventually. |  | 6 | 5
CJB updated 3-6-2020 | Vendor Name | CT – industrial frame | CT – aeroderivative
| Model | S&L Case 6, COMBUSTION TURBINE F CLASS, 240-MW SIMPLE CYCLE | S&L Case 5, COMBUSTION TURBINES AERODERIVATIVE, 100-MW SIMPLE CYCLE
New Generation Technology Cost and Performance Estimates | Arrangement
Number of (generating) Units
Shaded cells are not currently used. | Nominal MW net, plant | 233 | 105
CO2 Control % (up to 99.99%)
APCo, I&M, AEG, Kentucky Power, PSO, SWEPCO, AEP Generation Resources (AGR), BPCo (Buckeye), General | Location by Operating Company
Specific Location, if available | Text
PJM or SPP Regional Transmission Area? If neither, use None | Text - PJM, SPP, or None
Plant Configuration | Units / Inputs
Technology | Text | 1 | 1
Black Start Capability, total MW (must type in number even if Zero) | MW | 0 | 0
Does Land need to be purchased? Typical responses: No = existing property; wind = Lease; solar = Yes | Text, Yes, No, or Lease | Yes | Yes
Is this a typical "build" project or asset purchase (build, own, transfer) upon completion? | Text, Build or Buy. For Energy Storage, use Build. | Build | Build
Fuel Type | Natural Gas CT | Natural Gas CT | Natural Gas CT
Fuel Characteristic | Text | Gas | Gas
Fuel Availability | Text
Fuel Price Stability | Text
Fuel Cost, $/mmBtu | $/mmBtu
Heating Value, Btu/lb HHV | Btu/Lb HHV
Annual Fuel Usage, equivalent million tons/year | Million Tons/yr
Annual Heat Input (not valid for all technologies, but used in calculations), mmBtu | Million Btu (mmBtu)
Total Fuel Costs, $/MW-hr | $/MW-hr
Total Fuel Costs, $ million per year | $ Million
General Plant Description | Text
Capacity
Standard ISO MW @ 1,000 ft. Gross | MW gross
Parasitic Load, % | %
Standard ISO MW @1,000 feet, WITHOUT the steam turbine | Nominal MWac net
Standard ISO MW @ 1,000 feet WITH steam turbine | MW | 232.767 | 104.895
Steam Turbine (used in calcs) MW | MW
Actual DC to AC ratio (default = 1.00) | Number
DC capacity for solar; for all others = Standard ISO at 1,000 ft, MWac | Nominal MWdc net, plant
Energy Storage Duration, hours | Hours
Energy Storage Capability, MW-hr, AC | MW-hr
Minimum MW net, either calculation or from vendor (aka Turn Down Capability) | MW net
Minimum, Turndown, % (minimum load with 1 machine for combustion turbines) | %
Inlet Chilling Type for Combustion Turbines (See Notes page) | Text - None, Evaporative Cooler, or Chiller
Inlet Chilling Addition (check heat rate impact) MW | MW
Inlet Chilling Heat Rate Impact | Btu/kWh
Is Fuel Oil included? Yes or No (Not applicable to Fuel Oil Only units) | Text - Yes or No
Fuel Oil Capacity (check heat rate impact) MW | MW
Fuel Oil Heat Rate Impact | Btu/kWh
HRSG Capability, if Equipped, Unfired MW | MW
Duct Burners included ? Yes or No | Text - Yes or No
Duct Burners (included for all combined cycle HRSGs) MW | MW | 0 | 0
Duct Burner Heat Rate Impact | Btu/kWh
Total Potential HRSG + Duct Firing Capability, MW | MW
Spare Row | 0
Spare Row | 0
Winter (30F) MW net without fuel oil + steam turbine | MW net | 245.5692 | 110.6642
Winter (30F) MW net + fuel oil (if fuel oil included) + steam turbine | MW net
Summer (90F) MW net by itself + steam turbine | MW net
Summer (90F) MW net + inlet cooling + duct firing + steam turbine | MW net
Summer (90F) MW net without inlet cooling + duct firing + steam turbine | MW net | 238.2021 | 107.3443 | no duct filing
Summer (90F) MW net + inlet cooling without duct firing + steam turbine | MW net | 238.2021 | 107.3443
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. NO Steam Turbine Limit. | MW
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. May be steam turbine limited. USE THIS. | MW
Heat Rate (Higher Heating Value)
Full Load, HHV, net, with degradation (not applicable for all technologies, however, used in calculations) Btu/kW-hr | Btu/kWh
Full Load, HHV, net, with degradation and duct burner heat rate impact, Btu/kW-hr (if not combined cycle with duct burners, use the number above) | Btu/kWh
Full Load, HHV, net, with degradation and fuel oil (Winter) | Btu/kWh
Full Load, HHV, net, with degradation and inlet cooling, NO duct burners (Summer) | Btu/kWh | 9865.38 | 9087.504 | Set Cell C9 in worksheet NEW Data Inputs from Summary to EIA region for specific regional HR
Full Load, HHV, net, with degradation, inlet cooling, and duct burner heat rate impact (Summer) | Btu/kWh | 9865.38 | 9087.504
Full Load, HHV, net, with degradation and duct burners, NO inlet cooling heat rate impact | Btu/kWh
Full Load, HHV, net, with degradation, inlet cooling, power augmentation, HRSG, and duct firing. Does not include Fuel Oil Impact. | Btu/kWh | 9865.38 | 9087.504
75% Load, Btu/kW-hr | Btu/kWh | #REF! | #REF!
50% Load, Btu/kW-hr | Btu/kWh | #REF! | #REF!
25% Load, Btu/kW-hr | Btu/kWh | #REF! | #REF!
Average Annual (without duct burners), Btu/kW-hr | Btu/kWh
Estimated efficiency, HHV, full load, degraded, % | %
Energy Storage Roundtrip efficiency (82.67% is average) | %
Capacity Factor, %, for all but energy storage | %
Capacity Factor, %, for energy storage only | %
Annual Generation from Net Rating, MW-hr | MW-hr
Capital Cost, $/kW based on nominal MW | 2020 | Calculations from below. May not add due to rounding. | Calculations from below. May not add due to rounding.
Asset Purchase Price (not typical build) | $/kW
Steam generator | $/kW
Gasifier | $/kW
Air Separator | $/kW
Steam, Combustion, or Wind Turbines | $/kW
Black Start / Coping Power Combustion Turbines | $/kW
Solar Modules/Panels | $/kW
Inverters | $/kW
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $/kW
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $/kW
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $/kW
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $/kW
Duct Burners | $/kW
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $/kW
Plant Water Treatment (Demin/RO system, tanks, piping) | $/kW
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $/kW
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $/kW
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $/kW
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $/kW
Misc. Pumps and Piping not otherwise included | $/kW
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $/kW
Balance of Plant, BOP (adds from below) | $/kW
IT, Telecomm, SCADA, Metering, Telemetry, Software | $/kW
Security (including cameras), Roads, and Fencing | $/kW
Control Room | $/kW
Other BOP, not otherwise classified | $/kW
Gas Compression | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Freight/Shipping, Importation Duty, Fees, and Taxes | $/kW
Construction Labor | $/kW
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | $/kW
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | $/kW
Owner's Project and Construction Mgmt | $/kW
Developer Margin and Overheads | $/kW
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $/kW
First of a kind and/or Plug Number | $/kW
SO2 Polishing (used with CO2 capture) | $/kW
(AEP) O&M Mobilization Fee for a Buy | $/kW
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | $/kW
Project Contingency for a Build | $/kW
Project Contingency for a Buy | $/kW
EPC Contractor's Fee | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Fee Subtotal for Build (not used in calculation) | $/kW
Fee Subtotal for Buy (not used in calculation) | $/kW
Total Plant Cost (Overnight EPC) for Build Option | $/kW
Asset Purchase = Buy | $/kW
Owner's Costs | $/kW
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | $/kW
Owner's Costs for a BUY project (excluding Land) | $/kW
Inventory Capital | $/kW
Development and Legal Fees | $/kW
Regulatory Support Fees | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUILD | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUY | $/kW
Interconnection Studies (e.g., Tom Fecho) | $/kW
Enviro and building permits for BUILD | $/kW
Enviro and building permits for BUY | $/kW
AEP-paid sales tax, based on location | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Initial catalyst and chemicals | $/kW
Land Costs (for Buying Land; if Lease = O&M cost) | $/kW
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $/kW
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $/kW
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $/kW
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $/kW
Total Interconnects and Infrastructure (adds from below) | $/kW
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $/kW
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $/kW
Water Supply (Intake) and Wastewater Treatment | $/kW
Site Infrastructure (includes railroad and barge access) | $/kW
Landfill development | $/kW
Initial fuel Inventory (30 days for solid or liquid fuels) | $/kW
Total Plant Cost + Owner's Cost + Interconnects for Build | $/kW
Transmission Upgrade - not currently used | $/kW
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $/kW
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $/kW
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $/kW
Capital Cost | 2020
Asset Purchase Price (not typical build) | $ million
Steam generator | $ million
Gasifier | $ million
Air Separator | $ million
Steam, Combustion, or Wind Turbines | $ million
Black Start / Coping Power Combustion Turbines | $ million
Solar Modules/Panels | $ million
Inverters | $ million
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $ million
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $ million
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $ million
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $ million
Duct Burners | $ million
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $ million
Plant Water Treatment (Demin/RO system, tanks, piping) | $ million
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $ million
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $ million
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $ million
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $ million
Misc. Pumps and Piping not otherwise included | $ million
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $ million
Balance of Plant, BOP (adds from below) | $ million
IT, Telecomm, SCADA, Metering, Telemetry, Software | $ million
Security (including cameras), Roads, and Fencing | $ million
Control Room | $ million
Other BOP, not otherwise classified | $ million
Gas Compression | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Freight/Shipping, Importation Duty, Fees, and Taxes | 3%
Construction Labor | $ million
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | 12%
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | 5%
Owner's Project and Construction Mgmt | 5%
Developer Margin and Overheads | $ million
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $ million
First of a kind and/or Plug Number | $ million
SO2 Polishing (used with CO2 capture) | $ million
(AEP) O&M Mobilization Fee for a Buy | $ million
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | 1.25%
Project Contingency for a Build | 10%
Project Contingency for a Buy | $ million
EPC Contractor's Fee | 8%
Spare row | 0%
Spare row | 0%
Spare row | 0%
Fee Subtotal for Build (not used in calculation) | $ million
Fee Subtotal for Buy (not used in calculation) | $ million
Total Plant Cost (Overnight EPC) for Build Option | $ million
Asset Purchase = Buy | $ million
Owner's Costs | 0
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | 5%
Owner's Costs for a BUY project (excluding Land) | $ million
Inventory Capital | 1%
Development and Legal Fees | 1.25%
Regulatory Support Fees | 1%
Civil Work (surveys, geotech, grading, site installation) for BUILD | $ million
Civil Work (surveys, geotech, grading, site installation) for BUY | $ million
Interconnection Studies (e.g., Tom Fecho) | $ million
Enviro and building permits for BUILD | $ million
Enviro and building permits for BUY | $ million
AEP-paid sales tax, based on location | $ million
Spare row - check formulas | 0
Spare row - check formulas | 0
Spare row - check formulas | 0
Initial catalyst and chemicals | $ million
Land Costs (for Buying Land; if Lease = O&M cost) | $ million
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $ million
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $ million
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $ million
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $ million
Total Interconnects and Infrastructure (adds from below) | $ million
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $ million
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $ million
Water Supply (Intake) and Wastewater Treatment | $ million
Site Infrastructure (includes railroad and barge access) | $ million
Landfill development | $ million
Initial fuel Inventory (30 days for solid or liquid fuels) | $ million
Total Plant Cost + Owner's Cost + Interconnects for Build | $ million
Total Plant Cost + Owner's Cost + Interconnects for Buy | $ million
Transmission Upgrade - not currently used | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUY (Included in EPC) | $ million
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $ million | 161.5225 | 120.102 | Set Cell C9 in worksheet NEW Data Inputs from Summary to EIA region for specific costs
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $ million
Financial
AFUDC | $ million
Total Project Duration | months
AFUDC %, by operating company or equivalent, avg. annual rate | %
Financial Risk | Text (Low, Average, High)
Investment Life, years | Years (choose from 2, 3, 4, 5, 10, 15, 20, 25, 30, 33, 40, or 50 years) | 40 | 40
Economic Cost of Capital (AEP carrying cost, used in annual capital cost), % | %
Overhead / Allocation Rate for AEP operating company, % | %
Annual Capital Cost, $ million for Build | $ million
Annual Capital Cost, $ million for Buy | $ million
Capital Cost $/kW - year for Build | $/kW-year
Capital Cost $/kW - year for Buy | $/kW-year
Total Capital Costs, $/MW-hr | $/MW-hr
Operations & Maintenance (O&M)
Duty Cycle | Text
Capacity Factor | %
Annual Generation | MW-hr
Generating Facility Staff | Number (if part-time, use decimal)
Fixed O&M Costs
Fixed O&M as an EPRI/resource planning calculation, $/kW-year | $/kW-year | 7.1362 | 16.6171
Fixed O&M (adds from below), $ million | $ million
Plant Staff Payroll | $ million
General & Administrative Overheads (20% of Payroll) | $ million
Routine Maintenance, typically 1% of major equipment costs or input | $ million
Non-Natural Gas units Major Maintenance = 50% of the Variable O&M Major Maint. (per Resource Planning) | $ million
Utility (aux power and water) costs | $ million
Environmental and safety (monitoring, waste removal, etc.) | $ million
Buildings/grounds, SCADA, Communications, Software licensing, Other | $ million
Maint Expenses Not Otherwise Classified (Asset Management, collection system, substation work, wind turbine blade repairs, solar panel washing, energy storage potential cell upgrades, fuel cell stack replacement, misc. maint.) | $ million
O&M Service Agreement by 3rd party | $ million
Forecasting Services (hydro, wind, and solar) | $ million
Extended Warranties, per year | $ million
Land Lease Costs (not land purchase) | $ million
Natural Gas Major Maint. according to Resource Planning, using EPRI numbers. Calcs from below. | $ million
Property, Tax, and Insurance sum, $/MW-hr | $/MW-hr
Fixed O&M - $/MW-hr | $/MW-hr
Variable O&M Costs
Variable O&M (sums from below), $/MW-hr | $/MW-hr | 4.5875 | 4.7914
Consumables and Reagents | $/MW-hr
Major Maintenance = the other 50% of Variable O&M (per Resource Planning). | $/MW-hr
Variable O&M, $ million/year | $ million/yr
EPRI CO2 Capture and Storage Variable O&M, $ million/year, INCREMENTAL | $ million/yr
Total Variable O&M, $ million/year | $ million/year
Total Fixed & Variable O&M, $ million/year | $ million/yr
Total Fixed & Variable O&M, $/MW-hr | $/MW-hr
Production cost (Fuel + VOM) | $/MW-hr
Environmental
Water Usage, gpm | gallons / minute / unit, gpm
Water Usage, gal/year | gallons / year, total plant
Water Usage, gal/MW-hr | gal/MW-hr
* Some data are input, some are calculations. * | Check each emissions line
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
NOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
SOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Hg, Uncontrolled at exhaust, lb/TBtu | lb/TBtu
CO, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
CO2, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, ppm | ppm
NOx, Uncontrolled at exhaust, ppm | ppm
SOx, Uncontrolled at exhaust, ppm | ppm
Hg, Uncontrolled at exhaust, ppm | ppm
CO, Uncontrolled at exhaust, ppm | ppm
CO2, Uncontrolled at exhaust, ppm | ppm
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/hour | lb/hour
NOx, Uncontrolled at exhaust, lb/hour | lb/hour
SOx, Uncontrolled at exhaust, lb/hour | lb/hour
Hg, Uncontrolled at exhaust, lb/hour | lb/hour
CO, Uncontrolled at exhaust, lb/hour | lb/hour
CO2, Uncontrolled at exhaust, lb/hour | lb/hour
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/mmBtu | lb/mmBtu
NOx, Controlled, lb/mmBtu | lb/mmBtu | 0.03 | 0.09
SOx, Controlled, lb/mmBtu | lb/mmBtu | 0 | 0
Hg, Controlled, lb/TBtu | lb/Tbtu
CO, Controlled, lb/mmBtu | lb/mmBtu
CO2, Controlled, lb/mmBtu | lb/mmBtu | 117 | 117
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, ppm | ppm
NOx, Controlled, ppm | ppm
SOx, Controlled, ppm | ppm
Hg, Controlled, ppm | ppm
CO, Controlled, ppm | ppm
CO2, Controlled, ppm | ppm
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/MW-hr | lb/MW-hr
NOx, Controlled, lb/MW-hr | lb/MW-hr
SOx, Controlled, lb/MW-hr | lb/MW-hr
Hg, Controlled, lb/MW-hr | lb/MW-hr
CO, Controlled, lb/MW-hr | lb/MW-hr
CO2, Controlled, lb/MW-hr | lb/MW-hr
Control Efficiency Needed to meet Expected Permit Limit
Particulate Matter PM10 Control Efficiency % | %
NOx Control Efficiency % | %
SOx Control Efficiency % | %
Hg Control Efficiency % | %
CO Control Efficiency % | %
CO2 Control Efficiency % | %
Annual Emission Rate, Controlled
Particulate Matter PM10, Annual Emission Rate, Tons/year | Tons/yr
NOx, Annual Emission Rate, Tons/year | Tons/yr
SOx, Annual Emission Rate, Tons/year | Tons/yr
Hg, Annual Emission Rate, lb/year | lb/yr
CO, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Metric Tonnes/year | Tonnes/yr
Annual Captured Rate (what does not get emitted)
Particulate Matter PM10, Annual Captured Rate, Tons/year | Tons/yr
NOx, Annual Captured Rate, Tons/year | Tons/yr
SOx, Annual Captured Rate, Tons/year | Tons/yr
Hg, Annual Captured Rate, lb/year | lb/yr
CO, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Metric Tonnes/year | Tonnes/yr
Emission Fees (Title V)
Particulate Matter PM10 Emission Fee, $/Ton | $/Ton
NOx Emission Fee, $/Ton | $/Ton
SOx Emission Fee, $/Ton | $/Ton
Hg Emission Fee, $/lb | $/lb
CO Emission Fee, $/Ton | $/Ton
CO2 Emission Fee, $/Ton | $/Ton
Annual Emission Cost
Particulate Matter PM10 Annual Emission Cost, $ million | $ million
NOx Annual Emission Cost, $ million | $ million
SOx Annual Emission Cost, $ million | $ million
Hg Annual Emission Cost, $ million | $ million
CO Annual Emission Cost, $ million | $ million
CO2 Annual Emission Cost, $ million | $ million
Total Emission Cost $ million | $ million
Total Emission Cost, $/MW-hr | $/MW-hr
Energy Storage Capital Cost, Simple $ / kW-hr | $/kW-hr
Levelized Cost of Storage Capital, $/MW-hr | $/MW-hr
Levelized Cost of Storage Fuel, $/MW-hr | $/MW-hr
Levelized Cost of Storage O&M, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/kW-hr | $/kW-hr
Emissions, $/MW-hr | $/MW-hr
LCOS, Total with Emissions, $/MW-hr | $/MW-hr
First Year Cost of Electricity COE WITHOUT Incentives or Subsidies. NOT applicable to energy storage.
Capital, $/MW-hr | $/MW-hr
Fuel, $/MW-hr | $/MW-hr
O&M, $/MW-hr | $/MW-hr
Total without Emissions, $/MW-hr | $/MW-hr
Emissions, $/MW-hr | $/MW-hr
Total with Emissions, $/MW-hr | $/MW-hr
Transportation and Storage Cost of CO2, $/Tonne | $ / Tonne
Annual Cost of CO2 Transportation and Storage, $ million | $ million
Annual Cost of CO2 Transportation and Storage, $/MW-hr | $/MW-hr
Total Cost of Electricity, with Emissions and CO2, $/MW-hr (NOT applicable to energy storage) | $/MW-hr
Energy Storage Cycles over 1 year | Number
Energy Storage Depth of Discharge, % (80% is typical) | Number
Scheduled / Planned Outage Factor % | %
Planned Outage Hours | Hours
Planned Outage Days | Days
Forced Outage Factor % | %
Forced Outage Avg. Duration | Hours
Availability Factor % | %
Equivalent Availability Factor % | %
Typical Ramp Rate | MW / minute
Down Time (Minimum hrs) | Hours
Run Time (Minimum hrs) | Hours
Construction
Type of Site | Text
Footprint Needed, minimum acres | Acres
Required Gas Pressure, psig | psig
Commercial Availability, years | Years
Permit, License, and Design, years | Years
EPC (Engineer, Procure, Construct), years | Years
Total Project Duration, years | Years
Construction Cash Flow (%) -Yr 1 | % | 10% | 10%
Yr 2 | % | 35% | 35%
Yr 3 | % | 35% | 35%
Yr 4 | % | 20% | 20%
Yr 5 | % | 0% | 0%
Total | %
Total, All-in US$ 2020 for this Project | $ / kW
Escalation | $ / kW
Total, All-in As-Spent $US | $ / kW
Total, All-in US$ 2020 for this Project | $ million
Escalation | $ million
Total, All-in As-Spent $US | $ million
Numbers will NOT add due to categorization
Power Block | $ million
Balance of Plant | $ million
CO2 Capture Equipment | $ million
Labor | $ million
Interconnects and Infrastructure | $ million
Owner's costs with Sales Tax and Land | $ million
Project Contingency | $ million
AEP Allocations | $ million
Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for the Project | $ million
Power Block | %
Balance of Plant | %
CO2 Capture Equipment | %
Labor | %
Interconnects and Infrastructure | %
Owner's costs with Sales Tax and Land | %
Project Contingency | %
AEP Allocations | %
Commercially Viable | Year
Start Construction | Year
Commercial Operation Date | Year
Notes and Data Sources | Text
Note on C290: Slight Rounding error: BASE Cost in EIA report is $165,790M EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on D290: Slight Rounding error: BASE Cost in EIA report is $123.453M EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C314: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on D314: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C333: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on D333: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C480: 40 Month construction: 18M Dev, Permit, Engineer 22M Plant Construction
Note on D480: 40 Month construction: 18M Dev, Permit, Engineer 22M Plant Construction

## IRP Pull Data 2020 Small Nuc
Data feeds to other sheets. Some data not used for all technologies/fuels. |  | should be done 6-16-2020
CJB updated 3-5-2020 | Vendor Name | Small modular reactor
| Model | US DOE EIA S&L small modular reactors without AEP overheads
New Generation Technology Cost and Performance Estimates | Arrangement | 600 MW in 12 units
| Number of (generating) Units | 12
Shaded cells are not currently used. | Nominal MW net, plant | 600
| CO2 Control % (up to 99.99%) | 0%
APCo, I&M, AEG, Kentucky Power, PSO, SWEPCO, AEP Generation Resources (AGR), BPCo (Buckeye), General | Location by Operating Company | General
Specific Location, if available | Text | None
PJM or SPP Regional Transmission Area? If neither, use None | Text - PJM, SPP, or None | None
Plant Configuration | Units / Inputs
Technology | Text | 12 small nuclear reactors totalling 600 MW
Technology - Combustion turbine or recip engine? See also Fuel Type | Text, CT or RICE (or other) | other
If (gas) turbine, Simple or Combined Cycle? | Text, Simple Cycle, Combined Cycle, or None | None
Black Start Capability, total MW (must type in number even if Zero) | MW | 0
Does Land need to be purchased? Typical responses: No = existing property; wind = Lease; solar = Yes | Text, Yes, No, or Lease | Yes
Is this a typical "build" project or asset purchase (build, own, transfer) upon completion? | Text, Build or Buy. For Energy Storage, use Build. | Build
Fuel Type | Nuclear | Nuclear
Fuel Characteristic | Text | Solid
Fuel Availability | Text | Firm
Fuel Price Stability | Text | Stable
Fuel Cost, $/mmBtu | $/mmBtu | 0.96
Heating Value, Btu/lb HHV | Btu/Lb HHV | 1478933506.5451
Sulfur, % | % | 0
Ash, % | % | 0
Moisture, % | % | 0
Volatile Matter, VM, % | % | 0
Carbon, % | % | 0
H2, % | % | 0
O2, % | % | 0
N2, % | % | 0
Hg, lb/Tbtu | lb/Tbtu | 0
Annual Fuel Usage, equivalent million tons/year | Million Tons/yr | 1.6066e-05
Annual Heat Input (not valid for all technologies, but used in calculations), mmBtu | Million Btu (mmBtu) | 48139379.1792
Total Fuel Costs, $/MW-hr | $/MW-hr | 9.6442
Total Fuel Costs, $ million per year | $ Million | 45.6207
General Plant Description | Text | 600 MW small nuclear power plant based on 12 small reactor modules. USDOE EIA S&L report (see notes below)
Capacity
Standard ISO MW @ 1,000 ft. Gross | MW gross | 666.6667
Parasitic Load, % | % | 10%
Standard ISO MW @1,000 feet, WITHOUT the steam turbine | Nominal MWac net | 600
Standard ISO MW @ 1,000 feet WITH steam turbine | MW | 600
Steam Turbine (used in calcs) MW | MW | 600
Actual DC to AC ratio (default = 1.00) | Number | 1
DC capacity for solar; for all others = Standard ISO at 1,000 ft, MWac | Nominal MWdc net, plant | 600
Standard ISO MW thermal @ 1,000 ft | Nominal MW thermal | 1800
Energy Storage Duration, hours | Hours | 0
Energy Storage Capability, MW-hr, AC | MW-hr | 0
Spare Row
Minimum MW net, either calculation or from vendor (aka Turn Down Capability) | MW net | 5
Minimum, Turndown, % (minimum load with 1 machine for combustion turbines) | % | 10
Inlet Chilling Type for Combustion Turbines (See Notes page) | Text - None, Evaporative Cooler, or Chiller | None
Inlet Chilling Addition (check heat rate impact) MW | MW | 0
Inlet Chilling Heat Rate Impact | Btu/kWh | 0
Power Augmentation ? (See Notes page) | Text - None, Steam Injection, or Water Injection | None
Power Augmentation Addition (check heat rate impact) MW | MW | 0
Power Augmentation Heat Rate Impact | Btu/kWh | 0
0
Is Fuel Oil included? Yes or No (Not applicable to Fuel Oil Only units) | Text - Yes or No | No
Fuel Oil Capacity (check heat rate impact) MW | MW | 0
Fuel Oil Heat Rate Impact | Btu/kWh | 0
HRSG Capability, if Equipped, Unfired MW | MW | 0
Duct Burners included ? Yes or No | Text - Yes or No | No
Duct Burners (included for all combined cycle HRSGs) MW | MW | 0
Duct Burner Heat Rate Impact | Btu/kWh | 0
Total Potential HRSG + Duct Firing Capability, MW | MW | 0
Spare Row
Spare Row
Winter (30F) MW net without fuel oil + steam turbine | MW net | 633
Winter (30F) MW net + fuel oil (if fuel oil included) + steam turbine | MW net | 633
Summer (90F) MW net by itself + steam turbine | MW net | 582
Summer (90F) MW net + inlet cooling + duct firing + steam turbine | MW net | 582
Summer (90F) MW net without inlet cooling + duct firing + steam turbine | MW net | 582
Summer (90F) MW net + inlet cooling without duct firing + steam turbine | MW net | 582
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. NO Steam Turbine Limit. | MW | 582
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. May be steam turbine limited. USE THIS. | MW | 582
Spare Row
Potential Steam Generation (CHP only, 150 psig, saturated, at capacity factor) lb/year. Not applicable if other technology. (B&McD July 2017; see Notes) | lb/year | 5676480000
Potential Hot Water Generation (CHP only, 150 psig, saturated, at capacity factor) mmBtu/year. Not applicable if other technology. (B&McD July 2017; see Notes) | mmBtu/year | 13008600
Heat Rate (Higher Heating Value)
Full Load, HHV, net, with degradation (not applicable for all technologies, however, used in calculations) Btu/kW-hr | Btu/kWh | 10046
Full Load, HHV, net, with degradation and duct burner heat rate impact, Btu/kW-hr (if not combined cycle with duct burners, use the number above) | Btu/kWh | 10046
Full Load, HHV, net, with degradation and fuel oil (Winter) | Btu/kWh | 10046
Full Load, HHV, net, with degradation and inlet cooling, NO duct burners (Summer) | Btu/kWh | 10046
Full Load, HHV, net, with degradation, inlet cooling, and duct burner heat rate impact (Summer) | Btu/kWh | 10046
Full Load, HHV, net, with degradation and duct burners, NO inlet cooling heat rate impact | Btu/kWh | 10046
Full Load, HHV, net, with degradation, inlet cooling, power augmentation, HRSG, and duct firing. Does not include Fuel Oil Impact. | Btu/kWh | 10046
75% Load, Btu/kW-hr | Btu/kWh | 10258.9752
50% Load, Btu/kW-hr | Btu/kWh | 11797.8215
25% Load, Btu/kW-hr | Btu/kWh | 13271.3694
Average Annual (without duct burners), Btu/kW-hr | Btu/kWh | 10176.598
Estimated efficiency, HHV, full load, degraded, % | % | 33.96%
Energy Storage Roundtrip efficiency (82.67% is average) | % | 98%
Capacity Factor, %, for all but energy storage | % | 90%
Capacity Factor, %, for energy storage only | % | 0%
Annual Generation from Net Rating, MW-hr | MW-hr | 4730400 | 0
Spare row for notes, other calculations
Capital Cost, $/kW based on nominal MW | 2020 | Calculations from below. May not add due to rounding.
Asset Purchase Price (not typical build) | $/kW | 0
Steam generator | $/kW | 1080.6
Gasifier | $/kW | 0
Air Separator | $/kW | 0
Steam, Combustion, or Wind Turbines | $/kW | 0
Black Start / Coping Power Combustion Turbines | $/kW | 0
Solar Modules/Panels | $/kW | 0
Inverters | $/kW | 0
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $/kW | 0
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $/kW | 0
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $/kW | 0
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $/kW | 0
Duct Burners | $/kW | 0
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $/kW | 0
Plant Water Treatment (Demin/RO system, tanks, piping) | $/kW | 0
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $/kW | 0
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $/kW | 0
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $/kW | 432.24
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $/kW | 972.54
Misc. Pumps and Piping not otherwise included | $/kW | 0
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $/kW | 0
Spare row | $/kW | 0
Spare row | $/kW | 918.3333
Spare row | $/kW | 0
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $/kW | 4.2
Balance of Plant, BOP (adds from below) | $/kW | 1350.75
IT, Telecomm, SCADA, Metering, Telemetry, Software | $/kW | 0
Security (including cameras), Roads, and Fencing | $/kW | 0
Control Room | $/kW | 0
Other BOP, not otherwise classified | $/kW | 1350.75
Gas Compression | $/kW | 0
Spare row | $/kW | 0
Spare row | $/kW | 0
Spare row | $/kW | 0
Freight/Shipping, Importation Duty, Fees, and Taxes | $/kW | 0
Construction Labor | $/kW | 0
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | $/kW | 475.4463
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | $/kW | 0
Owner's Project and Construction Mgmt | $/kW | 0
Developer Margin and Overheads | $/kW | 0
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $/kW | 0
First of a kind and/or Plug Number | $/kW | 0
SO2 Polishing (used with CO2 capture) | $/kW | 0
(AEP) O&M Mobilization Fee for a Buy | $/kW | 0
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | $/kW | 0
Project Contingency for a Build | $/kW | 562.81
Project Contingency for a Buy | $/kW | 0
EPC Contractor's Fee | $/kW | 0
Spare row | $/kW | 0
Spare row | $/kW | 0
Spare row | $/kW | 0
Fee Subtotal for Build (not used in calculation) | $/kW | 1038.2563
Fee Subtotal for Buy (not used in calculation) | $/kW | 475.4463
Total Plant Cost (Overnight EPC) for Build Option | $/kW | 5796.9197
Asset Purchase = Buy | $/kW | 0
Owner's Costs | $/kW
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | $/kW | 392.2433
Owner's Costs for a BUY project (excluding Land) | $/kW | 0
Inventory Capital | $/kW | 0
Development and Legal Fees | $/kW | 0
Regulatory Support Fees | $/kW | 0
Civil Work (surveys, geotech, grading, site installation) for BUILD | $/kW | 0
Civil Work (surveys, geotech, grading, site installation) for BUY | $/kW | 0
Interconnection Studies (e.g., Tom Fecho) | $/kW | 0
Enviro and building permits for BUILD | $/kW | 0
Enviro and building permits for BUY | $/kW | 0
AEP-paid sales tax, based on location | $/kW | 0
Spare row - check formulas | $/kW | 0
Spare row - check formulas | $/kW | 0
Spare row - check formulas | $/kW | 0
0
Initial catalyst and chemicals | $/kW | 0
Land Costs (for Buying Land; if Lease = O&M cost) | $/kW | 1.75
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $/kW | 393.9933
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $/kW | 1.75
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $/kW | 6189.163
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $/kW | 1.8874e-14
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $/kW | 6190.913
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $/kW | 1.75
Total Interconnects and Infrastructure (adds from below) | $/kW | 0
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $/kW | 0
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $/kW | 0
Water Supply (Intake) and Wastewater Treatment | $/kW | 0
Site Infrastructure (includes railroad and barge access) | $/kW | 0
Landfill development | $/kW | 0
Initial fuel Inventory (30 days for solid or liquid fuels) | $/kW | 0
Total Plant Cost + Owner's Cost + Interconnects for Build | $/kW | 6190.913
Transmission Upgrade - not currently used | $/kW | 0
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $/kW | 0
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $/kW | 6190.913
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $/kW | 1.75
Capital Cost | 2020 | Inputs
Asset Purchase Price (not typical build) | $ million | 0
Steam generator | $ million | 648.36
Gasifier | $ million | 0
Air Separator | $ million | 0
Steam, Combustion, or Wind Turbines | $ million | 0
Black Start / Coping Power Combustion Turbines | $ million | 0
Solar Modules/Panels | $ million | 0
Inverters | $ million | 0
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $ million | 0
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $ million | 0
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $ million | 0
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $ million | 0
Duct Burners | $ million | 0
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $ million | 0
Plant Water Treatment (Demin/RO system, tanks, piping) | $ million | 0
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $ million | 0
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $ million | 0
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $ million | 259.344
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $ million | 583.524
Misc. Pumps and Piping not otherwise included | $ million | 0
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $ million | 0
Spare row | $ million
Spare row | $ million | 551
Spare row | $ million
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $ million | 2.52
Balance of Plant, BOP (adds from below) | $ million | 810.45
IT, Telecomm, SCADA, Metering, Telemetry, Software | $ million | 0
Security (including cameras), Roads, and Fencing | $ million | 0
Control Room | $ million | 0
Other BOP, not otherwise classified | $ million | 810.45
Gas Compression | $ million | 0
Spare row | $ million | 0
Spare row | $ million
Spare row | $ million | 0
Freight/Shipping, Importation Duty, Fees, and Taxes | 3% | 0
Construction Labor | $ million | 0
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | 12% | 285.2678
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | 5% | 0
Owner's Project and Construction Mgmt | 5% | 0
Developer Margin and Overheads | $ million
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $ million | 0
First of a kind and/or Plug Number | $ million | 0
SO2 Polishing (used with CO2 capture) | $ million | 0
(AEP) O&M Mobilization Fee for a Buy | $ million
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | 1.25% | 0
Project Contingency for a Build | 10% | 337.686
Project Contingency for a Buy | $ million | FALSE
EPC Contractor's Fee | 8% | 0
Spare row
Spare row
Spare row
Fee Subtotal for Build (not used in calculation) | $ million | 622.9538
Fee Subtotal for Buy (not used in calculation) | $ million | 285.2678
Total Plant Cost (Overnight EPC) for Build Option | $ million | 3478.1518
Asset Purchase = Buy | $ million | 0
Owner's Costs
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | 5% | 235.346
Owner's Costs for a BUY project (excluding Land) | $ million | FALSE
Inventory Capital | 1% | 0
Development and Legal Fees | 1.25% | 0
Regulatory Support Fees | 1% | 0
Civil Work (surveys, geotech, grading, site installation) for BUILD | $ million | 0
Civil Work (surveys, geotech, grading, site installation) for BUY | $ million | FALSE
Interconnection Studies (e.g., Tom Fecho) | $ million | 0
Enviro and building permits for BUILD | $ million | 0
Enviro and building permits for BUY | $ million | FALSE
AEP-paid sales tax, based on location | $ million | 0
Spare row - check formulas
Spare row - check formulas |  | 0
Spare row - check formulas
Initial catalyst and chemicals | $ million | 0
Land Costs (for Buying Land; if Lease = O&M cost) | $ million | 1.05
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $ million | 236.396
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $ million | 1.05
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $ million | 3713.4978
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $ million | 1.1324e-14
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $ million | 3714.5478
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $ million | 1.05
Total Interconnects and Infrastructure (adds from below) | $ million | 0
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $ million | 0
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $ million | 0
Water Supply (Intake) and Wastewater Treatment | $ million | 0
Site Infrastructure (includes railroad and barge access) | $ million | 0
Landfill development | $ million | 0
Initial fuel Inventory (30 days for solid or liquid fuels) | $ million | 0
Total Plant Cost + Owner's Cost + Interconnects for Build | $ million | 3714.5478
Total Plant Cost + Owner's Cost + Interconnects for Buy | $ million | 1.05
Transmission Upgrade - not currently used | $ million | 0
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $ million | 0
CO2 Capture and Storage (Retrofit or New Build) Cost for BUY (Included in EPC) | $ million | 0
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $ million | 3874.0027 | Set Cell C9 in worksheet NEW Data Inputs from Summary to EIA region for specific costs
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $ million | 1.05
Financial
AFUDC | $ million | 972.3943
Total Project Duration | months | 192
AFUDC %, by operating company or equivalent, avg. annual rate | % | 5.4538
Financial Risk | Text (Low, Average, High) | High
Investment Life, years | Years (choose from 2, 3, 4, 5, 10, 15, 20, 25, 30, 33, 40, or 50 years) | 40
Economic Cost of Capital (AEP carrying cost, used in annual capital cost), % | % | 10.8607
Overhead / Allocation Rate for AEP operating company, % | % | 13.76
Overhead / Allocation Costs, $ million for Build | $ million | 395.8913
Overhead / Allocation Costs, $ million for Buy | $ million | 3.016
Annual Capital Cost, $ million for Build | $ million | 517.4045
Annual Capital Cost, $ million for Buy | $ million | 107.4612
Capital Cost $/kW - year for Build | $/kW-year | 862.3408
Capital Cost $/kW - year for Buy | $/kW-year | 179.102
Nuclear Decommissioning Accrual, $ million/year | $ million / year | 10.503
Nuclear Decommissioning Accrual, $ million | $ million | 420.1214
General Decommissioning Cost, $ | $ million | 61.026
Assumes no salvage value
Remediation and/or Demolition Costs for Brownfield Site | $ million
Total Capital Costs, $/MW-hr | $/MW-hr | 109.3786
Operations & Maintenance (O&M)
Duty Cycle | Text | Base
Capacity Factor | % | 90%
Annual Generation | MW-hr | 4730400
Generating Facility Staff | Number (if part-time, use decimal) | 0
Fixed O&M Costs
Fixed O&M as an input from data sources for comparison, $/kW-year | $/kW-year | 82.57
Fixed O&M as an EPRI/resource planning calculation, $/kW-year | $/kW-year | 95
Fixed O&M (adds from below), $ million | $ million | 57
Plant Staff Payroll | $ million | 0
General & Administrative Overheads (20% of Payroll) | $ million | 0
Routine Maintenance, typically 1% of major equipment costs or input | $ million | 0
Non-Natural Gas units Major Maintenance = 50% of the Variable O&M Major Maint. (per Resource Planning) | $ million | 0
Utility (aux power and water) costs | $ million | 0
Environmental and safety (monitoring, waste removal, etc.) | $ million | 0
Buildings/grounds, SCADA, Communications, Software licensing, Other | $ million | 0
Maint Expenses Not Otherwise Classified (Asset Management, collection system, substation work, wind turbine blade repairs, solar panel washing, energy storage potential cell upgrades, fuel cell stack replacement, misc. maint.) | $ million | 57
O&M Service Agreement by 3rd party | $ million | 0
Forecasting Services (hydro, wind, and solar) | $ million | 0
Extended Warranties, per year | $ million | 0
Land Lease Costs (not land purchase) | $ million | 0
Natural Gas Major Maint. according to Resource Planning, using EPRI numbers. Calcs from below. | $ million | 0
(EPRI) natural gas fixed O&M, $ million | $ million | 0
(EPRI) natural gas scheduled Maintenance labor, $ million | $ million | 0
(EPRI) gas CT scheduled Maintenance materials, $ million | $ million | 0
(EPRI) natural gas variable O&M, $ million | $ million | 0
(EPRI) CO2 Capture and Storage Fixed O&M, $ million, INCREMENTAL | $ million | 0
Spare row not used | $ million
Spare row not used | $ million
Property, Taxes, and Insurance sum, $ million (adds from below) | $ million | 20.8689
Property costs (leases, royalties, etc.) (0.2% EPC) | $ million | 6.9563
Property Taxes (0.2% EPC) | $ million | 6.9563
Insurance costs (0.2% EPC) | $ million | 6.9563
Title Insurance | $ million | 0
Property, Tax, and Insurance sum, $/MW-hr | $/MW-hr | 4.4117
Fixed O&M - $/MW-hr | $/MW-hr | 12.2842
Variable O&M Costs
Variable O&M (sums from below), $/MW-hr | $/MW-hr | 3
Consumables and Reagents | $/MW-hr | 3
Major Maintenance = the other 50% of Variable O&M (per Resource Planning). | $/MW-hr | 0
Variable O&M, $ million/year | $ million/yr | 14.1912
EPRI CO2 Capture and Storage Variable O&M, $ million/year, INCREMENTAL | $ million/yr | 0
Total Variable O&M, $ million/year | $ million/year | 14.4673
Total Fixed & Variable O&M, $ million/year | $ million/yr | 71.1912
Total Fixed & Variable O&M, $/MW-hr | $/MW-hr | 15.0497
Production cost (Fuel + VOM) | $/MW-hr | 12.6442
Environmental
Production of sulfuric acid for IGCC | Tons/yr | 0
Sulfuric acid market value | $/Ton | 0
Sulfuric acid value | $ | 0
Water Usage, gpm | gallons / minute / unit, gpm | 0
Water Usage, gal/year | gallons / year, total plant | 0
Water Usage, gal/MW-hr | gal/MW-hr | 0
* Some data are input, some are calculations. * | Check each emissions line | Input or Calculation
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu | 0
NOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu | 0
SOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu | 0
Hg, Uncontrolled at exhaust, lb/TBtu | lb/TBtu | 0
CO, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu | 0
CO2, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu | 0
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, ppm | ppm
NOx, Uncontrolled at exhaust, ppm | ppm
SOx, Uncontrolled at exhaust, ppm | ppm
Hg, Uncontrolled at exhaust, ppm | ppm
CO, Uncontrolled at exhaust, ppm | ppm
CO2, Uncontrolled at exhaust, ppm | ppm
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/hour | lb/hour | 0
NOx, Uncontrolled at exhaust, lb/hour | lb/hour | 0
SOx, Uncontrolled at exhaust, lb/hour | lb/hour | 0
Hg, Uncontrolled at exhaust, lb/hour | lb/hour | 0
CO, Uncontrolled at exhaust, lb/hour | lb/hour | 0
CO2, Uncontrolled at exhaust, lb/hour | lb/hour | 0
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/mmBtu | lb/mmBtu | 0
NOx, Controlled, lb/mmBtu | lb/mmBtu | 0
SOx, Controlled, lb/mmBtu | lb/mmBtu | 0
Hg, Controlled, lb/TBtu | lb/Tbtu | 0
CO, Controlled, lb/mmBtu | lb/mmBtu | 0
CO2, Controlled, lb/mmBtu | lb/mmBtu | 0
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, ppm | ppm | 0
NOx, Controlled, ppm | ppm | 0
SOx, Controlled, ppm | ppm | 0
Hg, Controlled, ppm | ppm | 0
CO, Controlled, ppm | ppm | 0
CO2, Controlled, ppm | ppm | 0
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/MW-hr | lb/MW-hr | 0
NOx, Controlled, lb/MW-hr | lb/MW-hr | 0
SOx, Controlled, lb/MW-hr | lb/MW-hr | 0
Hg, Controlled, lb/MW-hr | lb/MW-hr | 0
CO, Controlled, lb/MW-hr | lb/MW-hr | 0
CO2, Controlled, lb/MW-hr | lb/MW-hr | 0
Control Efficiency Needed to meet Expected Permit Limit
Particulate Matter PM10 Control Efficiency % | % | 0
NOx Control Efficiency % | % | 0
SOx Control Efficiency % | % | 0
Hg Control Efficiency % | % | 0
CO Control Efficiency % | % | 0
CO2 Control Efficiency % | % | 0
Annual Emission Rate, Controlled
Particulate Matter PM10, Annual Emission Rate, Tons/year | Tons/yr | 0
NOx, Annual Emission Rate, Tons/year | Tons/yr | 0
SOx, Annual Emission Rate, Tons/year | Tons/yr | 0
Hg, Annual Emission Rate, lb/year | lb/yr | 0
CO, Annual Emission Rate, Tons/year | Tons/yr | 0
CO2, Annual Emission Rate, Tons/year | Tons/yr | 0
CO2, Annual Emission Rate, Metric Tonnes/year | Tonnes/yr | 0
Annual Captured Rate (what does not get emitted)
Particulate Matter PM10, Annual Captured Rate, Tons/year | Tons/yr | 0
NOx, Annual Captured Rate, Tons/year | Tons/yr | 0
SOx, Annual Captured Rate, Tons/year | Tons/yr | 0
Hg, Annual Captured Rate, lb/year | lb/yr | 0
CO, Annual Captured Rate, Tons/year | Tons/yr | 0
CO2, Annual Captured Rate, Tons/year | Tons/yr | 0
CO2, Annual Captured Rate, Metric Tonnes/year | Tonnes/yr | 0
Emission Fees (Title V)
Particulate Matter PM10 Emission Fee, $/Ton | $/Ton | 35
NOx Emission Fee, $/Ton | $/Ton | 25
SOx Emission Fee, $/Ton | $/Ton | 2
Hg Emission Fee, $/lb | $/lb | 0
CO Emission Fee, $/Ton | $/Ton | 0
CO2 Emission Fee, $/Ton | $/Ton | 0
Annual Emission Cost
Particulate Matter PM10 Annual Emission Cost, $ million | $ million | 0
NOx Annual Emission Cost, $ million | $ million | 0
SOx Annual Emission Cost, $ million | $ million | 0
Hg Annual Emission Cost, $ million | $ million | 0
CO Annual Emission Cost, $ million | $ million | 0
CO2 Annual Emission Cost, $ million | $ million | 0
Total Emission Cost $ million | $ million | 0
Avoided CO2 Cost (Same Technology), $/Tonne | $ / Tonne | 0
$/Tonne Captured and Sequestered | $ / Tonne | 0
$/Tonne Captured and Sequestered with Capacity and Energy Payments | $ / Tonne | 0
Total Emission Cost, $/MW-hr | $/MW-hr | 0
Energy Storage Capital Cost, Simple $ / kW-hr | $/kW-hr | #DIV/0!
Levelized Cost of Storage Capital, $/MW-hr | $/MW-hr | #DIV/0!
Levelized Cost of Storage Fuel, $/MW-hr | $/MW-hr | 9.841
Levelized Cost of Storage O&M, $/MW-hr | $/MW-hr | #DIV/0!
LCOS Total without Emissions, $/MW-hr | $/MW-hr | #DIV/0!
LCOS Total without Emissions, $/kW-hr | $/kW-hr | #DIV/0!
Emissions, $/MW-hr | $/MW-hr | 0
LCOS, Total with Emissions, $/MW-hr | $/MW-hr | #DIV/0!
First Year Cost of Electricity COE WITHOUT Incentives or Subsidies. NOT applicable to energy storage.
Capital, $/MW-hr | $/MW-hr | 109.3786
Fuel, $/MW-hr | $/MW-hr | 9.6442
O&M, $/MW-hr | $/MW-hr | 15.0497
Total without Emissions, $/MW-hr | $/MW-hr | 134.0725
Emissions, $/MW-hr | $/MW-hr | 0
Total with Emissions, $/MW-hr | $/MW-hr | 134.0725
Transportation and Storage Cost of CO2, $/Tonne | $ / Tonne | 0
Annual Cost of CO2 Transportation and Storage, $ million | $ million | 0
Annual Cost of CO2 Transportation and Storage, $/MW-hr | $/MW-hr | 0
Total Cost of Electricity, with Emissions and CO2, $/MW-hr (NOT applicable to energy storage) | $/MW-hr | 134.0725
Soft Data
Equipment description | Text | Small modular nuclear reactor US DOE EIA S&L small modular reactors without AEP overheads
Solar/wind/other equipment size | MW, kW, or watt, as applicable | 0
Number of Generating Units (e.g., solar panels, wind turbines) | Number | 12
Number of (Solar panels, wind turbines, etc.) | Number
Inverter Description | Text
Number of Inverters | Number
Energy Storage Volumetric Energy Density | watt-hour / liter
Energy Storage Specific Energy Density | watt-hour / kg
Energy Storage Specific Power Density | watts / kg
Energy Storage Cycles over 1 year | Number | 0
Energy Storage Depth of Discharge, % (80% is typical) | Number | 0
Energy Storage Roundtrip Efficiency, % (83% is typical) | % | 0.98
Energy Storage Use (energy = storage; power = frequency response) | Text, Energy or Power
Energy Storage Use (e.g., Frequency response, arbitrage, peak shaving, etc.) | Text
Stack Height, meters or feet, as appropriate | Text
Spare row
Spare row
Unit Availability
Black Start Capable (equipment in place)? | Text, Yes or No | No
Black Start Capability, MW | MW | 0
Dispatchable ? | Text, Yes or No | Yes
Volt - VAR Support ? | Text, Yes or No | Yes
Generation Reliability | Text, Good, Fair, or Poor | Fair
Flexibility of Operations | Text, Flexible or Inflexible | Flexible
Operational Complexity | Text, Simple or Complex | Complex
Location Benefits? (e.g., saving transmission losses, etc.) | Text, Yes or No
Used for Asset Deferral? (e.g., delay distribution upgrade) | Text, Yes or No
Spare row
Spare row
Scheduled / Planned Outage Factor % | % | Not available
Planned Outage Hours | Hours | #VALUE!
Planned Outage Days | Days | #VALUE!
Forced Outage Factor % | % | 0%
Forced Outage Avg. Duration | Hours | Not available
Availability Factor % | % | #VALUE!
Equivalent Availability Factor % | % | #VALUE!
Standard Start Time to Full Speed / No Load (FSNL) | Minutes
Standard Start Time from FSNL to Base Load | Minutes
Time from Zero to FSNL, Cold Start, Cold > 48 hours shutdown | Minutes
Time from Zero to FSNL, Warm Start, Warm < 48 hours shutdown | Minutes
Time from Zero to FSNL, Hot Start, Hot < 8 hours shutdown | Minutes
Hours between Overhauls | Number
Equivalent Starts | Number
Typical Ramp Rate | MW / minute
Down Time (Minimum hrs) | Hours | Not available
Run Time (Minimum hrs) | Hours | Not available
Spare row
Spare row
Construction
Type of Site | Text | Greenfield
Footprint Needed, minimum acres | Acres | 35
Required Gas Pressure, psig | psig | 0
Fuel Mass Flow, lb/hour | lb/hour | 0
Permitting Risk | Text, Low, Avg., or High | High
Technology Risk | Text, Low, Avg., or High | Unknown
Social Acceptance | Text, Low, Avg., or High | Unknown
Financial Risk (from above) | Text, Low, Avg., or High | High
Spare row
Spare row
Commercial Availability, years | Years | 10
Permit, License, and Design, years | Years | 2
EPC (Engineer, Procure, Construct), years | Years | 4
Total Project Duration, years | Years | 16
Construction Cash Flow (%) -Yr 1 | % | 20%
Yr 2 | % | 25%
Yr 3 | % | 25%
Yr 4 | % | 30%
Yr 5 | % | 0%
Total | % | 100%
Total, All-in US$ 2020 for this Project | $ / kW | 6190.913
Escalation | $ / kW | 1871.8425
Total, All-in As-Spent $US | $ / kW | 8062.7555
Total, All-in US$ 2020 for this Project | $ million | 3714.5478
Escalation | $ million | 1123.1055
Total, All-in As-Spent $US | $ million | 4837.6533
Numbers will NOT add due to categorization
Power Block | $ million | 2042.228
Balance of Plant | $ million | 810.45
CO2 Capture Equipment | $ million | 0
Labor | $ million | 0
Interconnects and Infrastructure | $ million | 2.52
Owner's costs with Sales Tax and Land | $ million | 236.396
Project Contingency | $ million | 337.686
AEP Allocations | $ million | 395.8913
Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for the Project | $ million | 3714.5478
Power Block | % | 54.9792
Balance of Plant | % | 21.8183
CO2 Capture Equipment | % | 0
Labor | % | 0
Interconnects and Infrastructure | % | 0.067841
Owner's costs with Sales Tax and Land | % | 6.3641
Project Contingency | % | 9.0909
AEP Allocations | % | 10.6579
Commercially Viable | Year | 2030
Start Construction | Year | 2022
Commercial Operation Date | Year | 2036
Graphs show % of costs for major items, NOT every item, without AEP allocations.
Shaded cells are not currently used.
Total All-in, As-spent, $/kW
Maximum across the worksheet = | 8987.7861
Average across the worksheet = | 8987.7861
Minimum across the worksheet = | 8987.7861
| Risk/Insurance equipment + labor, $/kW = | 4758.6633
Notes and Data Sources | Text | Limited data from USDOE EIA S&L report
Capital Cost and Performance Characteristic Estimates for Utility Scale Electric Power Generating Technologies, Feb. 2020
Case 12. Small Modular Reactor Nuclear Power Plant, 600 MW
No data on ramp rates, startups, O&M hours, etc.
Report states $95/kW-yr fixed O&M; $3.00/MW-hr variable.
No staffing numbers given.
Report states $6,191/kW net.
Fixed O&M includes labor, materials, and contracted services, and G&A.
Note on C317: Slight Rounding error: BASE Cost in EIA report is $3,714.5478M EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on E317: Slight Rounding error: BASE Cost in EIA report is $3,819,201M
Note on C382: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C389: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation

## IRP Pull Data 20 Energy Storage
Pulls from Master Sheets. Will feed Stop Light Grid sheet eventually. |  | Resource Screening
CJB updated 3-26-2020 | Vendor Name | Battery storage
| Model | CASE 18. BATTERY ENERGY STORAGE SYSTEM, 50 MW / 200 MWH
New Generation Technology Cost and Performance Estimates | Arrangement
| Number of (generating) Units | 1
Shaded cells are not currently used. | Nominal MW net, plant | 50
| CO2 Control % (up to 99.99%) | 0%
APCo, I&M, AEG, Kentucky Power, PSO, SWEPCO, AEP Generation Resources (AGR), BPCo (Buckeye), General | Location by Operating Company | General
Specific Location, if available | Text | None
PJM or SPP Regional Transmission Area? If neither, use None | Text - PJM, SPP, or None | None
Plant Configuration | Units / Inputs
Technology | Text | Unknown
Black Start Capability, total MW (must type in number even if Zero) | MW | 0
Does Land need to be purchased? Typical responses: No = existing property; wind = Lease; solar = Yes | Text, Yes, No, or Lease | No
Is this a typical "build" project or asset purchase (build, own, transfer) upon completion? | Text, Build or Buy. For Energy Storage, use Build. | Build
Fuel Type | Energy Storage | Energy Storage
Fuel Characteristic | Text | Electricity
Fuel Availability | Text | Firm or Spot
Fuel Price Stability | Text | Stable
Fuel Cost, $/mmBtu | $/mmBtu
Heating Value, Btu/lb HHV | Btu/Lb HHV
Annual Fuel Usage, equivalent million tons/year | Million Tons/yr
Annual Heat Input (not valid for all technologies, but used in calculations), mmBtu | Million Btu (mmBtu)
Total Fuel Costs, $/MW-hr | $/MW-hr
Total Fuel Costs, $ million per year | $ Million
General Plant Description | Text | 50 MW x 200 MW-hr AC storage system
Capacity
Standard ISO MW @ 1,000 ft. Gross | MW gross | 50
Parasitic Load, % | % | 0%
Standard ISO MW @1,000 feet, WITHOUT the steam turbine | Nominal MWac net | 50
Standard ISO MW @ 1,000 feet WITH steam turbine | MW | 50
Steam Turbine (used in calcs) MW | MW
Actual DC to AC ratio (default = 1.00) | Number
DC capacity for solar; for all others = Standard ISO at 1,000 ft, MWac | Nominal MWdc net, plant
Energy Storage Duration, hours | Hours | 4
Energy Storage Capability, MW-hr, AC | MW-hr | 200
Minimum MW net, either calculation or from vendor (aka Turn Down Capability) | MW net
Minimum, Turndown, % (minimum load with 1 machine for combustion turbines) | % | 25 | copied from Column D
Inlet Chilling Type for Combustion Turbines (See Notes page) | Text - None, Evaporative Cooler, or Chiller
Inlet Chilling Addition (check heat rate impact) MW | MW
Inlet Chilling Heat Rate Impact | Btu/kWh
Is Fuel Oil included? Yes or No (Not applicable to Fuel Oil Only units) | Text - Yes or No
Fuel Oil Capacity (check heat rate impact) MW | MW
Fuel Oil Heat Rate Impact | Btu/kWh
HRSG Capability, if Equipped, Unfired MW | MW
Duct Burners included ? Yes or No | Text - Yes or No
Duct Burners (included for all combined cycle HRSGs) MW | MW
Duct Burner Heat Rate Impact | Btu/kWh
Total Potential HRSG + Duct Firing Capability, MW | MW
Spare Row | 0
Spare Row | 0
Winter (30F) MW net without fuel oil + steam turbine | MW net
Winter (30F) MW net + fuel oil (if fuel oil included) + steam turbine | MW net
Summer (90F) MW net by itself + steam turbine | MW net
Summer (90F) MW net + inlet cooling + duct firing + steam turbine | MW net
Summer (90F) MW net without inlet cooling + duct firing + steam turbine | MW net
Summer (90F) MW net + inlet cooling without duct firing + steam turbine | MW net
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. NO Steam Turbine Limit. | MW
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. May be steam turbine limited. USE THIS. | MW
Heat Rate (Higher Heating Value)
Full Load, HHV, net, with degradation (not applicable for all technologies, however, used in calculations) Btu/kW-hr | Btu/kWh
Full Load, HHV, net, with degradation and duct burner heat rate impact, Btu/kW-hr (if not combined cycle with duct burners, use the number above) | Btu/kWh
Full Load, HHV, net, with degradation and fuel oil (Winter) | Btu/kWh
Full Load, HHV, net, with degradation and inlet cooling, NO duct burners (Summer) | Btu/kWh | 1000 | copied from Column D
Full Load, HHV, net, with degradation, inlet cooling, and duct burner heat rate impact (Summer) | Btu/kWh | 1000 | copied from Column D
Full Load, HHV, net, with degradation and duct burners, NO inlet cooling heat rate impact | Btu/kWh
Full Load, HHV, net, with degradation, inlet cooling, power augmentation, HRSG, and duct firing. Does not include Fuel Oil Impact. | Btu/kWh | 1000 | copied from Column D
75% Load, Btu/kW-hr | Btu/kWh | 1021.2 | copied from Column D
50% Load, Btu/kW-hr | Btu/kWh | 1174.38 | copied from Column D
25% Load, Btu/kW-hr | Btu/kWh | 1321.0601 | copied from Column D
Average Annual (without duct burners), Btu/kW-hr | Btu/kWh
Estimated efficiency, HHV, full load, degraded, % | %
Energy Storage Roundtrip efficiency (82.67% is average) | %
Capacity Factor, %, for all but energy storage | %
Capacity Factor, %, for energy storage only | %
Annual Generation from Net Rating, MW-hr | MW-hr
Capital Cost, $/kW based on nominal MW | 2020 | Calculations from below. May not add due to rounding.
Asset Purchase Price (not typical build) | $/kW
Steam generator | $/kW
Gasifier | $/kW
Air Separator | $/kW
Steam, Combustion, or Wind Turbines | $/kW
Black Start / Coping Power Combustion Turbines | $/kW
Solar Modules/Panels | $/kW
Inverters | $/kW
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $/kW
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $/kW
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $/kW
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $/kW
Duct Burners | $/kW
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $/kW
Plant Water Treatment (Demin/RO system, tanks, piping) | $/kW
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $/kW
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $/kW
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $/kW
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $/kW
Misc. Pumps and Piping not otherwise included | $/kW
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $/kW
Balance of Plant, BOP (adds from below) | $/kW
IT, Telecomm, SCADA, Metering, Telemetry, Software | $/kW
Security (including cameras), Roads, and Fencing | $/kW
Control Room | $/kW
Other BOP, not otherwise classified | $/kW
Gas Compression | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Freight/Shipping, Importation Duty, Fees, and Taxes | $/kW
Construction Labor | $/kW
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | $/kW
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | $/kW
Owner's Project and Construction Mgmt | $/kW
Developer Margin and Overheads | $/kW
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $/kW
First of a kind and/or Plug Number | $/kW
SO2 Polishing (used with CO2 capture) | $/kW
(AEP) O&M Mobilization Fee for a Buy | $/kW
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | $/kW
Project Contingency for a Build | $/kW
Project Contingency for a Buy | $/kW
EPC Contractor's Fee | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Fee Subtotal for Build (not used in calculation) | $/kW
Fee Subtotal for Buy (not used in calculation) | $/kW
Total Plant Cost (Overnight EPC) for Build Option | $/kW
Asset Purchase = Buy | $/kW
Owner's Costs | $/kW
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | $/kW
Owner's Costs for a BUY project (excluding Land) | $/kW
Inventory Capital | $/kW
Development and Legal Fees | $/kW
Regulatory Support Fees | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUILD | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUY | $/kW
Interconnection Studies (e.g., Tom Fecho) | $/kW
Enviro and building permits for BUILD | $/kW
Enviro and building permits for BUY | $/kW
AEP-paid sales tax, based on location | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Initial catalyst and chemicals | $/kW
Land Costs (for Buying Land; if Lease = O&M cost) | $/kW
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $/kW
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $/kW
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $/kW
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $/kW
Total Interconnects and Infrastructure (adds from below) | $/kW
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $/kW
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $/kW
Water Supply (Intake) and Wastewater Treatment | $/kW
Site Infrastructure (includes railroad and barge access) | $/kW
Landfill development | $/kW
Initial fuel Inventory (30 days for solid or liquid fuels) | $/kW
Total Plant Cost + Owner's Cost + Interconnects for Build | $/kW
Transmission Upgrade - not currently used | $/kW
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $/kW
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $/kW
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $/kW
Capital Cost | 2020
Asset Purchase Price (not typical build) | $ million
Steam generator | $ million
Gasifier | $ million
Air Separator | $ million
Steam, Combustion, or Wind Turbines | $ million
Black Start / Coping Power Combustion Turbines | $ million
Solar Modules/Panels | $ million
Inverters | $ million
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $ million
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $ million
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $ million
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $ million
Duct Burners | $ million
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $ million
Plant Water Treatment (Demin/RO system, tanks, piping) | $ million
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $ million
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $ million
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $ million
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $ million
Misc. Pumps and Piping not otherwise included | $ million
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $ million
Balance of Plant, BOP (adds from below) | $ million
IT, Telecomm, SCADA, Metering, Telemetry, Software | $ million
Security (including cameras), Roads, and Fencing | $ million
Control Room | $ million
Other BOP, not otherwise classified | $ million
Gas Compression | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Freight/Shipping, Importation Duty, Fees, and Taxes | 3%
Construction Labor | $ million
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | 12%
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | 5%
Owner's Project and Construction Mgmt | 5%
Developer Margin and Overheads | $ million
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $ million
First of a kind and/or Plug Number | $ million
SO2 Polishing (used with CO2 capture) | $ million
(AEP) O&M Mobilization Fee for a Buy | $ million
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | 1.25%
Project Contingency for a Build | 10%
Project Contingency for a Buy | $ million
EPC Contractor's Fee | 0%
Spare row | 0%
Spare row | 0%
Spare row | 0%
Fee Subtotal for Build (not used in calculation) | $ million
Fee Subtotal for Buy (not used in calculation) | $ million
Total Plant Cost (Overnight EPC) for Build Option | $ million
Asset Purchase = Buy | $ million
Owner's Costs | 0
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | 5%
Owner's Costs for a BUY project (excluding Land) | $ million
Inventory Capital | 1%
Development and Legal Fees | 1.25%
Regulatory Support Fees | 1%
Civil Work (surveys, geotech, grading, site installation) for BUILD | $ million
Civil Work (surveys, geotech, grading, site installation) for BUY | $ million
Interconnection Studies (e.g., Tom Fecho) | $ million
Enviro and building permits for BUILD | $ million
Enviro and building permits for BUY | $ million
AEP-paid sales tax, based on location | $ million
Spare row - check formulas | 0
Spare row - check formulas | 0
Spare row - check formulas | 0
Initial catalyst and chemicals | $ million
Land Costs (for Buying Land; if Lease = O&M cost) | $ million
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $ million
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $ million
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $ million
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $ million
Total Interconnects and Infrastructure (adds from below) | $ million
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $ million
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $ million
Water Supply (Intake) and Wastewater Treatment | $ million
Site Infrastructure (includes railroad and barge access) | $ million
Landfill development | $ million
Initial fuel Inventory (30 days for solid or liquid fuels) | $ million
Total Plant Cost + Owner's Cost + Interconnects for Build | $ million
Total Plant Cost + Owner's Cost + Interconnects for Buy | $ million
Transmission Upgrade - not currently used | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUY (Included in EPC) | $ million
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $ million | 70.2914 | Set Cell C9 in worksheet NEW Data Inputs from Summary to EIA region for specific costs
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $ million
Financial
AFUDC | $ million
Total Project Duration | months
AFUDC %, by operating company or equivalent, avg. annual rate | %
Financial Risk | Text (Low, Average, High)
Investment Life, years | Years (choose from 2, 3, 4, 5, 10, 15, 20, 25, 30, 33, 40, or 50 years) | 10
Economic Cost of Capital (AEP carrying cost, used in annual capital cost), % | %
Overhead / Allocation Rate for AEP operating company, % | %
Annual Capital Cost, $ million for Build | $ million
Annual Capital Cost, $ million for Buy | $ million
Capital Cost $/kW - year for Build | $/kW-year
Capital Cost $/kW - year for Buy | $/kW-year
Total Capital Costs, $/MW-hr | $/MW-hr
Operations & Maintenance (O&M)
Duty Cycle | Text
Capacity Factor | %
Annual Generation | MW-hr
Generating Facility Staff | Number (if part-time, use decimal)
Fixed O&M Costs
Fixed O&M as an EPRI/resource planning calculation, $/kW-year | $/kW-year | 25.2825
Fixed O&M (adds from below), $ million | $ million
Plant Staff Payroll | $ million
General & Administrative Overheads (20% of Payroll) | $ million
Routine Maintenance, typically 1% of major equipment costs or input | $ million
Non-Natural Gas units Major Maintenance = 50% of the Variable O&M Major Maint. (per Resource Planning) | $ million
Utility (aux power and water) costs | $ million
Environmental and safety (monitoring, waste removal, etc.) | $ million
Buildings/grounds, SCADA, Communications, Software licensing, Other | $ million
Maint Expenses Not Otherwise Classified (Asset Management, collection system, substation work, wind turbine blade repairs, solar panel washing, energy storage potential cell upgrades, fuel cell stack replacement, misc. maint.) | $ million
O&M Service Agreement by 3rd party | $ million
Forecasting Services (hydro, wind, and solar) | $ million
Extended Warranties, per year | $ million
Land Lease Costs (not land purchase) | $ million
Natural Gas Major Maint. according to Resource Planning, using EPRI numbers. Calcs from below. | $ million
Property, Tax, and Insurance sum, $/MW-hr | $/MW-hr
Fixed O&M - $/MW-hr | $/MW-hr
Variable O&M Costs
Variable O&M (sums from below), $/MW-hr | $/MW-hr | 0
Consumables and Reagents | $/MW-hr
Major Maintenance = the other 50% of Variable O&M (per Resource Planning). | $/MW-hr
Variable O&M, $ million/year | $ million/yr
EPRI CO2 Capture and Storage Variable O&M, $ million/year, INCREMENTAL | $ million/yr
Total Variable O&M, $ million/year | $ million/year
Total Fixed & Variable O&M, $ million/year | $ million/yr
Total Fixed & Variable O&M, $/MW-hr | $/MW-hr
Production cost (Fuel + VOM) | $/MW-hr
Environmental
Water Usage, gpm | gallons / minute / unit, gpm
Water Usage, gal/year | gallons / year, total plant
Water Usage, gal/MW-hr | gal/MW-hr
* Some data are input, some are calculations. * | Check each emissions line
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
NOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
SOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Hg, Uncontrolled at exhaust, lb/TBtu | lb/TBtu
CO, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
CO2, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, ppm | ppm
NOx, Uncontrolled at exhaust, ppm | ppm
SOx, Uncontrolled at exhaust, ppm | ppm
Hg, Uncontrolled at exhaust, ppm | ppm
CO, Uncontrolled at exhaust, ppm | ppm
CO2, Uncontrolled at exhaust, ppm | ppm
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/hour | lb/hour
NOx, Uncontrolled at exhaust, lb/hour | lb/hour
SOx, Uncontrolled at exhaust, lb/hour | lb/hour
Hg, Uncontrolled at exhaust, lb/hour | lb/hour
CO, Uncontrolled at exhaust, lb/hour | lb/hour
CO2, Uncontrolled at exhaust, lb/hour | lb/hour
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/mmBtu | lb/mmBtu
NOx, Controlled, lb/mmBtu | lb/mmBtu | 0
SOx, Controlled, lb/mmBtu | lb/mmBtu | 0
Hg, Controlled, lb/TBtu | lb/Tbtu | 0
CO, Controlled, lb/mmBtu | lb/mmBtu | 0
CO2, Controlled, lb/mmBtu | lb/mmBtu | 0
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, ppm | ppm
NOx, Controlled, ppm | ppm
SOx, Controlled, ppm | ppm
Hg, Controlled, ppm | ppm
CO, Controlled, ppm | ppm
CO2, Controlled, ppm | ppm
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/MW-hr | lb/MW-hr
NOx, Controlled, lb/MW-hr | lb/MW-hr
SOx, Controlled, lb/MW-hr | lb/MW-hr
Hg, Controlled, lb/MW-hr | lb/MW-hr
CO, Controlled, lb/MW-hr | lb/MW-hr
CO2, Controlled, lb/MW-hr | lb/MW-hr
Control Efficiency Needed to meet Expected Permit Limit
Particulate Matter PM10 Control Efficiency % | %
NOx Control Efficiency % | %
SOx Control Efficiency % | %
Hg Control Efficiency % | %
CO Control Efficiency % | %
CO2 Control Efficiency % | %
Annual Emission Rate, Controlled
Particulate Matter PM10, Annual Emission Rate, Tons/year | Tons/yr
NOx, Annual Emission Rate, Tons/year | Tons/yr
SOx, Annual Emission Rate, Tons/year | Tons/yr
Hg, Annual Emission Rate, lb/year | lb/yr
CO, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Metric Tonnes/year | Tonnes/yr
Annual Captured Rate (what does not get emitted)
Particulate Matter PM10, Annual Captured Rate, Tons/year | Tons/yr
NOx, Annual Captured Rate, Tons/year | Tons/yr
SOx, Annual Captured Rate, Tons/year | Tons/yr
Hg, Annual Captured Rate, lb/year | lb/yr
CO, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Metric Tonnes/year | Tonnes/yr
Emission Fees (Title V)
Particulate Matter PM10 Emission Fee, $/Ton | $/Ton
NOx Emission Fee, $/Ton | $/Ton
SOx Emission Fee, $/Ton | $/Ton
Hg Emission Fee, $/lb | $/lb
CO Emission Fee, $/Ton | $/Ton
CO2 Emission Fee, $/Ton | $/Ton
Annual Emission Cost
Particulate Matter PM10 Annual Emission Cost, $ million | $ million
NOx Annual Emission Cost, $ million | $ million
SOx Annual Emission Cost, $ million | $ million
Hg Annual Emission Cost, $ million | $ million
CO Annual Emission Cost, $ million | $ million
CO2 Annual Emission Cost, $ million | $ million
Total Emission Cost $ million | $ million
Total Emission Cost, $/MW-hr | $/MW-hr
Energy Storage Capital Cost, Simple $ / kW-hr | $/kW-hr
Levelized Cost of Storage Capital, $/MW-hr | $/MW-hr
Levelized Cost of Storage Fuel, $/MW-hr | $/MW-hr
Levelized Cost of Storage O&M, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/kW-hr | $/kW-hr
Emissions, $/MW-hr | $/MW-hr
LCOS, Total with Emissions, $/MW-hr | $/MW-hr
First Year Cost of Electricity COE WITHOUT Incentives or Subsidies. NOT applicable to energy storage.
Capital, $/MW-hr | $/MW-hr
Fuel, $/MW-hr | $/MW-hr
O&M, $/MW-hr | $/MW-hr
Total without Emissions, $/MW-hr | $/MW-hr
Emissions, $/MW-hr | $/MW-hr
Total with Emissions, $/MW-hr | $/MW-hr
Transportation and Storage Cost of CO2, $/Tonne | $ / Tonne
Annual Cost of CO2 Transportation and Storage, $ million | $ million
Annual Cost of CO2 Transportation and Storage, $/MW-hr | $/MW-hr
Total Cost of Electricity, with Emissions and CO2, $/MW-hr (NOT applicable to energy storage) | $/MW-hr
Energy Storage Cycles over 1 year | Number
Energy Storage Depth of Discharge, % (80% is typical) | Number
Scheduled / Planned Outage Factor % | %
Planned Outage Hours | Hours
Planned Outage Days | Days
Forced Outage Factor % | % | 0.5% | copied from column D, not provided in EIA report
Forced Outage Avg. Duration | Hours
Availability Factor % | %
Equivalent Availability Factor % | %
Typical Ramp Rate | MW / minute
Down Time (Minimum hrs) | Hours
Run Time (Minimum hrs) | Hours
Construction
Type of Site | Text
Footprint Needed, minimum acres | Acres
Required Gas Pressure, psig | psig
Commercial Availability, years | Years
Permit, License, and Design, years | Years
EPC (Engineer, Procure, Construct), years | Years
Total Project Duration, years | Years
Construction Cash Flow (%) -Yr 1 | % | 100%
Yr 2 | % | 0%
Yr 3 | % | 0%
Yr 4 | % | 0%
Yr 5 | % | 0%
Total | % | 100%
Total, All-in US$ 2020 for this Project | $ / kW
Escalation | $ / kW
Total, All-in As-Spent $US | $ / kW
Total, All-in US$ 2020 for this Project | $ million
Escalation | $ million
Total, All-in As-Spent $US | $ million
Numbers will NOT add due to categorization
Power Block | $ million
Balance of Plant | $ million
CO2 Capture Equipment | $ million
Labor | $ million
Interconnects and Infrastructure | $ million
Owner's costs with Sales Tax and Land | $ million
Project Contingency | $ million
AEP Allocations | $ million
Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for the Project | $ million
Power Block | %
Balance of Plant | %
CO2 Capture Equipment | %
Labor | %
Interconnects and Infrastructure | %
Owner's costs with Sales Tax and Land | %
Project Contingency | %
AEP Allocations | %
Commercially Viable | Year
Start Construction | Year
Commercial Operation Date | Year
Notes and Data Sources | Text
Note on C290: Slight Rounding error: BASE Cost in EIA report is $69.456M EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C314: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation

## IRP Pull Data 20 Recip Engines
Pulls from Master Sheets. Will feed Stop Light Grid sheet eventually. |  | 4
CJB updated 1-20-2020 with Wartsila data; NOT modified with EPRI data. Added 2 EPRI models 3-18-2020 | Vendor Name | Internal combustion engine
| Model | S&L Case 4, INTERNAL COMBUSTION ENGINES, 20 MW
New Generation Technology Cost and Performance Estimates | Arrangement
Number of (generating) Units
Shaded cells are not currently used. | Nominal MW net, plant | 21.4
CO2 Control % (up to 99.99%)
APCo, I&M, AEG, Kentucky Power, PSO, SWEPCO, AEP Generation Resources (AGR), BPCo (Buckeye), General | Location by Operating Company
Specific Location, if available | Text
PJM or SPP Regional Transmission Area? If neither, use None | Text - PJM, SPP, or None
Plant Configuration | Units / Inputs
Technology | Text | 1
Black Start Capability, total MW (must type in number even if Zero) | MW | 0
Does Land need to be purchased? Typical responses: No = existing property; wind = Lease; solar = Yes | Text, Yes, No, or Lease | Yes
Is this a typical "build" project or asset purchase (build, own, transfer) upon completion? | Text, Build or Buy. For Energy Storage, use Build. | Build
Fuel Type | Natural Gas Reciprocating Engines | Natural Gas CT
Fuel Characteristic | Text | Gas
Fuel Availability | Text
Fuel Price Stability | Text
Fuel Cost, $/mmBtu | $/mmBtu
Heating Value, Btu/lb HHV | Btu/Lb HHV
Annual Fuel Usage, equivalent million tons/year | Million Tons/yr
Annual Heat Input (not valid for all technologies, but used in calculations), mmBtu | Million Btu (mmBtu)
Total Fuel Costs, $/MW-hr | $/MW-hr
Total Fuel Costs, $ million per year | $ Million
General Plant Description | Text
Capacity
Standard ISO MW @ 1,000 ft. Gross | MW gross
Parasitic Load, % | %
Standard ISO MW @1,000 feet, WITHOUT the steam turbine | Nominal MWac net
Standard ISO MW @ 1,000 feet WITH steam turbine | MW | 21.4
Steam Turbine (used in calcs) MW | MW
Actual DC to AC ratio (default = 1.00) | Number
DC capacity for solar; for all others = Standard ISO at 1,000 ft, MWac | Nominal MWdc net, plant
Energy Storage Duration, hours | Hours
Energy Storage Capability, MW-hr, AC | MW-hr
Minimum MW net, either calculation or from vendor (aka Turn Down Capability) | MW net
Minimum, Turndown, % (minimum load with 1 machine for combustion turbines) | %
Inlet Chilling Type for Combustion Turbines (See Notes page) | Text - None, Evaporative Cooler, or Chiller
Inlet Chilling Addition (check heat rate impact) MW | MW
Inlet Chilling Heat Rate Impact | Btu/kWh
Is Fuel Oil included? Yes or No (Not applicable to Fuel Oil Only units) | Text - Yes or No
Fuel Oil Capacity (check heat rate impact) MW | MW
Fuel Oil Heat Rate Impact | Btu/kWh
HRSG Capability, if Equipped, Unfired MW | MW
Duct Burners included ? Yes or No | Text - Yes or No
Duct Burners (included for all combined cycle HRSGs) MW | MW | 0
Duct Burner Heat Rate Impact | Btu/kWh
Total Potential HRSG + Duct Firing Capability, MW | MW
Spare Row | 0
Spare Row | 0
Winter (30F) MW net without fuel oil + steam turbine | MW net | 22.577
Winter (30F) MW net + fuel oil (if fuel oil included) + steam turbine | MW net
Summer (90F) MW net by itself + steam turbine | MW net
Summer (90F) MW net + inlet cooling + duct firing + steam turbine | MW net
Summer (90F) MW net without inlet cooling + duct firing + steam turbine | MW net
Summer (90F) MW net + inlet cooling without duct firing + steam turbine | MW net | 20.758
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. NO Steam Turbine Limit. | MW
Max Theoretical Summer = Summer MW net + inlet cooling + HRSG + duct firing + steam turbine, MW. May be steam turbine limited. USE THIS. | MW
Heat Rate (Higher Heating Value)
Full Load, HHV, net, with degradation (not applicable for all technologies, however, used in calculations) Btu/kW-hr | Btu/kWh
Full Load, HHV, net, with degradation and duct burner heat rate impact, Btu/kW-hr (if not combined cycle with duct burners, use the number above) | Btu/kWh
Full Load, HHV, net, with degradation and fuel oil (Winter) | Btu/kWh
Full Load, HHV, net, with degradation and inlet cooling, NO duct burners (Summer) | Btu/kWh | 8295
Full Load, HHV, net, with degradation, inlet cooling, and duct burner heat rate impact (Summer) | Btu/kWh | 8295
Full Load, HHV, net, with degradation and duct burners, NO inlet cooling heat rate impact | Btu/kWh
Full Load, HHV, net, with degradation, inlet cooling, power augmentation, HRSG, and duct firing. Does not include Fuel Oil Impact. | Btu/kWh | 8295
75% Load, Btu/kW-hr | Btu/kWh | #REF!
50% Load, Btu/kW-hr | Btu/kWh | #REF!
25% Load, Btu/kW-hr | Btu/kWh | #REF!
Average Annual (without duct burners), Btu/kW-hr | Btu/kWh
Estimated efficiency, HHV, full load, degraded, % | %
Energy Storage Roundtrip efficiency (82.67% is average) | %
Capacity Factor, %, for all but energy storage | %
Capacity Factor, %, for energy storage only | %
Annual Generation from Net Rating, MW-hr | MW-hr
Capital Cost, $/kW based on nominal MW | 2019 | Calculations from below. May not add due to rounding.
Asset Purchase Price (not typical build) | $/kW
Steam generator | $/kW
Gasifier | $/kW
Air Separator | $/kW
Steam, Combustion, or Wind Turbines | $/kW
Black Start / Coping Power Combustion Turbines | $/kW
Solar Modules/Panels | $/kW
Inverters | $/kW
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $/kW
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $/kW
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $/kW
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $/kW
Duct Burners | $/kW
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $/kW
Plant Water Treatment (Demin/RO system, tanks, piping) | $/kW
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $/kW
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $/kW
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $/kW
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $/kW
Misc. Pumps and Piping not otherwise included | $/kW
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $/kW
Balance of Plant, BOP (adds from below) | $/kW
IT, Telecomm, SCADA, Metering, Telemetry, Software | $/kW
Security (including cameras), Roads, and Fencing | $/kW
Control Room | $/kW
Other BOP, not otherwise classified | $/kW
Gas Compression | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Freight/Shipping, Importation Duty, Fees, and Taxes | $/kW
Construction Labor | $/kW
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | $/kW
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | $/kW
Owner's Project and Construction Mgmt | $/kW
Developer Margin and Overheads | $/kW
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $/kW
First of a kind and/or Plug Number | $/kW
SO2 Polishing (used with CO2 capture) | $/kW
(AEP) O&M Mobilization Fee for a Buy | $/kW
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | $/kW
Project Contingency for a Build | $/kW
Project Contingency for a Buy | $/kW
EPC Contractor's Fee | $/kW
Spare row | $/kW
Spare row | $/kW
Spare row | $/kW
Fee Subtotal for Build (not used in calculation) | $/kW
Fee Subtotal for Buy (not used in calculation) | $/kW
Total Plant Cost (Overnight EPC) for Build Option | $/kW
Asset Purchase = Buy | $/kW
Owner's Costs | $/kW
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | $/kW
Owner's Costs for a BUY project (excluding Land) | $/kW
Inventory Capital | $/kW
Development and Legal Fees | $/kW
Regulatory Support Fees | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUILD | $/kW
Civil Work (surveys, geotech, grading, site installation) for BUY | $/kW
Interconnection Studies (e.g., Tom Fecho) | $/kW
Enviro and building permits for BUILD | $/kW
Enviro and building permits for BUY | $/kW
AEP-paid sales tax, based on location | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Spare row - check formulas | $/kW
Initial catalyst and chemicals | $/kW
Land Costs (for Buying Land; if Lease = O&M cost) | $/kW
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $/kW
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $/kW
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $/kW
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $/kW
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $/kW
Total Interconnects and Infrastructure (adds from below) | $/kW
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $/kW
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $/kW
Water Supply (Intake) and Wastewater Treatment | $/kW
Site Infrastructure (includes railroad and barge access) | $/kW
Landfill development | $/kW
Initial fuel Inventory (30 days for solid or liquid fuels) | $/kW
Total Plant Cost + Owner's Cost + Interconnects for Build | $/kW
Transmission Upgrade - not currently used | $/kW
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $/kW
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $/kW
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $/kW
Capital Cost | 2019
Asset Purchase Price (not typical build) | $ million
Steam generator | $ million
Gasifier | $ million
Air Separator | $ million
Steam, Combustion, or Wind Turbines | $ million
Black Start / Coping Power Combustion Turbines | $ million
Solar Modules/Panels | $ million
Inverters | $ million
Energy Storage Modules (Racking Frame/Cabinet), Battery management system (BMS), modules | $ million
Energy storage Balance of System BOS (container, monitors, thermal mgmt., fire suppression) | $ million
Energy storage Power conversion system PCS (inverters, switches, breakers, energy mgmt. system) | $ million
HRSG (usually includes SCR/CO; includes ammonia system and tank) | $ million
Duct Burners | $ million
Inlet Cooling (Evaporative Coolers, Fogging, Wet Compression, or Chillers) | $ million
Plant Water Treatment (Demin/RO system, tanks, piping) | $ million
Fuel Oil Capability, including tanks, piping, pumps, and combustor modifications | $ million
LNG Capability, including tanks, piping, vaporizer, compressor, refrigeration. 12-hour storage | $ million
Electrical (for solar = combiner boxes, cables, raceways, etc.; wind = cables; storage = PCS; RTUs) including transformers, grounding grid, lighting | $ million
Materials Handling / Solar Racking / Wind Turbine Tower / Hydro Dam / Gas Collection Systems / Battery Enclosures, etc. | $ million
Misc. Pumps and Piping not otherwise included | $ million
Environmental Controls not otherwise included, such as SCR/CO Catalysts | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Switchyard and Plant Interconnection to the grid (GSU transformer, switchgear, switchyard, breakers, etc.) | $ million
Balance of Plant, BOP (adds from below) | $ million
IT, Telecomm, SCADA, Metering, Telemetry, Software | $ million
Security (including cameras), Roads, and Fencing | $ million
Control Room | $ million
Other BOP, not otherwise classified | $ million
Gas Compression | $ million
Spare row | $ million
Spare row | $ million
Spare row | $ million
Freight/Shipping, Importation Duty, Fees, and Taxes | 3%
Construction Labor | $ million
EPC Fee ((Erection) Contractor's Gen'l Administrative and Profit, risk money, schedule guarantees) | 12%
EPC Services (The outside engineering firm's detailed design engr., procurement, expediting, construction and construction mgmt., QA/QC, startup, and training) | 5%
Owner's Project and Construction Mgmt | 5%
Developer Margin and Overheads | $ million
All CO2 Capture and Compression Equipment (equipment, additional utilities, connections, additional cooling water, etc.) | $ million
First of a kind and/or Plug Number | $ million
SO2 Polishing (used with CO2 capture) | $ million
(AEP) O&M Mobilization Fee for a Buy | $ million
AEP Start-up, Commissioning, and Integration - material and equip., not mgmt. and craft labor | 1.25%
Project Contingency for a Build | 10%
Project Contingency for a Buy | $ million
EPC Contractor's Fee | 8%
Spare row | 0%
Spare row | $ million - Wartsila Indicative EPC price
Spare row | 0%
Fee Subtotal for Build (not used in calculation) | $ million
Fee Subtotal for Buy (not used in calculation) | $ million
Total Plant Cost (Overnight EPC) for Build Option | $ million
Asset Purchase = Buy | $ million
Owner's Costs | 0
Owner's direct Construction cost, (plus prog mgmt, project mgmt, project controls, engineering, procurement, and construction oversight), Contingency, and Management Reserve (aka AEP PMEC) for a BUILD project | 5%
Owner's Costs for a BUY project (excluding Land) | $ million
Inventory Capital | 1%
Development and Legal Fees | 1.25%
Regulatory Support Fees | 1%
Civil Work (surveys, geotech, grading, site installation) for BUILD | $ million
Civil Work (surveys, geotech, grading, site installation) for BUY | $ million
Interconnection Studies (e.g., Tom Fecho) | $ million
Enviro and building permits for BUILD | $ million
Enviro and building permits for BUY | $ million
AEP-paid sales tax, based on location | $ million
Spare row - check formulas | 0
Spare row - check formulas | 0
Spare row - check formulas | 0
Initial catalyst and chemicals | $ million
Land Costs (for Buying Land; if Lease = O&M cost) | $ million
Owner's Costs Subtotal (not used in calculation) for Build, includes Sales Tax and Land | $ million
Owner's Costs Subtotal (not used in calculation) for Buy, includes Sales Tax and Land | $ million
Total Plant Cost (EPC) + Owner's Cost (WITHOUT Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (WITHOUT Sales Tax and Land) for Buy | $ million
Total Plant Cost (EPC) + Owner's Cost (with Sales Tax and Land) for Build | $ million
Asset Purchase + Owner's Cost (with Sales Tax and Land) for Buy | $ million
Total Interconnects and Infrastructure (adds from below) | $ million
Natural Gas Pipeline, Typical 5 Miles, See Inputs sheet | $ million
345 kV Transmission upgrade, 2.5 miles, (connecting to another's lines that the project has to pay for), see Inputs sheet | $ million
Water Supply (Intake) and Wastewater Treatment | $ million
Site Infrastructure (includes railroad and barge access) | $ million
Landfill development | $ million
Initial fuel Inventory (30 days for solid or liquid fuels) | $ million
Total Plant Cost + Owner's Cost + Interconnects for Build | $ million
Total Plant Cost + Owner's Cost + Interconnects for Buy | $ million
Transmission Upgrade - not currently used | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUILD (Included in EPC) | $ million
CO2 Capture and Storage (Retrofit or New Build) Cost for BUY (Included in EPC) | $ million
Total Plant Investment = Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for a Build Project | $ million | 38.5713 | Set Cell C9 in worksheet NEW Data Inputs from Summary to EIA region for specific costs
Total Asset Purchase = Asset Purchase + Owner's Cost + Interconnects + Transmission Upgrade for a Buy Project | $ million
Financial
AFUDC | $ million
Total Project Duration | months
AFUDC %, by operating company or equivalent, avg. annual rate | %
Financial Risk | Text (Low, Average, High)
Investment Life, years | Years (choose from 2, 3, 4, 5, 10, 15, 20, 25, 30, 33, 40, or 50 years) | 30
Economic Cost of Capital (AEP carrying cost, used in annual capital cost), % | %
Overhead / Allocation Rate for AEP operating company, % | %
Annual Capital Cost, $ million for Build | $ million
Annual Capital Cost, $ million for Buy | $ million
Capital Cost $/kW - year for Build | $/kW-year
Capital Cost $/kW - year for Buy | $/kW-year
Total Capital Costs, $/MW-hr | $/MW-hr
Operations & Maintenance (O&M)
Duty Cycle | Text
Capacity Factor | %
Annual Generation | MW-hr
Generating Facility Staff | Number (if part-time, use decimal)
Fixed O&M Costs
Fixed O&M as an EPRI/resource planning calculation, $/kW-year | $/kW-year | 35.8441
Fixed O&M (adds from below), $ million | $ million
Plant Staff Payroll | $ million
General & Administrative Overheads (20% of Payroll) | $ million
Routine Maintenance, typically 1% of major equipment costs or input | $ million
Non-Natural Gas units Major Maintenance = 50% of the Variable O&M Major Maint. (per Resource Planning) | $ million
Utility (aux power and water) costs | $ million
Environmental and safety (monitoring, waste removal, etc.) | $ million
Buildings/grounds, SCADA, Communications, Software licensing, Other | $ million
Maint Expenses Not Otherwise Classified (Asset Management, collection system, substation work, wind turbine blade repairs, solar panel washing, energy storage potential cell upgrades, fuel cell stack replacement, misc. maint.) | $ million
O&M Service Agreement by 3rd party | $ million
Forecasting Services (hydro, wind, and solar) | $ million
Extended Warranties, per year | $ million
Land Lease Costs (not land purchase) | $ million
Natural Gas Major Maint. according to Resource Planning, using EPRI numbers. Calcs from below. | $ million
Property, Tax, and Insurance sum, $/MW-hr | $/MW-hr
Fixed O&M - $/MW-hr | $/MW-hr
Variable O&M Costs
Variable O&M (sums from below), $/MW-hr | $/MW-hr | 5.8007
Consumables and Reagents | $/MW-hr
Major Maintenance = the other 50% of Variable O&M (per Resource Planning). | $/MW-hr
Variable O&M, $ million/year | $ million/yr
EPRI CO2 Capture and Storage Variable O&M, $ million/year, INCREMENTAL | $ million/yr
Total Variable O&M, $ million/year | $ million/year
Total Fixed & Variable O&M, $ million/year | $ million/yr
Total Fixed & Variable O&M, $/MW-hr | $/MW-hr
Production cost (Fuel + VOM) | $/MW-hr
Environmental
Water Usage, gpm | gallons / minute / unit, gpm
Water Usage, gal/year | gallons / year, total plant
Water Usage, gal/MW-hr | gal/MW-hr
* Some data are input, some are calculations. * | Check each emissions line
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
NOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
SOx, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Hg, Uncontrolled at exhaust, lb/TBtu | lb/TBtu
CO, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
CO2, Uncontrolled at exhaust, lb/mmBtu | lb/mmBtu
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, ppm | ppm
NOx, Uncontrolled at exhaust, ppm | ppm
SOx, Uncontrolled at exhaust, ppm | ppm
Hg, Uncontrolled at exhaust, ppm | ppm
CO, Uncontrolled at exhaust, ppm | ppm
CO2, Uncontrolled at exhaust, ppm | ppm
Uncontrolled Rate (at exhaust, vendor or USEPA AP-42)
Particulate Matter PM10, Uncontrolled at exhaust, lb/hour | lb/hour
NOx, Uncontrolled at exhaust, lb/hour | lb/hour
SOx, Uncontrolled at exhaust, lb/hour | lb/hour
Hg, Uncontrolled at exhaust, lb/hour | lb/hour
CO, Uncontrolled at exhaust, lb/hour | lb/hour
CO2, Uncontrolled at exhaust, lb/hour | lb/hour
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/mmBtu | lb/mmBtu
NOx, Controlled, lb/mmBtu | lb/mmBtu | 0.02
SOx, Controlled, lb/mmBtu | lb/mmBtu | 0
Hg, Controlled, lb/TBtu | lb/Tbtu
CO, Controlled, lb/mmBtu | lb/mmBtu | 0.03
CO2, Controlled, lb/mmBtu | lb/mmBtu | 117
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, ppm | ppm
NOx, Controlled, ppm | ppm
SOx, Controlled, ppm | ppm
Hg, Controlled, ppm | ppm
CO, Controlled, ppm | ppm
CO2, Controlled, ppm | ppm
Controlled Rate (Expected Permit Level, Calif. ARB or permit)
Particulate Matter PM10, Controlled, lb/MW-hr | lb/MW-hr
NOx, Controlled, lb/MW-hr | lb/MW-hr
SOx, Controlled, lb/MW-hr | lb/MW-hr
Hg, Controlled, lb/MW-hr | lb/MW-hr
CO, Controlled, lb/MW-hr | lb/MW-hr
CO2, Controlled, lb/MW-hr | lb/MW-hr
Control Efficiency Needed to meet Expected Permit Limit
Particulate Matter PM10 Control Efficiency % | %
NOx Control Efficiency % | %
SOx Control Efficiency % | %
Hg Control Efficiency % | %
CO Control Efficiency % | %
CO2 Control Efficiency % | %
Annual Emission Rate, Controlled
Particulate Matter PM10, Annual Emission Rate, Tons/year | Tons/yr
NOx, Annual Emission Rate, Tons/year | Tons/yr
SOx, Annual Emission Rate, Tons/year | Tons/yr
Hg, Annual Emission Rate, lb/year | lb/yr
CO, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Tons/year | Tons/yr
CO2, Annual Emission Rate, Metric Tonnes/year | Tonnes/yr
Annual Captured Rate (what does not get emitted)
Particulate Matter PM10, Annual Captured Rate, Tons/year | Tons/yr
NOx, Annual Captured Rate, Tons/year | Tons/yr
SOx, Annual Captured Rate, Tons/year | Tons/yr
Hg, Annual Captured Rate, lb/year | lb/yr
CO, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Tons/year | Tons/yr
CO2, Annual Captured Rate, Metric Tonnes/year | Tonnes/yr
Emission Fees (Title V)
Particulate Matter PM10 Emission Fee, $/Ton | $/Ton
NOx Emission Fee, $/Ton | $/Ton
SOx Emission Fee, $/Ton | $/Ton
Hg Emission Fee, $/lb | $/lb
CO Emission Fee, $/Ton | $/Ton
CO2 Emission Fee, $/Ton | $/Ton
Annual Emission Cost
Particulate Matter PM10 Annual Emission Cost, $ million | $ million
NOx Annual Emission Cost, $ million | $ million
SOx Annual Emission Cost, $ million | $ million
Hg Annual Emission Cost, $ million | $ million
CO Annual Emission Cost, $ million | $ million
CO2 Annual Emission Cost, $ million | $ million
Total Emission Cost $ million | $ million
Total Emission Cost, $/MW-hr | $/MW-hr
Energy Storage Capital Cost, Simple $ / kW-hr | $/kW-hr
Levelized Cost of Storage Capital, $/MW-hr | $/MW-hr
Levelized Cost of Storage Fuel, $/MW-hr | $/MW-hr
Levelized Cost of Storage O&M, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/MW-hr | $/MW-hr
LCOS Total without Emissions, $/kW-hr | $/kW-hr
Emissions, $/MW-hr | $/MW-hr
LCOS, Total with Emissions, $/MW-hr | $/MW-hr
First Year Cost of Electricity COE WITHOUT Incentives or Subsidies. NOT applicable to energy storage.
Capital, $/MW-hr | $/MW-hr
Fuel, $/MW-hr | $/MW-hr
O&M, $/MW-hr | $/MW-hr
Total without Emissions, $/MW-hr | $/MW-hr
Emissions, $/MW-hr | $/MW-hr
Total with Emissions, $/MW-hr | $/MW-hr
Transportation and Storage Cost of CO2, $/Tonne | $ / Tonne
Annual Cost of CO2 Transportation and Storage, $ million | $ million
Annual Cost of CO2 Transportation and Storage, $/MW-hr | $/MW-hr
Total Cost of Electricity, with Emissions and CO2, $/MW-hr (NOT applicable to energy storage) | $/MW-hr
Energy Storage Cycles over 1 year | Number
Energy Storage Depth of Discharge, % (80% is typical) | Number
Scheduled / Planned Outage Factor % | %
Planned Outage Hours | Hours
Planned Outage Days | Days
Forced Outage Factor % | %
Forced Outage Avg. Duration | Hours
Availability Factor % | %
Equivalent Availability Factor % | %
Typical Ramp Rate | MW / minute
Down Time (Minimum hrs) | Hours
Run Time (Minimum hrs) | Hours
Construction
Type of Site | Text
Footprint Needed, minimum acres | Acres
Required Gas Pressure, psig | psig
Commercial Availability, years | Years
Permit, License, and Design, years | Years
EPC (Engineer, Procure, Construct), years | Years
Total Project Duration, years | Years
Construction Cash Flow (%) -Yr 1 | % | 20%
Yr 2 | % | 50%
Yr 3 | % | 30%
Yr 4 | % | 0%
Yr 5 | % | 0%
Total | % | 100%
Total, All-in US$ 2019 for this Project | $ / kW
Escalation | $ / kW
Total, All-in As-Spent $US | $ / kW
Total, All-in US$ 2019 for this Project | $ million
Escalation | $ million
Total, All-in As-Spent $US | $ million
Numbers will NOT add due to categorization
Power Block | $ million
Balance of Plant | $ million
CO2 Capture Equipment | $ million
Labor | $ million
Interconnects and Infrastructure | $ million
Owner's costs with Sales Tax and Land | $ million
Project Contingency | $ million
AEP Allocations | $ million
Total Plant Cost + Owner's Cost + Interconnects + Transmission Upgrade for the Project | $ million
Power Block | %
Balance of Plant | %
CO2 Capture Equipment | %
Labor | %
Interconnects and Infrastructure | %
Owner's costs with Sales Tax and Land | %
Project Contingency | %
AEP Allocations | %
Commercially Viable | Year
Start Construction | Year
Commercial Operation Date | Year
Notes and Data Sources | Text
Note on C290: Slight Rounding error: BASE Cost in EIA report is $38.727M EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C314: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C315: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C333: EIA values were provided in 2019$, this value is escalated to a 2020 value based on EIA GDP inflation
Note on C480: 30 Month construction: 12M Dev, Permit, Engineer 18M Plant Construction

## Fuel Cost
[12 empty] | Eastern Bit Coal |  | WEST PRB
|  | COAL $/MBTU |  |  |  | GAS $/MBTU |  |  |  | Nuclear $/MBTU |  | Btu/lb: | 12500 | Btu/lb: | 8800
|  | Average of ML1-COAL (1) | TURK PRB avg of monthly (2) | PJM Growth | SPP Growth | TCO Deliv | PEPL TX-OK | PJM Growth | SPP Growth | Nuclear | Nuclear Growth | lb/MBTU: | 80 | lb/MBTU: | 113.6364 | OpCo: | APCO
| Inflation | PJM | SPP |  |  | PJM | SPP |  |  |  |  | $/ton | $/MBTU | $/ton | $/MBTU | Region: | PJM
2021 |  | 2.0638 |  |  |  | 2.8901 | 2.5842 |  |  | 0.96095 |  | 50.5039 | 2.0202 | 12.4962 | 0.71001
2022 | 1.676% | 2.0567 | 2.3176 | -0.3473% |  | 2.9593 | 2.6518 | 2.398% | 2.617% | 0.98147 | 2.135% | 51.9537 | 2.0781 | 12.7283 | 0.7232 | Year | Coal | Gas
2023 | 1.43% | 2.0997 | 2.3958 | 2.091% | 3.378% | 3.0424 | 2.7074 | 2.806% | 2.095% | 1.003 | 2.191% | 53.2987 | 2.1319 | 13.0739 | 0.74284 | 2023 | 2.0997 | 3.0424
2024 | 1.813% | 2.2183 | 2.5314 | 5.652% | 5.659% | 3.1764 | 2.8547 | 4.404% | 5.442% | 1.0253 | 2.227% | 54.4764 | 2.1791 | 13.4267 | 0.76288 | 2024 | 2.2183 | 3.1764
2025 | 1.986% | 2.2913 | 2.6092 | 3.291% | 3.071% | 3.5222 | 3.1889 | 10.89% | 11.71% | 1.0466 | 2.075% | 55.0814 | 2.2033 | 13.8222 | 0.78535 | 2025 | 2.2913 | 3.5222
2026 | 1.979% | 2.392 | 2.682 | 4.393% | 2.791% | 3.8599 | 3.5374 | 9.587% | 10.93% | 1.0673 | 1.981% | 56.1703 | 2.2468 | 14.203 | 0.80699 | 2026 | 2.392 | 3.8599
2027 | 2.035% | 2.535 | 2.7566 | 5.978% | 2.781% | 4.0826 | 3.8151 | 5.771% | 7.852% | 1.0886 | 1.996% | 57.2058 | 2.2882 | 14.56 | 0.82727 | 2027 | 2.535 | 4.0826
2028 | 2.117% | 2.4761 | 2.8362 | -2.324% | 2.89% | 4.2296 | 4.0188 | 3.599% | 5.337% | 1.1104 | 1.997% | 57.4636 | 2.2985 | 14.8989 | 0.84653 | 2028 | 2.4761 | 4.2296
2029 | 2.169% | 2.4643 | 2.9121 | -0.4779% | 2.674% | 4.2825 | 4.0925 | 1.251% | 1.835% | 1.1326 | 2.007% | 58.4688 | 2.3388 | 15.2504 | 0.8665 | 2029 | 2.4643 | 4.2825
2030 | 2.16% | 2.5175 | 2.97 | 2.16% | 1.989% | 4.2531 | 4.1023 | -0.6868% | 0.2384% | 1.1552 | 1.996% | 59.5675 | 2.3827 | 15.5841 | 0.88546 | 2030 | 2.5175 | 4.2531
2031 | 2.062% | 2.5694 | 3.0277 | 2.062% | 1.943% | 4.2829 | 4.1779 | 0.6994% | 1.842% | 1.178 | 1.97% | 60.5382 | 2.4215 | 15.9073 | 0.90383 | 2031 | 2.5694 | 4.2829
2032 | 2.005% | 2.6209 | 3.0595 | 2.005% | 1.05% | 4.3993 | 4.2685 | 2.719% | 2.169% | 1.2009 | 1.946% | 60.9135 | 2.4365 | 16.232 | 0.92227 | 2032 | 2.6209 | 4.3993
2033 | 1.894% | 2.6706 | 3.1295 | 1.894% | 2.288% | 4.5783 | 4.4525 | 4.069% | 4.311% | 1.2243 | 1.943% | 61.7043 | 2.4682 | 16.628 | 0.94478 | 2033 | 2.6706 | 4.5783
2034 | 1.841% | 2.7197 | 3.2111 | 1.841% | 2.607% | 4.7416 | 4.5975 | 3.568% | 3.257% | 1.2478 | 1.919% | 62.2836 | 2.4913 | 17.0997 | 0.97157 | 2034 | 2.7197 | 4.7416
2035 | 1.759% | 2.7676 | 3.3542 | 1.759% | 4.456% | 4.8325 | 4.6717 | 1.916% | 1.614% | 1.2714 | 1.896% | 62.5994 | 2.504 | 17.6148 | 1.0008 | 2035 | 2.7676 | 4.8325
2036 | 1.729% | 2.8154 | 3.4322 | 1.729% | 2.325% | 4.9285 | 4.771 | 1.987% | 2.127% | 1.2952 | 1.869% | 63.471 | 2.5388 | 18.1644 | 1.0321 | 2036 | 2.8154 | 4.9285
2037 | 1.727% | 2.864 | 3.5121 | 1.727% | 2.328% | 5.1047 | 4.933 | 3.575% | 3.396% | 1.3192 | 1.853% | 64.529 | 2.5812 | 18.7079 | 1.063 | 2037 | 2.864 | 5.1047
2038 | 1.718% | 2.9132 | 3.5939 | 1.718% | 2.329% | 5.2561 | 5.1086 | 2.966% | 3.559% | 1.3434 | 1.835% | 65.5926 | 2.6237 | 19.2202 | 1.0921 | 2038 | 2.9132 | 5.2561
2039 | 1.754% | 2.9643 | 3.6776 | 1.754% | 2.329% | 5.3853 | 5.2128 | 2.458% | 2.039% | 1.3675 | 1.794% | 66.8132 | 2.6725 | 19.5698 | 1.1119 | 2039 | 2.9643 | 5.3853
2040 | 1.851% | 3.0192 | 3.7633 | 1.851% | 2.33% | 5.5096 | 5.3738 | 2.309% | 3.089% | 1.3917 | 1.772% | 68.0148 | 2.7206 | 19.9288 | 1.1323 | 2040 | 3.0192 | 5.5096
2041 | 1.854% | 3.0752 | 3.851 | 1.854% | 2.33% | 5.625 | 5.5116 | 2.094% | 2.565% | 1.416 | 1.749% | 69.2951 | 2.7718 | 20.348 | 1.1561 | 2041 | 3.0752 | 5.625
2042 | 1.853% | 3.1321 | 3.9408 | 1.853% | 2.332% | 5.7904 | 5.6854 | 2.941% | 3.153% | 1.4404 | 1.717% | 70.6029 | 2.8241 | 20.8142 | 1.1826 | 2042 | 3.1321 | 5.7904
2043 | 1.892% | 3.1914 | 4.0327 | 1.892% | 2.332% | 5.9483 | 5.8633 | 2.727% | 3.13% | 1.4645 | 1.675% | 72.0779 | 2.8831 | 21.3619 | 1.2137 | 2043 | 3.1914 | 5.9483
2044 | 1.846% | 3.2503 | 4.1268 | 1.846% | 2.333% | 6.1064 | 6.0398 | 2.658% | 3.009% | 1.4885 | 1.639% | 73.4374 | 2.9375 | 21.9016 | 1.2444 | 2044 | 3.2503 | 6.1064
2045 | 1.839% | 3.3101 | 4.2231 | 1.839% | 2.334% | 6.2854 | 6.2121 | 2.931% | 2.853% | 1.5125 | 1.614% | 74.6384 | 2.9855 | 22.4452 | 1.2753 | 2045 | 3.3101 | 6.2854
2046 | 1.821% | 3.3704 | 4.3217 | 1.821% | 2.335% | 6.4984 | 6.4334 | 3.389% | 3.563% | 1.5365 | 1.584% | 75.7364 | 3.0295 | 22.9757 | 1.3054 | 2046 | 3.3704 | 6.4984
2047 | 1.834% | 3.4322 | 4.4226 | 1.834% | 2.335% | 6.7357 | 6.6357 | 3.651% | 3.143% | 1.5608 | 1.583% | 76.7589 | 3.0704 | 23.5699 | 1.3392 | 2047 | 3.4322 | 6.7357
2048 | 1.812% | 3.4944 | 4.5259 | 1.812% | 2.336% | 6.9572 | 6.8647 | 3.289% | 3.452% | 1.5855 | 1.583% | 77.7315 | 3.1093 | 24.2025 | 1.3751 | 2048 | 3.4944 | 6.9572
2049 | 1.8% | 3.5572 | 4.6316 | 1.8% | 2.335% | 7.1681 | 7.1789 | 3.031% | 4.577% | 1.6106 | 1.584% | 78.6225 | 3.1449 | 24.807 | 1.4095 | 2049 | 3.5572 | 7.1681
2050 | 1.738% | 3.6191 | 4.7399 | 1.738% | 2.338% | 7.4389 | 7.4531 | 3.778% | 3.819% | 1.636 | 1.573% | 79.5268 | 3.1811 | 25.385 | 1.4423 | 2050 | 3.6191 | 7.4389
2051 | 1.719% | 3.6813 | 4.8507 | 1.719% | 2.338% | 7.5668 | 7.5812 | 1.719% | 1.719% | 1.6641 | 1.719% | 0 | 0 | 0 | 0 | 2051 | 3.6813 | 7.5668
2052 | 1.7% | 3.7439 | 4.9641 | 1.7% | 2.338% | 7.6954 | 7.71 | 1.7% | 1.7% | 1.6924 | 1.7% | 0 | 0 | 0 | 0 | 2052 | 3.7439 | 7.6954
2053 | 1.681% | 3.8068 | 5.0803 | 1.681% | 2.341% | 7.8247 | 7.8396 | 1.681% | 1.681% | 1.7208 | 1.681% | 0 | 0 | 0 | 0 | 2053 | 3.8068 | 7.8247
2054 | 1.662% | 3.8701 | 5.1991 | 1.662% | 2.338% | 7.9548 | 7.9699 | 1.662% | 1.662% | 1.7494 | 1.662% | 0 | 0 | 0 | 0 | 2054 | 3.8701 | 7.9548
2055 | 1.643% | 3.9337 | 5.3208 | 1.643% | 2.341% | 8.0855 | 8.1009 | 1.643% | 1.643% | 1.7782 | 1.643% | 0 | 0 | 0 | 0 | 2055 | 3.9337 | 8.0855
2056 | 1.625% | 3.9976 | 5.4454 | 1.625% | 2.342% | 8.2169 | 8.2325 | 1.625% | 1.625% | 1.8071 | 1.625% | #REF! | #REF! | #REF! | #REF! | 2056 | 3.9976 | 8.2169
2057 | 1.607% | 4.0618 | 5.5329 | 1.607% | 1.607% | 8.3489 | 8.3648 | 1.607% | 1.607% | 1.8361 | 1.607% | #REF! | #REF! | #REF! | #REF! | 2057 | 4.0618 | 8.3489
2058 | 1.589% | 4.1264 | 5.6208 | 1.589% | 1.589% | 8.4815 | 8.4977 | 1.589% | 1.589% | 1.8653 | 1.589% | #REF! | #REF! | #REF! | #REF! | 2058 | 4.1264 | 8.4815
2059 | 1.571% | 4.1912 | 5.7091 | 1.571% | 1.571% | 8.6148 | 8.6312 | 1.571% | 1.571% | 1.8946 | 1.571% | #REF! | #REF! | #REF! | #REF! | 2059 | 4.1912 | 8.6148
2060 | 1.553% | 4.2563 | 5.7978 | 1.553% | 1.553% | 8.7486 | 8.7653 | 1.553% | 1.553% | 1.924 | 1.553% | #REF! | #REF! | #REF! | #REF! | 2060 | 4.2563 | 8.7486
2061 | 1.536% | 4.3217 | 5.8868 | 1.536% | 1.536% | 8.883 | 8.8999 | 1.536% | 1.536% | 1.9536 | 1.536% | #REF! | #REF! | #REF! | #REF! | 2061 | 4.3217 | 8.883
2062 | 1.519% | 4.3873 | 5.9763 | 1.519% | 1.519% | 9.0179 | 9.0351 | 1.519% | 1.519% | 1.9832 | 1.519% | #REF! | #REF! | #REF! | #REF! | 2062 | 4.3873 | 9.0179
Notes: (1) |  | Based off the average annual price of coal in Plexos, "2020 03 East Budget Coal Prices.xlsx"
(2) |  | Based off the average annual Turk Received Price, "Turk Fuel Cost in Future Operation (CO2)_PaulD .xlsx"
Note on C4: ApCo, KP, I&M
Note on D4: PSO

## AEP-CCRs
[6 empty] | Appalachian Power Company | [6 empty] | Invesment Life: 30 Years
[6 empty] | Annual Investment Carrying Charges | [6 empty] | OpCo: | APCO
[6 empty] | For Economic Analyses | [6 empty] | Return (1): | 7.52
[6 empty] | As of 12/31/2019 | [6 empty] | Carrying Cost Per Year: | 11.1764
[13 empty] | Region: | PJM
[13 empty] | EIA Region | 11 (PJMW)
Investment Life (Years)
| 2 | 3 | 4 | 5 | 10 | 15 | 20 | 25 | 30 | 33 | 40 | 50
Return (1) | 7.52 | 7.52 | 7.52 | 7.52 | 7.52 | 7.52 | 7.52 | 7.52 | 7.52 | 7.52 | 7.52 | 7.52
Depreciation (2) | 49.0011 | 31.8305 | 23.2313 | 18.0875 | 7.9378 | 4.6942 | 3.16 | 2.2968 | 1.7599 | 1.5295 | 1.1527 | 0.83464
FIT (3) (4) | 1.1283 | 0.81321 | 0.87 | 0.72461 | 0.68732 | 0.82944 | 0.85992 | 0.74881 | 0.67659 | 0.64442 | 0.58937 | 0.53925
Property Taxes, General & Admin Expenses | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.22
Carrying Cost Per Year | 58.8694 | 41.3837 | 32.8413 | 27.5522 | 17.3651 | 14.2637 | 12.7599 | 11.7856 | 11.1764 | 10.914 | 10.4821 | 10.1139
(1) Based on a 100% (as of 12/31/2019) and 0% incremental weighting of capital costs
(2) Sinking Fund annuity with R1 Dispersion of Retirements
(3) Assuming MACRS Tax Depreciation
(4) @ 21% Federal Income Tax Rate

## AFUDC
LLBU | Plant Item | 2020 - Jan | 2020 - Feb | 2020 - Mar | 2020 - Apr | 2020 - May | 2020 - Jun | 2020 - Jul | 2020 - Aug | 2020 - Sep | 2020 - Oct | 2020 - Nov | 2020 - Dec | 2021 - Jan | 2021 - Feb | 2021 - Mar | 2021 - Apr | 2021 - May | 2021 - Jun | 2021 - Jul | 2021 - Aug | 2021 - Sep | 2021 - Oct | 2021 - Nov | 2021 - Dec | 2022 - Jan | 2022 - Feb | 2022 - Mar | 2022 - Apr | 2022 - May | 2022 - Jun | 2022 - Jul | 2022 - Aug | 2022 - Sep | 2022 - Oct | 2022 - Nov | 2022 - Dec | 2023 - Jan | 2023 - Feb | 2023 - Mar | 2023 - Apr | 2023 - May | 2023 - Jun | 2023 - Jul | 2023 - Aug | 2023 - Sep | 2023 - Oct | 2023 - Nov | 2023 - Dec | 2024 - Jan | 2024 - Feb | 2024 - Mar | 2024 - Apr | 2024 - May | 2024 - Jun | 2024 - Jul | 2024 - Aug | 2024 - Sep | 2024 - Oct | 2024 - Nov | 2024 - Dec | 2025 - Jan | 2025 - Feb | 2025 - Mar | 2025 - Apr | 2025 - May | 2025 - Jun | 2025 - Jul | 2025 - Aug | 2025 - Sep | 2025 - Oct | 2025 - Nov | 2025 - Dec | 2026 - Jan | 2026 - Feb | 2026 - Mar | 2026 - Apr | 2026 - May | 2026 - Jun | 2026 - Jul | 2026 - Aug | 2026 - Sep | 2026 - Oct | 2026 - Nov | 2026 - Dec | 2027 - Jan | 2027 - Feb | 2027 - Mar | 2027 - Apr | 2027 - May | 2027 - Jun | 2027 - Jul | 2027 - Aug | 2027 - Sep | 2027 - Oct | 2027 - Nov | 2027 - Dec | 2028 - Jan | 2028 - Feb | 2028 - Mar | 2028 - Apr | 2028 - May | 2028 - Jun | 2028 - Jul | 2028 - Aug | 2028 - Sep | 2028 - Oct | 2028 - Nov | 2028 - Dec | 2029 - Jan | 2029 - Feb | 2029 - Mar | 2029 - Apr | 2029 - May | 2029 - Jun | 2029 - Jul | 2029 - Aug | 2029 - Sep | 2029 - Oct | 2029 - Nov | 2029 - Dec
Wheeling (S898,S988,200,210,413): Wheeling (S898,S988,200,210,413) | CPI Rate: CPI Rate | 3.393% | 3.396% | 3.402% | 3.405% | 3.424% | 3.426% | 3.418% | 3.442% | 3.466% | 3.479% | 3.518% | 3.542% | 3.503% | 3.513% | 3.522% | 3.526% | 3.541% | 3.541% | 3.541% | 3.541% | 3.541% | 3.541% | 3.54% | 3.534% | 3.72% | 3.72% | 3.72% | 3.72% | 3.72% | 3.72% | 3.72% | 3.72% | 3.72% | 3.72% | 3.72% | 3.72% | 3.932% | 3.932% | 3.932% | 3.932% | 3.932% | 3.932% | 3.932% | 3.932% | 3.932% | 3.932% | 3.932% | 3.932% | 3.94% | 3.94% | 3.94% | 3.94% | 3.94% | 3.94% | 3.94% | 3.94% | 3.94% | 3.94% | 3.94% | 3.94% | 3.875% | 3.875% | 3.875% | 3.875% | 3.875% | 3.875% | 3.875% | 3.875% | 3.875% | 3.875% | 3.875% | 3.875% | 4.016% | 4.016% | 4.016% | 4.016% | 4.016% | 4.016% | 4.016% | 4.016% | 4.016% | 4.016% | 4.016% | 4.016% | 4.05% | 4.05% | 4.05% | 4.05% | 4.05% | 4.05% | 4.05% | 4.05% | 4.05% | 4.05% | 4.05% | 4.05% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.168% | 4.168% | 4.168% | 4.168% | 4.168% | 4.168% | 4.168% | 4.168% | 4.168% | 4.168% | 4.168% | 4.168%
Wheeling (S898,S988,200,210,413): Wheeling (S898,S988,200,210,413) | AFUDC Debt Rate: AFUDC Debt Rate | 2.283% | 2.202% | 2.202% | 2.202% | 2.141% | 2.141% | 2.141% | 2.141% | 2.141% | 2.141% | 1.956% | 1.638% | 2.141% | 2.253% | 2.253% | 2.253% | 1.655% | 1.675% | 1.666% | 1.657% | 1.675% | 1.667% | 1.658% | 1.775% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404%
Wheeling (S898,S988,200,210,413): Wheeling (S898,S988,200,210,413) | AFUDC Equity Rate: AFUDC Equity Rate | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 1.942% | 5.468% | 0% | 0% | 0% | 0% | 5.28% | 5.224% | 5.249% | 5.274% | 5.222% | 5.245% | 5.269% | 4.321% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Kingsport (S895,S991,230,260): Kingsport (S895,S991,230,260) | AFUDC Debt Rate: AFUDC Debt Rate | 2.283% | 2.202% | 2.202% | 2.202% | 2.141% | 2.141% | 2.141% | 2.141% | 2.141% | 2.141% | 2.141% | 2.141% | 2.141% | 2.253% | 2.253% | 2.253% | 2.253% | 2.253% | 2.253% | 2.253% | 2.253% | 2.253% | 2.253% | 2.253% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404% | 2.404%
Kingsport (S895,S991,230,260): Kingsport (S895,S991,230,260) | AFUDC Equity Rate: AFUDC Equity Rate | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Kingsport (S895,S991,230,260): Kingsport (S895,S991,230,260) | CPI Rate: CPI Rate | 3.53% | 3.536% | 3.556% | 3.538% | 3.517% | 3.515% | 3.51% | 3.507% | 3.509% | 3.51% | 2.055% | 3.378% | 3.373% | 3.38% | 3.365% | 3.357% | 3.357% | 3.348% | 3.337% | 3.325% | 3.318% | 3.311% | 3.302% | 3.293% | 3.354% | 3.354% | 3.354% | 3.354% | 3.354% | 3.354% | 3.354% | 3.354% | 3.354% | 3.354% | 3.354% | 3.354% | 3.357% | 3.357% | 3.357% | 3.357% | 3.357% | 3.357% | 3.357% | 3.357% | 3.357% | 3.357% | 3.357% | 3.357% | 3.424% | 3.424% | 3.424% | 3.424% | 3.424% | 3.424% | 3.424% | 3.424% | 3.424% | 3.424% | 3.424% | 3.424% | 3.501% | 3.501% | 3.501% | 3.501% | 3.501% | 3.501% | 3.501% | 3.501% | 3.501% | 3.501% | 3.501% | 3.501% | 3.47% | 3.47% | 3.47% | 3.47% | 3.47% | 3.47% | 3.47% | 3.47% | 3.47% | 3.47% | 3.47% | 3.47% | 3.382% | 3.382% | 3.382% | 3.382% | 3.382% | 3.382% | 3.382% | 3.382% | 3.382% | 3.382% | 3.382% | 3.382% | 3.497% | 3.497% | 3.497% | 3.497% | 3.497% | 3.497% | 3.497% | 3.497% | 3.497% | 3.497% | 3.497% | 3.497% | 3.427% | 3.427% | 3.427% | 3.427% | 3.427% | 3.427% | 3.427% | 3.427% | 3.427% | 3.427% | 3.427% | 3.427%
APCO - Corp (S997,140,150,215,RB215): APCO - Corp (S997,140,150,215,RB215) | CPI Rate: CPI Rate | 4.706% | 4.71% | 4.731% | 4.731% | 4.78% | 4.78% | 4.779% | 4.779% | 4.779% | 4.788% | 4.766% | 4.725% | 5.088% | 4.753% | 4.759% | 4.759% | 4.784% | 4.769% | 4.744% | 4.745% | 4.748% | 4.733% | 4.718% | 4.692% | 4.723% | 4.723% | 4.723% | 4.723% | 4.723% | 4.723% | 4.723% | 4.723% | 4.723% | 4.723% | 4.723% | 4.723% | 4.722% | 4.722% | 4.722% | 4.722% | 4.722% | 4.722% | 4.722% | 4.722% | 4.722% | 4.722% | 4.722% | 4.722% | 4.676% | 4.676% | 4.676% | 4.676% | 4.676% | 4.676% | 4.676% | 4.676% | 4.676% | 4.676% | 4.676% | 4.676% | 4.662% | 4.662% | 4.662% | 4.662% | 4.662% | 4.662% | 4.662% | 4.662% | 4.662% | 4.662% | 4.662% | 4.662% | 4.671% | 4.671% | 4.671% | 4.671% | 4.671% | 4.671% | 4.671% | 4.671% | 4.671% | 4.671% | 4.671% | 4.671% | 4.653% | 4.653% | 4.653% | 4.653% | 4.653% | 4.653% | 4.653% | 4.653% | 4.653% | 4.653% | 4.653% | 4.653% | 4.645% | 4.645% | 4.645% | 4.645% | 4.645% | 4.645% | 4.645% | 4.645% | 4.645% | 4.645% | 4.645% | 4.645% | 4.583% | 4.583% | 4.583% | 4.583% | 4.583% | 4.583% | 4.583% | 4.583% | 4.583% | 4.583% | 4.583% | 4.583%
APCO - Corp (S997,140,150,215,RB215): APCO - Corp (S997,140,150,215,RB215) | AFUDC Equity Rate: AFUDC Equity Rate | 2.684% | 2.895% | 3.343% | 4.086% | 4.921% | 4.902% | 4.916% | 4.935% | 4.924% | 4.836% | 4.599% | 4.427% | 4.752% | 4.788% | 4.884% | 4.91% | 4.918% | 4.723% | 4.435% | 4.441% | 4.502% | 4.345% | 4.192% | 3.832% | 4.021% | 4.021% | 4.021% | 4.021% | 4.021% | 4.021% | 4.021% | 4.021% | 4.021% | 4.021% | 4.021% | 4.021% | 4.329% | 4.329% | 4.329% | 4.329% | 4.329% | 4.329% | 4.329% | 4.329% | 4.329% | 4.329% | 4.329% | 4.329% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 4.087% | 3.339% | 3.339% | 3.339% | 3.339% | 3.339% | 3.339% | 3.339% | 3.339% | 3.339% | 3.339% | 3.339% | 3.339% | 3.448% | 3.448% | 3.448% | 3.448% | 3.448% | 3.448% | 3.448% | 3.448% | 3.448% | 3.448% | 3.448% | 3.448% | 3.923% | 3.923% | 3.923% | 3.923% | 3.923% | 3.923% | 3.923% | 3.923% | 3.923% | 3.923% | 3.923% | 3.923% | 3.988% | 3.988% | 3.988% | 3.988% | 3.988% | 3.988% | 3.988% | 3.988% | 3.988% | 3.988% | 3.988% | 3.988% | 3.17% | 3.17% | 3.17% | 3.17% | 3.17% | 3.17% | 3.17% | 3.17% | 3.17% | 3.17% | 3.17% | 3.17%
APCO - Corp (S997,140,150,215,RB215): APCO - Corp (S997,140,150,215,RB215) | AFUDC Debt Rate: AFUDC Debt Rate | 2.352% | 2.312% | 2.331% | 2.401% | 2.435% | 2.444% | 2.438% | 2.428% | 2.433% | 2.431% | 2.412% | 2.519% | 2.613% | 2.431% | 2.435% | 2.422% | 2.431% | 2.43% | 2.414% | 2.405% | 2.409% | 2.399% | 2.39% | 2.378% | 2.437% | 2.437% | 2.437% | 2.437% | 2.437% | 2.437% | 2.437% | 2.437% | 2.437% | 2.437% | 2.437% | 2.437% | 2.474% | 2.474% | 2.474% | 2.474% | 2.474% | 2.474% | 2.474% | 2.474% | 2.474% | 2.474% | 2.474% | 2.474% | 2.477% | 2.477% | 2.477% | 2.477% | 2.477% | 2.477% | 2.477% | 2.477% | 2.477% | 2.477% | 2.477% | 2.477% | 2.463% | 2.463% | 2.463% | 2.463% | 2.463% | 2.463% | 2.463% | 2.463% | 2.463% | 2.463% | 2.463% | 2.463% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.458% | 2.461% | 2.461% | 2.461% | 2.461% | 2.461% | 2.461% | 2.461% | 2.461% | 2.461% | 2.461% | 2.461% | 2.461% | 2.43% | 2.43% | 2.43% | 2.43% | 2.43% | 2.43% | 2.43% | 2.43% | 2.43% | 2.43% | 2.43% | 2.43%
| 2020 - Dec | 10 yr avg
APCO
| AFUDC Debt Rate: AFUDC Debt Rate | 2.45%
| AFUDC Equity Rate: AFUDC Equity Rate | 3.915%
| Total | 6.365%

## GDP
Year |  | EIA GDP reference |  | EIA Economic Indicators.xlsx
|  | Real Gross Domestic Product |  | 2019 Index
2016
2017
2018
2019 | 2019 | 19061.3438 |  | 100%
2020 | 2020 | 19432.1895 | 1.946% | 101.9%
2021 | 2021 | 19772.7754 | 1.753% | 103.7%
2022 | 2022 | 20104.1074 | 1.676% | 105.5%
2023 | 2023 | 20391.5684 | 1.43% | 107%
2024 | 2024 | 20761.3574 | 1.813% | 108.9%
2025 | 2025 | 21173.6699 | 1.986% | 111.1%
2026 | 2026 | 21592.7676 | 1.979% | 113.3%
2027 | 2027 | 22032.2051 | 2.035% | 115.6%
2028 | 2028 | 22498.5645 | 2.117% | 118%
2029 | 2029 | 22986.4941 | 2.169% | 120.6%
2030 | 2030 | 23482.8926 | 2.16% | 123.2%
2031 | 2031 | 23967.2207 | 2.062% | 125.7%
2032 | 2032 | 24447.8223 | 2.005% | 128.3%
2033 | 2033 | 24910.9551 | 1.894% | 130.7%
2034 | 2034 | 25369.457 | 1.841% | 133.1%
2035 | 2035 | 25815.7148 | 1.759% | 135.4%
2036 | 2036 | 26262.1406 | 1.729% | 137.8%
2037 | 2037 | 26715.668 | 1.727% | 140.2%
2038 | 2038 | 27174.5898 | 1.718% | 142.6%
2039 | 2039 | 27651.1484 | 1.754% | 145.1%
2040 | 2040 | 28162.8828 | 1.851% | 147.7%
2041 | 2041 | 28685.1406 | 1.854% | 150.5%
2042 | 2042 | 29216.5879 | 1.853% | 153.3%
2043 | 2043 | 29769.3555 | 1.892% | 156.2%
2044 | 2044 | 30318.9316 | 1.846% | 159.1%
2045 | 2045 | 30876.5273 | 1.839% | 162%
2046 | 2046 | 31438.8027 | 1.821% | 164.9%
2047 | 2047 | 32015.2969 | 1.834% | 168%
2048 | 2048 | 32595.2969 | 1.812% | 171%
2049 | 2049 | 33181.9805 | 1.8% | 174.1% | Average Inflation 30 years | 1.858%
2050 | 2050 | 33758.8398 | 1.738% | 177.1% | Growth Rate last 5 years | -1.119%
2051 | 2051 |  | 1.719% | 180.2%
2052 | 2052 |  | 1.7% | 183.2%
2053 | 2053 |  | 1.681% | 186.3%
2054 | 2054 |  | 1.662% | 189.4%
2055 | 2055 |  | 1.643% | 192.5%
2056 | 2056 |  | 1.625% | 195.6%
2057 | 2057 |  | 1.607% | 198.8%
2058 | 2058 |  | 1.589% | 201.9%
2059 | 2059 |  | 1.571% | 205.1%
2060 | 2060 |  | 1.553% | 208.3%
| 2061 |  | 1.536% | 211.5%
| 2062 |  | 1.519% | 214.7%
| 2063 |  | 1.502% | 217.9%
| 2064 |  | 1.485% | 221.2%
| 2065 |  | 1.468% | 224.4%
| 2066 |  | 1.452% | 227.7%
| 2067 |  | 1.436% | 230.9%
| 2068 |  | 1.42% | 234.2%
| 2069 |  | 1.404% | 237.5%
| 2070 |  | 1.388% | 240.8%
| 2071 |  | 1.373% | 244.1%
| 2072 |  | 1.357% | 247.4%
| 2073 |  | 1.342% | 250.7%
| 2074 |  | 1.327% | 254.1%
| 2075 |  | 1.312% | 257.4%
| 2076 |  | 1.297% | 260.7%
| 2077 |  | 1.283% | 264.1%
| 2078 |  | 1.269% | 267.4%
| 2079 |  | 1.254% | 270.8%
| 2080 |  | 1.24% | 274.1%

## Allow Cst
AEP System
CO2 Allowance Price Forecast
| SO2 | NOX Annual | CO2
| Allowance | Allowance | Allowance
Year | Price | Price | Price | Infl Rate
2021 | 0 | 0 | 0 | 0%
2022 | 0 | 0 | 0 | 1.946%
2023 | 0 | 0 | 0 | 1.753%
2024 | 0 | 0 | 0 | 1.676%
2025 | 0 | 0 | 0 | 1.43%
2026 | 0 | 0 | 0 | 1.813%
2027 | 0 | 0 | 0 | 1.986%
2028 | 0 | 0 | 0 | 1.979%
2029 | 0 | 0 | 0 | 2.035%
2030 | 0 | 0 | 0 | 2.117%
2031 | 0 | 0 | 0 | 2.169%
2032 | 0 | 0 | 0 | 2.16%
2033 | 0 | 0 | 0 | 2.062%
2034 | 0 | 0 | 0 | 2.005%
2035 | 0 | 0 | 0 | 1.894%
2036 | 0 | 0 | 0 | 1.841%
2037 | 0 | 0 | 0 | 1.759%
2038 | 0 | 0 | 0 | 1.729%
2039 | 0 | 0 | 0 | 1.727%
2040 | 0 | 0 | 0 | 1.718%
2041 | 0 | 0 | 0 | 1.754%
2042 | 0 | 0 | 0 | 1.851%
2043 | 0 | 0 | 0 | 1.854%
2044 | 0 | 0 | 0 | 1.853%
2045 | 0 | 0 | 0 | 1.892%
2046 | 0 | 0 | 0 | 1.846%
2047 | 0 | 0 | 0 | 1.839%
2048 | 0 | 0 | 0 | 1.821%
2049 | 0 | 0 | 0 | 1.834%
2050 | 0 | 0 | 0 | 1.812%
2051 | 0 | 0 | 0 | 1.8%
2052 | 0 | 0 | 0 | 1.738%
2053 | 0 | 0 | 0 | 1.719%
2054 | 0 | 0 | 0 | 1.7%
2055 | 0 | 0 | 0 | 1.681%
2056 | 0 | 0 | 0 | 1.662%
2057 | 0 | 0 | 0 | 1.643%
2058 | 0 | 0 | 0 | 1.625%
2059 | 0 | 0 | 0 | 1.607%
2060 | 0 | 0 | 0 | 1.589%

## Y2020H1 Annual_Prices-Nominal
EIA | Power Prices ($/MWh) -Nominal $'s | [5 empty] | Coal ($/ton) FOB -Nominal $'s | [9 empty] | Natural Gas ($/mmbtu) -Nominal $'s | [7 empty] | Uranium Fuel UO2 ($/mmbtu) -Nominal $'s | Emissions ($/ton) -Nominal $'s |  |  | ($/short ton) -Nominal $'s | Heat Rates (mmbtu/MWh) |  | Capacity Prices ($/MW-day) -Nominal $'s |  | Renewable Energy Subsidies ** ($/MWh) -Nominal $'s | Inflation Factor
| PJM_AEP |  | SPP_Central |  | SPP_KSMO |  | 12395 Btu/lb 1.6# SO2 | 12500 Btu/lb 1.6# SO2 | 12000 Btu/lb 1.2# SO2 | 12000 Btu/lb 1.67# SO2 | 12500 Btu/lb 6# SO2 | 13000 Btu/lb 4# SO2 | 11512 Btu/lb 4.3# SO2 | 8800 Btu/lb 0.8# SO2 | 8400 Btu/lb 0.8# SO2 | 11700 Btu/lb 0.9# SO2
Year | On-Peak | Off-Peak | On-Peak | Off-Peak | On-Peak | Off-Peak | CAPP | CAPP CSX-Rail | CAPP Compliance | CAPP NYMEX | NAPP High Sulfur | NAPP Med Sulfur | I-Basin | PRB 8800 | PRB 8400 | Colorado | Henry Hub | TCO Pool | Dominion South Point Pool | TCO Deliv | HSC | PEPL TX-OK | Swing Service Adder |  |  | SO2 | NOX Annual | NOX Summer | CO2 | AEP GEN HUB - HR | SPP_Central - HR | AEP GEN HUB Hub Cap. | SPP_Central/KSMO Cap.
2021 | 25.8275 | 20.2833 | 23.1275 | 16.855 | 23.0425 | 16.7633 | 59.6318 | 59.6318 | 67.3224 | 59.6318 | 50.5039 | 52.9336 | 46.0094 | 12.4962 | 12.4962 | 42.8888 | 2.6167 | 2.37 | 2.3033 | 2.6158 | 2.5375 | 2.31 | 0.27422 | 0 | 0.96095 | 0 | 0 | 0 | 0 | 11.1299 | 10.2877 | 113.5542 | 25 | 11 | 0.953%
2022 | 26.83 | 20.4517 | 24.4525 | 16.9442 | 24.3675 | 16.8608 | 62.2755 | 62.2755 | 69.32 | 62.2755 | 51.9537 | 54.6057 | 46.9418 | 12.7283 | 12.7283 | 44.1329 | 2.68 | 2.43 | 2.3633 | 2.6792 | 2.5992 | 2.3717 | 0.28018 | 0 | 0.98147 | 0 | 0 | 0 | 0 | 11.2693 | 10.5732 | 130.18 | 25 | 11 | 2.135%
2023 | 28.8892 | 21.6175 | 26.6983 | 18.3533 | 26.605 | 18.2658 | 64.5605 | 64.5605 | 71.6748 | 64.5605 | 53.2987 | 56.3586 | 47.4365 | 13.0739 | 13.0739 | 45.2835 | 2.78 | 2.5058 | 2.4175 | 2.7567 | 2.7108 | 2.4217 | 0.28573 | 0 | 1.003 | 0 | 0 | 0 | 0 | 11.8241 | 11.363 | 120.36 | 25 | 11 | 2.191%
2024 | 29.5075 | 22.4067 | 27.6667 | 19.0817 | 27.5308 | 18.9575 | 66.9839 | 66.9839 | 74.3048 | 66.9839 | 54.4764 | 57.7257 | 47.9064 | 13.4267 | 13.4267 | 46.3571 | 2.9508 | 2.6333 | 2.5317 | 2.885 | 2.875 | 2.5633 | 0.29138 | 0 | 1.0253 | 0 | 0 | 0 | 0 | 11.4898 | 11.0986 | 152.47 | 30.46 | 11 | 2.227%
2025 | 30.3483 | 23.8408 | 28.0492 | 20.0792 | 28.0358 | 19.9875 | 69.3868 | 69.3868 | 77.2263 | 69.3868 | 55.0814 | 57.9792 | 48.4043 | 13.8222 | 13.8222 | 47.4276 | 3.2742 | 2.9667 | 2.86 | 3.225 | 3.1958 | 2.8917 | 0.29721 | 0 | 1.0466 | 0 | 0 | 0 | 0 | 10.4143 | 9.9007 | 184.72 | 47.7 | 12.2 | 2.075%
2026 | 30.4825 | 24.9975 | 28.0125 | 20.8858 | 27.9542 | 20.7617 | 71.8977 | 71.8977 | 80.5935 | 71.8977 | 56.1703 | 59.1656 | 48.9849 | 14.203 | 14.203 | 48.5607 | 3.6333 | 3.2925 | 3.1817 | 3.5567 | 3.5667 | 3.2342 | 0.30321 | 0 | 1.0673 | 0 | 0 | 0 | 0 | 9.3826 | 8.7872 | 217.26 | 64.675 | 12.2 | 1.981%
2027 | 31.4567 | 26.0575 | 29.5608 | 21.9692 | 29.47 | 21.8325 | 74.4798 | 74.4798 | 84.3441 | 74.4798 | 57.2058 | 60.6007 | 49.5964 | 14.56 | 14.56 | 49.7233 | 3.9042 | 3.5067 | 3.3942 | 3.7733 | 3.8325 | 3.5058 | 0.30931 | 0 | 1.0886 | 0 | 0 | 0 | 0 | 9.0601 | 8.5348 | 234.2812 | 103.29 | 12.2 | 1.996%
2028 | 32.2708 | 26.56 | 30.8283 | 22.77 | 30.7 | 22.6208 | 77.1345 | 77.1345 | 88.4586 | 77.1345 | 57.4636 | 61.9978 | 50.1152 | 14.8989 | 14.8989 | 50.9053 | 4.1058 | 3.645 | 3.5292 | 3.9142 | 4.0308 | 3.7033 | 0.31543 | 0 | 1.1104 | 0 | 0 | 0 | 0 | 8.9397 | 8.4316 | 238.9571 | 147.49 | 12.2 | 1.997%
2029 | 32.1242 | 26.6142 | 30.6833 | 22.8408 | 30.5425 | 22.68 | 79.8032 | 79.8032 | 92.802 | 79.8032 | 58.4688 | 63.3829 | 50.3659 | 15.2504 | 15.2504 | 52.1046 | 4.2208 | 3.6917 | 3.5583 | 3.9608 | 4.1475 | 3.7708 | 0.32168 | 0 | 1.1326 | 0 | 0 | 0 | 0 | 8.7894 | 8.2397 | 243.728 | 190.57 | 12.2 | 2.007%
2030 | 30.6208 | 26.3658 | 27.5942 | 22.3192 | 27.5117 | 22.1767 | 82.4157 | 82.4157 | 96.9693 | 82.4157 | 59.5675 | 64.7016 | 51.398 | 15.5841 | 15.5841 | 53.2881 | 4.2575 | 3.6558 | 3.465 | 3.925 | 4.1858 | 3.7742 | 0.3281 | 0 | 1.1552 | 0 | 0 | 0 | 0 | 8.445 | 7.3932 | 248.6186 | 232.275 | 12.2 | 1.996%
2031 | 29.1067 | 26.0208 | 23.7533 | 21.8558 | 23.7225 | 21.7042 | 85.0923 | 85.0923 | 100.3317 | 85.0923 | 60.5382 | 66.0101 | 52.6266 | 15.9073 | 15.9073 | 54.4774 | 4.2942 | 3.6783 | 3.4833 | 3.9483 | 4.2067 | 3.8433 | 0.33452 | 0 | 1.178 | 0 | 0 | 0 | 0 | 7.9721 | 6.2486 | 253.5812 | 253.5812 | 14.7 | 1.97%
2032 | 29.0017 | 26.3458 | 21.735 | 21.9617 | 21.6925 | 21.7992 | 87.8579 | 87.8579 | 103.5739 | 87.8579 | 60.9135 | 67.2925 | 53.8325 | 16.232 | 16.232 | 55.6175 | 4.415 | 3.7867 | 3.5858 | 4.0583 | 4.3283 | 3.9275 | 0.34098 | 0 | 1.2009 | 0 | 0 | 0 | 0 | 7.7074 | 5.5941 | 258.5772 | 258.5772 | 14.7 | 1.946%
2033 | 29.9342 | 27.3467 | 22.6283 | 22.7675 | 22.6042 | 22.5983 | 90.615 | 90.615 | 106.903 | 90.615 | 61.7043 | 68.4681 | 55.051 | 16.628 | 16.628 | 56.7646 | 4.5975 | 3.9558 | 3.7533 | 4.2308 | 4.5158 | 4.105 | 0.34748 | 0 | 1.2243 | 0 | 0 | 0 | 0 | 7.6168 | 5.5686 | 263.6084 | 263.6084 | 13.4 | 1.943%
2034 | 31.0017 | 28.4383 | 24.1725 | 24.2658 | 24.14 | 24.0892 | 93.7616 | 93.7616 | 110.3504 | 93.7616 | 62.2836 | 68.8112 | 56.1633 | 17.0997 | 17.0997 | 57.9881 | 4.7667 | 4.1117 | 3.9008 | 4.3875 | 4.6858 | 4.2433 | 0.35415 | 0 | 1.2478 | 0 | 0 | 0 | 0 | 7.5772 | 5.7416 | 268.7304 | 268.7304 | 12.2 | 1.919%
2035 | 31.9558 | 29.5867 | 24.3417 | 24.695 | 24.305 | 24.5125 | 96.9163 | 96.9163 | 113.8943 | 96.9163 | 62.5994 | 68.7435 | 57.2688 | 17.6148 | 17.6148 | 59.3512 | 4.8608 | 4.1942 | 3.9808 | 4.4717 | 4.7775 | 4.3108 | 0.36084 | 0 | 1.2714 | 0 | 0 | 0 | 0 | 7.6643 | 5.7002 | 273.8868 | 273.8868 | 11 | 1.896%
2036 | 32.1908 | 29.9675 | 25.0283 | 25.175 | 24.995 | 24.9958 | 100.1378 | 100.1378 | 117.5842 | 100.1378 | 63.471 | 69.8293 | 58.3765 | 18.1644 | 18.1644 | 60.8293 | 4.9608 | 4.2792 | 4.0642 | 4.5608 | 4.9058 | 4.4033 | 0.3677 | 0 | 1.2952 | 0 | 0 | 0 | 0 | 7.5688 | 5.7446 | 279.0793 | 279.0793 | 11 | 1.869%
2037 | 33.9917 | 31.53 | 27.1458 | 26.5983 | 27.1175 | 26.4192 | 103.4457 | 103.4457 | 121.4136 | 103.4457 | 64.529 | 71.2796 | 59.6778 | 18.7079 | 18.7079 | 62.3967 | 5.1408 | 4.4458 | 4.2233 | 4.73 | 5.0917 | 4.5583 | 0.37471 | 0 | 1.3192 | 0 | 0 | 0 | 0 | 7.6865 | 6.0087 | 284.2962 | 284.2962 | 9.8 | 1.853%
2038 | 35.8008 | 33.3583 | 28.7408 | 27.885 | 28.7167 | 27.6942 | 106.8567 | 106.8567 | 125.2961 | 106.8567 | 65.5926 | 72.6311 | 60.8746 | 19.2202 | 19.2202 | 64.0389 | 5.3008 | 4.5892 | 4.3642 | 4.8742 | 5.2633 | 4.7267 | 0.38194 | 0 | 1.3434 | 0 | 0 | 0 | 0 | 7.8383 | 6.1322 | 289.5636 | 289.5636 | 7.3 | 1.835%
2039 | 36.58 | 34.1575 | 29.5617 | 28.5108 | 29.5467 | 28.3242 | 110.3975 | 110.3975 | 129.0348 | 110.3975 | 66.8132 | 74.159 | 62.1945 | 19.5698 | 19.5698 | 65.7318 | 5.4317 | 4.7083 | 4.4783 | 4.9958 | 5.4142 | 4.8233 | 0.38944 | 0 | 1.3675 | 0 | 0 | 0 | 0 | 7.8037 | 6.1813 | 294.8758 | 294.8758 | 8.6 | 1.794%
2040 | 38.0867 | 35.4858 | 31.2292 | 29.7117 | 31.245 | 29.5217 | 114.0096 | 114.0096 | 132.9985 | 114.0096 | 68.0148 | 75.5954 | 63.3683 | 19.9288 | 19.9288 | 67.4746 | 5.5608 | 4.8217 | 4.5858 | 5.1125 | 5.5358 | 4.9767 | 0.39711 | 0 | 1.3917 | 0 | 0 | 0 | 0 | 7.9326 | 6.3219 | 300.1663 | 300.1663 | 7.3 | 1.772%
2041 | 38.7833 | 36.39 | 31.7033 | 30.6158 | 31.7158 | 30.4183 | 117.7167 | 117.7167 | 137.4683 | 117.7167 | 69.2951 | 77.3193 | 64.5721 | 20.348 | 20.348 | 69.2898 | 5.6833 | 4.93 | 4.69 | 5.22 | 5.6625 | 5.1067 | 0.40496 | 0 | 1.416 | 0 | 0 | 0 | 0 | 7.9056 | 6.2512 | 305.4866 | 305.4866 | 7.3 | 1.749%
2042 | 40.12 | 37.4883 | 33.725 | 32.21 | 33.7275 | 32.0017 | 121.0956 | 121.0956 | 142.2234 | 121.0956 | 70.6029 | 80.0506 | 65.9641 | 20.8142 | 20.8142 | 71.1581 | 5.8533 | 5.0825 | 4.8367 | 5.3775 | 5.8408 | 5.2725 | 0.4129 | 0 | 1.4404 | 0 | 0 | 0 | 0 | 7.9299 | 6.4363 | 310.8282 | 310.8282 | 7.3 | 1.717%
2043 | 41.25 | 38.3475 | 35.5692 | 33.9217 | 35.6117 | 33.71 | 123.5606 | 123.5606 | 146.5693 | 123.5606 | 72.0779 | 85.2291 | 67.3626 | 21.3619 | 21.3619 | 72.9881 | 6.015 | 5.2292 | 4.98 | 5.5275 | 6.0158 | 5.4425 | 0.42083 | 0 | 1.4645 | 0 | 0 | 0 | 0 | 7.9258 | 6.5742 | 316.1652 | 316.1652 | 6.1 | 1.675%
2044 | 43.1508 | 40.0092 | 37.8117 | 35.55 | 37.9092 | 35.34 | 126.8363 | 126.8363 | 151.0726 | 126.8363 | 73.4374 | 88.2631 | 68.6568 | 21.9016 | 21.9016 | 74.8482 | 6.1775 | 5.3783 | 5.1233 | 5.6775 | 6.19 | 5.6108 | 0.42894 | 0 | 1.4885 | 0 | 0 | 0 | 0 | 8.0583 | 6.7759 | 321.4625 | 321.4625 | 4.9 | 1.639%
2045 | 45.0058 | 41.6317 | 39.6208 | 37.0483 | 39.695 | 36.83 | 130.9131 | 130.9131 | 155.9762 | 130.9131 | 74.6384 | 90.8522 | 70.1529 | 22.4452 | 22.4452 | 76.8274 | 6.365 | 5.5467 | 5.2867 | 5.8483 | 6.37 | 5.775 | 0.43707 | 0 | 1.5125 | 0 | 0 | 0 | 0 | 8.1484 | 6.8982 | 326.7306 | 326.7306 | 2.4 | 1.614%
2046 | 46.7275 | 43.08 | 42.1333 | 39.06 | 42.2 | 38.8292 | 135.2432 | 135.2432 | 161.0727 | 135.2432 | 75.7364 | 93.0902 | 71.5798 | 22.9757 | 22.9757 | 78.9111 | 6.5792 | 5.7467 | 5.4817 | 6.0533 | 6.5767 | 5.9883 | 0.4451 | 0 | 1.5365 | 0 | 0 | 0 | 0 | 8.1696 | 7.0662 | 332.0038 | 332.0038 | 1.2 | 1.584%
2047 | 48.5367 | 44.8025 | 44.0192 | 40.885 | 44.0758 | 40.645 | 139.7556 | 139.7556 | 166.2836 | 139.7556 | 76.7589 | 95.3928 | 73.1329 | 23.5699 | 23.5699 | 81.1171 | 6.8242 | 5.9725 | 5.7017 | 6.2825 | 6.8325 | 6.1825 | 0.45316 | 0 | 1.5608 | 0 | 0 | 0 | 0 | 8.1612 | 7.1572 | 337.2636 | 337.2636 | 0 | 1.583%
2048 | 50.3933 | 46.5342 | 45.79 | 42.4 | 45.8508 | 42.1525 | 144.6475 | 144.6475 | 171.912 | 144.6475 | 77.7315 | 97.8643 | 74.7103 | 24.2025 | 24.2025 | 83.4505 | 7.0508 | 6.1833 | 5.9075 | 6.4958 | 7.0558 | 6.4033 | 0.46137 | 0 | 1.5855 | 0 | 0 | 0 | 0 | 8.1807 | 7.1874 | 342.6031 | 342.6031 | 0 | 1.583%
2049 | 51.93 | 47.9325 | 47.9283 | 44.1875 | 48.0283 | 43.9342 | 150.0037 | 150.0037 | 178.0198 | 150.0037 | 78.6225 | 101.0391 | 76.2844 | 24.807 | 24.807 | 85.8687 | 7.2658 | 6.3808 | 6.0992 | 6.6983 | 7.2767 | 6.7092 | 0.46972 | 0 | 1.6106 | 0 | 0 | 0 | 0 | 8.1677 | 7.1717 | 348.0264 | 348.0264 | 0 | 1.584%
2050 | 53.3792 | 49.2625 | 49.9058 | 45.8392 | 50.0017 | 45.57 | 155.0899 | 155.0899 | 183.8301 | 155.0899 | 79.5268 | 105.134 | 77.8553 | 25.385 | 25.385 | 88.171 | 7.54 | 6.635 | 6.3475 | 6.9592 | 7.5517 | 6.9733 | 0.47972 | 0 | 1.636 | 0 | 0 | 0 | 0 | 8.0738 | 7.1821 | 353.5399 | 353.5399 | 0 | 1.573%