## Numbers
KY PSC Case No. 2021-00183
AG 1-73
Attachment A
Page 1 of 5
Cross Bore Program
2017-2020
| # Laterals | Lateral Footage | Sanitary Footage | Storm Footage | # Push | Push Footages | Total Miles Cameraed | Total Spent | Total #Cross Bores
2017 | 81 | 3281 | 10823 | 4149 | 149 | 7069 | 4.8 | 46969 | 4
2018 | 876 | 29765 | 46387 | 28003 | 101 | 6103 | 20.88 | 237723 | 22
2019 | 586 | 22704 | 22316 | 9289 | 226 | 13683 | 12.9 | 146985 | 17
2020 | 177 | 7478 | 6591 | 2788 | 50 | 2853 | 3.7 | 77145 | 13
2021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 1720 | 63228 | 86117 | 44229 | 526 | 29708 | 42.28 | 508822 | 56

## 2017
KY PSC Case No. 2021-00183
AG 1-73
Attachment A
Page 2 of 5
Log # | Address | City | [7 empty] | Employee Reporting Conflict |  |  | Who Found? | How Found? |  | PSID |  | In Top 5% of Model | Date Found | Found Job Order |  | Installation Job Order |  | Date Installed |  | Damaged/Penetrated Structure (Size) |  |  |  |  | Material Type & Size of Company Facility Involved |  |  |  | Camera footage | Details of Cross Bore | Remediation Plan | [7 empty] | PSP PROJECT LEGEND |  |  |  | CHARGED TO:
|  |  | State | Zip | Country | County Name | County # | Mapped on GIS | Entered on Risk Model |  | Employee Phone Number | Employee email | Homeowner-Plumber / Municipality / Construction / Operations / Contractor |  | TCC |  | Map # | Map Ranking on Risk Model? |  |  | JO Type |  | JO TYPE |  | Installed By Contractor Company | Main Sanitary Sewer | Lateral Sanitary Sewer | Main Storm Sewer | Lateral Storm Sewer | Other Structure- specify | P - PLASTIC S- STEEL BS - BARE STL CS - CTD STL WT - WLD TRTD Main | P - PLASTIC BS - BARE STL Service | Leak? | Caused by Sewer Cleanout |  |  |  | Remed Job Order | JO Type | Remed Completion Date | ESIS Claim # | Status | Received Notify Form? | Charged to Legacy CB Project? | IRP -- INFRASTRUCTURE REPLACEMENT PROGRAM AMRP -- MAIN REPLACEMENT PROGRAM LEGACY CB -- CROSS BORE PRIOR TO 7/1/2007 NON-LEGACY CB -- CROSS BORE SINCE 7/1/2007 | PROJECT CHARGE TO: IRP / AMRP / LEGACY CB / OPERATIONS / CONTRACTOR | Remediation Costs | Company/ Contractor Remediated? | JO # | WM/DI | BU | ACCOUNT | HOME DP | CHRG DP | AFFIL | ACTIV | PROJECT | FACIL | PROJCD
17-1 | 132 PARIS AV | Lexington | KY | 40505 | USA | Fayette | 067 | YES | No |  |  |  | City of Lex | Camera | 2621 | 100290731 | 6720212B | na | 2017-07-24 | 17-5272864-00 | 2313 | 99-3962894-00 | 565 | 1999-07-19 | Contractor | 8" | [5 empty] | 1 1/4"P | NO |  | na | 1 1/4" P SERVICE LINE BORED THROUGH 8" SANITARY SEWER. Shawn D. states SL was not leaking. "Break" in comments refers to where he cut it to remove SL. | REMOVE SERVICE LINE | 17-5272864-00 | 2313 | 2017-07-24 |  | Executed | [8 empty] | 32 | 892 | 326210 | 326210 | 32 | 2313
17-2 | 835 Bryan Av | Lexington | KY | 40505 | USA | Fayette | 067 | YES | No | [5 empty] | 2621 | NA | 6720212F | na | 2017-06-29 | 17-5211603-00 | 2312 |  |  | 1/1/1800 | Company | [5 empty] | 3" BS |  | NO |  | na | 3" BS main in sewer manhole. Appears mh was bricked around main. Main line leak was close to mh and main was found in mh while checking for migration per Shannon B. | replaced 24' of 3" bs main | 17-5211672-00 | 2211 | 2017-07-01 |  | Executed | [8 empty] | 32 | 10700001 | 326210 | 326210 | 32 | 557 | 3200557 | WP7160 | AMRCB
17-3 | Trade Center Dr & New Circle Rd | Lexington | KY | 40505 | USA | Fayette | 067 | YES | No |  |  |  | City of Lex | Camera | 2621 | NA | 6720212P | na | 2017-09-21 |  |  | 96-0265056-00 | 561 | 1997-11-07 | Contractor | X |  |  |  |  | 2" P |  | No |  | na | Craig Prater with LFUCG reported cross bore found with camera | Remove gas main from Sanitary Main line | 17-5493830-00 | 2311 | IP |  | IP | [8 empty] | 32 | 8740000 | 326210 | 326210 | 32 | 2311
17-4 | 1755 Timber Creek Dr | Lexington | KY | 40509 | USA | Fayette | 067 | YES | No |  |  |  | Buchanan Cont. | Camera | 2621 | 500437301 | 6724208H | na | 2017-11-22 | 17-5595031-00 | 2312 | 96-2427454-00 | 563 | 1996-02-09 | Contractor |  |  | X |  |  |  | 1/2" P | No |  |  | 1/2" plastic service for 1755 Timber Creek cross bored through Storm main | Remove service & repair sewer | 17-5680514-00 | 2313 | 2017-12-27 |  | Executed | [8 empty] | 32 | 892 | 326210 | 326210 | 32 | 2313
Note on B9: Wells \ James \ D: Work is complete
Note on AQ9: Wells \ James \ D: Work is complete.

## 2018
KY PSC Case No. 2021-00183
AG 1-73
Attachment A
Page 3 of 5
Details | [9 empty] | Employee Reporting Conflict |  |  | Found by information |  | Miscellenous | [9 empty] | Damaged/Penetrated Structure (Size) |  |  |  |  | Material Type & Size of Company Facility Involved |  | Additional Information | [11 empty] | PSP PROJECT LEGEND |  |  |  | CHARGED TO:
Log # | Address | City | State | Zip | Country | County Name | County # | Mapped on GIS | Entered on Risk Model | Name | Phone Number | Email | Homeowner-Plumber / Municipality / Construction / Operations / Contractor | How Found? | TCC | PSID | Map # | In Top 5% of Model Ranking on Risk Model? | Date Found | Found Job Order | JO Type | Installation Job Order | JO TYPE | Date Installed | Main Sanitary Sewer | Lateral Sanitary Sewer | Main Storm Sewer | Lateral Storm Sewer | Other Structure- specify | P - PLASTIC S- STEEL BS - BARE STL CS - CTD STL WT - WLD TRTD Main | P - PLASTIC BS - BARE STL Service | Leak? | Caused by Sewer Cleanout | Camera footage | Details of Cross Bore | Remediation Plan | Remed Job Order | JO Type | Remed Completion Date | ESIS Claim # | Status | Received Notify Form? | Charged to Legacy CB Project? | IRP -- INFRASTRUCTURE REPLACEMENT PROGRAM AMRP -- MAIN REPLACEMENT PROGRAM LEGACY CB -- CROSS BORE PRIOR TO 7/1/2008 NON-LEGACY CB -- CROSS BORE SINCE 7/1/2008 | PROJECT CHARGE TO: IRP / AMRP / LEGACY CB / OPERATIONS / CONTRACTOR | Remediation Costs | Company/ Contractor Remediated? | JO # | WM/DI | BU | ACCOUNT | HOME DP | CHRG DP | AFFIL | ACTIV | PROJECT | FACIL | PROJCD
18-1 | 1115 Manchester St | Lexington | KY | 40508 | USA | Fayette | 067 | [5 empty] | City of Lex | Camera | 2621 | 500213382 | 6716212G | NA | 2018-02-27 | N/A |  | N/A |  | 1992-10-06 | X | [5 empty] | 1" P | NO |  |  | 1" P service bored through sanitary main in middle of street | Remove SL from sewer | 18-5900181-00 | 2313 | 2018-04-04 |  | EX |  |  | Legacy CB |  | 1801 |  |  |  | 32 | 892 | 326210 | 326210 | 32 | 2313
18-2 | Intersection of Larch Ln & N.Forbes Rd | Lexington | KY | 40511 | USA | Fayette | 067 | [5 empty] | Dodd Sorrell / Buchanan Cont. | Pre-Bore Camera Work | 2621 | NA | 6716216N | NA | 2018-02-14 | 17-0267170-00 | 557 | N/A |  | 1953 |  |  | X |  |  | 6" BS |  | NO |  |  | 6" Bare Steel LP gas main was inside 24 " concrete storm sewer. Possibly built around. | Line will be abandoned at end of AMRP job in area | 17-0267171-00 | 558 | 2018-04-27 | NA | CO | Y |  | Legacy CB | AMRP | 0 | Contractor |  |  | 32 | 10800011 | 3226210 | 3226210 | 32 | 558 | 3200558 | WP7171 | AMRCB
18-3 | 151 E. Maxwells St | Lexington | KY | 40508 | USA | Fayette | 067 |  |  | Mosin Awan |  |  | KY American Water | KAWC Employee | 2621 | 100321056 | 6716212L | NA | 2018-04-20 | 100321056-31 | PR | ? | ? | ? |  |  |  |  | Water Box |  | 3" CS | NO |  |  | Inactive CS 3" (thought to have been old SL) in water box | Determined inactive - Steve Griffey / John Preston / Lee McDonald 4-20-18 | 18-6047690-00 | 2312 | 2018-04-20 |  | EX |  |  | Legacy CB |  | 0 |  |  |  | 32 | 887 | 3226210 | 3226210 | 32 | 2312
18-4 | Corner of Moore St & Crooks St. FFB & RRB of 2800 Crooks St | Ashland | KY | 41101 | USA |  |  |  |  | Chris Holbrook |  |  | Brad Cofer - C J Hughes | Sewer Employee? |  | NA | 7356256E | NA |  | ? | [8 empty] | Sanitary Manhole | 4" BS |  | NO |  |  | See Comment Box | None Needed | NA |  | NA |  | CO |  |  |  |  | 0
18-5 | 215 Ridgeway Rd #3 Possible water -Sent mail to MC on 5-11. (Two lines not gas) | Lexington | KY | 40502 | USA | Fayette | 067 | [5 empty] | Jeremy Heckel - Buchanan Contract | Camera | 2621 | 500419743 | 6720208B | NA | 2018-05-10 | 18-6037599-00 | 2312 | 08-7642035-00 |  | 2008-12-18 |  |  | X |  |  |  |  | NO |  |  | See Comment Box | PENDING | NA |  | NA |  |  | Y |  |  |  | 0
18-6 | 202 Woodspoint Adv. MC of CB on 5-14 & of Repair date of 5-30. Advised Mrs. Detraz PO | Lexington | KY | 40502 | USA | Fayette | 067 | [5 empty] | Jeremy Heckel - Buchanan Contract | Camera | 2621 | NA | 6720208B | NA | 2018-05-11 | 18-6037599-00 | 2312 | 07-0262313-00 | 557 | 2009-03-11 |  |  | X |  |  | 6" P |  | NO |  |  | See Comment Box | PENDING | 18-6117960-00 | 2312 | 2018-05-30 |  | EX |  |  |  |  | 7689 | Contractor
18-7 | 202 Woodspoint Possible water - Not Gas. Sent picture (via email) advising MC & Kevin Wagner on 5-30-18 | Lexington | KY | 40502 | USA | Fayette | 067 | [5 empty] | Jeremy Heckel - Buchanan Contract | Camera | 2621 | NA | 6720208B | NA | 2018-05-11 | 18-6037599-00 | 2312 | [5 empty] | X |  |  |  |  | NO |  |  | See Comment Box | PENDING | [9 empty] | 0 |  |  |  | 32 | 887 | 3226210 |  | 32 | 2312
18-8 | 456 Sandalwood Dr Corner of Sandalwood & Wayland | Lexington | KY | 40505 | USA | Fayette | 067 |  |  | Les Stanfield |  |  | Grade 2+ DPI NUM: D000403 | Leak investigation / Excavated | 2621 | NA | 6720212D | NA | 2018-05-14 | 18-6098675-00 | 2211 |  |  | 1962-01-01 |  |  | X |  |  | 3" CS |  | Yes |  |  | Les Stanfield states storm sewer line was built around our line and concreted in. See also Cap Job | Remove from Sewer | 18-0267737-00 See Comment Box | 559 | 2018-06-08 | N/A | EX |  |  |  |  | 1059 |  |  |  | 32 | 10700001 | 3226210 | 3226210 | 32 | 559 | 3200559 | WP7737
18-9 | 216 Ridgeway Rd Adv. MC of CB via mail on 5-16 & of Repair date (5-30) on 5-17 | Lexington | KY | 40502 | USA | Fayette | 067 | [5 empty] | Jeremy Heckel - Buchanan Contract | Camera | 2621 | NA | 6720208B | NA | 2018-05-16 | 18-6037599-00 | 2312 | 07-0262313-00 | 557 | 2009-03-11 |  |  | X |  |  | 4" P |  | NO |  |  | See Comment Box | PENDING | 18-6122559-00 | 2312 | 2018-06-06 | NA | EX |  |  |  |  | 11860 | Contractor |  |  | 32 | 887 | 3226210 | 3226210 | 32 | 2312
18-10 | 557 Maryland Ave (555 Inactive). Advised Prater via email on 6-14-08 | Lexington | KY | 40508 | USA | Fayette | 067 | [5 empty] | Jeremy Heckel - Buchanan Contract | Camera | 2621 | NA |  | NA | 2018-05-23 | 18-6037599-00 | 2312 | NA | NA | NA |  | X |  |  |  | NA |  |  |  |  | Undetermined line in inactive lateral to 555 Maryland Ave | NA - Will Advise Craig Prater with LFUCG | NA | [8 empty] | 0
18-11 | Fithian St | Paris | KY | 40361 | USA | Bourbon | 017 |  |  | Austin Nichols |  |  | Austin Nichols | Leak Inspection | 2629 | NA | 6740232I | NA | 2018-05-23 | 26291814301 | PR | NA | [6 empty] | Sanitary Manhole | 3" BS |  | YES |  |  | Gas main found in sanitary sewer manhole | ABANDON 93' OF 3"BSLP MAIN | 18-0267748-00 | 558 | 2018-05-14 |  | CO |  |  |  |  | 5869 |  |  |  | 32 | 10800011 | 3226290 | 3226290 | 32 | 558 | 3200558 | WP7748 | AMRCB
18-12 | Ashwood @ Ash Point | Maysville | KY | 41056 | USA | Mason | 161 |  |  | Tyler Allison | 859-213-1965 |  | Jason Tuel Maysville Utilities | Searching for hidden manhole | 2632 | NA | 7256280B | NA | 2018-06-01 | 18-6161525-00 | 2311 | 94-0263614-00 | 555 | 1995-06-05 |  |  |  |  | Manhole | 2" (Yellow)P |  | NO |  |  | Maysville Utilities employee,(Jason Tuel), advised Tyler Allison of CB found inside sewer manhole. Apparently MH had been covered so location was unk. When found, he opened the lid and saw gas line inside. | Remove main from MH during week of 6-4-18 | 18-6169445-00 + 18-0267751-00 and 18-0267752-00 | 2312, 559, 560 | 2018-06-19 |  | EX |  |  |  |  | 3681 |  |  |  | 32 | 10800011 | 326320 | 326320 | 32 | 560 | 3200560 | WP7752
18-13 | 617 W Short St Lateral. 615 W Short (100298310) is Master | Lexington | KY | 40508 | USA | Fayette | 067 | [5 empty] | Colton Elkins / Buchanan Contract | Camera | 2621 | 615 W Short is * 100298310 Master | 6716212H |  | 2018-06-06 | 18-6118214-00 | 2312 | 09-7849245-00 | 565 | 2009-04-28 |  | X |  |  |  |  | 1" P | NO |  |  | Side of sanitary Lateral to 617 W Short St is busted out alongside of service line to 615 (master on manifold) installed by bore per job order. | Repair Sewer, move sl over w/o interrupting service? | Project ID 18-53546 18-6208267-00 | 2313 | 2018-06-26 |  | EX |  |  |  |  | 1218 | Company |  |  | 32 | 92300000 | 353300 | 353300 | 32 | 25101
18-14 | Chestnut St (behind Mueller Electric | Ashland | KY | 41101 | USA | Boyd | 019 |  |  |  | 606-327-2039 ask for Bruce Worthington |  | Stanley C. Harris, City of Ashland Waste Water Collection | Opened MH | 2631 |  |  |  | 2018-07-18 | [9 empty] | San MH | P | P | NO |  |  | Sewer Emp. Opened MH & saw plastic gas line | Matt Collet was sent. We drilled it to verify that it was dead. | [9 empty] | 0
18-15 | 601 Rose St | Lexington | KY | 40508 | USA | Fayette | 067 | [5 empty] | Colton Elkins / Buchanan Contract | Camera | 2621 | NA | 6716212O |  | 2018-07-19 | 18-6275585-00 | 2312 | 06-0261668-00 | 561 | 2006-10-02 | X |  |  |  |  | 6" P |  | NO |  |  | 6" plastic main visible in broken out top section of sewer | Point Repair by Buchanan | 18-6275585-00 Catalyst | [8 empty] | 4300
18-16 | Fountain Ct | Georgetown | KY | 40324 | USA | Scott |  |  |  | Shannon Barker
18-17 | 500 Gano St | PARIS | KY | 40361 | USA | Bourbon | 017 |  |  | Les Sharon | 859-421-5364 |  |  | Tim Rosencrans | 2629 | 100404938 | 6736232L |  | 2018-07-25 | 262918206-02 | PR? | UNK | UNK | 1971-06-07 |  |  |  |  | Storm Catch Basin |  | 1 1/4" CS | Yes |  | NA | 1 1/4" Coated Steel service line was inside styorm drain @ curb line. SL appears to have been built around the SL when drain was installed | Killed 1 1/4" ST SL at tap & ran new SL from main on left side of 500 Gano | 18-6310358-00 | 565 | 2018-07-30 |  | EX | Yes |  |  |  | 1190 | Company |  |  | 32 | 10700001 | 366290 | 366290 | 32 | 565 | 3200565 | WP0055 | AMRSL
18-18 | 171 Sherman Ave | Lexington | KY | 40502 | USA | Fayette | 067 |  |  | Eric Blanton |  |  | PR see comment box here (noted from DIS) | Cistern Lid fell into cistern during rain | 2621 | 100330821 | 6720212N |  | 2018-08-17 | 10033082129 | PR |  |  | 1987-01-01 |  |  |  |  | Abandoned Cistern | 4" P |  | No |  | NA | SINKHOLE EXPOSING ORANGE PIPE-POSSIBLY GAS/NO ODOR DETECTED/PER RENEE WAGNER/THERE/ALT# 859-396-6036/TOC 2040/RED BRICK HOME | Steve Griffey says plan is to simply fill abandoned cistern and pad our main in place | [5 empty] | Called
18-19 | 98 Goodrich Ave -advised tenant Blake Powers @ 270-903-69420 Dawes / Steele | Lexington | KY | 40503 | USA | Fayette | 067 | [5 empty] | Colton Elkins / Buchanan Contract | Camera | 2621 | 100316836 | 6716208K |  | 2018-08-20 | 18-6180173-00 | 2312 | 08-0262663-00 |  | 2009-05-12 |  | X |  |  |  | 2" P |  | No |  | 10.76 | 2" plastic MP gas main in sanitary lateral for 98 Goodrich found with camera crew | Company crew to raise/offset and repair lateral | 18-6373862-00 | 2312 | [11 empty] | 32 | 92300000 | 353300 | 353300 | 32 | 25101
18-20 | 651 W Short - Not Live gas line | Lexington | KY | 40508 | USA | Fayette | 067 | [5 empty] | Colton Elkins / Buchanan Contract | Camera | 2621 | 500509905 | 6716212H |  | 2018-08-24 | 18-6118214-00 | 2312 | 09-7797395-00 | 565 | 2009-03-31 |  |  | X |  |  |  | 1 1/4" S ??? | No |  | 33.83 | Our records show our service & main in area are plastic. Line in sewer does not look like plastic and is directly over top of our plastic main | NA | NA | NA
18-21 | W. Third Not Gas (looks like water) | Lexington | KY | 40508 | USA | Fayette | 067 | [5 empty] | Colton Elkins / Buchanan Contract | Camera | 2621 | NA | 6716212H |  | 2018-08-24 | 18-6118214-00 | 2312 | NA | NA | NA |  |  | X |  |  | Water |  |  |  |  | Looks like a water line in the storm sewer. Our main is plastic in this area | NA | NA | NA
18-22 | 2051 Cummins Ct | Lexington | KY | 40504 | USA | Fayette | 067 |  |  | Steve Griffey | Retired |  | Maintenance | Opened water meter box | 2621 | 100302666 | 6712212H |  | 2018-09-27 |  |  | NA | NA | 1968 |  |  |  |  | Water Box | 2" P |  | No |  |  | 2" plastice main inside water box found by maintenance while replacing water service | Off-set main around water box
Note on BD7: Wells \ James \ D: Maintenance of S.L.
Note on BD8: Wells \ James \ D: Maintenance of Mains
Note on AK9: Wells \ James \ D: John Preston states that he drilled the line and looked inside with a flashlight. He said the line was dead and there was no inserted line inside. He said Steve Griffey was to advise the water company. Lee McDonald was with John. Steve Griffey said it was apparently an old service line.
Note on B10: Wells \ James \ D: South side of Crooks in the middle of Moore St. From Google Earth Manhole looked like about 20 FFB 15 RRB
Note on N10: Wells \ James \ D: According to Brad Cofer, Bobby Dawes knows about this
Note on AJ10: Wells \ James \ D: Brad Cofer w/CJ Hughes was notified there was a line in the manhole. Line was excavated and found to be dead. Brad states he looked inside the line where it was exposed outside of the sewer manhole to determine this.
Note on AJ11: Wells \ James \ D: Jeremy Heckel Found Cross bore (possibly water) during camera work for cross bore program
Note on Y12: Wells \ James \ D: SL Installed 12-18-08
Note on AJ12: Wells \ James \ D: Jeremy Heckel Found Cross bore during camera work for cross bore program
Note on AL12: Wells \ James \ D: pave= 18-6156874-00 conc=18-6156872-00
Note on AJ13: Wells \ James \ D: Jeremy Heckel Found Cross bore (possibly water) during camera work for cross bore program
Note on B14: Wells \ James \ D: Shannon's mail dated 5-21 states " I will speak to Mr. Clayborne and I will be requesting that he has his crew onsite to make repairs to their facility."
Note on AJ14: Wells \ James \ D: *LEAK GRADE: 2+ 3% GAS FOUND IN CATCH BASIN AT CORNER OF SANDALWOOD & WAYLAND 20 FT SPREAD INTO ROADWAY NO OTHER MIGRATION 6PK OK - Leak was repaired 5-14-18. See Cap job to remediate
Note on AK14: Wells \ James \ D: SOME ONE BUILT STORM SEWER AROUND COATED STEEL 3" MP MAIN, HAS DETERIORATED PIPE A 2' SECTION, REST OF THE PIPE IS IN GOOD SHAPE. FIXED WITH PACK CLAMPS AND SOAPED, BHB NO READINGS.SMCHOLAN 130833
Note on AL14: Wells \ James \ D: 18-0267737-00 (559) 18-0267738-00 (560) project id 18-53039
Note on Y15: Wells \ James \ D: SL Installed 12-18-08
Note on AJ15: Wells \ James \ D: Jeremy Heckel Found Cross bore during camera work for cross bore program
Note on AL15: Wells \ James \ D: pave=18-6175977-00
Note on B17: Wells \ James \ D: Between George St & Cameron St.
Note on AG17: Wells \ James \ D: DPI# D097337
Note on AJ17: Wells \ James \ D: Manhole is in line with 3" BS LP that runs from right side of 190 Fithian towards RR tracks by Mt Airy Dr. Said BS LP is now abandoned 104' from Fithian
Note on Y18: Wells \ James \ D: Line alomg Ashwood 01-01-1984. Line in sewer is yellow
Note on B19: Wells \ James \ D: Lateral goes to 617 W Short. 615 is master psid for this manifold setting
Note on AL19: Wells \ James \ D: PAVE JO = 18-6232478-00
Note on AJ20: Wells \ James \ D: See pictures from Mike's email dated 7-25-18 in "Work in Progress" folder
Note on N24: Wells \ James \ D: 12 MOS=00 PR SINKHOLE EXPOSING ORANGE PIPE-POSSIBLY GAS/NO ODOR D ETECTED/PER RENEE WAGNER/THERE/ALT# 859-396-6036/TOC 2040/RED BRICK HOME
Note on W26: Wells \ James \ D: JO for plastic sl installed 2009

## 2019
KY PSC Case No. 2021-00183
AG 1-73
Attachment A
Page 4 of 5
Details | [9 empty] | Employee Reporting Conflict |  |  | Found by information |  | Miscellenous | [10 empty] | Damaged/Penetrated Structure (Size) |  |  |  |  | Material Type & Size of Company Facility Involved |  | Additional Information | [10 empty] | PSP PROJECT LEGEND |  |  |  | CHARGED TO:
Log # | Address | City | State | Zip | Country | County Name | County # | Mapped on GIS | Entered on Risk Model | Name | Phone Number | Email | Homeowner-Plumber / Municipality / Construction / Operations / Contractor | How Found? | TCC | PSID | Map # | In Top 5% of Model Ranking on Risk Model? | Date Found | Found Job Order | JO Type | Installation Job Order | JO TYPE | Date Installed | Installed By Contractor Company | Main Sanitary Sewer | Lateral Sanitary Sewer | Main Storm Sewer | Lateral Storm Sewer | Other Structure- specify | P - PLASTIC S- STEEL BS - BARE STL CS - CTD STL WT - WLD TRTD Main | P - PLASTIC BS - BARE STL Service | Leak? | Caused by Sewer Cleanout | Camera footage | Details of Cross Bore | Remediation Plan | Remed Job Order | JO Type | Remed Completion Date | Status | Received Notify Form? | Charged to Legacy CB Project? | IRP -- INFRASTRUCTURE REPLACEMENT PROGRAM AMRP -- MAIN REPLACEMENT PROGRAM LEGACY CB -- CROSS BORE PRIOR TO 7/1/2008 NON-LEGACY CB -- CROSS BORE SINCE 7/1/2008 | PROJECT CHARGE TO: IRP / AMRP / LEGACY CB / OPERATIONS / CONTRACTOR | Remediation Costs | Company/ Contractor Remediated? | JO # | WM/DI | BU | ACCOUNT | HOME DP | CHRG DP | AFFIL | ACTIV | PROJECT | FACIL | PROJCD
19-1 | 610 Cardinal Ln | Lexington | KY |  | USA | Fayette | 067 |  |  | Marcus Young gave to Jamie Ensminger |  |  | Homeowner called in due to sewer back up | Visual by Ensminger | 2621 |  |  |  | 2019-05-07 | 19-7039750-00 | 2312 | 05-0261464-00 | 559 | 2006-03-23 | Contractor |  | X |  |  |  | P |  | No |  |  | Plumber found and plant crew was called in to remove and make repairs. |  | 19-0268756 & 19-0268755 | 560 & 559 | 2019-05-13 | Completed |  | NO | [12 empty] | 19-63675
19-2 | 221 Hawthorne Dr | Frankfort | KY |  | USA | Franklin | 073 | [5 empty] | Jeremy Heckel of Buchanan Cont. | See Comment | 2623 |  |  |  | 2019-06-04 | N/A | [5 empty] | X |  |  |  |  | P |  | No |  |  | Sewer crew found while making repairs to broken clay tile. Flange had been broken and the gas pipe was under the sewer very close. Not really a cross bore but we could have broken the sewer pipe on installation. |  | 19-7113641-00 | 2312 | 2019-06-04 | Completed |  | NO |  |  |  |  | 19-7113641-00 |  | 32 | 887 | 32623 | 32623 | 32 | 2312
19-3 | 116 N Hanover | Lexington | KY |  | USA | Fayette | 067 |  |  | Ryan Vanderpool |  |  | Plumber | Excavated | 2621 |  |  |  | 2019-04-06 | 19-6952833-00 | 2312 | 08-0262481-00 | 561 | 2008-03-27 | Contractor |  | X |  |  |  | 4" P |  | No |  |  | See Comment | Raise Main | 19-6952834-00 | 2312 | 2019-05-22 | Completed |  | NO |  |  |  |  | 19-6952834-00 |  | 32 | 887 | 326210 | 32621 | 32 | 2312
19-4 | 602 Cardinal Ln | Lexington | KY |  | USA | Fayette | 067 | [5 empty] | Colton Elkins of Buchanan cont | targeted camera | 2621 |  |  |  | 2019-07-26 | 19-7160316-00 | 2312 | 05-0261467-00 | 563 | 2006-08-21 | Fishel | X |  |  |  |  | 4"PL |  | No |  |  | See comments here |  | 19-7275075-00 | 2312 | 2019-08-22 | Complete |  | Yes |  |  |  |  | 19-7275075-00 |  | 32 | 92300000 | 353300 | 353300 | 32 | 2312 | 19-65523
19-5 | 603 Cardinal Ln | Lexington | KY |  | USA | Fayette | 067 | [5 empty] | Colton Elkins of Buchanan cont | targeted camera | 2621 |  |  |  | 2019-07-29 | 19-7160316-00 |  |  |  | N/A |  |  | X | [5 empty] | No |  |  | Metro net lines |  |  |  |  | Not ours |  | No
19-6 | 622 Cardinal Ln | Lexington | KY |  | USA | Fayette | 067 | [5 empty] | Colton Elkins of Buchanan cont | targeted camera | 2621 |  |  |  | 2019-07-30 | 19-7160316-00 | 2312 |  |  | 2006-08-01 | Fishel |  | X |  |  |  | 4" PL |  | No |  |  | See comments here |  | 19-7282876-00 |  | 2019-08-27 | Complete |  | Yes |  |  |  |  | 19-7282876-00
19-7 | 621 Cardinal Ln | Lexington | KY |  | USA | Fayette | 067 | [5 empty] | Colton Elkins of Buchanan cont | targeted camera | 2621 |  |  |  | 2019-07-30 | 19-7160316-00 |  |  |  | N/A |  |  |  | X |  |  |  |  | No |  |  | Metro net lines |  |  |  |  | Not ours |  | No
19-8 | Bob-O- Link @ Jacana Dr | Lexington | KY |  | USA | Fayette | 067 | [5 empty] | Colton Elkins of Buchanan cont | targeted camera | 2621 |  |  |  | 2019-08-09 | 19-7160316-00 |  |  |  | 1947 | Company |  |  | X |  |  |  | 2" BS | No |  |  | See comments here |  | 19-7331202-00 |  | 2019-08-28 | Complete |  | Yes |  |  |  |  | 19-7331202-00 |  | 32 | 92300000 | 353300 | 353300 | 32 | 2312 | 19-65523
19-9 | 1816 Chatsworth | Lexington | KY |  | USA | Fayette | 067 |  |  | Jamie Ensminger |  |  | Jamie Ensminger |  | 2621 |  |  |  | 2019-08-12 |  |  |  |  | 1972-01-01 | [6 empty] | 2"PL |  | No |  |  | Severman found gas line needs raised and top of storm sewer repaired Plant department has order to make repairs |  | 20-7831206-00 |  |  | completed |  | No
19-10 | 237 E 5th St | Lexington | KY |  | USA | Fayette | 067 |  |  | Les Stanfield |  |  | Les Stanfield |  | 2621 |  |  |  | 2019-08-16 | [8 empty] | X |  |  |  | BS | Yes |  |  | Serviceman found gas line in catch basin leaking Construction made repairs |  |  |  |  | Completed |  | No
19-11 | Vista Dr at Rosemont | Lexington | KY |  | USA | Fayette | 067 | [5 empty] | Buchanan Cont | pulled lid | 2621 |  |  |  | 2019-10-17 |  |  |  |  | 1937-01-01 |  |  |  | X |  |  |  | 3" BS | No |  |  | Crew found in storm sewer basin while camera for bore project for construction dept this job goes to the plant department Made them aware of in email on 10/17/19 |  | 20-72887-00 |  | 2020-12-15 | Completed |  | No
19-12 | LaFayette St just north of Rosemont Garden | Lexington | KY |  | USA | Fayette | 067 |  |  | Colton (Buchanan) |  |  | Buchanan Cont | camera | 2621 |  |  |  | 2019-10-25 |  |  | 97-0265408 |  | 1987-01-01 | Fishel |  |  | X |  |  | 3" PL |  | No |  |  | Crew found in storm sewer with camera |  | 19-2069078-00 |  | 2020-04-14 | Completed |  | No Capital
19-13 | Chestnut just off of Winchester | Ashland | KY |  | USA | Boyd |  |  |  | City workers |  |  | City of Ashland | pulled lid |  |  |  |  | 2019-10-25 |  |  |  |  | N/A |  | X | [5 empty] | CS | No |  |  | Line has been identified as abandoned by plant department. They are to remove pipe and fill with foam. |  | 19-7552886-00 |  | 2019-10-26 | Completed |  | No
19-14 | 115 Westgate Ave | Lexington | KY |  |  | Fayette | 067 |  |  | Colton (Buchanan) |  |  | Buchanan Cont | camera |  |  |  |  | 2019-11-04 | 19-7325238-00 |  |  |  | 2008-09-04 |  |  |  | X |  |  |  | PL | No |  |  | 1/2" service bored throughed strom sewer | Plant crew to remove | 19-7566263-00 |  |  | Completed |  | Yes
19-15 | 129 Lackawanna | Lexington | KY |  |  | Fayette | 067 |  |  | City workers |  |  | City of Lexington | camera | 2621 |  |  |  | 2019-11-26 |  |  | 08-0262663 |  | 2009 | Dix and Assoc |  | X |  |  |  | 2"PL |  | No |  |  | 2 inch main in the top of the lateral to the home | Plant crew to remove | 19-7641338-00 |  |  | Completed |  | No |  |  |  | Company
19-16 | 118 Garrett | Lexington | KY |  |  | Fayette | 067 |  |  | Buchanan |  |  | Buchanan Cont | camera | 2621 |  | 6712212H | Yes | 2019-12-06 |  |  | 08-0262483 |  | 2008-07-01 | Miller |  | X |  |  |  | 2"PL |  | No |  |  | Main bored thru the top of the lateral to the home 4" | RLA to repair | 19-7637928-00 |  |  | Completed |  | Yes |  |  |  | Contractor | 19-7637928-00
19-17 | 124 Garrett | Lexington | KY |  |  | Fayette | 067 |  |  | Buchanan |  |  | Buchanan Cont | camera | 2621 |  | 6712212H | Yes | 2019-12-09 |  |  | 08-0262483 |  | 2008-07-01 | Miller |  | X |  |  |  | 2"PL |  | No |  |  | Main bored thru the bottom to the lateral to the home 4" | RLA to repair | 19-7637877-00 |  |  | Completed |  | Yes |  |  |  | Contractor | 19-7637877-00
Note on U7: Wells \ James \ D: Also J Ensminger Job # 19026875500
Note on O8: Wells \ James \ D: Found while excavating to make a point repair
Note on B9: Wells \ James \ D: Only 75' of plastic in the area. The rest 1800 steel
Note on AK9: Wells \ James \ D: CONFIRMED CROSS BORE 4 INCH PLASTIC LINE THROUGH SEWER. MAIN RAISED TO CLEAR CROSSBORE IN SEWER- DRIVEWAY APRON CUT- SEWER REPAIRED BY LFUGC SEWER DEPT.
Note on Z10: Knisley \ Mark \ Franklin:
Note on AK10: Knisley \ Mark \ Franklin: Sewer lateral was cut across the top by our 4 inch main repaired by RLA
Note on O11: Knisley \ Mark \ Franklin: this was a metro net line drilled through laterial sewer line
Note on AK12: Knisley \ Mark \ Franklin: Sewer lateral was cut across the top by our 4 inch main repaired by RLA
Note on O13: Knisley \ Mark \ Franklin: this was a metro net line drilled through laterial sewer line
Note on P13: Knisley \ Mark \ Franklin: this was a metro net line drilled through laterial sewer line
Note on O14: Knisley \ Mark \ Franklin: this was a metro net line drilled through laterial sewer line
Note on P14: Knisley \ Mark \ Franklin: this was a metro net line drilled through laterial sewer line
Note on AK14: Knisley \ Mark \ Franklin: Main was installed in 1947 City built around our main. Main was retired in past. We cut the pipe on the south side as the north side was already cut. Filled the pipe with foam and left it in the box that was build around it as not to damage it by removing the pipe. Mark Knisley

## 2020
KY PSC Case No. 2021-00183
AG 1-73
Attachment A
Page 5 of 5
Details | [6 empty] | Employee Reporting Conflict |  |  | Found by information |  | Miscellenous | [9 empty] | Damaged/Penetrated Structure (Size) |  |  |  |  | Material Type & Size of Company Facility Involved |  | Additional Information | [10 empty] | PSP PROJECT LEGEND |  |  |  | CHARGED TO:
Log # | Address | City | State | County Name | Mapped on GIS | Entered on Risk Model | Name | Phone Number | Email | Homeowner-Plumber / Municipality / Construction / Operations / Contractor | How Found? | TCC | PSID | Map # | In Top 5% of Model Ranking on Risk Model? | Date Found | Found Job Order | JO Type | Installation Job Order | JO TYPE | Date Installed | Main Sanitary Sewer | Lateral Sanitary Sewer | Main Storm Sewer | Lateral Storm Sewer | Other Structure- specify | P - PLASTIC S- STEEL BS - BARE STL CS - CTD STL WT - WLD TRTD Main | P - PLASTIC BS - BARE STL Service | Leak? | Caused by Sewer Cleanout | Camera footage | Details of Cross Bore | Remediation Plan | Remed Job Order | JO Type | Remed Completion Date | ESIS Claim # | Received Notify Form? | Charged to Legacy CB Project? | IRP -- INFRASTRUCTURE REPLACEMENT PROGRAM AMRP -- MAIN REPLACEMENT PROGRAM LEGACY CB -- CROSS BORE PRIOR TO 7/1/2008 NON-LEGACY CB -- CROSS BORE SINCE 7/1/2008 | PROJECT CHARGE TO: IRP / AMRP / LEGACY CB / OPERATIONS / CONTRACTOR | Remediation Costs | Company/ Contractor Remediated? | JO #
20-1 | 1351 Fontaine | Lexington | KY | Fayette |  |  | City Employee |  |  | City | Camera |  | 100326879 |  |  | 2020-01-29 |  | 565 | 19-6916715-00 |  | 2019-10-01 | X | [5 empty] | PL | No |  |  | Miller installed service to home boring under the street | Given back to Miller to repair |  |  |  | No |  | No |  |  |  |  | Contractor
20-2 | 1213 N Limestone | Lexington | KY | Fayette |  |  | Tyler |  |  | Buchanan | Camera |  |  |  |  | 2020-02-03 | [5 empty] | X | [5 empty] | 1" PL | No |  |  | 1 inch service thru san/sewer main | Given to plant department | [5 empty] | No |  |  |  |  | 20-7837775-00
20-3 | 114 Willow St | Frankfort | KY | Franklin |  |  | City Employee |  |  | City | Camera |  |  |  |  | 2020-01-01 |  |  |  |  | 1966-01-01 |  |  | X |  |  | 2" CS |  | No |  |  | this was a build around in storm catch basin built by the city of Frankfort | Given to engineering | [5 empty] | No
20-4 | 102 Spring St | Frankfort | KY | Franklin |  |  | City Employee |  |  | City | Camera |  |  |  |  | 2020-01-20 |  |  |  |  | 1978-01-01 |  |  | X |  |  | 2" CS |  | No |  |  | this was a build around in storm catch basin built by the city of Frankfort | Given to engineering | [5 empty] | No
20-5 | 100 Phillips | Frankfort | KY | Franklin |  |  | City Employee |  |  | City | Camera |  |  |  |  | 2020-01-01 |  |  |  |  | 1978-01-01 |  |  | X |  |  | 2" CS |  | No |  |  | this was a build around in storm catch basin built by the city of Frankfort | Given to engineering | [5 empty] | No
20-6 | 1509 Versailles Rd | Lexington | KY | Fayette |  |  | Buchanan |  |  | Buchanan | Camera |  |  |  |  | 2020-03-18 | [7 empty] | X |  |  |  | P | No |  |  | Bored thru storm sewer | Given to plant department |  |  | 2020-03-30 |  |  | No |  |  |  |  | 20-7946046-00
20-7 | 143 Goodrich Ave | Lexington | KY | Fayette |  |  | Contactor |  |  | Roto-router | Camera |  |  |  |  | 2020-03-25 | [6 empty] | X |  |  |  |  | P | No |  |  | Bored thru sewer lateral | Plant crew to remove gas line |  |  | 2020-03-26 |  |  | No |  |  |  |  | 20-7950639-00
20-8 | 147 Willis Ave | Frankfort | KY | Franklin |  |  | Plumber |  |  | Plumber | [5 empty] | 2020-05-13 | [6 empty] | X |  |  |  |  | 1" PL | no |  |  | 1 inch service thru lateral | Plant crew to remove gas line |  |  | 2020-05-13 |  |  | No |  |  |  |  | 20-8100948-00
20-9 | 112 Martin | Midway | KY | Woodford |  |  | City Employee |  |  | City | Open lid |  |  |  |  | 2020-08-17 | [5 empty] | X | [9 empty] | City water line not Gas |  |  |  | 2020-09-14 | [7 empty] | N/A
20-10 | 138 Sherman | Lexington | KY | Fayette |  |  | Buchanan |  |  | Buchanan | Camera |  |  |  |  | 2020-09-10 |  |  |  |  | 1987-01-21 | X | [5 empty] | P | no |  |  | Service to 138 Sherman found during Pre camera work for Construction work | Plant crew to remove gas line | 20-8474988-00 |  | 2020-10-08 |  |  | No |  |  |  |  | 20-8474988-00
20-11 | 2524 Checkerberry Dr | Lexington | KY | Fayette |  |  | Buchanan |  |  | Buchanan | Camera |  |  |  |  | 2020-09-28 |  |  |  |  | 2000-01-06 | X | [5 empty] | P | Yes |  |  | Plant crew responded and retired service at main | Retired | [5 empty] | No |  |  |  |  | 20-8481720-00
20-12 | Intersection of Forbes and Old Frankfort Pike | Lexington | KY | Fayette |  |  | Buchanan |  |  | Buchanan | Camera |  |  |  |  | 2020-11-05 |  |  |  |  | 1990-01-01 |  |  | X |  |  |  |  | no |  |  | Found by Pre camera work for new main installation | Retired | [5 empty] | No |  |  |  |  | This was not a gas line it was fiber optic
20-13 | 443 S Ashland St | Lexington | KY | f |  |  | Buchanan |  |  | Buchanan | Camera |  |  |  |  | 2020-12-11 |  |  |  |  | 2012-07-24 | X |  |  |  |  | 2" PL |  | no |  |  | Found by Pre camera work | Retired/Raised |  |  | 2021-01-14 |  |  | No |  |  |  | Company | 21-8745544-00