## Ckt Defects Reported 2019 PKV
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2019 | 2019-01-17 | Pikeville | 72340144 | DKY0103631 | 38830954D20408 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , guys/anchors: broken or missing | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Pole is rotten. Also no primary guy wire. Secondary guy wrapped around pole. | 1183 Marshall street prestonsburg ky.1189 HIGHLAND AVE | 2019-03-27
2019 | 2019-01-17 | Pikeville |  |  | 38830954D20719 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Service entrance is laying on the roof of bldg. also need guy marker. | South lake drive prestonsburg ky. Behind pro fitness.
2019 | 2019-01-17 | Pikeville |  |  | 38830954D40320 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Two guy wire without markers. Also there’s a very big hole around the base of the pole. | 29 club street prestonsburg ky | 2019-05-14
2019 | 2019-01-17 | Pikeville | 73374873 | DKY0105354 | 38830978A30109 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | already written to EDN100577 FOREIGN | Pole is rotten | 370 maple avenue prestonsburg ky. | 2020-01-02
2019 | 2019-01-17 | Pikeville | 73374645 | DKY0105274 | 38830978A30176 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 381 south Arnold avenue prestonsburg ky. At end of south Arnold avenue. | 2020-01-30
2019 | 2019-01-17 | Pikeville | 72357661 | DKY0103671 | 38830978A30179 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole is hollow. And rotten at bottom | Maple avenue prestonsburg ky. Across street from house 370. | 2019-02-14
2019 | 2019-01-17 | Pikeville | 73374645 | DKY0105274 | 38830978A30180 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Maple avenue prestonsburg ky. At corner of maple avenue and short street. | 2020-01-30
2019 | 2019-01-17 | Pikeville | 73374604 | 105195 | 38830978C10010 |  | 3410601-E.PRESTON / PRESTONSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 912 east Hughes street prestonsburg ky. | 2019-07-17
2019 | 2019-01-17 | Pikeville |  |  | 38830978C10024 |  | 3410601-E.PRESTON / PRESTONSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire without marker. | 1070 riverside drive prestonsburg ky | 2019-05-14
2019 | 2019-01-17 | Pikeville | 73374604 | 105195 | 38830978C10041 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | guys/anchors: broken or missing | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire wrapped around pole. Either remove guy or install anchor. Backs up long span of 4/0 quad secondary. | 939 south lake drive prestonsburg ky. Small street between south lake drive and south highland avenue. | 2019-07-17
2019 | 2019-01-17 | Pikeville |  |  | 38830978C10090 |  | 3410601-E.PRESTON / PRESTONSB | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Metering eclosure open on pole. Has been cut in clear but should be removed. | 637 McNally lane prestonsburg ky. Beside Tim short bldg.
2019 | 2019-01-17 | Pikeville | 73375373 | 105303 | 38830978C10126 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Top of pole is split allowing Hendrix bracket to pull partially through. | 781 east burchett street prestonsburg ky. | 2019-06-24
2019 | 2019-01-17 | Pikeville | 73374604 | 105195 | 38830978C10157 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | guys/anchors: broken or missing | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Secondary guy loose and wrapped around pole. Either need to remove guy completely or install anchor and re-attach guy. | 978 riverside drive prestonsburg ky | 2019-07-17
2019 | 2019-01-17 | Pikeville | 69041803 | DKY0098857 | 38830978C10240 | TRUE | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole is rotten at the base. | 558 riverside drive prestonsburg ky | 2019-04-03
2019 | 2019-01-17 | Pikeville | 69041803 | DKY0098857 | 38830978C10242 | TRUE | 3410601-E.PRESTON / PRESTONSB | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop rubbing the gutter of house | 602 riverside drive prestonsburg ky | 2019-04-03
2019 | 2019-01-17 | Pikeville | 73374604 | 105195 | 38830978C10275 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Pole has been removed from records but still in field. Not shown on field view. Close to pole 978-89. | South lake drive prestonsburg ky. In gravel lot across street from Mann auto outlet. | 2019-07-17
2019 | 2019-01-18 | Pikeville | 74135477 | 106112 | 38830930A20250 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole in slide. | 1162 Abbott mountain road prestonsburg ky. Behind drains unlimited on hill. | 2019-07-26
2019 | 2019-01-18 | Pikeville | 74078422 | 106186 | 38830930B00001 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Old cliff road prestonsburg ky. Across rr tracks. River crossing. | 2022-08-19
2019 | 2019-01-18 | Pikeville | 74078422 | DKY0106186 | 38830930B00080 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire hanging down pole . Need to remove or install anchor aand reattach guy. | 21 old cliff road prestonsburg ky. Across rr tracks between white houseand gray dw trailer. | 2022-08-19
2019 | 2019-01-18 | Pikeville | 74078364 | DKY0106122 | 38830930B00226 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Cliff road prestonsburg ky. @ corner of resource drive. | 2020-01-16
2019 | 2019-01-18 | Pikeville | 74078422 | DKY0106186 | 38830930B00438 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Arms are deteoriated. | Cliffside circle, prestonsburg ky. Cliff apts. riser pole for underground. | 2022-08-19
2019 | 2019-01-18 | Pikeville |  |  | 38830930D00009 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Remove guy wire hanging down pole. | Woodie blvd. prestonsburg ky. Mouth spradlin Branch. | 2019-07-26
2019 | 2019-01-18 | Pikeville | 74078280 | DKY0106109 | 38830930D00098 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needs guy marker | 2095 ky route 321 prestonsburg ky. Behind Mathewson Valley Gas. | 2019-12-11
2019 | 2019-01-18 | Pikeville | 74078280 | DKY0106109 | 38830930D00171 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Need guy marker | 715 spradlin Branch prestonsburg ky. | 2019-12-11
2019 | 2019-01-18 | Pikeville | 74078280 | DKY0106109 | 38830930D00193 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Secondary is sagged below comm. cables in both spans. Re-sag secondary. | Spradlyn Branch prestonsburg,ky. Quicksilver townhouses. | 2019-12-11
2019 | 2019-01-18 | Pikeville | 74078280 | DKY0106109 | 38830930D00239 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down the pole to ground. Is not energized. | 300 spradlin Branch prestonsburg ky. | 2019-12-11
2019 | 2019-01-18 | Pikeville | 74078364 | DKY0106122 | 38830954A10151 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarms are rotten. May consider changing pole too. River crossing. Will need yard machine. | 635 university drive prestonsburg ky. Across from the college beside the bridge. River crossing. | 2020-01-16
2019 | 2019-01-18 | Pikeville | 74078347 | DKY0106079 | 38830954A20522 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire loose. Tighten guy. | 60 S Hall alley prestonsburg ky. End of street | 2019-12-11
2019 | 2019-01-18 | Pikeville | 74078584 | DKY0106141 | 38830954A21123 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop low clearance on roof top. Approximately 6”. Might need to change pole out for clearance. Has been cut off before and has pole top extension on it. | 48 s hall alley prestonsburg ky. | 2019-09-30
2019 | 2019-01-18 | Pikeville | 74078364 | DKY0106122 | 38830954A30378 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Crossarm deteoriated and bowed. | West porter street, prestonsburg ky. | 2020-01-16
2019 | 2019-01-18 | Pikeville |  |  | 38830954A40172 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needs guy marker | 38830930B40269
2019 | 2019-01-18 | Pikeville | 74078347 | DKY0106079 | 38830954A40343 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire loose. Anchor has been cut off but there’s phone co. anchor to attach to. | Cabella lane,prestonsburg ky. Beside A- storage | 2019-12-11
2019 | 2019-01-18 | Pikeville | 74078347 | DKY0106079 | 38830954C20580 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH | cutout: damaged | lightning arresters/insulators: damaged |  | KPC |  | Replace silver top cutouts | 725 mays Branch prestonsburg ky | 2019-12-11
2019 | 2019-01-18 | Pikeville | 74078347 | DKY0106079 | 38830954C20958 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needs guy marker | Mays Branch, prestonsburg ky. | 2019-12-11
2019 | 2019-01-21 | Pikeville | 76909721 | DKY0110317 | 37820004000019 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | lightning arresters/insulators: damaged , guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Epoxilator melting down. Also needs guy marker. | State Hwy 194 E, Kentucky 41539, USA | 2022-06-17
2019 | 2019-01-21 | Pikeville | 12345 |  | 37820004000063 |  | 3408402-KIMPER / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needs guy markers..Double dead-end angle pole on left side of road going up elk horn Fork. | State Hwy 194 E, Kentucky 41539, USA | 2019-04-08
2019 | 2019-01-21 | Pikeville | 73033400 |  | 37820004000068 |  | 3408402-KIMPER / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needs guy markers. In front of tan dw with black shutters about 1/4 mile up elk horn Fork on left. | State Hwy 194 E, Kentucky 41539, USA | 2019-04-08
2019 | 2019-01-21 | Pikeville | 83965729 | DKY0120222 | 37820004000092 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire broken. Staples to pole. This is 3 phase angle pole. Had a stub pole across the highway but has been broken by car. Located behind kimper pharmacy. | State Hwy 194 E, Kentucky 41539, USA | 2023-05-26
2019 | 2019-01-21 | Pikeville |  |  | 37820004000114 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needs two guy markers. Buckarm pole beside car wash near L&M mart. | State Hwy 194 E, Kentucky 41539, USA
2019 | 2019-01-21 | Pikeville | 76909721 | DKY0110317 | 37820004000126 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire loose. Tighten guy. Double dead-end pole at the station. | State Hwy 194 E, Kentucky 41539, USA. | 2022-06-17
2019 | 2019-01-21 | Pikeville |  |  | 3782000400026 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire broke. Re-attach guy wire and install markers. | State Hwy 194 E, Kentucky 41539, USA | 2023-03-02
2019 | 2019-01-21 | Pikeville | 76909721 | DKY0110317 | 37820004000265 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down. | Elk horn Fork, State hwy 194 east kimper ky | 2022-06-17
2019 | 2019-01-21 | Pikeville | 83965799 | DKY0120216 | 37820028000050 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Remove inactive tap and pole. Primary is hanging down pole but is de-energized. At the foot of the hill on elk horn Fork on the left of road. | Elk horn Fork, State hwy 194 east, kimper ky. | 2023-05-24
2019 | 2019-01-21 | Pikeville | 1234 |  | 37820028000095 |  | 3408402-KIMPER / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needs guy markers. At the foot of hill on elk horn Fork on right. | Elk horn Fork, State hwy 194 east kimper ky. | 2019-04-08
2019 | 2019-01-21 | Pikeville | 73134422 |  | 37820053000166 |  | 3408402-KIMPER / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy loose hanging down pole. Either remove guy or reattach. | 18769 KY-194, Phyllis, KY 41554, USA | 2019-04-17
2019 | 2019-01-21 | Pikeville |  |  | 37820054000002 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | Service drop low enough to reach from ground. Take slack out of drop. Can raise up service pole another 5 feet. Located @ Hayes road behind white dw. | 22147 highway 194 @ Biggs, ky.
2019 | 2019-01-21 | Pikeville | 84898691 | DKY0120747 | 37820054000009 | TRUE | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer | 210 hunts Branch Road , Biggs, ky.
2019 | 2019-01-21 | Pikeville |  |  | 37820054000040 |  | 3408402-KIMPER / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needs guy marker | Cletis Webb Road, Phyllis ky
2019 | 2019-01-21 | Pikeville | 73134479 |  | 37820054000042 |  | 3408402-KIMPER / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needs guy markers | 19233 State hwy 194 east Phyllis ky | 2019-04-17
2019 | 2019-01-21 | Pikeville | 84898914 |  | 37820054000091 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten. Has huge hole in middle of the pole. | KY-194 & Victor Adkins Rd, Kentucky 41554, USA
2019 | 2019-01-21 | Pikeville | 73134766 |  | 37820054000093 |  | 3408402-KIMPER / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needs guy marker | Elliot Justice Rd, Kentucky 41554, USA | 2019-04-17
2019 | 2019-01-21 | Pikeville | 84898946 |  | 37820054000099 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | pole: leaning, burned more than 50% remaining |  | Foreign | YES | Pole is leaning. Has one service pulled very tight and another service can be reached from the ground. Install: 1957 | 20270 KY-194, Phyllis, KY 41554, USA
2019 | 2019-01-21 | Pikeville |  |  | 37820054000123 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Lightning arrestor blown. Replace arrestor | 19901 KY-194, Phyllis, KY 41554, USA | 2020-06-17
2019 | 2019-01-21 | Pikeville | 84899033 | DKY0120787 | 37820054000173 | TRUE | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive primary tap and secondary tap. | Hayes Road, hwy 194 @biggs ky.
2019 | 2019-01-21 | Pikeville | 84899118 | DKY0120835 | 37820054C20282 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove secondary pole. Pole is tagged 284. | State hwy 194 east, Biggs, ky.
2019 | 2019-01-22 | Pikeville | 77011314 | DKY0110360 | 37820052000126 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Secondary pole is rotten. It is tagged as pole 71. @ white brick house on Johnson lane. | 59 Johnson lane, highway 194 Phyllis, ky. | 2022-05-17
2019 | 2019-01-22 | Pikeville | 76909977 | DKY0112887 | 37820052000188 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire hanging down pole. Need to remove or reattach. Will need to install anchor to attach to. @ old car wash on right grapevine road just 1/4 mile before fire dept. | 15933 KY-194, Phyllis, KY 41554, USA | 2021-10-26
2019 | 2019-01-22 | Pikeville | 73132731 |  | 37820052000233 |  | 3408402-KIMPER / GRAPEVINE | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down pole energized. Remove drop.@ entrance to Johnson lane on right. | Johnson lane, hwy 194, Phyllis, ky. | 2019-04-17
2019 | 2019-01-22 | Pikeville | 83965729 | DKY0120222 | 37820052000245 | TRUE | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Secondary pole leaning considerably. Need to install anchor and guy. Behind a yellow dw trailer on right. Install: 1997 | 13803 KY-194, Phyllis, KY 41554, USA | 2023-05-26
2019 | 2019-01-22 | Pikeville | 73134479 |  | 37820053000016 |  | 3408402-KIMPER / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needs guy marker.@ old grapevine elementary school. | 177243 hwy 194 east, Phyllis, ky. | 2019-04-17
2019 | 2019-01-22 | Pikeville | 76910039 | DKY0112903 | 37820053000021 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack. Need to tighten.@ mouth of Rough Hollow. Take—off pole. | 17669 Highway 194 east, Phyllis, ky. | 2021-10-26
2019 | 2019-01-22 | Pikeville | COMPLETE IN FIELD | COMPLETE IN FIELD | 37820053000035 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire loose hanging down pole. Re-attach guy. Install markers. Takeoff pole for Honey Fork. | 17154 KY-194, Phyllis, KY 41554, USA
2019 | 2019-01-22 | Pikeville | 83965838 | DKY0120945 | 37820053000141 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop is nearly touching rooftop. First brick house on right on lower camp Branch. | 31 lower camp Branch, Phyllis ky.
2019 | 2019-01-22 | Pikeville | 76910039 | DKY0112903 | 37820053000273 | TRUE | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Secondary pole leaning pretty bad. Need to straighten. Last house on honey Fork. Install: 1974 | 431 Honey Fork Rd, Phyllis, KY 41554, USA | 2021-10-26
2019 | 2019-01-23 | Pikeville | 83965729 | DKY0120222 | 37820027000054 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Remove guy wire hanging down pole. Or install anchor to reattach guy. | 145 Chimney Fork, Ridge line Road, Raccoon ky. | 2023-05-26
2019 | 2019-01-23 | Pikeville | 73088767 |  | 37820027000225 |  | 3408402-KIMPER / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needs guy marker. Just below Thacker Hollow. | 4910 Ridge Line Rd, Raccoon, KY 41557, USA | 2019-04-12
2019 | 2019-01-23 | Pikeville | 76909977 | DKY0112887 | 37820028000002 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Anderson Road @ foot of elkhorn Fork on grapevine side of the mountain. | KY-194 & Anderson Rd, Kentucky 41554, USA | 2021-10-26
2019 | 2019-01-23 | Pikeville | 76909854 | DKY0110523 | 37820028000013 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop touching the side of the house. Probably need taller pole for clearance. | 219 river hurricane road, raccoon, ky. | 2022-04-08
2019 | 2019-01-23 | Pikeville | 76909854 | DKY0110523 | 37820028000018 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Low clearance on service drop. Need secondary pole installed. | 6100 Amos hill road, ridge line road, Phyllis, ky. | 2022-04-08
2019 | 2019-01-23 | Pikeville | 76909854 | DKY0110523 | 37820028000064 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire broken hanging down pole. Reattach guy. Going down hill on elkhorn Fork on grapevine side on right by guardrail. | State Hwy 194 E, Kentucky 41539, USA | 2022-04-08
2019 | 2019-01-23 | Pikeville | 76909854 | DKY0110523 | 37820028B40363 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Fuse is open but service drop hanging down pole. | Ridge Line Rd, Phyllis Kentucky, USA | 2022-04-08
2019 | 2019-01-23 | Pikeville | 73131401 |  | 37820051000013 |  | 3408402-KIMPER / GRAPEVINE | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop low clearance. Take slack out of drop. | 1449 river hurricane road, Raccoon, my. | 2019-04-17
2019 | 2019-01-23 | Pikeville | 83965888 | DKY0121187 | 37820051000062 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Lightning arrestor blown. Replace cutout and arrestor | 191 Jonican Rd, Raccoon, KY 41557, USA
2019 | 2019-01-23 | Pikeville | 73865717 | DKY0105851 | 37820051000142 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign |  | Conductor floating. Very long span crossing valley. Over 1000 ft between the two spans together..first pole from normal open point between kimper / grapevine and johns Creek/ raccoon circuits. Conductor appears to be 15 or more feet above pole. Will probably have to let conductors down to re-tie. | Ridge line road, raccoon ky. | 2019-10-24
2019 | 2019-01-23 | Pikeville | 83965926 | DKY0119965 | 37820051000176 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen from bottom of pole.@ mouth of Chimney Fork. | 4005 Ridge Line Rd, Kimper, KY 41539, USA | 2023-05-26
2019 | 2019-01-24 | Pikeville | 73374645 | DKY0105274 | 38830954B20271 |  | 3403301-PRESTONSB / CITY | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needs guy marker | Harkins Ave, Prestonsburg, KY 41653, USA | 2020-01-30
2019 | 2019-01-24 | Pikeville |  |  | 38830954B30164 |  | 3403301-PRESTONSB / CITY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop is rubbing gutters on church. First Christian Church. Take slack out of service drop for clearance. | 657 N Arnold Ave, Prestonsburg, KY 41653, USA
2019 | 2019-01-24 | Pikeville | 73374669 | 105257 | 38830954B30261 |  | 3403301-PRESTONSB / CITY | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needs guy markers | W Bridge St, Prestonsburg, KY 41653, USA | 2019-06-05
2019 | 2019-01-24 | Pikeville | 73374669 | 105257 | 38830954B30435 |  | 3403301-PRESTONSB / CITY | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needs guy marker. @ end of street next to school. | 770 N Arnold Ave, Prestonsburg, KY 41653, USA | 2019-06-05
2019 | 2019-01-24 | Pikeville | 72357341 | DKY0103666 | 38830954B30544 |  | 3403301-PRESTONSB / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole is rotten. Next to a wood privacy fence. | 432 Josephine Dr, Prestonsburg, KY 41653, USA | 2019-03-13
2019 | 2019-01-24 | Pikeville | 73375290 | DKY0105243 | 38830954B40276 |  | 3403301-PRESTONSB / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole is rotten. End of South Harkins street. | 98 South Harkins Avenue, Prestonsburg, Ky. | 2019-11-19
2019 | 2019-01-24 | Pikeville | 73374788 | DKY0105848 | 38830954B40560 |  | 3403301-PRESTONSB / CITY | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign |  | Top of pole has burned at some point. @Century 21 office. | 409 N Arnold Ave, Prestonsburg, KY 41653, USA | 2019-10-03
2019 | 2019-01-24 | Pikeville | 73374645 | DKY0105274 | 38830954B41099 |  | 3403301-PRESTONSB / CITY | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needs guy markers. @Family Eye Care office. | N Arnold Ave, Prestonsburg, KY 41653, USA | 2020-01-30
2019 | 2019-01-25 | Pikeville | 73374669 | 105257 | 38830954B10302 |  | 3403301-PRESTONSB / CITY | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. Near mountain metal. | Duncan St, Prestonsburg, KY 41653, USA | 2019-06-05
2019 | 2019-01-25 | Pikeville | 73374669 | 105257 | 38830954B20106 |  | 3403301-PRESTONSB / CITY | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needs guy marker | Stanley Ave, Prestonsburg, KY 41653, USA | 2019-06-05
2019 | 2019-01-25 | Pikeville | 73375274 | DKY0105449 | 38830954B20495 (not the actual pole ). READ COMMENTS. |  | 3403301-PRESTONSB / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole 38830954B20495 is a tall pole with xfmr bank behind van hoose lumber. The pole that is rotten is the secondary pole tapped off pole 495. The secondary pole is not shown on field view and does not have a pole tag.. it is beside the bldg behind vanhoose lumber where the scale is. Next to rr tracks. | Stanley Ave, Prestonsburg, KY 41653, USA | 2019-11-18
2019 | 2019-01-25 | Pikeville | 73374669 | 105257 | 38830954B20499 |  | 3403301-PRESTONSB / CITY | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Pole ground stolen. @ mouth happy hollow. | Happy Hollow, Prestonsburg, KY 41653, USA | 2019-06-05
2019 | 2019-01-28 | Pikeville |  |  | 38830955C00387 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | UG conduit: damaged or separated |  |  | KPC |  | Underground conduit held to pole with tape. Need to strap. | 974 Corn Fork Rd, Prestonsburg, KY 41653, USA
2019 | 2019-01-28 | Pikeville | 73375061 | DKY0105299 | 38830956000002 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole in slide. washed out | 1460 Corn Fork Rd, Prestonsburg, KY 41653, USA | 2019-08-29
2019 | 2019-01-28 | Pikeville |  |  | 38830979D00028 |  | 3410602-E.PRESTON / LANCER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker. Completed 1/28/19 D Lewis | 2307 KY-1428, Prestonsburg, KY 41653, USA | 2019-05-14
2019 | 2019-01-28 | Pikeville |  |  | 38830979D00104 |  | 3410602-E.PRESTON / LANCER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker. Completed 1/28/19 D Lewis | 58 Endicott Dr, Prestonsburg, KY 41653, USA | 2019-05-14
2019 | 2019-01-28 | Pikeville | 73374565 | 105157 | 38830979D00107 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire wrapped around pole. Either remove guy or install anchor and reattach guy wire. @ Rudd bldg. on left. | 2143 KY-1428, Prestonsburg, KY 41653, USA | 2019-07-17
2019 | 2019-01-28 | Pikeville |  |  | 38830980000002 |  | 3410602-E.PRESTON / LANCER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker. Completed 1/28/19 D Lewis | 2784 KY-1428, Prestonsburg, KY 41653, USA | 2019-05-14
2019 | 2019-01-28 | Pikeville | 73374778 | 105479 | 38831004000003 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop laying on roof. Probably need pole set to re-route or might take enough slack out for clearance. Also pole ground loose on pole. | 3149 KY-1428, Prestonsburg, KY 41653, USA | 2019-07-02
2019 | 2019-01-28 | Pikeville |  |  | 38831004000008 |  | 3410602-E.PRESTON / LANCER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy markers needed. Completed 1/28/19 D Lewis | 3456 KY-1428, Allen City, KY 41601, USA | 2019-05-14
2019 | 2019-01-28 | Pikeville | 73374565 | 105157 | 38831004000009 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire slack. Tighten guy. | 3542 KY-1428, Allen City, KY 41601, USA | 2019-07-17
2019 | 2019-01-28 | Pikeville | 73374565 | 105157 | 38831004000010 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign |  | Guy wire hanging down pole. Remove guy. In front of a metal bldg. | 3570 KY-1428, Allen City, KY 41601, USA | 2019-07-17
2019 | 2019-01-28 | Pikeville | 73391424 |  | 38831004000014 |  | 3410602-E.PRESTON / LANCER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy marker needed | 3792 KY-1428, Prestonsburg, KY 41653, USA | 2019-05-15
2019 | 2019-01-28 | Pikeville |  |  | 38831004000017 |  | 3410602-E.PRESTON / LANCER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needed guy marker. Completed 1/28/19 D Lewis | 3147 KY-1428, Prestonsburg, KY 41653, USA | 2019-05-14
2019 | 2019-01-29 | Pikeville | 73375335 | DKY0105386 | 38830954D30740 | TRUE | 3410602-E.PRESTON / LANCER | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground broken.@ second pole out of station. | S Lake Dr, Prestonsburg, KY 41653, USA | 2019-11-18
2019 | 2019-01-29 | Pikeville | 73374797 | DKY0105336 | 38830955B00103 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | already written to EDN100577 FOREIGN | Pole is rotten. Very rotten. Needs done ASAP. | 88 Cardinal Dr, Prestonsburg, KY 41653, USA | 2019-12-19
2019 | 2019-01-29 | Pikeville | 73375345 | DKY0105289 | 38830955B00127 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole rotten. Near Riverview Healthcare Center. | Sparrow Street, Prestonsburg, Ky. | 2019-11-13
2019 | 2019-01-29 | Pikeville | 73374810 | DKY0105385 | 38830955B00151 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign |  | Pole is rotten.@ end of street. | 25 Willow Ln, Prestonsburg, KY 41653, USA | 2019-12-09
2019 | 2019-01-29 | Pikeville |  |  | 38830955B00159 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needed guy marker | 151 Cardinal Dr, Prestonsburg, KY 41653, USA | 2019-01-29
2019 | 2019-01-29 | Pikeville | 73374598 | 105177 | 38830955B00182 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign |  | Crossarm burnt about 50 percent. @ James Adams middle school. In front. | 2520 S Lake Dr, Prestonsburg, KY 41653, USA | 2023-02-06
2019 | 2019-01-29 | Pikeville | 72418870 | DKY0103768 | 38830955B00185 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole is rotten.@ behind VFW club in parking lot. | 3090 S Lake Dr, Prestonsburg, KY 41653, USA | 2019-03-19
2019 | 2019-01-29 | Pikeville |  |  | 38830955B00205 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker | 73 N Circle Drive, Prestonsburg, Ky. | 2019-01-29
2019 | 2019-01-29 | Pikeville |  |  | 38830955B00206 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needed guy marker | Cooley Street, Prestonsburg, Ky. | 2019-01-29
2019 | 2019-01-29 | Pikeville | 72418870 | DKY0103768 | 38830955B00358 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire is touching roof. Might need to relocate anchor.@ in front of VFW club. Installed guy marker. | S Lake Dr, Prestonsburg, KY 41653, USA | 2019-03-19
2019 | 2019-01-29 | Pikeville | 73374598 | 105177 | 38830955B00381 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down.@ Bowling Alley. | Mayo Hollow, Prestonsburg, KY 41653, USA | 2023-02-06
2019 | 2019-01-29 | Pikeville |  |  | 38830955B00527 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker. Completed 1/29/10 D Lewis | Victoria Street, South Lake Drive, Prestonsburg, Ky. | 2019-01-29
2019 | 2019-01-29 | Pikeville |  |  | 38830955B00533 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needed guy marker | Sparrow Ln, Prestonsburg, KY 41653, USA | 2019-01-29
2019 | 2019-01-29 | Pikeville | 73374585 | DKY0105167 | 38830955B00540 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Installed guy marker. Needs guy insulator installed. | Poplar St, Prestonsburg, KY 41653, USA | 2022-09-07
2019 | 2019-01-29 | Pikeville | 73374585 | DKY0105167 | 38830955B00562 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Installed guy marker. Has a secondary guy wrapped around pole hanging loose. Backs up a long span of 4/0 quad secondary. Might need to install anchor or remove guy wire. Also outer shell of pole is rotten. Will be ok for now. @ in front of dollar general. | S Lake Dr, Prestonsburg, KY 41653, USA | 2022-09-07
2019 | 2019-01-29 | Pikeville |  |  | 38830955B20630 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker | 49 Sparrow Ln, Prestonsburg, KY 41653, USA | 2019-01-29
2019 | 2019-01-29 | Pikeville |  |  | 38830955B20633 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker | S Lake Dr, Prestonsburg, KY 41653, USA | 2019-01-29
2019 | 2019-01-29 | Pikeville |  |  | 38830979A00035 |  | 3410602-E.PRESTON / LANCER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needed guy marker | 140 N Riverview Lane, Prestonsburg, Ky. | 2019-05-14
2019 | 2019-01-29 | Pikeville | 73374874 | DKY0105381 | 38830979A00071 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | already written to EDN100577 FOREIGN | Pole is rotten. Installed guy marker. | 114 Hillside St, Prestonsburg, KY 41653, USA | 2019-12-30
2019 | 2019-01-29 | Pikeville |  |  | 38830979A00115 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop laying on roof. Probably need taller pole for clearance. | 50 Greer St, Prestonsburg, KY 41653, USA
2019 | 2019-01-30 | Pikeville |  |  | 38830955A00036 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker | Mayo Branch, Lake Road, Prestonsburg, Ky. | 2019-01-30
2019 | 2019-01-30 | Pikeville |  |  | 38830955B00563 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needed guy marker | S Lake Dr, Prestonsburg, KY 41653, USA | 2019-01-30
2019 | 2019-01-30 | Pikeville |  |  | 38830955C00475 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker | 710 Lake Road, Prestonsburg, Ky. | 2019-01-30
2019 | 2019-01-30 | Pikeville |  |  | 38830955D00164 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker | South Mays Avenue, Goble Roberts, Prestonsburg,Ky. | 2019-01-30
2019 | 2019-01-30 | Pikeville | 72418673 | DKY0103767 | 38830955D00234 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire hanging down pole loose. Remove guy. | Wells Dr, Prestonsburg, KY 41653, USA | 2019-03-14
2019 | 2019-01-30 | Pikeville |  |  | 38830955D00243 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker | 1st street, Goble Roberts, Prestonsburg, ky. | 2019-01-30
2019 | 2019-01-30 | Pikeville | 73374585 | DKY0105167 | 38830955D00267 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Top of anchor has been cut off. Guy is held with a come along grip. between the two truck scales @the coal company office. Installed guy marker. | Meadows Branch Rd, Kentucky 41653, USA | 2022-09-07
2019 | 2019-01-30 | Pikeville |  |  | 38830955D00291 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | crossarm/braces: deteriorated, not rotten |  | KPC |  | crossarms deteoriated pretty bad.4/0 service drop only about 8.5 ft off ground. Need set secondary pole for clearance.Might consider changing pole out also. | Meadows Branch Rd, Kentucky 41653, USA | 2023-10-11
2019 | 2019-01-30 | Pikeville | 72418673 | DKY0103767 | 38830955D00296 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole is rotten.@ Goble Roberts. Corner of Wells and Madison. | Wells Dr, Prestonsburg, KY 41653, USA | 2019-03-14
2019 | 2019-01-30 | Pikeville |  |  | 38830955D00323 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker | S Roberts Dr, Prestonsburg, KY 41653, USA | 2019-01-30
2019 | 2019-01-30 | Pikeville | 73375362 | 105366 | 38830955D00338 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole is rotten. | Meadows Branch Rd, Kentucky 41653, USA | 2019-08-06
2019 | 2019-01-30 | Pikeville |  |  | 38830955D00350 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire hanging down pole. Remove guy or reattach. Anchor is buried. | 174 1st St, Prestonsburg, KY 41653, USA | 2019-05-14
2019 | 2019-01-30 | Pikeville | 73374585 | DKY0105167 | 38830955D00472 | TRUE | 3410602-E.PRESTON / LANCER | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer and service | ky route 1428, prestonsburg, Ky. | 2022-09-07
2019 | 2019-01-30 | Pikeville |  |  | 38830979C00013 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker | Arron Court, Goble Roberts, Prestonsburg,Ky. | 2019-01-30
2019 | 2019-01-31 | Pikeville | 73374565 | 105157 | 38830979C00237 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire slack. Needs tightened. | Sugarloaf Branch, Prestonsburg, Ky. | 2019-07-17
2019 | 2019-01-31 | Pikeville |  |  | 38830979D00020 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Needed guy markers.@ Worldwide Equipment | 2011 KY-1428, Prestonsburg, KY 41653, USA | 2019-01-31
2019 | 2019-01-31 | Pikeville |  |  | 38830980000050 | TRUE | 3410602-E.PRESTON / LANCER | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | One phase of a three phase line laying on the ground. This phase is de-energized, however the other two phases are still energized. Dangerous situation. Needs to be cleared up ASAP. Can use truck when dry or frozen. #2 aluminum. | Dial Branch, Sugarloaf Branch, Prestonsburg, Ky. | 2019-05-14
2019 | 2019-01-31 | Pikeville |  |  | 38830980000050 | TRUE | 3410602-E.PRESTON / LANCER | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | One phase of a three phase line laying on the ground. This phase is de-energized, however the other two phases are still energized. Dangerous situation. Needs to be cleared up ASAP. Can use truck when dry or frozen. #2 aluminum. | Dial Branch, Sugarloaf Branch, Prestonsburg, Ky. | 2019-05-14
2019 | 2019-01-31 | Pikeville | 73736697 | DKY0105522 | 38830980000113 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Phase wire hanging down the pole. Line is de-energized however. Needs to be cleared up in case of contact by public. | Dial Branch, Sugarloaf Branch, Prestonsburg, Ky. | 2022-10-26
2019 | 2019-01-31 | Pikeville |  |  | 38830980000114 |  | 3410602-E.PRESTON / LANCER | Service work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker | Sugarloaf Branch, Kentucky 41653, USA | 2019-01-31
2019 | 2019-02-01 | Pikeville | 74070719 | DKY0106006 | 38831140C00004 |  | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Primary neutral on ground. # 2 aluminum. @ 5th pole from station. | Mineshaft Road, Evanston, Ky. | 2020-02-27
2019 | 2019-02-01 | Pikeville | 74070719 | DKY0106006 | 38831140C00036 | TRUE | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Primary neutral down/stolen. #4 copper. pole has been re-enforced at the ground previously. Appears to be reasonably solid but might consider going ahead and change pole out cause it may not be the safest to climb. Little bit of swampy area. Be best when dry or frozen. | Mineshaft Road, Evanston, Ky. | 2020-02-27
2019 | 2019-02-01 | Pikeville | 74070719 | DKY0106006 | 38831140C00037 |  | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Neutral down. Stolen. #4 copper | Mineshaft Road, Evanston, Ky. | 2020-02-27
2019 | 2019-02-04 | Pikeville | 74070747 | DKY0106191 | 38831091000020 |  | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer | 308 Hughes Creek Road, Evanston, Ky. | 2020-02-27
2019 | 2019-02-04 | Pikeville | 74070747 | DKY0106191 | 38831091000022 |  | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer | . 5 mi up Hughes Creek Road, Evanston, Ky. | 2020-02-27
2019 | 2019-02-04 | Pikeville |  |  | 38831092000011 |  | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer | Hughes Creek Road, Evanston, Ky. | 2019-07-26
2019 | 2019-02-04 | Pikeville |  |  | 38831092000017 |  | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Silk Stocking Road, Evanston, Ky. | 2019-07-26
2019 | 2019-02-04 | Pikeville |  |  | 38831092000018 |  | 3404002-SPRINGFOR / 1PHASEDIS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needed guy marker | Silk Stocking Road, Evanston, Ky. | 2019-02-04
2019 | 2019-02-04 | Pikeville | 74078796 | DKY0106149 | 38831092000024 |  | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Customer has built a shed around the pole. Also pole has been previously re-enforced. | Silk Stocking Road, Evanston, Ky. | 2020-02-12
2019 | 2019-02-05 | Pikeville | 74078256 | DKY0106057 | 38831023000004 |  | 3402501-MIDDLECRE / DISTRIBUTION | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire broken hanging down pole. Swampy area. | Poplar Branch, David Kentucky 41616, USA | 2019-11-06
2019 | 2019-02-05 | Pikeville | 74078256 | DKY0106057 | 38831023000028 |  | 3402501-MIDDLECRE / DISTRIBUTION | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove abandoned secondary pole. | 133 Poplar Branch, David, KY 41616, USA | 2019-11-06
2019 | 2019-02-05 | Pikeville | 74078256 | DKY0106057 | 38831023000032 |  | 3402501-MIDDLECRE / DISTRIBUTION | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire hanging down pole loose. Might need to hand dig new anchor. Did not see one. | 198 Triple S Road, David, Ky. | 2019-11-06
2019 | 2019-02-05 | Pikeville |  |  | 38831047000105 |  | 3402501-MIDDLECRE / DISTRIBUTION | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop very low. Can reach from ground. Old trailer on left of route 404 @ mouth of Triple S Road. Nobody living here. Meter has been removed.Contacted servicer and removed service. | Ky. Route 404 , David, Ky. | 2019-02-06
2019 | 2019-02-05 | Pikeville | 74078242 | DKY0106054 | 38831047000106 |  | 3402501-MIDDLECRE / DISTRIBUTION | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive secondary and pole. | Weddington Hollow, David, Ky. | 2019-11-06
2019 | 2019-02-06 | Pikeville | 74078242 | DKY0106054 | 38831047000023 |  | 3402501-MIDDLECRE / DISTRIBUTION | Service Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Pole is covered with vines | 6630 State Hwy 404, David, KY 41616, USA | 2019-11-06
2019 | 2019-02-06 | Pikeville |  |  | 38831047000034 |  | 3402501-MIDDLECRE / DISTRIBUTION | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop is touching the roof. Will need to set a secondary pole to correct or a pole in line maybe. The pole is tagged as 35 but on field view it’s 34. | 230 Official Hollow, David, KY 41616, USA
2019 | 2019-02-06 | Pikeville | 72482726 | 0103841 | 38831047000090 |  | 3402501-MIDDLECRE / DISTRIBUTION | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | pole: leaning, burned more than 50% remaining |  | KPC |  | 4/0 quad service only about 8 feet off ground. Xformer bank pole leaning . Need to install anchor and guy on xformer bank pole and probably on secondary pole 38831047000091 also to correct clearance. 1/4 mile above the station on left. | 6134 Hwy 404, David, Ky. | 2019-03-13
2019 | 2019-02-06 | Pikeville | 74078242 | DKY0106054 | 38831047000100 |  | 3402501-MIDDLECRE / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator melting down. Last house school house Hollow. Last primary pole. | David, KY 41616, USA | 2019-11-06
2019 | 2019-02-07 | Pikeville | 73172043 | 105107 | 37820058B00514 |  | 2970603-HURLEY / RACEFORK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | 335 Lick Branch, Rockhouse Road, Paw paw, Ky. | 2019-06-26
2019 | 2019-02-07 | Pikeville | 73172043 | 105107 | 37820081B00123 |  | 2970603-HURLEY / RACEFORK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guys are slack. Needs tightened. Double dead-end angle pole. | 6125 Paw paw creek, Hurley, Va. | 2019-06-26
2019 | 2019-02-07 | Pikeville | 73172043 | 105107 | 37820081B40542 |  | 2970603-HURLEY / RACEFORK | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | Neutral sagged below phone cables. Needs slack taken out.# 2 aluminum. Truck accessible. | 6060 paw paw creek, Hurley, Va. | 2019-06-26
2019 | 2019-02-08 | Pikeville | 72876560 | DKY0104784 | 37830161D00036 |  | 3407103-TOPMOST / KITE | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Anchor has been dozed out. Need to install anchor and reattach guy. @ just before Roaring Branch on right. | Highway 7 South, Topmost, Ky. | 2020-06-24
2019 | 2019-02-08 | Pikeville |  |  | 37830161D00163 |  | 3407103-TOPMOST / KITE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Customer has built a barn around the pole. @ just before Roaring Branch on the right. | Highway 7 south, Topmost, Ky.
2019 | 2019-02-08 | Pikeville | 72876510 | DKY0104585 | 37830185000033 |  | 3407103-TOPMOST / KITE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down.@ turn right up hill @Drew Lane. | 336 Hall Branch, Topmost, Ky. | 2019-12-18
2019 | 2019-02-08 | Pikeville | 72876673 | 104752 | 37830185000043 |  | 3407103-TOPMOST / KITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole washed out around in the creek. Could reach with tandem line truck boom to set pole. | 930 Hall Branch, Topmost, Ky. | 2019-07-12
2019 | 2019-02-12 | Pikeville | 73627821 | 105404 | 37830210000067 |  | 3407103-TOPMOST / KITE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Primary conductors too close to rooftop. Customer said he was planning on putting metal roof on this spring. Will need taller pole for clearance or relocate pole away from house . | 1251 Bates Branch Rd, Kite, KY 41828, USA | 2019-06-12
2019 | 2019-02-13 | Pikeville | 72876510 | DKY0104585 | 37830185000192 |  | 3407103-TOPMOST / KITE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive 2 pole tap and transformers. Take-off pole is 37830185000015. | Tuttle Dr, Kentucky 41828, USA | 2019-12-18
2019 | 2019-02-13 | Pikeville | 72876685 | DKY0104751 | 37830209000064 |  | 3407103-TOPMOST / KITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | already written to EDN100577 KPC pole | Pole partially washed out in creek.@ Sherman lane. | 1324 Mullins Branch Rd, Kite, KY 41828, USA | 2019-05-24
2019 | 2019-02-14 | Pikeville | 72876510 | DKY0104585 | 37830209000228 |  | 3407103-TOPMOST / KITE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Twist secondary laying across a telephone drop. Probably can take slack out of secondary to get clearance over phone cables. | Heritage Drive, Kite, KY. | 2019-12-18
2019 | 2019-02-15 | Pikeville |  |  | 37830234B10289 | TRUE | 3407103-TOPMOST / KITE | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole Ground Stolen. Repair completed. | 1132 Puncheon Branch Rd, Kite, KY 41828, USA | 2019-02-15
2019 | 2019-02-15 | Pikeville |  |  | 37830234B20288 | TRUE | 3407103-TOPMOST / KITE | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. Repaired on site. | Puncheon Creek, Kentucky 41339, USA | 2019-02-15
2019 | 2019-02-15 | Pikeville | 72876706 | 104756 | 37830258000040 |  | 3407103-TOPMOST / KITE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Anchor washed out partially. Last pole in Puncheon Creek. | 2535 Puncheon Branch Rd, Kite, KY 41828, USA | 2019-05-23
2019 | 2019-02-18 | Pikeville | 72876560 | DKY0104784 | 37830161D00024 |  | 3407101-TOPMOST / DEMA | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | Conductor needs to be re-tied. Appears to be barely hanging on insulator. Can use truck if dry or frozen.@ above Potato Branch on left side of road where line crosses the creek and railroad. 5th pole above Family Dollar store. | KYRoute 7, Topmost, ky. | 2020-06-24
2019 | 2019-02-18 | Pikeville | 72876560 | DKY0104784 | 37830161D40250 |  | 3407101-TOPMOST / DEMA | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Secondary pole leaning. Needs anchor and guy or needs to be straightened.Brick house on right across from Family Dollar. Install: 2018 | 6784 KY-7, Topmost, KY 41862, USA | 2020-06-24
2019 | 2019-02-18 | Pikeville |  |  | 37830234B10289 |  | 3407103-TOPMOST / KITE | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen | 1132 Puncheon Branch Rd, Kite, KY 41828, USA | 2019-03-21
2019 | 2019-02-18 | Pikeville |  |  | 37830234B20288 |  | 3407103-TOPMOST / KITE | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. Repairs completed today. | 1426 Puncheon Branch Rd, Kite, KY 41828, USA | 2019-03-21
2019 | 2019-02-19 | Pikeville | 70580284 - cancelled | DKY0101433 | 37830210000023 |  | 3407101-TOPMOST / DEMA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | already written to EDN100577 KPC pole | Pole is hollow. Septic system close by. | Johnson Lane, Rfk Dry Creek, Topmost, Ky. | 2023-05-11
2019 | 2019-02-20 | Pikeville |  |  | 37830090000005 |  | 3407101-TOPMOST / DEMA | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop laying on roof of mobile home. Old rusty brown looking mobile home on right. | Little Doty Branch, Dema, KY.
2019 | 2019-02-20 | Pikeville | 75959989 | DKY0109308 | 37830113000004 |  | 3407101-TOPMOST / DEMA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Just above Floyd / Knott co line on right. Mobile home on hill. | 250 KY-7, Dema, KY 41859, USA | 2020-05-12
2019 | 2019-02-21 | Pikeville | 74725280 | DKY0107026 | 37830089000058 |  | 3407101-TOPMOST / DEMA | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive 2 pole tap. Poles 37830089000090 and 91. @ the open point between Garrett/ Garrett and Topmost/Dema. @Floyd/ Knott County line. | Elsie Drive, Dema, KY. | 2020-01-30
2019 | 2019-02-21 | Pikeville |  |  | 37830113000018 |  | 3407101-TOPMOST / DEMA | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Secured loose pole ground. | KY Hwy. 899, Dema, KY. | 2019-02-21
2019 | 2019-02-21 | Pikeville | 73268301 | DKY0108636 | 37830113000024 |  | 3407101-TOPMOST / DEMA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer | Basket Drive, Ky route 899, Dema, KY. | 2021-07-27
2019 | 2019-02-21 | Pikeville | 74177235 | DKY0106549 | 37830113000070 |  | 3407101-TOPMOST / DEMA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | already written to EDN100577 FOREIGN | Secondary pole rotten at ground line. | 284 Freedom lane, Dema, KY. | 2020-03-11
2019 | 2019-02-21 | Pikeville |  |  | 37830114A00212 |  | 3407101-TOPMOST / DEMA | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , service: unused or abandoned, blanked meter base |  |  | KPC |  | Found service pole laying on ground. Service still attached and energized. Contacted DDC and de-energized service. | Little Doty Creek, Dema, KY. | 2019-02-21
2019 | 2019-02-21 | Pikeville | 74177096 | DKY0106825 | 37830161C00004 |  | 3407101-TOPMOST / DEMA | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole is hollow. NC switch pole. Install: 1968 | 5125 KY-7, Topmost, KY 41862, USA | 2020-01-27
2019 | 2019-02-21 | Pikeville | 74176534 | DKY0106436 | 37830161C00034 |  | 3407101-TOPMOST / DEMA | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop is barely clearing roof top. Need to re-sag service for clearance. Gray trailer on left. | 4833 KY-7, Topmost, KY 41862, USA | 2019-11-26
2019 | 2019-02-21 | Pikeville | 74176534 | DKY0106436 | 37830161D00180 |  | 3407101-TOPMOST / DEMA | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning. In a slide area. Lot of water around it. Needs straightened or install guy and anchor.`@Stumbo Drive. | 5770 KY-7, Topmost, KY 41862, USA | 2019-11-26
2019 | 2019-02-21 | Pikeville | 74177082 | DKY0106991 | 37830162000121 |  | 3407101-TOPMOST / DEMA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | already written to EDN100577 KPC pole | Rotten pole. | 6047 KY-7, Topmost, KY 41862, USA | 2023-05-11
2019 | 2019-02-26 | Pikeville | 74176534 | DKY0106436 | 37830114D00093 |  | 3407101-TOPMOST / DEMA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer and service..1 mile up on right. | Salisbury Branch, Dema, KY. | 2019-11-26
2019 | 2019-02-26 | Pikeville | 72866220 | 104565 | 37830138000053 | TRUE | 3407101-TOPMOST / DEMA | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Pole needs guy and anchor installed. Also remove pole and span beyond. Pole 37830138000054..last pole in Salisbury Branch. | Salisbury Branch Rd, Kentucky 41859, USA | 2019-08-16
2019 | 2019-02-26 | Pikeville | 74177160 | DKY0106830 | 37830138000067 |  | 3407101-TOPMOST / DEMA | Line Work | OH |  |  |  | KPC |  | outer she’ll of pole is rotten. | 60 Patten Branch of Beaver Creek Rd, Dema, KY 41859, USA | 2020-01-22
2019 | 2019-02-26 | Pikeville | 74177054 | DKY0106979 | 37830162000166 |  | 3407101-TOPMOST / DEMA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | already written to EDN100577 KPC pole | Pole partially washed out. In creek. | Wren Lane, Oldhouse Branch, Ky route 1091, Topmost, KY. | 2020-01-21
2019 | 2019-02-28 | Pikeville |  |  | 38821089C00124 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | guys/anchors: broken or missing | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Guy wire hanging loose down pole. Could not find anchor to re-attach. Pole is leaning in direction of guy already and appears to be filled around so it’s extra deep. Very short lateral. Will secure guy and make safe. Don’t think guy is needed. | 44600 KY-194, Freeburn, KY 41528, USA | 2019-02-28
2019 | 2019-02-28 | Pikeville | 73034975 | 104782 | 38821089C00303 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign |  | Crossarm deteoriated and bent. Not urgent but it is in STATION ZONE. | 44517 KY-194, Freeburn, KY 41528, USA | 2019-07-15
2019 | 2019-02-28 | Pikeville | 73034975 | 104782 | 38821089C00514 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | pole: leaning, burned more than 50% remaining | Forestry - DESCRIBE IN COMMENTS | KPC |  | Secondary pole leaning. Not serving anything but a d-d light at this time. Probably will need the dual axle line truck to reach from the road. Will also need some tree trimming. | 44517 KY-194, Freeburn, KY 41528, USA | 2019-07-15
2019 | 2019-03-01 | Pikeville | 73036673 | DKY0104927 | 38821089C00101 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | Service drop laying on roof. Will need to set pole for clearance. Might need backyard machine. | 44770 KY-194, Freeburn, KY 41528, USA | 2020-02-20
2019 | 2019-03-01 | Pikeville |  |  | 38821089D12114 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop is against roof. Probably need a secondary pole installed or re-route service from adjacent pole. | 153 justice hollow, barrenshee creek, Freeburn, KY.
2019 | 2019-03-01 | Pikeville | 73034827 | DKY0106053 | 38821113D00067 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | service: unused or abandoned, blanked meter base |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive secondary and pole 38821113D00264 | 383 Nicholas Fork, Barrenshee Creek, Freeburn, KY | 2019-09-09
2019 | 2019-03-01 | Pikeville | 73035790 | DKY0104907 | 38821114B00002 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning. Needs side guy and anchor. Also has two big holes in side of pole. Install: 1993 | 2118 Barrenshee Creek, Freeburn, KY 41528, USA | 2022-12-15
2019 | 2019-03-04 | Pikeville |  |  | 38821089D00289 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  |  |  | Foreign |  | Customer has built a home and it’s touching pole. | 45331 State route 194 Majestic, KY.
2019 | 2019-03-04 | Pikeville |  |  | 38821090B00007 |  | 3200202-BARRENSHE / VULCAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. Repaired same day. | 45516 State route 194 Freeburn, KY. | 2019-03-04
2019 | 2019-03-04 | Pikeville | 73035113 | DKY0104723 | 38821090C00190 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarm split. | 566 Woodman Creek, Majestic, KY. | 2020-02-17
2019 | 2019-03-04 | Pikeville | 73035583 | DKY0104898 | 38821090C00255 | TRUE | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning. Needs straightened. Anchor and guy. Can drill anchor. Install: 1975 | 326 Woodman Creek, Majestic, KY. | 2022-06-29
2019 | 2019-03-04 | Pikeville | 70548042 / (old #) 73035637 | DKY0101505 / (old #)104796 | 38821090D00154 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | already written to EDN100577 KPC pole | Pole is rotten. @ mouth of woodman Creek...Buckarm pole. | Woodman Creek, Majestic, KY. | 2020-04-29
2019 | 2019-03-04 | Pikeville | 73035573 | DKY0104778 | 38821091B00107 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning. Needs a side guy. No truck . Probably rock hole. Need flagging. @ 2.5 miles up woodman creek on hill. Install 1991 | Woodman Creek, Majestic , KY. | 2022-06-29
2019 | 2019-03-05 | Pikeville |  |  | 37820242000002 | TRUE | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Map does not show a transformer here. 25kva t/a | Ash camp Road | 2019-04-23
2019 | 2019-03-06 | Pikeville | 73035113 | DKY0104723 | 38821090D00096 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Dead-end insulator broken. | 47744 State route 194 Majestic, Ky | 2020-02-17
2019 | 2019-03-06 | Pikeville |  |  | 38821114C00128 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign |  | Guy wire broken. Need to re-attach. 3 phase Buckarm pole. 1/2guy wire. Don’t see anchor anywhere. | 48514 State route 194 Majestic, KY | 2019-04-08
2019 | 2019-03-06 | Pikeville | 73034975 | 104782 | 38821114D00158 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Remove secondary pole. Andsecondary from pole 38821114D00096. Pole is burnt badly. | 49234 State route 194, Stopover, KY. | 2019-07-15
2019 | 2019-03-06 | Pikeville |  |  | 38821115A00006 |  | 3200202-BARRENSHE / VULCAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen on fuse pole. Repaired on site. | Woodman Creek, Majestic, KY | 2019-03-06
2019 | 2019-03-06 | Pikeville |  |  | 38821115A30102 |  | 3200202-BARRENSHE / VULCAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen on recloser pole. Completed same day. | Woodman Creek, Majestic, KY | 2019-03-06
2019 | 2019-03-07 | Pikeville | 73118755 | DKY0104951 | 37820011A00066 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning. Straighten pole. Install: unknown | 1420 Hurricane Creek, Stopover, KY. | 2020-02-20
2019 | 2019-03-07 | Pikeville | 86180859 |  | 37820011A00519 |  | 3200202-BARRENSHE / VULCAN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Remove service drop hanging down pole. Service is de-energized. | Melon Fork, Hurricane Creek, Argo, KY.
2019 | 2019-03-07 | Pikeville |  |  | 38821139C00006 |  | 3200202-BARRENSHE / VULCAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack. Repaired same day. | Woodman Creek, Argo, KY. | 2019-03-07
2019 | 2019-03-07 | Pikeville | 73444241 | 105210 | 38821139C00011 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign |  | Pole is rotten. @ mouth of lower elk creek @ the bridge. | Lower Elk Creek, Argo, KY. | 2019-07-16
2019 | 2019-03-07 | Pikeville | 73035217 | 104749 | 38821140A00502 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Anchor washed out. Needs new anchor. | Lower Elk Creek, Argo, KY. | 2019-06-05
2019 | 2019-03-07 | Pikeville | 73035276 | 104739 | 38821140A00509 | TRUE | 3200202-BARRENSHE / VULCAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. About 1 mile up lower elk creek. | Rfk Lower Elk Creek, Argo, Ky | 2019-06-19
2019 | 2019-03-07 | Pikeville | 73035276 | 104739 | 38821140A00513 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy needs insulator. | 1317 Lower Elk Creek, Argo, KY. | 2019-06-19
2019 | 2019-03-08 | Pikeville | 73035462 | DKY0104750 | 37820011C00511 | TRUE | 3200202-BARRENSHE / VULCAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | already written to EDN100577 KPC pole | Pole is rotten | River Elk Road, Argo, KY. | 2022-08-17
2019 | 2019-03-08 | Pikeville | 73035462 | DKY0104750 | 37820011C00512 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service hanging down pole. It is De-energized | River Elk Road, Argo, KY. | 2022-08-17
2019 | 2019-03-08 | Pikeville |  |  | 38821139B00035 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarm split. No truck. On hillside. Railroad Crossing. Pole might be rotten. | Woodman Creek, Woodman, Ky. | 2022-12-08
2019 | 2019-03-11 | Pikeville | 73035462 | DKY0104750 | 37820011C00008 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Crossarm brace broken. | 53147 State Hwy 194 Woodman, KY. | 2022-08-17
2019 | 2019-03-11 | Pikeville | 73035513 | 104764 | 37820011D00018 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  |  |  | Foreign |  | Neutral wire hanging down pole. Span missing. | 53787 State Hwy 194 Argo, KY. | 2019-06-18
2019 | 2019-03-11 | Pikeville |  |  | 37820011D40628 |  | 3200202-BARRENSHE / VULCAN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on recloser pole. Repaired same day. | Upper Elk Creek Dr. Argo, KY. | 2019-03-11
2019 | 2019-03-11 | Pikeville | 73035513 | 104764 | 37820034C30069 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove unused secondary and poles 37820034C30069 and 70. Secondary is de-energized. | 1321 Camp Creek, Argo, Ky | 2019-06-18
2019 | 2019-03-11 | Pikeville | 73035513 | 104764 | 37820035A00005 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | pole: leaning, burned more than 50% remaining , guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire slack. Pole leaning. Has service drop low. Will try to take slack out of guy and pull pole back. Tightened guy but service drop still lower than should be. Customer service pole is rotten and he has plans to move equipment to new pole that he has set already. Might need to install secondary pole. | 297 Camp Creek, Argo, KY. | 2019-06-18
2019 | 2019-03-11 | Pikeville | Outage# 4970541 |  | 37820035A10544 |  | 3200202-BARRENSHE / VULCAN | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Secondary low. Needs slack taken out. Contacted DDC to create ticket for servicer to remove slack for proper clearance. Servicer corrected the clearance. | Whispering Hills, Camp Creek, Argo, KY. | 2019-03-11
2019 | 2019-03-12 | Pikeville | 73035430 | 104922 | 37820011A00056 | TRUE | 3200202-BARRENSHE / VULCAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Open wire secondary too close to roof of barn. Secondary could be removed. Transformer on adjacent poles. | 857 Hurricane Creek, Stopover, KY. | 2019-06-18
2019 | 2019-03-12 | Pikeville |  |  | 38821115D00008 |  | 3200202-BARRENSHE / VULCAN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on recloser pole. Repaired same day. | 5127 Woodman Summer Road, Woodman, KY. | 2019-03-12
2019 | 2019-03-12 | Pikeville |  |  | 38821139B00052 |  | 3200202-BARRENSHE / VULCAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen on transformer pole. Repaired same day. | 52162 State route 194, Stopover, KY. | 2019-03-12
2019 | 2019-03-13 | Pikeville |  |  | 38821139A00148 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop is barely clearing the roof. Need to raise drop up at point of attachment on the customers mast. Cream colored house on hill on the right. | 51509 State Hwy 194, Stopover, KY.
2019 | 2019-03-13 | Pikeville | 73035714 | DKY0104800 | 38821139A00161 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole in slide area. Partially washed out around. @ Cream colored house/ brown trim on hill on right. Long concrete driveway. Inspect bridge b4 crossing with large trucks. Install: 1978 | 50889 State Hwy 194, Stopover, KY. | 2020-02-05
2019 | 2019-03-13 | Pikeville | 73035430 | 104922 | 38821139A00164 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Loop insulator broken. | 51509 State Hwy 194, Stopover, KY. | 2019-06-18
2019 | 2019-03-13 | Pikeville | 73035430 | 104922 | 38821139A00176 |  | 3200202-BARRENSHE / VULCAN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down pole. De-energized. Remove drop. | 51424 State Hwy 194, Stopover, KY. | 2019-06-18
2019 | 2019-03-13 | Pikeville |  |  | 38821139B00128 |  | 3200202-BARRENSHE / VULCAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen on transformer pole. Repaired same day. | 51765 State Hwy 194, Stopover, Ky | 2019-03-13
2019 | 2019-03-14 | Pikeville | 74078769 | DKY0106206 | 38831123A00014 | TRUE | 3408101-SALISBURY / PRINTER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Top of pole is split.@ Hite Road entrance@ phone co. facilities. | KY. Route 2030, Printer, KY. | 2019-09-18
2019 | 2019-03-18 | Pikeville | 76439022 | DKY0109942 | 37830019000108 |  | 3408101-SALISBURY / PRINTER | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Spurlock Church Road, Printer, KY. | 2020-07-16
2019 | 2019-03-18 | Pikeville | 74077961 | DKY0106340 | 38831122000191 |  | 3408101-SALISBURY / PRINTER | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Secondary pole leaning towards road. Remove inactive secondary and pole. | 3520 KY. Route 122, Printer, KY.. | 2019-11-12
2019 | 2019-03-18 | Pikeville | 74078769 | DKY0106206 | 38831123A00014 | TRUE | 3408101-SALISBURY / PRINTER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole top is split. @ the entrance to route 2030 East next to phone co. boxes. | KY. Route 2030, Printer, KY. | 2019-09-18
2019 | 2019-03-18 | Pikeville | 74077961 | DKY0106340 | 38831123B00230 |  | 3408101-SALISBURY / PRINTER | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator melting down. Behind brick house. End of street. | 75 Woody Lane, KY route 122, Printer, KY. | 2019-11-12
2019 | 2019-03-18 | Pikeville | 74077961 | DKY0106340 | 38831123B00246 |  | 3408101-SALISBURY / PRINTER | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire partially missing. Hanging down below transformer with insulator still attached. Couldn’t find anchor. Need to install both. | KY. Route 122, Printer, KY. | 2019-11-12
2019 | 2019-03-18 | Pikeville | 74078195 | DKY0106027 | 38831146C00256 | TRUE | 3408101-SALISBURY / PRINTER | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer and secondary pole 38831146C00284. Cutout on xformer pole is broken and hanging down.@ just before Shop Branch, Printer on route 122 | KY. Route 122, Printer, KY. | 2019-11-07
2019 | 2019-03-18 | Pikeville | 74070777 | DKY0106016 | 38831147000091 |  | 3408101-SALISBURY / PRINTER | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator melting down. No truck. | 2034 Shop Branch, Printer, KY 41655, USA | 2019-11-07
2019 | 2019-03-18 | Pikeville | 74071223 | DKY0106011 | 38831147000193 | TRUE | 3408101-SALISBURY / PRINTER | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Last pole in gunstock. | Gunstock Hollow, Printer, KY. | 2019-11-07
2019 | 2019-03-18 | Pikeville |  |  | 38831147D40212 |  | 3408101-SALISBURY / PRINTER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole in slide area. | 3612 Trace Branch, Printer, KY. | 2019-07-26
2019 | 2019-03-18 | Pikeville | 76438988 | DKY0109951 | 38831148000066 |  | 3408101-SALISBURY / PRINTER | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning toward road. Has secondary pulled tight. Pole has been hit by truck or something presumably because it’s leaning. Install: 1989 | KY. Route 2030, Trace Branch, Honaker, KY. | 2022-05-18
2019 | 2019-03-18 | Pikeville | 86180928 |  | 38831148000273 |  | 3408101-SALISBURY / PRINTER | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down pole. | KY. route 2030, Trace Branch, Printer, KY.
2019 | 2019-03-20 | Pikeville | 74078195 | DKY0106027 | 38831146C00036 | TRUE | 3408101-SALISBURY / PRINTER | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive secondary and pole. | 4289 KY. Hwy. 122, Hunter, KY. | 2019-11-07
2019 | 2019-03-20 | Pikeville |  |  | 38831146C40306 |  | 3408101-SALISBURY / PRINTER | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | DirecTv | 4548 KY. Hwy 122, Hunter, KY.
2019 | 2019-03-21 | Pikeville | 84899211 | DKY0120962 | 37830047A00362 |  | 3403003-PIKEVILLE / CEDAR CREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | pole leaning..needs anchor and side guy. No truck. Install: 1986 | 988 Elisha Fork, Cedar Creek, Pikeville, KY.
2019 | 2019-03-21 | Pikeville | 83966317 | DKY0120215 | 37830047C00228 | TRUE | 3403003-PIKEVILLE / CEDAR CREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning. STATION ZONE. Next to recloser pole on Cedar Creek. Install: 1983 | Ivy Court, Cedar Creek, Pikeville, KY. | 2023-04-21
2019 | 2019-03-21 | Pikeville | 83966475 | DKY0120044 | 37830047C00306 |  | 3403003-PIKEVILLE / CEDAR CREEK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Pole leaning. Needs anchor and dead end guy. Conductors sagging. @ the gate where recloser pole is. 3 phase line going up hill. | Ivy Court, Cedar Creek, Pikeville, KY. | 2023-04-21
2019 | 2019-03-21 | Pikeville | 83966475 | DKY0120044 | 37830047C00307 |  | 3403003-PIKEVILLE / CEDAR CREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive pole and conductors. Wire laying on ground. 3 phase line going up hill at the gate where reclosers are. | Ivy Court, Cedar Creek, Pikeville, KY. | 2023-04-21
2019 | 2019-03-21 | Pikeville | 83966475 | DKY0120044 | 37830047C00308 |  | 3403003-PIKEVILLE / CEDAR CREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive pole and conductors. Old line that goes up the hill behind the reclosers. Pole leaning bad. | Ivy Court, Cedar Creek, Pikeville, KY. | 2023-04-21
2019 | 2019-03-21 | Pikeville |  |  | 37830048A11739 |  | 3403003-PIKEVILLE / CEDAR CREEK | Line Work | UG |  | transformers: leaking, damaged |  | KPC |  | Padmount transformer has been filled in around it and has the lock completely buried. Can’t open transformer. TRANSFORMER IS NOT LEAKING | Renee Drive, Pikeville, KY.
2019 | 2019-03-25 | Pikeville |  |  | 37830022000033 |  | 3403003-PIKEVILLE / CEDAR CREEK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Neutral conductor sagging below communication cables. Needs slack taken out. | 300 Wagner Fork, Hurricane Creek, Pikeville, KY. | 2023-03-02
2019 | 2019-03-25 | Pikeville | 83966634 | DKY0120424 | 37830022000201 |  | 3403003-PIKEVILLE / CEDAR CREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove single phase tap and transformer. Trees have grown up and are pushing the neutral up closer to the primary. Or ROW could be cut and leave be. Line is energized but no customers served off the transformer. | Wagner Fork, Hurricane Creek, Pikeville, KY. | 2023-06-19
2019 | 2019-03-25 | Pikeville |  |  | 38831150000327 |  | 3403003-PIKEVILLE / CEDAR CREEK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | Service drop laying on roof. Needs to be raised on customers service pole. Tan mobile home on right going up Hurricane Creek. | 3061 Hurricane Creek, Pikeville, KY.
2019 | 2019-03-26 | Pikeville |  |  | 37830023D40069 |  | 3403003-PIKEVILLE / CEDAR CREEK | Service Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC |  | Pole and transformer covered with vines. | 313 Adams Lane, Pikeville, KY. | 2023-10-11
2019 | 2019-03-26 | Pikeville | 74386645 |  | 37830024B20173 |  | 3403003-PIKEVILLE / CEDAR CREEK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire hanging down pole. Looks like anchor may have been dozed out. Single phase tap crosses the road just before the ramp to U.S. 23 | Bowles Park Drive, North Mayo Trail , Pikeville, KY. | 2019-08-27
2019 | 2019-03-26 | Pikeville |  |  | 37830024C00061 |  | 3403003-PIKEVILLE / CEDAR CREEK | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. Repaired same day. | 731 Ratliff Creek, Pikeville, KY. | 2019-03-26
2019 | 2019-03-26 | Pikeville | 77208518 | DKY0112524 | 38831152D21753 |  | 3403003-PIKEVILLE / CEDAR CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole in slide area. Line going up to cell tower on Ratliff Creek. Next to last pole. | Evergreen Lane, Ratliff Creek, Pikeville, KY. | 2021-02-08
2019 | 2019-03-27 | Pikeville | 77209119 | DKY0110700 | 37830048B10835 |  | 3410503-S.PIKEVIL / HOSPITAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten secondary pole. Lot behind Dairy Cheer. | Harley Drive, South Mayo Trail, Pikeville, KY. | 2020-12-08
2019 | 2019-03-27 | Pikeville | 86142571 |  | 37830048B10945 |  | 3410503-S.PIKEVIL / HOSPITAL | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire broken. Anchor is buried under pavement. Needs anchor installed. | Harley Drive, Pikeville, KY.
2019 | 2019-03-27 | Pikeville |  |  | 37830048B11400 |  | 3410503-S.PIKEVIL / HOSPITAL | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarm burnt in two. @ Pizza Hut | S Mayo Trail, Pikeville, KY 41501, USA | 2023-10-11
2019 | 2019-03-28 | Pikeville | 86143067 |  | 37830048D20107 |  | 3410503-S.PIKEVIL / HOSPITAL | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Crossarms are deteoriated.@Wrightway equipment rental @ mouth Lanks Branch. | S Mayo Trail, Pikeville, KY 41501, USA
2019 | 2019-03-28 | Pikeville |  |  | 37830048D20985 |  | 3410503-S.PIKEVIL / HOSPITAL | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Secondary sagged below communication cables. Neutral broken in secondary. @ Recloser pole. | S Mayo Trail, Pikeville, KY 41501, USA | 2023-10-11
2019 | 2019-03-28 | Pikeville | 86143067 |  | 37830048D21296 |  | 3410503-S.PIKEVIL / HOSPITAL | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | Customer has built an equipment rack around secondary pole. Appears they might have already made contact with our secondary conductors. Might need to relocate pole. @ Wrightway rental. | S Mayo Trail, Pikeville, KY 41501, USA
2019 | 2019-03-28 | Pikeville |  |  | 37830072A00214 |  | 3410503-S.PIKEVIL / HOSPITAL | Line Work | OH |  | pole: leaning, burned more than 50% remaining , lightning arresters/insulators: damaged |  | KPC |  | Pole leaning over building. Lightning arrestor blown. Truck access but difficult because of surrounding buildings. Street behind Happy Days Diner. Install: unknown | 132 Cypress Lane, South Mayo Trail, Pikeville, KY.
2019 | 2019-03-28 | Pikeville |  |  | 37830072A00561 |  | 3410503-S.PIKEVIL / HOSPITAL | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown. | 1144 S Mayo Trail, Pikeville, KY 41501, USA | 2023-03-02
2019 | 2019-03-29 | Pikeville |  |  | 37830024B40237 |  | 3403002-PIKEVILLE / MAINST | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | One Service drop low and another laying on metal roof. Take slack out of both. | 196 Riverview Dr, Pikeville, KY 41501, USA | 2023-03-02
2019 | 2019-03-29 | Pikeville | 86142446 |  | 37830024B40517 |  | 3403002-PIKEVILLE / MAINST | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs insulator installed. | 119 Mt Martha Dr, Pikeville, KY 41501, USA
2019 | 2019-03-29 | Pikeville |  |  | 37830024B40677 |  | 3403002-PIKEVILLE / MAINST | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop laying on roof. | Garred St, Pikeville, KY 41501, USA
2019 | 2019-03-29 | Pikeville | 86332863 | DKY0122642 | 37830024B41039 | TRUE | 3403002-PIKEVILLE / MAINST | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown. POLE HAS SOME EARLY ROT. OK FOR NOW BUT MIGHT CONSIDER CHANGING. | Hambley Blvd & Mountain Chase Dr, Pikeville, KY 41501, USA
2019 | 2019-03-29 | Pikeville |  |  | 37830024B41104 |  | 3403002-PIKEVILLE / MAINST | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole. Repaired same day. | 549 Scott Ave, Pikeville, KY 41501, USA | 2019-03-29
2019 | 2019-03-29 | Pikeville |  |  | 37830024B41191 |  | 3403002-PIKEVILLE / MAINST | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | Dish network | 139 Grace Road, Mt. Martha Trail, Pikeville, KY.
2019 | 2019-03-29 | Pikeville |  |  | 37830024B41519 |  | 3403002-PIKEVILLE / MAINST | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer bank. Repaired same day. | 551 Hambley Blvd, Pikeville, KY 41501, USA | 2019-03-29
2019 | 2019-03-29 | Pikeville | 86142446 |  | 37830024B41520 | TRUE | 3403002-PIKEVILLE / MAINST | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown. @ behind the Velocity Market Plaza. | 533 Hambley Blvd, Pikeville, KY 41501, USA
2019 | 2019-03-29 | Pikeville |  |  | 37830024D20394 |  | 3403002-PIKEVILLE / MAINST | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. Repaired same day. | Scott Ave, Pikeville, KY 41501, USA | 2019-03-29
2019 | 2019-04-01 | Pikeville |  |  | 37830024B40316 |  | 3403002-PIKEVILLE / MAINST | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack. Close to transformer. Pole ground stolen. Repaired same day | Poplar St, Pikeville, KY 41501, USA | 2019-04-01
2019 | 2019-04-01 | Pikeville |  |  | 37830024D20288 |  | 3403002-PIKEVILLE / MAINST | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack. Needs insulator. Close to transformer. | N Auxier Ave, Pikeville, KY 41501, USA | 2023-10-11
2019 | 2019-04-01 | Pikeville |  |  | 37830048A30442 |  | 3403002-PIKEVILLE / MAINST | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Anchor pulled out. Guy wire hanging down pole. Angle pole. | Julius Ave, Pikeville, KY 41501, USA | 2023-10-11
2019 | 2019-04-04 | Pikeville |  |  | 37830024B20740 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarm burnt in two. | N Bypass Rd, Pikeville, KY 41501, USA @ intersection of Loraine Street. | 2020-06-17
2019 | 2019-04-04 | Pikeville |  |  | 37830024B20936 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. @ State Dept. Office on the bypass. | N Mayo Trail, Pikeville, KY 41501, USA | 2019-04-04
2019 | 2019-04-04 | Pikeville |  |  | 37830024B30542 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole. Repaired same day | Redale Road, North Bypass, Pikeville, KY. | 2019-04-04
2019 | 2019-04-04 | Pikeville |  |  | 37830024B30747 |  | 3403001-PIKEVILLE / CITY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on switch pole. Repaired same day. | Redale Rd, Pikeville, KY 41501, USA
2019 | 2019-04-04 | Pikeville |  |  | 37830024B31048 |  | 3403001-PIKEVILLE / CITY | Line Work | OH |  |  | other: customer owned attachment | KPC |  | We apparently have installed a temporary overhead service for a faulty underground service. Don’t know how long it’s been this way. | Dobbins Drive, N Bypass Road, Pikeville, KY.
2019 | 2019-04-04 | Pikeville |  |  | 37830024B31136 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | Redale Rd, Pikeville, KY 41501, USA | 2019-04-04
2019 | 2019-04-04 | Pikeville |  |  | 37830024B31182 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | Owens Dr, Pikeville, KY 41501, USA | 2019-04-04
2019 | 2019-04-04 | Pikeville |  |  | 37830024B40745 |  | 3403001-PIKEVILLE / CITY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen. Repaired same day. | Redale Rd, Pikeville, KY 41501, USA | 2019-04-04
2019 | 2019-04-04 | Pikeville |  |  | 37830024D20760 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground cut on GOAB pole. Repaired same day. | N Bypass Rd, Pikeville, KY 41501, USA | 2019-04-04
2019 | 2019-04-04 | Pikeville | 86142476 |  | 37830024D20868 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole. | Ferguson Ln, Pikeville, KY 41501, USA
2019 | 2019-04-04 | Pikeville |  |  | 37830024D40909 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground cut on transformer bank pole. Repaired same day. | TTown Mountain Rd, Kentucky 41501, USA @ behind shopping center. | 2019-04-04
2019 | 2019-04-05 | Pikeville |  |  | 37820001000239 |  | 3403001-PIKEVILLE / CITY | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Customer has built a deck around secondary pole. | Town Mountain Rd & Blair St, Pikeville, KY 41501, USA | 2023-03-02
2019 | 2019-04-05 | Pikeville |  |  | 37830024C07796 |  | 3403001-PIKEVILLE / CITY | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive secondary pole.@ gray mobile home on right. Pole on left. | Powderhouse Hollow Rd, Pikeville, KY 41501, USA | 2023-10-11
2019 | 2019-04-05 | Pikeville |  |  | 37830024D10773 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | Northgate Dr, Pikeville, KY 41501, USA | 2019-04-05
2019 | 2019-04-05 | Pikeville | 86142476 |  | 37830024D30117 |  | 3403001-PIKEVILLE / CITY | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign |  | Crossarms are deteoriated. @ Professional bldg parking lot. | Mays Branch Rd, Pikeville, KY 41501, USA
2019 | 2019-04-05 | Pikeville |  |  | 37830024D30147 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2). Completed same day. One guy needs insulator. | Mays Branch Rd, Pikeville, KY 41501, USA
2019 | 2019-04-05 | Pikeville |  |  | 37830024D30962 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | Bill King Hollow, Pikeville, KY 41501, USA | 2019-04-05
2019 | 2019-04-05 | Pikeville |  |  | 37830024D31368 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | Northgate Dr, Pikeville, KY 41501, USA | 2019-04-05
2019 | 2019-04-08 | Pikeville |  |  | 37830024D20443 | TRUE | 3403001-PIKEVILLE / CITY | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | DirecTv | Wolford St, Pikeville, KY 41501, USA
2019 | 2019-04-08 | Pikeville |  |  | 37830024D20460 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | 3rd St, Pikeville, KY 41501, USA | 2019-04-08
2019 | 2019-04-08 | Pikeville |  |  | 37830024D21545 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | N Auxier Ave, Pikeville, KY 41501, USA | 2019-04-08
2019 | 2019-04-08 | Pikeville |  |  | 37830048C11383 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needs guy marker. Completed same day. | Chloe Rd & Bailey Blvd, Pikeville, KY 41501, USA | 2019-04-08
2019 | 2019-04-09 | Pikeville |  |  | 37820001000183 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | Starnes Drive, Walters Road, Pikeville, KY. | 2019-04-09
2019 | 2019-04-09 | Pikeville | 76907818 | DKY0110604 | 37820001000277 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole in slide area. Might be a job already written up on this. | Spring Ridge Drive, Walters Road, Pikeville, KY. | 2021-11-05
2019 | 2019-04-09 | Pikeville |  |  | 37820025A00058 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | Walters Road, Chloe Creek, Pikeville, KY. | 2019-04-09
2019 | 2019-04-09 | Pikeville |  |  | 37820025A00199 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC |  | Transformer appears to have been on fire or maybe hit by lightning. Doesn’t appear to be leaking though. | 751 Chloe Rd, Pikeville, KY 41501, USA | 2023-03-02
2019 | 2019-04-09 | Pikeville | 77011923 | DKY0110414 | 37820025A00283 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten. @ across the road from Starnes Drive. | Chloe Rd & Walters Rd, Pikeville, KY 41501, USA | 2020-12-10
2019 | 2019-04-09 | Pikeville |  |  | 37830048C30030 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | Melvina Drive, Chloe Creek, Pikeville, KY. | 2019-04-09
2019 | 2019-04-10 | Pikeville | 84899583 | DKY0120740 | 37820025C00237 |  | 3403001-PIKEVILLE / CITY | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive line @ head of Fife Fork. Pole is not on field view. | 351 Fife Fork, Chloe Creek, Pikeville, KY. | 2023-08-14
2019 | 2019-04-10 | Pikeville | 74385436 |  | 37820049000326 |  | 3403001-PIKEVILLE / CITY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Remove inactive service hanging down pole. De-energized. | 3075 Chloe Creek Road, Pikeville, KY. | 2019-08-27
2019 | 2019-04-11 | Pikeville | 84899662 |  | 37820025B00425 |  | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Duplex conductor sagged very low around hillside | 897 Harold’s Branch, Pikeville, KY.
2019 | 2019-04-11 | Pikeville |  |  | 37830048A21090 |  | 3410501-S.PIKEVIL / PIKEVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | S Mayo Trail, Pikeville, KY 41501, USA | 2019-04-11
2019 | 2019-04-11 | Pikeville |  |  | 37830048A21298 |  | 3410501-S.PIKEVIL / PIKEVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. @ nursing home | S Mayo Trail, Pikeville, KY 41501, USA | 2019-04-11
2019 | 2019-04-11 | Pikeville |  |  | 37830048A21606 |  | 3410501-S.PIKEVIL / PIKEVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | Narrows Rd, Pikeville, KY 41501, USA | 2019-04-11
2019 | 2019-04-11 | Pikeville |  |  | 37830048A21712 |  | 3410501-S.PIKEVIL / PIKEVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day @ Bingo place | Hambley Blvd, Pikeville, KY 41501, USA | 2019-04-11
2019 | 2019-04-11 | Pikeville |  |  | 37830048A40947 |  | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer bank. Repaired same day. | Wood Cir, Pikeville, KY 41501, USA | 2019-04-11
2019 | 2019-04-11 | Pikeville | 83966736 | DKY0120419 | 37830048D11380 |  | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy and anchor has been washed out by slide. @ behind apartment bldg. on right. | Harolds Branch, Pikeville, KY 41501, USA | 2023-05-05
2019 | 2019-04-15 | Pikeville |  |  | 37830048A30698 |  | 3410501-S.PIKEVIL / PIKEVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | S College St, Pikeville, KY 41501, USA | 2019-04-15
2019 | 2019-04-15 | Pikeville |  |  | 37830048A31603 |  | 3410501-S.PIKEVIL / PIKEVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | Hambley Blvd, Pikeville, KY 41501, USA | 2019-04-15
2019 | 2019-04-15 | Pikeville | 86142539 |  | 37830048A40026 | TRUE | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown. @ Behind KFC | Baird Ave, Pikeville, KY 41501, USA
2019 | 2019-04-15 | Pikeville |  |  | 37830048A40182 |  | 3410501-S.PIKEVIL / PIKEVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | Park St, Pikeville, KY 41501, USA | 2019-04-15
2019 | 2019-04-15 | Pikeville | 86360700 | DKY0122672 | 37830048A40387 | TRUE | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire is broken and hanging down pole. Needs re-attached. Next to guardrail. | 127 Jefferson St, Pikeville, KY 41501, USA
2019 | 2019-04-15 | Pikeville |  |  | 37830048A40685 |  | 3410501-S.PIKEVIL / PIKEVILLE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole. Repaired same day. | Wood Cir, Pikeville, KY 41501, USA | 2019-04-15
2019 | 2019-04-15 | Pikeville | 77208965 | DKY0110704 | 37830048A40864 |  | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Secondary pole is rotten. Not shown on field view. It’s shown on field view as 37830048A40864 | 137 Jefferson St, Pikeville, KY 41501, USA | 2020-12-10
2019 | 2019-04-15 | Pikeville | 86142539 |  | 37830048A41460 |  | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarm burnt in two. @ Health Dept. | West River Drive, Pikeville, KY 41501, USA
2019 | 2019-04-15 | Pikeville |  |  | 37830048C00981 |  | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | DirecTv. This secondary pole wasn’t shown on field view. It’s tapped off pole 37830048C11727. @ behind Hampton Inn. | 155 College St, Pikeville, KY 41501, USA
2019 | 2019-04-15 | Pikeville | 86142446 |  | 37830048C10298 |  | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown. @ In front of the Day Care. Corner of Azalea Alley and Bank Street. | Bank St, Pikeville, KY 41501, USA
2019 | 2019-04-15 | Pikeville |  |  | 37830048C11164 | TRUE | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown. @ in front of model city day care. | Bank St, Pikeville, KY 41501, USA | 2023-10-11
2019 | 2019-04-16 | Pikeville |  |  | 38821065D10094 |  | 3200204-BARRENSHE / POUNDING | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | River Rd, Freeburn, KY 41528, USA | 2019-04-16
2019 | 2019-04-16 | Pikeville | 74502947 | DKY0106692 | 38821065D20002 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service conductors hanging down pole. Needs to be removed. Pole is also covered in vines. Guy wire needs marker (2). Installed markers. | 1st St, Freeburn, KY 41528, USA | 2022-06-16
2019 | 2019-04-16 | Pikeville | 74329104 | DKY0106839 | 38821065D20155 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten. Also might want to consider changing pole 38821065D20154 and pole 38821065D20156 which is next poles in line. They don’t seem rotten but it’s chewed up pretty bad. | 85 School St, Freeburn, KY 41528, USA | 2020-02-27
2019 | 2019-04-16 | Pikeville | 74329147 | DKY0107029 | 38821065D20156 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | cutout: damaged | lightning arresters/insulators: damaged |  | Foreign |  | Lightning arrestor blown. Cutout and bracket is turned upside down. | 85 School St, Freeburn, KY 41528, USA | 2020-10-09
2019 | 2019-04-16 | Pikeville |  |  | 38821065D20157 |  | 3200204-BARRENSHE / POUNDING | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | School St, Freeburn, KY 41528, USA | 2019-04-16
2019 | 2019-04-16 | Pikeville | 74328932 | DKY0106753 | 38821065D20222 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole has burned. Been re-enforced temporary with crossarms . 3 phase river crossing in station zone. Install: 1990 | State Hwy 194 East, Freeburn, KY. | 2020-01-08
2019 | 2019-04-16 | Pikeville | 74328841 | DKY0106826 | 38821065D20302 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | KY-194, Freeburn, KY, USA | 2020-01-08
2019 | 2019-04-16 | Pikeville | 74502947 | DKY0106692 | 38821065D20999 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Secondary pole leaning. Needs straightened. @ Thomas Devenny lodge. Install: 1986 | KY-194, Freeburn, KY, USA | 2022-06-16
2019 | 2019-04-16 | Pikeville |  |  | 38821065D29026 |  | 3200204-BARRENSHE / POUNDING | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs markers. (2) Completed same day. | Pounding Mill Rd, Freeburn, KY, USA | 2019-04-16
2019 | 2019-04-16 | Pikeville | 74328841 | DKY0106826 | 38821065D30117 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Anchor washed out/ dug out. Needs replaced. | River Rd, Freeburn, KY 41528, USA | 2020-01-08
2019 | 2019-04-17 | Pikeville |  |  | 38821016D00257 |  | 3200204-BARRENSHE / POUNDING | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 10563 State Hwy 1056, McCarr, KY 41544, USA | 2019-04-17
2019 | 2019-04-17 | Pikeville |  |  | 38821017B20038 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | cutout: damaged |  |  | KPC |  | Cutout bracket loose. Turned upside down. | 294 Lovers Ln, McCarr, KY 41544, USA | 2019-09-11
2019 | 2019-04-17 | Pikeville | 74775118 | DKY0107031 | 38821041A00040 | TRUE | 3200204-BARRENSHE / POUNDING | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | already written to EDN100577 FOREIGN | POLE IS ROTTEN.......Also remove inactive single phase tap and transformer pole 38821041A00207 | 9639 State Hwy 1056, McCarr, KY 41544, USA | 2020-01-23
2019 | 2019-04-17 | Pikeville | 74509151 | DKY0106736 | 38821041B00023 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Pole top insulator broken on center phase. | 123 Peter Fork Rd, McCarr, KY 41544, USA | 2020-01-23
2019 | 2019-04-17 | Pikeville | 74328843 | DKY0106633 | 38821041B00219 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH |  | lightning arresters/insulators: damaged , guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. Also lightning arrestor blown. Needs replaced. | 422 Peter Fork Road, McCarr, KY. | 2022-06-16
2019 | 2019-04-17 | Pikeville |  |  | 38821065A00062 |  | 3200204-BARRENSHE / POUNDING | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 1228 Peter Fork Rd, McCarr, KY 41544, USA | 2019-04-17
2019 | 2019-04-17 | Pikeville | 74328843 | DKY0106633 | 38821065A22039 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | 4/2 secondary sagged low. Approximately 10 ft. Needs slack taken out. Pole is tagged as 39 but it’s 2039 on field view. | 1228 Peter Fork Rd, McCarr, KY 41544, USA | 2022-06-16
2019 | 2019-04-17 | Pikeville | 74328843 | DKY0106633 | 38821065B00085 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | Conductors sagged low. Neutral is below communication cables. Needs slack taken out. @ buckarm pole. Foot of the hill. | Pounding Mill Rd, Freeburn, KY, USA | 2022-06-16
2019 | 2019-04-17 | Pikeville |  |  | 38821065B00246 |  | 3200204-BARRENSHE / POUNDING | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Pounding Mill Rd, Freeburn, KY, USA | 2019-04-17
2019 | 2019-04-17 | Pikeville | 74328841 | DKY0106826 | 38821065D10305 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Cutout broken. | May horn Hill, River Rd, Freeburn, KY 41528, USA | 2020-01-08
2019 | 2019-04-18 | Pikeville |  |  | 38821016D00248 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | DirecTv ( 2 )..@ cream colored house with maroon shutters. | Auburn Street, State Hwy1056 , McCarr, KY.
2019 | 2019-04-18 | Pikeville |  |  | 38821040B00082 |  | 3200204-BARRENSHE / POUNDING | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. ( 2 ) Completed same day | Hatfield Branch, Kentucky 41544, USA | 2019-04-18
2019 | 2019-04-18 | Pikeville | 74329148 | DKY0106801 | 38821040C00076 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | already written to EDN100577 KPC pole | POLE HAS SOME ROT AT GROUND LEVEL. SOUNDS HOLLOW TOO. Needed guy marker. Installed same day | 183 Farley Bottom, McCarr, KY. | 2019-12-30
2019 | 2019-04-18 | Pikeville | 77011624 | DKY0110805 | 38821061D00150 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole leaning , partially washed out around. Secondary sagged below communication cables. | 606 Rfk Auburn Hollow, McCarr, KY. | 2020-12-29
2019 | 2019-04-18 | Pikeville |  |  | 38821064A00068 |  | 3200204-BARRENSHE / POUNDING | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | State Hwy 319 Hardy, KY. | 2019-04-18
2019 | 2019-04-18 | Pikeville | 74509151 | DKY0106736 | 38821064C00006 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown. @ near McCarr P.O. behind a red brick house. | 6925 State Hwy 1056 McCarr, KY. | 2020-01-23
2019 | 2019-04-18 | Pikeville |  |  | 38821064C00080 |  | 3200204-BARRENSHE / POUNDING | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Warm Hollow, McCarr, KY. | 2019-04-18
2019 | 2019-04-18 | Pikeville |  |  | 38821064C00225 |  | 3200204-BARRENSHE / POUNDING | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. | 7780 State Highway 1056 McCarr, KY. | 2019-04-18
2019 | 2019-04-23 | Pikeville | 74328854 | DKY0106694 | 38821064C00202 |  | 3200203-BARRENSHE / SLATE BRANCH | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer bank. | State Hwy 1056, Ransom, KY. | 2022-03-28
2019 | 2019-04-23 | Pikeville |  |  | 38821064C00203 |  | 3200203-BARRENSHE / SLATE BRANCH | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker ( 2 ) . Completed same day | State highway 1056, Ransom, KY. | 2019-04-23
2019 | 2019-04-23 | Pikeville | WR# 73174998 |  | 38821064C00204 |  | 3200203-BARRENSHE / SLATE BRANCH | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop sagged low. Needs slack taken out. @ Columbia gas plant. CONTACTED SERVICER AND CORRECTIVE ACTION WAS TAKEN TO REMEDY THE LOW CLEARANCE. | State highway 1056 Ransom, KY. | 2019-04-23
2019 | 2019-04-24 | Pikeville |  |  | 38821065D20141 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Boardwalk St, Freeburn, KY 41528, USA | 2019-04-24
2019 | 2019-04-24 | Pikeville |  |  | 38821065D20143 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Boardwalk St, Freeburn, KY 41528, USA | 2019-04-24
2019 | 2019-04-24 | Pikeville |  |  | 38821065D20168 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | West Oak Street, Freeburn, KY. | 2019-04-24
2019 | 2019-04-24 | Pikeville | 74328831 | DKY0106691 | 38821065D20198 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH |  | lightning arresters/insulators: damaged , guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Lightning arrestor blown. Also needs guy marker. Installed guy marker same day. | W Oak St, Freeburn, KY 41528, USA | 2020-04-21
2019 | 2019-04-24 | Pikeville | 74328831 | DKY0106691 | 38821065D40240 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole. | 114 Boardwalk St, Freeburn, KY 41528, USA | 2020-04-21
2019 | 2019-04-24 | Pikeville |  |  | 38821089A00231 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | State highway 194 east, Freeburn, KY. | 2019-04-24
2019 | 2019-04-24 | Pikeville |  |  | 38821089C00254 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs markers ( 2 ). Completed same day | 128 Boardwalk St, Freeburn, KY 41528, USA | 2019-04-24
2019 | 2019-04-24 | Pikeville |  |  | 38821089C00490 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Boardwalk St, Freeburn, KY 41528, USA | 2019-04-24
2019 | 2019-04-24 | Pikeville |  |  | 38821089C12131 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Installed marker same day. DirecTv | 44009 KY-194, Freeburn, KY 41528, USA
2019 | 2019-04-25 | Pikeville | 82530892 | DKY0117181 | 38821064D00225 | TRUE | 3200203-BARRENSHE / SLATE BRANCH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole burnt nearly in two. Also insulators and arrestor have been hit by lightning. This is a two pole hi- line angle structure with 4/0 conductors and very long spans on each side back in the mountains on top of Pounding Mill mountain @ Freeburn, KY. | Pounding Mill Mountain, Freeburn, KY.
2019 | 2019-04-25 | Pikeville |  |  | 38821113A00005 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning. Needs side guy installed. | 50 Combs Drive, State Hwy 194 East, Freeburn, KY. | 2019-08-28
2019 | 2019-04-25 | Pikeville | 73217482 | DKY0104876 | 38821113A00007 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop sagged low. Probably can’t raise it enough without installed a secondary pole for clearance. Also should talk to customer about service pole ..may need to be replaced | 56 Boardtree St, Phelps, KY 41553, USA | 2019-07-26
2019 | 2019-04-25 | Pikeville | 74329158 | DKY0108136 | 38821113A00015 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole washed out around in creek. | 40156 KY-194, Phelps, KY 41553, USA | 2022-04-27
2019 | 2019-04-25 | Pikeville | 74328808 | DKY0106993 | 38821113A00016 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guys slack on buckarm pole. One is 1/2 guy, the other 3/8. Need to tighten both. | 40052 KY-194, Freeburn, KY 41528, USA | 2020-02-19
2019 | 2019-04-25 | Pikeville | 73257068 |  | 38821113A00095 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack. Needs tightened. Needs marker. Installed same day. | 329 Billy Dotson Branch, Freeburn, KY. | 2019-05-01
2019 | 2019-04-25 | Pikeville | 73217728 | DKY0104878 | 38821113A00100 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop sagged low. Tied up in a tree. Can’t take enough slack out to get the required clearance. Probably need taller secondary pole or set an additional pole | 40646 KY-194, Phelps, KY 41553, USA | 2019-10-29
2019 | 2019-04-25 | Pikeville |  |  | 38821113A00266 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 167 Billy Dotson Branch, Freeburn, KY. | 2019-04-25
2019 | 2019-04-25 | Pikeville |  |  | 38821113B00022 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 18 Dart Bottom, Freeburn, KY. | 2019-04-25
2019 | 2019-04-25 | Pikeville |  |  | 38821113B00141 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 40024 State Hwy 194 East, Phelps, KY. | 2019-04-25
2019 | 2019-04-25 | Pikeville |  |  | 38821113B00152 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 118 Dart Bottom, Freeburn, KY. | 2019-04-25
2019 | 2019-04-25 | Pikeville | 74328808 | DKY0106993 | 38821113B00184 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC |  | Transformer hangers are bent pretty bad on bank pole. Also service attachment has pulled loose from building. | 39369 KY-194, Freeburn, KY 41528, USA | 2020-02-19
2019 | 2019-04-25 | Pikeville |  |  | 38821113B00195 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 56 Justice Bottom, Freeburn, KY. | 2019-04-25
2019 | 2019-04-25 | Pikeville | 73255597 |  | 38821113B00233 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown and conduits are separated at bottom of the pole. | 39905 KY-194, Phelps, KY 41553, USA | 2019-05-01
2019 | 2019-04-29 | Pikeville |  |  | 38821089A00251 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Park Road, Hwy 194, Phelps, KY. | 2019-04-29
2019 | 2019-04-29 | Pikeville |  |  | 38821089A00507 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole has been burned before and reinforced with crossarm. Road crossing 556 conductors. Also 3 phase conductor is close to Phelps Senior Citizen Center. | Park Road, State Hwy 194 East, Phelps, KY. | 2019-11-20
2019 | 2019-04-29 | Pikeville |  |  | 38821089B00015 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign |  | End of the crossarm is split. Phase closest to the road. | 42254 KY-194, Phelps, KY 41553, USA | 2019-08-28
2019 | 2019-04-29 | Pikeville | 74329090 | DKY0108608 | 38821089B00032 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is Rotten. Buckarm pole. | Joe McCoy Road, Phelps, KY. | 2020-03-16
2019 | 2019-04-29 | Pikeville | 74328808 | DKY0106993 | 38821089B00038 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND | lightning arresters/insulators: damaged | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Lightning arrestor blown. Pole ground stolen. Lash conductor hanging down pole de-energized. @ behind a red brick garage bldg. | 53 McCoy Bottom Road, Phelps, KY. | 2020-02-19
2019 | 2019-04-29 | Pikeville | 74766356 | DKY0107030 | 38821089B00083 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | crossarm/braces: broken/split | crossarm/braces: deteriorated, not rotten |  | KPC |  | Crossarms are deteoriated and brace is broken. | 78 Joe McCoy Rd, Phelps, KY 41553, USA | 2020-03-02
2019 | 2019-04-29 | Pikeville |  |  | 38821089B00375 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Customer has built a garage with the eave surrounding our pole. There’s also a low service drop barely clearing the roof of a house. And a satellite dish mounted on pole.@ behind a white dw. Dish Network. | 41516 State Hwy 194, Phelps, KY.
2019 | 2019-04-29 | Pikeville |  |  | 38821089B00392 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign |  | Crossarm is rotten. @ behind a white brick house | 61 McCoy Bottom Road, Phelps, KY. | 2019-08-28
2019 | 2019-04-29 | Pikeville |  |  | 38821089B00425 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Griffey Bottom, Phelps, KY. | 2019-04-29
2019 | 2019-04-29 | Pikeville |  |  | 38821089B00436 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign |  | Inactive service drop hanging down pole. Guy wire needs marker. Installed guy marker and removed drop same day. | 40 Joe McCoy Rd, Phelps, KY 41553, USA | 2019-04-29
2019 | 2019-04-29 | Pikeville | 74766356 | DKY0107030 | 38821089B00439 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire rusted off at ground. Do not see anchor. @ Church of God. | Gosling Bottom, Church House Lane, Phelps, KY. | 2020-03-02
2019 | 2019-04-29 | Pikeville | 74766356 | DKY0107030 | 38821089B00493 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | D-D light hanging down pole as well as duplex. Pole is inactive at this time. | Griffey Bottom, Phelps, KY. | 2020-03-02
2019 | 2019-04-29 | Pikeville |  |  | 38821089B12113 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day.@ behind Church of God. | Goosling Bottom, Phelps, KY, USA | 2019-04-29
2019 | 2019-04-30 | Pikeville | 74177228 | DKY0106546 | 37830040000118 |  | 3413402-GARRETT / LACKEY | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Customer has built around our secondary pole. Road crossing. | 14684 KY-550, Lackey, KY 41643, USA | 2020-03-11
2019 | 2019-04-30 | Pikeville | 77399570 | DKY0110764 | 37830040000120 | TRUE | 3413402-GARRETT / LACKEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten. | 14657 KY-550, Lackey, KY 41643, USA | 2022-05-10
2019 | 2019-04-30 | Pikeville | 83966807 | DKY0120425 | 37830041A10282 |  | 3413402-GARRETT / LACKEY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator insulators are deteoriated and beginning to melt down. | Slone Street, Garrett, KY.
2019 | 2019-04-30 | Pikeville | 74176706 | DKY0109320 | 37830041B00020 |  | 3413402-GARRETT / LACKEY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. @ near Potter Clinic. Next to Hwy. | Millard Allen Drive, Garrett, KY. | 2021-01-11
2019 | 2019-04-30 | Pikeville | 74176706 | DKY0109320 | 37830041B00021 |  | 3413402-GARRETT / LACKEY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator insulator melted down. | Millard Allen Drive, Lackey, KY. | 2021-01-11
2019 | 2019-04-30 | Pikeville |  |  | 37830041B00301 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | State Hwy 550 East, Garrett, KY. | 2019-04-30
2019 | 2019-04-30 | Pikeville | 73403817 |  | 37830041B00303 |  | 3413402-GARRETT / LACKEY | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. Non equipment @ Knott co. Line. | KY Hwy 550 East, Lackey, KY. | 2019-05-16
2019 | 2019-04-30 | Pikeville | 73389299 |  | 37830041B00305 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Service hanging down pole. De-energized. Need removed. | 14909 State Hwy 550 East, Lackey, KY. | 2019-05-15
2019 | 2019-04-30 | Pikeville | 73389299 |  | 37830041B00334 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | Duplex conductors tied up to primary neutral conductor. Take slack out of duplex. @ between family dollar and middle mart store. | KY-550, Garrett, KY. | 2019-05-15
2019 | 2019-04-30 | Pikeville | 74176706 | DKY0109320 | 37830064000109 |  | 3413402-GARRETT / LACKEY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown. @ behind Clicks Welding | 14389 KY-550, Mousie, KY 41839, USA | 2021-01-11
2019 | 2019-04-30 | Pikeville |  |  | 37830088000042 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Cool Bush Ln, Mousie, KY 41839, USA | 2019-04-30
2019 | 2019-04-30 | Pikeville | 74176606 | DKY0106969 | 37830088000099 |  | 3413402-GARRETT / LACKEY | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire hanging broken and hanging down pole. Need to replace anchor and reattach guy. @ about 1/2 mile up Bear Fork. | Bear Fork Rd, Mousie, KY 41839, USA | 2023-01-11
2019 | 2019-04-30 | Pikeville |  |  | 37830088000135 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 10372 KY-550, Mousie, KY 41839, USA | 2019-04-30
2019 | 2019-05-01 | Pikeville | 74176641 | DKY0106532 | 37830064000006 | TRUE | 3413402-GARRETT / LACKEY | Line Work | OH |  | lightning arresters/insulators: damaged , guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Center phase Epoxilator insulator breaking down. Also guy wire needed marker. Installed marker same day | KY. 550, Jones Fork, Lackey, KY. | 2022-09-12
2019 | 2019-05-01 | Pikeville |  |  | 37830064000029 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 13052 KY-550, Mousie, KY 41839, USA | 2019-05-01
2019 | 2019-05-01 | Pikeville |  |  | 37830064000032 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 12768 KY-550, Mousie, KY 41839, USA | 2019-05-01
2019 | 2019-05-01 | Pikeville | 74176641 | DKY0106532 | 37830064000070 | TRUE | 3413402-GARRETT / LACKEY | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Anchor washed out. Needs replaced and guy reattached.@ about half mile up. Angle pole on left of road. Might be able to attach to phone company anchor. | Dry Fork, Mousie, KY. | 2022-09-12
2019 | 2019-05-01 | Pikeville |  |  | 37830064000112 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire slack and needs marker. Completed same day. | KY-550, Mousie, KY, USA | 2019-05-01
2019 | 2019-05-01 | Pikeville | 74374485 | DKY0106535 | 37830064000114 |  | 3413402-GARRETT / LACKEY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop sagging low. Needs slack taken out. Might need a taller pole to get enough clearance. | 13139 KY-550, Mousie, KY 41839, USA | 2020-03-12
2019 | 2019-05-01 | Pikeville |  |  | 37830064000141 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 224 Triplett Branch, Mousie, KY 41839, USA | 2019-05-01
2019 | 2019-05-01 | Pikeville | 74176641 | DKY0106532 | 37830088000120 | TRUE | 3413402-GARRETT / LACKEY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Big Spring Branch, Mousie, KY. | 2022-09-12
2019 | 2019-05-08 | Pikeville |  |  | 37830087D00008 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | KY-1087 & Musical Loop, Mousie, KY 41839, USA | 2019-05-08
2019 | 2019-05-08 | Pikeville | 74176606 | DKY0106969 | 37830087D00011 |  | 3413402-GARRETT / LACKEY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator insulators are melting and tracking.@ recloser pole. | 5560 Ball Branch, Mousie, KY. | 2023-01-11
2019 | 2019-05-08 | Pikeville | 74176606 | DKY0106969 | 37830087D00029 |  | 3413402-GARRETT / LACKEY | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole | 5326 Hwy 1087 east, Mousie, KY. | 2023-01-11
2019 | 2019-05-08 | Pikeville | 74176606 | DKY0106969 | 37830087D00032 |  | 3413402-GARRETT / LACKEY | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen all the way to the transformer. | 5119 Hwy 1087 Easr, Mousie, KY. | 2023-01-11
2019 | 2019-05-08 | Pikeville | 74176588 | DKY0106462 | 37830087D20194 |  | 3413402-GARRETT / LACKEY | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire hanging down pole. Very short span, could probably remove it completely. | 412 Bruce Branch, hwy 1087 east, Mousie, KY. | 2019-11-26
2019 | 2019-05-08 | Pikeville |  |  | 37830111000101 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 3054 KY-1087, Leburn, KY 41831, USA | 2019-05-08
2019 | 2019-05-08 | Pikeville | 74176588 | DKY0106462 | 37830111000102 |  | 3413402-GARRETT / LACKEY | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove old crossarm from pole. | 416 Ball Branch Scool Road, Mousie, KY. | 2019-11-26
2019 | 2019-05-08 | Pikeville |  |  | 37830111000149 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 100 Branden Drive, Ball Branch, Mousie, KY. | 2019-05-08
2019 | 2019-05-08 | Pikeville | 74176588 | DKY0106462 | 37830111000157 |  | 3413402-GARRETT / LACKEY | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning. Needs a side guy to straighten. Also have low clearance on conductors to pole 199. Someone has put a rope around it at the telephone attachment. If we could straighten this pole it will help the clearance on pole 199 but not sure if it will be enough. | 3346 Ball Branch, Hwy 1087 East, Mousie, KY. | 2019-11-26
2019 | 2019-05-08 | Pikeville |  |  | 37830111000191 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Conley cemetery road, hwy 187 east, Mousie. KY. | 2019-05-08
2019 | 2019-05-08 | Pikeville |  |  | 37830111000199 |  | 3413402-GARRETT / LACKEY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Primary conductors are sagging low as well as service drop. It’s a short slack span of primary and I think we can remove enough slack for proper clearance. Service drop can have slack taken out at the house attachment point. Might want to consider a 5 foot taller pole also. | 3346 Ball Branch, hwy 187east, Mousie, KY.
2019 | 2019-05-08 | Pikeville |  |  | 37830112000101 |  | 3413402-GARRETT / LACKEY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Remove inactive service hanging down pole. De-energized @ transformer. Completed same day | Bear Fork Rd, Mousie, KY 41839, USA | 2019-05-08
2019 | 2019-05-09 | Pikeville | 74176606 | DKY0106969 | 37830087D00095 |  | 3413402-GARRETT / LACKEY | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole. | 9878 KY-550, Mousie, KY 41839, USA | 2023-01-11
2019 | 2019-05-09 | Pikeville |  |  | 37830135000002 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 8139 KY-550, Mousie, KY. | 2019-05-09
2019 | 2019-05-10 | Pikeville |  |  | 37830135000001 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 7364 Hwy 550 East, Mousie, KY. | 2019-05-10
2019 | 2019-05-10 | Pikeville |  |  | 37830135000050 |  | 3413402-GARRETT / LACKEY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop low clearance. Probably need to install secondary pole for clearance. | 7266 Hwy 550 East, Mousie, KY.
2019 | 2019-05-10 | Pikeville |  |  | 37830135000075 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 7441 Hwy 550 East, Mousie, KY. | 2019-05-10
2019 | 2019-05-10 | Pikeville |  |  | 37830135000127 |  | 3413402-GARRETT / LACKEY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop is low. Needs slack taken out of drop but not sure if we could get enough. Might need to install secondary pole. | 38 Store Daddy Way, Mousie, KY. | 2019-08-02
2019 | 2019-05-10 | Pikeville |  |  | 37830135C30171 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 112 Dismal Branch, Mousie, KY. | 2019-05-10
2019 | 2019-05-10 | Pikeville | 74176550 | DKY0106811 | 37830159000514 |  | 3413402-GARRETT / LACKEY | Line Work | OH | crossarm/braces: broken/split | crossarm/braces: deteriorated, not rotten |  | KPC |  | Crossarm is deteoriated/split. About 1/2 mile up pine tree hollow on right on hill. Might be able to use backyard bucket. | Pine Tree Hollow, Mousie, KY. | 2020-03-09
2019 | 2019-05-14 | Pikeville | 74176665 | DKY0109307 | 37830065D00054 |  | 3413401-GARRETT / GARRETT | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign |  | End of crossarm is split. Conductor tie wire is broken. @ RR crossing Mill Branch. NO TRUCK | Mill Creek, Kentucky 41666, USA
2019 | 2019-05-14 | Pikeville | 72062702 | DKY0104317 | 37830065D00156 |  | 3413401-GARRETT / GARRETT | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Primary conductors low. Can take enough slack out at the pole to get proper clearance I think. Might need pole in line. | Mill Creek, Wayland, KY. | 2020-06-17
2019 | 2019-05-14 | Pikeville | 72062702 | DKY0104317 | 37830065D00157 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole. Probably need to install ground rod. Couldn’t find it. | KY. Route 7, Wayland, KY. | 2020-06-17
2019 | 2019-05-14 | Pikeville |  |  | 37830065D00558 | TRUE | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Steele Creek Rd, Wayland, KY 41666, USA | 2019-05-14
2019 | 2019-05-14 | Pikeville |  |  | 37830065D00558 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND | guys/anchors: loose, damaged, need insulator/marker | other: customer owned attachment | KPC |  | Guy wire needs marker. Completed same day. Pole ground broken. Repaired same day. Customer has attached conduit and cable to our pole for service to adjacent camping sites. Talked to customer to have it removed. | Steele Creek Rd, Wayland, KY 41666, USA | 2019-08-28
2019 | 2019-05-14 | Pikeville | 73268301 | DKY0108636 | 37830089000054 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten. | 5023 KY-7, Wayland, KY 41666, USA | 2023-03-16
2019 | 2019-05-14 | Pikeville | 72062735 | DKY0105683 | 37830089000152 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | already written to EDN100577 FOREIGN | Pole outer shell is rotten. Road crossing, 3 phase. | KY Route 7, Wayland, KY. | 2020-06-17
2019 | 2019-05-15 | Pikeville |  |  | 37830065D00220 |  | 3413401-GARRETT / GARRETT | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | Dish Network | River St, Wayland, KY 41666, USA
2019 | 2019-05-15 | Pikeville |  |  | 37830065D00257 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Church Hill Drive, Wayland, KY. | 2019-05-15
2019 | 2019-05-15 | Pikeville |  |  | 37830065D00262 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Church Hill Drive, Wayland, KY. | 2019-05-15
2019 | 2019-05-15 | Pikeville |  |  | 37830065D00280 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | River St, Wayland, KY 41666, USA | 2019-05-15
2019 | 2019-05-15 | Pikeville |  |  | 37830066B00186 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 352 Co Rd 1086, Wayland, KY 41666, USA | 2019-05-15
2019 | 2019-05-15 | Pikeville |  |  | 37830090000045 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Moore Branch, Steele Creek, Wayland, KY. | 2019-05-15
2019 | 2019-05-15 | Pikeville |  |  | 37830090000046 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Moore Branch, Steele Creek, Wayland, KY. | 2019-05-15
2019 | 2019-05-15 | Pikeville |  |  | 37830090000047 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Moore Branch, Steele Creek, Wayland, KY. | 2019-05-15
2019 | 2019-05-16 | Pikeville |  |  | 37830016D00120 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 47 Birch Street, Garrett, KY. | 2019-05-16
2019 | 2019-05-16 | Pikeville |  |  | 37830016D00123 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 50 Esteps Branch, Kentucky 41630, USA | 2019-05-16
2019 | 2019-05-16 | Pikeville |  |  | 37830016D00135 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | W Garrett Road, Garrett, KY. | 2019-05-16
2019 | 2019-05-16 | Pikeville | 81540413 | DKY0116042 | 37830016D00288 |  | 3413401-GARRETT / GARRETT | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer | Elkhorn Branch, W Garrett Road, Garrett, KY. | 2022-05-09
2019 | 2019-05-16 | Pikeville |  |  | 37830041B00079 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 25 Punkin Center, Wayland, KY 41666, USA | 2019-05-16
2019 | 2019-05-16 | Pikeville | 75970354 | DKY0109322 | 37830041B00331 |  | 3413401-GARRETT / GARRETT | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer | Railroad Lane, Lackey, KY. | 2020-04-24
2019 | 2019-05-16 | Pikeville | 74176781 | DKY0106483 | 37830041D00156 |  | 3413401-GARRETT / GARRETT | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. Also has open wire secondary hanging down pole @ last pole in Martin Branch. | Martin Branch, Wayland, KY. | 2019-09-12
2019 | 2019-05-16 | Pikeville |  |  | 37830065A00105 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Extolled Bottom, Wayland, KY. | 2019-05-16
2019 | 2019-05-16 | Pikeville |  |  | 37830065A00413 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | George Road, Wayland, KY. | 2019-05-16
2019 | 2019-05-16 | Pikeville |  |  | 37830065A00462 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | George Road, Wayland, KY. | 2019-05-16
2019 | 2019-05-16 | Pikeville |  |  | 37830065A00539 |  | 3413401-GARRETT / GARRETT | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Remove service drop hanging down pole. Completed same day | Estill Bottom, Kentucky 41666, USA | 2019-05-16
2019 | 2019-05-16 | Pikeville | 74177213 | DKY0110011 | 37830065A00547 |  | 3413401-GARRETT / GARRETT | Line Work | OH |  | pole: leaning, burned more than 50% remaining | Forestry - DESCRIBE IN COMMENTS | KPC | YES | Pole has been burnt by house fire. Can be truck approach but will need some ROW Cut going up driveway. Also the line could be de-energized @ pole 518 @ bottom of the hill. Install: 1993 | Estill Bottom, Kentucky 41666, USA | 2022-04-07
2019 | 2019-05-16 | Pikeville | 74176781 | DKY0106483 | 37830065C00504 |  | 3413401-GARRETT / GARRETT | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. Satellite/ Dish Network (2) | Martin Branch, Wayland, KY. | 2019-09-12
2019 | 2019-05-20 | Pikeville |  |  | 37830016D00035 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | KY route 550, Garrett. KY. | 2019-05-20
2019 | 2019-05-20 | Pikeville |  |  | 37830016D00183 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 100 Front Street, Garrett, KY. | 2019-05-20
2019 | 2019-05-20 | Pikeville | 74176679 | DKY0109891 | 37830040C30043 | TRUE | 3413401-GARRETT / GARRETT | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarms are rotten/ deteoriated. | Magnolia Street, Garrett, KY. | 2021-04-21
2019 | 2019-05-20 | Pikeville | 74176679 | DKY0109891 | 37830040C30047 |  | 3413401-GARRETT / GARRETT | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire hanging down pole. Could be removed. Very short span it’s backing up. Don’t see the anchor to attach to. | Bridge Street, Garrett, KY. | 2021-04-21
2019 | 2019-05-20 | Pikeville |  |  | 37830041A10272 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen. Repaired same day. | Stone Coal Rd, Garrett, KY 41630, USA | 2019-05-20
2019 | 2019-05-20 | Pikeville |  |  | 37830041A10308 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Stone Coal Rd, Kentucky 41630, USA | 2019-05-20
2019 | 2019-05-20 | Pikeville |  |  | 37830041A10324 |  | 3413401-GARRETT / GARRETT | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop laying on roof top. I think we can remove enough slack for clearance. | Pine Street, Stonecoal Creek, Garrett, KY.
2019 | 2019-05-20 | Pikeville |  |  | 37831145000008 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Reed Branch, Garrett, KY. | 2019-05-20
2019 | 2019-05-20 | Pikeville | Trouble order 4305651 |  | 38831145000009 |  | 3413401-GARRETT / GARRETT | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Primary conductors low. I think there’s enough slack in the wire to get clearance if the slack is taken out. Called supervisor to have crew take immediate action. Completed same day | LFK Reed Branch, Garrett, KY. | 2019-05-20
2019 | 2019-05-21 | Pikeville |  |  | 37830016C00239 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | KY. Route 550, Hueysville, KY. | 2019-05-21
2019 | 2019-05-21 | Pikeville |  |  | 37830016C00244 |  | 3413401-GARRETT / GARRETT | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop laying on roof top. Think we can remove enough slack for clearance by raising it on the service pole. | KY. Route 550 , Hueysville, KY. | 2023-04-13
2019 | 2019-05-21 | Pikeville | 79920801 | DKY0113988 | 37830016C00282 |  | 3413401-GARRETT / GARRETT | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | YES | Secondary laying across communications cables. | Race Street, Salt Lick, Hueysville, KY. off Jefferson Rd. | 2021-08-30
2019 | 2019-05-21 | Pikeville |  |  | 37830017000014 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 35 Race St, Hueysville, KY 41640, USA | 2019-05-21
2019 | 2019-05-21 | Pikeville |  |  | 37830017000052 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | North Jefferson Road, Hueysville, KY. | 2019-05-21
2019 | 2019-05-21 | Pikeville |  |  | 37831144000069 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Bosco Tipple Road, Hueysville, KY. | 2019-05-21
2019 | 2019-05-23 | Pikeville |  |  | 38831144000064 |  | 3413401-GARRETT / GARRETT | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Primary and neutral going over garage roof. Neutral looks like it may be 3 to 4 ft. clearance. Primary might be 8 feet. Probably need to change to taller pole or set a pole in line to gain clearance. | KY 550 mo Brush Crk, Midas
2019 | 2019-05-23 | Pikeville |  |  | 38831145000232 |  | 3413401-GARRETT / GARRETT | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive single phase tap beginning at pole 232. LINE IS DE-ENERGIZED. 8 POLES AND SPANS TO REMOVE. WIRE DOWN IN COUPLE DIFFERENT SPOTS. ROW GROWTH PRETTY BAD. BACK IN THE MOUNTAINS BEHIND DUFF ELEMENTARY SCHOOL. | Eastern, KY 41425, out past Barron Allen's oil well drilling
2019 | 2019-05-24 | Pikeville |  |  | 37830212A00176 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 1700 KY. 466, Weeksbury, KY. | 2019-05-24
2019 | 2019-05-24 | Pikeville | 74176728 | DKY0106394 | 37830212A00301 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive secondary pole. | 1534 KY. 466, Weeksbury, KY. | 2022-05-18
2019 | 2019-05-24 | Pikeville |  |  | 37830212A00321 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 1712 KY. 466, Weeksbury, KY. | 2019-05-24
2019 | 2019-05-24 | Pikeville |  |  | 37830235000049 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on recloser pole. Repaired same day | Skull Fork, Weeksbury, KY. | 2019-05-24
2019 | 2019-05-24 | Pikeville | 74176468 | DKY0109220 | 37830235000056 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer | Skull Fork, Weeksbury, KY. | 2021-01-14
2019 | 2019-05-24 | Pikeville |  |  | 37830235000156 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen . | Skull Fork, Weeksbury, KY. | 2019-05-24
2019 | 2019-05-24 | Pikeville |  |  | 37830235000163 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Skull Fork, Weeksbury, KY. | 2019-05-24
2019 | 2019-05-24 | Pikeville |  |  | 37830235000175 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on sectionalizer pole. Repaired same day. | Skull Fork, Weeksbury, KY. | 2019-05-24
2019 | 2019-05-24 | Pikeville |  |  | 37830236A00078 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 3362 KY. 466, Weeksbury, KY. | 2019-05-24
2019 | 2019-05-24 | Pikeville |  |  | 37830236A00080 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 3530 KY. 466, Weeksbury, KY. | 2019-05-24
2019 | 2019-05-24 | Pikeville | 74176728 | DKY0106394 | 37830236A00090 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Anchor washed out/ Guy broken hanging down pole. | 3320 KY. 466, Weeksbury, KY. | 2022-05-18
2019 | 2019-05-28 | Pikeville |  |  | 37830188B00086 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop sagged low over roof top. Need to tighten and remove slack. Tan and brown mobile home on the right at the mouth of muddy gut. | 932 State route 466, Weeksbury, KY. | 2019-08-02
2019 | 2019-05-28 | Pikeville |  |  | 37830188B00090 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 1032 KY. Route 466, Weeksbury, KY. | 2019-05-28
2019 | 2019-05-28 | Pikeville | 75344063 | DKY0107717 | 37830188B00110 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Customer has built house right against our secondary pole. Need to relocate away from house. | 992 Ky 466, Weeksbury. KY. | 2019-12-19
2019 | 2019-05-28 | Pikeville | 74176468 | DKY0109220 | 37830234000182 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown. Needs replaced. | 576 Arnold Fork, Kite, KY. | 2021-01-14
2019 | 2019-05-28 | Pikeville |  |  | 37830236000076 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Shop Fork, Caleb Fork, Weeksbury, KY. | 2019-05-28
2019 | 2019-05-29 | Pikeville |  |  | 37830234000046 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 13796 KY Hwy 7 South, Kite, KY. | 2019-05-29
2019 | 2019-05-29 | Pikeville |  |  | 37830234000084 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 13254 KY Hwy 7 , Kite, KY. | 2019-05-29
2019 | 2019-05-29 | Pikeville |  |  | 37830234000092 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Hwy 7 South, Kite, KY. | 2019-05-29
2019 | 2019-05-29 | Pikeville |  |  | 37830234000096 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 110 Hwy 1498 North, Kite, KY. | 2019-05-29
2019 | 2019-05-29 | Pikeville |  |  | 37830258000002 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 13998 KY. Hwy 7 South, Kite, KY. | 2019-05-29
2019 | 2019-05-29 | Pikeville |  |  | 37830258000095 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 13984 KY Hwy 7 South, Kite, KY. | 2019-05-29
2019 | 2019-06-03 | Pikeville |  |  | 37830018000100 |  | 3402204-MCKINNEY / MAYTOWN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Durango Drive, Turkey Creek, Maytown, KY. | 2019-06-03
2019 | 2019-06-03 | Pikeville | 82243192 | DKY0116911 | 37830042B00141 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Conductor not tied in good. @ Elkhorn Park, Turkey Creek | Elkhorn Park Rd, Turkey Creek, Maytown, KY. | 2022-05-17
2019 | 2019-06-03 | Pikeville | 76956717 | DKY0110457 | 37830042B00142 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | crossarm/braces: deteriorated, not rotten |  | KPC | YES | Pole and crossarms are rotten. Near the head of turkey creek. | Turkey Creek Road, Maytown, KY. | 2021-10-15
2019 | 2019-06-03 | Pikeville |  |  | 37830042B00422 |  | 3402204-MCKINNEY / MAYTOWN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Turkey Creek, Maytown, KY. | 2019-06-03
2019 | 2019-06-03 | Pikeville |  |  | 37830043000008 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole. Repaired same day | KY. Route 1101, Drift, KY. | 2019-06-03
2019 | 2019-06-03 | Pikeville |  |  | 37830043000010 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole. Repaired same day | 1570 Co Rd 1101, Drift, KY 41619, USA | 2019-06-03
2019 | 2019-06-03 | Pikeville | 81215402 | DKY0115563 | 37830043000046 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | YES | Neutral sagged low. Needs slack taken out. | 1570 KY 1101, Drift, KY 41619 | 2022-01-24
2019 | 2019-06-03 | Pikeville |  |  | 37830043000114 |  | 3402204-MCKINNEY / MAYTOWN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 1570 Co Rd 1101, Drift, KY 41619, USA | 2019-06-03
2019 | 2019-06-04 | Pikeville |  |  | 38831079000130 |  | 3402204-MCKINNEY / MAYTOWN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 2179 Wilson Creek, Langley, KY. | 2019-06-04
2019 | 2019-06-04 | Pikeville |  |  | 38831097000139 |  | 3402204-MCKINNEY / MAYTOWN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Wilson Creek, Langley, KY. | 2019-06-04
2019 | 2019-06-04 | Pikeville |  |  | 38831121C00019 |  | 3402204-MCKINNEY / MAYTOWN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | N Front Street, Maytown, KY. | 2019-06-04
2019 | 2019-06-04 | Pikeville |  |  | 38831121C00091 |  | 3402204-MCKINNEY / MAYTOWN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Wilson Creek, Langley, KY. | 2019-06-04
2019 | 2019-06-04 | Pikeville | 86179410 |  | 38831121C00377 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown. | Plum Street, Langley, KY.
2019 | 2019-06-04 | Pikeville |  |  | 38831121C00398 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign |  | 6A primary conductor has only one strand holding it. | 435 Doc Allen Branch, Langley, KY 41645, USA | 2022-02-28
2019 | 2019-06-04 | Pikeville | 76169906 | Dky0109041 | 38831121D00062 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown.@ old school bldg. @ end of street. | 2nd Avenue, Maytown, KY. 41645 | 2020-04-02
2019 | 2019-06-04 | Pikeville |  |  | 38831121D00149 |  | 3402204-MCKINNEY / MAYTOWN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker (2) Completed same day | KY. Route 80, Langley, KY. | 2019-06-04
2019 | 2019-06-04 | Pikeville |  |  | 38831121D00181 |  | 3402204-MCKINNEY / MAYTOWN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Maple Street, Langley, KY. | 2019-06-04
2019 | 2019-06-04 | Pikeville |  |  | 38831122A10433 |  | 3402204-MCKINNEY / MAYTOWN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Johns Branch, Maytown, KY. 41645 | 2019-06-04
2019 | 2019-06-04 | Pikeville | 74217173 | DKY0106229 | 38831122A20462 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Low clearance over deck on service drop. Probably need taller secondary pole and raise the drop on customer service pole. | 58 Dogwood Heights, Langley, KY. | 2019-09-12
2019 | 2019-06-05 | Pikeville |  |  | 38821086C00087 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 52 KY. Route 1056, McAndrews, KY. | 2019-06-05
2019 | 2019-06-05 | Pikeville |  |  | 38821086C00091 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | McAndrews, KY 41543, USA | 2019-06-05
2019 | 2019-06-05 | Pikeville |  |  | 38821086C00395 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Service drop hanging down pole. Needs removed. Completed same day. | 3184 KY route 199, McAndrews, KY. | 2019-06-05
2019 | 2019-06-05 | Pikeville |  |  | 38821086C00406 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | May Fork, Pinsonfork, KY 41555, USA | 2019-06-05
2019 | 2019-06-05 | Pikeville |  |  | 38821087B00003 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Ball Fork, Pond Creek, McAndrews, KY. | 2019-06-05
2019 | 2019-06-05 | Pikeville |  |  | 38831145C00014 |  | 3402204-MCKINNEY / MAYTOWN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Warren Drive, Langley, KY. | 2019-06-05
2019 | 2019-06-05 | Pikeville | 74204121 | 106197 | 38831145C00030 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop is sagged low. Don’t think it can be raised high enough without setting secondary pole.@ end of Osborne Lane down street from Allen Central School | 37 Osborne Ln, Eastern, KY | 2019-08-21
2019 | 2019-06-05 | Pikeville |  |  | 38831145C00148 |  | 3402204-MCKINNEY / MAYTOWN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Gold Howard Loop, Langley, KY. | 2019-06-05
2019 | 2019-06-05 | Pikeville | 81521037 | DKY0116013 | 38831145C00173 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire hanging down pole. Pretty stiff 3 phase angle. Don’t see anchor to re-attach to. Probably will need to install anchor and attach guy. | 483 KY-80, Eastern, near entrance to Allen Central School | 2022-04-05
2019 | 2019-06-06 | Pikeville |  |  | 38821062D00058 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Charles Deskins Street, Pond Creek Road, Pinsonfork, KY. | 2019-06-06
2019 | 2019-06-06 | Pikeville | 74328787 | DKY0106679 | 38821062D00133 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarm broken/ neutral conductor down. On hillside. Pole appears to be solid but it also looks like a slide area. @ mouth of Pinsonfork on the hill behind tan 2 story house. | Pinsonfork Road, McAndrews, KY. | 2020-03-03
2019 | 2019-06-06 | Pikeville | 77409029 | DKY0110758 | 38821063B00012 |  | DKY0110758 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | crossarm/braces: deteriorated, not rotten |  | KPC | YES | Crossarms are rotten/ pole is not rotted but is pretty deteoriated. Probably should be changed along with the arms. | Harve Varney Road, KY Route 1056, McAndrews, KY. | 2022-06-06
2019 | 2019-06-06 | Pikeville |  |  | 38821063B00074 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | McAndrews, KY 41543, USA | 2019-06-06
2019 | 2019-06-06 | Pikeville | 74329019 | DKY0106745 | 38821086A00404 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Pole has been filled around and we have low clearance on the neutral conductor. | Pinsonfork Road, Pond Creek, McAndrews, KY. | 2019-12-05
2019 | 2019-06-06 | Pikeville |  |  | 38821086B00169 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 900 Runyon Branch, Pinsonfork, KY. | 2019-06-06
2019 | 2019-06-06 | Pikeville |  |  | 38821086B00415 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Charlie Runyon Road, Pinsonfork, KY. | 2019-06-06
2019 | 2019-06-06 | Pikeville |  |  | 38821086C00104 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Oakie Smith Road, KY. 199, Pinsonfork, KY. | 2019-06-06
2019 | 2019-06-06 | Pikeville | 74328787 | DKY0106679 | 38821086C00108 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Crossarm split/Lightning arrestor broken @ yellow house/gray shutters on left. | 451 KY. Route 1056, McAndrews, KY. | 2020-03-03
2019 | 2019-06-06 | Pikeville |  |  | 38821086C00292 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 3534 KY. 199, Pond Creek, McAndrews, KY. | 2019-06-06
2019 | 2019-06-06 | Pikeville |  |  | 38821086C00293 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 3500 KY. 199, Pond Creek, McAndrews, KY. | 2019-06-06
2019 | 2019-06-06 | Pikeville |  |  | 38821086C00407 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 3907 KY-199, Pinsonfork, KY 41555, USA | 2019-06-06
2019 | 2019-06-06 | Pikeville |  |  | 38821086D00238 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 24 Runyons Branch, Pinsonfork, KY 41555, USA | 2019-06-06
2019 | 2019-06-06 | Pikeville |  |  | 38821086D00274 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Pin type insulator broken. Can’t see that we’ll in pictures but it’s broken. Just before the gate. | 158 Rockhouse Branch Rd, Pinsonfork, KY 41555, USA | 2019-09-12
2019 | 2019-06-06 | Pikeville |  |  | 38821086D00334 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 4763 KY-199, Pinsonfork, KY 41555, USA | 2019-06-06
2019 | 2019-06-06 | Pikeville |  |  | 38821086D00449 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop sagged low. Needs slack taken out for clearance. | 156 Bennie Hatfield Road, Pinsonfork, KY.
2019 | 2019-06-06 | Pikeville |  |  | 38821110A00056 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Installed guy marker. Dish is Dish Network | 1267 Runyon Branch, Pinsonfork, KY. 40906
2019 | 2019-06-06 | Pikeville |  |  | 38821110A00062 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 1388 Runyon Branch, Pinsonfork, KY. | 2019-06-06
2019 | 2019-06-06 | Pikeville |  |  | 38821110B00078 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarm broken. Neutral conductor hanging close to open wire secondary. | 1758 Runyon Branch, Pinsonfork, KY. | 2019-09-12
2019 | 2019-06-06 | Pikeville | 74328773 | DKY0106764 | 38821110B00093 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning considerably. Needs to be straightened. Install: 1995 | Pinsonfork Road, McAndrews, KY. | 2020-10-09
2019 | 2019-06-06 | Pikeville |  |  | 38821110C20247 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Grants Branch Park, Pinsonfork, KY 41555, USA | 2019-06-06
2019 | 2019-06-06 | Pikeville |  |  | 38821110D00151 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | DirecTv | Straight Fork, Upper Pond Creek, Pinsonfork, KY.
2019 | 2019-06-06 | Pikeville |  |  | 38821110D40280 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop sagged low. Needs slack taken out for clearance. Last house on Williams Branch | Williams Branch, Upper Pond Creek, Pinsonfork, KY.
2019 | 2019-06-06 | Pikeville | 74328773 | DKY0106764 | 38821111B00001 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown | 6505 Straight Fork, Upper Pond Creek, Pinsonfork,KY. | 2020-10-09
2019 | 2019-06-06 | Pikeville | 74328998 | DKY0106739 | 38821135A00006 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole has several woodpecker holes. Install: 1967 | 6755 Straight Fork, Upper Pond Creek, Pinsonfork, KY. | 2020-03-03
2019 | 2019-06-07 | Pikeville |  |  | 38821038B00147 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Irick Street, Stone, KY. | 2019-06-07
2019 | 2019-06-07 | Pikeville | 74765559 | DKY0107027 | 38821038D00134 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire broken. Anchor pulled out. Buckarm pole. Needs to install anchor and reattach | KY. 199, Stone, KY. | 2019-10-15
2019 | 2019-06-07 | Pikeville |  |  | 38821038D00196 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. (2). Completed same day | 952 KY. 199, Stone, KY. | 2019-06-07
2019 | 2019-06-07 | Pikeville | 74765559 | DKY0107027 | 38821038D00296 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire broken. Stiff angle with heavy communication cables. Need to install anchor and re-attach guy. In front of White trailer/black shutters | KY. 199 , Stone, KY. | 2019-10-15
2019 | 2019-06-07 | Pikeville |  |  | 38821062B00149 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Wolfpen Branch, Mullen Fork, Stone, KY. | 2019-06-07
2019 | 2019-06-07 | Pikeville | 74329032 | DKY0106717 | 38821062B00389 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Pole partially burnt/ inactive transformer. Near head of Mullen Fork. | Mullen Fork, Stone, KY. | 2019-12-10
2019 | 2019-06-07 | Pikeville |  |  | 38821062B00401 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Mullen Fork, Stone, KY. | 2019-06-07
2019 | 2019-06-07 | Pikeville |  |  | 38821062C00397 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 1633 KY. 199, Stone, KY. | 2019-06-07
2019 | 2019-06-07 | Pikeville |  |  | 38831103000015 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Shady Lane, Cowpen Road, Pikeville, KY. | 2019-06-07
2019 | 2019-06-07 | Pikeville | 77208329 | DKY0110537 | 38831103000175 |  | 3402003-KEYSER / MULLINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten. | 79 Haynes Village, Rfk Cowpen, Pikeville, KY. | 2021-10-22
2019 | 2019-06-07 | Pikeville |  |  | 38831127A00107 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Lonesome Cedar Lane, Cowpen Road, Pikeville, KY. | 2019-06-07
2019 | 2019-06-07 | Pikeville |  |  | 38831127B00101 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 123 Cowpen Road, Pikeville, KY. | 2019-06-07
2019 | 2019-06-07 | Pikeville |  |  | 38831127B00232 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | N Mayo Trail, Pikeville, KY. | 2019-06-07
2019 | 2019-06-07 | Pikeville | 79706983 |  | 38831127B00507 |  | 3402003-KEYSER / MULLINS | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown on bank pole. @ old magic mart bldg. | Weddington Branch, Pikeville, KY. | 2021-06-11
2019 | 2019-06-07 | Pikeville | 86090594 |  | 38831151A00150 |  | 3402003-KEYSER / MULLINS | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown | 17 River Run, Coal Run Village, Pikeville, KY.
2019 | 2019-06-07 | Pikeville |  |  | 38831151A00199 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Flora Street, Coal Run Village, Pikeville, KY. | 2019-06-07
2019 | 2019-06-07 | Pikeville |  |  | 38831151A00379 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Middle Street, Coal Run Village, Pikeville, KY. | 2019-06-07
2019 | 2019-06-07 | Pikeville |  |  | 38831151C00120 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Ratliff Branch, Pikeville. KY. | 2019-06-07
2019 | 2019-06-07 | Pikeville |  |  | 38831151C00147 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Village Street, Coal Run Village, Pikeville, KY. | 2019-06-07
2019 | 2019-06-10 | Pikeville |  |  | 38831103000060 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Guy wire needs marker. (2) Completed same day | Cowpen Road, Pikeville, KY. | 2019-06-10
2019 | 2019-06-10 | Pikeville |  |  | 38831103000061 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Jenny Fork, Cowpen Road, Pikeville, KY. | 2019-06-10
2019 | 2019-06-10 | Pikeville | 76371020 | DKY0109804 | 38831103000078 |  | 3402003-KEYSER / MULLINS | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator insulator melting down. @ across from Adkins/sword drive. | Kinnikinnick Lane, Pikeville, KY.
2019 | 2019-06-10 | Pikeville |  |  | 38831103000186 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Jenny Fork, Cowpen Road, Pikeville, KY. | 2019-06-10
2019 | 2019-06-10 | Pikeville |  |  | 38831103000192 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Cowpen Road, Pikeville, KY. | 2019-06-10
2019 | 2019-06-10 | Pikeville |  |  | 38831103000213 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Andrew Street, Cowpen Road, Pikeville, KY. | 2019-06-10
2019 | 2019-06-10 | Pikeville |  |  | 38831103000225 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Adkins Lane, Cowpen Road, Pikeville, KY. | 2019-06-10
2019 | 2019-06-10 | Pikeville |  |  | 38831103000256 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Kinnikinnick Branch, Pikeville, KY. | 2019-06-10
2019 | 2019-06-10 | Pikeville |  |  | 38831103C40373 |  | 3402003-KEYSER / MULLINS | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop sagged low. Can be re-sagged at weatherhead to raise it enough for proper clearance. | 300 Jenny Fork, Cowpen Road, Pikeville, KY.
2019 | 2019-06-10 | Pikeville |  |  | 38831126C00709 |  | 3402003-KEYSER / MULLINS | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down pole. Energized. Removed drop same day. | Mullins Addition Drive, Pikeville, KY. | 2019-06-10
2019 | 2019-06-10 | Pikeville | 76371020 | DKY0109804 | 38831127A00268 |  | 3402003-KEYSER / MULLINS | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | End of crossarm is broken out allowing angle pin to lay over. | John Cornett Road, Ratliff Rd. Mullins, KY.
2019 | 2019-06-10 | Pikeville | Outage # 4547481 |  | 38831127A00311 |  | 3402003-KEYSER / MULLINS | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage | STOLEN NEUTRAL | KPC |  | #2 al. Primary neutral down behind apartment bldg. Can use truck to sag it @ pole 1126-665. Repaired 6-19-19 by R. Ray. | 59 Thacker Road, Pikeville, KY. | 2019-06-19
2019 | 2019-06-10 | Pikeville |  |  | 38831127A00437 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 65 Mullins hill, Pikeville, KY. | 2019-06-10
2019 | 2019-06-10 | Pikeville |  |  | 38831127A00446 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Mullins School Street, Pikeville, KY. | 2019-06-10
2019 | 2019-06-10 | Pikeville | 78701747 | DKY0112633 | 38831127A00538 |  | 3402003-KEYSER / MULLINS | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole has been partially burnt. Install: 1991 | 149 Ratliff Road, Mullins, KY. | 2021-10-28
2019 | 2019-06-10 | Pikeville |  |  | 38831127A00785 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | ACS Drive, Pikeville, KY. | 2019-06-10
2019 | 2019-06-10 | Pikeville |  |  | 38831127B00382 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Mossy Bottom, Pikeville, KY. | 2019-06-10
2019 | 2019-06-10 | Pikeville | 86090575 | DKY0122567 | 38831127B10696 |  | 3402003-KEYSER / MULLINS | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Aluminum street light pole damaged and leaning. Install: 2007 | Mossy Bottom Ct. Pikeville, KY.
2019 | 2019-06-11 | Pikeville |  |  | 38821129B00345 |  | 3402002-KEYSER / STONECOAL | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | Dish Network | 2359 Town Mountain Rd, Pikeville, KY 41501, USA
2019 | 2019-06-11 | Pikeville |  |  | 38831104B40196 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 75 Mount View Drive, lfk Stonecoal Road, Pikeville, KY. | 2019-06-11
2019 | 2019-06-11 | Pikeville |  |  | 38831127D00130 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. (3) Completed same day | Stone Coal Rd, Pikeville, KY 41501, USA | 2019-06-11
2019 | 2019-06-11 | Pikeville |  |  | 38831127D00656 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. (3) Completed same day | Stone Coal Rd, Pikeville, KY 41501, USA | 2019-06-11
2019 | 2019-06-11 | Pikeville |  |  | 38831128000017 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 2087 Stone Coal Rd, Pikeville, KY 41501, USA | 2019-06-11
2019 | 2019-06-11 | Pikeville | 79898080 | DKY0113961 | 38831128000018 | TRUE | 3402002-KEYSER / STONECOAL | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire hanging down pole. Angle pole. Needs to be reattached. Don’t see anchor anywhere. Probably will have to install anchor. Hand dig. | 2088 Stone Coal Rd, Pikeville, KY 41501, USA | 2021-09-06
2019 | 2019-06-11 | Pikeville | 82612447 | DKY0117274 | 38831128000026 |  | 3402002-KEYSER / STONECOAL | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator insulators melting down. Can’t really see very good from the pictures but with binoculars you can see good. | Mims Branch, Stonecoal Road, Pikeville, KY. | 2022-10-30
2019 | 2019-06-11 | Pikeville | 82551636 | DKY0117213 | 38831128000115 |  | 3402002-KEYSER / STONECOAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | YES | Remove inactive service hanging down pole. | 2065 Stone Coal Rd, Pikeville, KY 41501, USA | 2022-07-14
2019 | 2019-06-11 | Pikeville |  |  | 38831128000142 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 299 Weddington Hollow, Stonecoal Road, , KY. | 2019-06-11
2019 | 2019-06-11 | Pikeville | 82683217 | DKY0117375 | 38831128000214 | TRUE | 3402002-KEYSER / STONECOAL | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Service drop hanging down pole. Should be removed. | 233 Cushaw Branch, Stonecoal Road, Pikeville, KY. | 2022-07-12
2019 | 2019-06-11 | Pikeville |  |  | 38831151C00459 |  | 3402002-KEYSER / STONECOAL | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole. Repaired same day | Ramsey Dr, Pikeville, KY 41501, USA | 2019-06-11
2019 | 2019-06-11 | Pikeville |  |  | 38831152000173 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 508 US-119, Pikeville, KY 41501, USA | 2019-06-11
2019 | 2019-06-11 | Pikeville |  |  | 38831152000187 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Tollage Creek, Pikeville, KY 41501, USA | 2019-06-11
2019 | 2019-06-11 | Pikeville |  |  | 38831152000201 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 273 US-119, Pikeville, KY 41501, USA | 2019-06-11
2019 | 2019-06-12 | Pikeville | Outage ticket # 4488681 Completed by Paul Layne LCS |  | 37830024C00694 |  | 3402002-KEYSER / STONECOAL | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | Primary conductor floating. Contacted duty supervisor to have crew make repairs. Completed same day. | 234 Horseshoe Drive, Ratliff Creek, Pikeville, KY. | 2019-06-12
2019 | 2019-06-12 | Pikeville |  |  | 37830024C01188 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 1278 Ratliff Creek Rd, Pikeville, KY 41501, USA | 2019-06-12
2019 | 2019-06-12 | Pikeville | 77208403 | DKY0110555 | 38821105A20359 |  | 3402002-KEYSER / STONECOAL | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole leaning considerably. Will probably need backyard machine to straighten.@ line going to cell tower. 3rd pole from top. Install: 2014 | Zebulon Hwy & Knob Fork Rd, Kentucky 41501, USA | 2020-12-09
2019 | 2019-06-12 | Pikeville |  |  | 38821105A40430 |  | 3402002-KEYSER / STONECOAL | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen. Repaired same day | Knob Fork, Zebulon, KY. | 2019-06-12
2019 | 2019-06-12 | Pikeville |  |  | 38821105C00014 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Knob Fork Street, Zebulon, KY. | 2019-06-12
2019 | 2019-06-12 | Pikeville |  |  | 38821105C00082 |  | 3402002-KEYSER / STONECOAL | Line Work | OH | joint use attachments: clearance issues |  |  | Foreign |  | DirecTv (1) Dish Network (1) | Knob Fork Road, Zebulon, KY.
2019 | 2019-06-12 | Pikeville |  |  | 38821105D00143 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Ford Bottom, Zebulon, KY. | 2019-06-12
2019 | 2019-06-12 | Pikeville |  |  | 38821129C00252 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Kaney Branch, Pikeville, KY 41501, USA | 2019-06-12
2019 | 2019-06-12 | Pikeville |  |  | 38821129C20428 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Burning Fork Rd, Pikeville, KY, USA | 2019-06-12
2019 | 2019-06-12 | Pikeville | 82839571 | DKY0117502 | 38821129D00037 |  | 3402002-KEYSER / STONECOAL | Line Work | OH | UG conduit: damaged or separated |  |  | Foreign |  | Conduit separated at the bottom of the pole. | 977 Burning Fork Rd, Pikeville, KY 41501, USA | 2022-07-25
2019 | 2019-06-12 | Pikeville |  |  | 38821129D00231 |  | 3402002-KEYSER / STONECOAL | Line Work | OH | joint use attachments: clearance issues |  |  | Foreign |  | Dish Network (2) | 695 Burning Fork Rd, Pikeville, KY 41501, USA
2019 | 2019-06-12 | Pikeville | 86142370 | DKY0123112 | 38831151D00090 |  | 3402001-KEYSER / THOMPSON RD | Service Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators are melting down. @ lykins crk / coal run Hill..Can’t really tell that good from pictures but I looked thru binoculars. | Rfk Lykins Creek, Pikeville, KY.
2019 | 2019-06-12 | Pikeville |  |  | 38831151D00091 |  | 3402001-KEYSER / THOMPSON RD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Coal Run Hill, Pikeville, KY 41501, USA | 2019-06-12
2019 | 2019-06-12 | Pikeville |  |  | 38831151D00454 |  | 3402001-KEYSER / THOMPSON RD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Lykins Creek, Pikeville, KY 41501, USA | 2019-06-12
2019 | 2019-06-12 | Pikeville |  |  | 38831151D00548 |  | 3402001-KEYSER / THOMPSON RD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Coal Run Hill, Pikeville, KY 41501, USA | 2019-06-12
2019 | 2019-06-12 | Pikeville |  |  | 38831151D00554 |  | 3402001-KEYSER / THOMPSON RD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. (2) Completed same day | Coal Run Hill, Pikeville, KY 41501, USA | 2019-06-12
2019 | 2019-06-12 | Pikeville |  |  | 38831152D40362 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Ratliff Creek Rd, Pikeville, KY 41501, USA | 2019-06-12
2019 | 2019-06-13 | Pikeville | 73866587 | DKY0105971 | 37820006000003 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | already written to EDN100577 FOREIGN | Pole is hollow. | 194 Long Fork, Kimper, KY. | 2019-12-07
2019 | 2019-06-13 | Pikeville |  |  | 37820006000020 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 4875 State Hwy 194, Upper Johns Creek, Kimper, KY. | 2019-06-13
2019 | 2019-06-13 | Pikeville |  |  | 37820006000023 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 5063 Hwy 194, Kimper, KY. | 2019-06-13
2019 | 2019-06-13 | Pikeville |  |  | 37820006000057 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker (2) . Completed same day | Hwy 194, Upper Johns Creek, Kimper, KY. | 2019-06-13
2019 | 2019-06-13 | Pikeville | 73865701 | DKY0106283 | 37820030000065 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator melting down.@ Johns Creek Primitive Baptist Church | 2253 Long Fork, Kimper, KY. | 2019-10-02
2019 | 2019-06-13 | Pikeville |  |  | 37820031B00009 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | Service drop laying on roof. Needs to be raised for clearance. Can be raised 3 ft on customers pole and also has slack that can be taken out. | 3535 Long Fork, Kimper, KY.
2019 | 2019-06-13 | Pikeville | 77208567 | DKY0110670 | 37830024A10175 |  | 3402001-KEYSER / THOMPSON RD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole top is split allowing pole top pin to lay over. | 107 Phillips Dr, Pikeville, KY 41501, USA | 2020-12-10
2019 | 2019-06-13 | Pikeville |  |  | 37830024A10176 |  | 3402001-KEYSER / THOMPSON RD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. (2) Completed same day | Thompson Rd, Pikeville, KY 41501, USA | 2019-06-13
2019 | 2019-06-13 | Pikeville |  |  | 37830024A11054 |  | 3402001-KEYSER / THOMPSON RD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 120 Bryan St, Pikeville, KY 41501, USA | 2019-06-13
2019 | 2019-06-13 | Pikeville | 79046212 | DKY0112930 | 38831151D00667 |  | 3402001-KEYSER / THOMPSON RD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive primary tap and pole. Take-off is primary riser pole # 666. Primary underground is parked in pad mount xfmr. #522. primary overhead conductor is down. | 60 Billups Lane, Pikeville, KY | 2021-04-22
2019 | 2019-06-13 | Pikeville |  |  | 38831151D00728 |  | 3402001-KEYSER / THOMPSON RD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Heather Ln, Pikeville, KY 41501, USA | 2019-06-13
2019 | 2019-06-13 | Pikeville |  |  | 38831152000097 |  | 3402001-KEYSER / THOMPSON RD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Thompson Rd, Pikeville, KY 41501, USA | 2019-06-13
2019 | 2019-06-13 | Pikeville |  |  | 38831152000126 |  | 3402001-KEYSER / THOMPSON RD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Thompson Rd, Pikeville, KY 41501, USA | 2019-06-13
2019 | 2019-06-13 | Pikeville | 79012912 | DKY0112904 | 38831152000329 |  | 3402001-KEYSER / THOMPSON RD | Line Work | UG | UG conduit: damaged or separated |  |  | KPC |  | Pad mounted junction box has been hit by car. Probably need new box and guard posts around it. @ behind Berkshire motel | Thompson Rd, Pikeville, KY 41501, behind Berkshire Inn
2019 | 2019-06-13 | Pikeville |  |  | 38831152B10357 |  | 3402001-KEYSER / THOMPSON RD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Cassidy Blvd, Pikeville, KY 41501, USA | 2019-06-13
2019 | 2019-06-14 | Pikeville |  |  | 38821133000002 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Pritchard Fork, Gabriel Fork, Kimper, KY. | 2019-06-14
2019 | 2019-06-14 | Pikeville |  |  | 38821133000008 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Pritchard Fork, Gabriel Fork, Kimper, KY. | 2019-06-14
2019 | 2019-06-14 | Pikeville |  |  | 38821134000013 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Gabriel Fork, Kimper, KY. | 2019-06-14
2019 | 2019-06-14 | Pikeville |  |  | 38821134000030 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | West Fork San Gabriel River, California 91702, USA | 2019-06-14
2019 | 2019-06-17 | Pikeville |  |  | 37820004000033 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 747 Hurricane Creek, Kimper, KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville | 73865717 | DKY0105851 | 37820004000055 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  |  |  | Foreign |  | Neutral conductor down. | 1958 Hurricane Creek, Kimper, KY. | 2019-10-24
2019 | 2019-06-17 | Pikeville |  |  | 37820004000259 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 204 Fire Station Road, Kimper, KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville |  |  | 37820005000005 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 3578 KY. 194, Kimper, KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville |  |  | 37820005000025 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 2105 KY. 194, Kimper, KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville |  |  | 37820005000080 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 449 Layne Branch, Kimper, KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville |  |  | 37820005000186 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown on transformer bank. | 2607 KY. 194, Kimper, KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville |  |  | 37820006000050 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 47 Long Fork Road, Kimper, KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville |  |  | 37820029000008 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. Repaired same day | Layne Branch, Kimper. KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville |  |  | 38821108000108 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 6880 KY. 194, Kimper, KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville |  |  | 38821131000029 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire very slack. No marker. Repaired same day. | 1374 Sunshine Lane, Kimper, KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville |  |  | 38821131000073 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Sunshine Lane, Kimper, KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville |  |  | 38821132000013 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 8801 KY. 194, Kimper, KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville |  |  | 38821132000024 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | Service drop laying on roof top of mobile home. Can take slack out at transformer pole to get enough clearance. | 150 Varney Branch, Kimper, KY,
2019 | 2019-06-17 | Pikeville |  |  | 38821132000061 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole. Repaired same day | Hurricane Creek, Kimper, KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville |  |  | 38821132000132 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 9317 KY. 194, Kimper, KY. | 2019-06-17
2019 | 2019-06-17 | Pikeville |  |  | Z3821132000164 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 206 Spears Branch, Kimper, KY. | 2019-06-17
2019 | 2019-06-18 | Pikeville | 73865749 | DKY0106056 | 37820003000030 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Epoxilators are melting down. Truck access questionable but I think so. | 7219 Raccoon Road, Pikeville, KY. | 2019-09-10
2019 | 2019-06-19 | Pikeville |  |  | 38821105D00029 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 696 Raccoon Rd, Raccoon, KY 41557, USA | 2019-06-19
2019 | 2019-06-19 | Pikeville |  |  | 38821105D00125 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 1069 Raccoon Road, Pikeville, KY. | 2019-06-19
2019 | 2019-06-19 | Pikeville | 73865764 | DKY0106001 | 38821107000022 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator melting down. | 4600 KY-194, Kimper, KY 41539, USA | 2019-10-02
2019 | 2019-06-19 | Pikeville | 73865826 | DKY0105812 | 38821107000030 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Epoxilator melting down | 361 Lawson Branch, Kimper, KY 41539, USA | 2022-06-30
2019 | 2019-06-19 | Pikeville | 63681574 | DKY0093491 | 38821107000031 | TRUE | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melted down. Pretty bad. There’s 11 on this pole and 9 of them are melted. STATION ZONE. Can use truck if dry or frozen. | 4841 KY-194, Kimper, KY 41539, USA | 2022-07-12
2019 | 2019-06-19 | Pikeville | 73865826 | DKY0105812 | 38821107000032 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down | Lawson Branch, Kimper, KY. | 2022-06-30
2019 | 2019-06-19 | Pikeville | 73865826 | DKY0105812 | 38821107000034 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator melting down | 407 Lawson Pl, Minden, LA 71055, USA | 2022-06-30
2019 | 2019-06-19 | Pikeville |  |  | 38821107000057 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. (4) Completed same day | 3879 KY-194, Kimper, KY 41539, USA | 2019-06-19
2019 | 2019-06-19 | Pikeville | 73865764 | DKY0106001 | 38821107000102 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign |  | Pole is in a bind. Guy wire pulled too tight. Has pole pulled way back. @ High Ridge Mining on the hill. | KY. 194 , Kimper, KY. | 2019-10-02
2019 | 2019-06-19 | Pikeville |  |  | 38821108B30320 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Meat house Fork, Kimper, KY. | 2019-06-19
2019 | 2019-06-19 | Pikeville |  |  | 38821130000011 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 1888 Raccoon Road, Pikeville, KY. | 2019-06-19
2019 | 2019-06-19 | Pikeville | 73865898 | DKY0105958 | 38821130000033 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  |  |  | Foreign |  | Neutral conductor down. | 284 Grassy Fork, Raccoon, KY. | 2019-10-01
2019 | 2019-06-19 | Pikeville |  |  | 38821130000036 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 486 Grassy Fork, Raccoon, KY. | 2019-06-19
2019 | 2019-06-19 | Pikeville |  |  | 38821130000097 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 1721 Raccoon Road, Pikeville, KY. | 2019-06-19
2019 | 2019-06-19 | Pikeville |  |  | 38821130000215 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 868 Grassy Branch, Raccoon, KY. | 2019-06-19
2019 | 2019-06-19 | Pikeville |  |  | 38821131000009 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | May Branch, Grassy Fork, Raccoon, KY. | 2019-06-19
2019 | 2019-06-19 | Pikeville |  |  | 38821131000084 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | May Branch, Grassy Fork, Raccoon, KY. | 2019-06-19
2019 | 2019-06-19 | Pikeville |  |  | 38821139000068 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 602 Grassy Fork, Raccoon, KY. | 2019-06-19
2019 | 2019-06-24 | Pikeville |  |  | 37820002000148 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Raccoon Road, Raccoon, KY. | 2019-06-24
2019 | 2019-06-24 | Pikeville |  |  | 37820002000215 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Charles Branch, Frozen Creek, Raccoon, KY. | 2019-06-24
2019 | 2019-06-24 | Pikeville |  |  | 38820868C00049 |  | 2150501-BORDERLAND / NOLAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack. Needs tightened. Completed same day | 13173 State Hwy 292 , Hatfield, KY. | 2019-06-24
2019 | 2019-06-24 | Pikeville |  |  | 38820868D30351 |  | 2150501-BORDERLAND / NOLAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | State Hwy 292, Hatfield, KY. | 2019-06-24
2019 | 2019-06-24 | Pikeville |  |  | 38820869A10232 |  | 2150501-BORDERLAND / NOLAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 13190 State Hwy 292, Big Creek, KY. | 2019-06-24
2019 | 2019-06-24 | Pikeville | 74328550 | DKY0106668 | 38820892C00028 |  | 2150501-BORDERLAND / NOLAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarm rotten/deteoriated. | Bent Branch, North Big Creek, Hatfield, KY. | 2020-03-12
2019 | 2019-06-24 | Pikeville |  |  | 38820892C00033 |  | 2150501-BORDERLAND / NOLAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 11293 North Big Creek Road, Hatfield, KY. | 2019-06-24
2019 | 2019-06-24 | Pikeville |  |  | 38820892C00275 |  | 2150501-BORDERLAND / NOLAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 11120 North Big Creek Road, Hatfield, KY. | 2019-06-24
2019 | 2019-06-24 | Pikeville |  |  | 38820892C00276 |  | 2150501-BORDERLAND / NOLAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 11120 North Big Creek Road, Hatfield, KY. | 2019-06-24
2019 | 2019-06-24 | Pikeville |  |  | 38821130000030 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. (2) Completed same day | Frozen Creek, Raccoon, KY. | 2019-06-24
2019 | 2019-06-24 | Pikeville |  |  | 38821130000080 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 2684 Raccoon Road, Raccoon, KY. | 2019-06-24
2019 | 2019-06-24 | Pikeville |  |  | 38821130000084 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Thompson Hill, Raccoon, KY. | 2019-06-24
2019 | 2019-06-24 | Pikeville |  |  | 38821130000111 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | Church Way, Frozen Creek, Raccoon, KY. | 2019-06-24
2019 | 2019-06-24 | Pikeville |  |  | 38821130000257 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 68 Church Way, Frozen Creek, Raccoon, KY. | 2019-06-24
2019 | 2019-06-24 | Pikeville |  |  | 38821130000291 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | 2846 Brady Lane, Raccoon, KY. | 2019-06-24
2019 | 2019-06-25 | Pikeville | 74800025 | DKY0107506 | 38831053D00101 |  | 3400302-BETSY LAYNE / TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | already written to EDN100577 KPC pole | Pole is rotten. | 977 Toms Creek, Ivel, KY. | 2020-01-21
2019 | 2019-06-25 | Pikeville |  |  | 38831077A00311 |  | 3400302-BETSY LAYNE / TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. Completed same day | George Drive, Ivel, KY. | 2019-06-25
2019 | 2019-06-25 | Pikeville | 74799299 | DKY0107411 | 38831077B00060 |  | 3400302-BETSY LAYNE / TRAM | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive transformer. | North Main Street, Tram, KY. | 2019-12-30
2019 | 2019-06-25 | Pikeville |  |  | 38831077D00550 |  | 3400302-BETSY LAYNE / TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 474 Mare Creek, Stanville, KY 41659, USA | 2019-06-25
2019 | 2019-06-25 | Pikeville |  |  | 38831077D00581 |  | 3400302-BETSY LAYNE / TRAM | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop sagged low. Needs slack taken out. Can be done @ transformer pole or customer pole. Tan and brown mobile home near a bunch of old boats. | 368 Mare Creek Rd, Stanville, KY 41659, USA
2019 | 2019-06-25 | Pikeville | 74799309 | DKY0107422 | 38831078000077 |  | 3400302-BETSY LAYNE / TRAM | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive transformer. | Shop Branch of Mare Creek Rd, Kentucky 41659, USA | 2022-04-05
2019 | 2019-06-25 | Pikeville | 74799309 | DKY0107422 | 38831078000135 |  | 3400302-BETSY LAYNE / TRAM | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator melting down. | 376 Stratton Branch Road, Stanville, KY 41659, USA | 2022-04-05
2019 | 2019-06-25 | Pikeville |  |  | 38831078000209 |  | 3400302-BETSY LAYNE / TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 501 Shop Branch, Stanville, KY. | 2019-06-25
2019 | 2019-06-26 | Pikeville | 74328550 | DKY0106668 | 38820892B00011 |  | 2150501-BORDERLAND / NOLAN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown. | 188 Holly Drive, N Big Creek, Hatfield, KY. | 2020-03-12
2019 | 2019-06-26 | Pikeville |  |  | 38820892D00001 |  | 2150501-BORDERLAND / NOLAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2). Completed same day | Lowe Bottom, Hatfield, KY. | 2019-06-26
2019 | 2019-06-26 | Pikeville |  |  | 38820892D20041 |  | 2150501-BORDERLAND / NOLAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Lowe Bottom, Hatfield, KY. | 2019-06-26
2019 | 2019-06-26 | Pikeville |  |  | 38820893B00127 |  | 2150502-BORDERLAND/CHATTAROY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 5670 State Hwy 292 W, Hatfield, KY. | 2019-06-26
2019 | 2019-06-26 | Pikeville |  |  | 38820893B00226 |  | 2150502-BORDERLAND/CHATTAROY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | State Hwy 292, Kentucky 41514, USA | 2019-06-26
2019 | 2019-06-26 | Pikeville | 74328531 | DKY0106716 | 38820916A00051 |  | 2150501-BORDERLAND / NOLAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole has several woodpecker holes. RAILROAD CROSSING. Install: unknown | Swinge Camp Branch, Hatfield, KY. | 2023-01-18
2019 | 2019-06-26 | Pikeville |  |  | 38820916A00092 |  | 2150501-BORDERLAND / NOLAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Swinge Branch, Hatfield, KY. | 2019-06-26
2019 | 2019-06-26 | Pikeville | 74328531 | DKY0106716 | 38820916A00132 |  | 2150501-BORDERLAND / NOLAN | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | YES | Crossarm deteoriated/ split on the end. RAILROAD CROSSING | Swinge Camp Branch, Hatfield, KY. | 2023-01-18
2019 | 2019-06-26 | Pikeville |  |  | 38820916A00152 |  | 2150501-BORDERLAND / NOLAN | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on recloser pole. Repaired same day | Swinge Camp Branch, Hatfield, KY. | 2019-06-26
2019 | 2019-06-26 | Pikeville |  |  | 38820916B00014 |  | 2150501-BORDERLAND / NOLAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | North Big Creek, Hatfield, KY. | 2019-06-26
2019 | 2019-06-26 | Pikeville |  |  | 38820916C00063 |  | 2150501-BORDERLAND / NOLAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Burgett Branch, Hatfield, KY. | 2019-06-26
2019 | 2019-06-26 | Pikeville |  |  | 38820916C00165 |  | 2150501-BORDERLAND / NOLAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Burgett Branch, Hatfield, KY. | 2019-06-26
2019 | 2019-06-26 | Pikeville | 74476294 | DKY0106669 | 38820917C00315 |  | 2150502-BORDERLAND/CHATTAROY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown on transformer bank.@ Tug Fork Apt. Bldgs. | State Hwy 292 West, Hatfield, KY. | 2019-10-29
2019 | 2019-06-26 | Pikeville |  |  | 38820941C10145 |  | 2150502-BORDERLAND/CHATTAROY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Falls Branch, Hatfield, KY. | 2019-06-26
2019 | 2019-06-28 | Pikeville |  |  | 38820964B00010 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 2520 N Big Creek Rd, Hatfield, KY 41514, USA | 2019-06-28
2019 | 2019-06-28 | Pikeville |  |  | 38820964B00057 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. Also has satellite dish. DirecTv | Davidson Hill, Hatfield, KY.
2019 | 2019-06-28 | Pikeville |  |  | 38820964B00128 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 2557 N Big Creek Rd, Hatfield, KY 41514, USA | 2019-06-28
2019 | 2019-06-28 | Pikeville |  |  | 38820964B00143 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 2557 N Big Creek Rd, Hatfield, KY 41514, USA | 2019-06-28
2019 | 2019-06-28 | Pikeville |  |  | 38820964B00145 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop hanging down pole HOT. Removed same day | Davidson Hill, Hatfield, KY. | 2019-06-28
2019 | 2019-06-28 | Pikeville |  |  | 38820988A00025 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole. Repaired same day | 1983 N Big Creek Rd, Belfry, KY 41514, USA | 2019-06-28
2019 | 2019-06-28 | Pikeville | 74800232 | DKY0107568 | 38821052D00261 |  | 3400302-BETSY LAYNE / TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | already written to EDN100577 FOREIGN | POLE IS ROTTEN.. Guy wire needs marker. Installed marker. | Mockingbird Lane, Ivel, KY. | 2021-02-04
2019 | 2019-06-28 | Pikeville |  |  | 38831052D00267 |  | 3400302-BETSY LAYNE / TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | already written to EDN100577 FOREIGN | POLE IS ROTTEN | Mockingbird Lane, Ivel, KY. | 2021-02-15
2019 | 2019-06-28 | Pikeville |  |  | 38831052D00268 |  | 3400302-BETSY LAYNE / TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign |  | POLE IS ROTTEN | Mockingbird Lane, Ivel, KY. | 2019-06-28
2019 | 2019-06-28 | Pikeville |  |  | 38831053A00139 |  | 3400302-BETSY LAYNE / TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 220 Dillon Branch, Ivel, KY. | 2019-06-28
2019 | 2019-06-28 | Pikeville |  |  | 38831053A00168 |  | 3400302-BETSY LAYNE / TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Ivy Creek, Ivel, KY. | 2019-06-28
2019 | 2019-06-28 | Pikeville |  |  | 38831053A00172 |  | 3400302-BETSY LAYNE / TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Ivy Creek, Ivel, KY. | 2019-06-28
2019 | 2019-06-28 | Pikeville |  |  | 38831053A00244 |  | 3400302-BETSY LAYNE / TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Ivy Creek, Ivel, KY. | 2019-06-28
2019 | 2019-06-28 | Pikeville | 74799299 | DKY0107411 | 38831053B00207 |  | 3400302-BETSY LAYNE / TRAM | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | (1) Epoxilator broken. 5 others on the pole. @ mouth of Ivy Creek | U.S. Hwy 23 , Ivel, KY. | 2019-12-30
2019 | 2019-06-28 | Pikeville | 74799299 | DKY0107411 | 38831053C00222 |  | 3400302-BETSY LAYNE / TRAM | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator melting down. | 1670 Ivy Creek Road, Ivel, KY. | 2019-12-30
2019 | 2019-06-28 | Pikeville |  |  | 38831053C00223 |  | 3400302-BETSY LAYNE / TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Ivy Creek, Ivel, KY. | 2019-06-28
2019 | 2019-06-28 | Pikeville |  |  | 38831053C00229 |  | 3400302-BETSY LAYNE / TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Ivy Creek. Ivel, KY. | 2019-06-28
2019 | 2019-06-28 | Pikeville |  |  | 38831053C00254 |  | 3400302-BETSY LAYNE / TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | 2140 Ivy Creek, Ivel, KY. | 2019-06-28
2019 | 2019-06-29 | Pikeville |  |  | 38820939D00047 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. | 4830 North Big Creek, Hatfield, KY. | 2019-06-29
2019 | 2019-06-29 | Pikeville |  |  | 38820940A00010 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Gilliam Branch, North Big Creek, Hatfield, KY. | 2019-06-29
2019 | 2019-06-29 | Pikeville |  |  | 38820963A00046 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. | Elkins Fork, Higgins Road, Hatfield, KY. | 2019-06-29
2019 | 2019-06-29 | Pikeville |  |  | 38820963A00047 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. | Elkins Fork, Hatfield, KY. | 2019-06-29
2019 | 2019-06-29 | Pikeville |  |  | 38820963C00029 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day | Elkins Fork, Higgins Road, Hatfield, KY. | 2019-06-29
2019 | 2019-06-29 | Pikeville |  |  | 38820963D00085 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. | Rockhouse Fork, Kentucky, USA | 2019-06-29
2019 | 2019-06-29 | Pikeville |  |  | 38820987A00044 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. | Walnut Hollow,Rockhouse Fork, Hatfield, KY. | 2019-06-29
2019 | 2019-06-29 | Pikeville | 74329055 | DKY0106949 | 38820987A00063 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , service: unused or abandoned, blanked meter base |  |  | KPC | already written to EDN100577 KPC pole | Pole is rotten.. Remove secondary hanging down pole. De-energized | 206 Walters Fork, Rockhouse Fork, Hatfield, KY. | 2022-04-04
2019 | 2019-06-29 | Pikeville | 74737397 | DKY0106941 | 38820987A00068 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive transformer | 517 Walters Fork, Rockhouse, Hatfield, KY. | 2022-05-18
2019 | 2019-06-29 | Pikeville |  |  | 38820987C00009 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Rockhouse Fork, Hatfield, KY. | 2019-06-29
2019 | 2019-06-29 | Pikeville |  |  | 38820987D00022 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. | Rockhouse Fork, Hatfield, KY. | 2019-06-29
2019 | 2019-06-29 | Pikeville |  |  | 38820987D00024 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. | Rockhouse Fork, Hatfield, KY. | 2019-06-29
2019 | 2019-06-29 | Pikeville |  |  | 38821035C30001 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen. | Pinsonfork, Hatfield, KY. | 2019-06-29
2019 | 2019-06-29 | Pikeville |  |  | 38831035000012 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. | 1056 Pinsonfork, Hatfield, KY. | 2019-06-29
2019 | 2019-07-01 | Pikeville |  |  | 38821012A00037 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. | 37 Smith Cemetery Road, Sidney, KY. | 2019-07-01
2019 | 2019-07-01 | Pikeville |  |  | 38821012A00038 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. | 105 Smith Cemetery Road, Sidney, KY. | 2019-07-01
2019 | 2019-07-01 | Pikeville |  |  | 38821012A00091 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 226 Smith Cemetary Rd, Sidney, KY 41564, USA | 2019-07-01
2019 | 2019-07-01 | Pikeville | 74737397 | DKY0106941 | 38821012A00125 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack. Needs marker. Close to transformer. Repaired same day | 92 Smith Cemetery Road, Sidney, KY. | 2022-05-18
2019 | 2019-07-01 | Pikeville |  |  | 38821012A00224 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. (2) | 118 Willie Bevins Road, Sidney, KY. | 2019-07-01
2019 | 2019-07-01 | Pikeville |  |  | 38821012C00018 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , joint use attachments: clearance issues |  |  | KPC |  | Service drop sagged low. Also improper clearance from communications cables. | 99 Bogar Road, Sidney, KY.
2019 | 2019-07-01 | Pikeville |  |  | 38821012C00131 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. | 17690 East Big Creek Road, Sidney, KY. | 2019-07-01
2019 | 2019-07-01 | Pikeville |  |  | 38821012C00189 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. | Smith Cemetery Road, Sidney, KY. | 2019-07-01
2019 | 2019-07-01 | Pikeville | 84899745 | DKY0121589 | 38821012C00222 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC |  | Pole is completely engulfed in vines. | 17443 East Big Creek Road, Sidney, KY. | 2023-10-17
2019 | 2019-07-01 | Pikeville | 74329046 | DKY0106795 | 38821036B00027 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole washed out around in creek. | 1507 Rd Fork, Sidney, KY 41564, USA | 2019-12-04
2019 | 2019-07-01 | Pikeville |  |  | 38821036B10348 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | Unsure of ownership | 1029 Road Fork, Sidney, KY.
2019 | 2019-07-01 | Pikeville |  |  | 38821036C00036 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. | 1230 Dix Fork, Sidney, KY 41564, USA | 2019-07-01
2019 | 2019-07-01 | Pikeville |  |  | 38821060B00030 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. (2) | 3724 Dix Fork, Sidney, KY 41564, USA | 2019-07-01
2019 | 2019-07-01 | Pikeville |  |  | 38821060B00031 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker. | 3768 Dix Fork, Sidney, KY. | 2019-07-01
2019 | 2019-07-01 | Pikeville |  |  | 38821060D00025 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH | joint use attachments: clearance issues |  |  | Foreign |  | DirecTv | 3412 Dix Fork, Sidney, KY 41564, USA
2019 | 2019-07-02 | Pikeville |  |  | 38821013B00083 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. | Brunty Fork, Canada, KY 41519, USA | 2019-07-02
2019 | 2019-07-02 | Pikeville | 74737397 | DKY0106941 | 38821013B00093 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Secondary is sagged very low going to pole 370. Needs slack taken out. | 539 Brunty Fork, Canada, KY 41519, USA | 2022-05-18
2019 | 2019-07-02 | Pikeville |  |  | 38821013B00198 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | East Big Creek Road, Sidney, KY. | 2019-07-02
2019 | 2019-07-02 | Pikeville | 74329200 | DKY0106836 | 38821013B09003 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Lash secondary very low. Really long span. Needs pole in line to raise for clearance. @ sesco tanning. Takes off pole 198. | East Big Creek Road, Sidney, KY. | 2019-10-02
2019 | 2019-07-02 | Pikeville |  |  | 38821037A00163 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 630 Meathouse Fork. Sidney, KY. | 2019-07-02
2019 | 2019-07-02 | Pikeville |  |  | 38821037B00074 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | Service drop laying on roof. Needs slack taken out. Long drop, may need secondary pole. | 1286 Meathouse Fork, Sidney, KY.
2019 | 2019-07-02 | Pikeville |  |  | 38821037B00150 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Thacker Hollow, Meathouse Fork, Sidney, KY. | 2019-07-02
2019 | 2019-07-02 | Pikeville | 74739994 | DKY0106942 | 38821037C00048 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH |  |  |  | KPC |  | Neutral conductor down. From pole 46 to 48. Two spans. Can use truck on all but one pole. #4 copper wire. | Thornsberry Hollow, Pigeonroost Fork, Canada, KY. | 2020-03-10
2019 | 2019-07-02 | Pikeville |  |  | 38821037D00096 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 1720 Pigeonroost Fork, Canada, KY. | 2019-07-02
2019 | 2019-07-02 | Pikeville |  |  | 38821060D00075 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 2741 Stratton Fork, Meathouse Fork, Sidney, KY. | 2019-07-02
2019 | 2019-07-02 | Pikeville | 74739994 | DKY0106942 | 38821061A00097 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Secondary pole leaning. Needs to be straightened. Pole is tagged 177 but shows 97 on field view. Install: 1970 | 232 Daggs Branch, Meathouse Fork, Sidney. KY. | 2020-03-10
2019 | 2019-07-02 | Pikeville |  |  | 38821061B00045 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Meathouse Fork, Sidney, KY. | 2019-07-02
2019 | 2019-07-02 | Pikeville |  |  | 38821061C00154 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | May Hollow, Pigeonroost Fork, Canada, KY. | 2019-07-02
2019 | 2019-07-02 | Pikeville |  |  | 38831036D00235 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 1803 Stratton Fork, Meathouse Fork, Sidney, KY. | 2019-07-02
2019 | 2019-07-03 | Pikeville | 74799404 | DKY0107442 | 38821058B00029 | TRUE | 3411801-JOHNSCREE / META | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Crossarm deteoriated. | Meta Hwy. Pikeville, KY. | 2022-05-05
2019 | 2019-07-03 | Pikeville |  |  | 38821058B00030 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 9782 Meta Hwy, Pikeville, KY 41501, USA | 2019-07-03
2019 | 2019-07-03 | Pikeville |  |  | 38821058B00068 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | West Helena Avenue, Meta, KY. | 2019-07-03
2019 | 2019-07-03 | Pikeville | 81762498 | DKY0116333 | 38821058B00074 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 9458 Meta Hwy, Pikeville, KY 41501, USA | 2019-07-03
2019 | 2019-07-03 | Pikeville |  |  | 38821058C00112 |  | 3411801-JOHNSCREE / META | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign |  | Service drop hanging down pole. | 759 Smith Fork Rd, Pikeville, KY 41501, USA | 2019-07-03
2019 | 2019-07-03 | Pikeville |  |  | 38821058C00249 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 10835 Meta Lane, Meta, KY. | 2019-07-03
2019 | 2019-07-03 | Pikeville |  |  | 38821058D00351 |  | 3411801-JOHNSCREE / META | Line Work | OH | joint use attachments: clearance issues |  |  | Foreign |  |  | Scott Branch, Meta, KY. | 2020-02-25
2019 | 2019-07-03 | Pikeville |  |  | 38821082000070 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 33 S Blackburn Bottom, Pikeville, KY 41501, USA | 2019-07-03
2019 | 2019-07-03 | Pikeville |  |  | 38821082000108 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 95 N Blackburn Bottom, Pikeville, KY 41501, USA | 2019-07-03
2019 | 2019-07-03 | Pikeville | 74799404 | DKY0107442 | 38821083A00073 | TRUE | 3411801-JOHNSCREE / META | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Epoxilator melted down. | 65 Bevins Branch, Meta, KY. | 2022-05-05
2019 | 2019-07-03 | Pikeville |  |  | 38821083A00075 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 76 Lfk Bevins Branch, Meta, KY. | 2019-07-03
2019 | 2019-07-03 | Pikeville | 74799404 | DKY0107442 | 38821083B00039 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Epoxilators breaking down.@ Kellogg’s Plant. Pictures don’t show it very well. | State Hwy 194 East, Meta, KY. | 2022-05-05
2019 | 2019-07-03 | Pikeville |  |  | 38821083D00092 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator broken. First pole outside the STATION. Several epoxilators on this pole that are breaking down. | State Hwy 194 East, Meta, KY. | 2020-02-25
2019 | 2019-07-08 | Pikeville |  |  | 38821011B00015 |  | 3411801-JOHNSCREE / META | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole. | 1450 Bent Mountain Road, Pikeville, KY. | 2019-07-08
2019 | 2019-07-08 | Pikeville |  |  | 38821011B00027 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator broken. On hillside behind yellow & orange looking mobile home. Picture doesn’t show it very good but can be seen good with binoculars. | 2488 Brushy Road, Pikeville, KY. | 2020-02-25
2019 | 2019-07-08 | Pikeville |  |  | 38821035000237 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 362 Open Fork, Pikeville, KY 41501, USA | 2019-07-08
2019 | 2019-07-08 | Pikeville |  |  | 38821059000046 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 11618 Bent Branch Rd, Pikeville, KY 41501, USA | 2019-07-08
2019 | 2019-07-08 | Pikeville |  |  | 38821059000051 |  | 3411801-JOHNSCREE / META | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign |  | Service drop hanging down pole HOT. | 11718 Bent Branch Rd, Pikeville, KY 41501, USA | 2019-07-08
2019 | 2019-07-08 | Pikeville |  |  | 38821059000091 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Bear Road, Meta, KY. | 2019-07-08
2019 | 2019-07-09 | Pikeville |  |  | 38820986000032 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 4892 Lfk Brushy Road, Varney, KY. | 2019-07-09
2019 | 2019-07-09 | Pikeville | 74799857 | DKY0107537 | 38820986000068 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning significantly. Needs straightened. | Rye Straw Branch, Lfk Brushy Road, Varney, KY. | 2019-12-09
2019 | 2019-07-09 | Pikeville |  |  | 38821010000006 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Lfk Brushy Road, Pikeville, KY. | 2019-07-09
2019 | 2019-07-09 | Pikeville |  |  | 38821010000032 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 200 Stanley Fork, Rfk Brushy Road, Pikeville, KY. | 2019-07-09
2019 | 2019-07-09 | Pikeville |  |  | 38821010000069 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Lfk Brushy Road, Pikeville, KY. | 2019-07-09
2019 | 2019-07-09 | Pikeville | 74799857 | DKY0107537 | 38821010000096 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Lightning arrestor blown | 3093 Lfk Brushy Road, Pikeville, KY. | 2019-12-09
2019 | 2019-07-09 | Pikeville |  |  | 38821034000153 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen | Rfk Brushy Road, Pikeville, KY. | 2019-07-09
2019 | 2019-07-09 | Pikeville |  |  | 38821058A00395 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen . | Ford Mountain Road, Meta, KY. | 2019-07-09
2019 | 2019-07-09 | Pikeville |  |  | 38821058B00017 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 77 Deskins Rd, Pikeville, KY 41501, USA | 2019-07-09
2019 | 2019-07-09 | Pikeville |  |  | 38821058B00335 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Ford Mountain Road, Meta, KY. | 2019-07-09
2019 | 2019-07-10 | Pikeville |  |  | 38820937000033 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Curry Branch, Brushy Road, Varney, KY. | 2019-07-10
2019 | 2019-07-10 | Pikeville |  |  | 38820961000028 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Brushy Road, Varney, KY. | 2019-07-10
2019 | 2019-07-10 | Pikeville | 74799845 | DKY0107540 | 38820961000029 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  |  | KPC |  | Neutral conductor down. Also conductor hanging down pole from old lateral tap but it’s de-energized. #4 copper | 81 Rfk Brushy Road, Varney, KY. | 2020-01-02
2019 | 2019-07-10 | Pikeville | 74799845 | DKY0107540 | 38820961000039 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  |  | KPC |  | Neutral conductor down. #2 AA. Can use truck on one pole.@ about .7 mile up Rfk from the forks of Brushy. | Rfk Brushy Road, Varney, KY. | 2020-01-02
2019 | 2019-07-10 | Pikeville |  |  | 38820961000100 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 591 Rfk Brushy Road, Varney, KY. | 2019-07-10
2019 | 2019-07-10 | Pikeville | 74799845 | DKY0107540 | 38820985000059 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning considerably. Line is de-energized @ 38820985000057. Two spans. Last pole @ gas well. Install: 1982 | Little Branch, Rfk Brushy Road, Varney, KY. | 2020-01-02
2019 | 2019-07-10 | Pikeville |  |  | 38820985C30095 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. | 1875 Rfk Brushy Road, Varney, KY. | 2019-07-10
2019 | 2019-07-10 | Pikeville | 73866316 | 105809 | 38821009000010 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Neutral conductor down. Line is de-energized. Two span tap that could be removed. | Flutty Branch, Rfk Brushy Road, Varney, KY. | 2019-07-18
2019 | 2019-07-10 | Pikeville | 74799857 | DKY0107537 | 38821009000030 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Neutral conductor down. Last span of three span tap. Not currently serving any customers. Line should and could be De-energized @ take-off pole. Only one transformer on the tap and it’s open. | Flutty Branch, Rfk Brushy Road, Varney, KY. | 2019-12-09
2019 | 2019-07-11 | Pikeville | 74799877 | DKY0107525 | 38831031000049 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  |  | KPC |  | Neutral conductor down/ stolen. Can use truck on one pole. #4 copper wire | 1314 Hurts Branch, Gulnare, KY. | 2019-12-23
2019 | 2019-07-12 | Pikeville | 74799381 | DKY0107434 | 38821081D00004 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed same day. Guy wire hanging down pole. Can be removed. | 5986 Zebulon Hwy, Pikeville, KY 41501, USA | 2019-12-04
2019 | 2019-07-12 | Pikeville |  |  | 38821081D00006 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 6101 Zebulon Hwy, Pikeville, KY 41501, USA | 2019-07-12
2019 | 2019-07-12 | Pikeville |  |  | 38821081D00198 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 6157 Zebulon Hwy, Pikeville, KY 41501, USA | 2019-07-12
2019 | 2019-07-12 | Pikeville |  |  | 38821081D00213 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Zebulon Hwy, Pikeville, KY, USA | 2019-07-12
2019 | 2019-07-12 | Pikeville | 78780201 |  | 38821081D00220 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire rusted into. Needs new anchor buried and re-attached or it could be removed because it’s such a short span. | 6088 Zebulon Hwy, Pikeville, KY 41501, USA | 2022-05-06
2019 | 2019-07-12 | Pikeville |  |  | 38821081D00317 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 5900 Zebulon Hwy, Pikeville, KY. | 2019-07-12
2019 | 2019-07-12 | Pikeville | 74799381 | DKY0107434 | 38821082000055 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 802 Winn’s Branch, Zebulon, KY. | 2019-12-04
2019 | 2019-07-12 | Pikeville |  |  | 38821082000056 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Winn’s Branch, Zebulon, KY. | 2019-07-12
2019 | 2019-07-12 | Pikeville |  |  | 38821082000120 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  |  | Foreign |  | Neutral conductor down. #2 AA. No truck. | 164 Third Street, Winn’s Branch, Zebulon, KY. | 2020-02-25
2019 | 2019-07-12 | Pikeville |  |  | 38821082000133 |  | 3411801-JOHNSCREE / META | Service Work | OH |  |  |  | Foreign |  | Guy wire needs marker | Angela Street, Wynns Branch, Zebulon, KY. | 2019-07-12
2019 | 2019-07-12 | Pikeville | 74799381 | DKY0107434 | 38821105C00252 |  | 3411801-JOHNSCREE / META | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign |  | Service drop hanging down pole. Fresh dozed lot so customer might be needing service here. | 5342 Zebulon Hwy, Pikeville, KY 41501, USA | 2019-12-04
2019 | 2019-07-12 | Pikeville |  |  | 38821105C00336 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 5439 Zebulon Hwy, Pikeville, KY 41501, USA | 2019-07-12
2019 | 2019-07-12 | Pikeville |  |  | 38821106000064 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  |  | Foreign |  | Neutral conductor down/stolen. 1.2 mi up Winn’s Branch. | Winn’s Branch, Zebulon, KY. | 2020-02-25
2019 | 2019-07-15 | Pikeville | 74799833 | DKY0107441 | 38821033000049 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators are melting down.@ switch pole. | 3685 State Hwy 194 West, Pikeville, KY. | 2020-01-08
2019 | 2019-07-15 | Pikeville | 74800353 | DKY0107552 | 38821034000018 |  | 3411801-JOHNSCREE / META | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Low clearance on neutral conductor over building. Can remove enough slack for clearance I think in mid span. | 1309 Dry Branch , Hwy 194 West, Pikeville, KY. | 2020-02-05
2019 | 2019-07-15 | Pikeville |  |  | 38821057A00054 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Coal Hollow Road, Hwy 194 West, Pikeville, KY. | 2019-07-15
2019 | 2019-07-15 | Pikeville |  |  | 38821057A00226 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 145 Gross Hollow, Joe’s Creek, Pikeville, KY. | 2019-07-15
2019 | 2019-07-15 | Pikeville |  |  | 38821057A00294 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Coal Hollow Road, Hwy 194 West, Pikeville, KY. | 2019-07-15
2019 | 2019-07-15 | Pikeville |  |  | 38821057C00102 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 827 Dry Branch, Hwy 194 West, Pikeville, KY. | 2019-07-15
2019 | 2019-07-15 | Pikeville | 74799404 | DKY0107442 | 38821057C00103 |  | 3411801-JOHNSCREE / META | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Pole leaning/ guy wire hanging down pole. Needs to be re-attached. Probably will take Rock-eye. Angle pole. | 876 Dry Branch, Hwy 194 West, Pikeville, KY. | 2022-05-05
2019 | 2019-07-15 | Pikeville |  |  | 38821057D00158 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen | 111 Taylor Hill, Zebulon, KY. | 2019-07-15
2019 | 2019-07-15 | Pikeville |  |  | 38821081000066 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 261 wolfpen Hollow, Joes Creek, Pikeville, KY. | 2019-07-15
2019 | 2019-07-15 | Pikeville | 74799833 | DKY0107441 | 38821081B40345 |  | 3411801-JOHNSCREE / META | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down pole. Needs to be removed. | Wolfpen Hollow, Joes Creek, Pikeville, KY. | 2020-01-08
2019 | 2019-07-15 | Pikeville |  |  | 38831056D00213 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen. | Joes Creek, Pikeville, KY. | 2019-07-15
2019 | 2019-07-15 | Pikeville | 74799833 | DKY0107441 | 38831056D00254 |  | 3411801-JOHNSCREE / META | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole. All the way up to the transformer. Xformer not serving anything. | Joes Creek, Pikeville, KY. | 2020-01-08
2019 | 2019-07-16 | Pikeville |  |  | 38820985000040 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Gulnare, KY 41501, USA | 2019-07-16
2019 | 2019-07-16 | Pikeville | 74799857 | DKY0107537 | 38821009000028 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Pole top pin/ insulator bent back | 3610 Sycamore Creek, Gulnare, KY. | 2019-12-09
2019 | 2019-07-16 | Pikeville | 74799877 | DKY0107525 | 38831007D00055 |  | 3411801-JOHNSCREE / META | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarm brace broken. @ just below Sycamore. | 10954 KY-194, Gulnare, KY. | 2019-12-23
2019 | 2019-07-16 | Pikeville |  |  | 38831007D00144 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Sycamore Creek, Gulnare, KY. | 2019-07-16
2019 | 2019-07-16 | Pikeville | 74799877 | DKY0107525 | 38831008000023 |  | 3411801-JOHNSCREE / META | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground broken on transformer pole. | Maynard Fork, Sycamore Creek, Gulnare, KY. | 2019-12-23
2019 | 2019-07-16 | Pikeville |  |  | 38831008000024 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 117 Maynard Fork, Sycamore Creek, Gulnare, KY. | 2019-07-16
2019 | 2019-07-16 | Pikeville | 74799877 | DKY0107525 | 38831008000092 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator melting down. | 620 Maynard Fork, Sycamore Creek, Gulnare, KY. | 2019-12-23
2019 | 2019-07-16 | Pikeville |  |  | 38831031C10115 |  | 3411801-JOHNSCREE / META | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on step down transformer pole. | 26 Hurts Branch, Gulnare, KY. | 2019-07-16
2019 | 2019-07-17 | Pikeville |  |  | 38831056C00081 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 33 Stepp Branch, Hwy 194 West, Gulnare, KY. | 2019-07-17
2019 | 2019-07-17 | Pikeville | 74799833 | DKY0107441 | 38831056C00338 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  |  | KPC |  | Neutral conductor down. @ mouth of Millers Creek, turn right @ bridge. Go 1/4 mi. and cross tracks, go through gate. | Millers Creek, Gulnare, KY. | 2020-01-08
2019 | 2019-07-19 | Pikeville |  |  | 37830047D00166 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down. Not that bad right now. STATION ZONE. | Bob Amos Dr, Pikeville, KY 41501, USA
2019 | 2019-07-19 | Pikeville |  |  | 37830047D00175 |  | 3410502-S.PIKEVIL / ISLANDCRE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Bob Amos Dr, Pikeville, KY 41501, USA | 2019-07-19
2019 | 2019-07-19 | Pikeville | 83966882 | DKY0121091 | 37830048B40038 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down. STATION ZONE. Pole needs guy marker. Completed same day | Marion Branch Road, Pikeville, Ky
2019 | 2019-07-19 | Pikeville | 83966882 | DKY0121091 | 37830048B40183 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down. STATION ZONE. Installed guy marker. | Marion Branch Road, Pikeville, KY.
2019 | 2019-07-19 | Pikeville | 83966882 | DKY0121091 | 37830048B40185 | TRUE | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators melting down. 9 total. Hard to see in pictures. | 128 Island Creek Rd, Pikeville, KY 41501, USA
2019 | 2019-07-19 | Pikeville | 83966923 | DKY0121419 | 37830048B41142 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down | 167 Island Creek Rd, Pikeville, KY 41501, USA
2019 | 2019-07-19 | Pikeville |  |  | 38830048B11116 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators are melting. Not as bad as some but should be changed.. STATION ZONE INSIDE STATION FENCE. Pictures don’t really show very well but with binoculars you can see it. | S Mayo Trail, Pikeville, KY 41501, USA
2019 | 2019-07-22 | Pikeville |  |  | 37830047B00151 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down | 118 Nightingale Lane, Pikeville, KY.
2019 | 2019-07-22 | Pikeville |  |  | 37830047B00470 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown. @ just above Hoopwood Branch. | Rfk Island Creek, Pikeville, KY.
2019 | 2019-07-22 | Pikeville |  |  | 37830047B00519 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | Dish Network | 439 Hoopwood Branch, Rfk Island Creek, Pikeville, KY.
2019 | 2019-07-22 | Pikeville |  |  | 37830047D00032 |  | 3410502-S.PIKEVIL / ISLANDCRE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack. Needs tightened. Needs marker | 151 Nightingale Lane, Island Creek, Pikeville, KY. | 2019-07-22
2019 | 2019-07-22 | Pikeville |  |  | 37830047D10432 |  | 3410502-S.PIKEVIL / ISLANDCRE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Nightingale Lane, Pikeville, KY. | 2019-07-22
2019 | 2019-07-22 | Pikeville |  |  | 37830070000040 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  |  |  | KPC |  | 2 spans of neutral down. Can use truck on only one pole. Down between pole 40 and 42. #4 copper conductor. | 727 Keathley Branch, Rfk Toler Creek, Pikeville, KY.
2019 | 2019-07-22 | Pikeville | 76908000 | DKY0110179 | 37830071000026 | TRUE | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten. | 265 Coon Branch, Rfk Island Creek, Pikeville, KY.
2019 | 2019-07-22 | Pikeville |  |  | 37830071000106 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop laying on roof. Probably need secondary pole or change xformer pole to taller pole. | 575 Coon Branch, Rfk Island Creek, Pikeville, KY.
2019 | 2019-07-22 | Pikeville |  |  | 37830071000149 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning considerably. Has service drop low clearance. Needs side guy installed. No truck. Install: 1991 | 1136 Coon Branch, Island Creek, Pikeville, KY. | 2023-03-02
2019 | 2019-07-22 | Pikeville |  |  | 37830071000235 |  | 3410502-S.PIKEVIL / ISLANDCRE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 1203 Rfk Island Creek, Pikeville, KY. | 2019-07-22
2019 | 2019-07-22 | Pikeville |  |  | 37830071000264 |  | 3410502-S.PIKEVIL / ISLANDCRE | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down pole. | 478 Coon Branch, Island Creek, Pikeville, KY. | 2019-07-22
2019 | 2019-07-23 | Pikeville |  |  | 37830071000019 |  | 3410502-S.PIKEVIL / ISLANDCRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on switch pole. | 2482 Island Creek Rd, Pikeville, KY 41501, USA | 2019-07-23
2019 | 2019-07-23 | Pikeville | 83966923 | DKY0121419 | 37830072B00069 | TRUE | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down | 614 Lfk Island Creek, Pikeville, KY.
2019 | 2019-07-23 | Pikeville | 83966923 | DKY0121419 | 37830095000041 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down | 1528 Lfk Island Creek Road, Pikeville, KY. 41501
2019 | 2019-07-23 | Pikeville |  |  | 37830095000099 |  | 3410502-S.PIKEVIL / ISLANDCRE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Lfk Island Creek, Pikeville, KY. | 2019-07-23
2019 | 2019-07-24 | Pikeville |  |  | 37830095000073 | TRUE | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  |  |  | Foreign |  | Neutral conductor down/stolen. @ just above sleepy hollow. | Lfk Island Creek , Pikeville, KY. 41501 | 2023-10-11
2019 | 2019-07-25 | Pikeville |  |  | 37831101C20017 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Antique Lane, Stanville, KY. 41659 | 2019-07-25
2019 | 2019-07-25 | Pikeville | 74800121 | DKY0107547 | 38831101A00425 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | already written to EDN100577 KPC pole | Pole is rotten | Meade meadow lane, Stanville, KY. 41659 | 2020-01-20
2019 | 2019-07-25 | Pikeville |  |  | 38831101C10757 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole | Meade Meadow Lane, Stanville, KY. 41659 | 2019-07-25
2019 | 2019-07-25 | Pikeville | 74799162 | DKY0107413 | 38831101D10422 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Insulators broken on center and road phases. | Carmen Hollow Rd, Betsy Layne, KY, USA | 2020-07-23
2019 | 2019-07-26 | Pikeville | 74775118 | DKY0107031 | 38820992C00216 |  | 2150105-SPRIGG / MATEWAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | already written to EDN100577 KPC pole | Guy wire broken or rusted in two. pole leaning. Angle pole. Needs anchor installed and pole straightened.@. Pole just before fuse pole. | River Rd, Buskirk, Kentucky 41544, USA | 2020-01-23
2019 | 2019-07-26 | Pikeville | 74329182 | DKY0106779 | 38821016C00006 |  | 2150105-SPRIGG / MATEWAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Low clearance on service drop. Needs secondary pole installed. Servicer might be able to raise enough for clearance but I doubt it. | 159 River Road, Buskirk, KY. | 2020-01-22
2019 | 2019-07-26 | Pikeville |  |  | 38821016C00007 |  | 2150105-SPRIGG / MATEWAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | River Road, Buskirk, KY. | 2019-07-26
2019 | 2019-07-26 | Pikeville |  |  | 38821016C00009 |  | 2150105-SPRIGG / MATEWAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | River Road, Buskirk, KY. | 2019-07-26
2019 | 2019-07-26 | Pikeville |  |  | 38821016C00098 |  | 2150105-SPRIGG / MATEWAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | River Road, Buskirk, KY. | 2019-07-26
2019 | 2019-07-26 | Pikeville |  |  | 38821016C00103 |  | 2150105-SPRIGG / MATEWAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Spring Street, Buskirk, KY. | 2019-07-26
2019 | 2019-07-26 | Pikeville |  |  | 38821016C00115 |  | 2150105-SPRIGG / MATEWAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | River Rd, Buskirk, Kentucky 41544 | 2019-07-26
2019 | 2019-07-26 | Pikeville |  |  | 38821016C00199 |  | 2150105-SPRIGG / MATEWAN | Line Work | OH |  |  |  | KPC |  | #4 copper neutral down/stolen. 300 ft. Span. @ mouth of Lower Old House Branch. Might be able to use service truck when dry or frozen. | River Road, Buskirk, KY. | 2019-09-11
2019 | 2019-07-26 | Pikeville |  |  | 38821016C00280 |  | 2150105-SPRIGG / MATEWAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Huddle Street, Buskirk, KY. | 2019-07-26
2019 | 2019-07-26 | Pikeville |  |  | 38821016C00325 |  | 2150105-SPRIGG / MATEWAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | River Road, Buskirk, KY. | 2019-07-26
2019 | 2019-07-26 | Pikeville | 74775118 | DKY0107031 | 38821017A10124 |  | 2150105-SPRIGG / MATEWAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarm brace broken | River Street, Buskirk, KY. | 2020-01-23
2019 | 2019-07-26 | Pikeville |  |  | 38821017A10342 |  | 2150105-SPRIGG / MATEWAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | Ash wood Court, Buskirk, KY. | 2019-07-26
2019 | 2019-07-26 | Pikeville |  |  | 38821017A20386 |  | 2150105-SPRIGG / MATEWAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Bowling Road, Buskirk, KY. | 2019-07-26
2019 | 2019-07-26 | Pikeville |  |  | 38821017A20459 |  | 2150105-SPRIGG / MATEWAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Radio Hill Street, Buskirk, KY. | 2019-07-26
2019 | 2019-07-29 | Pikeville | 74800371 | DKY0108271 | 38831100B30306 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , joint use attachments: clearance issues |  |  | KPC |  | Service drop is laying across phone cable | 386 Spurlock Fork, Dana, KY. | 2020-03-23
2019 | 2019-07-29 | Pikeville | 74799162 | DKY0107413 | 38831101D20330 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators are melting down. Pictures don’t show it very well. | Hidden View Drive, Salem Church Rd, Harold, KY 41635, USA | 2020-07-23
2019 | 2019-07-29 | Pikeville |  |  | 38831124A00076 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 1269 Spurlock Fork, Dana, KY. | 2019-07-29
2019 | 2019-07-29 | Pikeville |  |  | 38831124B30300 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 152 Lfk Samson Fork, Dana, KY. | 2019-07-29
2019 | 2019-07-29 | Pikeville |  |  | 38831124C00184 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 5912 KY-1426, Dana, KY 41615, USA | 2019-07-29
2019 | 2019-07-29 | Pikeville | 74799120 | DKY0107360 | 38831125A00257 |  |  | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down | 60 Tanyard Hollow, Harold, KY 41635, USA | 2021-10-30
2019 | 2019-07-29 | Pikeville |  |  | 38831125A00292 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 6160 Sammy Clark Branch Rd, Harold, KY 41635, USA | 2019-07-29
2019 | 2019-07-29 | Pikeville |  |  | 38831125A00386 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. route 2030, Harold, KY. | 2019-07-29
2019 | 2019-07-29 | Pikeville | 74799120 | DKY0107360 | 38831125A00478 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged , guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Epoxilators melting down. | 50 Preachers Dr, Harold, KY 41635, USA | 2021-10-30
2019 | 2019-07-29 | Pikeville | 74799120 | DKY0107360 | 38831125A00522 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down. @ Capacitor bank pole | State Hwy 1426, Harold, KY. | 2021-10-30
2019 | 2019-07-29 | Pikeville | 74799162 | DKY0107413 | 38831125C10497 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Crossarm is deteoriated/split.. On step down pole | Salem Church Rd, Harold, KY 41635, USA | 2020-07-23
2019 | 2019-07-29 | Pikeville |  |  | 38831125C10969 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Salem Church Rd, Harold, KY 41635, USA | 2019-07-29
2019 | 2019-07-29 | Pikeville | 74799123 | DKY0107388 | 38831125C30010 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators are melting down. | Salem Church Rd, Harold, KY 41635, USA | 2022-05-11
2019 | 2019-07-29 | Pikeville |  |  | 3i831125C30007 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Salem Church Rd, Harold, KY 41635, USA | 2019-07-29
2019 | 2019-07-30 | Pikeville |  |  | 38831052A00071 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 181 Crum Branch, Banner, KY. 41649 | 2019-07-30
2019 | 2019-07-30 | Pikeville |  |  | 38831052B00158 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 211 S Rice Rd, Banner, KY 41603, USA | 2019-07-30
2019 | 2019-07-30 | Pikeville |  |  | 38831052D00119 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 504 Green Hall Branch, Banner, KY. 41603 | 2019-07-30
2019 | 2019-07-30 | Pikeville |  |  | 38831076000058 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 650 LfkOrchard Branch , Banner, KY. | 2019-07-30
2019 | 2019-07-30 | Pikeville | 74799135 | DKY0107359 | 38831076000064 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melted down.@ switch pole @ mouth of Cecil Branch. Across Creek. Probably use truck if dry or frozen. | 3011 KY-1426, Banner, KY 41603, USA | 2022-08-29
2019 | 2019-07-30 | Pikeville |  |  | 38831076000102 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 349 Water Birch Rd, Banner, KY 41603, USA | 2019-07-30
2019 | 2019-07-30 | Pikeville |  |  | 38831076000128 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 679 Orchard Branch, Banner, KY. | 2019-07-30
2019 | 2019-07-30 | Pikeville | 74799135 | DKY0107359 | 38831100000126 | TRUE | 3120101-STANVILLE/MUD CREEK | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down pole | Lynn Hollow, Hunts Fork, Dana, KY. | 2022-08-29
2019 | 2019-07-30 | Pikeville |  |  | 38831100000270 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Liberty Lane, Hunts Fork, Dana, KY. | 2019-07-30
2019 | 2019-07-30 | Pikeville | 74799120 | DKY0107360 | 38831125A00521 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators are melting down. @ in curve above Pikeville sportsman club. Vertical angle pole. | KY-1426, Harold, KY, USA | 2021-10-30
2019 | 2019-08-05 | Pikeville |  |  | 38831124D00123 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Big Branch, Little Mud Creek, Honaker, KY. | 2019-08-05
2019 | 2019-08-05 | Pikeville | 74799093 | DKY0107343 | 38831124D20327 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining | Forestry - DESCRIBE IN COMMENTS | KPC |  | Tree has layed over on secondary and caused the pole to lean considerably. | 393 Big Branch, Little Mud Creek, Honaker. KY. | 2019-12-17
2019 | 2019-08-05 | Pikeville | 74799120 | DKY0107360 | 38831125B00180 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators deteoriated/ melting. @ step down pole on Little Mud Creek. Also has lightning arrestor blown. | KY. Route 2030, Honaker, KY. | 2021-10-30
2019 | 2019-08-05 | Pikeville | 74799093 | DKY0107343 | 38831125B00635 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melted/deteoriated. @ Regulator pole on Little Mud Creek. | KY. Route 2030, Honaker, KY. | 2019-12-17
2019 | 2019-08-05 | Pikeville | 74799093 | DKY0107343 | 38831125B00655 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator deteoriated/ melting down.@ just past step down on little mud creek. | KY. Route 2030, Honaker, KY. | 2019-12-17
2019 | 2019-08-05 | Pikeville |  |  | 38831125B00656 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 2030, Honaker, KY. | 2019-08-05
2019 | 2019-08-05 | Pikeville |  |  | 38831148000159 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Bridge, 454 Spruce Pine Branch, Honaker, KY 41603, USA | 2019-08-05
2019 | 2019-08-05 | Pikeville |  |  | 38831148000251 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Little Mud Creek, Honaker, KY. | 2019-08-05
2019 | 2019-08-05 | Pikeville |  |  | 38831148000288 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 6340. KY. 2030, Honaker, KY. | 2019-08-05
2019 | 2019-08-06 | Pikeville |  |  | 38831125C10147 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Barn Branch Rd, Harold, KY 41635, USA | 2019-08-06
2019 | 2019-08-06 | Pikeville |  |  | 38831125C20788 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Old Harold Rd, Harold, KY 41635, USA | 2019-08-06
2019 | 2019-08-06 | Pikeville | 74800390 | DKY0107654 | 38831125C20796 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , joint use attachments: clearance issues |  |  | KPC |  | Secondary is laying on Phone cable. | Old Harold Rd, Harold, KY 41635, USA | 2020-01-14
2019 | 2019-08-06 | Pikeville | 74799123 | DKY0107388 | 38831125C30017 | TRUE | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators deteoriated/ melting. May be able to use truck if dry or frozen. | Track Road, Harold, KY. | 2022-05-11
2019 | 2019-08-06 | Pikeville |  |  | 38831125C30021 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Rfk Track Road, Harold, KY. 41635 | 2019-08-06
2019 | 2019-08-06 | Pikeville |  |  | 38831125C30135 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack. Needs tightened. | Hale Rd, Harold, KY 41635, USA | 2019-08-06
2019 | 2019-08-06 | Pikeville |  |  | 38831125C30141 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 979, Harold, KY. | 2019-08-06
2019 | 2019-08-06 | Pikeville |  |  | 38831125C30146 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Barn Branch Rd, Harold, KY 41635, USA | 2019-08-06
2019 | 2019-08-06 | Pikeville |  |  | 38831125C30293 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 34 Rfk Track Road, Harold, KY. | 2019-08-06
2019 | 2019-08-06 | Pikeville | 74799123 | DKY0107388 | 38831125C40039 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting/ deteoriated. @ Harold Hill. | 112 Old Harold Rd, Harold, KY 41635, USA | 2022-05-11
2019 | 2019-08-06 | Pikeville | 74799123 | DKY0107388 | 38831125C40409 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators deteoriated/ melting. Crossarm also looks to be deteoriated somewhat. @ RR CROSSING AT HAROLD | Track Road, Harold, KY. | 2022-05-11
2019 | 2019-08-06 | Pikeville |  |  | 38831125D00064 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Mellow Brook Ln, Kentucky 41635, USA | 2019-08-06
2019 | 2019-08-06 | Pikeville |  |  | 38831125D00073 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 73 Amba Lane, Harold, KY. 41635 | 2019-08-06
2019 | 2019-08-06 | Pikeville |  |  | 38831125D00421 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Dwayne and Brenda Drive, Harold, KY. 41635 | 2019-08-06
2019 | 2019-08-06 | Pikeville |  |  | 38831125D00428 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY-979, Harold, KY, USA | 2019-08-06
2019 | 2019-08-06 | Pikeville | 75145390 | DKY0107487 | 38831149000014 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  |  | KPC |  | #4 copper neutral down/ stolen. Also pole top pin bent over. | King Drive, Toler Creek, Harold, KY. 41635 | 2023-02-15
2019 | 2019-08-06 | Pikeville | 74799093 | DKY0107343 | 38831149000043 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole. Stolen all the way up to the transformer. | Clark Branch, Harold, KY. 41635 | 2019-12-17
2019 | 2019-08-06 | Pikeville | 74799093 | DKY0107343 | 38831149000044 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Anchor pulled out. Guy wrapped around pole. Need to install new anchor and reattach. | 3297 KY-979, Harold, KY 41635, USA | 2019-12-17
2019 | 2019-08-06 | Pikeville |  |  | 38831149B20305 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Webster Akers Cemetery Road, Harold, KY. 41635 | 2019-08-06
2019 | 2019-08-07 | Pikeville |  |  | 37830021000168 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Sturgill Branch, Toler Creek, Harold, KY. 41635 | 2019-08-07
2019 | 2019-08-07 | Pikeville |  |  | 37830021000219 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Sturgill Branch, Toler Creek, Harold, KY. 41635 | 2019-08-07
2019 | 2019-08-07 | Pikeville | 74799074 | DKY0107492 | 37830022000007 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy washed out and hanging down the pole. Guy needed marker. | 2677 Toler Creek Rd, Harold, KY 41635, USA | 2023-01-23
2019 | 2019-08-07 | Pikeville | 74321019 |  | 37830022000142 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down pole. | 171 S Floyd Hollow, Lfk Toler Creek, Harold, KY. 41635 | 2019-08-20
2019 | 2019-08-07 | Pikeville | WR 74224302 |  | 37830022000235 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Secondary pole is broken. Not serving anything. Transformer is de-energized. Could probably be removed or needs to be replaced. Probably can use line truck and drive in front of trailer with owner permission but no one currently living there. Contacted supervisor and pole was replaced on 8-9-19 by Rick Ray. | 2799 Toler Creek Rd, Harold, KY 41635, USA | 2019-08-09
2019 | 2019-08-07 | Pikeville | 74800098 | DKY0107520 | 37830046000142 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole top has been burnt. Install: 1986 | 4065 Toler Creek Rd, Harold, KY 41635, USA | 2020-02-27
2019 | 2019-08-07 | Pikeville | 74799074 | DKY0107492 | 38831149000022 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators deteoriated/melting.@ mouth of Gearheart Branch. Might be able to get off road enough to do without flaggers. | 1400 Toler Creek Rd, Harold, KY 41635, USA | 2023-01-23
2019 | 2019-08-09 | Pikeville |  |  | 37830139C00136 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. 979, Hi hat, KY. | 2019-08-09
2019 | 2019-08-09 | Pikeville |  |  | 37830139C00156 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Very long service drop. Customer has propped up with a board going over his roof. I think enough slack could be taken out for clearance but might need to install secondary pole since it’s so long. | Newman Branch, Clear Creek, KY. 979, Hi hat, KY.
2019 | 2019-08-09 | Pikeville |  |  | 37830139C00287 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | KY-979, Hi hat , KY. | 2019-08-09
2019 | 2019-08-09 | Pikeville |  |  | 37830140B00223 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on capacitor bank | KY. ROUTE 979, Hi hat, KY. | 2019-08-09
2019 | 2019-08-09 | Pikeville | 86143711 |  | 37830140B20381 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | (2) pole grounds stolen on step down pole. | Osborne Fork, Clear Creek, Hi hat, KY. 41636
2019 | 2019-08-09 | Pikeville | 86143711 |  | 37830140B20382 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on recloser pole. | Osborne Fork, Clear Creek, Hi hat, KY. 41636
2019 | 2019-08-09 | Pikeville |  |  | 37830140D00314 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 16371 KY. 979, Hi hat, KY. | 2019-08-09
2019 | 2019-08-09 | Pikeville | 81400408 | DKY0115870 | 37830140D40335 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive pole. Drop hanging down pole | 156 Moore Branch, Beaver, KY 41604, USA | 2022-01-25
2019 | 2019-08-12 | Pikeville |  |  | 37830117000160 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Tackett Fork, Beaver, KY 41604, USA | 2019-08-12
2019 | 2019-08-12 | Pikeville |  |  | 37830117000213 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Andy Branch, Kentucky 41660, USA | 2019-08-12
2019 | 2019-08-12 | Pikeville |  |  | 37830117000229 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Tackett Fork, Beaver, KY 41604, USA | 2019-08-12
2019 | 2019-08-12 | Pikeville |  |  | 37830141000030 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop hanging down pole | Smokey Branch, Tinkerfork, Beaver, KY. | 2019-08-12
2019 | 2019-08-12 | Pikeville |  |  | 37830141000037 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Tackett Fork, Beaver, KY 41604, USA | 2019-08-12
2019 | 2019-08-12 | Pikeville |  |  | 37830141000083 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Tackett Fork, Beaver, KY 41604, USA | 2019-08-12
2019 | 2019-08-12 | Pikeville |  |  | 37830142000012 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Smokey Branch, Tinkerfork, Beaver, KY. | 2019-08-12
2019 | 2019-08-13 | Pikeville | 86143149 |  | 37830021000103 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator melting down | 227 Newman's Branch, Grethel, KY 41631, USA
2019 | 2019-08-13 | Pikeville |  |  | 37830021000172 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground cut on transformer pole | Branhams Creek, Grethel, KY. | 2019-08-13
2019 | 2019-08-13 | Pikeville |  |  | 37830021B10277 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | Satellites on pole | 174 Newman's Branch, Grethel, KY 41631, USA
2019 | 2019-08-13 | Pikeville |  |  | 37830021B40257 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 6310 KY-979, Grethel, KY 41631, USA | 2019-08-13
2019 | 2019-08-13 | Pikeville |  |  | 37830045D40319 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 132 Nathan Carroll Dr, Grethel, KY 41631, USA | 2019-08-13
2019 | 2019-08-13 | Pikeville |  |  | 37830093000313 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down pole | 267 Adkins Branch, KY. Route 3379, Grethel, KY. | 2023-10-11
2019 | 2019-08-13 | Pikeville |  |  | 37830094000011 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 5549 KY. Route 3379, Grethel, KY. | 2019-08-13
2019 | 2019-08-13 | Pikeville | 86143129 |  | 37830094000120 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | Secondary sagged low. Pole and secondary can be removed or secondary needs to be sagged higher. Secondary is caught off with rope. | 6611 KY. 3379 , Grethel, KY,
2019 | 2019-08-14 | Pikeville |  |  | 37830068000065 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire hanging down pole. Needs to be reattached. No anchor in sight. Probably need to install anchor. Will be in customer yard. | 4000 KY-680, Grethel, KY 41631, head Hamilton Br where DW burned
2019 | 2019-08-14 | Pikeville |  |  | 37830069000001 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack. Needs tightened. | Dark Hollow, Grethel, KY. | 2023-10-11
2019 | 2019-08-14 | Pikeville | 86143149 |  | 37830069000002 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown | 8322 KY-979, Grethel, KY 41631, USA
2019 | 2019-08-14 | Pikeville | 86143149 |  | 37830069000003 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown | 8418 KY-979, Grethel, KY 41631, USA
2019 | 2019-08-14 | Pikeville |  |  | 37830069000011 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 8970 KY-979, Teaberry, KY 41660, USA | 2019-08-14
2019 | 2019-08-14 | Pikeville |  |  | 37830069000033 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Mink Branch, Teaberry, KY. | 2019-08-14
2019 | 2019-08-14 | Pikeville |  |  | 37830069000231 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Dark Hollow, Grethel, KY. | 2019-08-14
2019 | 2019-08-14 | Pikeville |  |  | 37830069000280 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole grounds stolen on step down transformer bank. (2) | 619 Mink Branch, Craynor, KY 41635, USA | 2019-08-14
2019 | 2019-08-14 | Pikeville |  |  | 37830069C10314 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Akers Branch, Grethel, KY. 41631 | 2019-08-14
2019 | 2019-08-14 | Pikeville |  |  | 37830139A40238 | TRUE | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 122, Hi hat, KY. | 2019-08-14
2019 | 2019-08-14 | Pikeville | 77025342 | DKY0110454 | 37830139A40238 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole is burnt. | 17618 KY-122, Hi Hat, KY 41636, USA | 2021-10-29
2019 | 2019-08-15 | Pikeville |  |  | 37830091B00119 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Cherokee Road, McDowell, KY. | 2019-08-15
2019 | 2019-08-15 | Pikeville | 78659493 | DKY0112522 | 37830114C00005 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH |  |  |  | Foreign |  | Pole is completely covered in kudzu vines. | 104 Buckeye Branch, Price, KY. | 2021-02-15
2019 | 2019-08-15 | Pikeville | 81402086 | DKY0115878 | 37830114C00007 | TRUE | 3403202-BEAVER CRK / PRICE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten | 272 Buckeye Branch, Price, KY. | 2023-06-20
2019 | 2019-08-15 | Pikeville |  |  | 37830115000110 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Frazier Ln, McDowell, KY 41636, USA | 2019-08-15
2019 | 2019-08-15 | Pikeville | 86143791 |  | 37830115000127 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown | 16229 KY-122, Hi Hat, KY 41636, USA
2019 | 2019-08-15 | Pikeville | 76958335 | DKY0110326 | 37830115000161 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole has a hole burnt into it. | 246 Tunnel Road, Price, KY. | 2022-08-22
2019 | 2019-08-15 | Pikeville | 80985890 | DKY0115316 | 37830139A10061 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire hanging down pole. Could be removed. | North Locust Road, Hi hat, KY. | 2022-01-25
2019 | 2019-08-15 | Pikeville |  |  | 37830139A30128 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 83 Creekside Dr, Hi Hat, KY 41636, USA | 2019-08-15
2019 | 2019-08-15 | Pikeville |  |  | 37830139A40389 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole | S Locust Rd, Hi hat, KY. | 2019-08-15
2019 | 2019-08-16 | Pikeville | 78433238 | DKY0112101 | 37830116000019 |  | McKINNEY - GIBSON / 4022-02 | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Primary conductor is down . It’s de-energized though. Should be put back up or removed entirely. | Toby Branch, Frazier Creek, McDowell, KY. | 2020-12-29
2019 | 2019-08-26 | Pikeville |  |  | 37830091B00287 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 12931 KY-122, Hi Hat, KY 41636, USA | 2019-08-26
2019 | 2019-08-26 | Pikeville | 86143674 |  | 37830115000057 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. About 15 ft. Up. | Spewing Camp Branch Rd, McDowell, KY, USA
2019 | 2019-08-26 | Pikeville |  |  | 37830115000153 | TRUE | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Spewing Camp Branch, McDowell, KY, USA | 2019-08-26
2019 | 2019-08-26 | Pikeville |  |  | 37830115000153 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 1586 Spewing Camp Branch, McDowell, KY. | 2019-08-26
2019 | 2019-08-26 | Pikeville | 86143674 |  | 37830115000202 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole. About 20 ft up. | Spewing Camp Branch, McDowell, KY, USA
2019 | 2019-08-27 | Pikeville | 81829315 | DKY0116404 | 38831074A00614 |  | 3408103-SALISBURY / MARTIN | Line Work | OH | service: unused or abandoned, blanked meter base |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer and service hanging down pole. | Joel Crisp Branch, Bucks Branch, Martin, KY. 41649 | 2022-05-03
2019 | 2019-08-27 | Pikeville |  |  | 38831074B00609 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Shelton Hollow, Bucks Branch, Martin, KY. 41649 | 2019-08-27
2019 | 2019-08-27 | Pikeville |  |  | 38831074C00235 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 737 Cracker Bottom, Martin, KY. 41649 | 2019-08-27
2019 | 2019-08-27 | Pikeville |  |  | 38831074C00316 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC |  | Pole is smothered by vines. | Bucks Branch, Martin, KY 41649, USA | 2023-10-19
2019 | 2019-08-27 | Pikeville |  |  | 38831074C00328 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Broad Hollow, Bucks Branch, Martin, KY. 41649 | 2019-08-27
2019 | 2019-08-27 | Pikeville |  |  | 38831074C00537 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | Cracker Bottom, Martin, KY. 41649 | 2019-08-27
2019 | 2019-08-27 | Pikeville |  |  | 38831074D00704 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | KY. Route 80, Martin, KY. 41649 | 2019-08-27
2019 | 2019-08-27 | Pikeville |  |  | 38831074D21072 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 80, Martin, KY. 41649 | 2019-08-27
2019 | 2019-08-27 | Pikeville |  |  | 38831098A00764 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Stephens Branch, Martin, KY 41649, USA | 2019-08-27
2019 | 2019-08-27 | Pikeville |  |  | 38831098C10927 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 80, Martin, KY. 41649 | 2019-08-27
2019 | 2019-08-28 | Pikeville |  |  | 38831097C30112 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Stephens Branch, Martin, KY. | 2019-08-28
2019 | 2019-08-28 | Pikeville |  |  | 38831098A00300 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Stephens Branch, Martin, KY. | 2019-08-28
2019 | 2019-08-28 | Pikeville |  |  | 38831098C00012 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 521 Dinwood, Martin, KY. | 2019-08-28
2019 | 2019-08-28 | Pikeville |  |  | 38831098C00580 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Ward Lane, Dinwood, Martin, KY. | 2019-08-28
2019 | 2019-08-29 | Pikeville | 79687775 | DKY0113736 | 38831097000089 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Anchor appears to have been washed out or dozed out. Angle pole. Should be put back. Probably need to install anchor to reattach guy. | 1392 Johns Branch above OCR Langley, KY 41645 | 2021-09-07
2019 | 2019-08-29 | Pikeville | 78736931 |  | 38831098B00070 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC |  | Pole covered in vines | 153 Warco Rd, Langley, KY 41645, USA | 2021-02-06
2019 | 2019-08-29 | Pikeville |  |  | 38831098B00448 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 80, Maytown, KY. | 2019-08-29
2019 | 2019-08-29 | Pikeville | 85780232 | DKY0121780 | 38831098C00468 |  | 3408103-SALISBURY / MARTIN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten..@ behind Total Pharmacy. | 98 Triangle Street, Martin, KY 41649, USA
2019 | 2019-08-29 | Pikeville |  |  | 38831098C00470 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Triangle Street, Martin, KY. 41649 | 2019-08-29
2019 | 2019-08-29 | Pikeville |  |  | 38831098C00491 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Main St, Martin, KY 41649, USA | 2019-08-29
2019 | 2019-08-29 | Pikeville |  |  | 38831098C00496 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 98 Triangle Street, Martin, KY 41649, USA | 2019-08-29
2019 | 2019-08-29 | Pikeville |  |  | 38831098C00702 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Beaver Valley Rd, Martin, KY 41649, USA | 2019-08-29
2019 | 2019-08-29 | Pikeville | 84551400 | DKY0119911 | 38831122000164 | TRUE | 3408103-SALISBURY / MARTIN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten | 1204 Henry’s Branch, Langley, KY. | 2023-03-14
2019 | 2019-08-29 | Pikeville |  |  | 38831146000203 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 1696 Henry’s Branch, Langley, KY. | 2019-08-29
2019 | 2019-08-30 | Pikeville |  |  | 38831074C00093 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Crossarms deteoriated/rotten. @ in front of post office. | Main St, Martin, KY 41649, USA | 2023-03-02
2019 | 2019-08-30 | Pikeville |  |  | 38831074C00116 |  | 3408103-SALISBURY / MARTIN | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground broken on transformer pole | N River St, Martin, KY 41649, USA | 2019-08-30
2019 | 2019-08-30 | Pikeville |  |  | 38831074D00007 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Chestnut St, Martin, KY 41649, USA | 2019-08-30
2019 | 2019-08-30 | Pikeville |  |  | 38831074D00014 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Clinic Dr, Martin, KY 41649, USA | 2019-08-30
2019 | 2019-08-30 | Pikeville |  |  | 38831074D00385 |  | 3408103-SALISBURY / MARTIN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten/hollow | Ruthie Daniels Drive, Martin, KY. | 2023-03-02
2019 | 2019-08-30 | Pikeville |  |  | 38831074D00410 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Elm Street, Martin, KY. | 2019-08-30
2019 | 2019-08-30 | Pikeville |  |  | 38831074D00511 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Ice Plant Hollow, Kentucky 41649, USA | 2019-08-30
2019 | 2019-08-30 | Pikeville |  |  | 38831074D00583 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Clinic Dr, Martin, KY 41649, USA | 2019-08-30
2019 | 2019-09-03 | Pikeville |  |  | 37830018000052 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 122, Drift, KY. | 2019-09-03
2019 | 2019-09-03 | Pikeville |  |  | 37830018000233 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Stumbo Hollow, Drift, KY. | 2019-09-03
2019 | 2019-09-03 | Pikeville |  |  | 37830018D00104 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Rfk Cow Hollow, Drift, KY. | 2019-09-03
2019 | 2019-09-03 | Pikeville | 76957117 | DKY0110216 | 37830018D00216 | TRUE | 3402202-MCKINNEY / GIBSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | YES | Pole is rotten. Also needs guy marker. Completed marker. | Lfk Cow Hollow, Drift, KY. | 2021-10-01
2019 | 2019-09-03 | Pikeville | 83985332 | DKY0118883 | 37830019B00041 | TRUE | 3402202-MCKINNEY / GIBSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | crossarm/braces: deteriorated, not rotten |  | Foreign | YES | Crossarm rotten/deteoriated. Top of pole rotten/split. Pole seems to be good other than the top. | 33 Upper Lane Siding Station, Drift, KY 41619, USA | 2023-06-19
2019 | 2019-09-03 | Pikeville |  |  | 38830019B20138 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 1101, Drift, KY. 41619 | 2019-09-03
2019 | 2019-09-04 | Pikeville |  |  | 37830024D00444 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 122, Minnie, KY. | 2019-09-04
2019 | 2019-09-04 | Pikeville |  |  | 37830042C00302 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 8057 KY-122, Printer, KY 41655, USA | 2019-09-04
2019 | 2019-09-04 | Pikeville |  |  | 37830042C00346 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Remove unused/ inactive service drop hanging down pole. De-energized. 4/0 conductor. 3 phase service. | 8164 KY-122, Minnie KY. Former battery repair industry below intersection.
2019 | 2019-09-04 | Pikeville |  |  | 37830042C00391 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | KY. Route 680 W, McDowell, KY. | 2019-09-04
2019 | 2019-09-04 | Pikeville |  |  | 37830042C00419 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY-122, McDowell, KY, USA | 2019-09-04
2019 | 2019-09-04 | Pikeville |  |  | 37830042C00448 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Parkview Dr, McDowell, KY 41619, USA | 2019-09-04
2019 | 2019-09-04 | Pikeville |  |  | 37830042C30523 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 122, Drift, KY. | 2019-09-04
2019 | 2019-09-04 | Pikeville | 82375270 |  | 37830042C40556 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Conductors sagged low. Low clearance. I think enough slack can be taken out to gain proper clearance. | Parkview Dr, Minnie, KY 41619 | 2022-05-24
2019 | 2019-09-04 | Pikeville |  |  | 37830042D00290 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Isom Moore Branch, Minnie, KY. | 2019-09-04
2019 | 2019-09-04 | Pikeville | 86180888 |  | 37830042D00349 | TRUE | 3402202-MCKINNEY / GIBSON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown | Sizemore Rd, McDowell, KY
2019 | 2019-09-04 | Pikeville |  |  | 37830042D00443 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | KY. Route 122, Minnie, KY. | 2019-09-04
2019 | 2019-09-04 | Pikeville |  |  | 37830042D00445 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 122, Minnie, KY. | 2019-09-04
2019 | 2019-09-04 | Pikeville | 78476719 | DKY0112504 | 37830066A00029 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | STOLEN NEUTRAL | KPC |  | 2 spans neutral stolen/missing. #4 copper wire. @ about half way up Sizemore mtn. Road crossing. | KY. Route 1086, McDowell, KY. | 2021-02-04
2019 | 2019-09-04 | Pikeville |  |  | 37830066C00154 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Glory Lane, Minnie, KY. | 2019-09-04
2019 | 2019-09-05 | Pikeville |  |  | 37830066C00037 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 9634 KY-122, Minnie, KY 41651, USA | 2019-09-05
2019 | 2019-09-05 | Pikeville |  |  | 37830066C00201 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 9688 KY-122, Minnie, KY 41651, USA | 2019-09-05
2019 | 2019-09-05 | Pikeville |  |  | 37830066D00015 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole | Doty Branch, McDowell, KY. | 2019-09-05
2019 | 2019-09-05 | Pikeville |  |  | 37830067A00018 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Johnson Rd, McDowell, KY, USA | 2019-09-05
2019 | 2019-09-05 | Pikeville |  |  | 37830067A00023 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Johnson Road, McDowell, KY. | 2019-09-05
2019 | 2019-09-05 | Pikeville |  |  | 37830067A00082 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 9813 KY-122, Minnie, KY 41651, USA | 2019-09-05
2019 | 2019-09-05 | Pikeville | 76957254 | DKY0110330 | 37830067A00102 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | other: customer owned attachment | KPC | YES | Pole is burnt at top. Also has satellite dish on pole. | 10653 KY-122, McDowell, KY 41647, USA | 2020-12-18
2019 | 2019-09-05 | Pikeville |  |  | 37830067A00338 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Customer has built a building around our pole. | Johnson Rd, McDowell, KY, USA | 2021-04-29
2019 | 2019-09-05 | Pikeville |  |  | 37830067A00405 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Halbert Ln, McDowell, KY 41647, USA | 2019-09-05
2019 | 2019-09-05 | Pikeville | 81211201 | DKY0115556 | 37830067B00122 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Conductors low clearance. Probably need pole in line. May be able to get enough slack out of wire to raise enough for clearance. | KY-122, McDowell, KY, off Big Bridge Rd | 2022-01-20
2019 | 2019-09-05 | Pikeville |  |  | 37830090C30133 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. | Doty Branch, McDowell, KY. | 2019-09-05
2019 | 2019-09-06 | Pikeville |  |  | 37830067A00002 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole | 221 May St, McDowell, KY 41647, USA | 2019-09-06
2019 | 2019-09-06 | Pikeville |  |  | 37830067A00011 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs insulator. Also needs marker. Installed marker . | May St, McDowell, KY 41647, USA
2019 | 2019-09-06 | Pikeville |  |  | 37830067A00067 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | KY-680, McDowell, KY, USA | 2019-09-06
2019 | 2019-09-06 | Pikeville |  |  | 37830067A00268 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY-680, McDowell, KY, USA | 2019-09-06
2019 | 2019-09-06 | Pikeville |  |  | 37830067A00410 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Glen Ward Ln, McDowell, KY 41647, USA | 2019-09-06
2019 | 2019-09-06 | Pikeville | 78714635 |  | 37830067C00407 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | Service drop laying on roof top. I think enough slack can be taken out of the drop to correct the clearance. | 779 Middle Branch, McDowell, KY 41647, USA | 2021-01-29
2019 | 2019-09-06 | Pikeville | 78713935 |  | 37830091C00102 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Remove inactive/unused service drop crossing the road. Low clearance. | Gearheart Branch, Frazier’s Creek, McDowell, KY. | 2021-01-29
2019 | 2019-09-06 | Pikeville |  |  | 37830091C00153 |  | 3402202-MCKINNEY / GIBSON | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC |  | Pole is completely covered in kudzu vines.Also pole 286 is covered with kudzu. They’re next to each other. | Gearheart Branch, Frazier’s Creek, McDowell, KY. | 2020-06-25
2019 | 2019-09-06 | Pikeville |  |  | 37830116000036 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  |  | KPC |  | Neutral conductor down/missing. #4 copper wire. Near head Ned’s Fork. On right on hillside. | Ned’s Fork, Frazier’s Creek, McDowell, KY.
2019 | 2019-09-09 | Pikeville |  |  | 38831101C10765 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | US-23, Stanville, KY 41659, USA | 2019-09-09
2019 | 2019-09-09 | Pikeville |  |  | 38831101C30628 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 258 Lower Hollow, Betsy Layne, KY 41605, USA | 2019-09-09
2019 | 2019-09-09 | Pikeville |  |  | 38831101C40140 |  | 3120103-STANVILLE/HAROLD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC |  | Pole covered with vines | 103 Lower Hollow, Betsy Layne, KY 41605, USA | 2020-05-05
2019 | 2019-09-09 | Pikeville |  |  | 38831101C40226 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole | Store Hollow, Betsy Layne, KY 41605, USA | 2019-09-09
2019 | 2019-09-09 | Pikeville |  |  | 38831101C40411 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Pike Floyd Hollow, Betsy Layne, KY, USA | 2019-09-09
2019 | 2019-09-09 | Pikeville | 74799184 | DKY0107350 | 38831101C40559 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  |  | conductors: excessive splices, deteriorated conductors | KPC |  | Lash secondary has come unwrapped and sagging. | 162 Pike Floyd Hollow, Betsy Layne, KY 41605, USA | 2019-12-03
2019 | 2019-09-09 | Pikeville | 74799184 | DKY0107350 | 38831101C40560 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker , conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | Service has been rolled up on pole. Needs slack cut out. Service is active account. Pole also needs guy marker. Completed guy marker. @ storage units. | 189 Pike Floyd Hollow, Betsy Layne, KY 41605, USA | 2019-12-03
2019 | 2019-09-09 | Pikeville |  |  | 38831101C40563 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator broken on step down pole. There’s a few more that are deteoriated on this pole also. | School St, Betsy Layne, KY 41605, USA | 2020-03-03
2019 | 2019-09-09 | Pikeville |  |  | 38831101C40609 |  | 3120103-STANVILLE/HAROLD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Pole ground stolen on step down transformer pole. And guy wire needs marker. | Pike Floyd Hollow, Betsy Layne, KY, USA | 2019-09-09
2019 | 2019-09-09 | Pikeville |  |  | 38831101C40713 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on recloser pole | George Rd, Betsy Layne, KY 41605, USA | 2019-09-09
2019 | 2019-09-09 | Pikeville |  |  | 38831101C40718 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Railroad Cir, Betsy Layne, KY 41605, USA | 2019-09-09
2019 | 2019-09-09 | Pikeville |  |  | 38831101D40368 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Bee Jack Ln, Betsy Layne, KY 41605, USA | 2019-09-09
2019 | 2019-09-09 | Pikeville |  |  | 38831102000021 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | N Stoney Brook Dr, Betsy Layne, KY, USA | 2019-09-09
2019 | 2019-09-09 | Pikeville |  |  | 38831102000255 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on step down transformer pole | Pike Floyd Hollow, Betsy Layne, KY, USA | 2019-09-09
2019 | 2019-09-10 | Pikeville |  |  | 38831101D40728 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | Coldwater Branch, Kentucky 41635, USA | 2019-09-10
2019 | 2019-09-10 | Pikeville |  |  | 38831125C40095 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 12194 US-23, Harold, KY 41635, USA | 2019-09-10
2019 | 2019-09-10 | Pikeville |  |  | 38831125C40097 |  | 3120103-STANVILLE/HAROLD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole | U.S. 23 South, Harold, Ky. | 2019-09-10
2019 | 2019-09-10 | Pikeville |  |  | 38831125C40615 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen on step down transformer | Old County Road, Harold, Ky. 41635 | 2019-09-10
2019 | 2019-09-10 | Pikeville |  |  | 38831125C40675 |  | 3120103-STANVILLE/HAROLD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole | 23 Old County Rd, Harold, KY 41635, USA | 2019-09-10
2019 | 2019-09-10 | Pikeville |  |  | Number Not Entered |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | U.S. 23 South, Harold, Ky. | 2019-09-10
2019 | 2019-09-11 | Pikeville |  |  | 38831125C40926 |  | 3120103-STANVILLE/HAROLD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground cut on transformer pole. | Right Penhook Rd, Harold, KY 41635, USA | 2019-09-11
2019 | 2019-09-11 | Pikeville |  |  | 38831125D00120 |  | 3120103-STANVILLE/HAROLD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole | Penhook Plains Road, Harold, Ky. 41635 | 2019-09-11
2019 | 2019-09-11 | Pikeville |  |  | 38831125D00122 |  | 3120103-STANVILLE/HAROLD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole | Penhook Plains Road, Harold, Ky. 41635 | 2019-09-11
2019 | 2019-09-11 | Pikeville |  |  | 38831126A00694 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 318 Right Penhook Road, Harold, Ky. | 2019-09-11
2019 | 2019-09-11 | Pikeville | 74799229 | DKY0107415 | 38831126B10056 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators melting down | 73 Damron Lane, Hurricane Creek, Harold, Ky. 41635 | 2019-11-28
2019 | 2019-09-11 | Pikeville |  |  | 38831126B10153 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 4th Street, Fox Bottom, Harold, Ky. 41635 | 2019-09-11
2019 | 2019-09-11 | Pikeville |  |  | 38831126B10186 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Hurricane Road, Harold, Ky. 41635 | 2019-09-11
2019 | 2019-09-11 | Pikeville |  |  | 38831126B10443 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 11 Campbell Ln, Pikeville, KY 41501, USA | 2019-09-11
2019 | 2019-09-11 | Pikeville |  |  | 38831150000079 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Spring Branch, Hurricane Creek, Pikeville, Ky. 41501 | 2019-09-11
2019 | 2019-09-11 | Pikeville | 74799229 | DKY0107415 | 38831150000187 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilator melting down | Spring Branch, Hurricane Creek, Pikeville, Ky. 41501 | 2019-11-28
2019 | 2019-09-12 | Pikeville | 74799205 | DKY0107374 | 38831126A00533 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Epoxilators are melting/deteoriated.@ in front of Mayhorns. | Deskins Drive, Pikeville, Ky. 41501 | 2023-06-16
2019 | 2019-09-12 | Pikeville |  |  | 38831150000014 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Hurricane Creek Rd, Kentucky 41501, USA | 2019-09-12
2019 | 2019-09-12 | Pikeville |  |  | 38831150000034 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 3600 Hurricane Creek Road, Pikeville, Ky. 41501 | 2019-09-12
2019 | 2019-09-12 | Pikeville | 74799229 | DKY0107415 | 38831150000035 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Neutral conductor down/stolen/missing. @ takeoff pole for Davis Road. Guy wire also broken. #4 copper wire. No truck on one pole. | 3540 Hurricane Creek Rd,Pikeville, Kentucky 41501, USA | 2019-11-28
2019 | 2019-09-12 | Pikeville |  |  | 38831150000178 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 375 Davis Road, Hurricane Creek, Pikeville, Ky. 41501 | 2019-09-12
2019 | 2019-09-13 | Pikeville | 74799205 | DKY0107374 | 38831102000145 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators deteoriated/ melting. Might be able to use truck if dry.@ behind trailer #12 | 620 Venters Ln, Pikeville, KY 41501, USA | 2023-06-16
2019 | 2019-09-13 | Pikeville |  |  | 38831102000146 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Venters Lane, Pikeville, Ky. 41501 | 2019-09-13
2019 | 2019-09-13 | Pikeville | 74799205 | DKY0107374 | 38831102000147 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown. Might be able to use truck if dry. | 620 Venters Ln, Pikeville, KY 41501, USA | 2023-06-16
2019 | 2019-09-13 | Pikeville |  |  | 38831102000190 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Senator Kelsey E Friend Blvd, Pikeville, KY 41501, USA | 2019-09-13
2019 | 2019-09-13 | Pikeville |  |  | 38831126A00106 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | 7734 N Mayo Trail, Pikeville, KY 41501, USA | 2019-09-13
2019 | 2019-09-13 | Pikeville |  |  | 38831126A00188 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire broken. Hanging down pole. | 7234 N Mayo Trail, Pikeville, KY 41501, USA | 2020-03-03
2019 | 2019-09-13 | Pikeville |  |  | 38831126C10947 | TRUE | 3120103-STANVILLE/HAROLD | Line Work | UG | UG conduit: damaged or separated |  |  | KPC |  | Poly pad for pad mount transformer is damaged. Transformer tilted.@ Venters Lane Habitat for humanity homes. | 29 Crossrock Ct, Pikeville, KY 41501, USA
2019 | 2019-09-16 | Pikeville |  |  | 38831027B00080 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 111 Main St, Allen City, KY 41601, USA | 2019-09-16
2019 | 2019-09-16 | Pikeville |  |  | 38831027D00228 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | N 2nd St, Allen City, KY 41601, USA | 2019-09-16
2019 | 2019-09-16 | Pikeville |  |  | 38831051000020 |  | 3400101-ALLEN / DISTRIBUTION | Line Work | UG |  | transformers: leaking, damaged |  | KPC |  | Underground junction box/ switch gear is damaged. It’s labeled as 1027-715 in the field but field view shows it as 1051-20. It’s beside of secondary pole 38831051000068 in the field. Next to walking track behind the golf course. | Oklahoma Hollow, Allen, Ky. 41601
2019 | 2019-09-18 | Pikeville |  |  | 38831003D00011 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY-1428, Allen City, KY, USA | 2019-09-18
2019 | 2019-09-18 | Pikeville | 86497873 | DKY0122937 | 38831003D00015 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY-1428, Allen City, KY, USA | 2019-09-18
2019 | 2019-09-18 | Pikeville |  |  | 38831003D00060 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | KY-1428, Allen City, KY, USA | 2019-09-18
2019 | 2019-09-18 | Pikeville |  |  | 38831003D00069 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Woods Lane, Allen, Ky. | 2019-09-18
2019 | 2019-09-18 | Pikeville | 76371951 | DKY0110393 | 38831003D00129 | TRUE | 3400101-ALLEN / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Epoxilator melting/deteoriated. | Mosley Branch, ky. 1428, Allen, Ky. | 2022-03-30
2019 | 2019-09-18 | Pikeville |  |  | 38831027A00209 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Hill Drive, Dwale, Ky. | 2019-09-18
2019 | 2019-09-18 | Pikeville |  |  | 38831027C00138 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | Monument Drive , Dwale, Ky. 41621 | 2019-09-18
2019 | 2019-09-18 | Pikeville |  |  | 38831027C00165 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Railroad Street, Dwale, Ky. | 2019-09-18
2019 | 2019-09-18 | Pikeville |  |  | 38831027C00546 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Nelson Drive, Dwale, Ky. 41621 | 2019-09-18
2019 | 2019-09-18 | Pikeville |  |  | 38831027C00654 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | N River Street, Dwale, Ky. | 2019-09-18
2019 | 2019-09-18 | Pikeville |  |  | 38831027C00658 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack and needs marker. | Monument Dr, Kentucky 41621, USA | 2019-09-18
2019 | 2019-09-19 | Pikeville |  |  | 38831027C00389 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Bridge Branch Road, Allen, Ky. | 2019-09-19
2019 | 2019-09-19 | Pikeville |  |  | 38831027C00497 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | New Allen Hill, Allen, Ky. 41601 | 2019-09-19
2019 | 2019-09-19 | Pikeville |  |  | 38831027D00374 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Bridge Branch Road, Allen, Ky. | 2019-09-19
2019 | 2019-09-19 | Pikeville |  |  | 38831028000002 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | U. S. Hwy. 23 South, Banner, Ky. | 2019-09-19
2019 | 2019-09-19 | Pikeville |  |  | 38831052A00327 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | U.S. 23 South, Banner, Ky. | 2019-09-19
2019 | 2019-09-19 | Pikeville |  |  | 38831052C00190 |  | 3400101-ALLEN / DISTRIBUTION | Line Work | OH | guys/anchors: broken or missing | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire rusted off. Needs to be reattached. Needs marker | U.S. 23 South, Banner, Ky. | 2019-09-19
2019 | 2019-09-20 | Pikeville | 75670851 | DKY0108273 | 37830163D00053 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Regulator pole leaning. Might want to install anchor and side guy. First pole outside Burton station. Install: 2000 | Upper Burton, Ky. Route 122, Wheelwright, Ky. 41650
2019 | 2019-09-20 | Pikeville | 79832808 | DKY0113890 | 37830187C00199 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Secondary pole leaning. Needs to be straightened. Probably need anchor and guy installed. On hillside just above Freewill Baptist Church. Install: 1978 | 257 KY-306, Bypro, KY 41669 | 2021-08-02
2019 | 2019-09-20 | Pikeville |  |  | 37830211C00343 |  | 3400602-BURTON / WHEELWRIG | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Main Street, Wheelwright, Ky. | 2019-09-20
2019 | 2019-09-20 | Pikeville | 76958453 | DKY0111432 | 37830211C00365 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten | 2063 Ky. 306, Wheelwright, Ky. | 2020-12-18
2019 | 2019-09-20 | Pikeville |  |  | 37830211D00035 |  | 3400602-BURTON / WHEELWRIG | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Stoker Branch Rd, Wheelwright, KY 41669, USA | 2019-09-20
2019 | 2019-09-20 | Pikeville |  |  | 37831087D00228 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten | 984 Main Street, Wheelwright, Ky. | 2020-06-17
2019 | 2019-09-23 | Pikeville |  |  | 37830188A00005 |  | 3400602-BURTON / WHEELWRIG | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Orchard Branch, Melvin, KY 41650, USA | 2019-09-23
2019 | 2019-09-23 | Pikeville |  |  | 37830188A00045 |  | 3400602-BURTON / WHEELWRIG | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 22524 KY-122, Bypro, KY 41612, USA | 2019-09-23
2019 | 2019-09-23 | Pikeville | 76958719 | DKY0111457 | 37830188B00117 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | YES | Pole is rotten. Guy needs marker. Completed marker. | Hen Pen Branch, Melvin, Ky. | 2021-11-06
2019 | 2019-09-23 | Pikeville |  |  | 37830188C00012 |  | 3400602-BURTON / WHEELWRIG | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack.. needs tightened. Needs marker. | Harris Hollow, Abner Fork Melvin, Ky. | 2019-09-23
2019 | 2019-09-24 | Pikeville |  |  | 37830163B00272 |  | 3400601-BURTON / LIGON-CLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Caudill Ln, Kentucky 41606, USA | 2019-09-24
2019 | 2019-09-24 | Pikeville |  |  | 37830163B00313 |  | 3400601-BURTON / LIGON-CLE | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Inactive service drop hanging down pole. De-energized. Should be removed. | Riley’s Branch, Bypro, Ky. 41612 | 2023-10-11
2019 | 2019-09-24 | Pikeville |  |  | 37830163C00218 |  | 3400601-BURTON / LIGON-CLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Riley’s Branch, Bypro, Ky. | 2019-09-24
2019 | 2019-09-24 | Pikeville |  |  | 37830163D00168 |  | 3400601-BURTON / LIGON-CLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Lower Burton, Bypro, Ky. | 2019-09-24
2019 | 2019-09-25 | Pikeville |  |  | 37830187A00355 |  | 3400601-BURTON / LIGON-CLE | Line Work | OH |  | pole: leaning, burned more than 50% remaining | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive secondary pole leaning pretty bad. Has tree on secondary. Needs to be straightened or removed. Secondary is de-energized. Behind house with cedar siding and green roof on left. Install: 1994 | 1113 Jacks Creek, Halo, Ky.
2019 | 2019-09-27 | Pikeville |  |  | 37820008A00146 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Big Branch, Calloway, Phelps, Ky. | 2019-09-27
2019 | 2019-09-27 | Pikeville |  |  | 37820008A00147 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Big Branch, Calloway, Phelps, Ky. | 2019-09-27
2019 | 2019-09-27 | Pikeville | 78750807 | DKY0112651 | 38821111D00012 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH | cutout: damaged |  |  | Foreign |  | Cutout is hanging straight down. Probably need to replace. Won’t be able to re-fuse as is.@ behind a garage. Truck access??? | Garden Spring Road, Lfk Blackberry, Ransom, Ky. | 2022-04-04
2019 | 2019-09-27 | Pikeville |  |  | 38821111D00015 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 3347 Lfk Blackberry, Ransom, Ky. | 2019-09-27
2019 | 2019-09-27 | Pikeville |  |  | 38821111D00195 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down pole. Should be removed | 3121 Lfk Blackberry, Ransom, Ky. | 2019-09-27
2019 | 2019-09-27 | Pikeville |  |  | 38831111D00106 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 3305 Lfk Blackberry, Ransom, Ky. | 2019-09-27
2019 | 2019-09-30 | Pikeville |  |  | 38821063D00137 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Dials Branch, Ransom, Ky. 41558 | 2019-09-30
2019 | 2019-09-30 | Pikeville | 84481985 | DKY0119792 | 38821064B00042 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire rusted in two at ground. Needs anchor installed. Can drill. Single phase angle pole. Secured guy to pole and cut off excess. | 585 Dials Branch, Ransom, Ky.
2019 | 2019-09-30 | Pikeville |  |  | 38821064B00086 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Neutral conductor stolen/ missing. 6A copper conductor. 600 ft. Span. | 1090 Dials Branch, Ransom, KY 41558, USA
2019 | 2019-09-30 | Pikeville |  |  | 38821064B00279 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 6126 ky. Hwy. 1056 Ransom, Ky. | 2019-09-30
2019 | 2019-09-30 | Pikeville |  |  | 38821064B40162 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 5730 State Hwy 1056, Ransom, Ky. | 2019-09-30
2019 | 2019-09-30 | Pikeville |  |  | 38821088A00154 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Big blue springs road, Ransom, Ky. | 2019-09-30
2019 | 2019-09-30 | Pikeville |  |  | 38821088B00121 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH | joint use attachments: clearance issues |  |  | Foreign |  | Phone company guy is broken and flipped up close to our primary conductor. Wrapped around pole. About .5 mi. up big blue springs Branch . | Big Blue Spring Branch, Ransom, Ky. | 2023-01-26
2019 | 2019-09-30 | Pikeville |  |  | 38821112C00156 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 1555 Big blue springs Branch, Ransom, Ky. | 2019-09-30
2019 | 2019-10-01 | Pikeville |  |  | 38821111B00094 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Upper Blackberry Rd, Ransom, Ky. 41558 | 2019-10-01
2019 | 2019-10-01 | Pikeville |  |  | 38821111B00094 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Upper Blackberry Rd, Ransom, Ky. 41558 | 2019-10-01
2019 | 2019-10-01 | Pikeville |  |  | 38821111B00094 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Upper Blackberry Rd, Ransom, Ky. 41558 | 2019-10-01
2019 | 2019-10-01 | Pikeville |  |  | 38821111B00094 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Upper Blackberry Rd, Ransom, Ky. 41558 | 2019-10-01
2019 | 2019-10-01 | Pikeville |  |  | 38821111B00094 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Upper Blackberry Rd, Ransom, Ky. 41558 | 2019-10-01
2019 | 2019-10-02 | Pikeville |  |  | 37820008C00008 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker (2) | State highway 632, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville |  |  | 37820008C00107 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | State Highway 632, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville |  |  | 37820008C00107 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | State Highway 632, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville |  |  | 37820008C00107 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | State Highway 632, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville |  |  | 37820008C00107 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | State Highway 632, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville |  |  | 37820008C00107 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | State Highway 632, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville |  |  | 37820008C00107 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | State Highway 632, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville |  |  | 37820008C10034 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | Calloway Road, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville |  |  | 37820008C10034 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | Calloway Road, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville |  |  | 37820008C30371 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Inactive service drop hanging down pole. De-energized./ XFR has been worked with WR # 82379521/DKY0117038 | State highway 632, Phelps, Ky. | 2022-05-25
2019 | 2019-10-02 | Pikeville | 82379521 | DKY0117038 | 37820009A00215 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive 3 phase tap beginning at pole 37820008C00333. There’s wire down in multiple places from there till the end of the tap. Several poles leaning badly. Metering pole is gone. Don’t know if it was removed by company persons or possibly stolen. Entire tap is de-energized at pole 37820008C00170 . | Bluestone Energy Coal Group, State Hwy 632, Phelps, Ky. | 2022-05-25
2019 | 2019-10-02 | Pikeville |  |  | 38821136D00010 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | State highway 632, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville |  |  | 38821136D00010 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | State highway 632, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville |  |  | 38821136D00010 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | State highway 632, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville |  |  | 38821136D00010 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | State highway 632, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville |  |  | 38821136D00010 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | State highway 632, Phelps, Ky. | 2019-10-02
2019 | 2019-10-02 | Pikeville | 84876355 | DKY0120988 | 38821136D00061 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten below ground. | 11890 State Hwy 632, Phelps, Ky.
2019 | 2019-10-02 | Pikeville | 82445355 | DKY0117083 | 38821137B00650 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive secondary pole. | 12714 State Hwy 632, Phelps, Ky. | 2022-06-27
2019 | 2019-10-02 | Pikeville |  |  | 38821137B00742 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | 4/0 lash service drop hanging down pole and laying on ground. It’s de-energized but needs to be removed. @ behind Phelps fire dept. I stapled it to the pole and cut off and removed the excess on the ground. | Maple Street, Phelps, Ky. | 2022-05-25
2019 | 2019-10-03 | Pikeville |  |  | 37820006000091 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Dinky Road, State Hwy 632, Kimper, Ky. | 2019-10-03
2019 | 2019-10-03 | Pikeville |  |  | 37820007D00050 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Remove inactive line beginning @ 37820007D00050 down to pole 37820007D00043. There’s wire hanging down pole in both places. It’s the end of the Coleman /Calloway circuit where it meets Coleman/Peter Creek about half mile before Smith Fork.//Wire was replace for service to mines/...DJM | State Highway 632, Phelps, Ky. | 2022-05-20
2019 | 2019-10-03 | Pikeville |  |  | 38821134000001 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Pond Fork, Kimper, Ky. | 2019-10-03
2019 | 2019-10-03 | Pikeville |  |  | 38821134000001 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Pond Fork, Kimper, Ky. | 2019-10-03
2019 | 2019-10-03 | Pikeville |  |  | 38821134000001 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Pond Fork, Kimper, Ky. | 2019-10-03
2019 | 2019-10-03 | Pikeville |  |  | 38821134000025 |  | 3408304-COLEMAN / CALLOWAY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Inactive service drop hanging down pole. Removed service. | Pond Fork, Kimper, Ky. | 2019-10-03
2019 | 2019-10-03 | Pikeville |  |  | 38821136D00042 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Carter Branch, Phelps, Ky. | 2019-10-03
2019 | 2019-10-03 | Pikeville |  |  | 38821136D00043 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Carter Branch, Phelps, Ky. | 2019-10-03
2019 | 2019-10-03 | Pikeville |  |  | 38821136D00052 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Carter Branch, Phelps, Ky. | 2019-10-03
2019 | 2019-10-14 | Pikeville |  |  | 37820008D00021 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Pole ground stolen on transformer pole. Guy wire needs marker | Smith Fork Rd, Phelps, KY, USA | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820008D00021 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Pole ground stolen on transformer pole. Guy wire needs marker | Smith Fork Rd, Phelps, KY, USA | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820008D00026 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Smith Fork Road, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820008D00026 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Smith Fork Road, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820008D00026 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Smith Fork Road, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820008D00026 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Smith Fork Road, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820008D00027 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire slack. (2)Needs marker. (2) | Smith Fork Road, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820008D00072 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 275 Low Gap Hlw., Smith Fork, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820008D00079 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. Completed guy marker. Satellite dish on pole. Directv | 17 Low Gap Hlw, Smith Fork Road, Phelps, Ky. | 2023-02-06
2019 | 2019-10-14 | Pikeville |  |  | 37820031C00011 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack. Needs marker (2) | Ash lick Fork, Smith Fork Road, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820032A00038 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole | Cow Branch, Smith Fork, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820032A00038 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole | Cow Branch, Smith Fork, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820032A00038 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole | Cow Branch, Smith Fork, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820032A00051 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire slack. Needs marker | Cow Branch, Smith Fork, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820032A00051 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire slack. Needs marker | Cow Branch, Smith Fork, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820032A00051 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire slack. Needs marker | Cow Branch, Smith Fork, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820032A00124 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on step down transformer pole. | Smith Fork, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820032A00155 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Ash lick Fork, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820032A00155 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Ash lick Fork, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820032A00155 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Ash lick Fork, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820032A00155 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Ash lick Fork, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville | 84101102 | DKY0118978 | 37820032B00025 | TRUE | 3408303-COLEMAN / PETERCRK | Line Work | OH |  |  |  | Foreign |  | Neutral conductor missing/stolen. (2) Long spans #4 copper. Truck to one pole. No truck on 2 other poles. Near head Smith Fork going up the hill. | Smith Fork Road, Phelps, Ky. | 2023-02-01
2019 | 2019-10-14 | Pikeville |  |  | 37820032C00002 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Smith Fork Road, Phelps, Ky. | 2019-10-14
2019 | 2019-10-14 | Pikeville |  |  | 37820032C00047 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Hensley Hollow, Smith Fork Road, Phelps, Ky. | 2019-10-14
2019 | 2019-10-15 | Pikeville |  |  | 38821113B00197 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 39180 State Hwy 194 East, Phelps, Ky. | 2019-10-15
2019 | 2019-10-15 | Pikeville |  |  | 38821113B00258 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | State Hwy 194 East, Phelps, Ky. | 2019-10-15
2019 | 2019-10-15 | Pikeville |  |  | 38821113B00258 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | State Hwy 194 East, Phelps, Ky. | 2019-10-15
2019 | 2019-10-15 | Pikeville |  |  | 38821113B00258 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | State Hwy 194 East, Phelps, Ky. | 2019-10-15
2019 | 2019-10-15 | Pikeville |  |  | 38821137A00123 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Belle Street, Phelps, Ky. | 2019-10-15
2019 | 2019-10-15 | Pikeville |  |  | 38821137A00123 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Belle Street, Phelps, Ky. | 2019-10-15
2019 | 2019-10-15 | Pikeville |  |  | 38821137A00123 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Belle Street, Phelps, Ky. | 2019-10-15
2019 | 2019-10-15 | Pikeville |  |  | 38821137A00330 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Ky. Hwy 632, Phelps, Ky. | 2019-10-15
2019 | 2019-10-15 | Pikeville |  |  | 38821137C30784 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down pole. De-energized | Bone Branch, Phelps, Ky. | 2019-10-15
2019 | 2019-10-16 | Pikeville |  |  | 37820009C00044 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Phillips Branch, Jamboree, Ky. | 2019-10-16
2019 | 2019-10-16 | Pikeville |  |  | 37820009C00047 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Phillips Branch, Jamboree, Ky. | 2019-10-16
2019 | 2019-10-16 | Pikeville |  |  | 37820009C00047 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Phillips Branch, Jamboree, Ky. | 2019-10-16
2019 | 2019-10-16 | Pikeville | 86180779 |  | 37820009C00048 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole | 320 Phillips Branch, Jamboree, Ky.
2019 | 2019-10-16 | Pikeville | 77011408 | DKY0110362 | 38821137C40645 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten. | 363 Mereda Branch, Phelps, Ky. | 2020-12-11
2019 | 2019-10-16 | Pikeville |  |  | 38821137C40797 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Merda Branch, Phelps, Ky. | 2019-10-16
2019 | 2019-10-16 | Pikeville |  |  | 38821137C40797 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Merda Branch, Phelps, Ky. | 2019-10-16
2019 | 2019-10-16 | Pikeville |  |  | 38821137C40797 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Merda Branch, Phelps, Ky. | 2019-10-16
2019 | 2019-10-16 | Pikeville |  |  | 38821137D00306 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Mereda Branch, Phelps, Ky. | 2019-10-16
2019 | 2019-10-16 | Pikeville |  |  | 38821137D00685 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | Mereda Branch, Phelps, Ky. | 2019-10-16
2019 | 2019-10-16 | Pikeville | 84411419 | DKY0119607 | 38821138C00068 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign |  | Crossarm brace broken. Just before the open point with Barrenshee/Vulcan circuit. | 3017 Widow Branch, State Hwy 2062, Stopover, Ky. | 2023-11-08
2019 | 2019-10-16 | Pikeville |  |  | 38821138D00139 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down pole energized. De-energized xformer and removed drop. | 109 Hamilton Branch, Widows Branch, Stopover, Ky. | 2019-10-16
2019 | 2019-10-17 | Pikeville |  |  | 37820009D00067 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820009D00068 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820009D00068 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville | 84317676 | DKY0119434 | 37820009D00142 | TRUE | 3408303-COLEMAN / PETERCRK | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign |  | Crossarm brace broken. Just before Cam mining haul road. | State Hwy 194 East, Jamboree, Ky. | 2023-02-09
2019 | 2019-10-17 | Pikeville |  |  | 37820009D00238 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | State Hwy 194 East, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820009D00241 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820009D00241 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820009D00241 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820009D00241 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville | 84398086 | DKY0119584 | 37820032C00070 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Lightning arrestor blown. Can truck if dry. | 2265 Beech Creek, Jamboree, Ky.
2019 | 2019-10-17 | Pikeville |  |  | 37820033A00041 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820033A00041 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820033A00041 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820033A00041 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820033A00048 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820033A00048 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820033A00048 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Beech Creek, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820033D00013 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | 34249 State Hwy 194 East, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-17 | Pikeville |  |  | 37820057A00050 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 32450 State Hwy 194 East, Jamboree, Ky. | 2019-10-17
2019 | 2019-10-21 | Pikeville |  |  | 37820055A40005 | TRUE | 3403801-SECONDFOR / DISTRIBUTION | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen.@ 3rd pole out of station. | Second Fork, Biggs, Ky.
2019 | 2019-10-21 | Pikeville | 84452216 | DKY0119682 | 37820078000252 |  | 3403801-SECONDFOR / DISTRIBUTION | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Cutout broke/ hanging down pole. @ mouth of First Fork. Also could remove secondary pole 37820078000253 which is tapped off pole 252. | Big Creek, Biggs, Ky. | 2023-06-28
2019 | 2019-10-21 | Pikeville | 86180703 |  | 37820079000125 | TRUE | 3403801-SECONDFOR / DISTRIBUTION | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen. | Second Fork, Biggs, Ky.
2019 | 2019-10-22 | Pikeville |  |  | 37820053000313 |  | 3414901-FISHTRAP / DISTRIBUTION | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. | Island Creek, Phyllis, Ky. 41554 | 2019-10-22
2019 | 2019-10-22 | Pikeville |  |  | 37820053000313 |  | 3414901-FISHTRAP / DISTRIBUTION | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. | Island Creek, Phyllis, Ky. 41554 | 2019-10-22
2019 | 2019-10-22 | Pikeville |  |  | 37820053000313 |  | 3414901-FISHTRAP / DISTRIBUTION | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. | Island Creek, Phyllis, Ky. 41554 | 2019-10-22
2019 | 2019-10-22 | Pikeville |  |  | 37820053000313 |  | 3414901-FISHTRAP / DISTRIBUTION | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. | Island Creek, Phyllis, Ky. 41554 | 2019-10-22
2019 | 2019-10-24 | Pikeville |  |  | 37820220C20355 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Laura Ann Ln, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville |  |  | 37820220C20355 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Laura Ann Ln, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville |  |  | 37820220C20355 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Laura Ann Ln, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville |  |  | 37820220C40025 |  | 3421002-BREAKS/GRASSY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole | Lower Branch Rd, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville |  |  | 37820220C40025 |  | 3421002-BREAKS/GRASSY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole | Lower Branch Rd, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville |  |  | 37820220C40025 |  | 3421002-BREAKS/GRASSY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole | Lower Branch Rd, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville | 86180754 |  | 37820220C40361 |  | 3421001-BREAKS/CITY | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole. May need to install new ground rod. Could not find it. | Lower Branch Rd, Elkhorn City, KY 41522, USA
2019 | 2019-10-24 | Pikeville |  |  | 37820220C40496 |  | 3421001-BREAKS/CITY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole | Ohio St, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville |  |  | 37820220C40496 |  | 3421001-BREAKS/CITY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole | Ohio St, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville |  |  | 37820220C40496 |  | 3421001-BREAKS/CITY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole | Ohio St, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville |  |  | 37820220C40496 |  | 3421001-BREAKS/CITY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole | Ohio St, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville | 86180754 |  | 37820220C40938 |  | 3421001-BREAKS/CITY | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen. Probably need to install ground rod. Could not find it. | Ohio St, Elkhorn City, KY 41522, USA
2019 | 2019-10-24 | Pikeville | 86180719 |  | 37820220C40940 |  | 3421001-BREAKS/CITY | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen. Probably will need to install ground rod. Could not find it. | Clinchfield St, Elkhorn City, KY 41522, USA
2019 | 2019-10-24 | Pikeville |  |  | 37820220D00364 |  | 3421001-BREAKS/CITY | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign |  | Secondary pole covered in vines. | Ohio St, Elkhorn City, KY 41522, USA | 2020-05-05
2019 | 2019-10-24 | Pikeville |  |  | 37820220D00860 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Carson St, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville |  |  | 37820220D00860 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Carson St, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville |  |  | 37820220D10208 |  | 3421001-BREAKS/CITY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole | Hatcher St, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville |  |  | 37820220D10725 |  | 3421001-BREAKS/CITY | Service Work | OH |  | pole: leaning, burned more than 50% remaining , guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Top of pole @ the cutout bracket is burnt about half way thru. Guy wire slack. Needs marker. Completed guy and marker. | 7th St, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville |  |  | 37820220D10725 |  | 3421001-BREAKS/CITY | Service Work | OH |  | pole: leaning, burned more than 50% remaining , guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Top of pole @ the cutout bracket is burnt about half way thru. Guy wire slack. Needs marker. Completed guy and marker. Install: 1990 | 7th St, Elkhorn City, KY 41522, USA | 2019-10-24
2019 | 2019-10-24 | Pikeville | 86179825 |  | 37820220D30897 |  | 3421001-BREAKS/CITY | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen on transformer pole. Too high to reach from ground. Probably will need to install new ground rod. | Carson Island Rd, Elkhorn City, KY 41522, USA
2019 | 2019-10-24 | Pikeville | 86179825 |  | 37820220D40967 |  | 3421001-BREAKS/CITY | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. Probably need to install new ground rod. Pole ground too high to reach. | Carson Island Rd, Elkhorn City, KY 41522, USA
2019 | 2019-10-24 | Pikeville | 86179825 |  | 37820220D40968 |  | 3421001-BREAKS/CITY | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. Probably need to install new ground rod. Too high to reach from ground. | Carson Island Rd, Elkhorn City, KY 41522, USA
2019 | 2019-10-25 | Pikeville |  |  | 37820196B00084 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Cedar Hill Road, Elkhorn City, Ky. | 2019-10-25
2019 | 2019-10-25 | Pikeville |  |  | 37820196B00084 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Cedar Hill Road, Elkhorn City, Ky. | 2019-10-25
2019 | 2019-10-25 | Pikeville |  |  | 37820196B00177 |  | 3421001-BREAKS/CITY | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen. | Beaver Creek Rd, Kentucky, USA | 2019-10-25
2019 | 2019-10-25 | Pikeville |  |  | 37820196B00177 |  | 3421001-BREAKS/CITY | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen. | Beaver Creek Rd, Kentucky, USA | 2019-10-25
2019 | 2019-10-25 | Pikeville | 78727377 |  | 37820196B40898 |  | 3421001-BREAKS/CITY | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen. Too high to reach from ground. | Little Beaver Road, Elkhorn City, Ky. | 2021-02-01
2019 | 2019-10-25 | Pikeville | 78726861 |  | 37820196B40899 |  | 3421001-BREAKS/CITY | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen. Cut too high on pole to reach from ground. | Little Beaver Road, Elkhorn City, Ky. | 2021-02-01
2019 | 2019-10-25 | Pikeville |  |  | 37820220C20078 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Bridge St, Elkhorn City, KY 41522, USA | 2019-10-25
2019 | 2019-10-25 | Pikeville |  |  | 37820220C20078 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Bridge St, Elkhorn City, KY 41522, USA | 2019-10-25
2019 | 2019-10-25 | Pikeville |  |  | 37820220C20111 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Pine St, Elkhorn City, KY 41522, USA | 2019-10-25
2019 | 2019-10-25 | Pikeville | 78726143 |  | 37820220C20139 |  | 3421001-BREAKS/CITY | Service Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Metering cable hanging down pole loose.@ double kwik | Elkhorn City, KY 41522, USA | 2021-02-01
2019 | 2019-10-25 | Pikeville |  |  | 37820220C20460 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | E Russell St, Elkhorn City, KY 41522, USA | 2019-10-25
2019 | 2019-10-25 | Pikeville | 78725877 |  | 37820220C20469 |  | 3421001-BREAKS/CITY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign |  | Service drop rolled up on pole. | 182 Main St, Elkhorn City, KY 41522, USA | 2021-02-01
2019 | 2019-10-25 | Pikeville | 82239453 | DKY0116912 | 37820220C20510 |  | 3421001-BREAKS/CITY | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Lightning arrestor blown.@ behind the bank at the bridge. | E Russell St, Elkhorn City, KY 41522, USA | 2022-05-04
2019 | 2019-10-25 | Pikeville | 86179769 |  | 37820220C20668 | TRUE | 3421001-BREAKS/CITY | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire hanging down pole. Needs to be re-attached. Could not find anchor. Probably need to install new anchor. @ double kwik. | Elkhorn City, KY 41522, USA
2019 | 2019-10-25 | Pikeville |  |  | 37820220C20684 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Main St, Elkhorn City, KY 41522, USA | 2019-10-25
2019 | 2019-10-25 | Pikeville |  |  | 37820220C20684 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Main St, Elkhorn City, KY 41522, USA | 2019-10-25
2019 | 2019-10-25 | Pikeville | 86179738 |  | 37820220D10090 |  | 3421001-BREAKS/CITY | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Lightning arrestors blown (2) on transformer bank.@ in front of subway. | W Russell St, Elkhorn City, KY 41522, USA
2019 | 2019-10-25 | Pikeville |  |  | 37820220D10379 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Stillhouse Ave, Elkhorn City, KY 41522, USA | 2019-10-25
2019 | 2019-10-25 | Pikeville |  |  | 37820220D10379 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Stillhouse Ave, Elkhorn City, KY 41522, USA | 2019-10-25
2019 | 2019-10-25 | Pikeville |  |  | 37820220D10379 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Stillhouse Ave, Elkhorn City, KY 41522, USA | 2019-10-25
2019 | 2019-10-25 | Pikeville |  |  | 37820220D10379 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Stillhouse Ave, Elkhorn City, KY 41522, USA | 2019-10-25
2019 | 2019-10-25 | Pikeville |  |  | 37821096B40876 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY-80, Elkhorn City, KY, USA | 2019-10-25
2019 | 2019-10-28 | Pikeville | 86179808 |  | 37820220A00143 |  | 3421001-BREAKS/CITY | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC |  | Pole covered in vines. Line crosses RR tracks. | John Moore Branch, Elkhorn City, Ky. 41522
2019 | 2019-10-28 | Pikeville | 86179808 |  | 37820220A30240 |  | 3421001-BREAKS/CITY | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign |  | Pole covered in vines. | John Moore Branch, Elkhorn City, Ky. 41522
2019 | 2019-10-28 | Pikeville |  |  | 37820220B00224 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Price Ave, Elkhorn City, KY 41522, USA | 2019-10-28
2019 | 2019-10-28 | Pikeville |  |  | 37820220B00224 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Price Ave, Elkhorn City, KY 41522, USA | 2019-10-28
2019 | 2019-10-28 | Pikeville |  |  | 37820220B00224 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Price Ave, Elkhorn City, KY 41522, USA | 2019-10-28
2019 | 2019-10-28 | Pikeville |  |  | 37820220B00464 |  | 3421001-BREAKS/CITY | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign |  | Crossarm split / deteoriated on end.@ Price Avenue | 1288 Hwy 197, Elkhorn City, Ky. 41522 | 2023-10-19
2019 | 2019-10-28 | Pikeville |  |  | 37820220D00572 | TRUE | 3421001-BREAKS/CITY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | Service drop low clearance. Probably need to install new secondary pole. | 255 Virgie St, Elkhorn City, KY 41522, USA
2019 | 2019-10-28 | Pikeville | 86179718 |  | 37820244000006 |  | 3421001-BREAKS/CITY | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Epoxilator melting/deteoriated. Might be able to reach from Road? | 227 Pond Branch Rd, Elkhorn City, KY 41522, USA
2019 | 2019-10-28 | Pikeville |  |  | 37820244000013 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Hwy 197, Elkhorn Creek, Elkhorn City, Ky. 41522 | 2019-10-28
2019 | 2019-10-28 | Pikeville |  |  | 37820244000098 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Fish Pond Bottom, Elkhorn City, Ky. | 2019-10-28
2019 | 2019-10-28 | Pikeville |  |  | 37820244000098 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Fish Pond Bottom, Elkhorn City, Ky. | 2019-10-28
2019 | 2019-10-28 | Pikeville |  |  | 37820244000098 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Fish Pond Bottom, Elkhorn City, Ky. | 2019-10-28
2019 | 2019-10-29 | Pikeville |  |  | 37820243B00012 |  | 3421001-BREAKS/CITY | Line Work | OH | cutout: damaged | lightning arresters/insulators: damaged |  | Foreign |  | Epoxilator melting/deteoriated. @ just before E & R Road on left. Also has broken cutout on the pole. | 4189 Ky 197, Elkhorn City, Ky. 41522 | 2023-10-19
2019 | 2019-10-29 | Pikeville | 86179491 |  | 37820243B00017 |  | 3421001-BREAKS/CITY | Line Work | OH |  | crossarm/braces: deteriorated, not rotten , lightning arresters/insulators: damaged |  | Foreign |  | Epoxilators deteoriated/melted. One has tracked already and burnt crossarm. Take-off pole for Adams Branch. | 3915 Ky. Hwy. 197, Elkhorn City, Ky. 41522
2019 | 2019-10-29 | Pikeville |  |  | 37820243B00183 |  | 3421001-BREAKS/CITY | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Epoxilator deteoriated/melting | 4397 KY 197, Elkhorn City, Ky. 41522 | 2023-10-19
2019 | 2019-10-29 | Pikeville |  |  | 37820243C00062 |  | 3421001-BREAKS/CITY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole | Kettlecamp Branch, Elkhorn City, Ky. 41522 | 2019-10-29
2019 | 2019-10-29 | Pikeville |  |  | 37820243D00027 |  | 3421001-BREAKS/CITY | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Epoxilators deteoriated/ melting down..take-off pole for water branch. | Water Branch, Elkhorn City, Ky. | 2023-10-19
2019 | 2019-10-29 | Pikeville |  |  | 37820243D00213 |  | 3421001-BREAKS/CITY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign |  | Service drop hanging down pole | Cure Hill, Elkhorn City, Ky. 41522 | 2019-10-29
2019 | 2019-10-29 | Pikeville | 86179527 |  | 37820243D00352 | TRUE | 3421001-BREAKS/CITY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Secondary low clearance over roadway.@ across from water Branch on hill. | 197 Elkhorn St, Elkhorn City, KY 41522, USA
2019 | 2019-10-29 | Pikeville |  |  | 37820244000016 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Hwy 197, Elkhorn Creek, Elkhorn City, Ky. 41522 | 2019-10-29
2019 | 2019-10-29 | Pikeville |  |  | 37820244000045 | TRUE | 3421001-BREAKS/CITY | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Lightning arrestor blown on regulator pole.@ entrance to Elkhorn Stone quarry. | 197 Elkhorn St, Elkhorn City, KY 41522, USA | 2023-10-19
2019 | 2019-10-30 | Pikeville |  |  | 37830334000045 |  | 3409502-BURDINE / LEVISA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown | 1040 Marshals Branch, Burdine, Ky. | 2023-10-19
2019 | 2019-10-30 | Pikeville |  |  | 37830334A40126 |  | 3409502-BURDINE / LEVISA | Line Work | OH |  |  |  | KPC |  | Neutral conductor down. #2 aluminum. No truck. @ head of Lfk at gas wells. | Marshals Branch, Burdine, Ky. | 2023-10-19
2019 | 2019-10-30 | Pikeville |  |  | 37830358C00026 |  | 3409502-BURDINE / LEVISA | Line Work | OH |  |  |  | KPC |  | Neutral conductor down/stolen.#4 copper wire. No truck on one pole. | Mc Peek Branch, Burdine, Ky.
2019 | 2019-10-30 | Pikeville |  |  | 37830358C00192 |  | 3409502-BURDINE / LEVISA | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC |  | Pole covered in vines. About half mile up on left. | McPeeks Branch, Burdine, Ky. | 2020-05-05
2019 | 2019-10-30 | Pikeville |  |  | 37830358D00338 |  | 3409502-BURDINE / LEVISA | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC |  | Pole covered in vines. @ behind old mine equipment place just before rr tracks on right. | 12633 U.S. Hwy 23, Burdine, Ky. | 2020-05-05
2019 | 2019-10-30 | Pikeville |  |  | 37830358D30358 |  | 3409502-BURDINE / LEVISA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack and needs marker | U.S. Hwy 23, Burdine, Ky. | 2019-10-30
2019 | 2019-10-30 | Pikeville |  |  | 37830358D30358 |  | 3409502-BURDINE / LEVISA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack and needs marker | U.S. Hwy 23, Burdine, Ky. | 2019-10-30
2019 | 2019-10-30 | Pikeville |  |  | 37830358D30358 |  | 3409502-BURDINE / LEVISA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack and needs marker | U.S. Hwy 23, Burdine, Ky. | 2019-10-30
2019 | 2019-10-30 | Pikeville |  |  | 37830358D30358 |  | 3409502-BURDINE / LEVISA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack and needs marker | U.S. Hwy 23, Burdine, Ky. | 2019-10-30
2019 | 2019-10-30 | Pikeville |  |  | 37830358D30358 |  | 3409502-BURDINE / LEVISA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack and needs marker | U.S. Hwy 23, Burdine, Ky. | 2019-10-30
2019 | 2019-10-30 | Pikeville |  |  | 37830358D30358 |  | 3409502-BURDINE / LEVISA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire slack and needs marker | U.S. Hwy 23, Burdine, Ky. | 2019-10-30
2019 | 2019-10-31 | Pikeville |  |  | 37830311000032 |  | 3409502-BURDINE / LEVISA | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole | Granny Vanover Branch, Dorton, Ky. | 2019-10-31
2019 | 2019-10-31 | Pikeville |  |  | 37830311000032 |  | 3409502-BURDINE / LEVISA | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen on transformer pole | Granny Vanover Branch, Dorton, Ky. | 2019-10-31
2019 | 2019-10-31 | Pikeville | 86179447 |  | 37830335A00236 | TRUE | 3409502-BURDINE / LEVISA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 324 Contrary Hollow Rd, Dorton, Ky.
2019 | 2019-10-31 | Pikeville | 78735601 |  | 37830335A00308 |  | 3409502-BURDINE / LEVISA | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign |  | Service drop rolled up on pole | 1335 Big Shelby Creek, Jenkins, KY 41537, USA | 2021-02-02
2019 | 2019-10-31 | Pikeville |  |  | 37830335B00037 |  | 3409502-BURDINE / LEVISA | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign |  | Pole covered in vines | 5967 U.S. 23, Dorton/ Jenkins Hwy, Burdine, Ky. | 2020-05-05
2019 | 2019-10-31 | Pikeville |  |  | 37830335B00119 |  | 3409502-BURDINE / LEVISA | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign |  | Pole covered in vines | 5967 U. S. 23 Dorton/Jenkins Hwy. Burdine, Ky. | 2020-05-05
2019 | 2019-11-01 | Pikeville | 84322637 | DKY0119413 | 37830311000092 |  | 3409502-BURDINE / LEVISA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer.@ across from Dorton station. | 15087 US-23, Jenkins, KY 41537, USA | 2023-02-01
2019 | 2019-11-01 | Pikeville | 78736126 |  | 37830311000126 |  | 3409502-BURDINE / LEVISA | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop rolled up on pole top.@ across from Dorton station. | U.S. Hwy 23 S , Dorton, Ky. | 2021-02-02
2019 | 2019-11-01 | Pikeville |  |  | 37830335C00166 |  | 3409502-BURDINE / LEVISA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Cane Branch, Elkhorn Creek, Elkhorn City, Ky. | 2019-11-01
2019 | 2019-11-01 | Pikeville |  |  | 37830335C00166 |  | 3409502-BURDINE / LEVISA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Cane Branch, Elkhorn Creek, Elkhorn City, Ky. | 2019-11-01
2019 | 2019-11-01 | Pikeville |  |  | 37830335D00084 |  | 3409502-BURDINE / LEVISA | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign |  | Pole covered in vines | 16 Kelly Mountain Road, Elkhorn City, Ky. | 2020-05-05
2019 | 2019-11-01 | Pikeville |  |  | 37830336000046 |  | 3409502-BURDINE / LEVISA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker (2) | Kelly Mountain Road, Elkhorn City, Ky. | 2019-11-01
2019 | 2019-11-04 | Pikeville |  |  | 37830312000030 |  | 3409502-BURDINE / LEVISA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Upper Pigeon Road, Shelby Gap, Ky. | 2019-11-04
2019 | 2019-11-04 | Pikeville |  |  | 37830312000200 |  | 3409502-BURDINE / LEVISA | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Lightning arrestor blown | 13109 Elkhorn Creek, Shelby Gap, Ky. | 2023-10-19
2019 | 2019-11-04 | Pikeville |  |  | 37830312B30234 |  | 3409502-BURDINE / LEVISA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Hylton Church Rd & Elkhorn Creek, Kentucky 41563, USA | 2019-11-04
2019 | 2019-11-04 | Pikeville | 86179471 |  | 37830335C00092 | TRUE | 3409502-BURDINE / LEVISA | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Epoxilators deteoriated/melting. Truck??? | 36 Anderson Branch Rd, Shelby Gap, KY 41563, USA
2019 | 2019-11-04 | Pikeville | 86179471 |  | 37830335C00258 |  | 3409502-BURDINE / LEVISA | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections , lightning arresters/insulators: damaged |  | KPC |  | Epoxilator deteoriated/melting | Anderson Branch Road, Shelby Gap, Ky. 41563
2019 | 2019-11-04 | Pikeville | 77209360 | DKY0110763 | 37830335C00333 |  | 3409502-BURDINE / LEVISA | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Secondary pole leaning. Appears to be slide area. May need guy and anchor installed to straighten or relocate pole. Install: 1993 | 256 Anderson Branch Rd, Shelby Gap, KY 41563, USA | 2022-08-15
2019 | 2019-11-04 | Pikeville | 86179471 |  | 37830336000005 |  | 3409502-BURDINE / LEVISA | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Epoxilators Deteoriated/melting | 14576 Elkhorn Creek, Shelby Gap, KY 41563, USA
2019 | 2019-11-04 | Pikeville | 86186026 |  | 37830336000077 | TRUE | 3409502-BURDINE / LEVISA | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Epoxilator deteoriated/ melted | 14195 Elkhorn Creek, Shelby Gap, KY 41563, USA
2019 | 2019-11-06 | Pikeville |  |  | 38830785D10414 |  | 3409001-W.PAINTSV / PAINTSVIL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Court St, Paintsville, KY 41240, USA | 2019-11-06
2019 | 2019-11-06 | Pikeville |  |  | 38830785D10414 |  | 3409001-W.PAINTSV / PAINTSVIL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Court St, Paintsville, KY 41240, USA | 2019-11-06
2019 | 2019-11-06 | Pikeville |  |  | 38830785D10414 |  | 3409001-W.PAINTSV / PAINTSVIL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Court St, Paintsville, KY 41240, USA | 2019-11-06
2019 | 2019-11-06 | Pikeville |  |  | 38830785D10414 |  | 3409001-W.PAINTSV / PAINTSVIL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Court St, Paintsville, KY 41240, USA | 2019-11-06
2019 | 2019-11-06 | Pikeville |  |  | 38830785D10414 |  | 3409001-W.PAINTSV / PAINTSVIL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Court St, Paintsville, KY 41240, USA | 2019-11-06
2019 | 2019-11-06 | Pikeville |  |  | 38830785D10414 |  | 3409001-W.PAINTSV / PAINTSVIL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Court St, Paintsville, KY 41240, USA | 2019-11-06
2019 | 2019-11-06 | Pikeville |  |  | 38830785D10414 |  | 3409001-W.PAINTSV / PAINTSVIL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Court St, Paintsville, KY 41240, USA | 2019-11-06
2019 | 2019-11-06 | Pikeville |  |  | 38830785D10445 |  | 3409001-W.PAINTSV / PAINTSVIL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Elm St, Paintsville, KY 41240, USA | 2019-11-06
2019 | 2019-11-06 | Pikeville |  |  | 38830785D21186 |  | 3409001-W.PAINTSV / PAINTSVIL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten | 512 Elm St, Paintsville, KY 41240, USA
2019 | 2019-11-08 | Pikeville |  |  | 38830785D10807 |  | 3409001-W.PAINTSV / PAINTSVIL | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Metering enclosure open. Missing meter cover. @ metering just outside station gate. | William Henry Dixon Blvd, Paintsville, KY 41240, USA
2019 | 2019-11-14 | Pikeville | 76371048 | DKY0109767 | 38830785A41557 |  | 3409003-W.PAINTSV / PLAZA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown on switch pole. OPEN POINT. @ football field. Middle arrestor. | US-23, Paintsville, KY, USA | 2021-05-05
2019 | 2019-11-14 | Pikeville |  |  | 38830785B31031 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | US-23, Paintsville, KY, USA | 2019-11-14
2019 | 2019-11-14 | Pikeville |  |  | 38830785B31113 |  | 3409003-W.PAINTSV / PLAZA | Line Work | OH |  | lightning arresters/insulators: damaged , guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Lightning arrestor blown. Also needs guy marker. Completed marker. | US-23, Paintsville, KY, USA | 2020-05-19
2019 | 2019-11-14 | Pikeville | 76371132 | DKY0109736 | 38830785B41079 |  | 3409003-W.PAINTSV / PLAZA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators deteoriated/melted. @ BEHIND RAMADA INN | 625 Main St, Paintsville, KY 41240, USA | 2021-04-29
2019 | 2019-11-14 | Pikeville | 76371132 | DKY0109736 | 38830785B41080 |  | 3409003-W.PAINTSV / PLAZA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Epoxilators deteoriated/melted. @ BEHIND RAMADA INN | 625 Main St, Paintsville, KY 41240, USA | 2021-04-29
2019 | 2019-11-14 | Pikeville |  |  | 38830785D20851 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Main St, Paintsville, KY 41240, USA | 2019-11-14
2019 | 2019-11-14 | Pikeville |  |  | 38830785D21063 |  | 3409003-W.PAINTSV / PLAZA | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC |  | Pole covered with vines | 617 Main St, Paintsville, KY 41240, USA | 2020-05-06
2019 | 2019-11-14 | Pikeville |  |  | 38830785D21334 |  | 3409003-W.PAINTSV / PLAZA | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC |  | Pole covered with vines | 3rd St, Paintsville, KY 41240, USA | 2020-05-06
2019 | 2019-11-15 | Pikeville | 76371048 | DKY0109767 | 38830785D20083 |  | 3409003-W.PAINTSV / PLAZA | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Crossarms are deteoriated. | 205 S Mayo Trail, Paintsville, KY 41240, USA | 2021-05-05
2019 | 2019-11-15 | Pikeville |  |  | 38830785D20202 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | 2nd St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville |  |  | 38830785D20202 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | 2nd St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville | 76371375 | DKY0109903 | 38830785D20204 |  | 3409003-W.PAINTSV / PLAZA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten and slabbed.//THIS POLE WAS REPLACED ON A HENDRIX REPLACEMENT JOB | 124 East St, Paintsville, KY 41240, USA | 2023-05-17
2019 | 2019-11-15 | Pikeville |  |  | 38830785D20212 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Court St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville |  |  | 38830785D20212 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Court St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville |  |  | 38830785D20246 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Broadway St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville |  |  | 38830785D20246 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Broadway St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville |  |  | 38830785D20246 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Broadway St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville | 76371132 | DKY0109736 | 38830785D20260 |  | 3409003-W.PAINTSV / PLAZA | Line Work | OH | service: unused or abandoned, blanked meter base | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Anchor bent/ rusted/ pulled out. Guy wire slack. Also service drop rolled up on pole. | 412 3rd St, Paintsville, KY 41240, USA | 2021-04-29
2019 | 2019-11-15 | Pikeville |  |  | 38830785D20595 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Broadway St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville | 70079084 | DKY0100624 | 38830785D20635 |  | 3409003-W.PAINTSV / PLAZA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten. | 324 Church St, Paintsville, KY 41240, USA | 2023-03-02
2019 | 2019-11-15 | Pikeville |  |  | 38830785D21027 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Main St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville |  |  | 38830785D21027 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Main St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville |  |  | 38830785D21027 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire needs marker | Main St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville |  |  | 38830785D21576 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Main St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville |  |  | 38830785D21576 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Main St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville |  |  | 38830785D21576 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Main St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-15 | Pikeville |  |  | 38830785D21576 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Main St, Paintsville, KY 41240, USA | 2019-11-15
2019 | 2019-11-20 | Pikeville |  |  | 38830784C20507 |  | 3409003-W.PAINTSV / PLAZA | Line Work | UG | UG conduit: damaged or separated |  |  | KPC |  | Polypad for padmount transformer is busted/broken. | 178 Easy Street, Arrowhead Estates, Paintsville, KY. 41256
2019 | 2019-11-20 | Pikeville |  |  | 38830785A21238 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | S Mayo Trail, Paintsville, KY 41240, USA | 2019-11-20
2019 | 2019-11-20 | Pikeville |  |  | 38830785A21238 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | S Mayo Trail, Paintsville, KY 41240, USA | 2019-11-20
2019 | 2019-11-21 | Pikeville | 76371541 | DKY0109847 | 38830808000066 |  | 3409003-W.PAINTSV / PLAZA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , guys/anchors: broken or missing |  |  | KPC | YES | Pole is slabbed. Leaning considerably, in a slide area, guy wire broken. Probably need to relocate pole.@ behind fire department on hill. | 119 Horne Branch, U.S. Hwy. 460, Paintsville, KY. | 2022-05-16
2019 | 2019-11-21 | Pikeville | 76371048 | DKY0109767 | 38830808000077 |  | 3409003-W.PAINTSV / PLAZA | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole leaning considerably. Needs to be straightened. Install: 1974 | Collins Fork Road, KY. 2039, Paintsville, KY. | 2021-05-05
2019 | 2019-11-21 | Pikeville |  |  | 38830808000099 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Verne Horne Dr. Paintsville, Kentucky 41256, USA | 2019-11-21
2019 | 2019-11-21 | Pikeville |  |  | 38830808000099 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Verne Horne Dr. Paintsville, Kentucky 41256, USA | 2019-11-21
2019 | 2019-11-21 | Pikeville |  |  | 38830808000105 |  | 3409003-W.PAINTSV / PLAZA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker. (2) Completed same day. Satellite dish on pole. ( Dish Network) | 247 Verne Horne Dr, Staffordsville, KY 41256, USA
2019 | 2019-11-21 | Pikeville | 76371514 | DKY0109745 | 38830808000177 |  | 3409003-W.PAINTSV / PLAZA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is burnt at the cutout bracket | 761 KY. 2039, Paintsville, KY. | 2020-12-09
2019 | 2019-11-25 | Pikeville | 76371491 | DKY0109911 | 38830809000218 |  | 3409003-W.PAINTSV / PLAZA | Line Work | OH |  |  | STOLEN NEUTRAL | KPC |  | Neutral conductor down/stolen. #4 copper | US-23 & McCarty Branch Rd, Kentucky 41222, USA | 2021-01-07
2019 | 2019-12-02 | Pikeville |  |  | 38830785A11127 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Hidden Valley Rd, Paintsville, KY 41240, USA | 2019-12-02
2019 | 2019-12-02 | Pikeville |  |  | 38830785A11133 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Hidden Valley Rd, Paintsville, KY 41240, USA | 2019-12-02
2019 | 2019-12-02 | Pikeville |  |  | 38830785A11133 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Hidden Valley Rd, Paintsville, KY 41240, USA | 2019-12-02
2019 | 2019-12-02 | Pikeville |  |  | 38830785A11134 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Hidden Valley Rd, Paintsville, KY 41240, USA | 2019-12-02
2019 | 2019-12-03 | Pikeville |  |  | 38830760D00094 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Rule Branch, Staffordsville, KY. 41256 | 2019-12-03
2019 | 2019-12-03 | Pikeville |  |  | 38830760D00124 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Stafford Springs, Staffordsville, KY. 41256 | 2019-12-03
2019 | 2019-12-03 | Pikeville |  |  | 38830760D00124 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Stafford Springs, Staffordsville, KY. 41256 | 2019-12-03
2019 | 2019-12-03 | Pikeville | 76371031 | DKY0109535 | 38830760D00279 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer | Salyers Hill, Rule Branch, Staffordsville, KY. | 2021-04-28
2019 | 2019-12-03 | Pikeville |  |  | 38830760D00340 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Park Drive, Staffordsville, KY. | 2019-12-03
2019 | 2019-12-03 | Pikeville |  |  | 38830784C00221 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Little Mudlick Road, Staffordsville, KY. 41256 | 2019-12-03
2019 | 2019-12-03 | Pikeville |  |  | 38830784C40569 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Stave Branch, Staffordsville, KY. | 2019-12-03
2019 | 2019-12-04 | Pikeville |  |  | 38830760B00207 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Fish trap Hill, Staffordsville, KY. | 2019-12-04
2019 | 2019-12-04 | Pikeville |  |  | 38830760B00237 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | Blanton Drive, Staffordsville, KY. | 2019-12-04
2019 | 2019-12-04 | Pikeville |  |  | 38830760B00248 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | Blanton Drive, Staffordsville, KY. | 2019-12-04
2019 | 2019-12-05 | Pikeville |  |  | 38830784C20563 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Line Work | UG | transformers: leaking, damaged, unused near waterway/drainage OR school property , UG conduit: damaged or separated |  |  | KPC |  | Conductors exposed on padmount transformer. Pad appears to be partially crushed.@ Cross creek subdivision. Contacted LCS Tommy Goble on 12/6/19 by phone to have repairs made and he said he would take care of this. | West Dorton Blvd. Staffordsville, KY. 41256 | 2020-05-19
2019 | 2019-12-11 | Pikeville |  |  | 38830782000013 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 6828 KY. Route 40, Oil Springs , KY. | 2019-12-11
2019 | 2019-12-11 | Pikeville |  |  | 38830783000099 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | 4060 KY. Route 40, Staffordsville, KY. | 2019-12-11
2019 | 2019-12-11 | Pikeville | 76371031 | DKY0109535 | 38830783000121 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightning arrestor blown on capacitor bank. On center phase. | 5050 KY-40, Staffordsville, KY 41256, USA | 2021-04-28
2019 | 2019-12-11 | Pikeville |  |  | 38830806000072 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Inactive service drop hanging down pole. | 642 Grassy Fork, Staffordsville, KY 41256, USA | 2019-12-11
2019 | 2019-12-12 | Pikeville |  |  | 38830737000117 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service drop hanging down pole | Shady Ln, Kentucky 41274, USA | 2019-12-12
2019 | 2019-12-12 | Pikeville |  |  | 38830761000192 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | U.S. Hwy 23, Paintsville, KY. 41256 | 2019-12-12
2019 | 2019-12-12 | Pikeville |  |  | 38830761000192 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | U.S. Hwy 23, Paintsville, KY. 41256 | 2019-12-12
2019 | 2019-12-12 | Pikeville |  |  | 38830761000192 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker (2) | U.S. Hwy 23, Paintsville, KY. 41256 | 2019-12-12
2019 | 2019-12-12 | Pikeville |  |  | 38830761000230 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 201 , Paintsville, KY. | 2019-12-12
2019 | 2019-12-12 | Pikeville |  |  | 38830761000230 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 201 , Paintsville, KY. | 2019-12-12
2019 | 2019-12-12 | Pikeville |  |  | 38830761000230 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy wire needs marker | KY. Route 201 , Paintsville, KY. | 2019-12-12
2019 | 2019-12-16 | Pikeville | 76371031 | DKY0109535 | 38830737000059 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Line Work | OH | crossarm/braces: broken/split | crossarm/braces: deteriorated, not rotten |  | KPC |  | Crossarms rotten/ deteoriated.@ Johnson County Christian School sign. Next to Dollar General on U.S. 23. Also has lightning arrestor blown. Transformer is open and inactive but meter base is also open. Could remove transformer. | Christian Way, Wittensville, KY. | 2021-04-28

## Ckt Defects Reported 2020 PKV
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2020 | 2020-01-06 | Pikeville |  |  | 38830806000007 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | KY. 825, Oil Springs, KY. 41238 | 2020-01-06
2020 | 2020-01-06 | Pikeville |  |  | 38830806000041 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Caudill Fork, Staffordsville, KY. | 2020-01-06
2020 | 2020-01-06 | Pikeville |  |  | 38830806000041 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Caudill Fork, Staffordsville, KY. | 2020-01-06
2020 | 2020-01-06 | Pikeville |  |  | 38830806000046 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Caudill Branch, Staffordsville, KY. | 2020-01-06
2020 | 2020-01-06 | Pikeville |  |  | 38830806000046 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Caudill Branch, Staffordsville, KY. | 2020-01-06
2020 | 2020-01-06 | Pikeville |  |  | 38830806000046 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Caudill Branch, Staffordsville, KY. | 2020-01-06
2020 | 2020-01-06 | Pikeville | 76370524 | DKY0109667 | 38830806000081 |  | 3401101-FALCON / FALC-OILS | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop. Transformer is also inactive. | 155 Orchard Br Rd, Staffordsville, KY 41256, USA | 2022-05-04
2020 | 2020-01-06 | Pikeville |  |  | 38830806000126 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Caudill Branch, Staffordsville, KY. | 2020-01-06
2020 | 2020-01-06 | Pikeville | 76370524 | DKY0109667 | 38830806000142 |  | 3401101-FALCON / FALC-OILS | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire hanging down pole. Anchor is buried under ground. Stapled guy wire to pole. | 7876 KY-40, Oil Springs, KY 41238, USA | 2022-05-04
2020 | 2020-01-06 | Pikeville |  |  | 38830806000273 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY. route 40, Oil Springs, KY. | 2020-01-06
2020 | 2020-01-07 | Pikeville |  |  | 38830830000110 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 7547 US-460, Oil Springs, KY 41238, USA | 2020-01-07
2020 | 2020-01-07 | Pikeville |  |  | 38830830000167 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 7586 US-460, Oil Springs, KY 41238, USA | 2020-01-07
2020 | 2020-01-07 | Pikeville |  |  | 38830830000167 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 7586 US-460, Oil Springs, KY 41238, USA | 2020-01-07
2020 | 2020-01-08 | Pikeville |  |  | 38830829A40164 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | 3773 US-460, Salyersville, KY 41465, USA | 2020-01-08
2020 | 2020-01-08 | Pikeville |  |  | 38830830B30176 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY. 825 Riceville, KY. | 2020-01-08
2020 | 2020-01-08 | Pikeville |  |  | 38830854000004 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY. Route 825, Riceville, KY. | 2020-01-08
2020 | 2020-01-09 | Pikeville |  |  | 38830902000008 |  | 3401101-FALCON / FALC-OILS | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground cut on transformer pole. | 750 Narrows Fork, Riceville, KY. | 2020-01-09
2020 | 2020-01-09 | Pikeville |  |  | 38830902000008 |  | 3401101-FALCON / FALC-OILS | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground cut on transformer pole. | 750 Narrows Fork, Riceville, KY. | 2020-01-09
2020 | 2020-01-09 | Pikeville | 76371269 | DKY0109751 | 38830902000012 | TRUE | 3401101-FALCON / FALC-OILS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Top of pole is split. @ head of Narrows Fork. Angle pole. Pole seems solid at base but it was installed in 1952. Might want to change pole. | Narrows Fork, Swamp Branch, Riceville, KY. | 2022-04-28
2020 | 2020-01-09 | Pikeville | 75916564 | DKY0108649 | 38830902000051 |  | 3401101-FALCON / FALC-OILS | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop low. Customer has propped up with a tree branch. Probably needs secondary pole installed for clearance. | 1279 Brushy Fork, Riceville, KY. | 2020-03-18
2020 | 2020-01-09 | Pikeville | 84808504 | DKY0120570 | 38830903000002 |  | 3401101-FALCON / FALC-OILS | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator melting/deteoriated. | 1266 Riceville Rd, Paintsville, KY 41240, USA | 2023-05-10
2020 | 2020-01-10 | Pikeville | 76371438 | DKY0110006 | 38830805D30272 |  | 3401101-FALCON / FALC-OILS | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Long span of duplex , low clearance over mobile home. Needs slack taken out for clearance. Pole might also need anchor and guy installed. | 6894 KY. Route 40, Oil Springs, KY. | 2022-03-23
2020 | 2020-01-10 | Pikeville | 76370524 | DKY0109667 | 38830806000199 |  | 3401101-FALCON / FALC-OILS | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | (5) Lightning arrestors blown on regulator pole. | 8412 KY-40, Oil Springs, KY 41238, USA | 2022-05-04
2020 | 2020-01-10 | Pikeville |  |  | 38830829000067 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 183 Painters Lick Rd, Salyersville, KY 41465, USA | 2020-01-10
2020 | 2020-01-13 | Pikeville |  |  | 38830828000042 |  | 3401101-FALCON / FALC-OILS | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND , guys/anchors: broken or missing |  |  | KPC | NO | Anchor rusted off, guy wire hanging down pole. Needs new anchor installed. Road crossing. Also pole ground stolen. Made repairs on pole ground.@ a barn on the right just before Painters Lick. | KY-40 & Falcon Rd, Kentucky 41465, USA
2020 | 2020-01-13 | Pikeville | 76371440 | DKY0109945 | 38830828000175 |  | 3401101-FALCON / FALC-OILS | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive line from this pole to end of line @ pole 38830829000088, which is the open point between Falcon/Oil Springs and Falcon/Burning Fork circuits. Line is down in several spans. Some poles are truck accessible and some are not. Will need to install anchor and guy at this pole. 9 spans to be removed. | 668 Horse Pen Branch, Salyersville, KY. | 2020-07-06
2020 | 2020-01-13 | Pikeville |  |  | 38830828000177 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Horse pen Branch, Salyersville, KY. | 2020-01-13
2020 | 2020-01-13 | Pikeville |  |  | 38830828000186 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | White Lick Branch, Salyersville, KY. | 2020-01-13
2020 | 2020-01-13 | Pikeville |  |  | 38830828000186 |  | 3401101-FALCON / FALC-OILS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | White Lick Branch, Salyersville, KY. | 2020-01-13
2020 | 2020-01-14 | Pikeville |  |  | 38830829000042 |  | 3401101-FALCON / FALC-OILS | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Behind White House with green metal roof on left about mile up painters lick. | Painters Lick Road, Salyersville, KY. | 2020-01-14
2020 | 2020-01-14 | Pikeville | 79475711 | DKY0113481 | 38830829000043 |  | 3401101-FALCON / FALC-OILS | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire hanging down pole. Needs to be reattached to anchor. | Painters Lick Road, Salyersville, KY.
2020 | 2020-01-14 | Pikeville | COMPLETE IN FIELD | COMPLETE IN FIELD | 38830829000049 |  | 3401101-FALCON / FALC-OILS | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Conductor floating. Pole is tagged as 829 but there’s no 829 showing in field view. | Painters Lick Road, Salyersville, KY.
2020 | 2020-01-14 | Pikeville | 76370985 | DKY0109711 | 38830851D00157 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire hanging down pole. Needs to be reattached. Angle pole. Don’t see the anchor. Probably will have to install one. First pole from the open point. About .3 mile from route 40. | Mash Fork Road, KY. 2020 Salyersville, KY. 41465 | 2021-03-22
2020 | 2020-01-14 | Pikeville |  |  | 38830851D00650 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 700 KY-2020, Salyersville, KY 41465, USA | 2020-01-14
2020 | 2020-01-14 | Pikeville | 76370985 | DKY0109711 | 38830852000137 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown (2). Hollow behind Falcon station. | KY-40 & Falcon Rd, Kentucky 41465, USA | 2021-03-22
2020 | 2020-01-14 | Pikeville | 76370985 | DKY0109711 | 38830852000206 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | UG conduit: damaged or separated |  |  | KPC | NO | Underground conduit broken/ conductors exposed. | 59 Teacher Lane, KY. 2020, Salyersville, KY. 41465 | 2021-03-22
2020 | 2020-01-15 | Pikeville | 76371003 | DKY0109757 | 38830852000044 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators melting/deteoriated. Take-off pole @ Burton Fork, of Mash Fork. | 2744 KY. 2020, Salyersville, KY. | 2021-05-05
2020 | 2020-01-15 | Pikeville | 76371003 | DKY0109757 | 38830852000146 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown. @ Crosscreek Rd. | KY. 2020, Mashfork Road, Salyersville, Ky | 2021-05-05
2020 | 2020-01-15 | Pikeville | 76371003 | DKY0109757 | 38830852000158 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/ melting and pin type insulators broken. Hard to tell from pictures. Beware of possible Doberman Pinscher.Might be truck access if dry. | 504 Burton Fork, KY. 2020, Salyersville, KY. | 2021-05-05
2020 | 2020-01-15 | Pikeville | 76371003 | DKY0109757 | 38830852000210 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/melting | 274 Burton Fork, Mash Fork, Salyersville, KY. | 2021-05-05
2020 | 2020-01-15 | Pikeville | 76371003 | DKY0109757 | 38830852000217 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator melting/deteoriated. Can probably use truck when good and dry if customer will allow. | 274 Burton Fork, Mash Fork, Salyersville, KY. | 2021-05-05
2020 | 2020-01-15 | Pikeville |  |  | 38830852C20388 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire slack. Needs marker | Fairchild Branch, Mash Fork, Salyersville, KY. | 2020-01-15
2020 | 2020-01-15 | Pikeville | 76370985 | DKY0109711 | 38830852D10410 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire broken on stub pole. Guy crosses road. Don’t see anchor. Probably will need to install one. Just before Fairchild Branch on Mash Fork. | KY-2020, Salyersville, KY 41465, USA | 2021-03-22
2020 | 2020-01-15 | Pikeville |  |  | 38830876C00056 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Rockhouse Fork, Salyersville, KY. 41465 | 2020-01-15
2020 | 2020-01-15 | Pikeville |  |  | 38830876C00404 |  | 3401103-FALCON / BURNINGFK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | De-engergized / Inactive service drop hanging down pole . Needs to be removed | 1220 KY. Route 460, Salyersville, KY.
2020 | 2020-01-16 | Pikeville | 76370940 | DKY0109713 | 38830853000078 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Primary conductor tie-wire broken | 4292 Rockhouse Fork, Salyersville, KY. | 2022-05-05
2020 | 2020-01-16 | Pikeville |  |  | 38830876B00203 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | US-460, Salyersville, KY, USA | 2020-01-16
2020 | 2020-01-16 | Pikeville |  |  | 38830876C00126 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Limestone Road, Salyersville, KY. | 2020-01-16
2020 | 2020-01-16 | Pikeville |  |  | 38830876C00287 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Limestone Road, Salyersville, KY. | 2020-01-16
2020 | 2020-01-16 | Pikeville |  |  | 38830876D00105 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 371 Limestone Branch Rd, Salyersville, KY 41465, USA | 2020-05-19
2020 | 2020-01-17 | Pikeville |  |  | 38830875A00322 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | US-460, Salyersville, KY, USA | 2020-01-17
2020 | 2020-01-17 | Pikeville | 76370962 | DKY0109732 | 38830875A00536 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown. Behind the IGA | 288 Parkway Dr, Salyersville, KY 41465, USA | 2021-01-20
2020 | 2020-01-17 | Pikeville |  |  | 38830875A30252 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Gardner Trail, Salyersville, KY 41465, USA | 2020-01-17
2020 | 2020-01-17 | Pikeville |  |  | 38830875C00016 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Flossie May Drive, Salyersville, KY. | 2020-01-17
2020 | 2020-01-17 | Pikeville |  |  | 38830875C00046 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | US-460, Salyersville, KY, USA | 2020-01-17
2020 | 2020-01-17 | Pikeville |  |  | 38830875C00197 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | 322 Allen Dr, Salyersville, KY 41465, USA | 2020-01-17
2020 | 2020-01-17 | Pikeville |  |  | 38830875C00199 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | 600 Allen Dr, Salyersville, KY 41465, USA | 2020-01-17
2020 | 2020-01-17 | Pikeville |  |  | 38830875C00380 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | 695 Parkway Dr, Salyersville, KY 41465, USA
2020 | 2020-01-17 | Pikeville |  |  | 38830875C00508 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Parkway Dr, Salyersville, KY 41465, USA | 2020-01-17
2020 | 2020-01-17 | Pikeville |  |  | 38830875C00508 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Parkway Dr, Salyersville, KY 41465, USA | 2020-01-17
2020 | 2020-01-17 | Pikeville |  |  | 38830875C00554 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Parkway Dr, Salyersville, KY 41465, USA | 2020-01-17
2020 | 2020-01-17 | Pikeville |  |  | 38830875C00571 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Allen Dr, Salyersville, KY 41465, USA | 2020-01-17
2020 | 2020-01-17 | Pikeville | 76370962 | DKY0109732 | 38830875C00743 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 817 Parkway Dr, Salyersville, KY 41465, USA | 2021-01-20
2020 | 2020-01-17 | Pikeville |  |  | 38830875C10993 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | US-460, Salyersville, KY, USA | 2020-01-17
2020 | 2020-01-17 | Pikeville |  |  | 38830876B00257 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Old Burning Fork Rd, Salyersville, KY 41465, USA | 2020-01-17
2020 | 2020-01-17 | Pikeville |  |  | 38830876B00380 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Old Burning Fork Rd, Salyersville, KY 41465, USA | 2020-01-17
2020 | 2020-01-20 | Pikeville |  |  | 38830875C00683 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | East Mtn. Pkwy. Salyersville, KY. | 2020-01-20
2020 | 2020-01-20 | Pikeville | 76370962 | DKY0109732 | 38830875D00077 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole. Stolen all the way up to phone cable. | 379 Lick Fork, Salyersville, KY. | 2021-01-20
2020 | 2020-01-20 | Pikeville |  |  | 38830876B00028 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on recloser pole | Old Burning Fork Road, Salyersville, KY. | 2020-01-20
2020 | 2020-01-20 | Pikeville |  |  | 38830876B00028 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on recloser pole | Old Burning Fork Road, Salyersville, KY. | 2020-01-20
2020 | 2020-01-20 | Pikeville |  |  | 38830876B00028 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on recloser pole | Old Burning Fork Road, Salyersville, KY. | 2020-01-20
2020 | 2020-01-20 | Pikeville | 76370962 | DKY0109732 | 38830876B00284 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive transformer and service. Transformer de-energized. | Rockhouse Fork Road, Salyersville, KY. | 2021-01-20
2020 | 2020-01-20 | Pikeville |  |  | 38830876B00327 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Secondary pole covered in vines. Behind Fast Lane tobacco. | 635 East Mtn. Pkwy, Salyersville, KY.
2020 | 2020-01-20 | Pikeville |  |  | 38830876B40787 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | U.S. 460, Salyersville, KY. | 2020-01-20
2020 | 2020-01-20 | Pikeville | WR # 75612527 |  | 38830876D20842 |  | 3401103-FALCON / BURNINGFK | Service Work | UG | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Underground service conductor exposed. Customer breaker is off but meter is still energized. Sealed the breaker box for safety and contacted MRO SUPERVISOR TO HAVE THE METER BOOTED OR BLANKED OFF. MRO SUPERVISOR SAID HE WOULD HAVE IT TAKEN CARE OF. Mobile home has been moved out. @ Mobile home park on left before getting into Salyersville. | U.S. 460, Salyersville, KY. | 2020-01-20
2020 | 2020-01-20 | Pikeville |  |  | 38830876D20845 |  | 3401103-FALCON / BURNINGFK | Line Work | UG | UG conduit: damaged or separated |  |  | KPC | NO | Underground pedestal knocked over. Potential exposure of secondary conductors. @ Mobile home park on left before you get into Salyersville. | U.S. 460, Salyersville, KY.
2020 | 2020-01-21 | Pikeville |  |  | 38830876B00246 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Cain Drive, Salyersville, KY. | 2020-01-21
2020 | 2020-01-21 | Pikeville | 76370940 | DKY0109713 | 38830900000005 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken. Hanging down pole. Anchor rusted off. Will need to install anchor. 3 phase angle pole. | 1870 Old Burning Fork Road, Salyersville, KY. | 2022-05-05
2020 | 2020-01-21 | Pikeville |  |  | 38830900000070 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 2548 Old Burning Fork Road, Salyersville, KY. | 2020-01-21
2020 | 2020-01-21 | Pikeville |  |  | 38830900000223 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Willow Drive, Salyersville, KY. | 2020-01-21
2020 | 2020-01-21 | Pikeville |  |  | 38830900A30124 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Cain Drive, Salyersville, KY. | 2020-01-21
2020 | 2020-01-21 | Pikeville |  |  | 38830900D10299 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Baseball Drive, Salyersville, KY. | 2020-01-21
2020 | 2020-01-22 | Pikeville |  |  | 38830900000027 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Bellows Road, Salyersville, KY. | 2020-01-22
2020 | 2020-01-22 | Pikeville | 76370940 | DKY0109713 | 38830900000166 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm braces broken. | 3189 Old Burning Fork Road, Salyersville, KY. | 2022-05-05
2020 | 2020-01-22 | Pikeville |  |  | 38830900000252 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Bellows Road, Salyersville, KY. | 2020-01-22
2020 | 2020-01-22 | Pikeville |  |  | 38830901000141 |  | 3401103-FALCON / BURNINGFK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. | 3460 Old Burning Fork Road, Bradley, KY. | 2020-01-22
2020 | 2020-01-22 | Pikeville |  |  | 38830901000141 |  | 3401103-FALCON / BURNINGFK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. | 3460 Old Burning Fork Road, Bradley, KY. | 2020-01-22
2020 | 2020-01-22 | Pikeville |  |  | 38830901000141 |  | 3401103-FALCON / BURNINGFK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. | 3460 Old Burning Fork Road, Bradley, KY. | 2020-01-22
2020 | 2020-01-22 | Pikeville |  |  | 38830924000027 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Jim Arnett Branch Road, Salyersville, KY. | 2020-01-22
2020 | 2020-01-22 | Pikeville | 76371296 | DKY0109868 | 38830924C40078 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole washed out around in creek. It’s a fairly new pole, could potentially use and reset. Pole was installed in 2008. Angle pole. | Jim Arnett Branch Road, Salyersville, KY. | 2021-09-27
2020 | 2020-01-23 | Pikeville |  |  | 38830901000204 |  | 3401103-FALCON / BURNINGFK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop laying on roof top. Enough slack can be taken out I believe for clearance. | 3944 Old Burning Fork Road, Ivyton, KY.
2020 | 2020-01-23 | Pikeville | 76371463 | DKY0109967 | 38830925000047 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  |  | STOLEN NEUTRAL | KPC | NO | Neutral conductor down/stolen. #4 copper | 440 Ivyton Road, Salyersville, KY. | 2021-01-14
2020 | 2020-01-24 | Pikeville | 76370940 | DKY0109713 | 38830901000116 | TRUE | 3401103-FALCON / BURNINGFK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | YES | Primary conductor floating. Pole washed out around. No truck.@ Short Fork Road. First pole towards Salyersville. | East Mtn. Pkwy, Salyersville, KY. | 2022-05-05
2020 | 2020-01-24 | Pikeville |  |  | 38830901000126 |  | 3401103-FALCON / BURNINGFK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole | 67 Short Fork Road, Salyersville, KY.
2020 | 2020-01-24 | Pikeville |  |  | 38830901000212 |  | 3401103-FALCON / BURNINGFK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole | Trojan Powder Road, Salyersville, KY. | 2020-01-24
2020 | 2020-01-24 | Pikeville |  |  | 38830901000212 |  | 3401103-FALCON / BURNINGFK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole | Trojan Powder Road, Salyersville, KY. | 2020-01-24
2020 | 2020-01-24 | Pikeville |  |  | 38830925000024 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | East Mtn Pkwy, Ivyton, KY. | 2020-01-24
2020 | 2020-01-24 | Pikeville |  |  | 38830925C40203 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | East Mtn Pkwy, Ivyton, KY. | 2020-01-24
2020 | 2020-01-24 | Pikeville |  |  | 38830926000030 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | East Mtn Pkwy. Ivyton, KY. | 2020-01-24
2020 | 2020-01-27 | Pikeville | 76371709 | DKY0109963 | 38830785C30548 |  | 3420101-MAYO TRAIL / NIPPA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten. Take-off pole @ Wells Hollow | 642 Boyd Branch, Paintsville, KY. | 2023-10-11
2020 | 2020-01-27 | Pikeville | 76371177 | DKY0109793 | 38830785C31352 |  | 3420101-MAYO TRAIL / NIPPA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Pole top insulator broken | 61 Smokey Hollow, Boyd Branch, Paintsville, KY. | 2021-02-02
2020 | 2020-01-27 | Pikeville | 76493932 | DKY0109502 | 38830786A00106 |  | 3420101-MAYO TRAIL / NIPPA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole is burned. @ mouth of Boyd Branch. Take-off pole for Rockhouse road. | KY. Route 581, Paintsville, KY. | 2020-05-18
2020 | 2020-01-28 | Pikeville |  |  | 38830738B00014 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground cut on fuse pole | 1145 KY. Route 993, Paintsville, KY. | 2020-01-28
2020 | 2020-01-28 | Pikeville |  |  | 38830738B00014 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground cut on fuse pole | 1145 KY. Route 993, Paintsville, KY. | 2020-01-28
2020 | 2020-01-28 | Pikeville |  |  | 38830738B00014 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground cut on fuse pole | 1145 KY. Route 993, Paintsville, KY. | 2020-01-28
2020 | 2020-01-28 | Pikeville |  |  | 38830738B00014 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground cut on fuse pole | 1145 KY. Route 993, Paintsville, KY. | 2020-01-28
2020 | 2020-01-28 | Pikeville |  |  | 38830738B00100 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY. Route 993, Paintsville, KY. | 2020-01-28
2020 | 2020-01-28 | Pikeville |  |  | 38830738B00114 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 651 KY. Route 993, Paintsville, KY. | 2020-01-28
2020 | 2020-01-28 | Pikeville |  |  | 38830738B00114 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 651 KY. Route 993, Paintsville, KY. | 2020-01-28
2020 | 2020-01-28 | Pikeville | 76371152 | DKY0109742 | 38830738C00150 |  | 3420101-MAYO TRAIL / NIPPA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer and service. Arrestor blown. | 979 Baker Branch, Paintsville, KY. | 2020-07-22
2020 | 2020-01-28 | Pikeville | 76371152 | DKY0109742 | 38830738D00023 |  | 3420101-MAYO TRAIL / NIPPA | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire hanging down pole. Will need to install new anchor. Can use truck | 1529 KY. Route 993, Paintsville, KY. | 2020-07-22
2020 | 2020-01-28 | Pikeville | 76371152 | DKY0109742 | 38830738D00192 |  | 3420101-MAYO TRAIL / NIPPA | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Anchor washed out. Needs replacing. | 1140 KY. Route 993, Paintsville, KY. | 2020-07-22
2020 | 2020-01-29 | Pikeville | 76371561 | DKY0109807 | 38830714000006 |  | 3420101-MAYO TRAIL / NIPPA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | lightning arresters/insulators: damaged |  | KPC | YES | Pole is rotten/ hollow. Lightning arrestor blown. 40 class 5 pole. Installed 1948. | 822 Lindy Branch, Paintsville, KY. | 2022-10-24
2020 | 2020-01-29 | Pikeville | 76371177 | DKY0109793 | 38830714000018 |  | 3420101-MAYO TRAIL / NIPPA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 822 Lindy Branch, Paintsville, KY. | 2021-02-02
2020 | 2020-01-29 | Pikeville |  |  | 38830738A00065 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer bank | 81 Church Drive, KY. Route 1559, Paintsville, KY. | 2020-01-29
2020 | 2020-01-29 | Pikeville |  |  | 38830738A00065 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer bank | 81 Church Drive, KY. Route 1559, Paintsville, KY. | 2020-01-29
2020 | 2020-01-29 | Pikeville |  |  | 38830738A00065 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer bank | 81 Church Drive, KY. Route 1559, Paintsville, KY. | 2020-01-29
2020 | 2020-01-29 | Pikeville |  |  | 38830738A00065 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer bank | 81 Church Drive, KY. Route 1559, Paintsville, KY. | 2020-01-29
2020 | 2020-01-29 | Pikeville |  |  | 38830738A00065 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer bank | 81 Church Drive, KY. Route 1559, Paintsville, KY. | 2020-01-29
2020 | 2020-01-29 | Pikeville |  |  | 38830738A00065 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer bank | 81 Church Drive, KY. Route 1559, Paintsville, KY. | 2020-01-29
2020 | 2020-01-29 | Pikeville |  |  | 38830738A00078 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 491 Hilltop Road, KY. Route 1559, Paintsville, KY. | 2020-01-29
2020 | 2020-01-29 | Pikeville | 76371177 | DKY0109793 | 38830738A00175 |  | 3420101-MAYO TRAIL / NIPPA | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken, hanging down pole. Will need to install anchor. Truck accessible. | Ceramics Drive, KY. Route 1559, Paintsville, KY. | 2021-02-02
2020 | 2020-01-29 | Pikeville |  |  | 38830738A00264 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 226 Rfk Lindy Branch, Paintsville, KY. | 2020-01-29
2020 | 2020-01-29 | Pikeville |  |  | 38830738A00264 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 226 Rfk Lindy Branch, Paintsville, KY. | 2020-01-29
2020 | 2020-01-29 | Pikeville | 76371177 | DKY0109793 | 38830738A00412 |  | 3420101-MAYO TRAIL / NIPPA | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire hanging down pole/ pole leaning. Also has satellite dish on pole. May or may not be truck access to anchor. Might need rockeye. | 64 Lindy Branch, Paintsville, KY. | 2021-02-02
2020 | 2020-01-30 | Pikeville |  |  | 38830785D30088 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Brown Branch, Paintsville, KY. | 2020-01-30
2020 | 2020-01-30 | Pikeville |  |  | 38830786B00071 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY. Route 581, Paintsville. KY. | 2020-01-30
2020 | 2020-01-30 | Pikeville |  |  | 38830786B00462 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Green town loop, Paintsville, KY. | 2020-01-30
2020 | 2020-01-30 | Pikeville | 76371201 | DKY0109747 | 38830810A00092 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Ponderosa Drive, Paintsville, KY. | 2021-01-18
2020 | 2020-01-31 | Pikeville | 69255600 | DKY0099328 | 38830785D40106 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten/hollow. Conductors cross railroad tracks. Buckarm pole. 45 class 2 pole. Set in 1960. Might want to have flaggers because of closeness to RR. This pole has been inspected before by someone. Already had rotten pole tag on it. | KY. Route 581, Paintsville, KY. | 2022-03-08
2020 | 2020-01-31 | Pikeville | 76371833 | DKY0109668 | 38830785D40116 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground. 45 class 5 pole. Installed 1968. In front of apartment bldgs. | 600 Euclid Avenue, Paintsville, KY. | 2023-02-25
2020 | 2020-01-31 | Pikeville | 76371765 | DKY0109705 | 38830785D40132 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground. 45 class 5 pole. Installed 1973 | 227 Preston Street, Paintsville, KY. | 2020-12-11
2020 | 2020-01-31 | Pikeville |  |  | 38830785D40137 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Highland Avenue, Paintsville, KY. | 2020-01-31
2020 | 2020-01-31 | Pikeville | 76371780 | DKY0109910 | 38830785D40149 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | CONCRETE pole has large crack going up to Telecomm cable. | 309 Euclid Avenue, Paintsville, KY. | 2023-02-25
2020 | 2020-01-31 | Pikeville |  |  | 38830785D40153 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | 210 Frank Street, Paintsville, KY. | 2020-01-31
2020 | 2020-01-31 | Pikeville |  |  | 38830785D40356 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | State Street, Paintsville, KY. | 2020-01-31
2020 | 2020-01-31 | Pikeville | 76371754 | DKY0109676 | 38830785D40500 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground and hollow. 40 class 5 pole. Installed 1969 | Highland Avenue, Paintsville, KY. | 2020-12-11
2020 | 2020-01-31 | Pikeville |  |  | 38830785D40501 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Highland Avenue, Paintsville, KY. | 2020-01-31
2020 | 2020-01-31 | Pikeville |  |  | 38830785D40501 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Highland Avenue, Paintsville, KY. | 2020-01-31
2020 | 2020-01-31 | Pikeville |  |  | 38830785D40641 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Depot Road, Paintsville, KY. | 2020-01-31
2020 | 2020-01-31 | Pikeville |  |  | 38830785D40642 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning considerably. Conductors cross bridge and river. Has transformer bank on it and 3 phase drop. | 104 Depot Road, Paintsville, KY.
2020 | 2020-01-31 | Pikeville |  |  | 38830785D40988 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | River Road, Paintsville, KY. | 2020-01-31
2020 | 2020-01-31 | Pikeville |  |  | 38830786B00059 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lewis Drive, Paintsville, KY. | 2020-01-31
2020 | 2020-01-31 | Pikeville |  |  | 38830786B00059 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lewis Drive, Paintsville, KY. | 2020-01-31
2020 | 2020-01-31 | Pikeville | 76371733 | DKY0109708 | 38830809C30078 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | YES | Outer shell of pole is rotten. Guy wire needs marker. Installed guy marker. 40 class 2 pole. Installed 1980 | River Road, Paintsville, KY. | 2020-06-04
2020 | 2020-01-31 | Pikeville |  |  | 38830809C30325 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | River Road, Paintsville, KY. | 2020-01-31
2020 | 2020-02-03 | Pikeville |  |  | 38830809C10167 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Broadway Street, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville |  |  | 38830809C10169 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Broadway Street, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville |  |  | 38830809C10330 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Broadway Street, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville | 76371911 | DKY0109628 | 38830809C30102 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is in early stage of rot at ground line. 30 class 5 pole. It’s tagged as pole 100 but field view shows it to be pole 102. | 813 Broadway Street, Paintsville, KY. | 2020-12-08
2020 | 2020-02-03 | Pikeville |  |  | 38830809C30126 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 116 12th Street, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville |  |  | 38830809C30127 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 204 12th Street, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville | 76371197 | DKY0109786 | 38830809C30133 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH |  | lightning arresters/insulators: damaged , guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Lightning arrestor blown. Also needs guy marker. Installed the marker. | 824 12th Street, Paintsville, KY. | 2021-01-19
2020 | 2020-02-03 | Pikeville |  |  | 38830809C30161 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Broadway Street, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville |  |  | 38830809C30177 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Woodland Drive, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville |  |  | 38830809C30177 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Woodland Drive, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville |  |  | 38830809C30351 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Pine Street, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville | 76371869 | DKY0109602 | 38830809C30360 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Outer shell of pole is rotten. 35 class 5 pole. | 1008 Maple Street, Paintsville, KY. | 2020-06-03
2020 | 2020-02-03 | Pikeville |  |  | 38830809C30361 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Maple street, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville |  |  | 38830809C30370 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Depot Road, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville |  |  | 38830809C30372 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Boyd Street, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville |  |  | 38830809C30382 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Pine Street, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville |  |  | 38830809C30388 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Broadway Street, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville | 76371909 | DKY0109563 | 38830809C30482 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole in early stage of rot at ground line. 30 class 5 pole. Installed in 1964 | 813 Broadway Street, Paintsville, KY. | 2020-05-27
2020 | 2020-02-03 | Pikeville |  |  | 38830809C30514 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Stafford Avenue, Paintsville, KY. | 2020-02-03
2020 | 2020-02-03 | Pikeville | 76371201 | DKY0109747 | 38830809C30546 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 247 Pine Street, Paintsville, KY. | 2021-01-18
2020 | 2020-02-03 | Pikeville |  |  | 38830809C40355 |  | 3420102-MAYO TRAIL / EUCLID | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Large rotten tree laying on secondary. Has adjacent poles under stress. Guy wire needs marker. Installed the marker. Top of hill @ Depot street and Turkey knob street. | 635 Depot Street, Paintsville, KY. | 2020-05-08
2020 | 2020-02-04 | Pikeville |  |  | 38830809000190 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 6th Street, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809000233 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Jennifer Drive, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C10051 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 6th Street, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville | 83967642 | DKY0121366 | 38830809C10290 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker , transformers: leaking, damaged |  | KPC | NEEDS ADDITIONAL CHECK | Transformer is barely hanging on bracket. Will need to install new bracket and maybe transformer too. Guy wire needs marker. Installed marker. | Madison Avenue, Paintsville, KY. | 2023-08-22
2020 | 2020-02-04 | Pikeville |  |  | 38830809C10297 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 7th Street, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C10300 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 7th Street, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville | 76371197 | DKY0109786 | 38830809C10432 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire hanging down pole. Guy wire rusted off at ground. Anchor is buried. Will probably need to install new anchor. | FM Stafford Avenue, Paintsville, KY. | 2021-01-19
2020 | 2020-02-04 | Pikeville |  |  | 38830809C10768 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Madison Avenue, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C10768 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Madison Avenue, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C10768 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Madison Avenue, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C30086 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Jefferson Avenue, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C30088 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Jefferson Street, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C30106 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 11th Street, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C30354 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 10th Street, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C30496 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | FM Stafford Avenue, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C30496 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | FM Stafford Avenue, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C30496 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | FM Stafford Avenue, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C30583 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Lincoln Avenue, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C40276 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Pine view Lane, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C40795 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ridge Point View Court, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville | 76371197 | DKY0109786 | 38830809C40841 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken | KY. 321 North, Paintsville, KY. | 2021-01-19
2020 | 2020-02-04 | Pikeville |  |  | 38830809C40935 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY. 321 North, Paintsville, KY. | 2020-02-04
2020 | 2020-02-04 | Pikeville |  |  | 38830809C41058 |  | 3420102-MAYO TRAIL / EUCLID | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Pine view Lane, Paintsville, KY. | 2020-02-04
2020 | 2020-02-05 | Pikeville | 76371201 | DKY0109747 | 38830810A00084 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH |  | lightning arresters/insulators: damaged , guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Lightning arrestor blown. Guy wire needs marker. Installed marker. | River Road, Paintsville, KY. | 2021-01-18
2020 | 2020-02-05 | Pikeville |  |  | 38830851B00166 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 160 Broadway Street, Salyersville, KY. | 2020-02-05
2020 | 2020-02-05 | Pikeville |  |  | 38830851B00559 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 353 Broadway Street, Salyersville, KY. | 2020-02-05
2020 | 2020-02-05 | Pikeville |  |  | 38830851B00559 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 353 Broadway Street, Salyersville, KY. | 2020-02-05
2020 | 2020-02-05 | Pikeville |  |  | 38830851C00146 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 1537 East Maple Street, Salyersville, KY. | 2020-02-05
2020 | 2020-02-05 | Pikeville |  |  | 38830851C00207 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Collins Road, Salyersville, KY. | 2020-02-05
2020 | 2020-02-05 | Pikeville | 76370871 | DKY0109632 | 38830851C00420 |  | 3401102-FALCON / SALYERSVI | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | End of crossarm is split/ rotten. Just above Mile Branch Road on right. Pole seems ok but it was set in 1964. | Falcon Road, Salyersville, KY.
2020 | 2020-02-05 | Pikeville |  |  | 38830851C00561 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Bennie Patrick Road, Salyersville, Ky | 2020-02-05
2020 | 2020-02-05 | Pikeville | 76370849 | DKY0109649 | 38830851D00362 |  | 3401102-FALCON / SALYERSVI | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm deteoriated/ split on the end. Just above Will May Branch on left. | 1032 East Maple Street, Salyersville, KY. | 2022-07-25
2020 | 2020-02-05 | Pikeville | 76370871 | DKY0109632 | 38830852000106 |  | 3401102-FALCON / SALYERSVI | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown. Also Satellite dish on pole. Directv. | 2319 Falcon Road,Salyersville, KY.
2020 | 2020-02-05 | Pikeville | 76370871 | DKY0109632 | 38830852000119 |  | 3401102-FALCON / SALYERSVI | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm burnt in two. Might be truck access when dry with permission from property owner. 3 phase angle pole. | 2113 Falcon Road,Salyersville, KY.
2020 | 2020-02-07 | Pikeville |  |  | 38830826000041 |  | 3401102-FALCON / SALYERSVI | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Rolled up at base of pole. | Long Branch Rd, Kentucky 41465, USA | 2020-02-07
2020 | 2020-02-07 | Pikeville |  |  | 38830826000041 |  | 3401102-FALCON / SALYERSVI | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Rolled up at base of pole. | Long Branch Rd, Kentucky 41465, USA | 2020-02-07
2020 | 2020-02-07 | Pikeville | 76370849 | DKY0109649 | 38830826000046 |  | 3401102-FALCON / SALYERSVI | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and service. Transformer near waterway. Last pole in Long Branch. | Long Branch Road, Salyersville, KY. | 2022-07-25
2020 | 2020-02-07 | Pikeville |  |  | 38830851B00543 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Meade Dr, Salyersville, KY 41465, USA | 2020-02-07
2020 | 2020-02-07 | Pikeville |  |  | 38830851B00632 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Waterworks Street, Salyersville, KY. | 2020-02-07
2020 | 2020-02-07 | Pikeville |  |  | 38830875A00147 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | W Maple St, Salyersville, KY 41465, USA | 2020-02-07
2020 | 2020-02-07 | Pikeville |  |  | 38830875A00147 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | W Maple St, Salyersville, KY 41465, USA | 2020-02-07
2020 | 2020-02-10 | Pikeville |  |  | 38830849D20088 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Middle Fork, Salyersville, KY. | 2020-02-10
2020 | 2020-02-10 | Pikeville | 76370918 | DKY0109693 | 38830849D40083 |  | 3401102-FALCON / SALYERSVI | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire hanging down pole. Pole seems to be fine. Do not see the anchor anywhere. Probably need to install new anchor on hill. Customer has a bunch of equipment parked where anchor was apparently. Might be able to use truck when dry or frozen. | Middle Fork, Salyersville, KY. | 2021-01-21
2020 | 2020-02-11 | Pikeville |  |  | 38830850000080 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Will May Branch, Salyersville, KY. | 2020-02-11
2020 | 2020-02-11 | Pikeville | 76370849 | DKY0109649 | 38830850000112 |  | 3401102-FALCON / SALYERSVI | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Primary conductor floating. Needs to be re-tied. | 331 Elk Creek Road, Salyersville, KY. | 2022-07-25
2020 | 2020-02-11 | Pikeville |  |  | 38830850000154 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Will May Branch, Salyersville, KY. | 2020-02-11
2020 | 2020-02-11 | Pikeville | 76371285 | DKY0109818 | 38830851A00416 |  | 3401102-FALCON / SALYERSVI | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground. 35 class 5 pole. Last house in Cornbread Hollow. | 736 Cornbread Hollow, Salyersville, KY. | 2020-12-09
2020 | 2020-02-12 | Pikeville |  |  | 38830850000142 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | West 460, Salyersville, KY. | 2020-02-12
2020 | 2020-02-12 | Pikeville |  |  | 38830874000063 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY. Route 30, Salyersville, KY. | 2020-02-12
2020 | 2020-02-12 | Pikeville |  |  | 38830874000063 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY. Route 30, Salyersville, KY. | 2020-02-12
2020 | 2020-02-12 | Pikeville |  |  | 38830874000063 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY. Route 30, Salyersville, KY. | 2020-02-12
2020 | 2020-02-12 | Pikeville |  |  | 38830875A00541 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dixie Avenue, Salyersville, KY. | 2020-02-12
2020 | 2020-02-12 | Pikeville |  |  | 38830875A00541 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dixie Avenue, Salyersville, KY. | 2020-02-12
2020 | 2020-02-12 | Pikeville |  |  | 38830875A30528 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dixie Avenue, Salyersville, KY. | 2020-02-12
2020 | 2020-02-13 | Pikeville |  |  | 38830875A00002 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | May Drive, Salyersville, KY. | 2020-02-13
2020 | 2020-02-13 | Pikeville |  |  | 38830875A00053 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Combs Street, Salyersville, KY. | 2020-02-13
2020 | 2020-02-13 | Pikeville |  |  | 38830875A00127 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Kentucky Street, Salyersville, KY. | 2020-02-13
2020 | 2020-02-13 | Pikeville |  |  | 38830875A00177 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dixie Avenue, Salyersville, KY. | 2020-02-13
2020 | 2020-02-13 | Pikeville |  |  | 38830875A00205 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Gardner Trail, Salyersville, KY. | 2020-02-13
2020 | 2020-02-13 | Pikeville | 76370918 | DKY0109693 | 38830875A00230 |  | 3401102-FALCON / SALYERSVI | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown on transformer bank. Behind Learning Center on Gardner Trail. | Lemaster Road, Salyersville, KY. | 2021-01-21
2020 | 2020-02-13 | Pikeville |  |  | 38830875A00256 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dixie Avenue, Salyersville, KY. | 2020-02-13
2020 | 2020-02-13 | Pikeville |  |  | 38830875A00256 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dixie Avenue, Salyersville, KY. | 2020-02-13
2020 | 2020-02-13 | Pikeville |  |  | 38830875A00326 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | May Drive, Salyersville, KY. | 2020-02-13
2020 | 2020-02-13 | Pikeville |  |  | 38830875A00326 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | May Drive, Salyersville, KY. | 2020-02-13
2020 | 2020-02-13 | Pikeville |  |  | 38830875A00494 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lemaster Road, Salyersville, KY. | 2020-02-13
2020 | 2020-02-13 | Pikeville |  |  | 38830875A00494 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lemaster Road, Salyersville, KY. | 2020-02-13
2020 | 2020-02-13 | Pikeville | 76370918 | DKY0109693 | 38830875A00495 |  | 3401101-FALCON / FALC-OILS | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown. Might be truck access when dry. | 440 Cardinal Court, Salyersville, KY. | 2021-01-21
2020 | 2020-02-13 | Pikeville |  |  | 38830875A30204 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Gardner Trail, Salyersville, KY. | 2020-02-13
2020 | 2020-02-13 | Pikeville |  |  | 38830875A30702 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Gardner Trail, Salyersville, KY. | 2020-02-13
2020 | 2020-02-14 | Pikeville | 73877102 | DKY0108616 | 38821131000015 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | reported by TRC - added to defect tracker on 02/14/2020 with info from email - PRB | May Branch | 2020-03-05
2020 | 2020-02-14 | Pikeville | 76370918 | DKY0109693 | 38830875A00235 |  | 3401102-FALCON / SALYERSVI | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown. | 470 Gardner Trail, Salyersville, Ky. | 2021-01-21
2020 | 2020-02-14 | Pikeville |  |  | 38830875A00255 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | College Street, Salyersville, Ky. | 2020-02-14
2020 | 2020-02-14 | Pikeville |  |  | 38830875A00268 |  | 3401102-FALCON / SALYERSVI | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Elam Street, Salyersville, Ky. | 2020-05-19
2020 | 2020-02-14 | Pikeville |  |  | 38830875A00285 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Minix Drive, Salyersville, Ky. | 2020-02-14
2020 | 2020-02-14 | Pikeville |  |  | 38830875A00286 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Minix Drive, Salyersville, Ky. | 2020-02-14
2020 | 2020-02-14 | Pikeville |  |  | 38830875B00059 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | College Street, Salyersville, Ky. | 2020-02-14
2020 | 2020-02-14 | Pikeville |  |  | 38830875B00263 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | College Street, Salyersville, Ky. | 2020-02-14
2020 | 2020-02-14 | Pikeville |  |  | 38830875B00447 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Superior Road, Salyersville, Ky. | 2020-02-14
2020 | 2020-02-14 | Pikeville |  |  | 38830875B00447 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Superior Road, Salyersville, Ky. | 2020-02-14
2020 | 2020-02-14 | Pikeville |  |  | 38830875B00620 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | College Street, Salyersville, Ky. | 2020-02-14
2020 | 2020-02-17 | Pikeville |  |  | 37820149000055 |  | 3403701-RUSSELLFO / LITTLEBEA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Beaver Creek Road, Elkhorn City, Ky. | 2020-02-17
2020 | 2020-02-17 | Pikeville |  |  | 37820149000055 |  | 3403701-RUSSELLFO / LITTLEBEA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Beaver Creek Road, Elkhorn City, Ky. | 2020-02-17
2020 | 2020-02-17 | Pikeville |  |  | 37820149000055 |  | 3403701-RUSSELLFO / LITTLEBEA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Beaver Creek Road, Elkhorn City, Ky. | 2020-02-17
2020 | 2020-02-17 | Pikeville |  |  | 37820149000096 |  | 3403701-RUSSELLFO / LITTLEBEA | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen on switch pole/ open point. | Beaver Creek Road, Elkhorn City, Ky. | 2020-02-17
2020 | 2020-02-17 | Pikeville | 84844048 |  | 37820173000063 |  | 3403701-RUSSELLFO / LITTLEBEA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole washed out around. Just below the station. IN STATION ZONE. | Lfk Little Beaver, Elkhorn City, Ky.
2020 | 2020-02-17 | Pikeville |  |  | 37820173B30133 |  | 3403701-RUSSELLFO / LITTLEBEA | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on recloser pole. | Lfk Little Beaver, Elkhorn City, Ky. | 2020-02-17
2020 | 2020-02-17 | Pikeville |  |  | 37820173B30133 |  | 3403701-RUSSELLFO / LITTLEBEA | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on recloser pole. | Lfk Little Beaver, Elkhorn City, Ky. | 2020-02-17
2020 | 2020-02-18 | Pikeville | 76958874 | DKY0111514 | 37820196000097 |  | 3403701-RUSSELLFO / LITTLEBEA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground. VERY BAD SHAPE. 45 class 5 pole. Contacted SDS by email to have this pole replaced soon. | 955 Little Beaver Road, Elkhorn City, Ky. | 2020-11-05
2020 | 2020-02-18 | Pikeville |  |  | 37820196000259 |  | 3403701-RUSSELLFO / LITTLEBEA | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Removed drop. | 939 Little Beaver Road, Elkhorn City, Ky. | 2020-02-18
2020 | 2020-02-18 | Pikeville |  |  | 37820197000075 | TRUE | 3403701-RUSSELLFO / LITTLEBEA | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Crossarm brace broken. | 645 Rfk Little Beaver Road, Elkhorn City, Ky.
2020 | 2020-02-18 | Pikeville |  |  | 37820197000172 |  | 3403701-RUSSELLFO / LITTLEBEA | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Removed drop. | 1558 Rfk Little Beaver, Elkhorn City, Ky. | 2020-02-18
2020 | 2020-02-18 | Pikeville |  |  | 37820197000225 |  | 3403701-RUSSELLFO / LITTLEBEA | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Removed drop. | Lfk Little Beaver Road, Elkhorn City, Ky. | 2020-02-18
2020 | 2020-02-18 | Pikeville |  |  | 37820197000225 |  | 3403701-RUSSELLFO / LITTLEBEA | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Removed drop. | Lfk Little Beaver Road, Elkhorn City, Ky. | 2020-02-18
2020 | 2020-02-19 | Pikeville |  |  | 37820198000025 |  | 3403701-RUSSELLFO / LITTLEBEA | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Removed drop. | Trace Fork Road, Elkhorn City, Ky. | 2020-02-19
2020 | 2020-02-19 | Pikeville |  |  | 37820220C20124 |  | 3421001-BREAKS/CITY | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign | NO | Primary conductor floating. Needs to be re-tied . @ Dollar General store. | 130 East Elkhorn Street, Elkhorn City, Ky.
2020 | 2020-02-20 | Pikeville |  |  | 37820147B00163 |  | 3400702-DRAFFIN / YELLOWHIL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 140 Yellow Hill Spur, Regina, Ky. | 2020-02-20
2020 | 2020-02-21 | Pikeville |  |  | 37820123000083 |  | 3400702-DRAFFIN / YELLOWHIL | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Service drop hanging down pole. Removed drop | Frankie Fork, Harless Creek, Regina, Ky.
2020 | 2020-02-21 | Pikeville |  |  | 37820147A00183 |  | 3400702-DRAFFIN / YELLOWHIL | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen on transformer pole | 660 Harless Creek Road, Regina, Ky.
2020 | 2020-02-21 | Pikeville |  |  | 37820147C00515 |  | 3400702-DRAFFIN / YELLOWHIL | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Removed drop | 1190 Jimmies Creek Road, Regina, Ky. | 2020-02-21
2020 | 2020-02-24 | Pikeville |  |  | 37820148000019 |  | 3400701-DRAFFIN / BELCHER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 1873 Road Creek, Draffin, Ky. | 2020-02-24
2020 | 2020-02-25 | Pikeville |  |  | 37820171D00135 |  | 3400701-DRAFFIN / BELCHER | Line Work | OH |  | lightning arresters/insulators: damaged , guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Lightning arrestor blown. Guy wire needs marker. Installed marker. Might be truck access if dry. | 661 Jessie Branch, Belcher, Ky.
2020 | 2020-02-25 | Pikeville |  |  | 37820171D00155 |  | 3400701-DRAFFIN / BELCHER | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. | 14723 Regina/Belcher Hwy, Belcher, Ky.
2020 | 2020-02-25 | Pikeville |  |  | 37820172000014 |  | 3400701-DRAFFIN / BELCHER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Ferrells Creek Road. Belcher, Ky. | 2020-02-25
2020 | 2020-02-25 | Pikeville |  |  | 37820172000014 |  | 3400701-DRAFFIN / BELCHER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Ferrells Creek Road. Belcher, Ky. | 2020-02-25
2020 | 2020-02-25 | Pikeville | 84844179 | DKY0121362 | 37820172000232 | TRUE | 3400701-DRAFFIN / BELCHER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at ground line. | 15667 Ferrells Creek Road, Belcher, Ky. | 2023-10-02
2020 | 2020-02-25 | Pikeville | 76958775 | DKY0111458 | 37820172000257 | TRUE | 3400701-DRAFFIN / BELCHER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line. 35 class 5 pole. | 139 Blue Pond, Belcher, Ky. | 2022-06-28
2020 | 2020-02-25 | Pikeville | 86691083 |  | 37820195000003 |  | 3400701-DRAFFIN / BELCHER | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap, De-energized primary conductor hanging down pole. Need to remove entire lateral to pole 37820195000076 | 100 Jessie Branch, Belcher, Ky.
2020 | 2020-02-26 | Pikeville |  |  | 37820148000072 |  | 3400701-DRAFFIN / BELCHER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NO | Top of pole has two pretty good size holes. It seems solid at ground line. Probably good enough until next inspection cycle. | 804 Honey Fork, Belcher, Ky.
2020 | 2020-02-26 | Pikeville |  |  | 37820172000145 |  | 3400701-DRAFFIN / BELCHER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 16379 Ferrells Creek Road, Belcher, Ky. | 2020-02-26
2020 | 2020-02-26 | Pikeville | 86691031 |  | 37820172000258 |  | 3400701-DRAFFIN / BELCHER | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive secondary and pole. Secondary is cut loose from transformer pole and laying in trees. | 1577 old Ferrells Creek Road, Belcher, Ky.
2020 | 2020-02-26 | Pikeville |  |  | 37820196000024 |  | 3400701-DRAFFIN / BELCHER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Top of pole is split. Probably could just put a thru bolt to hold together or cut top of pole and lower the transformer, etc. | Shop Branch, Belcher, Ky.
2020 | 2020-02-26 | Pikeville |  |  | 37820196000070 |  | 3400701-DRAFFIN / BELCHER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky Hwy. 80 East, Belcher, Ky. | 2020-02-26
2020 | 2020-02-26 | Pikeville |  |  | 37820196000070 |  | 3400701-DRAFFIN / BELCHER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky Hwy. 80 East, Belcher, Ky. | 2020-02-26
2020 | 2020-02-26 | Pikeville |  |  | 37820196000070 |  | 3400701-DRAFFIN / BELCHER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky Hwy. 80 East, Belcher, Ky. | 2020-02-26
2020 | 2020-02-27 | Pikeville |  |  | 37820125000189 |  | 3409402-FEDSCREEK / LICKCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Riles Branch, Lick Creek, Mouthcard, Ky. | 2020-02-27
2020 | 2020-02-27 | Pikeville |  |  | 37820125B30225 |  | 3409402-FEDSCREEK / LICKCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Elswick Fork, Lick Creek, Mouthcard, Ky. | 2020-02-27
2020 | 2020-02-27 | Pikeville |  |  | 37820148000158 |  | 3409402-FEDSCREEK / LICKCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown. No truck. Line feeds cell tower. Will need pickup or side by side to access. | Abner Fork, Ferrells Creek, Belcher, Ky.
2020 | 2020-02-27 | Pikeville |  |  | 37820148000162 |  | 3409402-FEDSCREEK / LICKCREEK | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections , guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire broken, hanging down pole. Pole ground stolen also. Can attack guy to stub pole or anchor. Line feeds cell tower. Will need pickup truck or side by side to access. | Abner Fork, Ferrells Creek, Belcher, Ky.
2020 | 2020-02-27 | Pikeville |  |  | 37820148000163 |  | 3409402-FEDSCREEK / LICKCREEK | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign | NO | Top of pole is split. Needs a thru bolt or could lower conductors if necessary. Difficult location. Will need pickup or side by side to access. Road to cell tower. Also has pole ground stolen. | Abner Fork, Ferrells Creek, Belcher, Ky.
2020 | 2020-02-27 | Pikeville |  |  | 37820148000164 |  | 3409402-FEDSCREEK / LICKCREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Pole is leaning considerably. Needs straightening. Probably will need to install anchor and side guy. Line goes to AT&T tower. Will need side by side or pickup truck to access. Will be hand dig anchor. Also has lightning arrestor blown and pole ground stolen. | Abner Fork, Ferrells Creek, Belcher, Ky.
2020 | 2020-02-27 | Pikeville |  |  | 37820149000064 |  | 3409402-FEDSCREEK / LICKCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Weddington Branch, Belcher, Ky. | 2020-02-27
2020 | 2020-02-27 | Pikeville |  |  | 37820149000160 |  | 3409402-FEDSCREEK / LICKCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lick Creek, Mouthcard, Ky. | 2020-02-27
2020 | 2020-02-27 | Pikeville |  |  | 37820149000160 |  | 3409402-FEDSCREEK / LICKCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lick Creek, Mouthcard, Ky. | 2020-02-27
2020 | 2020-02-27 | Pikeville |  |  | 37820149000160 |  | 3409402-FEDSCREEK / LICKCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lick Creek, Mouthcard, Ky. | 2020-02-27
2020 | 2020-02-28 | Pikeville | WR 75939164 |  | 37820148000160 |  | 3409402-FEDSCREEK / LICKCREEK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop low clearance. Service knob pulled away from service pole. Contacted area servicer to make immediate repairs. | 1039 Abner Fork, Ferrells Creek, Belcher, Ky. | 2020-02-28
2020 | 2020-02-28 | Pikeville |  |  | 37820149000089 |  | 3409402-FEDSCREEK / LICKCREEK | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Guy wire broken, hanging down pole. 3 phase angle pole. | Ferrells Creek Road, Belcher, Ky.
2020 | 2020-02-28 | Pikeville |  |  | 37820149000135 |  | 3409402-FEDSCREEK / LICKCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Lick Creek Road, Belcher, Ky.
2020 | 2020-02-28 | Pikeville |  |  | 37820172000278 |  | 3409402-FEDSCREEK / LICKCREEK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | Ferrells Creek Road, Belcher, Ky. | 2020-02-28
2020 | 2020-03-02 | Pikeville |  |  | 37820148000089 |  | 3409402-FEDSCREEK / LICKCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NEEDS ADDITIONAL CHECK | I believe the top of this pole may be broken. It’s a 3 phase Buckarm pole. Conductors cross the road. 45 class 2 pole. No truck . Should have LCS to look at this pole and see what he thinks. | 247 Old Ferrells Creek Lane, Belcher, Ky.
2020 | 2020-03-02 | Pikeville |  |  | 37820149000188 |  | 3409402-FEDSCREEK / LICKCREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Removed drop. | Lick Creek Road, Belcher, Ky. | 2020-03-02
2020 | 2020-03-02 | Pikeville |  |  | 37820149000188 |  | 3409402-FEDSCREEK / LICKCREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Removed drop. | Lick Creek Road, Belcher, Ky. | 2020-03-02
2020 | 2020-03-02 | Pikeville |  |  | 37820149000188 |  | 3409402-FEDSCREEK / LICKCREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Removed drop. | Lick Creek Road, Belcher, Ky. | 2020-03-02
2020 | 2020-03-03 | Pikeville | 76959048 | DKY0110550 | 37820126000133 | TRUE | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole is split. 3 phase angle pole with 4/0 conductors. | 22317 U.S. Hwy. 460, Mouthcard, Ky.
2020 | 2020-03-03 | Pikeville |  |  | 37820126000149 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire hanging down pole. Needs new anchor and guy installed. Probably will be hand dig anchor. Conductors cross Hwy 460. | 22426 U.S. Hwy. 460, Mouthcard, Ky.
2020 | 2020-03-04 | Pikeville | 77231790 | DKY0112505 | 37820126000042 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is in slide area/ leaning. | 442 Little Card Road, Mouthcard, Ky.
2020 | 2020-03-04 | Pikeville |  |  | 37820126000048 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. De-energized. Transformer open. | 443 Big Card Creek, Mouthcard, Ky.
2020 | 2020-03-04 | Pikeville |  |  | 37820126000053 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 227 North Levisa Road, Mouthcard, Ky. | 2020-03-04
2020 | 2020-03-04 | Pikeville |  |  | 37820126000079 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Big Card Creek, Mouthcard, Ky. | 2020-03-04
2020 | 2020-03-04 | Pikeville |  |  | 37820126000123 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 66 North Levisa Road, Mouthcard, Ky. | 2020-03-04
2020 | 2020-03-04 | Pikeville |  |  | 37820126000225 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 179 Big Card Creek, Mouthcard, Ky. | 2020-03-04
2020 | 2020-03-04 | Pikeville |  |  | 37820126000235 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  |  | other: customer owned attachment | KPC | NO | Customer entrance/weatherhead is bent/ damaged. About 1/4 mile up little card creek on right. | Little Card Creek, Mouthcard, Ky.
2020 | 2020-03-04 | Pikeville |  |  | 37820150000037 | TRUE | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 711 Big Card Creek, Mouthcard, Ky.
2020 | 2020-03-04 | Pikeville |  |  | 37820150000041 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 829 Big Card Creek, Mouthcard, Ky. | 2020-03-04
2020 | 2020-03-04 | Pikeville |  |  | 37820150000059 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 2051 Big Card Creek, Mouthcard, Ky.
2020 | 2020-03-05 | Pikeville | 86515868 |  | 37820079000077 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer and service hanging down pole | 2221 Motley Fork, Fedscreek, Ky.
2020 | 2020-03-05 | Pikeville | 84899804 | DKY0121268 | 37820080000017 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive line and poles from pole 37820080000017 to pole 37820080000021. Primary and neutral down in separate places. Line is de-energized. | 2570 Motley Fork, Fedscreek, Ky. | 2023-07-28
2020 | 2020-03-05 | Pikeville |  |  | 37820103000051 | TRUE | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/missing. #6a copper. | Miller Fork of Motley Fork, Fedscreek, Ky. | 2023-12-18
2020 | 2020-03-05 | Pikeville |  |  | 37820103000170 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive secondary pole. Wire hanging down pole. Pole is not shown on field view. It’s about .2 mile up Miller Fork. | Miller Fork of Motley Fork, Fedscreek, Ky.
2020 | 2020-03-05 | Pikeville |  |  | 37820103000180 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer and service hanging down pole. | 808 Motley Fork, Fedscreek, Ky.
2020 | 2020-03-05 | Pikeville | 84844361 |  | 37820103B00027 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at ground line. Recloser pole feeding motley Fork. | 76 Motley Fork, Fedscreek, Ky.
2020 | 2020-03-05 | Pikeville | 77011272 | DKY0110356 | 37820103B00134 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line. 40 class 2 pole. Installed 1967 | 124 Motley Fork, Fedscreek, Ky. | 2020-12-11
2020 | 2020-03-05 | Pikeville |  |  | 37820127000009 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Removed drop. | 1856 Fedscreek Road, Fedscreek, Ky. | 2020-03-05
2020 | 2020-03-06 | Pikeville |  |  | 37820080B40774 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 384 Dicks Fork, Fedscreek, Ky. | 2020-03-06
2020 | 2020-03-06 | Pikeville | 86515868 |  | 37820104000003 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown. @ Fedscreek Baptist Church. | 3038 Fedscreek Road, Fedscreek, Ky.
2020 | 2020-03-06 | Pikeville | 86529598 |  | 37820104000050 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm deteoriated/ rotten. Pole seems solid but it was installed in 1947. Might want to change pole. | 435 Dicks Fork, Fedscreek, Ky. | 2023-12-18
2020 | 2020-03-06 | Pikeville |  |  | 37820104000209 | TRUE | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Transformer is de-energized | 565 Millers Fork, Fedscreek, Ky.
2020 | 2020-03-06 | Pikeville |  |  | 37820105A00006 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 1785 Dicks Fork, Fedscreek, Ky. | 2020-03-06
2020 | 2020-03-06 | Pikeville |  |  | 37820128A00038 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken, hanging down pole. Anchor is visible. Just needs to be attached. | 416 Henry Branch, Laurel Fork, Fedscreek, Ky.
2020 | 2020-03-06 | Pikeville | 86515735 |  | 37820128A00109 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive secondary pole. | 478 Henry Branch, Laurel Fork, Fedscreek, Ky.
2020 | 2020-03-06 | Pikeville |  |  | 37830080000043 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 559 Dicks Fork, Fedscreek, Ky. | 2020-03-06
2020 | 2020-03-06 | Pikeville |  |  | 37830080000043 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 559 Dicks Fork, Fedscreek, Ky. | 2020-03-06
2020 | 2020-03-09 | Pikeville |  |  | 37820126000009 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | South River Road, Mouthcard, Ky. | 2020-03-09
2020 | 2020-03-09 | Pikeville | 86431073 | DKY0122794 | 37820150000026 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole is leaning considerably. Needs straightening. May need to install anchor with side guy. | 660 Little Hackney Creek, Mouthcard, Ky. | 2023-12-18
2020 | 2020-03-09 | Pikeville |  |  | 37820150000031 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  | lightning arresters/insulators: damaged , guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Lightning arrestor blown. Also has guy wire hanging down pole. Will need to install anchor. Probably hand dig. Will need ROAD SIGNS. Have to block road. | 968 Little Hackney Creek, Mouthcard, Ky.
2020 | 2020-03-09 | Pikeville |  |  | 37820150000254 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH | cutout: damaged |  |  | KPC | NO | Cutout/ Lightning arrestor bracket turned sideways . Can’t operate cutout. | 976 Little Hackney Creek, Mouthcard, Ky.
2020 | 2020-03-09 | Pikeville |  |  | 37820151000017 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | South River Road, Mouthcard, Ky. | 2020-03-10
2020 | 2020-03-09 | Pikeville | 84396111 | DKY0119587 | 37820151000055 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop laying across roof of mobile home. Probably going to need secondary pole set. | 50 Little Hackney Creek, Mouthcard, Ky. | 2023-03-02
2020 | 2020-03-09 | Pikeville | 86690736 |  | 37820151000200 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 24913 South Levisa Road, Mouthcard, Ky.
2020 | 2020-03-10 | Pikeville |  |  | 37820126000010 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 175 South St, New York, NY 10038, USA
2020 | 2020-03-10 | Pikeville |  |  | 37820126000241 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | North River Road,Mouthcard, Ky. | 2020-03-10
2020 | 2020-03-10 | Pikeville |  |  | 37820127000016 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/stolen between pole 16 and 17. | Big Hackney Creek, Mouthcard, Ky.
2020 | 2020-03-10 | Pikeville | 86515659 |  | 37820151000173 | TRUE | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm rotten/split on the end. Uphill phase .@ across RR tracks on hill behind white DW mobile home. | 1040 South River Road, Mouthcard, Ky.
2020 | 2020-03-10 | Pikeville |  |  | 37820151000226 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop rolled up hanging down pole. Removed drop. | 153 South River Road,Mouthcard, Ky. | 2020-03-10
2020 | 2020-03-11 | Pikeville |  |  | 37820073A00050 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Shelby Yard, Shelbiana, Ky. 41562 | 2020-03-11
2020 | 2020-03-11 | Pikeville |  |  | 37820073A00051 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | Shelby Yard, Shelbiana, Ky. 41562 | 2020-03-11
2020 | 2020-03-11 | Pikeville |  |  | 37820073A00058 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | Shelby Yard, Shelbiana, Ky. 41562 | 2020-03-11
2020 | 2020-03-11 | Pikeville |  |  | 37820073A00617 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on step down transformer pole. | Shelby Yard, Shelbiana, Ky. 41562 | 2020-03-11
2020 | 2020-03-11 | Pikeville |  |  | 37820073B00010 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dry Fork Shelby, Shelbiana, Ky. 41562 | 2020-03-11
2020 | 2020-03-11 | Pikeville |  |  | 37820073B00011 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Shelby Dry Fork, Shelbiana, Ky. 41562 | 2020-03-11
2020 | 2020-03-11 | Pikeville |  |  | 37820073B00048 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | Shelby Yard, Shelbiana, Ky. 41562 | 2020-03-11
2020 | 2020-03-11 | Pikeville | 76907675 | DKY0110162 | 37820073B00332 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line. 35 class 5 | 367 Shelby Yard, Shelbiana, KY 41562, USA | 2020-12-08
2020 | 2020-03-11 | Pikeville | 83967750 | DKY0121106 | 37820097000026 | TRUE | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm rotten. | 2160 Shelby Dry Fork, Shelbiana, Ky.
2020 | 2020-03-11 | Pikeville | 83967750 | DKY0121106 | 37820121000005 | TRUE | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken. | 2293 Shelby Dry Fork, Shelbiana, Ky.
2020 | 2020-03-11 | Pikeville |  |  | 37830096D00239 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire slack. Needs tightened. Installed new marker. | Old Shelbiana Rd, Pikeville, KY 41501, USA | 2020-03-11
2020 | 2020-03-12 | Pikeville | 84876385 | DKY0120784 | 37820121000319 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive secondary pole and secondary. | 3898 Shelby Dry Fork, Shelbiana, KY 41562, USA | 2023-06-01
2020 | 2020-03-12 | Pikeville | 85404347 | DKY0121196 | 37820121B30363 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Secondary pole leaning. Needs straightening. | 3513 Shelby Dry Fork, Shelbiana, KY 41562, USA | 2023-07-11
2020 | 2020-03-12 | Pikeville |  |  | 37830120C00045 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Collins Highway, Shelbiana, Ky. | 2020-03-12
2020 | 2020-03-12 | Pikeville | 83967750 | DKY0121106 | 37830120C00137 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Neutral conductor down. Also crossarm brace broken. | 1572 Collins Hwy, Shelbiana, KY 41562, USA
2020 | 2020-03-12 | Pikeville |  |  | 37830120C00138 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down. . Road crossing. | 1572 Collins Hwy, Shelbiana, Ky.
2020 | 2020-03-12 | Pikeville | 83967750 | DKY0121106 | 37830120C00141 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarms deteoriated/ rotten. Crosses RR TRACK. | 2317 Collins Hwy, Shelbiana, Ky.
2020 | 2020-03-12 | Pikeville |  |  | 37830120C00151 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Collins Hwy, Shelbiana, Ky. | 2020-03-12
2020 | 2020-03-12 | Pikeville |  |  | 37830120D00018 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Buckfield Rd, Kentucky 41501, USA | 2020-03-12
2020 | 2020-03-12 | Pikeville | 83967950 |  | 37830120D00060 | TRUE | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  | crossarm/braces: deteriorated, not rotten | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Crossarm is deteoriated/ end is split allowing crossarm pin to lay over. Also should remove inactive transformer and service. | 354 Collins Street, Shelbiana, Ky.
2020 | 2020-03-12 | Pikeville |  |  | 37830120D00061 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on step down transformer pole. | 360 Collins Street, Shelbiana, Ky. | 2020-03-12
2020 | 2020-03-12 | Pikeville | 78732961 |  | 37830120D00323 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Needs removed. | 208 Collins Street, Shelbiana, Ky. | 2021-02-02
2020 | 2020-03-13 | Pikeville |  |  | 37830120B00153 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 1140 Sookeys Creek,Pikeville, Ky. | 2020-03-13
2020 | 2020-03-13 | Pikeville |  |  | 37830120B00153 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 1140 Sookeys Creek,Pikeville, Ky. | 2020-03-13
2020 | 2020-03-13 | Pikeville |  |  | 37830120B00153 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 1140 Sookeys Creek,Pikeville, Ky. | 2020-03-13
2020 | 2020-03-13 | Pikeville |  |  | 37830144A00006 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 4189 Collins Hwy, Pikeville, Ky. | 2020-03-13
2020 | 2020-03-13 | Pikeville |  |  | 37830144A00019 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 68 Little Creek , Pikeville, Ky. | 2020-03-13
2020 | 2020-03-13 | Pikeville |  |  | 37830144A00019 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 68 Little Creek , Pikeville, Ky. | 2020-03-13
2020 | 2020-03-13 | Pikeville |  |  | 37830144C00275 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 447 Little Creek, Pikeville, Ky. | 2020-03-13
2020 | 2020-03-13 | Pikeville |  |  | 37830168000012 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 2201 Little Creek, Pikeville, Ky. | 2020-03-13
2020 | 2020-03-13 | Pikeville |  |  | 37830168000012 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 2201 Little Creek, Pikeville, Ky. | 2020-03-13
2020 | 2020-03-13 | Pikeville |  |  | 37830168000012 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 2201 Little Creek, Pikeville, Ky. | 2020-03-13
2020 | 2020-03-13 | Pikeville |  |  | 37830168000012 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 2201 Little Creek, Pikeville, Ky. | 2020-03-13
2020 | 2020-03-13 | Pikeville |  |  | 37830168000025 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 525 Deadening Fork, Little Creek, Pikeville, Ky. | 2020-03-13
2020 | 2020-03-13 | Pikeville |  |  | 37830168000090 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 725 Deadening Fork, Little Creek, Pikeville, Ky. | 2020-03-13
2020 | 2020-03-13 | Pikeville |  |  | 37830168000090 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 725 Deadening Fork, Little Creek, Pikeville, Ky. | 2020-03-13
2020 | 2020-03-16 | Pikeville |  |  | 37830096B40452 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | U.S. Hwy. 23 South, Pikeville, Ky. | 2020-03-16
2020 | 2020-03-16 | Pikeville |  |  | 37830096B40452 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | U.S. Hwy. 23 South, Pikeville, Ky. | 2020-03-16
2020 | 2020-03-16 | Pikeville |  |  | 37830096C10468 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Pole top insulator damaged. Line going to cell tower. | Smiley Fork, Pikeville, Ky.
2020 | 2020-03-16 | Pikeville | 83967987 | DKY0121077 | 37830143C00003 | TRUE | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator broken. Next to the recloser pole. @ RR tracks. | 5595 Robinson Creek Road, Pikeville, Ky.
2020 | 2020-03-16 | Pikeville |  |  | 37830143C00006 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 5800 Robinson Creek Road, Pikeville, Ky. | 2020-03-16
2020 | 2020-03-16 | Pikeville |  |  | 37830144A00065 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 5116 Collins Hwy, Pikeville, Ky. | 2020-03-16
2020 | 2020-03-16 | Pikeville |  |  | 37830144A00310 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Hot meter base open. Blanked it off. | 5359 Robinson Creek Road, Pikeville, Ky. | 2020-03-16
2020 | 2020-03-16 | Pikeville | 83967987 | DKY0121077 | 37830144A00311 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator melting down. No truck. | 5359 Robinson Creek Road, Pikeville, Ky.
2020 | 2020-03-17 | Pikeville | 84874982 |  | 37830119000007 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole is split. Pictures don’t show it very good. | 504 Sugarcamp Branch,Robinson Creek, Pikeville, Ky.
2020 | 2020-03-17 | Pikeville | 83968056 | DKY0120551 | 37830119A40173 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken | Robinson Creek Road, Pikeville, Ky. | 2023-05-12
2020 | 2020-03-17 | Pikeville | 83968056 | DKY0120551 | 37830119A40178 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm is rotten/split. | Robinson Creek Road, Pikeville, Ky. | 2023-05-12
2020 | 2020-03-17 | Pikeville | 83968056 | DKY0120551 | 37830119D10170 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken. | Robinson Creek Road, Pikeville, Ky. | 2023-05-12
2020 | 2020-03-17 | Pikeville | 83968056 | DKY0120551 | 37830119D10186 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken. | Robinson Creek Road, Pikeville, Ky. | 2023-05-12
2020 | 2020-03-17 | Pikeville |  |  | 37830143C00044 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 61 Peter Branch, Robinson Creek, Pikeville, Ky. | 2020-03-17
2020 | 2020-03-17 | Pikeville |  |  | 37830143C00086 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 5986 Robinson Creek Road, Pikeville, Ky. | 2020-03-17
2020 | 2020-03-17 | Pikeville | 83967818 | DKY0120961 | 37830143C00335 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken hanging down pole. Probably will need to install new anchor. | 5878 Robinson Creek Road, Pikeville, Ky.
2020 | 2020-03-17 | Pikeville |  |  | 37830143C00382 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 5940 Robinson Creek Road, Pikeville, Ky. | 2020-03-17
2020 | 2020-03-17 | Pikeville |  |  | 37830143C00382 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 5940 Robinson Creek Road, Pikeville, Ky. | 2020-03-17
2020 | 2020-03-17 | Pikeville |  |  | 37830143C00382 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 5940 Robinson Creek Road, Pikeville, Ky. | 2020-03-17
2020 | 2020-03-17 | Pikeville |  |  | 37830143D00095 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole washed out in creek. About half mile up Peter Branch. 45 class 5 pole. | Peter Branch, Robinson Creek, Pikeville, Ky. | 2023-03-02
2020 | 2020-03-18 | Pikeville | 84898299 | DKY0122070 | 37830142000098 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive 3 phase line from pole 37830142000098 to pole 37830142A30189. 3 spans. Head of Bear Fork. | Bear Fork, Robinson Creek, Pikeville, Ky. | 2023-12-27
2020 | 2020-03-18 | Pikeville | 83967987 | DKY0121077 | 37830142000139 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator melting down. | 8601 Robinson Creek Road, Pikeville, Ky.
2020 | 2020-03-18 | Pikeville | 033053099 |  | 37830143A00311 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  |  | other: customer owned attachment | KPC | NO | Customers entrance conduit is bent over. @ Valley Grace Church @ mouth of Bear Fork. | 7711 Robinson Creek Road, Pikeville, Ky. | 2021-04-13
2020 | 2020-03-18 | Pikeville |  |  | 37830143C00134 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 5580 Robinson Creek Road, Pikeville, Ky. | 2020-03-18
2020 | 2020-03-18 | Pikeville |  |  | 37830144B00330 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 100 Nursing Home Lane,Robinson Creek Road, Pikeville, Ky. | 2020-03-18
2020 | 2020-03-18 | Pikeville |  |  | 37830144B00331 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 200 Nursing Home Lane, Robinson Creek Road, Pikeville, Ky. | 2020-03-18
2020 | 2020-03-18 | Pikeville |  |  | 37830144B00338 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 163 Douglas Pkwy. Robinson Creek Road, Pikeville, Ky. | 2020-03-18
2020 | 2020-03-18 | Pikeville |  |  | 37830144B00355 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Nursing Home Lane, Robinson Creek Road, Pikeville, Ky. | 2020-03-18
2020 | 2020-03-18 | Pikeville |  |  | 37830144B00434 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 125 Douglas Pkwy. Robinson Creek Road , Pikeville, Ky. | 2020-03-18
2020 | 2020-03-18 | Pikeville |  |  | 37830144B00434 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 125 Douglas Pkwy. Robinson Creek Road , Pikeville, Ky. | 2020-03-18
2020 | 2020-03-18 | Pikeville |  |  | 37830144B00434 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 125 Douglas Pkwy. Robinson Creek Road , Pikeville, Ky. | 2020-03-18
2020 | 2020-03-18 | Pikeville |  |  | 37830144B00471 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 111 Douglas Pkwy, Pikeville, Ky. | 2020-03-18
2020 | 2020-03-18 | Pikeville |  |  | 37830144B00471 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 111 Douglas Pkwy, Pikeville, Ky. | 2020-03-18
2020 | 2020-03-19 | Pikeville |  |  | 37830143D00035 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (3) | 281 Country Lane, Pikeville, Ky. | 2020-03-19
2020 | 2020-03-19 | Pikeville |  |  | 37830143D00117 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 427 Country Lane, Pikeville, Ky. | 2020-03-19
2020 | 2020-03-19 | Pikeville |  |  | 37830167D00410 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | 7725 U.S. Hwy 23 South, Pikeville, Ky. | 2020-03-19
2020 | 2020-03-19 | Pikeville |  |  | 37830168000133 | TRUE | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator broken. @ Country Lane, Esco. | 6758 U.S. Hwy 23 South, Pikeville, Ky.
2020 | 2020-03-20 | Pikeville |  |  | 37820049A20253 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Padmount transformer does not have a padlock. Installed lock. | 552 Foxcroft Lane, Pikeville, Ky. | 2020-03-20
2020 | 2020-03-20 | Pikeville |  |  | 37820049A20254 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Padmount transformer is partially scooted of the pad. | 552 Foxcroft Lane, Pikeville, Ky.
2020 | 2020-03-20 | Pikeville |  |  | 37830072C00527 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Padmount transformer is scooted partially off the pad. | 258 Foxcroft Lane, Pikeville, Ky.
2020 | 2020-03-20 | Pikeville |  |  | 37830072C00613 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Yorkwood Forest, Pikeville, Ky. | 2020-03-20
2020 | 2020-03-20 | Pikeville |  |  | 37830072D00017 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | South Mayo Trail, Pikeville, Ky. | 2020-03-20
2020 | 2020-03-20 | Pikeville |  |  | 37830072D00636 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Yorkwood Forest, Pikeville, Ky. | 2020-03-20
2020 | 2020-03-20 | Pikeville |  |  | 37830096A20544 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Marion Branch, Pikeville, Ky. | 2020-03-20
2020 | 2020-03-20 | Pikeville |  |  | 37830096A20544 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Marion Branch, Pikeville, Ky. | 2020-03-20
2020 | 2020-03-20 | Pikeville |  |  | 37830096C00005 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Fords Branch Lane, Pikeville, Ky. | 2020-03-20
2020 | 2020-03-20 | Pikeville |  |  | 37830096C00005 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Fords Branch Lane, Pikeville, Ky. | 2020-03-20
2020 | 2020-03-20 | Pikeville |  |  | 37830096C00281 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Old School House Road, Pikeville, Ky. | 2020-03-20
2020 | 2020-03-23 | Pikeville | 83929093 | DKY0119665 | 37820097000059 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at ground line | 958 Greasy Creek, Shelbiana, Ky. | 2023-08-24
2020 | 2020-03-23 | Pikeville | 86690848 |  | 37820097000175 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 1624 Greasy Creek, Shelbiana, Ky.
2020 | 2020-03-23 | Pikeville |  |  | 37820097000343 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Primary conductor tie wire broken. | 115 Lucy Branch, Greasy Creek, Shelbiana, Ky. | 2023-03-02
2020 | 2020-03-23 | Pikeville |  |  | 37820097000346 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on step down transformer pole. | 850 Greasy Creek, Shelbiana, Ky. | 2020-03-23
2020 | 2020-03-23 | Pikeville |  |  | 37820098A00120 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Slone Street, Millard, Ky. | 2020-03-23
2020 | 2020-03-23 | Pikeville |  |  | 37820098A00127 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | N Patton Street, Millard, Ky. | 2020-03-23
2020 | 2020-03-23 | Pikeville |  |  | 37820098A00127 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | N Patton Street, Millard, Ky. | 2020-03-23
2020 | 2020-03-23 | Pikeville |  |  | 37820098A00298 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Sutton Bottom, Greasy Creek, Shelbiana, Ky. | 2020-03-23
2020 | 2020-03-23 | Pikeville | 76907592 | DKY0110152 | 37820098A00348 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten. 35 class 5 pole | 72 Justice Auto Road, Millard, Ky. | 2020-07-06
2020 | 2020-03-23 | Pikeville |  |  | 37820098A00585 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 5491 E Shelbiana Road, Millard, Ky. | 2020-03-23
2020 | 2020-03-24 | Pikeville |  |  | 37820049000232 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 4070 Chloe Creek Road, Pikeville, Ky. | 2020-03-24
2020 | 2020-03-24 | Pikeville |  |  | 37820049000240 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker. Completed. Satellite dish on pole | 228 Buck Branch, Chloe Creek, Pikeville, Ky.
2020 | 2020-03-24 | Pikeville |  |  | 37820049000316 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire slack. Needs tightened. Installed marker | 106 Sulphur Springs Hollow, Chloe Creek, Pikeville, Ky. | 2020-03-24
2020 | 2020-03-24 | Pikeville |  |  | 37820049000316 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire slack. Needs tightened. Installed marker | 106 Sulphur Springs Hollow, Chloe Creek, Pikeville, Ky. | 2020-03-24
2020 | 2020-03-24 | Pikeville |  |  | 37820050A10261 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. | 474 Kendrick Fork, Chloe Creek Road, Pikeville, Ky. | 2020-03-24
2020 | 2020-03-24 | Pikeville |  |  | 37830096C00138 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | 1577 W Shelbiana Road, Pikeville, Ky. | 2020-03-24
2020 | 2020-03-24 | Pikeville |  |  | 37830096C00138 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | 1577 W Shelbiana Road, Pikeville, Ky. | 2020-03-24
2020 | 2020-03-24 | Pikeville |  |  | 37830096D00161 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | W Shelbiana Road, Pikeville, Ky. | 2020-03-24
2020 | 2020-03-24 | Pikeville |  |  | 37830096D00161 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | W Shelbiana Road, Pikeville, Ky. | 2020-03-24
2020 | 2020-03-25 | Pikeville |  |  | 37820025C00256 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 657 Ivy Fork, Chloe Creek , Pikeville, Ky. | 2020-03-25
2020 | 2020-03-25 | Pikeville |  |  | 37820025C00256 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 657 Ivy Fork, Chloe Creek , Pikeville, Ky. | 2020-03-25
2020 | 2020-03-25 | Pikeville |  |  | 37820049000022 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 1076 Red Creek, Pikeville, Ky. | 2020-03-25
2020 | 2020-03-25 | Pikeville |  |  | 37820049000163 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive secondary pole and secondary conductor | 183 Rfk Red Creek, Pikeville, Ky. | 2020-06-17
2020 | 2020-03-25 | Pikeville |  |  | 37820049000319 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole | 1139 Red Creek, Pikeville, Ky. | 2020-03-25
2020 | 2020-03-25 | Pikeville |  |  | 37820049000319 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole | 1139 Red Creek, Pikeville, Ky. | 2020-03-25
2020 | 2020-03-25 | Pikeville |  |  | 37820049D30363 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 1521 Red Creek, Pikeville, Ky. | 2020-03-25
2020 | 2020-03-25 | Pikeville | 83929083 | DKY0119924 | 37820050000081 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive transformer and line going to pole 37820050000178.@ Head of Rfk | 777 Rfk Red Creek, Pikeville, Ky. | 2023-12-26
2020 | 2020-03-25 | Pikeville |  |  | 37820073A00347 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | W Shelbiana Road, Pikeville, Ky. | 2020-03-25
2020 | 2020-03-25 | Pikeville | 83929201 | DKY0120853 | 37820073D00140 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator melting. 3 phase double dead end on hill. | 4180 E Shelbiana Road, Pikeville, Ky.
2020 | 2020-03-25 | Pikeville |  |  | 37820073D00455 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | W Shelbiana Road, Pikeville, Ky. | 2020-03-25
2020 | 2020-03-26 | Pikeville |  |  | 38820990C40133 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Old Hardy Road, Belfry, Ky. | 2020-03-26
2020 | 2020-03-26 | Pikeville |  |  | 38820990C40138 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Old Hardy Rd, Kentucky 41514, USA | 2020-03-26
2020 | 2020-03-26 | Pikeville |  |  | 38820990C40208 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Old Hardy Road, Belfry, Ky. | 2020-03-26
2020 | 2020-03-26 | Pikeville |  |  | 38820990C40407 |  | 3200302-BELFRY / TOLER | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NEEDS ADDITIONAL CHECK | Service drop low over deck. App. 8 ft. Might need to change transformer pole or install secondary pole for clearance. Installed guy marker. | 144 Toler Lane, Belfry, Ky. | 2020-03-26
2020 | 2020-03-26 | Pikeville |  |  | 38820990C40408 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Toler Lane, Belfy, Ky. 41514 | 2020-03-26
2020 | 2020-03-26 | Pikeville |  |  | 38820990C49000 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | U.S. Hwy 119, Belfry, Ky. | 2020-03-26
2020 | 2020-03-26 | Pikeville | 77011793 | DKY0110406 | 38820990D20415 |  | 3200302-BELFRY / TOLER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line. Early rot. Top of pole has been burnt and extended with crossarm. | 97 Carroll Hunt Lane, Belfry, Ky.
2020 | 2020-03-26 | Pikeville |  |  | 38820990D20440 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Carroll Hunt Lane, Belfry, Ky. | 2020-03-26
2020 | 2020-03-26 | Pikeville |  |  | 38820990D20462 |  | 3200302-BELFRY / TOLER | Line Work | OH |  |  | other: customer owned attachment | KPC | NEEDS ADDITIONAL CHECK | Customer has built a garage/storage building around our transformer pole. | 97 Carroll Hunt Lane, Belfry, Ky.
2020 | 2020-03-26 | Pikeville |  |  | 38820990D20492 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Varney Road, Belfry, Ky. | 2020-03-26
2020 | 2020-03-26 | Pikeville |  |  | 38820990D30191 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Old Hardy Lane, Belfry, Ky. | 2020-03-26
2020 | 2020-03-26 | Pikeville |  |  | 38820990D30191 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Old Hardy Lane, Belfry, Ky. | 2020-03-26
2020 | 2020-03-26 | Pikeville |  |  | 38820990D30195 |  | 3200302-BELFRY / TOLER | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen on transformer pole | 480 Old Hardy Rd, Belfry, KY 41514, USA | 2020-03-26
2020 | 2020-03-26 | Pikeville |  |  | 38821014C30118 |  | 3200302-BELFRY / TOLER | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral conductor down/ on the ground. Between poles 118 and 117. Looks like #6 weatherproof. About half mile up Varney Road. | Varney Rd, Belfry, Ky.
2020 | 2020-03-26 | Pikeville |  |  | 38821014C30120 |  | 3200302-BELFRY / TOLER | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole is leaning considerably. Needs straightening. Already has side guy on it. Might need to be re-located. | 815 Varney Road, Belfry, Ky. | 2022-09-23
2020 | 2020-03-27 | Pikeville |  |  | 38820990C40141 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 115 Old Hardy Rd, Hatfield, KY 41514, USA | 2020-03-27
2020 | 2020-03-27 | Pikeville |  |  | 38820990C40314 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Toler Road, Belfry, Ky. | 2020-03-27
2020 | 2020-03-27 | Pikeville |  |  | 38820990C40479 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Toler Road, Belfry, Ky. | 2020-03-27
2020 | 2020-03-27 | Pikeville | 77011832 | DKY0110363 | 38820991A00071 | TRUE | 3200302-BELFRY / TOLER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten . 35 class 5 pole. Will need flagging signs. | 569 Broadhead Hollow, Toler, KY 41514, USA | 2022-08-08
2020 | 2020-03-27 | Pikeville |  |  | 38821015A00192 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Hardy Lane, Hardy, Ky. | 2020-03-27
2020 | 2020-03-27 | Pikeville |  |  | 38821063A00001 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Narrows Branch, Hardy, Ky. | 2020-03-27
2020 | 2020-03-27 | Pikeville | 77011655 | DKY0110408 | 38821063A00113 |  | 3200302-BELFRY / TOLER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole has been burned and repaired with crossarm. | 3417 Narrows Branch, Hardy, Ky. | 2020-12-17
2020 | 2020-03-30 | Pikeville |  |  | 38821039C00161 |  | 3200302-BELFRY / TOLER | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 4035 Hardy Lane, Hardy, Ky.
2020 | 2020-03-30 | Pikeville |  |  | 38821039C00232 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Right Turkey Toe, Hardy, Ky. | 2020-03-30
2020 | 2020-03-30 | Pikeville | 82681753 | DKY0117341 | 38821039D20272 |  | 3200302-BELFRY / TOLER | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Low clearance on service drop. It’s only about 7 ft. off the ground. Probably need to install secondary pole for clearance. | 1530 Mudlick Road, Hardy, Ky. | 2022-07-14
2020 | 2020-03-30 | Pikeville |  |  | 38821040A00018 | TRUE | 3200302-BELFRY / TOLER | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/stolen. #4 copper. No truck | 122 Left Turkey Toe, Hardy , Ky.
2020 | 2020-03-30 | Pikeville |  |  | 38821040A00066 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Right Turkey Toe, Hardy, Ky. | 2020-03-30
2020 | 2020-03-30 | Pikeville |  |  | 38821040A00066 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Right Turkey Toe, Hardy, Ky. | 2020-03-30
2020 | 2020-03-30 | Pikeville | 81169859 | DKY0115522 | 38821063C00023 |  | 3200302-BELFRY / TOLER | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarms are rotten/deteoriated | 2096 Mudlick Branch, Hardy , Ky. | 2022-01-25
2020 | 2020-03-31 | Pikeville | 82836902 | DKY0117495 | 38820966D00035 |  | 3200302-BELFRY / TOLER | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Needs removed. | Compton Bottom, Kentucky, USA | 2022-09-07
2020 | 2020-03-31 | Pikeville |  |  | 38820966D00384 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Compton Bottom, Goody, Ky. | 2020-03-31
2020 | 2020-03-31 | Pikeville |  |  | 38820966D00612 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Compton Bottom, Goody, Ky. | 2020-03-31
2020 | 2020-03-31 | Pikeville |  |  | 38820966D00612 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Compton Bottom, Goody, Ky. | 2020-03-31
2020 | 2020-03-31 | Pikeville |  |  | 38820966D00612 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Compton Bottom, Goody, Ky. | 2020-03-31
2020 | 2020-03-31 | Pikeville |  |  | 38820966D00613 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Compton Bottom, Goody, Ky. | 2020-03-31
2020 | 2020-03-31 | Pikeville |  |  | 38820966D00613 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Compton Bottom, Goody, Ky. | 2020-03-31
2020 | 2020-03-31 | Pikeville |  |  | 38820966D00678 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Forest Hills Road, Belfry, Ky. | 2020-03-31
2020 | 2020-03-31 | Pikeville |  |  | 38820966D00678 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Forest Hills Road, Belfry, Ky. | 2020-03-31
2020 | 2020-03-31 | Pikeville |  |  | 38820966D00680 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Forest Hills Road, Belfry, Ky. | 2020-03-31
2020 | 2020-03-31 | Pikeville |  |  | 38820990A00060 |  | 3200302-BELFRY / TOLER | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken | 1488 Forest Hills Road, Forest Hills, Ky.
2020 | 2020-03-31 | Pikeville |  |  | 38820990C20226 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | U.S. Hwy 119 N, Belfry, Ky. | 2020-03-31
2020 | 2020-03-31 | Pikeville |  |  | 38820990C40224 |  | 3200302-BELFRY / TOLER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | U.S. Hwy. 119 N, Belfry, Ky. | 2020-03-31
2020 | 2020-04-01 | Pikeville |  |  | 38820990D20317 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (3) | U.S. Hwy 119 North, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014A00029 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Murphy Bottom Road, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014A00030 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Murphy Bottom Road, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014A00030 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Murphy Bottom Road, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014A00364 |  | 3200301-BELFRY / BELFRY | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree branch hanging on phase wire. Could cause outage. | Pecco Hollow, Belfry, Ky. | 2022-12-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014B10211 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Pecco Hollow, Belfry, Ky. 41514, USA | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014B10211 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Pecco Hollow, Belfry, Ky. 41514, USA | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014B40134 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Loftis Tipple Road, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014B40134 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Loftis Tipple Road, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014C10078 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Park Avenue, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014C10325 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Pegs Branch, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014C10394 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Watson Hill, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014C10394 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Watson Hill, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014C10394 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Watson Hill, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014C10603 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Hill crest Avenue, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014C20052 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Murphy Bottom Road, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014C20052 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Murphy Bottom Road, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014C20199 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Main Street, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014C20199 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Main Street, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014C20199 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Main Street, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014D00039 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | U.S. Hwy 119 North, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014D00039 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | U.S. Hwy 119 North, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014D00039 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | U.S. Hwy 119 North, Belfry, Ky. | 2020-04-01
2020 | 2020-04-01 | Pikeville |  |  | 38821014D00039 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | U.S. Hwy 119 North, Belfry, Ky. | 2020-04-01
2020 | 2020-04-02 | Pikeville |  |  | 38821014B40277 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Wildwood Lane, Belfry, Ky. | 2020-04-02
2020 | 2020-04-02 | Pikeville |  |  | 38821037D00054 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Coeburn Hollow Rd, Huddy, KY, USA | 2020-04-02
2020 | 2020-04-02 | Pikeville |  |  | 38821038A20061 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Coeburn Hollow Rd, Huddy, KY, USA | 2020-04-02
2020 | 2020-04-02 | Pikeville |  |  | 38821038A20548 |  | 3200301-BELFRY / BELFRY | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wires broken on stub pole. Needs to be re-attached. Probably need to install anchor on hill. Backs up 3 phase Buckarm pole. | 22250 E Big Creek Rd, Huddy, KY 41535, USA
2020 | 2020-04-02 | Pikeville |  |  | 38821038A30037 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Jerry Bottom Rd, Huddy, KY 41535, USA | 2020-04-02
2020 | 2020-04-02 | Pikeville |  |  | 38821038A30106 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Doyle Mountain, Huddy, KY 41535, USA | 2020-04-02
2020 | 2020-04-02 | Pikeville |  |  | 38821038A30333 |  | 3200301-BELFRY / BELFRY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 38 Worley Rd, Huddy, KY 41535, USA
2020 | 2020-04-02 | Pikeville |  |  | 38821038A30415 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 180 Cherry Hill, Huddy, Ky. 41535 | 2020-04-02
2020 | 2020-04-02 | Pikeville |  |  | 38821038A40093 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Grimmett Ln, Huddy, KY 41535, USA | 2020-04-02
2020 | 2020-04-02 | Pikeville |  |  | 38821038A40595 |  | 3200301-BELFRY / BELFRY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Needs removed. | 128 Church St, Huddy, KY 41535, USA | 2020-04-02
2020 | 2020-04-03 | Pikeville |  |  | 37830214C00038 | TRUE | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilators deteoriated/melting | 1951 Ky. Hwy. 610 W, Virgie, Ky.
2020 | 2020-04-03 | Pikeville |  |  | 37830214C00131 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator melting/deteoriated | 202 Tunnel Road, Virgie, Ky.
2020 | 2020-04-03 | Pikeville | 74798325 | DKY0116033 | 37830214C00187 | TRUE | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | Foreign | YES | Pole leaning/washed out around in creek. | 2209 Ky. Hwy. 610 W, Virgie, Ky. | 2022-03-04
2020 | 2020-04-03 | Pikeville | 83929228 | DKY0119923 | 37830214D00011 | TRUE | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | Foreign | YES | Pole leaning/ washed out around in creek. STATION ZONE. Second pole out of station. | Ky. Hwy. 610 W, Jonancy, Ky.
2020 | 2020-04-03 | Pikeville |  |  | 37830214D00012 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator deteoriated/melting | 326 Jonancy Lane, Jonancy, Ky.
2020 | 2020-04-03 | Pikeville |  |  | 37830214D00071 | TRUE | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator deteoriated/ melting | 151 Jonancy Bottom, Jonancy, Ky.
2020 | 2020-04-03 | Pikeville |  |  | 37830214D00403 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky. Hwy. 610 W, Jonancy, Ky. | 2020-04-03
2020 | 2020-04-03 | Pikeville |  |  | 37830215A00424 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Service drop hanging down pole | 158 Elwood Drive, Jonancy, Ky.
2020 | 2020-04-03 | Pikeville |  |  | 37830215B00054 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker (2) | Elwood Drive, Jonancy, Ky. | 2020-04-03
2020 | 2020-04-03 | Pikeville |  |  | 37830215B00401 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Service drop hanging down pole | 158 Elwood Drive, Jonancy, Ky.
2020 | 2020-04-06 | Pikeville |  |  | 37830167B00141 | TRUE | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Pole top pin is bent over. | Penny Road, Virgie, Ky.
2020 | 2020-04-06 | Pikeville |  |  | 37830167B00423 | TRUE | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign | NO | Pole top pin layer over. Conductor is barely tied in. | 303 Bartley Hollow, Penny Road, Virgie, Ky.
2020 | 2020-04-06 | Pikeville |  |  | 37830167D00396 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown | 240 Rob Damron Road, Penny Road, Virgie, Ky.
2020 | 2020-04-06 | Pikeville |  |  | 37830190D00061 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Ky. Hwy 610 West, Virgie, Ky. | 2020-04-06
2020 | 2020-04-07 | Pikeville |  |  | 37830190D00158 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop laying on roof. Probably need to install secondary pole for clearance. | 394 Long Fork Road, Virgie, Ky.
2020 | 2020-04-07 | Pikeville |  |  | 37830190D00245 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker. Completed. Also satellite dish on pole. | 316 Long Fork Road, Virgie, Ky.
2020 | 2020-04-07 | Pikeville |  |  | 37830190D00292 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole.Needs removed | 600 Long Fork Road, Virgie, Ky. | 2020-04-07
2020 | 2020-04-07 | Pikeville |  |  | 37830190D00389 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole.Needs removed | Ky. Hwy 610 West, Virgie, Ky. | 2020-04-07
2020 | 2020-04-07 | Pikeville |  |  | 37830191B00058 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 769 Long Fork, Virgie, Ky. | 2020-04-07
2020 | 2020-04-07 | Pikeville |  |  | 37830214C00060 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown | 1285 Long Fork Road,Virgie, Ky.
2020 | 2020-04-07 | Pikeville |  |  | 37830214C00061 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Tackett Branch, Virgie, Ky. | 2020-04-07
2020 | 2020-04-07 | Pikeville |  |  | 37830237C00155 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 3530 Long Fork Road,Virgie, Ky. | 2020-04-07
2020 | 2020-04-08 | Pikeville |  |  | 37830236000002 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Marshals Branch, Long Fork Road, Virgie, Ky. 41572 | 2020-04-08
2020 | 2020-04-08 | Pikeville |  |  | 37830236000002 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Marshals Branch, Long Fork Road, Virgie, Ky. 41572 | 2020-04-08
2020 | 2020-04-08 | Pikeville |  |  | 37830237B00035 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | other: customer owned attachment | Foreign | NO | Service drop low clearance. Approximately 8.5 ft. above ground. Customer service pole is rotten and propped up. It’s a long drop, probably need to install secondary pole. | 5858 Long Fork, Virgie, KY 41572, USA
2020 | 2020-04-08 | Pikeville |  |  | 37830260000084 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Neutral conductor down/missing. #2 aluminum conductor. | 7564 Speight Rd, Virgie, KY 41572, USA
2020 | 2020-04-09 | Pikeville |  |  | 37830284000103 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Long Fork Road, Virgie, Ky. | 2020-04-09
2020 | 2020-04-09 | Pikeville |  |  | 37830308000024 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Long Fork, Kentucky 41572, USA | 2020-04-09
2020 | 2020-04-20 | Pikeville | 78695313 |  | 37830190B00303 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. | 1846 Indian Creek Road, Virgie, Ky. | 2021-01-27
2020 | 2020-04-21 | Pikeville |  |  | 37830165000196 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators melting/deteoriated | 2872 Little Robinson Creek, Virgie, KY 41572, USA
2020 | 2020-04-21 | Pikeville | 86515583 |  | 37830166000024 | TRUE | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/melting | Little Fork Road, Little Robinson Creek, Virgie, Ky.
2020 | 2020-04-21 | Pikeville |  |  | 37830166000070 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator melting/deteoriated | 2476 Little Robinson Creek, Virgie, KY 41572, USA | 2023-12-18
2020 | 2020-04-21 | Pikeville |  |  | 37830166000248 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 1353 Little Fork, Virgie, KY 41572, USA
2020 | 2020-04-22 | Pikeville |  |  | 38830786B00364 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Tulip St, Paintsville, KY 41240, USA | 2020-04-22
2020 | 2020-04-22 | Pikeville |  |  | 38830810A00299 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Henry St, Paintsville, KY 41240, USA | 2020-04-22
2020 | 2020-04-22 | Pikeville |  |  | 38830810A00301 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Henry St, Paintsville, KY 41240, USA | 2020-04-22
2020 | 2020-04-22 | Pikeville |  |  | 38830810B00022 |  | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarms are deteoriated | 2496 Ky. Rte. 1107, Paintsville, Ky.
2020 | 2020-04-22 | Pikeville |  |  | 38830810B00029 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Davis Branch, Paintsville, Ky. | 2020-04-22
2020 | 2020-04-22 | Pikeville |  |  | 38830810B00029 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Davis Branch, Paintsville, Ky. | 2020-04-22
2020 | 2020-04-22 | Pikeville |  |  | 38830810B00197 |  | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | YES | Pole is rotten at ground line. Guy wire needs marker .Completed marker . 35 class 4 pole | 57 Roberts Branch, Paintsville, KY 41240, USA | 2020-04-22
2020 | 2020-04-22 | Pikeville |  |  | 38830810B00197 |  | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | YES | Pole is rotten at ground line. Guy wire needs marker .Completed marker . 35 class 4 pole | 57 Roberts Branch, Paintsville, KY 41240, USA | 2020-04-22
2020 | 2020-04-22 | Pikeville |  |  | 38830810B00197 |  | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | YES | Pole is rotten at ground line. Guy wire needs marker .Completed marker . 35 class 4 pole | 57 Roberts Branch, Paintsville, KY 41240, USA | 2020-04-22
2020 | 2020-04-22 | Pikeville |  |  | 38830810B00197 |  | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | YES | Pole is rotten at ground line. Guy wire needs marker .Completed marker . 35 class 4 pole | 57 Roberts Branch, Paintsville, KY 41240, USA | 2020-04-22
2020 | 2020-04-22 | Pikeville |  |  | 38830834A00116 | TRUE | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarms are rotten | 821 Ky. Rte. 302, West Van Lear, Ky.
2020 | 2020-04-23 | Pikeville |  |  | 3830810 D10780 |  | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer and secondary | Ky. Rte. 40 East, Meally, Ky.
2020 | 2020-04-23 | Pikeville |  |  | 38830787B40155 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole. | Meek Road, Ky. Rte. 40 East, Meally, Ky. | 2020-04-23
2020 | 2020-04-23 | Pikeville |  |  | 38830787B40155 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole. | Meek Road, Ky. Rte. 40 East, Meally, Ky. | 2020-04-23
2020 | 2020-04-23 | Pikeville |  |  | 38830787B40155 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole. | Meek Road, Ky. Rte. 40 East, Meally, Ky. | 2020-04-23
2020 | 2020-04-23 | Pikeville |  |  | 38830787B40155 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole. | Meek Road, Ky. Rte. 40 East, Meally, Ky. | 2020-04-23
2020 | 2020-04-23 | Pikeville |  |  | 38830810B20443 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 100 N Buckingham Ave, West Van Lear, KY 41268, USA | 2020-04-23
2020 | 2020-04-23 | Pikeville |  |  | 38830811000094 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Buffalo Road, Meally, Ky. | 2020-04-23
2020 | 2020-04-23 | Pikeville |  |  | 38830811000195 |  | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 612 Buffalo Rd, Meally, Ky.
2020 | 2020-04-23 | Pikeville | 77133651 | DKY0110387 | 38830811000197 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service hanging down pole. Transformer is open | 751 Buffalo Rd, Meally, KY 41234, USA | 2021-01-26
2020 | 2020-04-23 | Pikeville |  |  | 38830811000253 |  | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole is leaning considerably. Wire sagging low. Needs anchor and guy wire installed. | 891 Buffalo Rd, Meally, KY 41234, USA
2020 | 2020-04-23 | Pikeville |  |  | 38830811B00004 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Ky Rte. 40 East, Meally, Ky. | 2020-04-23
2020 | 2020-04-23 | Pikeville |  |  | 38830811B00060 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 239 Short Fork, Meally, Ky. | 2020-04-23
2020 | 2020-04-23 | Pikeville |  |  | 38830811B00069 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 400 Loon Branch, Meally, KY 41234, USA | 2020-04-23
2020 | 2020-04-23 | Pikeville |  |  | 38830834A00034 |  | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer and hardware. | Dawkins Avenue, West Van Lear, Ky.
2020 | 2020-04-23 | Pikeville |  |  | 38830834A00062 | TRUE | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 253 N Buckingham Ave, West Van Lear, KY 41268, USA
2020 | 2020-04-23 | Pikeville |  |  | 38830834C00012 |  | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop about 1” clearance over mobile home. Can take some slack out of drop but don’t know if it would be enough for clearance. Probably need to install secondary pole for clearance. | 306 Boat Gunnel Hollow, Ky. Route 40 East, Meally, Ky.
2020 | 2020-04-23 | Pikeville |  |  | 38830834C00326 | TRUE | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 481 Webb Hollow, Van Lear, KY 41265, USA
2020 | 2020-04-24 | Pikeville |  |  | 38830810C00070 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Woodland Estates, Paintsville, Ky. | 2020-04-24
2020 | 2020-04-24 | Pikeville |  |  | 38830810C00070 |  | 3420103-MAYO TRAIL / DAVIS BR | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Woodland Estates, Paintsville, Ky. | 2020-04-24
2020 | 2020-04-27 | Pikeville |  |  | 37830214D00006 | TRUE | 3401001-ELWOOD / DORTON | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown | 63 Jonancy Bottom, Jonancy, Ky. 41572
2020 | 2020-04-27 | Pikeville |  |  | 37830238000005 |  | 3401001-ELWOOD / DORTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Ky Hwy. 610 West, Jonancy, Ky. | 2020-04-27
2020 | 2020-04-27 | Pikeville |  |  | 37830239000070 |  | 3401001-ELWOOD / DORTON | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator melting/deteoriated | 755 Elswick Branch, Jonancy, Ky.
2020 | 2020-04-27 | Pikeville | 80146122 | DKY0114654 | 37830239000182 |  | 3401001-ELWOOD / DORTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer on pole 182. Also remove secondary and secondary pole 239-208.Probably can truck transformer pole if dry. | 815 Elswick Fork, Jonancy, Ky. | 2021-09-27
2020 | 2020-04-27 | Pikeville |  |  | 37830239000221 |  | 3401001-ELWOOD / DORTON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated | 1033 Elswick Branch, Jonancy, Ky.
2020 | 2020-04-27 | Pikeville |  |  | 37830262000222 |  | 3401001-ELWOOD / DORTON | Service Work | OH |  | lightning arresters/insulators: damaged , guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Beefhide Creek, Dorton, Ky. | 2020-04-28
2020 | 2020-04-28 | Pikeville |  |  | 37830262000044 |  | 3401001-ELWOOD / DORTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Beef hide Creek, Dorton, Ky. | 2020-04-28
2020 | 2020-04-28 | Pikeville |  |  | 37830262000044 |  | 3401001-ELWOOD / DORTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Beef hide Creek, Dorton, Ky. | 2020-04-28
2020 | 2020-04-28 | Pikeville |  |  | 37830262000051 |  | 3401001-ELWOOD / DORTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Lick Fork, Beefhide Creek, Dorton, Ky. | 2020-04-28
2020 | 2020-04-28 | Pikeville |  |  | 37830286000041 |  | 3401001-ELWOOD / DORTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Brushy Fork Rd & Beefhide Creek, Kentucky 41537, USA | 2020-04-28
2020 | 2020-04-28 | Pikeville |  |  | 37830286000041 |  | 3401001-ELWOOD / DORTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Brushy Fork Rd & Beefhide Creek, Kentucky 41537, USA | 2020-04-28
2020 | 2020-04-28 | Pikeville |  |  | 37830286000041 |  | 3401001-ELWOOD / DORTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Brushy Fork Rd & Beefhide Creek, Kentucky 41537, USA | 2020-04-28
2020 | 2020-04-28 | Pikeville |  |  | 37830310000112 |  | 3401001-ELWOOD / DORTON | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop laying on roof of house | 1794 Lick Fork, Beefhide Creek, Dorton, Ky.
2020 | 2020-04-28 | Pikeville |  |  | 37830310000150 |  | 3401001-ELWOOD / DORTON | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wires (3) hanging down pole. Needs reattached. Don’t see anchors . Probably need to install anchors. | Johns Fork, Beefhide Creek, Dorton, Ky.
2020 | 2020-04-28 | Pikeville |  |  | 37830310000163 |  | 3401001-ELWOOD / DORTON | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/missing . 2 spans down to dead end pole 46. Nothing served beyond this pole 163. Last two spans could actually be removed but would need a dead end,anchor and guy on pole 183. | Johns Fork Rd, Kentucky 41537, USA
2020 | 2020-04-29 | Pikeville |  |  | 37830263B00025 |  | 3401001-ELWOOD / DORTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Ky Hwy 610 West, Dorton, Ky. | 2020-04-29
2020 | 2020-04-29 | Pikeville |  |  | 37830263B00093 |  | 3401001-ELWOOD / DORTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY-610, Kentucky, USA | 2020-04-29
2020 | 2020-04-29 | Pikeville |  |  | 37830263B00093 |  | 3401001-ELWOOD / DORTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY-610, Kentucky, USA | 2020-04-29
2020 | 2020-04-29 | Pikeville |  |  | 37830263B10139 |  | 3401001-ELWOOD / DORTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky Hwy 610 West, Dorton, Ky. | 2020-04-29
2020 | 2020-04-30 | Pikeville |  |  | 37830287000104 |  | 3401001-ELWOOD / DORTON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 612 Owl Branch, Kentucky 41537, USA
2020 | 2020-04-30 | Pikeville |  |  | 37830287000105 |  | 3401001-ELWOOD / DORTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Owl Branch, Kentucky 41537, USA | 2020-04-30
2020 | 2020-04-30 | Pikeville |  |  | 37830287000146 |  | 3401001-ELWOOD / DORTON | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive secondary pole. | 495 Owl Branch, Dorton, Ky.
2020 | 2020-04-30 | Pikeville |  |  | 37830287000152 |  | 3401001-ELWOOD / DORTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Secondary pole is leaning | 1593 Dorton/ Jenkins Hwy. Dorton, Ky.
2020 | 2020-04-30 | Pikeville |  |  | 37830287000214 | TRUE | 3401001-ELWOOD / DORTON | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown | 218 Owl Branch, Dorton, Ky.
2020 | 2020-04-30 | Pikeville |  |  | 37830287000313 |  | 3401001-ELWOOD / DORTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole is leaning. Needs straightening. Might need side guy installed. | 814 Owl Branch, Dorton, Ky.
2020 | 2020-05-04 | Pikeville |  |  | 38830654A00579 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Shady Lane, West Liberty, Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654A00579 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Shady Lane, West Liberty, Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654B00171 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Davis Lane, West Liberty, Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654B00171 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Davis Lane, West Liberty, Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654B00171 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Davis Lane, West Liberty, Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654B00172 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Liberty Road, West Liberty, Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654B00172 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Liberty Road, West Liberty, Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654B00275 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Liberty Road, West Liberty, Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654B00397 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Townhouse Lane, West Liberty, Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654B00397 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Townhouse Lane, West Liberty, Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654B00692 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Davis Lane, West Liberty , Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654B00692 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Davis Lane, West Liberty , Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654C00626 |  | 3401802-INDEX / HOSPITAL | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer bank and service. | Wells Hills Lane, West Liberty, Ky.
2020 | 2020-05-04 | Pikeville |  |  | 38830654D00004 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Wells Hills Lane, West Liberty, Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654D00374 |  | 3401802-INDEX / HOSPITAL | Line Work | OH | UG conduit: damaged or separated |  |  | KPC | NO | Underground conduit separated. Only has tape holding it to the pole. | 51 Wells Hill, West Liberty, Ky.
2020 | 2020-05-04 | Pikeville |  |  | 38830654D00449 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Liberty Road, West Liberty, Ky. | 2020-05-04
2020 | 2020-05-04 | Pikeville |  |  | 38830654D00498 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Wells Hills Lane, West Liberty, Ky. | 2020-05-04
2020 | 2020-05-05 | Pikeville |  |  | 38830654D00166 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Riverside Drive, West Liberty, Ky. | 2020-05-05
2020 | 2020-05-05 | Pikeville |  |  | 38830654D00246 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Riverside Drive, West Liberty, Ky. | 2020-05-05
2020 | 2020-05-05 | Pikeville |  |  | 38830654D00299 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Riverview Drive, West Liberty, Ky. | 2020-05-05
2020 | 2020-05-05 | Pikeville |  |  | 38830655A00065 | TRUE | 3401802-INDEX / HOSPITAL | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Walnut Road, West Liberty, Ky.
2020 | 2020-05-05 | Pikeville |  |  | 38830655B00084 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Gardner Drive, West Liberty, Ky. | 2020-05-05
2020 | 2020-05-06 | Pikeville |  |  | 38830654B00389 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Reed Ln, West Liberty, KY 41472, USA | 2020-05-06
2020 | 2020-05-06 | Pikeville |  |  | 38830654B00389 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Reed Ln, West Liberty, KY 41472, USA | 2020-05-06
2020 | 2020-05-06 | Pikeville |  |  | 38830654B00389 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Reed Ln, West Liberty, KY 41472, USA | 2020-05-06
2020 | 2020-05-06 | Pikeville |  |  | 38830654B00389 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Reed Ln, West Liberty, KY 41472, USA | 2020-05-06
2020 | 2020-05-06 | Pikeville |  |  | 38830654B00522 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dixie Ln, West Liberty, KY 41472, USA | 2020-05-06
2020 | 2020-05-06 | Pikeville |  |  | 38830654D00258 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire slack. Needs tightened. needs marker (3) | Daisy Knob Road, West Liberty, Ky. | 2020-05-06
2020 | 2020-05-06 | Pikeville |  |  | 38830654D00501 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Daisy Knob Rd, West Liberty, KY 41472, USA | 2020-05-06
2020 | 2020-05-06 | Pikeville |  |  | 38830654D00501 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Daisy Knob Rd, West Liberty, KY 41472, USA | 2020-05-06
2020 | 2020-05-06 | Pikeville |  |  | 38830678A30284 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Reed Ln, West Liberty, KY 41472, USA | 2020-05-06
2020 | 2020-05-06 | Pikeville |  |  | 38830678C00101 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Circle Drive, West Liberty, Ky. | 2020-05-06
2020 | 2020-05-06 | Pikeville |  |  | 38830678C00178 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Circle Road, West Liberty, Ky. | 2020-05-06
2020 | 2020-05-07 | Pikeville |  |  | 38830654D00367 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker (2) | Keeton Heights, West Liberty, KY 41472, USA | 2020-05-07
2020 | 2020-05-07 | Pikeville |  |  | 38830654D00367 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker (2) | Keeton Heights, West Liberty, KY 41472, USA | 2020-05-07
2020 | 2020-05-07 | Pikeville |  |  | 38830654D00400 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Brooks Ln, West Liberty, KY 41472, USA | 2020-05-07
2020 | 2020-05-07 | Pikeville |  |  | 38830678C00108 | TRUE | 3401801-INDEX / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 391 Keeton Ave, West Liberty, KY 41472, USA
2020 | 2020-05-07 | Pikeville |  |  | 38830678C00173 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (4) | Dogwood Ln, West Liberty, KY 41472, USA | 2020-05-07
2020 | 2020-05-07 | Pikeville |  |  | 38830678C00185 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Sugar Maple Ln, West Liberty, KY 41472, USA | 2020-05-07
2020 | 2020-05-07 | Pikeville |  |  | 38830678C00185 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Sugar Maple Ln, West Liberty, KY 41472, USA | 2020-05-07
2020 | 2020-05-07 | Pikeville |  |  | 38830678C00188 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Dogwood Ln, West Liberty, KY 41472, USA | 2020-05-07
2020 | 2020-05-07 | Pikeville |  |  | 38830678C00200 |  | 3401801-INDEX / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 100 Poplar Ct, West Liberty, KY 41472, USA
2020 | 2020-05-07 | Pikeville |  |  | 38830679000158 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dogwood Ln, West Liberty, KY 41472, USA | 2020-05-07
2020 | 2020-05-08 | Pikeville |  |  | 38830655B00271 |  | 3401801-INDEX / DISTRIBUTION | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Primary conductor floating. | 148 Spaws Creek, West Liberty, Ky.
2020 | 2020-05-08 | Pikeville |  |  | 38830678D00058 |  | 3401801-INDEX / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Dead-end Insulator broken | 672 County Garage Rd, West Liberty, KY 41472, USA
2020 | 2020-05-08 | Pikeville |  |  | 38830679000015 |  | 3401801-INDEX / DISTRIBUTION | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive primary and secondary tap all the way to pole 134. Primary is gone already. Road crossing. Take off pole out in bottom. Transformer pole may be accessible if dry or frozen. | Hwy 460 E, West Liberty, KY 41472, USA
2020 | 2020-05-08 | Pikeville |  |  | 38830679000089 |  | 3401801-INDEX / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 405 County Garage Rd, West Liberty, KY 41472, USA
2020 | 2020-05-11 | Pikeville |  |  | 38830727000041 |  | 3401801-INDEX / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 2849 Jones Creek Road, West Liberty, Ky.
2020 | 2020-05-12 | Pikeville |  |  | 38830679000040 |  | 3401801-INDEX / DISTRIBUTION | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire hanging down pole. Needs reattached. Anchor is there. | Hwy 460 E, West Liberty, KY 41472, USA
2020 | 2020-05-12 | Pikeville |  |  | 38830727000051 |  | 3401801-INDEX / DISTRIBUTION | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive section of line. (4) spans and (3) poles. Wire down several spans. | May Branch, White Oak, Ky.
2020 | 2020-05-12 | Pikeville |  |  | 38830727000053 |  | 3401801-INDEX / DISTRIBUTION | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive section of line (2) spans and (3) poles to end of line at pole 63 | May Branch, White Oak, Ky.
2020 | 2020-05-14 | Pikeville |  |  | 38830801000109 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Pine Valley Road, White oak, Ky. | 2020-05-14
2020 | 2020-05-18 | Pikeville | 79932455 | DKY0113994 | 38820941D00432 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer and service | 1140 SR 292, South Williamson, Ky. | 2022-04-19
2020 | 2020-05-18 | Pikeville |  |  | 38820941D00472 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Wilson Loop, South Williamson, Ky. | 2020-05-18
2020 | 2020-05-18 | Pikeville |  |  | 38820942B20023 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 638 Central Ave, South Williamson, KY 41503, USA | 2020-05-18
2020 | 2020-05-18 | Pikeville |  |  | 38820942B31428 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Virginia Avenue, South Williamson, Ky. | 2020-05-18
2020 | 2020-05-18 | Pikeville | 79834580 | DKY0113893 | 38820965A00058 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 290 Caney Fork, Turkey Creek, South Williamson, Ky. | 2022-02-16
2020 | 2020-05-18 | Pikeville |  |  | 38820965A00071 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Secondary conductor on ground. | 707 Caney Fork, Turkey Creek, South Williamson, Ky. | 2023-02-03
2020 | 2020-05-19 | Pikeville |  |  | 38820964D00035 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 5388 Long Branch, Sidney, Ky. | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820965B00040 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 176 Cold Fork, Turkey Creek, KY 41514, USA | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820965B00095 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 478 Cold Fork, Turkey Creek, KY 41514, USA | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820965B00162 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 390 Cold Fork, Turkey Creek, KY 41514, USA | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820965C00194 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Church of Christ Road, Turkey Creek, Ky. 41514 | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820965C00194 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Church of Christ Road, Turkey Creek, Ky. 41514 | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820965C00194 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Church of Christ Road, Turkey Creek, Ky. 41514 | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820965C00194 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Church of Christ Road, Turkey Creek, Ky. 41514 | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820965D00032 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | 2208 Turkey Creek Rd, Belfry, KY 41514, USA | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820989A00139 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Sukey Fork , Turkey Creek, Belfry, Ky. | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820989B00144 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 412 Sukey Fork, Belfry, KY 41514, USA | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820989B00144 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 412 Sukey Fork, Belfry, KY 41514, USA | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820989B00144 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 412 Sukey Fork, Belfry, KY 41514, USA | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820989B00144 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 412 Sukey Fork, Belfry, KY 41514, USA | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820989B00144 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 412 Sukey Fork, Belfry, KY 41514, USA | 2020-05-19
2020 | 2020-05-19 | Pikeville | 79931635 | DKY0113993 | 38820989B00231 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 412 Sukey Fork, Belfry, KY 41514, USA | 2021-08-12
2020 | 2020-05-19 | Pikeville |  |  | 38820989C00214 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 2749 Turkey Creek Rd, Belfry, KY 41514, USA | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820989C00214 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 2749 Turkey Creek Rd, Belfry, KY 41514, USA | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820989C00214 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 2749 Turkey Creek Rd, Belfry, KY 41514, USA | 2020-05-19
2020 | 2020-05-19 | Pikeville | Outage # 4855371 |  | 38820989C00266 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop low clearance. Contacted servicer to have corrected. | 2749 Turkey Creek Rd, Belfry, KY 41514, USA | 2020-05-19
2020 | 2020-05-19 | Pikeville |  |  | 38820989D00196 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 277 May Branch, Turkey Creek, KY 41514, USA | 2020-05-19
2020 | 2020-05-20 | Pikeville |  |  | 38820941D00545 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 229 Wilson Loop, South Williamson, KY 41503, USA | 2020-05-20
2020 | 2020-05-20 | Pikeville |  |  | 38820942A20671 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line. @ in front of Enterprise rental. | W 3rd Ave, Williamson, WV 25661, USA | 2023-01-04
2020 | 2020-05-20 | Pikeville |  |  | 38820942A21417 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | N Sunset Blvd, Williamson, WV 25661, USA | 2020-05-20
2020 | 2020-05-21 | Pikeville | 84378756 | DKY0119548 | 38820966A20482 |  | 3417601-NEW CAMP / SOUTH SIDE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | lightning arresters/insulators: damaged |  | KPC | YES | Lightning arrestor blown | 491 New Camp Rd, South Williamson, KY 41503, USA | 2023-05-09
2020 | 2020-05-21 | Pikeville |  |  | 38820966A30644 |  | 3417601-NEW CAMP / SOUTH SIDE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Suspension insulator damaged by lightning on old transmission tower. @ on hill in front of Wendy’s. Pictures don’t show it very well. Have to use binoculars.Transmission tower is no longer in use/ line has been rerouted.....DJM | Goody, KY 41514, USA
2020 | 2020-05-21 | Pikeville |  |  | 38820966A30694 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | State Hwy 292 East, Goody, Ky. | 2020-05-21
2020 | 2020-05-21 | Pikeville |  |  | 38820966A30694 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | State Hwy 292 East, Goody, Ky. | 2020-05-21
2020 | 2020-05-26 | Pikeville |  |  | 38820966A30694 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | State Hwy 292 E, Kentucky 41514, USA | 2020-05-26
2020 | 2020-05-26 | Pikeville |  |  | 38820966A30694 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | State Hwy 292 E, Kentucky 41514, USA | 2020-05-26
2020 | 2020-05-26 | Pikeville |  |  | 38820966A40090 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 30 Goody Rd, Belfry, KY 41514, USA | 2020-05-26
2020 | 2020-05-26 | Pikeville |  |  | 38820966A40616 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 275 Southside Mall Rd, Forest Hills, KY 41527, USA | 2020-05-26
2020 | 2020-05-26 | Pikeville |  |  | 38820966B00610 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Southside Mall Road, South Williamson, Ky. | 2020-05-26
2020 | 2020-05-26 | Pikeville |  |  | 38820966C10104 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | State Hwy 292 E, Kentucky 41514, USA | 2020-05-26
2020 | 2020-05-26 | Pikeville |  |  | 38820966C10108 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 306 State Hwy 292 East, Goody, Ky | 2020-05-26
2020 | 2020-05-26 | Pikeville |  |  | 38820966C10463 |  | 3417601-NEW CAMP / SOUTH SIDE | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Box Elder tree completely covering pole | 339 State Hwy 292 East, Goody, Ky. | 2020-06-02
2020 | 2020-05-26 | Pikeville |  |  | 38820966C20100 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 379 State Hwy 292 East, Goody, Ky. | 2020-05-26
2020 | 2020-05-26 | Pikeville |  |  | 38820966C20100 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 379 State Hwy 292 East, Goody, Ky. | 2020-05-26
2020 | 2020-05-26 | Pikeville |  |  | 38820966D00080 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Mall Road, South Williamson, Ky. | 2020-05-26
2020 | 2020-05-26 | Pikeville |  |  | 38820966D00650 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Southside Mall Road, Goody, Ky. | 2020-05-26
2020 | 2020-05-26 | Pikeville |  |  | 38820967A00095 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | State Hwy 292 E, Kentucky 41514, USA | 2020-05-26
2020 | 2020-05-26 | Pikeville |  |  | 38820967A00095 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | State Hwy 292 E, Kentucky 41514, USA | 2020-05-26
2020 | 2020-05-26 | Pikeville | 79811410 | DKY0113883 | 38820967B00114 |  | 3417601-NEW CAMP / SOUTH SIDE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm split. On hill. | 197 Aflex Bottom, Belfry, KY 41514, USA | 2021-11-05
2020 | 2020-05-26 | Pikeville | 82896568 | DKY0117591 | 38820967B00386 |  | 3417601-NEW CAMP / SOUTH SIDE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive pole and transformer . Also remove inactive poles 126 and 1020. One pole is truck access. | 561 Aflex Cemetery Road, Aflex, Ky. | 2022-08-09
2020 | 2020-05-26 | Pikeville | 77011883 | DKY0110494 | 38820967B01027 |  | 3417601-NEW CAMP / SOUTH SIDE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Secondary pole rotten. Does not have a pole tag and is not shown on field view. Taps off pole 115. The pole is next to the street @ 197 Aflex Bottom. | 197 Aflex Bottom, Belfry, KY 41514, USA | 2020-12-15
2020 | 2020-05-27 | Pikeville |  |  | 38830858A00209 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | Cannel Coal Gap, Van Lear, Ky. 41222 | 2020-05-27
2020 | 2020-05-27 | Pikeville |  |  | 38830858A00209 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | Cannel Coal Gap, Van Lear, Ky. 41222 | 2020-05-27
2020 | 2020-05-27 | Pikeville |  |  | 38830858A00209 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | Cannel Coal Gap, Van Lear, Ky. 41222 | 2020-05-27
2020 | 2020-05-27 | Pikeville |  |  | 38830858A00209 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | Cannel Coal Gap, Van Lear, Ky. 41222 | 2020-05-27
2020 | 2020-05-27 | Pikeville |  |  | 38830858A00211 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Cannel Coal Gap, West Van Lear, Ky. 41222 | 2020-05-27
2020 | 2020-05-27 | Pikeville |  |  | 38830858A00211 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Cannel Coal Gap, West Van Lear, Ky. 41222 | 2020-05-27
2020 | 2020-05-27 | Pikeville |  |  | 38830858A00211 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Cannel Coal Gap, West Van Lear, Ky. 41222 | 2020-05-27
2020 | 2020-05-27 | Pikeville |  |  | 38830858A00216 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Cannel Coal Gap, West Van Lear, Ky. | 2020-05-27
2020 | 2020-05-27 | Pikeville |  |  | 38830858A20425 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive transformer and secondary pole 885 and service. | 31 Cannel Ln, Hagerhill, KY 41222, USA
2020 | 2020-05-28 | Pikeville |  |  | 38830858A00210 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Cannel Coal Gap, Hager Hill, Ky. | 2020-05-28
2020 | 2020-05-28 | Pikeville |  |  | 38830858A00212 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on switch pole. | Cannel Coal Gap, Hager Hill, Ky. | 2020-05-28
2020 | 2020-05-28 | Pikeville |  |  | 38830858A00212 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on switch pole. | Cannel Coal Gap, Hager Hill, Ky. | 2020-05-28
2020 | 2020-05-28 | Pikeville |  |  | 38830858A00212 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on switch pole. | Cannel Coal Gap, Hager Hill, Ky. | 2020-05-28
2020 | 2020-05-28 | Pikeville |  |  | 38830858A00212 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on switch pole. | Cannel Coal Gap, Hager Hill, Ky. | 2020-05-28
2020 | 2020-05-28 | Pikeville |  |  | 38830858A00212 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on switch pole. | Cannel Coal Gap, Hager Hill, Ky. | 2020-05-28
2020 | 2020-05-28 | Pikeville |  |  | 38830858A00212 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on switch pole. | Cannel Coal Gap, Hager Hill, Ky. | 2020-05-28
2020 | 2020-05-28 | Pikeville |  |  | 38830858A00217 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Cannel Coal Gap, Hager Hill, Ky. | 2020-05-28
2020 | 2020-06-01 | Pikeville |  |  | 38830835B00184 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is partially washed out in creek. Has bayonet on top. | 185 Wolfpen Branch, Van Lear, Ky.
2020 | 2020-06-01 | Pikeville |  |  | 38830858A00219 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Cannel Coal Gap, Hager Hill, Ky. | 2020-06-01
2020 | 2020-06-01 | Pikeville |  |  | 38830858A40223 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on switch pole | Cannel Coal Gap, Hager Hill, Ky. | 2020-06-01
2020 | 2020-06-01 | Pikeville |  |  | 38830858A40223 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on switch pole | Cannel Coal Gap, Hager Hill, Ky. | 2020-06-01
2020 | 2020-06-01 | Pikeville |  |  | 38830859A00004 |  | 3409301-KENWOOD / WVANLEAR | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Miller’s Creek, Van Lear, Ky. | 2020-06-01
2020 | 2020-06-02 | Pikeville |  |  | 38830837B30097 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (3) | Middle Fork Rd, Inez, KY 41224, USA | 2020-06-02
2020 | 2020-06-02 | Pikeville |  |  | 38830837B40074 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Airport Road, Inez, Ky. | 2020-06-02
2020 | 2020-06-02 | Pikeville |  |  | 38830861000036 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Airport Road, Inez, Ky. | 2020-06-02
2020 | 2020-06-02 | Pikeville |  |  | 38830861000038 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Airport Road, Inez, Ky. | 2020-06-02
2020 | 2020-06-02 | Pikeville |  |  | 38830861A30070 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Airport Road, Inez, Ky. | 2020-06-02
2020 | 2020-06-03 | Pikeville |  |  | 38830814D00022 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 900 Davella Road, Inez, Ky. | 2020-06-03
2020 | 2020-06-03 | Pikeville |  |  | 38830814D00049 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | 87 Setser Branch, Davella, Ky. | 2020-06-03
2020 | 2020-06-03 | Pikeville |  |  | 38830814D00054 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | McGinnis Branch, Davella Road, Inez, Ky. | 2020-06-03
2020 | 2020-06-03 | Pikeville |  |  | 38830814D00071 | TRUE | 3411401-DEWEY / INEZ | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 457 Setser Branch, Davella Road, Inez, Ky.
2020 | 2020-06-03 | Pikeville |  |  | 38830815B00137 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 225 Nathan Place, Davella Road, Inez, Ky. | 2020-06-03
2020 | 2020-06-03 | Pikeville |  |  | 38830815B00138 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 1800 Main St, Jefferson, MA 01522, USA | 2020-06-03
2020 | 2020-06-03 | Pikeville |  |  | 38830815B00138 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 1800 Main St, Jefferson, MA 01522, USA | 2020-06-03
2020 | 2020-06-03 | Pikeville |  |  | 38830837D00054 |  | 3411401-DEWEY / INEZ | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken @ attachment point on pole. Still attached to the anchor. In front of gas well on Ky. Rte. 3 | Middle Fork Rd, Inez, KY 41224, USA
2020 | 2020-06-03 | Pikeville |  |  | 38830838A00095 |  | 3411401-DEWEY / INEZ | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | 3049 Davella Road, Inez, Ky.
2020 | 2020-06-03 | Pikeville |  |  | 38830838B00111 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Davella Rd, Kentucky 41214, USA | 2020-06-03
2020 | 2020-06-03 | Pikeville |  |  | 38830838C00010 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | 1539 Davella Road, Inez, Ky. | 2020-06-03
2020 | 2020-06-03 | Pikeville |  |  | 38830838C00108 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 2305 Davella Road, Inez, Ky. | 2020-06-03
2020 | 2020-06-04 | Pikeville |  |  | 38830791A00116 |  | 3411401-DEWEY / INEZ | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. De-energized | 133 Blackberry Road, Davella, Ky. | 2020-06-04
2020 | 2020-06-04 | Pikeville |  |  | 38830791A00116 |  | 3411401-DEWEY / INEZ | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. De-energized | 133 Blackberry Road, Davella, Ky. | 2020-06-04
2020 | 2020-06-04 | Pikeville |  |  | 38830791B00064 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Cumbo Road, Davella, Ky. | 2020-06-04
2020 | 2020-06-04 | Pikeville |  |  | 38830791C00164 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Blackburn Trailer Park, Davis Branch, Davella, Ky. | 2020-06-04
2020 | 2020-06-04 | Pikeville |  |  | 38830815A00014 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Davella Rd & Blackberry Rd, Kentucky 41224, USA | 2020-06-04
2020 | 2020-06-04 | Pikeville |  |  | 38830815A00014 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Davella Rd & Blackberry Rd, Kentucky 41224, USA | 2020-06-04
2020 | 2020-06-04 | Pikeville |  |  | 38830815A00014 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Davella Rd & Blackberry Rd, Kentucky 41224, USA | 2020-06-04
2020 | 2020-06-04 | Pikeville |  |  | 38830815A00014 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Davella Rd & Blackberry Rd, Kentucky 41224, USA | 2020-06-04
2020 | 2020-06-04 | Pikeville |  |  | 38830815A00032 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Babe Delong Road, Davella, Ky. | 2020-06-04
2020 | 2020-06-04 | Pikeville |  |  | 38830815C00071 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Venters Branch, Davella, Ky. | 2020-06-04
2020 | 2020-06-08 | Pikeville |  |  | 38830767C00138 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Otto Road, Inez, Ky. | 2020-06-08
2020 | 2020-06-08 | Pikeville |  |  | 38830767C00142 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Otto Road, Inez, Ky. | 2020-06-08
2020 | 2020-06-08 | Pikeville |  |  | 38830767C00150 |  | 3411401-DEWEY / INEZ | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on goab pole. | Otto Road, Inez, Ky. | 2020-06-08
2020 | 2020-06-08 | Pikeville |  |  | 38830767D00053 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Preece Road, Inez, Ky. | 2020-06-08
2020 | 2020-06-08 | Pikeville |  |  | 38830767D00053 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Preece Road, Inez, Ky. | 2020-06-08
2020 | 2020-06-08 | Pikeville |  |  | 38830767D00128 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | McGinnis Drive, Inez, Ky. | 2020-06-08
2020 | 2020-06-08 | Pikeville |  |  | 38830768A30390 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dogwood Heights, Inez, Ky. | 2020-06-08
2020 | 2020-06-08 | Pikeville |  |  | 38830768A30391 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dogwood Heights, Inez, Ky. | 2020-06-08
2020 | 2020-06-08 | Pikeville |  |  | 38830768A30391 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dogwood Heights, Inez, Ky. | 2020-06-08
2020 | 2020-06-08 | Pikeville |  |  | 38830791C00008 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Debord Road, Inez, Ky. | 2020-06-08
2020 | 2020-06-08 | Pikeville |  |  | 38830791C20159 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Debord Road, Inez, Ky. | 2020-06-08
2020 | 2020-06-08 | Pikeville |  |  | 38830791D00205 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Crum Branch, Inez, Ky. | 2020-06-08
2020 | 2020-06-09 | Pikeville |  |  | 38830767C00009 |  | 3411401-DEWEY / INEZ | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines. Next to recloser pole. | 307 Saltwell Rd, Inez, KY 41224, USA | 2020-11-16
2020 | 2020-06-09 | Pikeville |  |  | 38830767C00096 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 307 Saltwell Rd, Inez, KY 41224, USA | 2020-06-09
2020 | 2020-06-09 | Pikeville |  |  | 38830767C00114 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 565 Saltwell Rd, Tomahawk, KY 41262, USA | 2020-06-09
2020 | 2020-06-09 | Pikeville |  |  | 38830767C00114 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 565 Saltwell Rd, Tomahawk, KY 41262, USA | 2020-06-09
2020 | 2020-06-10 | Pikeville |  |  | 38830742D00010 |  | 3411401-DEWEY / INEZ | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | 334 Lower Wolf Branch, Tomahawk, Ky. | 2020-06-10
2020 | 2020-06-10 | Pikeville |  |  | 38830766A00122 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Avonelle Lane, Rockhouse Fork, Tomahawk, Ky.
2020 | 2020-06-10 | Pikeville |  |  | 38830766C00022 |  | 3411401-DEWEY / INEZ | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole has vines all over the transformer, cutout, etc. Customer says his power has been off twice when it rains because the fuse blows. | 52 Sherrill Spence Road, Rockhouse Fork, Tomahawk, Ky. | 2020-11-16
2020 | 2020-06-10 | Pikeville |  |  | 38830766C00079 |  | 3411401-DEWEY / INEZ | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 200 Horse Branch, Tomahawk, Ky.
2020 | 2020-06-10 | Pikeville |  |  | 38830766C00100 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Sherrill Spence Road, Tomahawk, Ky. | 2020-06-10
2020 | 2020-06-10 | Pikeville |  |  | 38830766D00090 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Rockhouse Fork, Tomahawk, Ky. | 2020-06-10
2020 | 2020-06-10 | Pikeville |  |  | 38830766D00094 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Rockhouse Fork, Tomahawk, Ky. | 2020-06-10
2020 | 2020-06-10 | Pikeville |  |  | 38830789D00025 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Trace Fork, Rockhouse Fork, Tomahawk, Ky. | 2020-06-10
2020 | 2020-06-10 | Pikeville |  |  | 38830790A00068 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Trace Branch, Rockhouse Fork, Tomahawk, Ky. | 2020-06-10
2020 | 2020-06-10 | Pikeville |  |  | 38830790A00068 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Trace Branch, Rockhouse Fork, Tomahawk, Ky. | 2020-06-10
2020 | 2020-06-10 | Pikeville |  |  | 38830790C00015 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Rockhouse Fork, Tomahawk, Ky. | 2020-06-10
2020 | 2020-06-10 | Pikeville |  |  | 38830790C00015 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Rockhouse Fork, Tomahawk, Ky. | 2020-06-10
2020 | 2020-06-10 | Pikeville |  |  | 38830790C00096 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 99 Ayscue Hollow, Rockhouse Fork, Tomahawk, Ky.
2020 | 2020-06-10 | Pikeville |  |  | 38830814A00077 |  | 3411401-DEWEY / INEZ | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree laying on neutral conductor | Edgar Setser Road, Rockhouse Fork, Tomahawk, Ky. | 2020-11-16
2020 | 2020-06-11 | Pikeville |  |  | 38830743C00049 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Quail Hollow, Inez, KY 41224, USA | 2020-06-11
2020 | 2020-06-11 | Pikeville |  |  | 38830743C00049 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Quail Hollow, Inez, KY 41224, USA | 2020-06-11
2020 | 2020-06-11 | Pikeville |  |  | 38830743C00092 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | New Berry Ln, Inez, KY 41224, USA | 2020-06-11
2020 | 2020-06-11 | Pikeville |  |  | 38830743C00103 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Quail Hollow, Inez, KY 41224, USA | 2020-06-11
2020 | 2020-06-11 | Pikeville |  |  | 38830743C00122 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines . Next to bldg. 88 and apt. 122 | Quail Hollow, Inez, KY 41224, USA
2020 | 2020-06-11 | Pikeville |  |  | 38830743C00157 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Rockcastle Road, Inez, Ky. 41224 | 2020-06-11
2020 | 2020-06-11 | Pikeville |  |  | 38830743C00157 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Rockcastle Road, Inez, Ky. 41224 | 2020-06-11
2020 | 2020-06-11 | Pikeville |  |  | 38830743C00166 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines . Two poles next to each other.@ beside Oddfellows Lodge. | Old Paintsville Road, Inez, Ky.
2020 | 2020-06-11 | Pikeville |  |  | 38830743C30187 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Robinson Trailer Park Rd, Inez, KY 41224, USA | 2020-06-11
2020 | 2020-06-11 | Pikeville |  |  | 38830743D00098 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Wildflower Drive, Inez, Ky. 41224 | 2020-06-11
2020 | 2020-06-11 | Pikeville |  |  | 38830744B00338 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Haney Place, Inez, Ky. 41224 | 2020-06-11
2020 | 2020-06-11 | Pikeville |  |  | 38830744B00338 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Haney Place, Inez, Ky. 41224 | 2020-06-11
2020 | 2020-06-11 | Pikeville |  |  | 38830767C00001 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Lower Saltwell Road, Inez, Ky. 41224 | 2020-06-11
2020 | 2020-06-11 | Pikeville |  |  | 38830767C00001 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Lower Saltwell Road, Inez, Ky. 41224 | 2020-06-11
2020 | 2020-06-11 | Pikeville |  |  | 38830767C00136 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lower Saltwell Rd,Inez, Kentucky 41224, USA | 2020-06-11
2020 | 2020-06-15 | Pikeville |  |  | 38830720D00072 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Harvey Horn Drive, Turkey Creek, Inez, Ky. | 2020-06-15
2020 | 2020-06-15 | Pikeville |  |  | 38830720D00082 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Harvey Horn Drive, Turkey Creek, Inez, Ky. | 2020-06-15
2020 | 2020-06-15 | Pikeville |  |  | 38830720D00087 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Turkey Creek, Inez, KY 41224, USA | 2020-06-15
2020 | 2020-06-15 | Pikeville |  |  | 38830744A20087 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Wicker field Road, Inez, Ky. | 2020-06-15
2020 | 2020-06-15 | Pikeville |  |  | 38830744A20359 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Wickerfield Rd, Inez, KY 41224, USA | 2020-06-15
2020 | 2020-06-15 | Pikeville |  |  | 38830744A30326 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Flat Hollow, Turkey Creek, Inez, Ky. 41224 | 2020-06-15
2020 | 2020-06-15 | Pikeville |  |  | 38830744A40100 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Kennedy Drive, Inez, Ky. | 2020-06-15
2020 | 2020-06-15 | Pikeville |  |  | 38830744A40104 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Republican Drive, Inez, Ky. 41224 | 2020-06-15
2020 | 2020-06-15 | Pikeville |  |  | 38830744A40302 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Cassidy Ave, Inez, KY 41224, USA | 2020-06-15
2020 | 2020-06-15 | Pikeville |  |  | 38830744A40347 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Republican Drive, Inez, Ky. 41224 | 2020-06-15
2020 | 2020-06-15 | Pikeville |  |  | 38830744A40347 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Republican Drive, Inez, Ky. 41224 | 2020-06-15
2020 | 2020-06-15 | Pikeville |  |  | 38830744A40362 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Arlen Lane, Inez, Ky. | 2020-06-15
2020 | 2020-06-15 | Pikeville |  |  | 38830744C00143 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lick Branch, Turkey Creek, Inez, Ky. 41224 | 2020-06-15
2020 | 2020-06-16 | Pikeville |  |  | 38820649B00026 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Tug River Road, Webb, Ky. | 2020-06-16
2020 | 2020-06-16 | Pikeville |  |  | 38820649B30300 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Tug River Road, Webb, Ky. | 2020-06-16
2020 | 2020-06-16 | Pikeville |  |  | 38820649B30300 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Tug River Road, Webb, Ky. | 2020-06-16
2020 | 2020-06-16 | Pikeville |  |  | 38820673A00024 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Turkey Creek, Inez, Ky. | 2020-06-16
2020 | 2020-06-16 | Pikeville |  |  | 38820673A00024 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Turkey Creek, Inez, Ky. | 2020-06-16
2020 | 2020-06-16 | Pikeville |  |  | 38820697A00011 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer . First pole off 3 phase | Big Mud lick Road, Turkey Creek, Inez, Ky.
2020 | 2020-06-16 | Pikeville |  |  | 38820697A00014 |  | 3411401-DEWEY / INEZ | Service Work | OH |  |  | other: customer owned attachment | KPC | NO | Customers entrance bent over | Spruce Pine Fork, Turkey Creek, Inez, Ky.
2020 | 2020-06-16 | Pikeville |  |  | 38820697B00071 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Spruce Pine Fork, Turkey Creek, Inez, Ky. | 2020-06-16
2020 | 2020-06-16 | Pikeville | 79595929 | DKY0113621 | 38830672D00236 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Church Fork, Calf Creek, Webb, Ky. | 2021-07-14
2020 | 2020-06-17 | Pikeville |  |  | 38830671D30521 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Johnson Bottom, Rockcastle Road, Inez, Ky.
2020 | 2020-06-17 | Pikeville |  |  | 38830695C00015 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Johnson Bottom, Texas 78028, USA | 2020-06-17
2020 | 2020-06-17 | Pikeville |  |  | 38830695C00015 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Johnson Bottom, Texas 78028, USA | 2020-06-17
2020 | 2020-06-17 | Pikeville |  |  | 38830695C00028 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Garland Spencer Drive, Inez, Ky. | 2020-06-17
2020 | 2020-06-17 | Pikeville |  |  | 38830695C00036 |  | 3411401-DEWEY / INEZ | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Angle pole leaning. Missing guy wire. Needs new anchor and guy installed. | 4721 Rockcastle Road, Inez, Ky.
2020 | 2020-06-17 | Pikeville |  |  | 38830695C00043 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Rockcastle Road, Inez, Ky. 41224 | 2020-06-17
2020 | 2020-06-17 | Pikeville |  |  | 38830695C00081 |  | 3411401-DEWEY / INEZ | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole | Garland Spencer Drive, Inez, Ky.
2020 | 2020-06-17 | Pikeville |  |  | 38830696A00030 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Big Lick Road, Inez, Ky. | 2020-06-17
2020 | 2020-06-17 | Pikeville |  |  | 38830696A00030 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Big Lick Road, Inez, Ky. | 2020-06-17
2020 | 2020-06-17 | Pikeville |  |  | 38830696A00059 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Big Lick Branch Rd, Kentucky 41224, USA | 2020-06-17
2020 | 2020-06-17 | Pikeville |  |  | 38830696A00067 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Big Lick Road, Rockcastle Road, Inez, Ky. | 2020-06-17
2020 | 2020-06-17 | Pikeville |  |  | 38830696A00093 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Big Lick Road, Rockcastle Road, Inez, Ky. | 2020-06-17
2020 | 2020-06-17 | Pikeville |  |  | 38830696A00093 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Big Lick Road, Rockcastle Road, Inez, Ky. | 2020-06-17
2020 | 2020-06-17 | Pikeville |  |  | 38830696A00093 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Big Lick Road, Rockcastle Road, Inez, Ky. | 2020-06-17
2020 | 2020-06-18 | Pikeville |  |  | 38830647D00008 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Little Laurel River, Kentucky, USA | 2020-06-18
2020 | 2020-06-18 | Pikeville |  |  | 38830648A00563 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Buffalo Horn Road, Webb, Ky. | 2020-06-18
2020 | 2020-06-18 | Pikeville |  |  | 38830648B00036 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Webb Hollow, Buffalo Horn Road, Webb, Ky. | 2020-06-18
2020 | 2020-06-18 | Pikeville |  |  | 38830648B00036 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Webb Hollow, Buffalo Horn Road, Webb, Ky. | 2020-06-18
2020 | 2020-06-18 | Pikeville |  |  | 38830648B00048 |  | 3411401-DEWEY / INEZ | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole is leaning. Customer concerned about service drop being low over her house. Pole top is split slightly and pole top pin layed over. Drop clears roof by about 6 inches. | 259 Preston Lane, Inez, Ky.
2020 | 2020-06-18 | Pikeville |  |  | 38830672A00072 |  | 3411401-DEWEY / INEZ | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Neutral conductor sagged below communication cables. Primary conductor approximately 3.5 feet above cable. Span between pole 72 and 73. | 199 Peter Cave Branch, Inez, Ky.
2020 | 2020-06-18 | Pikeville | 79649600 | DKY0113689 | 38830672A00129 |  | 3411401-DEWEY / INEZ | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer . Behind old grassy school. | Grassy School Road, Inez, Ky. | 2021-07-07
2020 | 2020-06-18 | Pikeville |  |  | 38830672D00158 |  | 3411401-DEWEY / INEZ | Service Work | OH |  |  | other: customer owned attachment | KPC | NO | Customers entrance is bent over | 1263 Porter - Johnson Road, Peter Cave Branch, Inez, Ky.
2020 | 2020-06-22 | Pikeville |  |  | 38820577D00003 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole covered with vines . Could cause outage. | 4847 Yellow Creek Road, Inez, Ky.
2020 | 2020-06-22 | Pikeville |  |  | 38820577D00044 |  | 3411401-DEWEY / INEZ | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Installed guy marker. Satellite dish on pole (dish). Pole ground stolen also. | Yellow Creek Road, Inez, Ky.
2020 | 2020-06-22 | Pikeville |  |  | 38820601A00020 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Yellow Creek Road, Inez, Ky. | 2020-06-22
2020 | 2020-06-22 | Pikeville |  |  | 38820601A00025 |  | 3411401-DEWEY / INEZ | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning. Needs straightening. Probably a side guy installed. | Yellow Creek Road, Inez, Ky.
2020 | 2020-06-22 | Pikeville |  |  | 38820601A00201 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Yellow Creek Road, Inez, Ky. | 2020-06-22
2020 | 2020-06-22 | Pikeville |  |  | 38820601A00201 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Yellow Creek Road, Inez, Ky. | 2020-06-22
2020 | 2020-06-22 | Pikeville | 77208110 | DKY0110655 | 38820601B00056 |  | 3411401-DEWEY / INEZ | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | YES | Pole has been re-enforced at ground level with metal. Rest of pole seems solid still but the pole was installed in 1960. Probably will be fine for now but wouldn’t hurt to change in the not so near future. Installed guy marker. | 307 Blankenship Branch, Yellow Creek, Inez, Ky. | 2020-10-14
2020 | 2020-06-22 | Pikeville | 79488837 | DKY0113507 | 38820601C00036 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive tap including poles 134, pole 87, and secondary pole 175. Primary is down/missing. | 5436 Yellow Creek Road, Inez, Ky. | 2021-06-02
2020 | 2020-06-22 | Pikeville |  |  | 38820601C00106 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Yellow Creek Road, Inez, Ky. | 2020-06-22
2020 | 2020-06-22 | Pikeville |  |  | 38820601C00106 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Yellow Creek Road, Inez, Ky. | 2020-06-22
2020 | 2020-06-22 | Pikeville |  |  | 38820601C00106 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Yellow Creek Road, Inez, Ky. | 2020-06-22
2020 | 2020-06-22 | Pikeville |  |  | 38820601C00173 |  | 3411401-DEWEY / INEZ | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines | 5411 Yellow Creek Road,Inez, Ky. | 2020-11-16
2020 | 2020-06-22 | Pikeville | 77207993 | DKY0110653 | 38820625A00034 |  | 3411401-DEWEY / INEZ | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole top has a fiberglass extension. Angle pole . Probably be able to use line truck with long boom. | 8387 Yellow Creek, Inez, Ky. | 2020-09-09
2020 | 2020-06-22 | Pikeville |  |  | 38820625B00001 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Yellow Creek Road, Inez, Ky. | 2020-06-22
2020 | 2020-06-22 | Pikeville | 79587397 | DKY0113612 | 38820625B00007 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole covered with vines. Remove inactive transformer | Yellow Creek Road, Inez, Ky. | 2021-07-14
2020 | 2020-06-22 | Pikeville | 79575767 | DKY0113597 | 38820625B00008 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Yellow Creek Road, Inez, Ky. | 2021-08-25
2020 | 2020-06-22 | Pikeville |  |  | 38820625B00011 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 9334 Yellow Creek Road, Inez, Ky.
2020 | 2020-06-23 | Pikeville |  |  | 38820769B00127 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Setser Road, Coldwater Road, Inez, Ky. | 2020-06-23
2020 | 2020-06-23 | Pikeville |  |  | 38830768A00018 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole covered with vines | 130 Mary Dr, Inez, KY 41224, USA
2020 | 2020-06-23 | Pikeville |  |  | 38830768A30247 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Carlos Webb Road, Inez, Ky. | 2020-06-23
2020 | 2020-06-23 | Pikeville |  |  | 38830768A30247 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Carlos Webb Road, Inez, Ky. | 2020-06-23
2020 | 2020-06-23 | Pikeville |  |  | 38830768A30247 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Carlos Webb Road, Inez, Ky. | 2020-06-23
2020 | 2020-06-23 | Pikeville |  |  | 38830768A30248 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Carlos Webb Road, Inez, Ky. | 2020-06-23
2020 | 2020-06-23 | Pikeville |  |  | 38830768A30306 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive secondary pole. | 100 Carlos Webb Road, Inez, Ky.
2020 | 2020-06-23 | Pikeville |  |  | 38830768B00126 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Camp Branch, Coldwater Road, Inez, Ky. | 2020-06-23
2020 | 2020-06-23 | Pikeville |  |  | 38830768B00126 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Camp Branch, Coldwater Road, Inez, Ky. | 2020-06-23
2020 | 2020-06-23 | Pikeville |  |  | 38830768B00126 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Camp Branch, Coldwater Road, Inez, Ky. | 2020-06-23
2020 | 2020-06-23 | Pikeville |  |  | 38830768C00022 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Coldwater Road, Inez, Ky. | 2020-06-23
2020 | 2020-06-23 | Pikeville |  |  | 38830768C00087 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines | 43 Lower Carter Branch, Coldwater Road, Inez, Ky.
2020 | 2020-06-23 | Pikeville |  |  | 38830768C00194 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Camp Branch, Inez, Ky. | 2020-06-23
2020 | 2020-06-23 | Pikeville |  |  | 38830768C00238 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines . Pole is tagged 239 but field view shows 268. | 269 Lafferty Lane, Coldwater Road, Inez, Ky. 41224
2020 | 2020-06-23 | Pikeville |  |  | 38830768D00062 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Camp Branch, Inez, Ky. 41224 | 2020-06-23
2020 | 2020-06-23 | Pikeville |  |  | 38830792C00002 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is completely covered with vines | 1840 Coldwater Rd, Inez, KY 41224, USA
2020 | 2020-06-23 | Pikeville |  |  | 38830792C00016 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Moore Branch, Inez, Ky. | 2020-06-23
2020 | 2020-06-24 | Pikeville |  |  | 38830744B00284 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky. Hwy. 645, Inez, Ky. | 2020-06-24
2020 | 2020-06-24 | Pikeville |  |  | 38830744B00296 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Murray Road, Inez, Ky. | 2020-06-24
2020 | 2020-06-24 | Pikeville |  |  | 38830744B00296 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Murray Road, Inez, Ky. | 2020-06-24
2020 | 2020-06-24 | Pikeville |  |  | 38830744D00359 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky. Hwy. 645, Inez, Ky. | 2020-06-24
2020 | 2020-06-24 | Pikeville |  |  | 38830816B00020 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Parsons Branch, Inez, Ky. | 2020-06-24
2020 | 2020-06-24 | Pikeville |  |  | 38830816B00065 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Parsons Branch, Coldwater Road, Inez, Ky. | 2020-06-24
2020 | 2020-06-24 | Pikeville |  |  | 38830816B40101 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Parsons Branch, Inez, Ky. | 2020-06-24
2020 | 2020-06-24 | Pikeville |  |  | 38830816D00018 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Coldwater Road, Inez, Ky. | 2020-06-24
2020 | 2020-06-24 | Pikeville |  |  | 38830816D00018 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Coldwater Road, Inez, Ky. | 2020-06-24
2020 | 2020-06-24 | Pikeville |  |  | 38830816D00018 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Coldwater Road, Inez, Ky. | 2020-06-24
2020 | 2020-06-24 | Pikeville |  |  | 38830816D00018 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Coldwater Road, Inez, Ky. | 2020-06-24
2020 | 2020-06-25 | Pikeville |  |  | 38820745A00124 |  | 3411401-DEWEY / INEZ | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | KY-40 & Blacklog Rd, Inez, KY 41224, USA
2020 | 2020-06-25 | Pikeville |  |  | 38820769A00132 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Preece Hill, Inez, KY. | 2020-06-25
2020 | 2020-06-25 | Pikeville |  |  | 38820769D00171 |  | 3411401-DEWEY / INEZ | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. De-energized | 468 Thickety Fork, Little Rockcastle, Inez, KY.
2020 | 2020-06-25 | Pikeville |  |  | 38820770A00022 |  | 3411401-DEWEY / INEZ | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop laying on metal roof. | 6280 Buck Creek, Beauty, KY.
2020 | 2020-06-25 | Pikeville |  |  | 38830744D00010 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky. Rte 40, Inez, KY. | 2020-06-25
2020 | 2020-06-25 | Pikeville |  |  | 38830744D00010 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky. Rte 40, Inez, KY. | 2020-06-25
2020 | 2020-06-25 | Pikeville |  |  | 38830744D00010 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky. Rte 40, Inez, KY. | 2020-06-25
2020 | 2020-06-25 | Pikeville |  |  | 38830744D00354 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY-40, Inez, KY, USA | 2020-06-25
2020 | 2020-06-25 | Pikeville |  |  | 38830768C00108 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Joseph Lane, Inez, KY. | 2020-06-25
2020 | 2020-06-25 | Pikeville |  |  | 38830768C00108 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Joseph Lane, Inez, KY. | 2020-06-25
2020 | 2020-06-25 | Pikeville |  |  | 38830768C00176 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Aaron Street, Inez, KY. 41224 | 2020-06-25
2020 | 2020-06-25 | Pikeville |  |  | 38830768D00114 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Joseph Lane, Inez, KY. | 2020-06-25
2020 | 2020-06-29 | Pikeville |  |  | 38820770B00072 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary pole # 162. | 695 Little Peter Cave Branch, Lovely, KY.
2020 | 2020-06-29 | Pikeville |  |  | 38820770B00147 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Little PeterCave Branch, Lovely, KY. | 2020-06-29
2020 | 2020-06-29 | Pikeville |  |  | 38820770B00161 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Little Peter Cave Branch, Lovely, KY. | 2020-06-29
2020 | 2020-06-29 | Pikeville |  |  | 38820770B00161 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Little Peter Cave Branch, Lovely, KY. | 2020-06-29
2020 | 2020-06-29 | Pikeville |  |  | 38820771A40021 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Hewitt Street, Lovely, KY. | 2020-06-29
2020 | 2020-06-29 | Pikeville |  |  | 38820771A40022 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Second Street, Lovely, KY.
2020 | 2020-06-29 | Pikeville |  |  | 38820771A40223 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | N Wolf Creek, Lovely, KY. | 2020-06-29
2020 | 2020-06-29 | Pikeville | 77207913 | DKY0110611 | 38820771B10185 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole has been burned and temporarily repaired with crossarm. | Chapman Bottom, Lovely, KY. | 2020-12-14
2020 | 2020-06-29 | Pikeville |  |  | 38820771B10187 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Chapman Bottom, Lovely, KY. | 2020-06-29
2020 | 2020-06-30 | Pikeville |  |  | 38820794D00264 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Bertha Hale Lane, Pilgrim, Ky. | 2020-06-30
2020 | 2020-06-30 | Pikeville |  |  | 38820794D00275 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | N Wolf Creek, Pilgrim, Ky. | 2020-06-30
2020 | 2020-06-30 | Pikeville |  |  | 38820795B11116 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Holty Branch Road, Pilgrim, Ky. 41250 | 2020-06-30
2020 | 2020-06-30 | Pikeville |  |  | 38820818C00010 | TRUE | 3202202-LOVELY / WOLFCREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 40 White Oak Branch, Pilgrim, Ky.
2020 | 2020-06-30 | Pikeville |  |  | 38820818D00093 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines | 1265 White Oak Branch, Pilgrim, Ky.
2020 | 2020-06-30 | Pikeville | 77207856 | DKY0110607 | 38820818D00180 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole has been burned and temporarily repaired with crossarm. | Mary Ellen Lane, Emily Creek, Pilgrim, Ky. | 2020-12-11
2020 | 2020-06-30 | Pikeville |  |  | 38820819A00015 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Emily Creek, Pilgrim, Ky. | 2020-06-30
2020 | 2020-06-30 | Pikeville |  |  | 38820819C00037 | TRUE | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 2572 Emily Creek, Pilgrim, Ky.
2020 | 2020-06-30 | Pikeville | 77207609 | DKY0110606 | 38820842C00112 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole has been burned and temporarily repaired with crossarm. | 1329 White Oak Branch, Pilgrim, Ky. | 2020-12-09
2020 | 2020-07-01 | Pikeville |  |  | 38820794D00250 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | N Wolf Creek, Pilgrim, Ky. | 2020-07-01
2020 | 2020-07-01 | Pikeville |  |  | 38820818A00025 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker and insulator. Installed marker. | 642 N Wolf Creek, Pilgrim, Ky.
2020 | 2020-07-01 | Pikeville |  |  | 38820818A00028 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | N Wolf Creek, Pilgrim, Ky. | 2020-07-01
2020 | 2020-07-01 | Pikeville |  |  | 38820818A00049 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | N Wolf Creek Rd, Kentucky, USA | 2020-07-01
2020 | 2020-07-01 | Pikeville |  |  | 38820818A00124 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Gauze Hollow, N Wolf Creek, Pilgrim, Ky.
2020 | 2020-07-01 | Pikeville |  |  | 38820818A00134 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Gauze Hollow, Pilgrim, Ky. | 2020-07-01
2020 | 2020-07-01 | Pikeville |  |  | 38820818A00134 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Gauze Hollow, Pilgrim, Ky. | 2020-07-01
2020 | 2020-07-01 | Pikeville |  |  | 38820842A00038 | TRUE | 3202202-LOVELY / WOLFCREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken. Angle pole. Probably needs new anchor installed. | Big Peter Cave Road, Pigeonroost Road, Pilgrim, Ky.
2020 | 2020-07-01 | Pikeville |  |  | 38820890A00001 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down . #2 aa wire. | 4629 Pigeonroost Road, Pilgrim, Ky.
2020 | 2020-07-01 | Pikeville |  |  | 38820890A00003 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral conductor sagging very low beneath communications cables. Needs slack taken out.@ Wolf Creek Church of the Brethren. | Pigeonroost Road, N Wolf Creek, Pilgrim, Ky.
2020 | 2020-07-01 | Pikeville | 84625259 | DKY0120025 | 38820890C00059 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/missing | 217 Caney Fork, Pigeonroost Road, Pilgrim, Ky. | 2023-03-31
2020 | 2020-07-01 | Pikeville |  |  | 38820890C00069 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Caney Fork, Pigeonroost Road, Pilgrim, Ky.
2020 | 2020-07-01 | Pikeville |  |  | 38820914C00005 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer . Last pole in Pigeonroost | Pigeonroost Road, N Wolf Creek, Pilgrim, Ky.
2020 | 2020-07-02 | Pikeville |  |  | 38820793D00027 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ralph Moore Lane, Pigeonroost, Ky. | 2020-07-02
2020 | 2020-07-02 | Pikeville |  |  | 38820794B00252 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ked Fletcher Hollow, Pigeonroost, Ky. | 2020-07-02
2020 | 2020-07-02 | Pikeville | 77207762 | DKY0110564 | 38820817D00073 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line | 87 Jeff Jude Road, Pigeonroost, Ky. | 2021-01-05
2020 | 2020-07-02 | Pikeville |  |  | 38820818A00080 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | Rocky Branch, Pigeonroost, Ky. | 2020-07-02
2020 | 2020-07-02 | Pikeville |  |  | 38820818A20118 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | N Wolf Creek, Pilgrim, Ky. | 2020-07-02
2020 | 2020-07-02 | Pikeville |  |  | 38820818B00062 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | S Wolf Creek, Pigeonroost, Ky. | 2020-07-02
2020 | 2020-07-02 | Pikeville |  |  | 38820841A00134 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | S Wolf Creek, Pigeonroost, Ky. | 2020-07-02
2020 | 2020-07-02 | Pikeville |  |  | 38820841B00055 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | S Wolf Creek, Pigeonroost,Ky. | 2020-07-02
2020 | 2020-07-02 | Pikeville |  |  | 38820841B00056 | TRUE | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 3850 S Wolf Creek, Pigeonroost, Ky.
2020 | 2020-07-06 | Pikeville |  |  | 38820841A00138 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 3959 Wolf Creek, Pilgrim, Ky.
2020 | 2020-07-06 | Pikeville |  |  | 38830960000014 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Big Branch, Wolf Creek , Varney, Ky.
2020 | 2020-07-07 | Pikeville |  |  | 38820818A00028 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Wolf Creek, Pigeonroost, Ky. | 2020-07-07
2020 | 2020-07-07 | Pikeville |  |  | 38830912D00027 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Meathouse Fork, Pilgrim, Ky. | 2020-07-07
2020 | 2020-07-07 | Pikeville |  |  | 38830936C00546 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Guy wire broken hanging down pole. Needs to be removed or new anchor installed. | 8896 Meathouse Fork, Pilgrim, Ky.
2020 | 2020-07-07 | Pikeville |  |  | 38830936D00022 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole. | 10072 Meathouse Fork, Pilgrim, Ky.
2020 | 2020-07-07 | Pikeville |  |  | 38830936D00534 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 3533 Big Branch, Endicott, Ky. | 2020-07-07
2020 | 2020-07-08 | Pikeville |  |  | 38830858A00224 |  | 3409302-KENWOOD / AUXIER | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Industrial Park, Auxier, KY. 41602 | 2020-07-08
2020 | 2020-07-08 | Pikeville |  |  | 38830858B00153 |  | 3409302-KENWOOD / AUXIER | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm burnt in two. | Oak lawn Estates, Auxier, KY.
2020 | 2020-07-08 | Pikeville |  |  | 38830858B00163 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Panther Blvd. Auxier, KY. 41222 | 2020-07-08
2020 | 2020-07-08 | Pikeville |  |  | 38830858B00299 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Industrial Park, Auxier, KY. | 2020-07-08
2020 | 2020-07-08 | Pikeville |  |  | 38830858B00368 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Panther Blvd. Auxier, KY. 41222 | 2020-07-08
2020 | 2020-07-08 | Pikeville |  |  | 38830858B00395 |  | 3409302-KENWOOD / AUXIER | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | 795 Industrial Park, Auxier, KY.
2020 | 2020-07-09 | Pikeville |  |  | 38830882A00496 |  | 3409302-KENWOOD / AUXIER | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with trees | Sky Harbor Lane, Auxier, KY. | 2020-11-16
2020 | 2020-07-09 | Pikeville |  |  | 38830882D00104 |  | 3409302-KENWOOD / AUXIER | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines and and two spans back to pole 106 is covered with trees. Needs cut. | 168 Happy Hollow, Auxier, KY. | 2020-11-16
2020 | 2020-07-09 | Pikeville | 77837059 | DKY0111411 | 38830882D00148 |  | 3409302-KENWOOD / AUXIER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is hollow. Set in 1946 | 31 Depot Hollow, Auxier, KY. | 2020-12-17
2020 | 2020-07-13 | Pikeville |  |  | 38830882D00033 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Fords Gap Rd, Auxier, KY, USA | 2020-07-13
2020 | 2020-07-13 | Pikeville |  |  | 38830882D00222 |  | 3409302-KENWOOD / AUXIER | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines | Hopson St, Auxier, KY 41602, USA
2020 | 2020-07-13 | Pikeville |  |  | 38830882D10911 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Railroad St, Auxier, KY 41602, USA | 2020-07-13
2020 | 2020-07-13 | Pikeville |  |  | 38830882D10972 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | N River St, Auxier, KY 41602, USA | 2020-07-13
2020 | 2020-07-14 | Pikeville |  |  | 38830905000041 |  | 3409302-KENWOOD / AUXIER | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines | 1275 Little Paint Creek, Prestonsburg, Ky. 41216 | 2020-11-16
2020 | 2020-07-14 | Pikeville |  |  | 38830906000042 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | George Branch, Auxier, KY 41602, USA | 2020-07-14
2020 | 2020-07-14 | Pikeville |  |  | 38830906000043 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | George Branch, Auxier, KY 41602, USA | 2020-07-14
2020 | 2020-07-15 | Pikeville |  |  | 38830881000143 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Bear Hollow, East Point, Ky. | 2020-07-15
2020 | 2020-07-15 | Pikeville |  |  | 38830881000170 |  | 3409302-KENWOOD / AUXIER | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines . @ near mouth Bear Hollow | 4597 US-23, East Point, KY 41216, USA
2020 | 2020-07-15 | Pikeville |  |  | 38830906000060 |  | 3409302-KENWOOD / AUXIER | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | U.S. 23 N, East Point, Ky.
2020 | 2020-07-16 | Pikeville |  |  | 38830833C00028 |  | 3409303-KENWOOD / HAGERHILL | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | 1401 Ky. 1428, Hager Hill, Ky.
2020 | 2020-07-16 | Pikeville |  |  | 38830833C00115 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky. 1428, Hager Hill, Ky. | 2020-07-16
2020 | 2020-07-16 | Pikeville |  |  | 38830833C00116 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky. 1428, Hager Hill, Ky. | 2020-07-16
2020 | 2020-07-16 | Pikeville |  |  | 38830833C00589 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Cherry Hill Lane, Hager Hill, Ky. 41222 | 2020-07-16
2020 | 2020-07-16 | Pikeville | 77837031 | DKY0111343 | 38830834A00384 |  | 3409303-KENWOOD / HAGERHILL | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole has a large hole in it near the braces. Conductors crosses highway. Probably need line truck with longest reach. Pole was installed in 1960. | Ky. 1428, Hager Hill, Ky. 41222 | 2021-02-05
2020 | 2020-07-16 | Pikeville |  |  | 38830834A00472 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 154 Winding Way Dr, Hagerhill, KY 41222, USA | 2020-07-16
2020 | 2020-07-16 | Pikeville |  |  | 38830834B00554 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Winding Way Drive, Hager Hill, Ky. 41222 | 2020-07-16
2020 | 2020-07-20 | Pikeville |  |  | 38830833B00065 |  | 3409303-KENWOOD / HAGERHILL | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators melting/deteoriated | 1110 Middle Fork, Collista, Ky.
2020 | 2020-07-20 | Pikeville |  |  | 38830833D00423 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 111 Paradise Acres, Hagerhill, KY 41222, USA | 2020-07-20
2020 | 2020-07-21 | Pikeville |  |  | 38830857000062 |  | 3409303-KENWOOD / HAGERHILL | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines | 1750 Little Lick Fork Rd, Hagerhill, KY 41222, USA
2020 | 2020-07-21 | Pikeville |  |  | 38830857000218 |  | 3409303-KENWOOD / HAGERHILL | Forestry | OH |  |  | circuit is on schedule for reclear 2021 | KPC | NO | Pole is covered by trees | 750 Little lick Fork, Ky. Rte. 1750, Paintsville, Ky. | 2020-11-16
2020 | 2020-07-27 | Pikeville |  |  | 38830856000002 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Middle Fork, Hager Hill, Ky. | 2020-07-27
2020 | 2020-07-28 | Pikeville | 86689244 |  | 37820193A00211 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer | 4320 Poorbottom Road, Regina, Ky.
2020 | 2020-07-28 | Pikeville | 86689244 |  | 37820193A00410 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer .@ Anthony Coleman Road on poorbottom. | 4734 Poorbottom Road, Regina, Ky.
2020 | 2020-07-28 | Pikeville |  |  | 37820193B00194 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on switch pole | Poorbottom Road, Regina, Ky. | 2020-07-28
2020 | 2020-07-29 | Pikeville | 78705203 |  | 37830216000033 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Service drop hanging down pole. Needs removed. | 180 Hopkins Fork, Ky. Hwy 611, Pikeville, Ky. | 2021-01-28
2020 | 2020-07-29 | Pikeville |  |  | 37830216C20512 |  | 3401702-HENRYCLAY / REGINA | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS- Nothing laying over the primary here. | KPC | NO | Tree laying directly over the primary. Could cause outage. | 1220 Hopkins Fork, Ky. Hwy 611, Pikeville, Ky. | 2020-12-16
2020 | 2020-07-31 | Pikeville | 78706160 |  | 37830215C00348 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive Service drop rolled up on pole. | 626 Andy Newsome Branch, Dorton, Ky. | 2021-02-04
2020 | 2020-07-31 | Pikeville |  |  | 37830263C00167 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown | 297 Dorton Creek, Dorton, Ky.
2020 | 2020-07-31 | Pikeville |  |  | 37830263C10436 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 68 Flatwoods, Dorton, Ky. | 2020-07-31
2020 | 2020-07-31 | Pikeville |  |  | 37830263D00107 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown | 1293 Dorton Creek, Dorton, Ky.
2020 | 2020-08-04 | Pikeville |  |  | 37820169000110 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Pole is covered in vines | 1368 Bad Fork Rockhouse, Regina, Ky.
2020 | 2020-08-04 | Pikeville | 86689244 |  | 37820170B20618 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 445 Bad Fork Rockhouse, Regina, Ky.
2020 | 2020-08-05 | Pikeville |  |  | 37820121000041 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Greasy Creek, Shelbiana, Ky. | 2020-08-05
2020 | 2020-08-05 | Pikeville |  |  | 37820121000045 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Greasy Creek, Shelbiana, Ky. | 2020-08-05
2020 | 2020-08-05 | Pikeville |  |  | 37820145000062 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Greasy Creek, Shelbiana, Ky. | 2020-08-05
2020 | 2020-08-05 | Pikeville |  |  | 37820145000067 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Greasy Creek, Shelbiana, Ky. | 2020-08-05
2020 | 2020-08-05 | Pikeville |  |  | 37820145000272 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Yates Hollow, Greasy Creek, Shelbiana, Ky. | 2020-08-05
2020 | 2020-08-05 | Pikeville |  |  | 37820169000263 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Jones Rd & Rockhouse Creek Rd, Kentucky 41522, USA | 2020-08-05
2020 | 2020-08-06 | Pikeville |  |  | 37820170000125 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines | 125 Wild Rose Drive, Regina, Ky.
2020 | 2020-08-07 | Pikeville |  |  | 37820194A00205 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Marrowbone Creek Road, Regina, Ky. | 2020-08-07
2020 | 2020-08-07 | Pikeville |  |  | 37820194C00057 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 3752 Marrowbone Creek Road, Regina, Ky. | 2020-08-07
2020 | 2020-08-07 | Pikeville |  |  | 37820194C00086 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Pole top and transformer covered with vines | 224 Lfk Dry Fork, Regina, Ky.
2020 | 2020-08-07 | Pikeville |  |  | 37820194C00092 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 533 Rfk Dry Fork, Regina, Ky.
2020 | 2020-08-07 | Pikeville |  |  | 37820194C00367 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Service drop hanging on pole. | 224 Lfk Dry Fork, Regina, Ky.
2020 | 2020-08-10 | Pikeville |  |  | 37820122000035 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines. Could cause outage. | 567 Winwright Road, Millard, Ky.
2020 | 2020-08-10 | Pikeville |  |  | 37820122000043 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines . Conductor cross railroad tracks. Could cause outage. | 232 Winston Branch, Millard, Ky.
2020 | 2020-08-10 | Pikeville |  |  | 37820146000038 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Millard Hwy, Regina, Ky. | 2020-08-10
2020 | 2020-08-10 | Pikeville |  |  | 37820146000038 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Millard Hwy, Regina, Ky. | 2020-08-10
2020 | 2020-08-10 | Pikeville |  |  | 37820146000109 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Marrowbone Creek Road, Wolfpit, Ky. | 2020-08-10
2020 | 2020-08-10 | Pikeville |  |  | 37820146000225 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Marrowbone Creek Road, Wolfpit, Ky. | 2020-08-10
2020 | 2020-08-10 | Pikeville |  |  | 37820146C30262 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Millard Hwy, Regina, Ky. | 2020-08-10
2020 | 2020-08-12 | Pikeville |  |  | 37820098C00312 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Rocky Road, Millard, Ky. | 2020-08-12
2020 | 2020-08-12 | Pikeville |  |  | 37820098C00312 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Rocky Road, Millard, Ky. | 2020-08-12
2020 | 2020-08-12 | Pikeville |  |  | 37820098C40763 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Rocky Road, Millard, Ky. | 2020-08-12
2020 | 2020-08-12 | Pikeville | 86690954 |  | 37820122000277 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive 3 phase line beginning @ 122-277 thru 122-281.@ Hollow behind old prep plant at Millard. | Ripely Branch, Millard, Ky.
2020 | 2020-08-13 | Pikeville |  |  | 37820075000218 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Fish trap Road, Millard, Ky. | 2020-08-13
2020 | 2020-08-13 | Pikeville |  |  | 37820075000223 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Fish trap Road, Millard, Ky. | 2020-08-13
2020 | 2020-08-13 | Pikeville |  |  | 37820075000223 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Fish trap Road, Millard, Ky. | 2020-08-13
2020 | 2020-08-13 | Pikeville |  |  | 37820075000235 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Fish trap Road, Millard, Ky. | 2020-08-13
2020 | 2020-08-13 | Pikeville |  |  | 37820075000239 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Fish trap Road, Millard, Ky. | 2020-08-13
2020 | 2020-08-13 | Pikeville |  |  | 37820098C00137 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Fishtrap Road, Millard, Ky. | 2020-08-13
2020 | 2020-08-17 | Pikeville |  |  | 37820217A00158 |  | 3401703-HENRYCLAY / ASHCAMP | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS- Circuit is planned for cycle maintenance in 2021. Tree will be trimmed or removed at that time. | KPC | NO | Poplar tree growing up in line. Could cause outage. | Little Big Branch, Lookout, Ky. | 2020-12-16
2020 | 2020-08-17 | Pikeville |  |  | 37820217B00112 |  | 3401703-HENRYCLAY / ASHCAMP | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Bowling Fork, Lookout, Ky. | 2020-08-17
2020 | 2020-08-17 | Pikeville |  |  | 37820217C00012 |  | 3401703-HENRYCLAY / ASHCAMP | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Bowling Fork, Lookout, Ky. | 2020-08-17
2020 | 2020-08-17 | Pikeville |  |  | 37820217C00360 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on step down transformer pole | Little Big Branch, Lookout, Ky. | 2020-08-17
2020 | 2020-08-17 | Pikeville |  |  | 37820217C00360 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on step down transformer pole | Little Big Branch, Lookout, Ky. | 2020-08-17
2020 | 2020-08-17 | Pikeville |  |  | 37820217D00079 |  | 3401703-HENRYCLAY / ASHCAMP | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Democrat Hollow, Hellier, Ky. | 2020-08-17
2020 | 2020-08-17 | Pikeville |  |  | 37830240000130 |  | 3401703-HENRYCLAY / ASHCAMP | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Bowling Fork, Lookout, Ky. | 2020-08-17
2020 | 2020-08-18 | Pikeville |  |  | 37820218000053 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | 510 Brushy Fork, Hellier, Ky.
2020 | 2020-08-18 | Pikeville |  |  | 37820241C00141 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 360 Edge water Road, Helier, Ky.
2020 | 2020-08-18 | Pikeville |  |  | 37820242000261 |  | 3401703-HENRYCLAY / ASHCAMP | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Ashcamp Rd, Kentucky, USA | 2020-08-18
2020 | 2020-08-18 | Pikeville |  |  | 37820242000301 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator melting/deteoriated. On Step down pole. | Brushy Branch, Hellier, Ky.
2020 | 2020-08-18 | Pikeville | Outage # 4342621 |  | 37820242000338 |  | 3401703-HENRYCLAY / ASHCAMP | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Hot service drop hanging down pole. Called DDC to make ticket for servicer and waited till servicer arrived to remove service. | Happy Hollow, Ashcamp Road, Elkhorn City, Ky. | 2020-08-18
2020 | 2020-08-19 | Pikeville |  |  | 37820242000053 |  | 3401703-HENRYCLAY / ASHCAMP | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS- Will have a crew get this when in the area or on routine cycle maintenance in 2021. | Foreign | NO | Tree on secondary cable. | 1107 Jackson Branch, Elkhorn City, Ky. | 2020-12-16
2020 | 2020-08-19 | Pikeville |  |  | 37820242000218 |  | 3401703-HENRYCLAY / ASHCAMP | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Jackson Branch, Elkhorn City, Ky. | 2020-08-19
2020 | 2020-08-19 | Pikeville |  |  | 37820243B00071 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Pole is covered in vines | 130 Little Branch, Elkhorn City, Ky.
2020 | 2020-08-19 | Pikeville |  |  | 37820243B00274 |  | 3401703-HENRYCLAY / ASHCAMP | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS- Tree has already been taken care of. | Foreign | NO | Tree in a slide. Laying over primary. | 215 Little Branch, Elkhorn City, Ky. | 2020-12-16
2020 | 2020-08-19 | Pikeville |  |  | 37820243B00275 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Guy wire broken. Pole leaning.Hand dig anchor or possibly rockeye. | 215 Little Branch, Elkhorn City, Ky.
2020 | 2020-08-19 | Pikeville |  |  | 37820267000006 |  | 3401703-HENRYCLAY / ASHCAMP | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Atkins Belcher Road, Elkhorn City, Ky. | 2020-08-19
2020 | 2020-08-19 | Pikeville | 86688322 | DKY0123329 | 37820267000008 | TRUE | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | End of crossarm is split causing pin and insulator to lay over. Pole has single phase recloser on it. | Spa Court, Elkhorn Creek, Elkhorn City, Ky. | 2023-12-18
2020 | 2020-08-20 | Pikeville | 86032043 | DKY0122140 | 37820242000099 | TRUE | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator broken. | 10624 Ashcamp Road, Ashcamp, Ky. | 2023-10-17
2020 | 2020-08-20 | Pikeville |  |  | 37820266000152 |  | 3401703-HENRYCLAY / ASHCAMP | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | J C Ratliff Road, Ashcamp, Ky. | 2020-08-20
2020 | 2020-08-20 | Pikeville | 86515609 |  | 37820266000162 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown | 880 Mill Branch, Ashcamp, Ky.
2020 | 2020-08-24 | Pikeville | 86515583 |  | 37820265A00132 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators melting/deteoriated | 612 Rfk Sycamore, Elkhorn City, Ky.
2020 | 2020-08-24 | Pikeville | 86515583 |  | 37820265B00029 | TRUE | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/melting | 448 Sycamore Creek, Elkhorn City, Ky.
2020 | 2020-08-24 | Pikeville |  |  | 37820265B00033 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilators deteoriated/melting. Might not be reachable with truck unless you go in the field next to West Care. | Bartleytown Road, Elkhorn City, Ky. | 2023-07-13
2020 | 2020-08-24 | Pikeville | 86529256 |  | 37820265D00185 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Crossarm deteoriated/rotten. Could probably back in customer yard if dry. | Bartleytown Road, Elkhorn City, Ky. | 2023-12-18
2020 | 2020-08-25 | Pikeville | 86515609 |  | 37820241B00162 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown. @ Hellier 2 hill behind church. | 1320 Allegheny Rd, Hellier, KY 41534, USA
2020 | 2020-08-25 | Pikeville | 77837168 | DKY0111428 | 37820241C00113 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole is burnt almost all the way up. | 300 Allegheny Rd, Hellier, KY 41534, USA | 2021-10-08
2020 | 2020-08-25 | Pikeville | 86529474 |  | 37820266000026 | TRUE | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | lightning arresters/insulators: damaged |  | Foreign | YES | Pole is rotten. Epoxilators deteoriated/melting. @ across from Ashcamp Church of Christ. Just above Ashcamp. | 7015 Elkhorn Creek, Ashcamp, Ky.
2020 | 2020-08-25 | Pikeville |  |  | 37820266000205 |  | 3401703-HENRYCLAY / ASHCAMP | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS- Vines are dead on this pole. | Foreign | NO | Pole is smothered with vines. | 7587 Elkhorn Creek, Ashcamp, Ky. | 2020-12-16
2020 | 2020-08-25 | Pikeville |  |  | 37820266000206 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines | 7587 Elkhorn Creek, Ashcamp, KY 41512, USA
2020 | 2020-08-26 | Pikeville |  |  | 38820771D00194 |  | 3202203-LOVELY / MT.STERLINGBR. | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Transformer is covered with vines.@Dixie Lane. | 3893 Ky 292, Lovely, Ky.
2020 | 2020-08-26 | Pikeville |  |  | 38820771D00432 |  | 3202203-LOVELY / MT.STERLINGBR. | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dixie Lane, Lovely, Ky. | 2020-08-26
2020 | 2020-08-26 | Pikeville |  |  | 38820820A00174 |  | 3202203-LOVELY / MT.STERLINGBR. | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole. | 1342 Long Branch, Lovely, Ky. | 2020-08-26
2020 | 2020-08-26 | Pikeville |  |  | 38820820A00226 |  | 3202203-LOVELY / MT.STERLINGBR. | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lone Branch, Lovely, Ky. | 2020-08-26
2020 | 2020-08-26 | Pikeville |  |  | 38820820B00193 |  | 3202203-LOVELY / MT.STERLINGBR. | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Long Branch, Lovely, Ky. | 2020-08-26
2020 | 2020-08-26 | Pikeville |  |  | 38820820B21781 | TRUE | 3202203-LOVELY / MT.STERLINGBR. | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole. | 210 Russell Workman Rd. Long Branch, Lovely, Ky.
2020 | 2020-08-27 | Pikeville |  |  | 38820820C20244 |  | 3202203-LOVELY / MT.STERLINGBR. | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 7294 KY-292, Belfry, KY 41514, USA
2020 | 2020-08-27 | Pikeville |  |  | 38820820C40080 | TRUE | 3202203-LOVELY / MT.STERLINGBR. | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 7815 KY-292, Belfry, KY 41514, USA
2020 | 2020-08-28 | Pikeville |  |  | 38820820C20131 |  | 3202203-LOVELY / MT.STERLINGBR. | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Inactive conductors hanging down pole . Use to be a river crossing. Customer ask to have guy removed in his yard and conductors taken out. | 7421 Riverfront Road, Lovely, KY 41231, USA
2020 | 2020-08-31 | Pikeville |  |  | 38820747B20442 |  | 3202201-LOVELY / LOVELY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive Service drop hanging down pole . Needs removed. | Locust Street, Lovely, Ky. | 2020-08-31
2020 | 2020-08-31 | Pikeville |  |  | 38820771A30416 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Chestnut Drive, Lovely, Ky. | 2020-08-31
2020 | 2020-08-31 | Pikeville |  |  | 38820771A30422 |  | 3202201-LOVELY / LOVELY | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections , lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown on transformer bank.@ behind Subway | Ferguson St, Lovely, KY 41231, USA
2020 | 2020-08-31 | Pikeville |  |  | 38820771A30423 |  | 3202201-LOVELY / LOVELY | Line Work | OH |  |  | other: customer owned attachment | KPC | NO | Customer has attached service cable to our pole. Should be removed. @ behind Zip zone/ Subway shop. | Ferguson St, Lovely, KY 41231, USA
2020 | 2020-08-31 | Pikeville |  |  | 38820771A40423 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lees Way, Lovely, KY, USA | 2020-08-31
2020 | 2020-09-01 | Pikeville |  |  | 38820745C00084 |  | 3202201-LOVELY / LOVELY | Line Work | OH | service: unused or abandoned, blanked meter base | transformers: leaking, damaged |  | KPC | NO | Transformer bushing is damaged/ broken. Service drop low clearance, should be removed. | 1256 Rfk Big Elk Creek, Beauty, Ky.
2020 | 2020-09-01 | Pikeville |  |  | 38820746A00134 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Buck Creek, Kentucky, USA | 2020-09-01
2020 | 2020-09-01 | Pikeville |  |  | 38820746A00302 | TRUE | 3202201-LOVELY / LOVELY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 1013 Rfk Big Elk Creek, Beauty, Ky.
2020 | 2020-09-01 | Pikeville |  |  | 38820746B00316 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Big Elk Rd, Beauty, KY, USA | 2020-09-01
2020 | 2020-09-02 | Pikeville |  |  | 38820746D40306 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Collins Creek, Warfield, Ky. | 2020-09-02
2020 | 2020-09-02 | Pikeville |  |  | 38820747A20496 |  | 3202201-LOVELY / LOVELY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Floyd Street, Warfield, Ky.
2020 | 2020-09-02 | Pikeville |  |  | 38820747B10204 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Collins Creek Road, Warfield, Ky. | 2020-09-02
2020 | 2020-09-02 | Pikeville |  |  | 38820770C00048 |  | 3202201-LOVELY / LOVELY | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines | 1024 Collins Creek, Warfield, Ky.
2020 | 2020-09-02 | Pikeville |  |  | 38820770C00156 |  | 3202201-LOVELY / LOVELY | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines | Howell Road, Collins Creek, Warfield, Ky.
2020 | 2020-09-03 | Pikeville |  |  | 38820698D00009 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Hode Road, Warfield, Ky. | 2020-09-03
2020 | 2020-09-03 | Pikeville |  |  | 38820698D00188 | TRUE | 3202201-LOVELY / LOVELY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Low Gap Hollow, Little Elk Creek, Warfield, Ky.
2020 | 2020-09-03 | Pikeville |  |  | 38820723A00256 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Elementary Loop, Hode Road, Warfield, Ky. | 2020-09-03
2020 | 2020-09-03 | Pikeville |  |  | 38820746C00051 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Hode Road, Warfield, Ky. | 2020-09-03
2020 | 2020-09-03 | Pikeville |  |  | 38820746D30386 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Firehouse Ln, Warfield, KY 41267, USA | 2020-09-03
2020 | 2020-09-04 | Pikeville |  |  | 38820673C00240 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Hode Road, Warfield, Ky. | 2020-09-04
2020 | 2020-09-04 | Pikeville |  |  | 38820673C00249 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Hode Road, Warfield, Ky. | 2020-09-04
2020 | 2020-09-04 | Pikeville |  |  | 38820673D00211 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Jarrell Branch, Warfield, Ky. | 2020-09-04
2020 | 2020-09-04 | Pikeville |  |  | 38820674B00280 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Williams Branch, Warfield, Ky. | 2020-09-04
2020 | 2020-09-04 | Pikeville |  |  | 38820674B00285 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Williams Branch, Hode Road, Warfield, Ky. | 2020-09-04
2020 | 2020-09-04 | Pikeville |  |  | 38820674B00340 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker (2) | Hode Road, Warfield, Ky. | 2020-09-04
2020 | 2020-09-04 | Pikeville |  |  | 38820674B00355 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Wendy Street, Hode Road, Warfield, Ky. | 2020-09-04
2020 | 2020-09-04 | Pikeville |  |  | 38820674B00355 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Wendy Street, Hode Road, Warfield, Ky. | 2020-09-04
2020 | 2020-09-04 | Pikeville |  |  | 38820698C00142 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Sunset Spur, Ky. 292, Warfield, Ky. | 2020-09-04
2020 | 2020-09-08 | Pikeville |  |  | 38820697D00075 |  | 3202201-LOVELY / LOVELY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 109 Mann Drive, Big Elk Road, Beauty, Ky.
2020 | 2020-09-08 | Pikeville |  |  | 38820697D00105 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lower Poplar Fork, Big Elk Road, Beauty, Ky.
2020 | 2020-09-08 | Pikeville | 85842590 | DKY0121876 | 38820697D00106 |  | 3202201-LOVELY / LOVELY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 3699 Lower Poplar Fork, Beauty, Ky.
2020 | 2020-09-09 | Pikeville |  |  | 38820673C00077 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Turkey Creek, Inez, Ky. | 2020-09-09
2020 | 2020-09-09 | Pikeville |  |  | 38820673C00208 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Turkey Creek, Inez, Ky. | 2020-09-09
2020 | 2020-09-09 | Pikeville | 85854684 | DKY0121886 | 38820673D00218 | TRUE | 3202201-LOVELY / LOVELY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer | 488 Turkey Creek, Inez, Ky.
2020 | 2020-09-10 | Pikeville |  |  | 38820674B00103 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky 292, Warfield, Ky. | 2020-09-10
2020 | 2020-09-10 | Pikeville |  |  | 38820698C00168 | TRUE | 3202201-LOVELY / LOVELY | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire hanging down pole. Needs reattached. Probably need new anchor installed. | 4453 Ky. 292, Warfield, Ky.
2020 | 2020-09-10 | Pikeville |  |  | 38820698D00005 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 3561 Ky. 292, Warfield, Ky. | 2020-09-10
2020 | 2020-09-10 | Pikeville |  |  | 38820722C00095 |  | 3202201-LOVELY / LOVELY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole. | Stone coal road, Ky. 292, Warfield, Ky.
2020 | 2020-09-10 | Pikeville |  |  | 38820722C00109 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Hode Road Ky. 292, Warfield, Ky. | 2020-09-10
2020 | 2020-09-10 | Pikeville |  |  | 38820722C00120 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | My. 292, Stonecoal Road, Warfield, Ky. | 2020-09-10
2020 | 2020-09-10 | Pikeville |  |  | 38820746C00284 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Firehouse Ln, Warfield, KY 41267, USA | 2020-09-10
2020 | 2020-09-11 | Pikeville |  |  | 38820673D00048 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Turkey Creek, Inez, Ky. | 2020-09-11
2020 | 2020-09-11 | Pikeville |  |  | 38820673D00227 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Hode Road, Warfield, Ky. | 2020-09-11
2020 | 2020-09-11 | Pikeville |  |  | 38820674B00316 |  | 3202201-LOVELY / LOVELY | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | White Road, Warfield, Ky. | 2020-09-11
2020 | 2020-09-14 | Pikeville |  |  | 38820673D00086 |  | 3202201-LOVELY / LOVELY | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on switch pole | Turkey Creek, Inez, Ky.
2020 | 2020-09-14 | Pikeville |  |  | 38820697D00068 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lower Poplar Fork, Big Elk Road, Beauty, Ky. | 2020-09-14
2020 | 2020-09-14 | Pikeville |  |  | 38820721D00017 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lower Poplar Fork, Big Elk Road, Beauty, Ky. | 2020-09-14
2020 | 2020-09-15 | Pikeville |  |  | 38820697C00077 |  | 3202201-LOVELY / LOVELY | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on transformer pole | Music Lane, Big Elk Road, Beauty, Ky.
2020 | 2020-09-15 | Pikeville |  |  | 38820722B00112 |  | 3202201-LOVELY / LOVELY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Needs removed. | 1599 Big Elk Road, Beauty, Ky.
2020 | 2020-09-15 | Pikeville |  |  | 38820746A00144 |  | 3202201-LOVELY / LOVELY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Needs removed. | 19 Gospel Light Road, Beauty, Ky.
2020 | 2020-09-16 | Pikeville |  |  | 38820673C00231 |  | 3202201-LOVELY / LOVELY | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | Ky 292, Turkey Creek, Inez, Ky.
2020 | 2020-09-17 | Pikeville |  |  | 38820746B00099 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Beauty, KY, USA | 2020-09-17
2020 | 2020-09-17 | Pikeville |  |  | 38820746B00215 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky. Rte. 40, Beauty, Ky. | 2020-09-17
2020 | 2020-09-17 | Pikeville |  |  | 38820770A00030 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky. Rte. 40, Beauty, Ky. | 2020-09-17
2020 | 2020-09-17 | Pikeville |  |  | 38820770A30277 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Everett Lane, Beauty, Ky. | 2020-09-17

## Ckt Defects Reported 2021 PKV
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2021 | 2021-01-05 | Pikeville |  |  | 38830930B00051 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Screw Anchor
2021 | 2021-01-05 | Pikeville | 78447677 | DKY0112119 | 38830930B00260 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2021-01-28
2021 | 2021-01-05 | Pikeville | 78782000 | DKY0112727 | 38830930B00285 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Screw Anchor |  | 2022-02-01
2021 | 2021-01-05 | Pikeville | 78782000 | DKY0112727 | 38830930E40269 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO |  |  | 2022-02-01
2021 | 2021-01-05 | Pikeville |  |  | 38830954A10386 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  |  |  | KPC | NO
2021 | 2021-01-05 | Pikeville |  |  | 38830954C20682 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO
2021 | 2021-01-13 | Pikeville | 80775217 | DKY0115343 | 37820051000063 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES |  |  | 2022-09-07
2021 | 2021-01-13 | Pikeville | 82379701 | DKY0117039 | 37820076000114 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  |  | KPC | YES |  |  | 2022-12-27
2021 | 2021-01-13 | Pikeville | 78637473 | DKY0112529 | 37820027000037 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  |  | KPC | YES |  |  | 2021-10-21
2021 | 2021-01-13 | Pikeville |  |  | 37820051000021 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  |  | KPC | NO | Install 30-6 clearance pole to correct low service drop |  | 2022-05-12
2021 | 2021-01-13 | Pikeville | 78637477 | DKY0112540 | 37820051000023 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2021-10-21
2021 | 2021-01-13 | Pikeville | 82379509 | DKY0117090 | 37820051000105 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES |  |  | 2023-01-19
2021 | 2021-01-13 | Pikeville | 82296847 | DKY0116967 | 37820052000113 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  |  | KPC | NO | replace anchor and straighten pole |  | 2022-06-24
2021 | 2021-01-13 | Pikeville | 78637460 | DKY0112543 | 37820052000138 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  |  | KPC | YES |  |  | 2021-10-27
2021 | 2021-01-13 | Pikeville | 83965729 | DKY0120222 | 37820052000245 | TRUE | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  |  | KPC | NO | Install anchor and guy wire to straighten pole |  | 2023-05-26
2021 | 2021-01-13 | Pikeville | 82473122 | DKY0117149 | 37820053000026 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  |  | Foreign | YES
2021 | 2021-01-13 | Pikeville | 82298055 | DKY0116971 | 37820053000201 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  |  | KPC | NO | Straighten pole |  | 2022-05-20
2021 | 2021-01-13 | Pikeville | 76910039 | DKY0112903 | 37820053000273 | TRUE | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  |  | KPC | NO | straighten pole |  | 2021-10-26
2021 | 2021-01-13 | Pikeville | 81217755 | DKY0115565 | 37820054000021 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  |  | KPC | NO | Replace crossarms |  | 2022-05-05
2021 | 2021-01-13 | Pikeville |  |  | 37820076000033 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  |  |  | KPC | NO | Straighten pole |  | 2022-05-25
2021 | 2021-01-13 | Pikeville | 86445352 | DKY0122822 | 37820175000006 |  | 2974101-BIG ROCK / CONAWAY | Line Work | OH |  |  |  | KPC | YES | The correct pole number is 37820175A30009
2021 | 2021-01-14 | Pikeville | 78648753 | DKY0112554 | 38830954D20507 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | THIS JOB COMPLETED ON 2/9/21 BY ROBIE BLAIR |  | 2021-02-09
2021 | 2021-01-14 | Pikeville | 78733733 | DKY0112621 | 38830978000128 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Replace anchor and guy |  | 2022-03-29
2021 | 2021-01-14 | Pikeville | 86653792 | DKY0123267 | 38830978000308 | TRUE | 3410601-E.PRESTON / PRESTONSB | Line Work | OH |  |  |  | KPC | NO | Remove vines
2021 | 2021-01-19 | Pikeville |  |  | 38830954D30760 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarms deteoriated. Not seriously yet but keep an eye on. Check again on next inspection cycle. STATION ZONE. First pole outside station fence. | Prestonsburg, KY 41653, USA
2021 | 2021-01-19 | Pikeville |  |  | 38830955B00575 |  | 3410602-E.PRESTON / LANCER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Greer St, Prestonsburg, KY 41653, USA | 2021-01-19
2021 | 2021-01-20 | Pikeville |  |  | 38830955B00566 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire hanging down pole..Rusted in two at anchor. Needs to be reattached.@ Church of Christ @ Lancer. | Ky. Rte. 1428, Lancer, Ky.
2021 | 2021-01-20 | Pikeville | 78774314 | DKY0112718 | 38830955D00298 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | End of crossarm is split.@ corner of Wells Drive/ 1st street. | Wells Drive, Goble Robert’s Addition, Prestonsburg, Ky. | 2022-03-30
2021 | 2021-01-20 | Pikeville | 73374585 | DKY0105167 | 38830955D00472 | TRUE | 3410602-E.PRESTON / LANCER | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer and service | Ky. 1428, Lancer, Ky. | 2022-09-07
2021 | 2021-01-21 | Pikeville | 78689936 | DKY0112619 | 38830955D00117 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is hollow about 1 ft above ground line to about 4 ft. Up. 75 ft pole installed 1967 | Sawmill Road, Goble Robert’s Addition, Lancer, Ky. | 2021-05-22
2021 | 2021-01-22 | Pikeville | 78690005 | DKY0112824 | 38830955C00067 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | crossarm/braces: deteriorated, not rotten |  | KPC | YES | Crossarm is rotten/deteoriated. Pole is still solid but it was installed 1947 so might want to change pole as well. @ Lee Bug Lane. May need flagging. | 1198 Corn Fork, Prestonsburg, Ky. | 2021-03-31
2021 | 2021-01-22 | Pikeville |  |  | 38830956000074 |  | 3410602-E.PRESTON / LANCER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Corn Fork, Prestonsburg, Ky. | 2021-01-22
2021 | 2021-01-26 | Pikeville | 80874255 | DKY0115195 | 38831024000003 |  | 3402501-MIDDLECRE / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property , conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Need to remove hot tap risers on pole 1024-3. There is wire down on pole 1024-18 and an empty transformer laying on the ground. One of the cutouts on pole 3 is still closed in even though the fuse is blown. Also have empty transformers on the ground at pole 1024-1 and 1024-2. Field view shows this line to be de-energized at pole 1048-60 but it’s not, IT IS STILL HOT.....Located @ old Frasure Creek tipple on the right just below Middle Creek Station. | Ky. Rte. 404 David, Ky. IA Beverly Ann tipple | 2021-11-08
2021 | 2021-01-26 | Pikeville |  |  | 38831047000013 |  | 3402501-MIDDLECRE / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Foothill Drive, David, Ky. | 2021-01-26
2021 | 2021-01-27 | Pikeville |  |  | 37830111000026 |  | 3414501-CONSOLIDATE COAL / COAL COMPANY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Crossarm pin is bent over.@ mouth of Martin Branch. | KY-550, Mousie, KY, USA
2021 | 2021-01-29 | Pikeville |  |  | 37830161A40209 |  | 3407102-TOPMOST / CANEY | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive 3 phase line beginning at pole 37830161A40204. Eleven poles total. Wire down in several locations. Top of pole laying on the ground @ pole 204. | Topmost, Ky. tap down into head of Slone Br.
2021 | 2021-01-29 | Pikeville |  |  | 37830161D00101 |  | 3407102-TOPMOST / CANEY | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. @ Topmost Station | Topmost, Ky. | 2021-01-29
2021 | 2021-02-01 | Pikeville |  |  | 37830161D20220 |  | 3407102-TOPMOST / CANEY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on switch pole. @ Topmost Station | Topmost, Ky. | 2021-02-01
2021 | 2021-02-01 | Pikeville |  |  | 37830185000033 | TRUE | 3407103-TOPMOST / KITE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/melting | 336 Hall Branch, Topmost, Ky.
2021 | 2021-02-04 | Pikeville |  |  | 37830161D20221 |  | 3407103-TOPMOST / KITE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen on switch pole.@ outside station fence. | Topmost, Ky. | 2021-02-04
2021 | 2021-02-22 | Pikeville | 78973863 | DKY0113057 | 38831091000021 |  | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten. Previously re-enforced @ ground line. Installed 1951 | Hughes Creek Road, Evanston, Ky. | 2023-10-02
2021 | 2021-02-22 | Pikeville | 78973853 | DKY0113042 | 38831092000009 |  | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten. Has been previously re-enforced @ ground line. Installed 1969 | Main CP Road, Evanston, Ky.
2021 | 2021-02-22 | Pikeville | 78973842 | DKY0113036 | 38831140C00036 |  | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten. Has been previously re-enforced @ ground line. Installed 1969 | Mineshaft Road, Evanston, Ky.
2021 | 2021-02-22 | Pikeville | 78973825 | DKY0113029 | 38831140C00048 |  | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten @ ground line. Has been previously treated @ ground. Installed 1950 | Mineshaft Road, Evanston,Ky.
2021 | 2021-02-22 | Pikeville | 77215039 | DKY0110767 | 38831140C00049 | TRUE | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten @ground line. Installed 1952....behind Spring Fork Station. | Mineshaft Road, Evanston, Ky.
2021 | 2021-02-25 | Pikeville |  |  | 37830161D00119 |  | 3407101-TOPMOST / DEMA | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. @ Outside station fence. | Topmost, Ky. | 2021-02-25
2021 | 2021-02-25 | Pikeville |  |  | 37830161D40249 |  | 3407101-TOPMOST / DEMA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire slack. Laying close to transformer bushing. UNSAFE CONDITION | Potato Branch, Topmost, Ky. | 2021-02-25
2021 | 2021-02-25 | Pikeville |  |  | 37830185000071 |  | 3407101-TOPMOST / DEMA | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive 2 pole tap beginning @ pole 3783018500071. The fuse cutout is open on pole 185-70. Primary conductor on ground between 185-71 and 185-100. | 1001 Potato Branch, Topmost, Ky.
2021 | 2021-03-02 | Pikeville | 78973807 | DKY0113028 | 37830113000024 | TRUE | 3407101-TOPMOST / DEMA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | YES | Pole was installed 1946. Soft @ ground level but not rotten. Should consider changing within next few years. Also has inactive transformer that needs removed. | Basket Drive, Raven, Ky. | 2021-07-27
2021 | 2021-03-02 | Pikeville |  |  | 37830114A00202 |  | 3407101-TOPMOST / DEMA | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Needs removed. | 323 Whispering Pine Road, Ky. Hwy 7, Topmost, Ky. | 2021-03-02
2021 | 2021-03-02 | Pikeville | 78973783 | DKY0113024 | 37830114D00093 |  | 3407101-TOPMOST / DEMA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole washed out in creek. | 1171 Salisbury Branch, Topmost, Ky. | 2021-07-19
2021 | 2021-03-03 | Pikeville |  |  | 38831123B00127 | TRUE | 3408101-SALISBURY / PRINTER | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer on pole 38831123B00127 and secondary pole # 38831123B10331 | Meade Drive, Printer, Ky.
2021 | 2021-03-05 | Pikeville |  |  | 38821089D00069 |  | 3200202-BARRENSHE / VULCAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Barrenshee Creek, Freeburn, Ky. | 2021-03-05
2021 | 2021-03-08 | Pikeville | 73035583 | DKY0104898 | 38821090C00255 | TRUE | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole is leaning considerably. Needs straightening. Probably needs side guy.@ Second pole above recloser pole on Woodman Creek. | 314 Woodman Creek, Majestic, Ky. | 2022-06-29
2021 | 2021-03-08 | Pikeville | 81561683 | DKY0116089 | 38821138C00120 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Angle pin layed way over.@ On top of hill above the regulator pole. | 50078 State Hwy. 194 East, Stopover, Ky.
2021 | 2021-03-08 | Pikeville |  |  | 38821140A00509 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Neutral conductor sagging 3 ft. below communication cables in mid span. Needs slack taken out. | 1317 Lower Elk Creek, Woodman, Ky.
2021 | 2021-03-09 | Pikeville |  |  | 38821089D00395 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole is leaning. Needs side guy and anchor. | 44770 Ky. 194 East, Freeburn, Ky.
2021 | 2021-03-09 | Pikeville |  |  | 38821139B00081 |  | 3200202-BARRENSHE / VULCAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Woodman Creek Road, Woodman, Ky. | 2021-03-09
2021 | 2021-03-11 | Pikeville | 83966317 | DKY0120215 | 37830047C00228 | TRUE | 3403003-PIKEVILLE / CEDAR CREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole is leaning considerably. Needs side guy and anchor. | Ivy Court, Cedar Creek, Pikeville, Ky. 41501 | 2023-04-21
2021 | 2021-03-17 | Pikeville |  |  | 37830048B30084 |  | 3410503-S.PIKEVIL / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Narrows Road, Pikeville, Ky. | 2021-03-17
2021 | 2021-03-19 | Pikeville |  |  | 37830024D21859 |  | 3403002-PIKEVILLE / MAINST | Line Work | UG |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Padmount transformer needs guard posts.@ across from office of economic development. | Hambley Boulevard, Pikeville, Ky.
2021 | 2021-03-19 | Pikeville |  |  | 37830048C11675 |  | 3403002-PIKEVILLE / MAINST | Line Work | UG |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Padmount transformer needs guard posts. @ Dueling Barrels Brewery . Also padmount 48-1944 right beside it. | Hambley Boulevard , Pikeville, Ky.
2021 | 2021-03-22 | Pikeville | Outage # 4364961 |  | 37830024D30129 |  | 3403001-PIKEVILLE / CITY | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Primary conductor is floating. Only about 8-10 inches from the pole. Contacted duty supervisor and repairs completed 3/23/21 | 172 Bill King Hollow, Pikeville, Ky. | 2021-03-23
2021 | 2021-03-24 | Pikeville |  |  | 37830024D20096 |  | 3403001-PIKEVILLE / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Third Street, Pikeville, Ky. | 2021-03-24
2021 | 2021-03-24 | Pikeville |  |  | 37830024D20443 | TRUE | 3403001-PIKEVILLE / CITY | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker. Satellite dish on pole. Directv | Wolford Stret, Pikeville, Ky.
2021 | 2021-03-24 | Pikeville | 79156492 | DKY0113292 | 37830024D20451 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line. | 172 Third Street, Pikeville, Ky. | 2021-10-15
2021 | 2021-03-25 | Pikeville | 79198391 | DKY0113503 | 37830048A30374 |  | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten | 120 S College Street, Pikeville, Ky. | 2021-10-01
2021 | 2021-03-25 | Pikeville |  |  | 37830048A30668 |  | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown on transformer bank pole. @ in front of the Kinzer Family Residential Center. | South College Street, Pikeville, Ky.
2021 | 2021-03-25 | Pikeville | 86142539 |  | 37830048A40026 | TRUE | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown on transformer bank pole. @ KFC | Baird Avenue, Pikeville, Ky.
2021 | 2021-03-25 | Pikeville | COMPLETE IN FIELD | COMPLETE IN FIELD | 37830048C11164 |  | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown on transformer bank pole. | 151 Bank Street, Pikeville, Ky.
2021 | 2021-03-29 | Pikeville | 82530892 | DKY0117181 | 38821064D00225 | TRUE | 3200203-BARRENSHE / SLATE BRANCH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | lightning arresters/insulators: damaged |  | KPC | YES | Pole is burned badly. Lightning arrestors and insulators damaged by lightning.@ turn up hill at top of pounding mill road to old strip road. | Freeburn, KY 41528, USA
2021 | 2021-03-30 | Pikeville |  |  | 38821017B20040 |  | 3200204-BARRENSHE / POUNDING | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lovers Lane, Buskirk, Ky. | 2021-03-30
2021 | 2021-03-30 | Pikeville | 84246110 | DKY0119255 | 38821017B20453 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | lightning arresters/insulators: damaged |  | KPC | YES | Lightning arrestor blown. @ Lovers Lane. | 10183 State Hwy 1056, McCarr, KY 41544, USA | 2023-05-18
2021 | 2021-03-30 | Pikeville | 79198460 | DKY0113531 | 38821061D00334 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is burned at the cutout bracket. Pole is tagged 1016- 334 in field but field view doesn’t show it. It’s between poles 138 and 139. | 10582 State Hwy 1056, McCarr, KY 41544, USA | 2021-10-29
2021 | 2021-04-01 | Pikeville | 84827127 | DKY0120372 | 38821065A00058 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | guys/anchors: broken or missing | lightning arresters/insulators: damaged |  | KPC | NO | Anchor washed out. Needs replaced . Guy wire hanging down pole. Lightning arrestor blown. | 1060 Peter Fork Road, McCarr, Ky.
2021 | 2021-04-01 | Pikeville | 82554781 | DKY0117219 | 38821065D10365 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive single phase tap and transformer. Remove poles 365, 268 and 269. | Rivermill Road, Freeburn, Ky. | 2022-07-12
2021 | 2021-04-06 | Pikeville |  |  | 38821089A00425 |  | 3200201-BARRENSHE / FREEBURN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Park Rd, Freeburn, KY 41528, USA | 2021-04-06
2021 | 2021-04-06 | Pikeville | 84011665 | DKY0118871 | 38821112C00048 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 469 Robinette Branch, Freeburn, Ky. | 2022-12-21
2021 | 2021-04-08 | Pikeville | 77399570 | DKY0110764 | 37830040000120 |  | 3413402-GARRETT / LACKEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line//THIS POLE WAS REPLACED ON DKY0116432/81827834 ON 5/10/22 BY ROBIE BLAIR | 14654 KY-550, Lackey, KY 41643, USA | 2022-05-10
2021 | 2021-04-08 | Pikeville | 74176641 | DKY0106532 | 37830064000006 | TRUE | 3413402-GARRETT / LACKEY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator melting. Middle Epoxilator. | Ky. Hwy. 550 East, Lackey, Ky. | 2022-09-12
2021 | 2021-04-12 | Pikeville |  |  | 37830111B20243 |  | 3413402-GARRETT / LACKEY | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Remove or repair inactive single phase line down by recent ice storms. Wire down in all 6 spans from pole 111-243 to pole 111-249. Line is not serving any customers currently.@ Head of Ball Branch. | KY-1087, Mousie, KY, USA
2021 | 2021-04-13 | Pikeville |  |  | 37830111000039 |  | 3413402-GARRETT / LACKEY | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop laying on roof. Needs slack taken out for clearance. @ Old Baptist Drive just about the church. | 9677 KY-550, Mousie, KY 41839, USA
2021 | 2021-04-13 | Pikeville |  |  | 37830111000051 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Huff Town Rd, Mousie, Kentucky 41839, USA | 2021-04-13
2021 | 2021-04-14 | Pikeville | 76450126 | DKY0109453 | 37830135000134 |  | 3413402-GARRETT / LACKEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is in early rot at ground line. Keep an eye on it. Check again in few years. | Pine Tree Hollow, Mousie, Ky. | 2021-11-09
2021 | 2021-04-14 | Pikeville | 86528838 |  | 37830135000162 |  | 3413402-GARRETT / LACKEY | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning on hill. Probably needs anchor installed and side guy. About .5 mile up turtle Branch just above the end of the coal company 3 phase. | Turtle Branch, Mousie, Ky.
2021 | 2021-04-15 | Pikeville | 74176679 | DKY0109891 | 37830040C30043 |  | 3413401-GARRETT / GARRETT | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarms are deteoriated/ rotten. @ Corner of Front and Center Street. | 201 Front Street, Garrett, Ky. | 2021-04-21
2021 | 2021-04-15 | Pikeville |  |  | 37830041A00063 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen | S Ralphs Road, Garrett, Ky. 41630 | 2021-04-15
2021 | 2021-04-21 | Pikeville |  |  | 37830041B10355 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Railroad Lane, Garrett, Ky. | 2021-04-21
2021 | 2021-04-21 | Pikeville |  |  | 37830065A00084 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | George Road, Estill, Ky. | 2021-04-21
2021 | 2021-04-21 | Pikeville | 80997130 | DKY0115339 | 37830065A10079 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at ground line. Requested AT&T to replace on 11/18/21 and completed write up. | 422 Estill Bottom, Estill, Ky. | 2021-12-16
2021 | 2021-04-27 | Pikeville | 76956912 | DKY0110460 | 37830066B00084 | TRUE | 3413401-GARRETT / GARRETT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is washed out in creek. Only about 2 feet in ground. | 929 Ky. 1086, Wayland, Ky. 41666 | 2021-06-08
2021 | 2021-04-27 | Pikeville |  |  | 37830066B00112 |  | 3413401-GARRETT / GARRETT | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilators are deteoriated/melting. Almost top of hill @Steele Crk. On left over the hill. | 2872 Ky 1086, Wayland, Ky. 41666
2021 | 2021-04-29 | Pikeville |  |  | 37830234000042 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator deteoriated/melting. @ mouth of Arnold Fork. | 13491 Ky. Hwy. 7 South, Kite, Ky.
2021 | 2021-04-29 | Pikeville |  |  | 37830258000107 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Service drop laying on the ground. De-energized. Needs removed. | West Fork, Kite, Ky. | 2021-04-29
2021 | 2021-05-03 | Pikeville |  |  | 37830188B00048 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Service drop hanging down pole. Needs removed | Ky Rte. 466, Melvin, Ky. | 2021-05-03
2021 | 2021-05-03 | Pikeville |  |  | 37830212D00244 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Caleb Fork, Weeksbury, Ky. | 2021-05-03
2021 | 2021-05-05 | Pikeville | 86404148 | DKY0122747 | 37820217C00214 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | YES | asset pole reported on 12/11/17 by external pole inspectors - moving to ckt defect tracker on 05/05/21 to close out asset pole smartsheet - work order was written to replace pole, but it was sent to cancel with a remark that INACTIVE LINE NEEDS REMOVED instead of replace pole | 7504 Marrowbone creek Rd Elkhorn City, KY
2021 | 2021-05-05 | Pikeville |  |  | 37830212B00139 |  | 3412901-WEEKSBURY / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Minerva Lane, Weeksbury, Ky. | 2021-05-05
2021 | 2021-05-05 | Pikeville | 79515321 | DKY0113640 | 38820746A00232 |  | 3202201-LOVELY / LOVELY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | asset pole reported on 10/27/16 by external pole inspectors - moving to ckt defect tracker on 05/05/21 to close out asset pole smartsheet | near intersection Right Fork Buck Creek and Big Elk Road | 2021-06-23
2021 | 2021-05-06 | Pikeville |  |  | 37830043000008 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen on transformer pole | Ky. Rte. 1101, Drift, Ky. | 2021-05-06
2021 | 2021-05-06 | Pikeville |  |  | 37830043000010 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen on transformer pole | Ky Rte. 1101, Drift, Ky. | 2021-05-06
2021 | 2021-05-06 | Pikeville | 86529655 |  | 37830043A10007 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken | Ky. Rte. 1101, Drift, Ky.
2021 | 2021-05-10 | Pikeville |  |  | 38831121D00328 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer is covered with vines | 238 Three Oaks Lane, Langley, Ky.
2021 | 2021-05-10 | Pikeville |  |  | 38831145C00084 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines. @ across from Hayes Family Dentistry and below Allen Central School. | Spencer Street, Ky. 80, Eastern, Ky.
2021 | 2021-05-10 | Pikeville |  |  | 38831145C00143 |  | 3402204-MCKINNEY / MAYTOWN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Old Ky. 80, Eastern, Ky. | 2021-05-10
2021 | 2021-05-10 | Pikeville |  |  | 38831145C00212 | TRUE | 3402204-MCKINNEY / MAYTOWN | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines | Ousley Drive, Eastern, Ky.
2021 | 2021-05-11 | Pikeville |  |  | 38831122000235 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator deteoriated/melted | 130 Earla Drive, Turkey Creek, Maytown, Ky.
2021 | 2021-05-11 | Pikeville |  |  | 38831146000226 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator deteoriated/melting | 925 Turkey Creek, Langley, Ky.
2021 | 2021-05-13 | Pikeville |  |  | 38821062C00108 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Pond Creek Road, McAndrews, Ky. | 2021-05-13
2021 | 2021-05-17 | Pikeville |  |  | 38821086D00329 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Bennie Hatfield Road, McAndrews, Ky. | 2021-05-17
2021 | 2021-05-17 | Pikeville |  |  | 38821110C00134 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Pond Creek Road, McVeigh, Ky. | 2021-05-17
2021 | 2021-05-17 | Pikeville |  |  | 38821110C00166 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Sawmill Road, McVeigh, Ky. | 2021-05-17
2021 | 2021-05-17 | Pikeville |  |  | 38821110C00168 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Sawmill Road, McVeigh, Ky. | 2021-05-17
2021 | 2021-05-17 | Pikeville |  |  | 38821110C00169 |  | 3201001-TOM WATKINS / POND CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Sawmill Road, McVeigh, Ky. | 2021-05-17
2021 | 2021-05-17 | Pikeville |  |  | 38821110D00040 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 8044 Straight Hollow, McVeigh, Ky.
2021 | 2021-05-17 | Pikeville |  |  | 38821111B00001 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 6448 Straight Hollow, McVeigh, Ky.
2021 | 2021-05-19 | Pikeville |  |  | 38831103000278 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Haynes Village, Pikeville, Ky. | 2021-05-19
2021 | 2021-05-19 | Pikeville |  |  | 38831103000318 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Rfk Cowpen Road, Pikeville, Ky. | 2021-05-19
2021 | 2021-05-19 | Pikeville |  |  | 38831104000081 |  | 3402003-KEYSER / MULLINS | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Neutral conductor down/missing. 1.5 miles up Rfk. No truck to poles. | Rfk Cowpen, Pikeville, Ky.
2021 | 2021-05-19 | Pikeville |  |  | 38831127A00444 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Arrowhead Estates, Mullins, Ky. | 2021-05-19
2021 | 2021-05-20 | Pikeville |  |  | 38831103000168 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Jennys Fork, Cowpen, Pikeville, Ky. | 2021-05-20
2021 | 2021-05-20 | Pikeville |  |  | 38831103000271 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Kinnikinnick Road, Mullins, Ky. | 2021-05-20
2021 | 2021-05-20 | Pikeville |  |  | 38831103000299 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  |  |  | KPC | NO | Guy wire needs marker | Ridge Point Road, Pikeville, Ky. | 2021-05-20
2021 | 2021-05-21 | Pikeville |  |  | 38831151A00655 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | N Mayo Trail, Pikeville, Ky. | 2021-05-21
2021 | 2021-05-24 | Pikeville |  |  | 38831128000018 |  | 3402002-KEYSER / STONECOAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NO | Pole is rotten at ground line. @ next to a red barn/garage on the right. | 2088 Stonecoal Road, Pikeville, Ky. | 2022-05-06
2021 | 2021-05-24 | Pikeville | 82683217 | DKY0117375 | 38831128000214 | TRUE | 3402002-KEYSER / STONECOAL | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole | 233 Cushaw Branch, Stonecoal Creek, Pikeville, Ky. | 2022-07-12
2021 | 2021-05-27 | Pikeville |  |  | 38821105D00060 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign | NO | Need to put slack in service drop. Customer says it’s pulling his mast over. | 138 Taylor Road, Zebulon, Ky.
2021 | 2021-05-27 | Pikeville |  |  | 38821105D00346 | TRUE | 3402002-KEYSER / STONECOAL | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer | 229 Taylor Road, Zebulon, Ky.
2021 | 2021-05-27 | Pikeville |  |  | 38821129D00020 |  | 3402002-KEYSER / STONECOAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Burning Fork Road, Pikeville, Ky. | 2021-05-27
2021 | 2021-06-01 | Pikeville | 79586015 | DKY0113604 | 37830070000118 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  |  |  | KPC | YES |  |  | 2021-06-08
2021 | 2021-06-01 | Pikeville |  |  | 38821129B00104 |  | 3402002-KEYSER / STONECOAL | Forestry | OH |  |  | Circuit has since been sprayed after reported date | KPC | NO | Pole and transformer is covered with vines | 2648 Ratliff Creek Road, Pikeville, Ky. | 2023-09-30
2021 | 2021-06-01 | Pikeville |  |  | 38831151D00090 | TRUE | 3402001-KEYSER / THOMPSON RD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/ melting | 142 Coal Run Hill, Pikeville, Ky. | 2023-03-02
2021 | 2021-06-01 | Pikeville |  |  | 38831151D00103 |  | 3402001-KEYSER / THOMPSON RD | Service Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer is covered with vines | 50 Coal Run Hill, Pikeville, Ky.
2021 | 2021-06-02 | Pikeville |  |  | 38831151D00388 |  | 3402001-KEYSER / THOMPSON RD | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer is covered with vines | 124 Lakeview Drive, Pikeville, Ky.
2021 | 2021-06-04 | Pikeville |  |  | 38821105D00344 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Montrose Drive, Raccoon Creek, Pikeville, Ky. | 2021-06-04
2021 | 2021-06-04 | Pikeville |  |  | 38821106000002 |  | 3411802-JOHNSCREE / RACCOON | Forestry | OH |  |  | Circuit has since been sprayed after reported date | KPC | NO | Pole is covered in vines | Charles Farm Drive, Raccoon Creek, Pikeville, Ky. | 2023-09-30
2021 | 2021-06-07 | Pikeville |  |  | 37820002000015 | TRUE | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Insulator damaged/ broken. No truck. Behind house on hill. | 1035 Frozen Fork, Raccoon, Ky.
2021 | 2021-06-07 | Pikeville |  |  | 37820002000064 | TRUE | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator broken. Mouth of 58 Branch | 4480 Raccoon Road, Pikeville, Ky.
2021 | 2021-06-07 | Pikeville |  |  | 37820026000062 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral conductor down. | 2178 Lfk Upper Chloe, Pikeville, Ky. | 2023-12-18
2021 | 2021-06-07 | Pikeville |  |  | 37820050000040 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. Last pole in hollow. | Wolfpen Fork, Lower Pompey , Pikeville, Ky. | 2023-07-07
2021 | 2021-06-07 | Pikeville |  |  | 38821130000024 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Pole and transformer is covered with vines | 153 Johns Branch, Raccoon, Ky.
2021 | 2021-06-08 | Pikeville |  |  | 38821108000224 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown on step- down transformer bank. | 344 Sunshine Lane, Kimper, Ky.
2021 | 2021-06-09 | Pikeville | 63681574 | DKY0093491 | 38821107000031 | TRUE | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators are very deteoriated. | Lawson Branch, Raccoon, Ky. | 2022-07-12
2021 | 2021-06-10 | Pikeville | 86515890 |  | 37820006000004 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown. @ Little Virgie Church | 50 Long Fork, Upper Johns Creek, Pikeville, Ky.
2021 | 2021-06-10 | Pikeville | 84009648 | DKY0118868 | 37820031A00036 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer and single phase tap. Line is de-energized @ pole 31-2 | 729 Cane Fork, Long Fork, Upper Johns Creek, Pikeville, Ky. | 2022-12-20
2021 | 2021-06-10 | Pikeville | 84010875 | DKY0118869 | 37820031B00004 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown | 3255 Long Fork, Upper Johns Creek, Pikeville, Ky. | 2022-12-20
2021 | 2021-06-11 | Pikeville |  |  | 38820868B00156 |  | 2150501-BORDERLAND / NOLAN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service hanging down pole. | 319 Lick Fork, N Big Creek Road, Hatfield, Ky.
2021 | 2021-06-11 | Pikeville |  |  | 38820868B00168 |  | 2150501-BORDERLAND / NOLAN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Lick Branch, N Big Creek Road, Hatfield, Ky.
2021 | 2021-06-14 | Pikeville |  |  | 38820917C00417 |  | 2150502-BORDERLAND/CHATTAROY | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Pole and transformer is covered in vines | 4264 State Hwy. 292 W , South Williamson | 2023-10-10
2021 | 2021-06-14 | Pikeville |  |  | 38820917D00423 |  | 2150502-BORDERLAND/CHATTAROY | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer is covered in vines. Take-off pole for Falls Branch. | State Hwy. 292 W, South Williamson | 2023-10-10
2021 | 2021-06-15 | Pikeville | 79877911 | DKY0113949 | 38820964B00125 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Recloser pole is rotten/damaged at ground line. | 2631 N Big Creek Road, Sidney, Ky. | 2021-11-23
2021 | 2021-06-15 | Pikeville | 80118619 | DKY0114238 | 38820988A00028 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Both Crossarm braces are broken. She’ll of pole at ground level has started to rot. Might want to replace pole. Just before Thacker Road | 1976 N Big Creek Road, Sidney, Ky. | 2021-10-08
2021 | 2021-06-15 | Pikeville | 81172275 | DKY0115527 | 38820988B00007 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | End of crossarm is split. Side opposite the road. Questionable if truck can reach. | 810 N Big Creek Road, Sidney, Ky. | 2022-02-11
2021 | 2021-06-23 | Pikeville |  |  | 38821061C10369 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop laying on phone cables. Needs slack taken out or change secondary pole to raise for clearance. | 2270 Pigeonroost Branch, Sidney, Ky.
2021 | 2021-06-24 | Pikeville |  |  | 38820991D20094 |  | 2150103-SPRIGG / SPRIGG | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lower Stringtown Road, Belfry, Ky. | 2021-06-24
2021 | 2021-06-24 | Pikeville |  |  | 38820991D20311 |  | 2150103-SPRIGG / SPRIGG | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Lower Stringtown Road, Belfry, Ky. | 2021-06-24
2021 | 2021-06-24 | Pikeville |  |  | 38820991D40136 |  | 2150103-SPRIGG / SPRIGG | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | State Hwy 292, Burnwell, Ky. | 2021-06-24
2021 | 2021-06-24 | Pikeville |  |  | 38820991D40137 |  | 2150103-SPRIGG / SPRIGG | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | McCoy Street, State Hwy 292, Belfry, Ky. | 2021-06-24
2021 | 2021-06-24 | Pikeville |  |  | 38820991D40265 |  | 2150103-SPRIGG / SPRIGG | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | State Hwy 292, Burnwell, Ky, | 2021-06-24
2021 | 2021-06-28 | Pikeville |  |  | 38820992C20464 |  | 2150105-SPRIGG / MATEWAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | River Road, Buskirk, Ky. | 2021-06-28
2021 | 2021-06-28 | Pikeville |  |  | 38821016C00018 |  | 2150105-SPRIGG / MATEWAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | River Road, Buskirk, Ky. | 2021-06-28
2021 | 2021-06-28 | Pikeville |  |  | 38821017A20394 |  | 2150105-SPRIGG / MATEWAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Spring Street, Buskirk, Ky. | 2021-06-28
2021 | 2021-06-28 | Pikeville | 79154956 | DKY0113093 | 38821017B21949 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole is leaning badly. Someone has put temporary guy to hold it. Needs to be straightened/relocated. @ behind the apartment building at mouth of lovers lane. | Lovers Lane,Buskirk, Ky. | 2021-11-16
2021 | 2021-06-28 | Pikeville |  |  | 38821041D00260 |  | 2150105-SPRIGG / MATEWAN | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines. Near the end of lovers lane. | Lovers Lane, Buskirk, Ky.
2021 | 2021-06-29 | Pikeville |  |  | 38821083A00073 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator is deteoriated/melted | 31 Lfk Bevins Branch, Meta, Ky.
2021 | 2021-06-30 | Pikeville | 84656719 | DKY0120089 | 38821057D00005 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire broken, hanging down pole. | 7819 Zebulon Hwy, Pikeville, KY 41501, USA | 2023-06-02
2021 | 2021-06-30 | Pikeville |  |  | 38821058B00029 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm is rotten/deteoriated. Across street from old Happy Mart | 9810 Meta Hwy, Meta, KY 41501, USA
2021 | 2021-06-30 | Pikeville |  |  | 38821082000251 |  | 3411801-JOHNSCREE / META | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Needs removed. | 146 N Blackburn Bottom, Meta, ky.
2021 | 2021-07-01 | Pikeville | 80671509 | DKY0114952 | 38821058D00038 |  | 3411801-JOHNSCREE / META | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Pole has early rot of outer shell at ground line. It’s ok for now but need to keep watch. Satellite dish on pole | 10126 Bent Branch Rd, Pikeville, KY 41501, USA | 2021-10-25
2021 | 2021-07-01 | Pikeville |  |  | 38821082000130 |  | 3411801-JOHNSCREE / META | Service Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree on service drop. | 555 Wynns Branch, Zebulon, Ky.
2021 | 2021-07-06 | Pikeville |  |  | 38821059000035 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Neutral conductor down/missing. #4 copper | 1318 Scott Fork, Meta, Ky.
2021 | 2021-07-07 | Pikeville | 84621552 | DKY0120012 | 38820986000124 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive primary tap. Very low over the road. Neutral conductor is head high. | 524 Hurricane Branch, Varney, Ky. | 2023-05-24
2021 | 2021-07-07 | Pikeville | 84620952 | DKY0120010 | 38820987A00001 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive primary tap hanging down pole. Needs to be removed. | 170 John Young Branch, Varney, Ky. | 2023-05-24
2021 | 2021-07-09 | Pikeville |  |  | 38830984000087 |  | 3411801-JOHNSCREE / META | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken. On hill. | 700 Mills Branch, Gulnare, Ky.
2021 | 2021-07-13 | Pikeville |  |  | 38831031000033 |  | 3411801-JOHNSCREE / META | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Neutral conductor down/missing. #4 copper | 1314 Hurts Branch, Gulnare, Ky.
2021 | 2021-07-15 | Pikeville | 83966882 | DKY0121091 | 37830048B40185 | TRUE | 3410502-S.PIKEVIL / ISLANDCRE | Forestry | OH |  |  | Circuit maintenance scheduled for 2024 | Foreign | NO | Pole is covered in vines | 128 Island Creek Road, Pikeville, Ky.
2021 | 2021-07-19 | Pikeville |  |  | 37830046000199 |  | 3410502-S.PIKEVIL / ISLANDCRE | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole. | 47 Spears Branch, Toler Creek, Pikeville, Ky.
2021 | 2021-07-22 | Pikeville |  |  | 37830095C20309 |  | 3410502-S.PIKEVIL / ISLANDCRE | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole | 418 Road Fork, Island Creek, Pikeville, Ky.
2021 | 2021-07-23 | Pikeville |  |  | 37830164000217 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole | 210 Lfk Slone Hollow, Ligon, Ky.
2021 | 2021-07-26 | Pikeville |  |  | 37830069000060 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Howell Branch, Branham Creek, Galveston, Ky. | 2021-07-26
2021 | 2021-07-26 | Pikeville |  |  | 37830094000243 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral conductor down/missing. Step down transformer pole. #4 copper | 150 Hall Branch, Branham Creek, Galveston,Ky.
2021 | 2021-07-28 | Pikeville |  |  | 37830117000013 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Remove inactive primary conductors hanging down pole. @ mouth Mitchell Branch. Take-off pole. | Mitchell Branch, Ky 979, Beaver, Ky. 41604
2021 | 2021-07-28 | Pikeville |  |  | 37830118B10076 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole. @ Top of hill between Tinkerfork and Branham Creek. | Tinker Fork, Kentucky 41660, USA
2021 | 2021-07-28 | Pikeville |  |  | 37830141000016 | TRUE | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/missing. #4 copper | 1827 Rfk Tinkerfork, Beaver, Ky.
2021 | 2021-07-28 | Pikeville |  |  | 37830141000023 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/missing. #4 copper. | 2525 Rfk Tinkerfork, Beaver, Ky.
2021 | 2021-07-28 | Pikeville |  |  | 37830141000139 | TRUE | 3403201-BEAVERCRE / LIGON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole | 2658 Rfk Tinkerfork, Beaver, Ky.
2021 | 2021-07-28 | Pikeville |  |  | 37830141000205 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken | 120 Tackett Fork, Beaver, Ky.
2021 | 2021-08-02 | Pikeville |  |  | 37830139A10043 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | N Locust Road, Hi Hat, Ky. | 2021-08-02
2021 | 2021-08-02 | Pikeville |  |  | 37830139A40103 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines | 315 S Locust Road, Hi Hat, Ky.
2021 | 2021-08-02 | Pikeville |  |  | 37830139B00080 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Meade Hill, Hi Hat, Ky. | 2021-08-02
2021 | 2021-08-02 | Pikeville |  |  | 37830139B00359 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Raider Drive, Hi Hat, Ky. | 2021-08-02
2021 | 2021-08-02 | Pikeville |  |  | 37830139B00408 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Raider Drive, Ky. Rte. 122, Hi Hat, Ky. | 2021-08-02
2021 | 2021-08-05 | Pikeville |  |  | 37830090000114 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole | 255 Cherokee Branch, Price, Ky.
2021 | 2021-08-05 | Pikeville |  |  | 37830091B00042 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Ky. Rte. 122, Price, Ky. | 2021-08-05
2021 | 2021-08-05 | Pikeville |  |  | 37830091B00048 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered in vines. Across creek. | 12869 Ky. Rte. 122, Price, Ky.
2021 | 2021-08-05 | Pikeville | 81402086 | DKY0115878 | 37830114C00007 | TRUE | 3403202-BEAVER CRK / PRICE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at ground line. | 272 Buckeye Branch, Price, Ky. | 2023-06-20
2021 | 2021-08-09 | Pikeville |  |  | 38831098D00248 |  | 3408103-SALISBURY / MARTIN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Outer shell of pole is rotted at ground line. About 1 1/2 inches around pole. Probably ok for now but should consider changing pole within next few years.. Across road from Garth Vocational. | 1143 Left Beaver Road, Martin, Ky.
2021 | 2021-08-10 | Pikeville |  |  | 38831074D00045 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is completely covered with vines | Old Railroad Street, Martin, Ky.
2021 | 2021-08-10 | Pikeville |  |  | 38831074D00400 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Cliff Road, Martin, Ky. | 2021-08-10
2021 | 2021-08-12 | Pikeville |  |  | 38831074D00582 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 183 Autumn Drive, Martin, Ky | 2021-08-12
2021 | 2021-08-12 | Pikeville |  |  | 38831098A00294 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Stephens Branch, Martin, Ky. | 2021-08-12
2021 | 2021-08-12 | Pikeville |  |  | 38831098A00300 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Stephens Branch, Martin, Ky. | 2021-08-12
2021 | 2021-08-12 | Pikeville |  |  | 38831098A00385 |  | 3408103-SALISBURY / MARTIN | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree on neutral conductor. Mid span between poles 384 and 385 | Muddy Branch Road, Stephens Branch, Martin, Ky.
2021 | 2021-08-12 | Pikeville |  |  | 38831098D00578 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 245 Red Isom Hollow, Martin, Ky. | 2021-08-12
2021 | 2021-08-13 | Pikeville |  |  | 38831122000091 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Henry’s Branch, Maytown, Ky. | 2021-08-13
2021 | 2021-08-13 | Pikeville | 84551400 | DKY0119911 | 38831122000164 | TRUE | 3408103-SALISBURY / MARTIN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at ground line | 1294 Henry’s Branch, Maytown, Ky. | 2023-03-14
2021 | 2021-08-16 | Pikeville |  |  | 37830018D00216 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Pole is rotten at ground line | 99 Cow Hollow, Drift, Ky.
2021 | 2021-08-17 | Pikeville |  |  | 37830042D00442 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky. Rte. 122, Minnie, Ky. | 2021-08-17
2021 | 2021-08-17 | Pikeville |  |  | 37830067A00089 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole | Johnson Road, McDowell, Ky.
2021 | 2021-08-18 | Pikeville | 83985332 | DKY0118883 | 37830019B00041 | TRUE | 3402202-MCKINNEY / GIBSON | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Crossarms are deteoriated/rotten. Top of pole looks rotten. | 33 Upper Lane Siding Station, Minnie, Ky. | 2023-06-19
2021 | 2021-08-18 | Pikeville |  |  | 37830067C00185 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | conductors: excessive splices, deteriorated conductors | KPC | NO | Neutral conductor down/ stolen. #4 copper | Mary Branch, McDowell, KY.
2021 | 2021-08-23 | Pikeville |  |  | 37830092000011 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  |  | Foreign | NO | Neutral conductor down/stolen. #4 copper. Between poles 11 and 102 | 2191 Frasure Creek, McDowell, Ky.
2021 | 2021-08-23 | Pikeville |  |  | 37830092000015 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (3) | Frasure Creek, McDowell, KY 41647, USA | 2021-08-23
2021 | 2021-08-31 | Pikeville |  |  | 38831003D10346 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Park Street, Dwale, Ky. | 2021-08-31
2021 | 2021-08-31 | Pikeville |  |  | 38831027C00132 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Railroad Street, Dwale, Ky. | 2021-08-31
2021 | 2021-08-31 | Pikeville |  |  | 38831027C00181 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 23 Hall Street, Allen, Ky. | 2021-08-31
2021 | 2021-08-31 | Pikeville |  |  | 38831027C10722 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | S River Street, Dwale, Ky. | 2021-08-31
2021 | 2021-08-31 | Pikeville |  |  | 38831027D00246 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 44 S Fifth Street, Allen, Ky. | 2021-08-31
2021 | 2021-09-01 | Pikeville | 76371951 | DKY0110393 | 38831003D00129 | TRUE | 3400101-ALLEN / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator deteoriated/melted | 89 Mosley Branch , Allen, Ky. | 2022-03-30
2021 | 2021-09-01 | Pikeville |  |  | 38831003D00294 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Allen-Banner Road, Ky 1428, Allen, Ky. | 2021-09-01
2021 | 2021-09-01 | Pikeville |  |  | 38831027C00558 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ky. 1428, Allen, Ky. | 2021-09-01
2021 | 2021-09-01 | Pikeville |  |  | 38831052C00216 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker , transformers: leaking, damaged |  | KPC | NO | Guy wire needs marker | U.S. Hwy. 23 South, Ivel, Ky. | 2021-09-01
2021 | 2021-09-07 | Pikeville |  |  | 37830187D00049 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral conductor down. Hanging down pole. 6A copper | 951 Golf Course Road, Wheelwright, Ky.
2021 | 2021-09-07 | Pikeville |  |  | 37830211C00307 | TRUE | 3400602-BURTON / WHEELWRIG | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive secondary hanging down pole | 239 Robert Hood Drive, Wheelwright, Ky.
2021 | 2021-09-07 | Pikeville |  |  | 37830211C00311 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop is only about 6.5 ft. off the ground in mid span. Don’t think enough slack could be taken out for proper clearance. Probably could be re-routed to come off secondary pole #404 behind house or may need to install pole in line between poles 311 and 318 | 256 Robert Hood Drive, Wheelwright, Ky.
2021 | 2021-09-07 | Pikeville |  |  | 37830211C00320 |  | 3400602-BURTON / WHEELWRIG | Forestry | OH |  |  | Circuit has since been sprayed after reported date | KPC | NO | Pole and transformer is covered with vines. | Shop Fork Street, Wheelwright, Ky. | 2023-09-30
2021 | 2021-09-08 | Pikeville |  |  | 37830187C00014 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Pole is washed out in creek. Questionable if truckable. First pole above recloser pole. per Derek Coleman email, MAY 24, 2022 I visited this site Saturday, 5-21-2022, and work has been done to this pole to put material around the pole. This pole is on the creek bank and has had rock and dirt placed around it. The structure is in good shape and not rotted. Only issue was previous creek bank slipping, which has been correct. 3-Phase Pole 37830187C00014 is located at Bypro along KY122 and no work appears to be needed and this needs removed from the Tracker. | 21628 Ky 122, Bypro , Ky. | 2022-05-24
2021 | 2021-09-08 | Pikeville |  |  | 37830211C00342 |  | 3400602-BURTON / WHEELWRIG | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Main Street, Wheelwright, Ky. | 2021-09-08
2021 | 2021-09-08 | Pikeville |  |  | 37830211C00396 |  | 3400602-BURTON / WHEELWRIG | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove service drop hanging down pole | 210 Stoker Branch, Wheelwright, Ky.
2021 | 2021-09-08 | Pikeville |  |  | 37830211D00036 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken | 486 Stoker Branch, Wheelwright, Ky.
2021 | 2021-09-13 | Pikeville |  |  | 37830163A00110 |  | 3400601-BURTON / LIGON-CLE | Forestry | OH |  |  | Circuit has since been sprayed after reported date | KPC | NO | Pole and transformer is covered with vines | 69 Buckingham Bottom Road, Bevinsville, Ky. | 2023-09-30
2021 | 2021-09-14 | Pikeville |  |  | 37830163A00158 |  | 3400601-BURTON / LIGON-CLE | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole | 20026 KY-122, Bevinsville, KY 41606, USA
2021 | 2021-09-21 | Pikeville | 81025975 | DKY0115364 | 38821087C20514 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is in slide. | State Hwy. 1056, Belfry, Ky. | 2021-12-02
2021 | 2021-09-23 | Pikeville |  |  | 38821064B00085 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Neutral conductor down/missing. #4 copper | 1090 Dials Branch, Ransom, Ky.
2021 | 2021-09-23 | Pikeville |  |  | 38821087D00093 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken hanging down pole. Needs to be reattached to anchor. @ take off pole for middle fork. | 814 Upper Blackberry Rd, Ransom, KY 41558, USA
2021 | 2021-09-23 | Pikeville |  |  | 38821111B00055 | TRUE | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 1900 Upper Blackberry Rd, Ransom, KY 41558, USA
2021 | 2021-09-23 | Pikeville |  |  | 38821111D00028 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 255 Pickle Bean Hollow, Ransom, KY 41558, USA
2021 | 2021-09-28 | Pikeville | 84101102 | DKY0118978 | 37820032B00025 | TRUE | 3408303-COLEMAN / PETERCRK | Line Work | OH |  |  |  | Foreign | NO | #4 copper neutral conductor down/missing. About 2 miles up smith fork about half way up the hill near the head. | Smith Fork Rd, Phelps, KY, USA | 2023-02-01
2021 | 2021-09-28 | Pikeville | 84103225 | DKY0118981 | 37820032B00063 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/missing. #4 copper | 243 Staggerweed Fork, Phelps, KY 41553, USA | 2023-01-06
2021 | 2021-09-29 | Pikeville |  |  | 38821136D00019 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Abby Branch, Phelps, KY 41553, USA | 2021-09-29
2021 | 2021-09-29 | Pikeville |  |  | 38821136D20026 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Mill Branch Rd, Phelps, KY 41553, USA | 2021-09-29
2021 | 2021-09-29 | Pikeville |  |  | 38821137A00330 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Gregory St, Phelps, KY 41553, USA | 2021-09-29
2021 | 2021-09-29 | Pikeville |  |  | 38821137B00434 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Phelps 632 Rd, Kentucky 41553, USA | 2021-09-29
2021 | 2021-09-30 | Pikeville |  |  | 38821137D00308 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 16 Mt Wolford Rd, Phelps, KY 41553, USA
2021 | 2021-10-04 | Pikeville |  |  | 37820009D00034 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | State Hwy 194 East, Jamboree, Ky. | 2021-10-04
2021 | 2021-10-04 | Pikeville | 84317676 | DKY0119434 | 37820009D00142 | TRUE | 3408303-COLEMAN / PETERCRK | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Crossarm brace broken | 35805 State Hwy. 194 East, Jamboree, Ky. | 2023-02-09
2021 | 2021-10-04 | Pikeville | 81201445 | DKY0115548 | 37820057A00071 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  | conductors: excessive splices, deteriorated conductors , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive poles and transformers. Poles 37820057A00071, 72, and 73 and wire which is rolled up around pole 72 | Allen Branch, State Hwy 194 E, Phelps, Ky. | 2022-01-11
2021 | 2021-10-04 | Pikeville |  |  | 38830954B40585 |  | EAST PRESTONSBURG - PRESTONSBURG / 4106-01 | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service Drop low at 9'-6" across front Yard and Driveway. RLC. Technician made filed trip. Customer had called in low service and a Servicer corrected the low clearance condition. RLC 10062021 | 116 Birch Oak Ln, Prestonsburg, KY 41653 | 2021-10-06
2021 | 2021-10-06 | Pikeville | 82294903 | DKY0116974 | 38831125C30017 | TRUE | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/melting | 136 Track Road, Harold, Ky.
2021 | 2021-10-06 | Pikeville |  |  | 38831125C30214 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Barn Branch Road, Harold, Ky. | 2021-10-06
2021 | 2021-10-06 | Pikeville |  |  | 38831125C30583 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Barn Branch Road, Harold, Ky. | 2021-10-06
2021 | 2021-10-07 | Pikeville |  |  | 38831124D00063 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  |  | KPC | NO | #4 copper neutral conductor down/missing. Vines covered pole | 444 Big Branch, Honaker, Ky.
2021 | 2021-10-07 | Pikeville | 86113094 | DKY0122282 | 38831124D00065 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer and secondary wire hanging down pole | 550 Big Branch, Honaker, Ky.
2021 | 2021-10-07 | Pikeville |  |  | 38831148000045 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  |  | KPC | NO | #4 copper neutral conductor down/missing between poles 45 and 46 | 947 Big Branch, Honaker, Ky.
2021 | 2021-10-12 | Pikeville |  |  | 38831052B00256 | TRUE | 3120101-STANVILLE/MUD CREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole | 255 Gunnell Branch, Dana, Ky.
2021 | 2021-10-12 | Pikeville |  |  | 38831052B00324 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole | 28 Rice Branch, Banner, Ky.
2021 | 2021-10-13 | Pikeville |  |  | 38831100000126 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole | 89 Lynn Hollow, Dana, KY.
2021 | 2021-10-13 | Pikeville |  |  | 38831100000211 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken on angle pole. Needs reattached. Probably need to install anchor. | 3699 Ky. Rte. 1426, Dana, Ky.
2021 | 2021-10-13 | Pikeville |  |  | 38831124A00023 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Pole top pin and insulator bent over | 1274 Samson Fork, Dana, Ky.
2021 | 2021-10-13 | Pikeville |  |  | 38831124B00028 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Samson Fork, Dana, Ky. | 2021-10-13
2021 | 2021-10-14 | Pikeville |  |  | 37830021000003 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Sturgill Branch, Harold, Ky. | 2021-10-14
2021 | 2021-10-14 | Pikeville |  |  | 38831125D00664 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Toler Creek, Harold, Ky. | 2021-10-14
2021 | 2021-10-14 | Pikeville |  |  | 38831125D00806 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Mellowbrook Lane, Harold, Ky. | 2021-10-14
2021 | 2021-10-18 | Pikeville |  |  | 38831125C10596 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Primary conductor floating on Capacitor pole. End of crossarm is split. Just before turnoff to Little Mud Creek. | Ky Rte. 979 , Harold, Ky.
2021 | 2021-10-20 | Pikeville |  |  | 38831078000104 |  | 3120102-STANVILLE/TRAM | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole | 2361 Mare Creek Road, Stanville, Ky.
2021 | 2021-10-20 | Pikeville |  |  | 38831078000181 |  | 3120102-STANVILLE/TRAM | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole | 2925 Mare Creek Road, Stanville, Ky.
2021 | 2021-10-20 | Pikeville |  |  | 38831101C10258 |  | 3120102-STANVILLE/TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Jacobs Street, Stanville, Ky. | 2021-10-20
2021 | 2021-10-21 | Pikeville |  |  | 38831077B00006 |  | 3120102-STANVILLE/TRAM | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm rotten/deteoriated | Blevins Road, Tram, Ky.
2021 | 2021-10-21 | Pikeville | 82578123 | DKY0117287 | 38831077B00148 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole is split. Pole top pin layer over. Pole was installed 1947, probably rotten at ground. Top of hill, mountain crossing in Tram. | 501 Main Street, Tram, Ky. | 2022-10-12
2021 | 2021-10-21 | Pikeville | 82630738 | DKY0117298 | 38831077D00093 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line | 125 Third Street, Tram, Ky. | 2022-09-16
2021 | 2021-10-28 | Pikeville |  |  | 38831101C40563 | TRUE | 3120103-STANVILLE/HAROLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator broken on step down pole. | 19 School St, Betsy Layne, KY 41605, USA
2021 | 2021-10-28 | Pikeville |  |  | 38831101C40564 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer is covered with vines | 71 School St, Betsy Layne, KY 41605, USA
2021 | 2021-10-29 | Pikeville |  |  | 38831102000012 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 879 Pike Floyd Hollow, Pikeville, KY 41501, USA | 2021-10-29
2021 | 2021-11-01 | Pikeville |  |  | 38831102000037 | TRUE | 3120103-STANVILLE/HAROLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Top of pole is split down to Xarm brace attachment point. | 794 Coldwater Branch, Betsy Layne, Ky.
2021 | 2021-11-01 | Pikeville |  |  | 38831102000041 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 1015 Coldwater Branch, Betsy Layne, Ky.
2021 | 2021-11-01 | Pikeville | 85864653 | DKY0121918 | 38831125C40615 | TRUE | 3120103-STANVILLE/HAROLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown on step down pole. | 120 Old County Road, Harold, Ky.
2021 | 2021-11-19 | Pikeville |  |  | 37830047A30576 |  | 3411701-CEDAR CREEK/HOOPWOOD | Line Work | UG |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Padmount transformer is partially buried. | 124 Magnolia Drive, Pikeville, Ky.
2021 | 2021-11-19 | Pikeville |  |  | 37830047A30630 |  | 3411701-CEDAR CREEK/HOOPWOOD | Line Work | UG |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Padmount transformer is nearly completely buried. | 134 Winston Drive, Pikeville, Ky.
2021 | 2021-11-19 | Pikeville |  |  | 38831150000060 |  | 3411702-CEDAR CREEK/IVY COURT | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm braces broken. Crossarm is tilted up. On hill just Above fire department. | 2835 Hurricane Creek, Pikeville, Ky.

## Ckt Defects Reported 2022 PKV
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2022 | 2022-01-03 | Pikeville |  |  | 37820055A40005 | TRUE | 3403801-SECONDFOR / DISTRIBUTION | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. Second pole out of station. | Second Fork, Biggs, KY.
2022 | 2022-01-04 | Pikeville |  |  | 37820055000017 |  | 3403801-SECONDFOR / DISTRIBUTION | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Second Fork, Biggs, Ky. | 2022-01-04
2022 | 2022-01-04 | Pikeville | 86180703 |  | 37820079000125 | TRUE | 3403801-SECONDFOR / DISTRIBUTION | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Second Fork, Biggs, Ky.
2022 | 2022-01-04 | Pikeville |  |  | 37820079000129 |  | 3403801-SECONDFOR / DISTRIBUTION | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Second Fork, Biggs, Ky
2022 | 2022-01-10 | Pikeville | 85533557 | DKY0121368 | 37820053000248 | TRUE | 3408402-KIMPER / GRAPEVINE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Primary phase hanging down pole. Needs to be cleared up for safety reasons. Both A and C phase reclosers are open on pole 37820053000280 but disconnects are closed. Probably has been left this way during storm. There’s a single phase tap pole that is by the road which is tagged as 248 but it’s tagged wrong according to Atlas. Pole 248 is the 3 phase pole underneath the road. | Millers Creek Road, Grapevine, Ky. | 2023-12-12
2022 | 2022-01-12 | Pikeville |  |  | 37820220C40941 |  | 3421001-BREAKS/CITY | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Ohio Street, Elkhorn City, Ky.
2022 | 2022-01-12 | Pikeville |  |  | 37820220C40942 |  | 3421001-BREAKS/CITY | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Ohio Street, Elkhorn City, Ky.
2022 | 2022-01-12 | Pikeville |  |  | 37820220D00817 |  | 3421001-BREAKS/CITY | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Secondary pole is leaning considerably | 750 Terry Taylor Road, Elkhorn City, KY.
2022 | 2022-01-12 | Pikeville |  |  | 37820221000003 |  | 3421001-BREAKS/CITY | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Inactive Service drop hanging down pole | 455 Upper Branch, Elkhorn City, Ky.
2022 | 2022-01-13 | Pikeville |  |  | 37820196B00022 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | 28 S Short St, Elkhorn City, KY 41522, USA | 2022-01-13
2022 | 2022-01-13 | Pikeville |  |  | 37820196B00199 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY-80, Elkhorn City, KY, USA | 2022-01-13
2022 | 2022-01-13 | Pikeville |  |  | 37820196B30058 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | KY-80, Elkhorn City, KY, USA | 2022-01-13
2022 | 2022-01-13 | Pikeville | 86179769 |  | 37820220C20668 | TRUE | 3421001-BREAKS/CITY | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken and hanging down pole. 3 phase road crossing. Will need new anchor installed. @ BP Double Kwik. | Pike St, Elkhorn City, KY 41522, USA
2022 | 2022-01-19 | Pikeville |  |  | 37820243C00296 |  | 3421001-BREAKS/CITY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Needs removed | 871 Kettlecamp Branch, Elkhorn City, Ky.
2022 | 2022-01-19 | Pikeville |  |  | 37820243D00018 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Water Branch, Elkhorn City, Ky. | 2022-01-19
2022 | 2022-01-19 | Pikeville |  |  | 37820244000045 | TRUE | 3421001-BREAKS/CITY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown on regulator pole. @ entrance road to Elkhorn Stone. On center phase. | Elkhorn Creek & KY-197, Elkhorn City, KY 41522, USA | 2023-10-19
2022 | 2022-01-25 | Pikeville |  |  | 37830312000111 |  | 3409502-BURDINE / LEVISA | Line Work | OH | crossarm/braces: broken/split | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Pole top broken out. This line is de-energized but the 3 phase crosses the main road, Ky. 197. If it falls , the conductors will be in road. Could cause vehicle accident.@ Elkhorn park, Upper Pigeon Road. Needs to be removed. | 12428 Elkhorn Creek, Pikeville, Ky.
2022 | 2022-01-25 | Pikeville | 86179471 |  | 37830335C00092 | TRUE | 3409502-BURDINE / LEVISA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators melting/ deteoriated | 36 Anderson Branch, Elkhorn Creek, Pikeville, Ky.
2022 | 2022-01-25 | Pikeville | 86186026 |  | 37830336000077 | TRUE | 3409502-BURDINE / LEVISA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator deteoriated | 14195 Elkhorn Creek, Pikeville, Ky.
2022 | 2022-01-26 | Pikeville | 86179447 |  | 37830335A00236 | TRUE | 3409502-BURDINE / LEVISA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 324 Contrary Hollow, Pikeville, Ky.
2022 | 2022-01-27 | Pikeville |  |  | 38830785D20340 |  | 3409001-W.PAINTSV / PAINTSVIL | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree limb hanging on phase wire. Could cause outage. | 447 Mill Street, Paintsville, Ky.
2022 | 2022-01-31 | Pikeville |  |  | 38830785D20275 |  | 3409003-W.PAINTSV / PLAZA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestors blown on transformer bank. @ Corner of Main & Church Street. | 457 Main Street, Paintsville, Ky.
2022 | 2022-02-10 | Pikeville |  |  | 38830737B40369 |  | 3409002-W.PAINTSV / STAFFORDSVILLE | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Secondary conductor sagged low. Needs slack taken out. | 72 Collins Drive, Wittensville, Ky.
2022 | 2022-02-14 | Pikeville |  |  | 38830828000177 |  | 3401101-FALCON / FALC-OILS | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 212 Horsepen Branch, Salyersville, Ky.
2022 | 2022-02-15 | Pikeville |  |  | 38830902000012 |  | 3401101-FALCON / FALC-OILS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Top of pole is rotten/split. Might be able to lower. Pole was installed 1952 | 1066 Narrows Branch, Riceville, Ky.
2022 | 2022-02-16 | Pikeville |  |  | 38830830000024 |  | 3401101-FALCON / FALC-OILS | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/ stolen | 11481 Ky. Rte. 825, Riceville, Ky.
2022 | 2022-02-17 | Pikeville |  |  | 38830806000141 |  | 3401101-FALCON / FALC-OILS | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Needs to be removed. | 343 Orchard Branch, Oil Springs, Ky.
2022 | 2022-02-18 | Pikeville |  |  | 38830877000044 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Beartree Fork, Salyersville, Ky. | 2022-02-18
2022 | 2022-02-21 | Pikeville | 83565072 | DKY0118285 | 38830901000041 |  | 3401103-FALCON / BURNINGFK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Needs to be removed. | 301 Dry Bread Fork, Salyersville, Ky. | 2022-10-26
2022 | 2022-02-21 | Pikeville |  |  | 38830925000081 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 1225 Big Lick Road, Salyersville, Ky.
2022 | 2022-02-23 | Pikeville |  |  | 38830900000023 |  | 3401103-FALCON / BURNINGFK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Howard Drive, Ivyton, Ky. | 2022-02-23
2022 | 2022-02-24 | Pikeville |  |  | 38830876D41040 |  | 3401103-FALCON / BURNINGFK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole | E Mountain Parkway, Salyersville, Ky.
2022 | 2022-02-24 | Pikeville |  |  | 38830901000116 |  | 3401103-FALCON / BURNINGFK | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Primary conductor floating | Short Fork, Salyersville, Ky.
2022 | 2022-02-25 | Pikeville |  |  | 38830876B00198 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire hanging down pole. Guy insulator is laying against transformer riser wire. Old road behind BP station. | 569 Old Burning Fork Road, Salyersville, Ky.
2022 | 2022-02-28 | Pikeville |  |  | 38830785C10571 |  | 3420101-MAYO TRAIL / NIPPA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Boyd Branch, Nippa,Ky. | 2022-02-28
2022 | 2022-03-02 | Pikeville |  |  | 38830809C40796 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | UG | UG conduit: damaged or separated |  |  | KPC | NO | Underground pedestal damaged by car. No lock on it. | 816 Point view Court, Paintsville, Ky.
2022 | 2022-03-03 | Pikeville |  |  | 38830851C00346 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Clifton Branch, Salyersville, Ky. | 2022-03-03
2022 | 2022-03-04 | Pikeville |  |  | 38830851B00233 |  | 3401102-FALCON / SALYERSVI | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Meade Branch, Salyersville, Ky.
2022 | 2022-03-04 | Pikeville |  |  | 38830851B00546 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Hall Street, Salyersville, Ky. | 2022-03-04
2022 | 2022-03-04 | Pikeville |  |  | 38830874000212 |  | 3401102-FALCON / SALYERSVI | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down pole. Needs removed. | 1128 Ky. Rte. 30 ,Salyersville, Ky.
2022 | 2022-03-07 | Pikeville |  |  | 38830826000041 |  | 3401102-FALCON / SALYERSVI | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Wire down from pole 41 to pole 46 in head of hollow. In-line dead-end cut at pole 42. Needs neutral put back to pole 42 and dead-end cut there and remove or clear up wire from pole 42 to 46.
2022 | 2022-03-07 | Pikeville |  |  | 38830875A00729 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dixie Addition, Salyersville, Ky. | 2022-03-07
2022 | 2022-03-08 | Pikeville |  |  | 38830875B00059 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | College Street, Salyersville, Ky. | 2022-03-08
2022 | 2022-03-08 | Pikeville |  |  | 38830875B00059 |  | 3401102-FALCON / SALYERSVI | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | College Street, Salyersville, Ky. | 2022-03-08
2022 | 2022-03-09 | Pikeville |  |  | 37820197000040 |  | 3403701-RUSSELLFO / LITTLEBEA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Little Beaver Road, Elkhorn City, Ky. | 2022-03-09
2022 | 2022-03-09 | Pikeville |  |  | 37820197000075 | TRUE | 3403701-RUSSELLFO / LITTLEBEA | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken | 645 Rfk Little Beaver, Elkhorn City, Ky.
2022 | 2022-03-09 | Pikeville |  |  | 37820197000202 |  | 3403701-RUSSELLFO / LITTLEBEA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Rfk Little Beaver, Elkhorn City, Ky.
2022 | 2022-03-10 | Pikeville |  |  | 37820123000120 |  | 3400702-DRAFFIN / YELLOWHIL | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Obey Fork, Harless Creek, Regina, Ky.
2022 | 2022-03-10 | Pikeville |  |  | 37820147A00496 |  | 3400702-DRAFFIN / YELLOWHIL | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 137 Plymale Branch, Regina, Ky.
2022 | 2022-03-10 | Pikeville |  |  | 37820147C00139 |  | 3400702-DRAFFIN / YELLOWHIL | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 1284 Jimmies Creek, Regina, Ky.
2022 | 2022-03-10 | Pikeville |  |  | 37820148000101 |  | 3400701-DRAFFIN / BELCHER | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Needs to be removed | 1769 Road Creek, Belcher, Ky.
2022 | 2022-03-11 | Pikeville | 84844179 | DKY0121362 | 37820172000232 | TRUE | 3400701-DRAFFIN / BELCHER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at ground line | 15667 Ferrells Creek Road, Belcher, Ky. | 2023-10-02
2022 | 2022-03-11 | Pikeville | 76958775 | DKY0111458 | 37820172000257 | TRUE | 3400701-DRAFFIN / BELCHER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line | 139 Blue Pond Fk. Belcher, Ky. | 2022-06-28
2022 | 2022-03-14 | Pikeville |  |  | 38820625B00016 | TRUE | 3411401-DEWEY / INEZ | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Pole top insulator is missing. Conductor tie wire is very close to pole top pin. | 9261 Yellow Creek, Inez, Ky.
2022 | 2022-03-15 | Pikeville |  |  | 37820125000204 |  | 3409402-FEDSCREEK / LICKCREEK | Service Work | OH | guys/anchors: broken or missing , service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Needs to be removed | Lfk Elswick Fk. Lick Creek, Ky.
2022 | 2022-03-15 | Pikeville |  |  | 37820149000015 |  | 3409402-FEDSCREEK / LICKCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is washed out around in the creek. Maybe only 2 ft in ground. | 1375 Rfk Abner Fork, Belcher, Ky.
2022 | 2022-03-15 | Pikeville |  |  | 37820172C10331 |  | 3409402-FEDSCREEK / LICKCREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Needs to be removed. | 1673 Old Ferrells Creek Road, Belcher, Ky.
2022 | 2022-03-16 | Pikeville | 76959048 | DKY0110550 | 37820126000133 | TRUE | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Top of pole is split. Could cause outage. | 22317 U.S. 460 , Mouthcard, Ky.
2022 | 2022-03-16 | Pikeville |  |  | 37820150000037 | TRUE | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 631 Big Card Creek, Mouthcard, Ky.
2022 | 2022-03-16 | Pikeville |  |  | 37820150000058 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 1950 Big Card Creek, Mouthcard, Ky.
2022 | 2022-03-16 | Pikeville |  |  | 37820150000064 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/ missing. #4 copper | 185 Slone Fork, Big Card Creek, Mouthcard, Ky.
2022 | 2022-03-16 | Pikeville |  |  | 37820151000083 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 651 Big Hackney Creek, Mouthcard, Ky.
2022 | 2022-03-16 | Pikeville | 86515659 |  | 37820151000173 | TRUE | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm is split. Could cause outage. Can’t see it unless using binoculars from road. | 1040 South River Road, Mouthcard, Ky.
2022 | 2022-03-17 | Pikeville |  |  | 37820103000051 | TRUE | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/missing | Miller Branch, Motley Fork, Mouthcard, Ky. | 2023-12-18
2022 | 2022-03-17 | Pikeville |  |  | 37820126000018 |  | 3409401-FEDSCREEK / FEDSCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 234 N Levisa Road, Mouthcard, Ky.
2022 | 2022-03-18 | Pikeville |  |  | 37820104000209 | TRUE | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Needs to be removed. Transformer is deenergized. | 565 Miller Fork, Fedscreek, Steele, Ky.
2022 | 2022-03-18 | Pikeville |  |  | 37820104000224 |  | 3409401-FEDSCREEK / FEDSCREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Needs to be removed. | 202 Millers Fork, Steele, Ky.
2022 | 2022-03-21 | Pikeville |  |  | 37820073A00043 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove pole hardware which is still attached to conductor. This use to be pole 73-A-44 and apparently has been broken on storm or something and hardware was left this way. @ Old Shelby Knoll, Shelbiana RR Yard, Pikeville, Ky. Line is de-energized @ 73-A-58 | Shelbiana, Ky.
2022 | 2022-03-21 | Pikeville | 83967750 | DKY0121106 | 37820097000026 | TRUE | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Crossarm is rotten/ deteoriated | 2173 Dry Fork, Shelbiana, Ky.
2022 | 2022-03-21 | Pikeville | 83967750 | DKY0121106 | 37820121000005 | TRUE | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken | 2293 Dry Fork, Shelbiana, Ky.
2022 | 2022-03-21 | Pikeville |  |  | 37830096D00337 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Old Shelbiana Road, Pikeville, Ky. | 2022-03-21
2022 | 2022-03-21 | Pikeville |  |  | 37830096D30449 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Old Shelbiana Road, Pikeville, Ky. | 2022-03-21
2022 | 2022-03-22 | Pikeville | 83967950 |  | 37830120D00060 | TRUE | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer with service drop hanging down pole. | 323 Collins Street, Pikeville, Ky.
2022 | 2022-03-22 | Pikeville |  |  | 37830144A00413 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Colley Hills, Pikeville, Ky. | 2022-03-22
2022 | 2022-03-22 | Pikeville |  |  | 37830144A00448 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Colley Hills, Pikeville, Ky. | 2022-03-22
2022 | 2022-03-22 | Pikeville |  |  | 37830144A00448 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Colley Hills, Pikeville, Ky. | 2022-03-22
2022 | 2022-03-23 | Pikeville |  |  | 37830144B00338 |  | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/ melting. @ Carl D. Perkins apt. bldg. | Douglas Parkway, Pikeville, Ky.
2022 | 2022-03-23 | Pikeville |  |  | 37830168000133 | TRUE | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator broken | U.S. Hwy. 23 S. Pikeville, Ky.
2022 | 2022-03-24 | Pikeville | 83967987 | DKY0121077 | 37830143C00003 | TRUE | 3411902-FORDSBRAN / ROBINSONC | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator deteoriated/damaged | 5595 Robinson Creek Road, Pikeville, Ky.
2022 | 2022-03-24 | Pikeville |  |  | 37830144A00062 |  | 3411902-FORDSBRAN / ROBINSONC | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Colley Hills Road, Pikeville, Ky. | 2022-03-24
2022 | 2022-03-28 | Pikeville | 84280948 | DKY0119339 | 38830834C00006 |  | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line | 665 Dicey Fork, Meally, Ky.
2022 | 2022-03-28 | Pikeville |  |  | 38830834C00326 | TRUE | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 481 Webb Hollow, Van Lear, Ky.
2022 | 2022-03-29 | Pikeville |  |  | 38830835000238 |  | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken. Hanging down pole. | 1060 Fitch Branch, Meally, Ky.
2022 | 2022-03-30 | Pikeville | 84262655 | DKY0119284 | 38830810B00197 |  | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line///THIS WAS COMPLETED ON DKY0119284/84262655 ON 1/31/23 BY TOMMY GOBLE | Roberts Branch, Davis Branch, Paintsville, Ky. | 2023-01-31
2022 | 2022-03-30 | Pikeville |  |  | 38830834A00062 | TRUE | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 253 N Buckingham Ave. W Van Lear, Ky.
2022 | 2022-03-30 | Pikeville |  |  | 38830834A00116 | TRUE | 3420103-MAYO TRAIL / DAVIS BR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarms are rotten. | Boyd St. Ky. 302 , West Van Lear, Ky.
2022 | 2022-04-04 | Pikeville |  |  | 37820073D00066 |  | 3411901-FORDSBRAN / SHELBY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Tom Adkins Rd, Kentucky 41562, USA | 2022-04-04
2022 | 2022-04-05 | Pikeville |  |  | 37820025C00168 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 679 Ivy Fork, Pikeville, Ky.
2022 | 2022-04-05 | Pikeville | 86529076 |  | 37820049000185 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at ground line | 457 Rfk Red Creek, Pikeville, Ky.
2022 | 2022-04-07 | Pikeville |  |  | 38820990D30194 |  | 3200302-BELFRY / TOLER | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Guy / Anchor washed / dozed out. | 434 Old Hardy Rd, Belfry, KY 41514, USA
2022 | 2022-04-12 | Pikeville |  |  | 38820990A00065 |  | 3200302-BELFRY / TOLER | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm broken on hill. This is a double arm. | 59 Beech Hollow, Forest Hills, Belfry, Ky.
2022 | 2022-04-12 | Pikeville | 77011832 | DKY0110363 | 38820991A00071 | TRUE | 3200302-BELFRY / TOLER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line | 569 Broadhead Hollow, Toler, KY 41514, USA | 2022-08-08
2022 | 2022-04-12 | Pikeville |  |  | 38821040A00038 |  | 3200302-BELFRY / TOLER | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/ missing. Down between poles 18 and 38. On left behind gray mobile home. | 158 Left Turkey Toe Branch, Hardy, KY 41531, USA
2022 | 2022-04-19 | Pikeville |  |  | 38821014B40125 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy wire needs marker | Mountain View Road, Belfry, Ky. | 2022-04-19
2022 | 2022-04-19 | Pikeville |  |  | 38821014B40259 |  | 3200301-BELFRY / BELFRY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Mountain View Road, Belfry, Ky. | 2022-04-19
2022 | 2022-04-25 | Pikeville |  |  | 37830214C00038 | TRUE | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilators deteoriated / melting | 1951 Ky. Hwy 610 West, Virgie, Ky.
2022 | 2022-04-25 | Pikeville | 83929228 | DKY0119923 | 37830214D00011 | TRUE | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NEEDS ADDITIONAL CHECK | Pole is washed out around in the Creek. In the station zone. Could cause outage. 4th pole out of the station. | Ky. Hwy 610 West, Virgie, Ky.
2022 | 2022-04-25 | Pikeville |  |  | 37830214D00071 | TRUE | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilators deteoriated/ melting | 84 Jonancy Bottom, Virgie, Ky.
2022 | 2022-04-27 | Pikeville |  |  | 37830167B00141 | TRUE | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Pole top pin layed way over. Angle pole. Could cause outage | Penny Street, Virgie, Ky.
2022 | 2022-04-27 | Pikeville |  |  | 37830167B00361 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 19 Bartley Hollow, Penny Road, Virgie, Ky.
2022 | 2022-04-27 | Pikeville |  |  | 37830167B00423 | TRUE | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign | NO | Tie wire is broken. Could cause outage | 303 Bartley Hollow, Virgie, Ky.
2022 | 2022-05-02 | Pikeville |  |  | 37830236000028 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Inactive service drop hanging down pole. Needs to be removed | Rfk Marshals Branch, Virgie, Ky.
2022 | 2022-05-04 | Pikeville | 86515583 |  | 37830166000024 | TRUE | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/ melted | Little Fork, Little Robinson Creek, Virgie, Ky.
2022 | 2022-05-04 | Pikeville |  |  | 37830189D20378 |  | 3401002-ELWOOD / VIRGIE-IN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop | 135 Curt Tackett Road, Virgie, Ky.
2022 | 2022-05-05 | Pikeville |  |  | 37830141000081 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral conductor down/ missing | 388 Mtn. view Drive, Tackett Fork, Beaver, Ky.
2022 | 2022-05-10 | Pikeville | 82275169 | DKY0116940 | 38821058B00015 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  |  | KPC | YES | Pole Rotten at Top |  | 2022-05-19
2022 | 2022-05-11 | Pikeville |  |  | 37830214D00006 | TRUE | 3401001-ELWOOD / DORTON | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown REPORTED BY D LEWIS on MAY 9, 2022 - added manually due to issues with app - prb | 63 Jonancy Bottom, Virgie, KY 41572, USA
2022 | 2022-05-11 | Pikeville |  |  | 37830238000098 |  | 3401001-ELWOOD / DORTON | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | REPORTED BY D LEWIS on MAY 9, 2022 - added manually due to issues with app - prb |  | 2022-05-09
2022 | 2022-05-11 | Pikeville |  |  | 37830310000086 |  | 3401001-ELWOOD / DORTON | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | REPORTED BY D LEWIS on MAY 9, 2022 - added manually due to issues with app - prb |  | 2022-05-09
2022 | 2022-05-13 | Pikeville | 82287882 | DKY0116962 | 38831078000032 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | Forestry - DESCRIBE IN COMMENTS | KPC | YES | Tree clearing for R/W | 50 Stratton Branch Rd, Stanville, KY 41659, USA | 2022-06-08
2022 | 2022-05-14 | Pikeville | 82294903 | DKY0116974 | 38831125C30017 | TRUE | 3120101-STANVILLE/MUD CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Turned in by Bobby Tackett | Track Rd
2022 | 2022-05-14 | Pikeville | 82301346 | DKY0118167 | 38831125C40409 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Turned in by Bobby Tackett | Track Rd
2022 | 2022-05-17 | Pikeville |  |  | 37830287000214 | TRUE | 3401001-ELWOOD / DORTON | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Lightning arrestor blown | 198 Three Mile Creek, Dorton, Ky.
2022 | 2022-05-18 | Pikeville |  |  | 38830654B00412 |  | 3401802-INDEX / HOSPITAL | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer is covered with vines | 87 Townhouse Lane, West Liberty, Ky.
2022 | 2022-05-19 | Pikeville |  |  | 38830654D00217 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Glenn Avenue, West Liberty, Ky. | 2022-05-19
2022 | 2022-05-19 | Pikeville |  |  | 38830654D30872 |  | 3401802-INDEX / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Liberty Heights Court, West Liberty, Ky. | 2022-05-19
2022 | 2022-05-19 | Pikeville |  |  | 38830655A00065 | TRUE | 3401802-INDEX / HOSPITAL | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 253 Walnut Road, West Liberty, Ky.
2022 | 2022-05-19 | Pikeville | 82356614 | DKY0117017 | 38830856000026 |  | 3409303-KENWOOD / HAGERHILL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 2792 Middle Fork | 2022-06-01
2022 | 2022-05-20 | Pikeville | 81328186 | DKY0117033 | 38821012A00029 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES |  | 468 N Big Creek Rd, Sidney, KY 41564, USA | 2023-06-08
2022 | 2022-05-23 | Pikeville |  |  | 38830801000030 |  | 3401801-INDEX / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 8195 U.S. 460, Winnie, Ky.
2022 | 2022-05-25 | Pikeville |  |  | 38830655B00281 |  | 3401801-INDEX / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown@ behind hardware store. | 919 Prestonsburg Street, West Liberty, Ky.
2022 | 2022-05-25 | Pikeville |  |  | 38830655B00369 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Dogwood Lane, West Liberty,Ky. | 2022-05-25
2022 | 2022-05-25 | Pikeville |  |  | 38830678C00108 | TRUE | 3401801-INDEX / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 154 Keaton Avenue, West Liberty, Ky.
2022 | 2022-05-26 | Pikeville | 82450831 | DKY0117093 | 38830853000055 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 3026 New Paintsville Rd, Salyersville, KY 41465, USA | 2022-08-17
2022 | 2022-05-26 | Pikeville | 82448864 | DKY0117092 | 38830853000057 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 3101 New Paintsville Rd, Salyersville, KY 41465, USA | 2022-08-09
2022 | 2022-05-31 | Pikeville |  |  | 38830678A00237 |  | 3401801-INDEX / DISTRIBUTION | Service Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Pole and transformer is covered with vines | 112 Melody Circle, West Liberty, Ky.
2022 | 2022-06-01 | Pikeville | 82479652 | DKY0117133 | 38830876B00026 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2022-07-14
2022 | 2022-06-01 | Pikeville | 82479577 | DKY0117132 | 38830876B00111 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole needs replaced. Ground line pole |  | 2022-07-14
2022 | 2022-06-02 | Pikeville |  |  | 38820941B00108 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | 553 Taylor Fork, Belfry, KY 41514, USA
2022 | 2022-06-02 | Pikeville |  |  | 38820941B00414 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer is covered with vines | Fletcher Hill, Nosben Fork, Belfry, Ky. | 2023-10-10
2022 | 2022-06-02 | Pikeville |  |  | 38820941B00435 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Taylor Fork, Turkey Creek, Belfry, Ky. | 2022-06-02
2022 | 2022-06-02 | Pikeville |  |  | 38820941D00294 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | Taylor Fork, Belfry, Ky. 41514
2022 | 2022-06-02 | Pikeville |  |  | 38820965A00005 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker (2) | Taylor Fork, Belfry, Ky.41514 | 2022-06-02
2022 | 2022-06-02 | Pikeville | 82496065 | DKY0117158 | 38820967a00096 |  | 3417601-NEW CAMP / SOUTH SIDE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | THIS WAS COMPLETED DKY0117158/82496065 ON 8/9/22 BY AUSTIN HALL | State Hwy 292 E, Kentucky 41514, USA | 2022-08-09
2022 | 2022-06-02 | Pikeville | 82496151 | DKY0117159 | 38820967A00305 |  | 3417601-NEW CAMP / SOUTH SIDE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | THIS WAS COMPLETED DKY0117490/82829617 ON 8/9/22 BY AUSTIN HALL |  | 2022-08-09
2022 | 2022-06-03 | Pikeville |  |  | 38820941D00208 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | 639 Turkey Creek Rd, Belfry, KY 41514, USA
2022 | 2022-06-03 | Pikeville | 84150341 | DKY0119119 | 38820964D00081 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole washed out in creek | 5455 Turkey Creek Rd, Belfry, KY 41514, USA | 2023-01-17
2022 | 2022-06-03 | Pikeville |  |  | 38820989B00308 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole | 429 Flower Garden Hollow, Turkey Creek, KY 41514, USA
2022 | 2022-06-06 | Pikeville |  |  | 38820942B20018 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO |  | Central Avenue, Belfry, Ky. | 2022-06-06
2022 | 2022-06-06 | Pikeville |  |  | 38820942B20078 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace is broken.@ New Camp Loop. On hill | 750 SR 292, Belfry, Ky.
2022 | 2022-06-07 | Pikeville |  |  | 38820942B41434 |  | 3417601-NEW CAMP / SOUTH SIDE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Appalachian Plaza, Belfry, Ky. | 2022-06-07
2022 | 2022-06-07 | Pikeville |  |  | 38820942B41445 |  | 3417601-NEW CAMP / SOUTH SIDE | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | Appalachian Plaza, Belfry, Ky.
2022 | 2022-06-07 | Pikeville |  |  | 38820966A32769 |  | 3417601-NEW CAMP / SOUTH SIDE | Line Work | UG | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NEEDS ADDITIONAL CHECK | Padmount transformer doesn’t have a pad underneath@ Long John Silvers | Appalachian Plaza, Belfry, Ky.
2022 | 2022-06-08 | Pikeville |  |  | 38820966A40616 |  | 3417601-NEW CAMP / SOUTH SIDE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown on transformer bank @ McDonalds | Southside Mall, Belfry, Ky.
2022 | 2022-06-09 | Pikeville |  |  | 38830858A00090 |  | 3409301-KENWOOD / WVANLEAR | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | 109 Carnell Lane, Van Lear, Ky.
2022 | 2022-06-09 | Pikeville |  |  | 38830858B00236 |  | 3409301-KENWOOD / WVANLEAR | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Industrial Park, Van Lear, Ky. | 2022-06-09
2022 | 2022-06-10 | Pikeville | 82573942 | DKY0117234 | 38820990D20403 |  | 3200302-BELFRY / TOLER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2022-08-18
2022 | 2022-06-13 | Pikeville |  |  | 38830837D00066 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines.@ Ky. Rte. 3 | Middle Fork Road, Inez, Ky..
2022 | 2022-06-13 | Pikeville |  |  | 38830839A00018 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | Mudlick Branch, Ky. Rte. 3 , Davella, Ky.
2022 | 2022-06-13 | Pikeville |  |  | 38830851B00458 |  | 3401102-FALCON / SALYERSVI | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 124 flint br
2022 | 2022-06-13 | Pikeville |  |  | 38830861000029 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | Airport Road, Inez, Ky.
2022 | 2022-06-13 | Pikeville |  |  | 38830861000031 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | Airport Road, Inez, Ky.
2022 | 2022-06-13 | Pikeville |  |  | 38830861A30175 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Airport Road, Inez, Ky. | 2022-06-13
2022 | 2022-06-13 | Pikeville |  |  | 38830861C20126 |  | 3411401-DEWEY / INEZ | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken | Industrial Drive, Inez, Ky.
2022 | 2022-06-14 | Pikeville | 82674650 | DKY0117336 | 38821014A00049 |  | 3200301-BELFRY / BELFRY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES |  | 49 Pine Street Belfry | 2022-08-17
2022 | 2022-06-14 | Pikeville |  |  | 38830814D00020 |  | 3411401-DEWEY / INEZ | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarms are deteoriated | Davella Road, Davella, Ky.
2022 | 2022-06-14 | Pikeville |  |  | 38830814D00071 | TRUE | 3411401-DEWEY / INEZ | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 457 Setser Branch, Davella, Ky.
2022 | 2022-06-15 | Pikeville |  |  | 38830767D00062 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Fairview Farm Lane, Inez, Ky. | 2022-06-15
2022 | 2022-06-15 | Pikeville |  |  | 38830791B00064 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Newsome Road, Inez, Ky. | 2022-06-15
2022 | 2022-06-15 | Pikeville |  |  | 38830791B00086 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | Blackberry Road, Inez, Ky.
2022 | 2022-06-15 | Pikeville |  |  | 38830791B00181 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | Middle Fork Road, Ky. Rte. 3, Inez, Ky.
2022 | 2022-06-15 | Pikeville |  |  | 38830791C00164 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Blackburn Trailer Park, Inez, Ky. | 2022-06-15
2022 | 2022-06-16 | Pikeville |  |  | 37830335D00209 |  | 3409502-BURDINE / LEVISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES |  | 16187 Elkhorn Creek
2022 | 2022-06-16 | Pikeville |  |  | 38830742D00025 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/ missing | 251 Upper Wolf Branch, Tomahawk, Ky.
2022 | 2022-06-16 | Pikeville |  |  | 38830766A00037 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Hinkle Loop, Tomahawk, Ky. | 2022-06-16
2022 | 2022-06-16 | Pikeville |  |  | 38830766C00104 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Horse Branch, Tomahawk, Ky. | 2022-06-16
2022 | 2022-06-16 | Pikeville |  |  | 38830767C00014 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Saltwell Branch, Inez, Ky. | 2022-06-16
2022 | 2022-06-16 | Pikeville |  |  | 38830767C00141 |  | 3411401-DEWEY / INEZ | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen | Otto Drive, Inez, Ky. | 2022-06-16
2022 | 2022-06-21 | Pikeville |  |  | 38830766D00071 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Trace Fork, Tomahawk, Ky. | 2022-06-21
2022 | 2022-06-21 | Pikeville |  |  | 38830790C00103 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Ponderosa Drive, Tomahawk, Ky. | 2022-06-21
2022 | 2022-06-22 | Pikeville | Trouble ticket # 4274351 |  | 38830768C00110 |  | 3411401-DEWEY / INEZ | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Customer service pole rotted and about to fall. Service drop laying on the ground. Contacted DDC to have trouble ticket sent to servicer. Servicer arrived and corrected the unsafe condition by opening the transformer and cutting service loose from customers service pole so customer can replace. Customer will call back for service when ready. | 11 Upper James Lane, Coldwater Road, Inez, Ky. | 2022-06-22
2022 | 2022-06-22 | Pikeville |  |  | 38830768C00115 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Camp Branch, Inez, Ky. | 2022-06-22
2022 | 2022-06-22 | Pikeville |  |  | 38830768D00144 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | No guy marker | Moore Branch, Inez, Ky. | 2022-06-22
2022 | 2022-06-22 | Pikeville |  |  | 38830768D00213 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | No guy marker | Cardinal Estates, Inez, Ky. | 2022-06-22
2022 | 2022-06-22 | Pikeville |  |  | 38830768D00214 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | No guy marker | Cardinal Estates, Inez, Ky. | 2022-06-22
2022 | 2022-06-22 | Pikeville |  |  | 38830792C00017 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Moore Branch, Inez, Ky. | 2022-06-22
2022 | 2022-06-22 | Pikeville |  |  | 38830792C00066 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | No guy marker | Cassidy Road, Inez, Ky. | 2022-06-22
2022 | 2022-06-22 | Pikeville |  |  | 38830792D00039 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | No guy marker | Collins Road, Inez, Ky. | 2022-06-22
2022 | 2022-06-22 | Pikeville |  |  | 38830792D00095 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | No guy marker | Collins Road, Inez, Ky. | 2022-06-22
2022 | 2022-06-23 | Pikeville |  |  | 38830816B00048 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker (2) | Glenn Road, Inez, Ky. | 2022-06-23
2022 | 2022-06-23 | Pikeville |  |  | 38830816C00069 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | No guy marker | Coldwater Road, Inez, Ky. | 2022-06-23
2022 | 2022-06-27 | Pikeville |  |  | 38820769C00047 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | No guy marker | Little Rockcastle, Inez, Ky. | 2022-06-27
2022 | 2022-06-28 | Pikeville |  |  | 38830743C00001 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Kentucky Avenue, Inez, Ky. | 2022-06-28
2022 | 2022-06-28 | Pikeville |  |  | 38830743C00010 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Penix Drive, Inez, Ky. | 2022-06-28
2022 | 2022-06-28 | Pikeville |  |  | 38830743C00146 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Penix Drive, Inez, Ky. | 2022-06-28
2022 | 2022-06-28 | Pikeville |  |  | 38830744A20388 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | No guy marker (2) | New berry Lane, Inez, Ky. | 2022-06-28
2022 | 2022-06-28 | Pikeville |  |  | 38830767C00137 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | No guy marker (2) | Lower Saltwell, Inez, Ky. | 2022-06-28
2022 | 2022-06-28 | Pikeville |  |  | 38830768A00237 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer is covered with vines | Boone Branch, Inez, Ky.
2022 | 2022-06-28 | Pikeville |  |  | 38830768A00347 |  | 3411401-DEWEY / INEZ | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Angle pin/ insulator layer way over. Could cause outage. | Eli Road, Inez, Ky.
2022 | 2022-06-29 | Pikeville |  |  | 38830720C00053 |  | 3411401-DEWEY / INEZ | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Primary conductor has strands broken and stretched out. Could cause outage. Pictures don’t show it very good. | Union Road, Turkey Creek, Inez, Ky.
2022 | 2022-06-29 | Pikeville | WR 82560839 |  | 38830720D00099 |  | 3411401-DEWEY / INEZ | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | BOTH CROSSARM BRACES BROKEN..@ about two miles up Turkey Creek. Called SDS to have crew make repairs. Repairs completed next day. | Turkey Creek, Inez, Ky. | 2022-07-01
2022 | 2022-06-29 | Pikeville |  |  | 38830744C00315 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Horn Branch, Inez, Ky. | 2022-06-29
2022 | 2022-06-30 | Pikeville |  |  | 38820625B00001 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Fluty Lick Cemetery Road, Inez, Ky. | 2022-06-30
2022 | 2022-06-30 | Pikeville |  |  | 38820673A00198 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Turkey Creek, Inez, Ky. | 2022-06-30
2022 | 2022-07-05 | Pikeville |  |  | 38820601C00173 |  | 3411401-DEWEY / INEZ | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer is covered with vines | 5411 Yellow Creek Road, Inez, Ky,
2022 | 2022-07-05 | Pikeville |  |  | 38820625B00016 | TRUE | 3411401-DEWEY / INEZ | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Loop insulator is broken/ missing. Could cause outage. Only about one inch from contacting pole top pin. | 9261 Yellow Creek Road, Inez, Ky.
2022 | 2022-07-07 | Pikeville |  |  | 38830695C00052 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Johnson Bottom, Inez, Ky. | 2022-07-07
2022 | 2022-07-07 | Pikeville |  |  | 38830695C00079 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Johnson Bottom, Inez, Ky. | 2022-07-07
2022 | 2022-07-07 | Pikeville |  |  | 38830695C00079 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Johnson Bottom, Inez, Ky. | 2022-07-07
2022 | 2022-07-07 | Pikeville |  |  | 38830695C00105 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Johnson Bottom, Inez, Ky. | 2022-07-07
2022 | 2022-07-07 | Pikeville |  |  | 38830696A00035 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Big Lick Road, Inez, Ky. | 2022-07-07
2022 | 2022-07-07 | Pikeville |  |  | 38830696A00052 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Big Lick Road, Inez, Ky. | 2022-07-07
2022 | 2022-07-07 | Pikeville |  |  | 38830696A00063 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Samson Fork Inez, Ky. | 2022-07-07
2022 | 2022-07-07 | Pikeville |  |  | 38830696A00074 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Big Lick Road, Inez, Ky. | 2022-07-07
2022 | 2022-07-07 | Pikeville |  |  | 38830696A00080 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Samson Fork, Inez, Ky. | 2022-07-07
2022 | 2022-07-08 | Pikeville |  |  | 38820745B00044 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Patrick Lane, Inez, Ky. | 2022-07-08
2022 | 2022-07-08 | Pikeville |  |  | 38820769C00011 |  | 3411401-DEWEY / INEZ | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken on hill across from Albert Pinson Road. No truck | 5434 Ky. Rte 40, Inez, Ky.
2022 | 2022-07-08 | Pikeville |  |  | 38820771B10190 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker (2) | Wolf Creek, Lovely, Ky. | 2022-07-08
2022 | 2022-07-08 | Pikeville |  |  | 38830744D00359 |  | 3411401-DEWEY / INEZ | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Coldwater Road, Inez, Ky. | 2022-07-08
2022 | 2022-07-11 | Pikeville |  |  | 38820771B10465 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker (2) | N Wolf Creek, Lovely, Ky. | 2022-07-11
2022 | 2022-07-11 | Pikeville |  |  | 38830936C00031 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Meathouse Road, Lovely, Ky. | 2022-07-11
2022 | 2022-07-12 | Pikeville |  |  | 37820030000086 | TRUE | 3411802-JOHNSCREE / RACCOON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO |  |  | 2022-07-13
2022 | 2022-07-12 | Pikeville |  |  | 38820770B00147 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Little Peter Cave Road, Lovely, Ky. | 2022-07-12
2022 | 2022-07-12 | Pikeville |  |  | 38820770D00061 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | N Wolf Creek, Inez, Ky. | 2022-07-12
2022 | 2022-07-12 | Pikeville | 73374704 | DKY0105275 | 38830832000021 |  | 3409303-KENWOOD / HAGERHILL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2022 | 2022-07-13 | Pikeville | 82801737 | DKY0117463 | 37820030000086 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 1031 Long Fork Rd Kimper | 2022-08-18
2022 | 2022-07-13 | Pikeville |  |  | 38820794D00259 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Wolf Creek, Lovely, Ky. | 2022-07-13
2022 | 2022-07-13 | Pikeville |  |  | 38820818C00010 | TRUE | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer and service drop hanging down pole | 56 White Oak Branch, Lovely, Ky.
2022 | 2022-07-13 | Pikeville |  |  | 38820819A00015 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Emily Creek, Lovely, Ky. | 2022-07-13
2022 | 2022-07-13 | Pikeville |  |  | 38820819C00037 | TRUE | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 2850 Emily Creek, Lovely, Ky.
2022 | 2022-07-13 | Pikeville |  |  | 38820819C00072 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Emily Creek, Lovely, Ky. | 2022-07-13
2022 | 2022-07-13 | Pikeville |  |  | 38820819C00072 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Emily Creek, Lovely, Ky. | 2022-07-13
2022 | 2022-07-14 | Pikeville |  |  | 38820841A00040 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarms broken about 200 yards back on hill..It’s 3 phase line but only the center phase is energized. The two outside phases are de-energized @pole 38820841A00063. It’s probably been left this way during storm. Located just below Dye Bottom and recloser pole 38820841A00146. It’s the very end of the three phase line. Contacted the SDS to determine how to proceed. | S Wolf Creek, Lovely, Ky.
2022 | 2022-07-14 | Pikeville |  |  | 38820841B00056 | TRUE | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 3850 S Wolf Creek, Lovely, Ky.
2022 | 2022-07-18 | Pikeville |  |  | 38820818B00149 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Dans Branch, Pigeonroost, Pilgrim, Ky. | 2022-07-18
2022 | 2022-07-18 | Pikeville |  |  | 38820818B00149 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Dans Branch, Pigeonroost, Pilgrim, Ky. | 2022-07-18
2022 | 2022-07-18 | Pikeville |  |  | 38820841C00196 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Anchor rod rusted and pulled out of the ground. | Big Peter Cave Road, Pigeonroost, Pilgrim, Ky.
2022 | 2022-07-18 | Pikeville |  |  | 38820842A00019 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken, hanging down pole | 2096 Pigeonroost Road, Pilgrim, Ky.
2022 | 2022-07-18 | Pikeville |  |  | 38820842A00038 | TRUE | 3202202-LOVELY / WOLFCREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken | 469 Big Peter Cave Road, Pilgrim, Ky.
2022 | 2022-07-18 | Pikeville |  |  | 38820890C00072 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Lick Fork, Pigeonroost, Pilgrim, Ky. | 2022-07-18
2022 | 2022-07-19 | Pikeville |  |  | 38820794B00088 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Little Rockcastle, Inez, Ky. | 2022-07-19
2022 | 2022-07-19 | Pikeville |  |  | 38820794B00088 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Little Rockcastle, Inez, Ky. | 2022-07-19
2022 | 2022-07-19 | Pikeville |  |  | 38820794B00147 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Little Rockcastle, Inez, Ky. | 2022-07-19
2022 | 2022-07-19 | Pikeville |  |  | 38820818A00075 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Frog Pond Road, Little Rockcastle, Inez, Ky.
2022 | 2022-07-19 | Pikeville |  |  | 38820890C00025 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 758 Caney Fork, Pigeonroost, Pilgrim, Ky.
2022 | 2022-07-20 | Pikeville |  |  | 38820817D00034 |  | 3202202-LOVELY / WOLFCREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | S Wolf Creek, Lovely, Ky. | 2022-07-20
2022 | 2022-07-20 | Pikeville |  |  | 38820818A00183 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is completely covered with vines | 3990 Little Rockcastle, Inez, Ky.
2022 | 2022-07-20 | Pikeville |  |  | 38820818A00213 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | S Wolf Creek, Lovely, Ky.
2022 | 2022-07-20 | Pikeville |  |  | 38830818A00230 |  | 3202202-LOVELY / WOLFCREEK | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | 467 S Wolf Creek, Lovely, Ky.
2022 | 2022-07-21 | Pikeville |  |  | 38830858B30235 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. First pole outside station. | Hager Hill, Ky. | 2022-07-21
2022 | 2022-07-22 | Pikeville |  |  | 38830858B00362 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Homestead Lane, Prestonsburg, Ky. | 2022-07-22
2022 | 2022-07-22 | Pikeville |  |  | 38830882A00453 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker Airport Drive, Auxier, Ky. |  | 2022-07-22
2022 | 2022-07-25 | Pikeville |  |  | 38830882C00468 |  | 3409302-KENWOOD / AUXIER | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | DANGER TREE. Leaning over single phase. | 321 Jockey Hollow, Auxier, Ky. | 2023-10-10
2022 | 2022-07-25 | Pikeville |  |  | 38830882D00051 |  | 3409302-KENWOOD / AUXIER | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines. Pole 81 and 50 also. On hill behind RR tracks | Spradlin Street, Auxier, Ky.
2022 | 2022-07-25 | Pikeville |  |  | 38830882D00104 |  | 3409302-KENWOOD / AUXIER | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | Patton Hollow Road, Auxier, Ky.
2022 | 2022-07-26 | Pikeville |  |  | 38830882D00090 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | 2nd Avenue, Auxier, Ky. | 2022-07-26
2022 | 2022-07-26 | Pikeville |  |  | 38830882D00442 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | 2nd Avenue, Auxier, Ky. | 2022-07-26
2022 | 2022-07-27 | Pikeville |  |  | 38830881000074 |  | 3409302-KENWOOD / AUXIER | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree Laying on secondary and primary neutral…Contacted the SDS to have it removed. | 430 Hager Branch, East Point, Ky.
2022 | 2022-07-27 | Pikeville |  |  | 38830881000078 |  | 3409302-KENWOOD / AUXIER | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator deteoriated/melted | 660 Hager Branch, East Point, Ky.
2022 | 2022-08-01 | Pikeville |  |  | 38830881000037 |  | 3409302-KENWOOD / AUXIER | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/ missing | Bear Hollow, Kentucky 41216, USA
2022 | 2022-08-01 | Pikeville |  |  | 38830882A00067 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | East Point, Prestonsburg, Ky. | 2022-08-01
2022 | 2022-08-01 | Pikeville |  |  | 38830905B40153 |  | 3409302-KENWOOD / AUXIER | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 930 Lfk Little Paint, Prestonsburg, Ky.
2022 | 2022-08-01 | Pikeville |  |  | 38830905B40237 |  | 3409302-KENWOOD / AUXIER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Little Paint Rd, Kentucky 41216, USA | 2022-08-01
2022 | 2022-08-02 | Pikeville |  |  | 38830833C00529 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Rolling Hills, Hager Hill, Ky. | 2022-08-02
2022 | 2022-08-02 | Pikeville |  |  | 38830858B30895 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. First pole outside station | Prestonsburg, KY 41653, USA | 2022-08-02
2022 | 2022-08-03 | Pikeville |  |  | 38830832000092 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Johnson Branch, Collista, Ky. | 2022-08-03
2022 | 2022-08-03 | Pikeville |  |  | 38830832000092 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Johnson Branch, Collista, Ky. | 2022-08-03
2022 | 2022-08-03 | Pikeville |  |  | 38830832C10153 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Ky. 2039, Riceville, Ky. | 2022-08-03
2022 | 2022-08-03 | Pikeville |  |  | 38830833A10667 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Ky. 825, Collista, Ky. | 2022-08-03
2022 | 2022-08-03 | Pikeville |  |  | 38830833A20614 |  | 3409303-KENWOOD / HAGERHILL | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | Tackett Branch, Collista, Ky. | 2023-11-08
2022 | 2022-08-03 | Pikeville |  |  | 38830858A00182 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground cut on switch pole. | Industrial Park Drive, Hager Hill, Ky. | 2022-08-03
2022 | 2022-08-03 | Pikeville |  |  | 38830858A00932 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen | Industrial Park Dr, Kentucky 41222, USA | 2022-08-03
2022 | 2022-08-04 | Pikeville | 83079084 | DKY0117640 | 38820917C00319 |  | 2150502-BORDERLAND/CHATTAROY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 4280 State Hwy 292 W | 2022-09-19
2022 | 2022-08-04 | Pikeville |  |  | 38830880000019 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Middle Fork, Paintsville, Ky. | 2022-08-04
2022 | 2022-08-08 | Pikeville |  |  | 38830857000090 |  | 3409303-KENWOOD / HAGERHILL | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | 520 Little Lick Fork, East Point, Ky.
2022 | 2022-08-09 | Pikeville |  |  | 38830880000050 |  | 3409303-KENWOOD / HAGERHILL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Ky. Rte. 1750, Hager Hill, Ky. | 2022-08-09
2022 | 2022-08-10 | Pikeville |  |  | 37830240000102 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Little Fork, Pikeville, Ky. | 2022-08-10
2022 | 2022-08-11 | Pikeville |  |  | 37830239C10024 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 981 Lizzie Fork, Pikeville, Ky.
2022 | 2022-08-12 | Pikeville |  |  | 37830240000094 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 245 Rockhouse Road, Pikeville, Ky.
2022 | 2022-08-12 | Pikeville |  |  | 37830240000155 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 424 Rockhouse Road, Pikeville, Ky.
2022 | 2022-08-12 | Pikeville |  |  | 37830263C00165 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Secondary pole leaning badly. In a slide area. Transformer is de-energized. Inactive account. Needs to be removed. @ Old Dorton Road, Dorton Hill. | Dorton Hill, Pikeville, Ky.
2022 | 2022-08-15 | Pikeville |  |  | 37830263D00108 | TRUE | 3401702-HENRYCLAY / REGINA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 1349 Dorton Creek, Pikeville, Ky.
2022 | 2022-08-15 | Pikeville |  |  | 37830263D00108 | TRUE | 3401702-HENRYCLAY / REGINA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 1293 Dorton Creek, Pikeville, Ky
2022 | 2022-08-16 | Pikeville |  |  | 37820169000038 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Rockhouse Fork, Regina, Ky. | 2022-08-16
2022 | 2022-08-16 | Pikeville |  |  | 37820169000038 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Rockhouse Fork, Regina, Ky. | 2022-08-16
2022 | 2022-08-16 | Pikeville |  |  | 37820169000217 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Wire hanging down pole on hill. De-energized @ 169-54 on step down pole. | 394 Rfk Rockhouse, Regina, Ky.
2022 | 2022-08-16 | Pikeville |  |  | 37820169000234 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop hanging down pole on hill. Transformer is de-energized. | 139 Rfk Rockhouse, Regina, Ky.
2022 | 2022-08-16 | Pikeville |  |  | 37820193D00016 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Marrowbone Creek Road, Pikeville, Ky. | 2022-08-16
2022 | 2022-08-16 | Pikeville |  |  | 37820194A00330 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown on step down transformer | Bad Fork, Rockhouse, Regina, Ky.
2022 | 2022-08-17 | Pikeville |  |  | 37820121000074 |  | 3401702-HENRYCLAY / REGINA | Forestry | OH |  |  | Circuit has since been sprayed after reported date | KPC | NO | Pole is covered with vines | Greasy Creek, Shelbiana, Ky. | 2023-09-30
2022 | 2022-08-17 | Pikeville |  |  | 37820121000113 |  | 3411901-FORDSBRAN / SHELBY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral conductor down beside road. Contacted DDC to have trouble ticket made. Contacted SDS to have repairs made. | 2247 Greasy Creek Road, Pikeville, Ky.
2022 | 2022-08-17 | Pikeville |  |  | 37820145000225 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop hanging down pole. | 645 Gardner Fork, Shelbiana, Ky.
2022 | 2022-08-17 | Pikeville |  |  | 37830192000006 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 924 Rfk Greasy Creek, Shelbiana, Ky.
2022 | 2022-08-22 | Pikeville |  |  | 37820145000030 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Primary and neutral, low clearance near garbage dump. Between poles 29 and 30. @ top of hill between Wolfpit and Kendrick Fork of Greasy Creek. | Wolfpit Branch, Regina, Ky.
2022 | 2022-08-22 | Pikeville |  |  | 37820170000027 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/ melted | 1455 Marrowbone Creek Road, Regina, Ky.
2022 | 2022-08-22 | Pikeville |  |  | 37820170000062 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Marrowbone Creek Road, Regina, Ky. | 2022-08-22
2022 | 2022-08-22 | Pikeville |  |  | 37820170A30604 |  | 3401702-HENRYCLAY / REGINA | Line Work | OH | cutout: damaged |  |  | KPC | NO | Transformer cutout is broken. No truck. Inactive account. | 955 Wolfpit Branch, Regina, Ky.
2022 | 2022-08-23 | Pikeville |  |  | 37820098C00063 |  | 3401702-HENRYCLAY / REGINA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Rocky Road, Pikeville, Ky. | 2022-08-23
2022 | 2022-08-23 | Pikeville |  |  | 37820099000003 |  | 3401702-HENRYCLAY / REGINA | Forestry | OH |  |  | Circuit has since been sprayed after reported date | KPC | NO | Pole is covered with vines | 1706 Rocky Rd, Pikeville, KY 41501, USA | 2023-09-30
2022 | 2022-08-25 | Pikeville |  |  | 37820122000043 | TRUE | 3401702-HENRYCLAY / REGINA | Forestry | OH |  |  | Circuit has since been sprayed after reported date | KPC | NO | Pole is covered with vines | 276 Winston Branch, Pikeville, KY 41501, USA | 2023-09-30
2022 | 2022-08-26 | Pikeville | 83246117 | DKY0117804 | 38821111A00129 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2022-09-09
2022 | 2022-08-29 | Pikeville |  |  | 37820217B00047 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Switch pole is completely covered with vines | 1134 Bowling Fork Rd, Elkhorn City, KY 41522, USA
2022 | 2022-08-29 | Pikeville |  |  | 37820218000019 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator is broken. Could cause outage | Brushy Fork Hellier, Elkhorn City, Ky.
2022 | 2022-08-29 | Pikeville |  |  | 37820241C00125 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator is broken. Could cause outage. @ Hellier Missionary Baptist Church | 8405 Allegheny Road, Elkhorn City, Ky.
2022 | 2022-08-29 | Pikeville |  |  | 37830240000128 |  | 3401703-HENRYCLAY / ASHCAMP | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker (2) | Pikeville, KY 41501, USA | 2022-08-29
2022 | 2022-08-30 | Pikeville | 86032043 | DKY0122140 | 37820242000099 | TRUE | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator is broken | 10624 Ashcamp Branch, Elkhorn City, Ky. | 2023-10-17
2022 | 2022-08-30 | Pikeville |  |  | 37820267000006 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop is tied to a tree. Clearance issue. Probably need secondary pole installed or slack taken out. | 111 Adkins-Belcher Road, Elkhorn City, Ky.
2022 | 2022-08-30 | Pikeville | 86688322 | DKY0123329 | 37820267000008 | TRUE | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | End of crossarm is rotted/ split. Arm pin is layer over. Could cause outage | Spa Court, Elkhorn Creek, Elkhorn City, Ky. | 2023-12-18
2022 | 2022-08-31 | Pikeville | 86515583 |  | 37820265B00029 | TRUE | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated / melting | 500 Sycamore Road, Elkhorn City, Ky.
2022 | 2022-08-31 | Pikeville |  |  | 37820265C00088 |  | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 387 Marion Branch, Elkhorn City, Ky.
2022 | 2022-08-31 | Pikeville | 86529474 |  | 37820266000026 | TRUE | 3401703-HENRYCLAY / ASHCAMP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | lightning arresters/insulators: damaged |  | Foreign | YES | Pole is rotten at ground line. Epoxilators are deteoriated/melted | 7057 Elkhorn Creek, Elkhorn City, Ky.
2022 | 2022-09-06 | Pikeville |  |  | 38820795C00084 |  | 3202203-LOVELY / MT.STERLINGBR. | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | State Hwy 292, Lovely, Ky. | 2022-09-06
2022 | 2022-09-06 | Pikeville |  |  | 38820820A00168 |  | 3202203-LOVELY / MT.STERLINGBR. | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs marker | Long Branch, Lovely, Ky. | 2022-09-06
2022 | 2022-09-06 | Pikeville |  |  | 38820820A00172 |  | 3202203-LOVELY / MT.STERLINGBR. | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Inactive transformer. Needs to be removed | 1066 Long Branch, Lovely, Ky.
2022 | 2022-09-06 | Pikeville |  |  | 38820820A00174 |  | 3202203-LOVELY / MT.STERLINGBR. | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer. Needs to be removed | 1342 Long Branch, Lovely, Ky.
2022 | 2022-09-06 | Pikeville |  |  | 38820820A00189 |  | 3202203-LOVELY / MT.STERLINGBR. | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy markers (2) | Long Branch, Lovely, Ky. | 2022-09-06
2022 | 2022-09-06 | Pikeville |  |  | 38820820B21781 | TRUE | 3202203-LOVELY / MT.STERLINGBR. | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service drop hanging down pole. Needs to be removed. | 210 Russell Workman Road, Lovely, Ky.
2022 | 2022-09-07 | Pikeville |  |  | 38820820C40080 | TRUE | 3202203-LOVELY / MT.STERLINGBR. | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 7815 State Hwy 292, Lovely, Ky.
2022 | 2022-09-07 | Pikeville |  |  | 38820820D00144 |  | 3202203-LOVELY / MT.STERLINGBR. | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole is split. River crossing. Could cause outage. | 7981 State Hwy 292, Lovely, Ky.
2022 | 2022-09-07 | Pikeville | 83314021 | DKY0117891 | 38821014A00192 |  | 3200301-BELFRY / BELFRY | Line Work | UG | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 188 Murphy Bottom Rd, Belfry, KY 41514, USA | 2022-12-20
2022 | 2022-09-14 | Pikeville |  |  | 38820698B00050 |  | 3202201-LOVELY / LOVELY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Parsley Road, Big Elk Creek, Beauty, Ky.
2022 | 2022-09-14 | Pikeville |  |  | 38820745C00076 |  | 3202201-LOVELY / LOVELY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 38 Osborne Road, Beauty, Ky.
2022 | 2022-09-14 | Pikeville | 85775311 | DKY0121772 | 38820746A00067 |  | 3202201-LOVELY / LOVELY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Inactive transformer. Needs to be removed. | 145 Rfk Buck Creek, Beauty, Ky.
2022 | 2022-09-14 | Pikeville |  |  | 38820746A00302 | TRUE | 3202201-LOVELY / LOVELY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 1013 Rfk Big Elk Creek, Beauty, Ky.
2022 | 2022-09-14 | Pikeville | 85838917 | DKY0121868 | 38820746B00166 |  | 3202201-LOVELY / LOVELY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Inactive transformer needs to be removed. | 79 Bone Hollow, Beauty, Ky.
2022 | 2022-09-14 | Pikeville | 85838917 | DKY0121868 | 38820746B00168 |  | 3202201-LOVELY / LOVELY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 445 Bone Hollow, Beauty, Ky.
2022 | 2022-09-14 | Pikeville |  |  | 38820746D30314 |  | 3202201-LOVELY / LOVELY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Ground hog Branch, Warfield, Ky. | 2022-09-14
2022 | 2022-09-16 | Pikeville |  |  | 38820698D00188 | TRUE | 3202201-LOVELY / LOVELY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Little Elk Creek, Hode Road, Warfield, Ky.
2022 | 2022-09-16 | Pikeville |  |  | 38820722C00120 |  | 3202201-LOVELY / LOVELY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 2875 Hode Road, Warfield, Ky.
2022 | 2022-09-16 | Pikeville |  |  | 38820723A00250 |  | 3202201-LOVELY / LOVELY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 2617 Hode Road, Warfield, Ky.
2022 | 2022-09-19 | Pikeville |  |  | 38820674B00316 |  | 3202201-LOVELY / LOVELY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 170 White Road, Warfield, Ky.
2022 | 2022-09-19 | Pikeville |  |  | 38820698C00168 | TRUE | 3202201-LOVELY / LOVELY | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire is broken. Probably need to install new anchor. | 4519 Hode Road, Warfield, Ky.
2022 | 2022-09-20 | Pikeville | 85854684 | DKY0121886 | 38820673D00187 | TRUE | 3202201-LOVELY / LOVELY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Dempsey Hollow, Warfield, Ky.
2022 | 2022-09-20 | Pikeville | 85854684 | DKY0121886 | 38820673D00187 | TRUE | 3202201-LOVELY / LOVELY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Dempsey Hollow, Warfield, Ky.
2022 | 2022-09-20 | Pikeville | 85854684 | DKY0121886 | 38820673D00203 |  | 3202201-LOVELY / LOVELY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 8125 Hode Road, Warfield, Ky.
2022 | 2022-09-20 | Pikeville | 85854684 | DKY0121886 | 38820673D00218 | TRUE | 3202201-LOVELY / LOVELY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 512 Turkey Creek Road, Warfield, Ky.
2022 | 2022-09-21 | Pikeville | 83418093 | DKY0118049 | 38821064D00055 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 515 Right Fork Peter Fork Rd, McCarr, KY 41544, USA | 2022-12-19
2022 | 2022-09-27 | Pikeville | 85835500 | DKY0121856 | 38830830000081 |  | 3401101-FALCON / FALC-OILS | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and service. By customer request so he can do dozer work.@ just beyond 825 intersection on right. | 5808 U.S. 460, Paintsville. Ky. | 2023-10-30
2022 | 2022-09-29 | Pikeville | 85836729 | DKY0121859 | 38830851D00157 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 624 Mash Fork Road, Salyersville, Ky. | 2023-10-13
2022 | 2022-09-29 | Pikeville |  |  | 38830852000016 |  | 3401103-FALCON / BURNINGFK | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Trees grown up in line next to recloser pole. Needs to be trimmed according to customer wishes. Could cause outage. Two big maples in customer yard. | 1279 Mash Fork, Salyersville, Ky. | 2023-11-08
2022 | 2022-09-29 | Pikeville | 85836729 | DKY0121859 | 38830876D00181 |  | 3401103-FALCON / BURNINGFK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 802 Rockhouse Fork Road, Salyersville, Ky. | 2023-10-13
2022 | 2022-09-30 | Pikeville |  |  | 38830785D40124 |  | 3420102-MAYO TRAIL / EUCLID | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Phone cables are wrapped around our 3 phase Hendrix. River crossing. Could cause outage. Safety concerns. | 109 Bridge Street, Paintsville, Ky.
2022 | 2022-10-03 | Pikeville | Trouble ticket # 4970041 |  | 38830806000204 |  | 3401101-FALCON / FALC-OILS | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Customer service pole has fallen to the ground. Service is ENERGIZED. Needs to be disconnected. Talked to customer and from what I can get from him it’s apparently been this way for a while. Contacted DDC to create trouble ticket for servicer. | 8684 Ky. Rte 40, Falcon, Ky. | 2022-10-03
2022 | 2022-10-05 | Pikeville |  |  | 38831124A00024 |  | 3120101-STANVILLE/MUD CREEK | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Large rotten poplar tree inside ROW leaning over single phase line. Could cause outage. | 1459 Samson Fork, Dana, Ky.
2022 | 2022-10-21 | Pikeville | 86228581 | DKY0122485 | 38831073000009 |  | 3408103-SALISBURY / MARTIN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property , joint use attachments: clearance issues |  |  | KPC | NO | Remove inactive transformer. @ mouth Ferrell Road . No truck access | 2115 Stephens Branch Road, Martin, Ky. | 2023-12-18
2022 | 2022-10-21 | Pikeville | 86228581 | DKY0122485 | 38831098A30843 | TRUE | 3408103-SALISBURY / MARTIN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 253 Stephens Branch Road, Martin, Ky. | 2023-12-18
2022 | 2022-10-24 | Pikeville |  |  | 38831147000166 | TRUE | 3408101-SALISBURY / PRINTER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ switch pole, next to a cemetery. | 3406 Trace Branch, Printer, Ky.
2022 | 2022-10-24 | Pikeville | 86042878 | DKY0122163 | 38831148B20331 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 3780 Trace Branch, Printer, Ky. | 2023-12-14
2022 | 2022-10-25 | Pikeville | 86216925 |  | 37830018009001 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 3017 Turkey Creek, Maytown, Ky.
2022 | 2022-10-25 | Pikeville |  |  | 38831146000068 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 2015 Turkey Creek,Maytown, Ky.
2022 | 2022-11-02 | Pikeville | 83734366 | DKY0118536 | 38821061B00080 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2022-11-14
2022 | 2022-11-03 | Pikeville | 85814496 | DKY0121802 | 37830045000049 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. No truck | 2612 Ky. 3379, Branham Creek, Galveston, Ky. | 2023-12-27
2022 | 2022-11-03 | Pikeville |  |  | 38831077D10727 |  | 3120102-STANVILLE/TRAM | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground cut on recloser pole. | Mare Creek Road, Stanville, Ky. | 2022-11-03
2022 | 2022-11-03 | Pikeville |  |  | 38831077D10727 |  | 3120102-STANVILLE/TRAM | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground cut on recloser pole. | Mare Creek Road, Stanville, Ky. | 2022-11-03
2022 | 2022-11-22 | Pikeville | 85756903 | DKY0121727 | 37820008A00038 | TRUE | 3408304-COLEMAN / CALLOWAY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1292 Calloway Branch, Phelps, KY 41553, USA | 2023-12-12
2022 | 2022-11-22 | Pikeville |  |  | 38821064C00065 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Pole washed out in creek. Remove inactive transformer. @ Old Lexington Coal gate. | Hatfield Branch, Hardy, Ky.
2022 | 2022-11-23 | Pikeville | 85608432 | DKY0121495 | 37820027000079 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 317 River Hurricane, Kimper, Ky. | 2023-09-05
2022 | 2022-12-05 | Pikeville |  |  | 38821062C00398 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ behind church. | 1633 Upper Pond Creek, McAndrews, Ky.
2022 | 2022-12-06 | Pikeville |  |  | 38821033000036 |  | 3421301-RACCOON/ZEBULON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 3630 State Hwy 194, Pikeville, Ky.
2022 | 2022-12-07 | Pikeville |  |  | 37830261000009 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 6651 Long Fork, Virgie, Ky.
2022 | 2022-12-08 | Pikeville | 83958769 | DKY0118805 | 38821014C20054 |  | 3200301-BELFRY / BELFRY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 352 Murphy Bottom Rd, Belfry, KY 41514, USA | 2023-01-03
2022 | 2022-12-14 | Pikeville | 84635062 | DKY0120053 | 38830929000107 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Pole has been backfilled around. Clearance issues. Also remove inactive transformer. @ U.S. 23 across from Drains Unlimited. Highway crossing. | Pennington Drive, Prestonsburg, Ky.
2022 | 2022-12-14 | Pikeville | 85837741 | DKY0121861 | 38830930B00070 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. Might be truck accessible when dry/frozen. | Abbott Mountain, Prestonsburg, Ky. | 2023-10-31
2022 | 2022-12-14 | Pikeville |  |  | 38830930B00226 |  | 3403302-PRESTONSB / UNIVERSIT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Resource Drive, Prestonsburg, Ky. | 2022-12-14
2022 | 2022-12-15 | Pikeville | 85468263 | DKY0121276 | 38830930B00179 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 1588 Ky. 321, Prestonsburg, Ky. | 2023-08-09
2022 | 2022-12-15 | Pikeville | 85837741 | DKY0121861 | 38830954A10833 |  | 3403302-PRESTONSB / UNIVERSIT | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. @ Car wash | W. Porter Street, Prestonsburg, Ky. | 2023-10-31
2022 | 2022-12-15 | Pikeville |  |  | 38830954A40171 |  | 3403302-PRESTONSB / UNIVERSIT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Mays Branch, Prestonsburg, Ky. | 2022-12-15
2022 | 2022-12-15 | Pikeville |  |  | 38830954A40222 |  | 3403302-PRESTONSB / UNIVERSIT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | N Lake Drive, Prestonsburg, Ky. | 2022-12-15
2022 | 2022-12-16 | Pikeville |  |  | 38830954B20268 |  | 3403301-PRESTONSB / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | S. Stanley Avenue, W. Prestonsburg, Ky. | 2022-12-16
2022 | 2022-12-16 | Pikeville |  |  | 38830954B30799 |  | 3403301-PRESTONSB / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Scott Lane, Prestonsburg, Ky. | 2022-12-16
2022 | 2022-12-16 | Pikeville |  |  | 38830954B40157 |  | 3403301-PRESTONSB / CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | N. Arnold Avenue , Prestonsburg, Ky. | 2022-12-16

## Ckt Defects Reported 2023 PKV
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2023 | 2023-01-04 | Pikeville |  |  | 38821081D40325 |  | 3421301-RACCOON/ZEBULON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 5788 Zebulon Hwy, Pikeville, KY 41501, USA
2023 | 2023-01-04 | Pikeville |  |  | 38821106000045 |  | 3421301-RACCOON/ZEBULON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Montrose Drive, Zebulon, Ky. | 2023-01-04
2023 | 2023-01-05 | Pikeville |  |  | 38821033000077 |  | 3421301-RACCOON/ZEBULON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 3441 KY-194, Pikeville, KY 41501, USA
2023 | 2023-01-05 | Pikeville |  |  | 38821034000101 |  | 3421301-RACCOON/ZEBULON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1420 Dry Branch, Pikeville, Ky.
2023 | 2023-01-05 | Pikeville |  |  | 38821057D00072 |  | 3421301-RACCOON/ZEBULON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 129 Mikes Branch, Pikeville, KY 41501, USA
2023 | 2023-01-05 | Pikeville |  |  | 38821057D00152 |  | 3421301-RACCOON/ZEBULON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Mikes Branch, Kentucky 41501, USA | 2023-01-05
2023 | 2023-01-05 | Pikeville |  |  | 38821057D00305 |  | 3421301-RACCOON/ZEBULON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop rolled up on pole. | 111 Taylor Hill, Pikeville, Ky.
2023 | 2023-01-05 | Pikeville |  |  | 38821081000017 |  | 3421301-RACCOON/ZEBULON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NEEDS ADDITIONAL CHECK | Pole washed out in creek | 130 Maynard Hill, Pikeville, KY 41501, USA
2023 | 2023-01-05 | Pikeville |  |  | 38821081000043 |  | 3421301-RACCOON/ZEBULON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Zebulon Hwy, Pikeville, KY, USA | 2023-01-05
2023 | 2023-01-05 | Pikeville |  |  | 38821081D00010 |  | 3421301-RACCOON/ZEBULON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Zebulon Highway, Pikeville, Ky. | 2023-01-05
2023 | 2023-01-05 | Pikeville |  |  | 38821081D00101 |  | 3421301-RACCOON/ZEBULON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy marker | Winn’s Branch, Zebulon, Ky. | 2023-01-05
2023 | 2023-01-06 | Pikeville |  |  | 38821081000309 |  | 3421301-RACCOON/ZEBULON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 285 Wolfpen Hollow, Pikeville, KY 41501, USA
2023 | 2023-01-06 | Pikeville |  |  | 38831032000075 |  | 3421301-RACCOON/ZEBULON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 8225 Ky. Hwy 194 , Pikeville, Ky.
2023 | 2023-01-06 | Pikeville |  |  | 38831032B40139 |  | 3421301-RACCOON/ZEBULON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 8426 Ky. Hwy. 194 W. Pikeville, Ky.
2023 | 2023-01-06 | Pikeville |  |  | 38831056D00286 |  | 3421301-RACCOON/ZEBULON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 7143 Joes Creek, Pikeville, Ky.
2023 | 2023-01-06 | Pikeville |  |  | 38831080C20113 |  | 3421301-RACCOON/ZEBULON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Millers Creek, Pikeville, Ky. | 2023-01-06
2023 | 2023-01-06 | Pikeville |  |  | 38831104B10232 |  | 3421301-RACCOON/ZEBULON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ coal mine in head of Rfk. | Rfk Cowpen, Pikeville, Ky.
2023 | 2023-01-09 | Pikeville |  |  | 38820937000031 | TRUE | 3421301-RACCOON/ZEBULON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ next to white trailer. | 712 Curry Branch Brushy Road, Pikeville, Ky.
2023 | 2023-01-09 | Pikeville |  |  | 38831008000004 |  | 3421301-RACCOON/ZEBULON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Sycamore Road, Pikeville, Ky. | 2023-01-09
2023 | 2023-01-09 | Pikeville |  |  | 38831008000085 |  | 3421301-RACCOON/ZEBULON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer.@ in curve going down the mountain. | Mill Branch Brushy Rd. Pikeville, Ky.
2023 | 2023-01-10 | Pikeville |  |  | 38831007A30157 |  | 3421301-RACCOON/ZEBULON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ above Jackson Branch above half mile. Abandoned mobile home on right. Gate near road. | State Hwy 194 W. Pikeville, Ky.
2023 | 2023-01-12 | Pikeville |  |  | 38821130000048 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1219 Grassy Branch, Raccoon, KY 41557, USA
2023 | 2023-01-12 | Pikeville |  |  | 38821130000145 |  | 3421302-RACCOON/FROZEN CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Grassy Branch, Raccoon, KY 41557, USA | 2023-01-12
2023 | 2023-01-12 | Pikeville |  |  | 38821130000325 |  | 3421302-RACCOON/FROZEN CREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop hanging down the pole | 1852 Raccoon Rd, Raccoon, KY 41557, USA
2023 | 2023-01-12 | Pikeville |  |  | 38821131000003 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 2440 Grassy Branch, Raccoon, Ky.
2023 | 2023-01-12 | Pikeville |  |  | 38821131000110 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 137 May Branch, Raccoon, Ky.
2023 | 2023-01-12 | Pikeville | 84214640 | DKY0119194 | 38821137B00632 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 12638 Phelps 632 Rd, Phelps, KY 41553, USA | 2023-05-23
2023 | 2023-01-16 | Pikeville |  |  | 37820002000015 | TRUE | 3421302-RACCOON/FROZEN CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Pin type insulator broken. Hillside phase | 1035 Frozen Creek, Raccoon, Ky.
2023 | 2023-01-16 | Pikeville |  |  | 37820002000173 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 3622 Raccoon Rd, Raccoon, KY 41557, USA
2023 | 2023-01-16 | Pikeville |  |  | 37820002000209 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | joint use attachments: clearance issues |  |  | Foreign | YES | Customer has built his deck around secondary pole. | 62 McCoy Hollow, Raccoon, KY 41557, USA
2023 | 2023-01-16 | Pikeville | Outage 4441341 |  | 37820002000226 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator insulator broken on step-down pole. Could cause outage. Contacted Steve Ray to have crew make repairs. Repaired same day. | 51 Rocky Hollow, Raccoon, Ky. | 2022-01-16
2023 | 2023-01-17 | Pikeville |  |  | 37820002000064 | TRUE | 3421302-RACCOON/FROZEN CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator insulator broken on double dead-end pole. I contacted Steve Ray to have crew make repairs. He said they would take care of it. | 4480 Raccoon Road, Raccoon, Ky.
2023 | 2023-01-17 | Pikeville |  |  | 37820002000207 |  | 3421302-RACCOON/FROZEN CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | 4156 Raccoon Road, Raccoon, Ky. | 2023-01-17
2023 | 2023-01-17 | Pikeville | 85631388 | DKY0121524 | 37820050000015 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property , service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive transformer and service hanging down the pole. | 2779 Lower Pompey, Pikeville, Ky. | 2023-12-26
2023 | 2023-01-17 | Pikeville | 85631388 | DKY0121524 | 37820050000018 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 2630 Lower Pompey, Pikeville, Ky. | 2023-12-26
2023 | 2023-01-17 | Pikeville | 85631388 | DKY0121524 | 37820050000039 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 365 Wolfpen Branch, Pikeville, Ky. | 2023-12-26
2023 | 2023-01-17 | Pikeville | 85631388 | DKY0121524 | 37820050000212 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 2379 Lower Pompey, Pikeville, Ky. | 2023-12-26
2023 | 2023-01-17 | Pikeville |  |  | 37820074000030 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilator insulator broken | 981 Lower Pompey, Pikeville, Ky.
2023 | 2023-01-18 | Pikeville | 85499327 | DKY0121364 | 37820027000030 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 250 Upper Pompey, Pikeville, Ky. | 2024-01-03
2023 | 2023-01-18 | Pikeville |  |  | 37820003000089 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/melting.@ Regulator pole in head of Raccoon. | 7394 Raccoon Road, Pikeville, Ky.
2023 | 2023-01-18 | Pikeville | 85446347 | DKY0121250 | 37820026000007 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 5378 Raccoon Road, Raccoon, Ky. | 2023-07-11
2023 | 2023-01-18 | Pikeville |  |  | 37820027000009 |  | 3421302-RACCOON/FROZEN CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Raccoon Road, Raccoon, Ky. | 2023-01-18
2023 | 2023-01-18 | Pikeville | 85446347 | DKY0121250 | 37820027000017 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 288 Lynn Lane, Ridgeline Road, Raccoon, Ky. | 2023-07-11
2023 | 2023-01-18 | Pikeville | 85499327 | DKY0121364 | 37820027000117 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and two pole secondary ext. pole 235 & 236 | 250 Upper Pompey, Pikeville, Ky. | 2024-01-03
2023 | 2023-01-18 | Pikeville | 85446347 | DKY0121250 | 37820027000149 |  | 3421301-RACCOON/ZEBULON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 6276 Raccoon Road, Raccoon, Ky. | 2023-07-11
2023 | 2023-01-18 | Pikeville | 85446347 | DKY0121250 | 37820027000184 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. Just up Possum Fork on right. | Ridge line Road, Pikeville, Ky. | 2023-07-11
2023 | 2023-01-18 | Pikeville | 85499327 | DKY0121364 | 37820051000197 |  | 3421302-RACCOON/FROZEN CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary pole # 51-191 | 1159 Upper Pompey, Pikeville, Ky. | 2024-01-03
2023 | 2023-01-20 | Pikeville |  |  | 38830955B00425 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown. No truck | 108 S Circle Drive, Prestonsburg, Ky.
2023 | 2023-01-20 | Pikeville |  |  | 38830955B00437 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated / melting | 94 Mayo Hollow, Prestonsburg, Ky.
2023 | 2023-01-20 | Pikeville | 85854997 | DKY0121887 | 38830955C00257 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 215 Corn Fork, Prestonsburg, Ky. | 2023-10-31
2023 | 2023-01-20 | Pikeville | 86638722 | DKY0123183 | 38830956000005 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | YES | Remove inactive transformer. Probably should replace this pole. Installed 1947 | 1522 Corn Fork, Prestonsburg, Ky.
2023 | 2023-01-20 | Pikeville | 85854997 | DKY0121887 | 38830956000012 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. About 2 miles up on right. No truck | Corn Fork, Prestonsburg, Ky. | 2023-10-31
2023 | 2023-01-20 | Pikeville |  |  | 38830956000041 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Tie wire broken. About 3 miles up beside a big rock. | Corn Fork , Prestonsburg, Ky.
2023 | 2023-01-20 | Pikeville |  |  | 38830956000066 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive pole and transformer. Small hollow on the left about 1.7 miles up. | 1710 Corn Fork, Prestonsburg, Ky.
2023 | 2023-01-23 | Pikeville |  |  | 38830955B00179 |  | 3410602-E.PRESTON / LANCER | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm deteoriated/rotten | Mitchell Street, Lancer, Ky.
2023 | 2023-01-23 | Pikeville |  |  | 38830955B00556 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm is split all the way across. Pole is 1962 model. Might want to change pole while changing Crossarm.@ between Bingham street & Bevins street. | 3081 S Lake Drive, Prestonsburg, Ky.
2023 | 2023-01-23 | Pikeville |  |  | 38830955D00007 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , crossarm/braces: broken/split |  |  | KPC | YES | Crossarm broken. Pole was installed 1938. Should be replaced. River crossing from Goble Roberts Addition. On hill, no truck. About 1/4 mile before turning into Goble Roberts. | Ky 1428, Prestonsburg, Ky.
2023 | 2023-01-23 | Pikeville |  |  | 38830955D00209 |  | 3410602-E.PRESTON / LANCER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | S Roberts Drive, Prestonsburg, Ky. | 2023-01-23
2023 | 2023-01-23 | Pikeville |  |  | 38830979C00007 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken. Probably need to install new anchor. Buckarm next to recloser pole. | Sugarloaf Branch, Prestonsburg, Ky.
2023 | 2023-01-23 | Pikeville |  |  | 38830979C00106 |  | 3410602-E.PRESTON / LANCER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Worldwide Equipment Drive, Sugarloaf, Ky. | 2023-01-23
2023 | 2023-01-23 | Pikeville |  |  | 38830979D00065 |  | 3410602-E.PRESTON / LANCER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Taylor Loop Drive, Sugarloaf, Ky. | 2023-01-23
2023 | 2023-01-23 | Pikeville |  |  | 38830980000027 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole has been re-enforced at ground level. Installed in 1949. Probably should be replaced | 1373 Sugarloaf Branch, Prestonsburg, Ky.
2023 | 2023-01-23 | Pikeville |  |  | 38831004000018 |  | 3410602-E.PRESTON / LANCER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Merrit Branch, Ky. 1428, Allen, Ky.
2023 | 2023-01-24 | Pikeville | 84290995 | DKY0119372 | 37820029000009 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 1269 Layne Branch, Kimper, KY 41539, USA | 2023-02-07
2023 | 2023-01-25 | Pikeville |  |  | 38831047000031 |  | 3402501-MIDDLECRE / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Official Hollow, David, Ky. | 2023-01-25
2023 | 2023-01-27 | Pikeville | 82111714 | DKY0116768 | 37830018000153 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2023 | 2023-01-27 | Pikeville | 82114296 | DKY0116769 | 37830018000154 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2023 | 2023-01-27 | Pikeville | 82114762 | DKY0116771 | 37830018000156 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2023 | 2023-01-27 | Pikeville | 83979193 | DKY0118842 | 38831101D40533 | TRUE | 3120103-STANVILLE/HAROLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2023 | 2023-01-27 | Pikeville | 83979193 | DKY0118842 | 38831101D40533 | TRUE | 3120103-STANVILLE/HAROLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 38831101D40533B Step down platform
2023 | 2023-01-27 | Pikeville | 83514705 | DKY0118215 | 38831125C30016 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2023 | 2023-01-27 | Pikeville | 82294903 | DKY0116974 | 38831125C30017 | TRUE | 3120101-STANVILLE/MUD CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2023 | 2023-01-27 | Pikeville | 83489784 | DKY0118173 | 38831125C40532 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2023 | 2023-01-27 | Pikeville | 82116877 | DKY0116772 | 38831146000118 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2023 | 2023-01-30 | Pikeville | 86421667 | DKY0122771 | 38831092000016 |  | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole washed out around in creek. 2 spans #4 copper neutral conductor down/ stolen. | Boss Row, Evanston, Ky, | 2024-01-03
2023 | 2023-01-30 | Pikeville |  |  | 38831140A00025 |  | 3404002-SPRINGFOR / 1PHASEDIS | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary | Mineshaft Road, Evanston, Ky.
2023 | 2023-01-31 | Pikeville | 85608432 | DKY0121495 | 37820027000079 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 317 River Hurricane, Kimper, Ky. | 2023-09-05
2023 | 2023-01-31 | Pikeville |  |  | 37820004000125 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Epoxilators badly deteriorated/melted. 2nd pole from station near RR tracks and garage bldg. | 9591 State Hwy 194 E, Kimper, Ky.
2023 | 2023-01-31 | Pikeville |  |  | 37820004000265 |  | 3408401-KIMPER / LONG FORK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/melted | 11121 Elkhorn Fork, Kimper, Ky.
2023 | 2023-01-31 | Pikeville | 85608432 | DKY0121495 | 37820027000081 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 206 River Hurricane, Kimper, Ky. | 2023-09-05
2023 | 2023-01-31 | Pikeville | 85586782 | DKY0121463 | 37820051000071 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive 2 pole tap and transformers on poles 110 and 75. | Jonican Creek, Raccoon, Ky. | 2023-12-11
2023 | 2023-01-31 | Pikeville | 83964164 | DKY0119926 | 37820051000202 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 3178 Ridgeline Road, Raccoon, Ky. | 2023-08-21
2023 | 2023-01-31 | Pikeville | 85608432 | DKY0121495 | 37820052000051 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 915 River Hurricane, Kimper, Ky. | 2023-09-05
2023 | 2023-01-31 | Pikeville | 84331281 | DKY0119437 | 37820171C00008 |  | 3400701-DRAFFIN / BELCHER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole Burnt at Top | 13171 Regina Belcher Hwy | 2023-02-21
2023 | 2023-01-31 | Pikeville | 84325703 | DKY0119422 | 37830047D00030 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole Burnt at top | 25 Nightingale Ln | 2023-02-22
2023 | 2023-01-31 | Pikeville |  |  | 38821132000098 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/melting. @ first pole next to station fence. Pictures don’t show good because of weather. Use binoculars. | State Hwy 194 E , Kimper, Ky.
2023 | 2023-01-31 | Pikeville | 84313273 | DKY0119461 | 38831075000023 |  | 3408103-SALISBURY / MARTIN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2023-02-13
2023 | 2023-01-31 | Pikeville | 84322151 | DKY0119454 | 38831098C00221 |  | 3408103-SALISBURY / MARTIN | Line Work | UG | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1PH primary with OH and UG services. Track possible, needs to reviewed by Forman. | 255 KY Route 3188, Kentucky, USA | 2023-07-05
2023 | 2023-02-01 | Pikeville | 84342657 | DKY0119503 | 37820149000155 |  | 3409402-FEDSCREEK / LICKCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2023-02-14
2023 | 2023-02-01 | Pikeville | 84344944 | DKY0119477 | 38820942B41431 |  | 3417601-NEW CAMP / SOUTH SIDE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 29320 US-119, South Williamson, KY 41503, USA | 2023-05-03
2023 | 2023-02-03 | Pikeville | 85533557 | DKY0121368 | 37820053000248 | TRUE | 3408402-KIMPER / GRAPEVINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Island Creek Road, Grapevine , Ky. | 2023-12-12
2023 | 2023-02-03 | Pikeville | 85533557 | DKY0121368 | 37820054000085 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Elliott Justice Road, Grapevine, Ky. | 2023-12-12
2023 | 2023-02-06 | Pikeville | 84898691 | DKY0120747 | 37820054000009 | TRUE | 3408402-KIMPER / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , transformers: leaking , damaged , unused near waterway/drainage OR school property |  |  | Foreign | YES | Pole rotten at ground line. Installed 1945. Remove inactive transformer. | 210 Hunts Branch Road, Biggs, Ky.
2023 | 2023-02-06 | Pikeville | 85616235 | DKY0121504 | 37820054000012 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 296 Hunts Branch Road, Biggs, Ky.
2023 | 2023-02-06 | Pikeville | 84899033 | DKY0120787 | 37820054000173 | TRUE | 3408402-KIMPER / GRAPEVINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 22251 Biggs Road, Biggs, Ky.
2023 | 2023-02-06 | Pikeville | 85533557 | DKY0121368 | 37820054000225 |  | 3408402-KIMPER / GRAPEVINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | State Hwy 194 E, Biggs, Ky. | 2023-12-12
2023 | 2023-02-07 | Pikeville | 84364249 | DKY0119537 | 38831124B00169 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 1704 Sansom Branch, Dana, KY | 2023-02-20
2023 | 2023-02-08 | Pikeville | 84391832 | DKY0119580 | 38820966A10481 |  | 3417601-NEW CAMP / SOUTH SIDE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | New Camp Rd, Kentucky 41503, USA | 2023-05-09
2023 | 2023-02-08 | Pikeville |  |  | 38830954B40079 |  | 3410601-E.PRESTON / PRESTONSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | S Highland Ave, Prestonsburg, KY 41653, USA | 2023-02-08
2023 | 2023-02-08 | Pikeville |  |  | 38830954B40707 |  | 3410601-E.PRESTON / PRESTONSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | N Highland Ave, Prestonsburg, KY 41653, USA | 2023-02-08
2023 | 2023-02-08 | Pikeville |  |  | 38830954B40708 |  | 3410601-E.PRESTON / PRESTONSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | S Highland Ave, Prestonsburg, KY 41653, USA | 2023-02-08
2023 | 2023-02-08 | Pikeville |  |  | 38830954D20087 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotting at ground level | 530 Westminister St, Prestonsburg, KY 41653, USA
2023 | 2023-02-08 | Pikeville |  |  | 38830954D20098 |  | 3410601-E.PRESTON / PRESTONSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Deep St, Prestonsburg, KY 41653, USA | 2023-02-08
2023 | 2023-02-08 | Pikeville |  |  | 38830954D40509 |  | 3410601-E.PRESTON / PRESTONSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | S Lake Dr, Prestonsburg, KY 41653, USA | 2023-02-08
2023 | 2023-02-08 | Pikeville | 86653792 | DKY0123267 | 38830978000308 | TRUE | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is split at top down to neutral. Pole sits in creek. | 1524 Town Branch, Prestonsburg, Ky.
2023 | 2023-02-08 | Pikeville |  |  | 38830978C10090 | TRUE | 3410601-E.PRESTON / PRESTONSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Riverside Dr, Prestonsburg, KY 41653, USA | 2023-02-08
2023 | 2023-02-08 | Pikeville | 84644614 | dky0120064 | 38830978C10117 |  | 3410601-E.PRESTON / PRESTONSB | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer bank and secondary pole. | S Highland Ave, Prestonsburg, KY 41653, USA
2023 | 2023-02-10 | Pikeville | 84411258 | DKY0119606 | 38821087B00009 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 750 Ball Fork Rd, Pinsonfork, KY 41555, USA | 2023-06-12
2023 | 2023-02-14 | Pikeville |  |  | 37830161B00080 |  | 3407103-TOPMOST / KITE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Lion Branch Rd & Roaring Branch Rd, Kentucky 41862, USA
2023 | 2023-02-14 | Pikeville |  |  | 37830161B00152 |  | 3407103-TOPMOST / KITE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Lion Branch, Roaring Branch, Topmost, Ky.
2023 | 2023-02-14 | Pikeville |  |  | 37830185000033 | TRUE | 3407103-TOPMOST / KITE | Line Work | OH |  | crossarm/braces: deteriorated, not rotten , lightning arresters/insulators: damaged |  | KPC | NO | Crossarms deteriorated and Epoxilators melted | 333 Hall Branch Rd, Topmost, KY 41862, USA
2023 | 2023-02-14 | Pikeville |  |  | 37830185000177 |  | 3407103-TOPMOST / KITE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Mullins Branch Road, Topmost, Ky.
2023 | 2023-02-14 | Pikeville |  |  | 37830185000187 |  | 3407103-TOPMOST / KITE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 714 Hall Branch Rd, Topmost, KY 41862, USA
2023 | 2023-02-14 | Pikeville |  |  | 37830209000056 |  | 3407103-TOPMOST / KITE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 804 Mullins Branch, Topmost, Ky.
2023 | 2023-02-14 | Pikeville |  |  | 37830209000122 |  | 3407103-TOPMOST / KITE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 800 Mullins Branch, Topmost, Ky.
2023 | 2023-02-14 | Pikeville | 84425121 | DKY0119637 | 38821109D00518 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 211 Cow Hollow, McAndrews, KY 41543, USA | 2023-06-07
2023 | 2023-02-15 | Pikeville | 84439595 | DKY0119723 | 38820916B00002 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | THIS WAS REPLACED ON 3/7/23 DURING STORM WORK BY PAUL LAYNE | 6505 N BIG CREEK RD BELFRY, KY 41514, USA | 2023-03-07
2023 | 2023-02-15 | Pikeville | 84439766 | DKY0119667 | 38820939D00057 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 4830 N Big Creek Rd, Belfry, KY 41514, USA | 2023-05-23
2023 | 2023-02-17 | Pikeville |  |  | 37830209000137 |  | 3407103-TOPMOST / KITE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Heritage Drive, Kite, Ky. | 2023-02-17
2023 | 2023-02-17 | Pikeville |  |  | 37830209B40040 |  | 3407103-TOPMOST / KITE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. May need pads for truck if customer will allow to drive through yard. | Bill Dee Hall Branch Rd, Kentucky 41828, USA
2023 | 2023-02-17 | Pikeville |  |  | 37830209C10002 |  | 3407103-TOPMOST / KITE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. Just above Mullins Branch on left. | 9280 KY-7, Kite, KY 41828, USA
2023 | 2023-02-17 | Pikeville |  |  | 37830233000012 |  | 3407103-TOPMOST / KITE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 11701 Bill Dee Hall Branch, Kite, Ky.
2023 | 2023-02-17 | Pikeville |  |  | 37830233000130 |  | 3407103-TOPMOST / KITE | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Primary conductor floating | 10381 Bill Dee Hall Branch, Kite, Ky.
2023 | 2023-02-17 | Pikeville |  |  | 37830234000050 |  | 3407103-TOPMOST / KITE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary pole. | 515 Puncheon Creek, Topmost, Ky.
2023 | 2023-02-17 | Pikeville |  |  | 37830234000053 |  | 3407103-TOPMOST / KITE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Blackhawk Road/ Puncheon Creek, Topmost, Ky.
2023 | 2023-02-17 | Pikeville |  |  | 37830234000054 |  | 3407103-TOPMOST / KITE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Blackhawk Road, Puncheon Creek, Topmost, Ky.
2023 | 2023-02-20 | Pikeville |  |  | 37820081D00115 |  | 2970603-HURLEY / RACEFORK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 5664 Paw Paw Creek, Hurley, Va.
2023 | 2023-02-21 | Pikeville |  |  | 37830113000018 |  | 3407101-TOPMOST / DEMA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector (2) | Old Mill Road, Dema, Ky. | 2023-02-21
2023 | 2023-02-21 | Pikeville |  |  | 37830113000108 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer.@ end of single phase on Ky 899 | Ky. Hwy 899, Dema, Ky.
2023 | 2023-02-23 | Pikeville |  |  | 37830138000169 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer…behind brick house @ mouth Patton Branch | 3565 KY-7, Dema, KY 41859, USA
2023 | 2023-02-23 | Pikeville | 85736777 | DKY0121691 | 37830161C00172 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 5125 KY-7, Topmost, KY 41862, USA | 2023-08-30
2023 | 2023-02-23 | Pikeville | 85736777 | DKY0121691 | 37830161C00178 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. On left just up Caudill Branch | Caudill Branch, Topmost, Ky. | 2023-08-30
2023 | 2023-02-23 | Pikeville |  |  | 37830162000064 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Old House Branch Rd & Squire Ln, Kentucky 41859, USA
2023 | 2023-02-23 | Pikeville |  |  | 37830162000077 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | YES | Remove inactive transformer. Pole installed 1962 | Old House Branch Rd, Kentucky, USA
2023 | 2023-02-23 | Pikeville |  |  | 37830186000010 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Gauley Road, Dry Creek, Topmost, Ky.
2023 | 2023-02-23 | Pikeville |  |  | 37830186000046 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1252 Lfk Dry Creek, Topmost, Ky.
2023 | 2023-02-23 | Pikeville |  |  | 37830186000114 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1079 Lfk Dry Creek, Topmost, Ky.
2023 | 2023-02-24 | Pikeville |  |  | 37830185000066 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 560 Potato Branch Rd, Topmost, KY 41862, USA
2023 | 2023-02-24 | Pikeville |  |  | 37830186000120 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 2124 Rfk Dry Creek, Topmost, Ky.
2023 | 2023-02-24 | Pikeville |  |  | 37830210000012 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary pole and secondary on pole 66 | 2812 Rfk Dry Creek, Topmost, Ky.
2023 | 2023-02-24 | Pikeville |  |  | 37830210000034 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer.. last pole Johnson Lane. | Johnson Ln, Kentucky 41862, USA
2023 | 2023-02-24 | Pikeville |  |  | 37830210000088 |  | 3407101-TOPMOST / DEMA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer..head of Rfk Dry Creek on right | 3921 Rfk Dry Creek, Topmost, Ky.
2023 | 2023-02-27 | Pikeville | 84491946 | DKY0119794 | 37830071000134 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace Rotten Pole//THIS POLE WAS REPLACED DURING WIND STORM TROUBLE ON 3/7/23 | 1068 Coon Br | 2023-03-07
2023 | 2023-02-27 | Pikeville | 84491959 | DKY0119821 | 37830071000137 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace Rotten Pole//THIS POLE WAS REPLACED DURING WIND STORM TROUBLE 3/7/2023 | 1126 Coon Br | 2023-03-07
2023 | 2023-02-27 | Pikeville |  |  | 38831123A00019 |  | 3408101-SALISBURY / PRINTER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer and secondary | 3110 Frogtown Lane, Printer, Ky.
2023 | 2023-02-27 | Pikeville |  |  | 38831123B00033 |  | 3408101-SALISBURY / PRINTER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Meade Drive, Printer, Ky.
2023 | 2023-02-27 | Pikeville |  |  | 38831123B00127 | TRUE | 3408101-SALISBURY / PRINTER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary pole. | Meade Drive, Printer, Ky.
2023 | 2023-02-27 | Pikeville | 84491943 | DKY0119823 | 38831125B00449 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 2029 KY ROUTE 979, HAROLD, KY 41635-9026 | 2023-03-24
2023 | 2023-02-27 | Pikeville |  |  | 38831147000030 |  | 3408101-SALISBURY / PRINTER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 278 Shop Branch, Hunter, Ky.
2023 | 2023-02-27 | Pikeville |  |  | 38831147000120 |  | 3408101-SALISBURY / PRINTER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 458 Gunstock Branch, Printer, Ky.
2023 | 2023-02-27 | Pikeville |  |  | 38831147000166 | TRUE | 3408101-SALISBURY / PRINTER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 3406 Trace Branch, Printer, Ky.
2023 | 2023-02-27 | Pikeville |  |  | 38831147000166 | TRUE | 3408101-SALISBURY / PRINTER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Printer, KY 41655, USA
2023 | 2023-02-27 | Pikeville |  |  | 38831147000188 |  | 3408101-SALISBURY / PRINTER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 334 Spurlock Fork Rd, Dana, KY 41615, USA
2023 | 2023-02-27 | Pikeville |  |  | 38831147000331 |  | 3408101-SALISBURY / PRINTER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 3380 Trace Branch, Printer, Ky.
2023 | 2023-02-28 | Pikeville | 84492068 | DKY0119830 | 37830209000078 |  | 3407103-TOPMOST / KITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES |  | MULLINS BRANCH, KITE, KY | 2023-03-24
2023 | 2023-02-28 | Pikeville | 84551247 | DKY0119900 | 38831099000107 |  | 3408103-SALISBURY / MARTIN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at top and leaning. Replace xfmr and xco. | 112 Hannah Lane
2023 | 2023-02-28 | Pikeville |  |  | 38831146C00058 |  | 3408101-SALISBURY / PRINTER | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Dogwood Drive, Printer, Ky. | 2023-02-28
2023 | 2023-02-28 | Pikeville |  |  | 38831146C00287 |  | 3408101-SALISBURY / PRINTER | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive secondary pole. | 4733 KY-122, Printer, KY 41655, USA
2023 | 2023-02-28 | Pikeville |  |  | 38831146D00010 |  | 3408101-SALISBURY / PRINTER | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary pole.. @ bridge @mouth Hunter Branch. | KY-122, Printer, Ky.
2023 | 2023-03-01 | Pikeville |  |  | 38821089C00276 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary pole. | 213 Old Shoe Hollow, Freeburn, Ky.
2023 | 2023-03-01 | Pikeville |  |  | 38821089D00400 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer. Pole is tagged as 400 but I think it’s pole 180 on atlas...it’s where house has burned. | 45331 Vulcan Road, Freeburn, Ky.
2023 | 2023-03-01 | Pikeville | 85443567 | DKY0121238 | 38821090A20347 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 45584 Vulcan Road, Freeburn, Ky. | 2024-01-12
2023 | 2023-03-01 | Pikeville |  |  | 38821113D00265 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary pole 266 | 252 Nicholas Fork, Freeburn, Ky.
2023 | 2023-03-02 | Pikeville | 84491977 | DKY0119874 | 37830071000037 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at groundline//THIS POLE REPLACED DURING WIND STORM TROUBLE 3/7/23 | 1068 Coon Br, Pikeville, Ky. | 2023-03-07
2023 | 2023-03-02 | Pikeville | 84582352 | DKY0119938 | 37830091B00247 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Light | 13513 KY ROUTE 122, PRICE, KY 41636-9017 | 2023-04-26
2023 | 2023-03-02 | Pikeville | 84537327 | DKY0119880 | 38831052D00317 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 186 Lakeview Dr, Ivel, KY 41642, USA | 2023-03-17
2023 | 2023-03-03 | Pikeville | 84481996 | DKY0119907 | 38821089A00045 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at top | 254 N Johnson Bottom Rd, Freeburn, KY 41528, USA | 2023-05-08
2023 | 2023-03-03 | Pikeville | 85443567 | DKY0121238 | 38821090C20344 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 323 Woodman Creek, Majestic, Ky. | 2024-01-12
2023 | 2023-03-03 | Pikeville | 85436443 | DKY0121227 | 38821091B40048 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary poles 47 and 91. | 2736 Woodman Creek, Majestic, Ky.
2023 | 2023-03-03 | Pikeville |  |  | 38821114B00050 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Primary neutral down.. #2 aluminum | 282 Lynntrough Hollow, Majestic, Ky.
2023 | 2023-03-03 | Pikeville | 85436443 | DKY0121227 | 38821115A00039 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 3424 Woodman Creek Road, Majestic, Ky.
2023 | 2023-03-06 | Pikeville | 85395615 | DKY0121174 | 38821138C00055 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 50936 State Hwy 194 E. Majestic, Ky.
2023 | 2023-03-06 | Pikeville | 85395615 | DKY0121174 | 38821139B00057 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 52055 State Hwy 194 E. Majestic, Ky.
2023 | 2023-03-06 | Pikeville | 85395615 | DKY0121174 | 38821139B00109 |  | 3200202-BARRENSHE / VULCAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 52055 State Hwy 194 E. Majestic, Ky.
2023 | 2023-03-09 | Pikeville |  |  | 37830024A30049 |  | 3403003-PIKEVILLE / CEDAR CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary pole # 1530 | 176 Ratliff Creek Rd, Pikeville, KY 41501, USA
2023 | 2023-03-09 | Pikeville |  |  | 37830024A31116 |  | 3403003-PIKEVILLE / CEDAR CREEK | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Small tree laying on secondary conductor | 166 Hillcrest Heights, Pikeville, KY 41501, USA
2023 | 2023-03-09 | Pikeville |  |  | 37830024B10977 |  | 3403003-PIKEVILLE / CEDAR CREEK | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm rotten/deteoriated. @Walters Chevrolet lot. River crossing. | 455 N Mayo Trail, Pikeville, KY 41501, USA
2023 | 2023-03-14 | Pikeville |  |  | 37830023D40005 |  | 3403003-PIKEVILLE / CEDAR CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Bowles Park Dr, Pikeville, KY 41501, USA | 2023-03-14
2023 | 2023-03-14 | Pikeville |  |  | 37830023D40101 |  | 3403003-PIKEVILLE / CEDAR CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Bowles Park Dr, Pikeville, KY 41501, USA | 2023-03-14
2023 | 2023-03-15 | Pikeville |  |  | 37830072A00516 |  | 3410503-S.PIKEVIL / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | S Mayo Trail, Pikeville, KY 41501, USA | 2023-03-15
2023 | 2023-03-15 | Pikeville |  |  | 37830072B00364 |  | 3410503-S.PIKEVIL / HOSPITAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | S Mayo Trail, Pikeville, KY 41501, USA | 2023-03-15
2023 | 2023-03-16 | Pikeville |  |  | 37830024B40377 |  | 3403002-PIKEVILLE / MAINST | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Poplar St, Pikeville, KY 41501, USA | 2023-03-16
2023 | 2023-03-16 | Pikeville | 86332863 | DKY0122642 | 37830024B41039 | TRUE | 3403002-PIKEVILLE / MAINST | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line | Mountain Chase Dr, Pikeville, KY 41501, USA
2023 | 2023-03-16 | Pikeville | 86142446 |  | 37830024B41520 | TRUE | 3403002-PIKEVILLE / MAINST | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | Hambley Blvd, Pikeville, KY 41501, USA
2023 | 2023-03-20 | Pikeville |  |  | 37830024B41194 |  | 3403002-PIKEVILLE / MAINST | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer bank | Hambley Blvd, Pikeville, KY 41501, USA
2023 | 2023-03-20 | Pikeville |  |  | 37830048C10348 |  | 3403002-PIKEVILLE / MAINST | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | YES | Crossarms rotten/ deteoriated. Pole was installed 1947, seems to be solid at ground level though. | 165 High St, Pikeville, KY 41501, USA
2023 | 2023-03-20 | Pikeville | 84663953 | DKY0120136 | 38820967A00148 |  | 2150103-SPRIGG / SPRIGG | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 56 Reed St, Belfry, KY 41514, USA | 2023-05-24
2023 | 2023-03-20 | Pikeville | 84659886 | DKY0120102 | 38820991D40222 |  | 2150103-SPRIGG / SPRIGG | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 54 McCoy St, Belfry, KY 41514, USA | 2023-07-24
2023 | 2023-03-20 | Pikeville | 84659399 | DKY0120100 | 38821082000070 |  | 3411801-JOHNSCREE / META | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2023-07-18
2023 | 2023-03-23 | Pikeville | 86377061 | DKY0122698 | 37820001000055 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Change pole installed 194y | 340 Williams Hollow, Pikeville, Ky.
2023 | 2023-03-23 | Pikeville | 86377285 | DKY0122719 | 37820001000056 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Change pole installed 1946. | 396 Williams Hollow, Pikeville, Ky.
2023 | 2023-03-23 | Pikeville | 86377208 | DKY0122715 | 37820001000087 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Change pole installed 1947 | 370 Williams Hollow, Pikeville, Ky.
2023 | 2023-03-23 | Pikeville |  |  | 37830024D30130 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 178 Bill King Hollow, Pikeville, Ky.
2023 | 2023-03-23 | Pikeville |  |  | 37830024D31308 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Secondary pole rotten @ ground line…Behind gray building @ mo. of Mays Branch. | 457 Town Mountain Road, Pikeville, Ky.
2023 | 2023-03-27 | Pikeville |  |  | 37820025A00342 |  | 3403001-PIKEVILLE / CITY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 605 Chloe Road, Pikeville, Ky.
2023 | 2023-03-28 | Pikeville |  |  | 37830024B21449 |  | 3403001-PIKEVILLE / CITY | Line Work | UG |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Padmount transformer is covered and surrounded with trees. | 232 Northmonte Drive, Pikeville, Ky.
2023 | 2023-03-28 | Pikeville |  |  | 37830024D10529 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop laying on metal roof. Looks like the service drop can be raised enough to get off the roof but it still probably won’t have proper clearance. Probably need to install taller transformer pole or re-route service drop by installing secondary pole. | 131 Layne Hollow, Pikeville, Ky.
2023 | 2023-03-28 | Pikeville | 86349750 | DKY0122648 | 37830024D20162 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Secondary pole rotten at ground line | 116 Lily Circle, Pikeville, Ky.
2023 | 2023-03-29 | Pikeville |  |  | 37830048A20062 |  | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Fiddler Court, Pikeville, Ky.
2023 | 2023-03-29 | Pikeville |  |  | 37830048A21092 | TRUE | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer@ Bingo Place | S Mayo Trail, Pikeville, Ky.
2023 | 2023-03-30 | Pikeville |  |  | 37820025B00191 |  | 3410501-S.PIKEVIL / PIKEVILLE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Harold’s Branch, Pikeville, Ky. | 2023-03-30
2023 | 2023-03-30 | Pikeville |  |  | 37830048A30381 |  | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning considerably. Has service drop pulled banjo tight going to red roof house down below. Need to straighten pole. Install anchor and guy. | 113 Jefferson Street, Pikeville, Ky.
2023 | 2023-03-30 | Pikeville | 86353948 | DKY0122660 | 37830048A30550 |  | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace pole installed in 1948 | 213 Jefferson Street, Pikeville, Ky.
2023 | 2023-04-10 | Pikeville | 82530892 | DKY0117181 | 38821064D00225 | TRUE | 3200203-BARRENSHE / SLATE BRANCH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole burned nearly completely in two. Insulators broken/damaged | Pounding Mill Mtn. Freeburn, Ky.
2023 | 2023-04-11 | Pikeville | 84758219 | DKY0120344 | 38820965D00090 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | Turkey Creek Rd, Kentucky, USA | 2023-06-13
2023 | 2023-04-11 | Pikeville |  |  | 38821089B00034 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarms are deteoriated. | 200 Joe McCoy Road, Freeburn, Ky.
2023 | 2023-04-12 | Pikeville |  |  | 38821089A00046 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | N Johnson Bottom Rd. Freeburn, Ky. | 2023-07-07
2023 | 2023-04-12 | Pikeville |  |  | 38821089A00301 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | S Johnson Bottom Rd. Freeburn, Ky.
2023 | 2023-04-12 | Pikeville |  |  | 38821089A00434 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ near a burned out mobile home. Not sure if this is the right pole number. Mapping is off. | Hurley Rdg. Freeburn, Ky.
2023 | 2023-04-12 | Pikeville |  |  | 38821089B00330 |  | 3200201-BARRENSHE / FREEBURN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 41804 State Hwy 194, Freeburn, Ky.
2023 | 2023-04-13 | Pikeville | Outage # 4971321 |  | 38821041B00026 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | crossarm/braces: broken/split , conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Crossarm broken. Phase floating, barely off the ground.@ On hill on right about 1/4 mile going up Peter Fork. White garage bldg by the road with red trim. On hill behind it. Contacted DDC to have crew make immediate repairs. | 161 Peter Fork Road, McCarr, Ky. | 2023-04-13
2023 | 2023-04-13 | Pikeville | 85382917 | DKY0121153 | 38821065B00174 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary pole 38821065B09003 | 1659 Peter Fork Road, McCarr,Ky. | 2023-12-20
2023 | 2023-04-13 | Pikeville | 84982842 | DKY0120609 | 38821065B00265 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove 3 spans of inactive single phase and transformer on pole 38821065A00353. Transformer is truck accessible, the other two are maybe. | Pounding Mill Mtn. Freeburn, Ky. | 2023-05-15
2023 | 2023-04-13 | Pikeville | 85382917 | DKY0121153 | 38821065B12014 |  | 3200204-BARRENSHE / POUNDING | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1680 Peter Fork Rd. McCarr, Ky. | 2023-12-20
2023 | 2023-04-17 | Pikeville |  |  | 37830064000009 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Ky. 550, Lackey, Ky. | 2023-04-17
2023 | 2023-04-17 | Pikeville |  |  | 37830064000227 |  | 3413402-GARRETT / LACKEY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ across road from Webb Hollow. | 14305 Ky. Hwy. 550, Lackey, Ky.
2023 | 2023-04-17 | Pikeville |  |  | 37830088000070 |  | 3413402-GARRETT / LACKEY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Big Spring Branch, Lackey, Ky.
2023 | 2023-04-17 | Pikeville |  |  | 37830088000167 |  | 3413402-GARRETT / LACKEY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ beside road just before old Consol tipple. | Ky Hwy 550 E, Lackey, Ky.
2023 | 2023-04-18 | Pikeville | 86453257 | DKY0122841 | 37830087000111 |  | 3413402-GARRETT / LACKEY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 880 Bruce Branch, Mousie, Ky. | 2024-01-08
2023 | 2023-04-18 | Pikeville |  |  | 37830087D00028 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Musical Loop, Mousie, Ky. | 2023-04-18
2023 | 2023-04-18 | Pikeville |  |  | 37830087D00028 |  | 3413402-GARRETT / LACKEY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Musical Loop, Mousie, Ky. | 2023-04-18
2023 | 2023-04-18 | Pikeville |  |  | 37830088000019 |  | 3413402-GARRETT / LACKEY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ just above Consol tipple on left. | 10908 Ky 550 E, Lackey, Ky.
2023 | 2023-04-18 | Pikeville | 86453257 | DKY0122841 | 37830111000085 |  | 3413402-GARRETT / LACKEY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ On hill opposite Lazar Drive. | 3720 Ky. 1087 E, Mousie, Ky. | 2024-01-08
2023 | 2023-04-18 | Pikeville | 86453257 | DKY0122841 | 37830111000091 |  | 3413402-GARRETT / LACKEY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 3175 Hwy 1087 E, Mousie, Ky. | 2024-01-08
2023 | 2023-04-19 | Pikeville | 86483571 | DKY0122911 | 37830111000020 |  | 3413402-GARRETT / LACKEY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 8684 Ky 550 E, Mousie, Ky. | 2024-01-11
2023 | 2023-04-19 | Pikeville | 86483571 | DKY0122911 | 37830112000002 |  | 3413402-GARRETT / LACKEY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 294 Martin Branch, Mousie, Ky. | 2024-01-11
2023 | 2023-04-19 | Pikeville | 86450793 | DKY0122837 | 37830135000046 |  | 3413402-GARRETT / LACKEY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Hummingbird Lane, Mousie, Ky. | 2024-01-05
2023 | 2023-04-19 | Pikeville | 86450793 | DKY0122837 | 37830159000510 |  | 3413402-GARRETT / LACKEY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Frasure Drive, Mousie, Ky. | 2024-01-05
2023 | 2023-04-19 | Pikeville | 86450793 | DKY0122837 | 37830159000513 |  | 3413402-GARRETT / LACKEY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 495 Pine Tree Hollow, Mousie, Ky. | 2024-01-05
2023 | 2023-04-20 | Pikeville | 84889361 | DKY0120571 | 37830067A00135 | TRUE | 3402202-MCKINNEY / GIBSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2023 | 2023-04-20 | Pikeville | 84889361 | DKY0120571 | 37830067A00135 | TRUE | 3402202-MCKINNEY / GIBSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2023 | 2023-04-21 | Pikeville | 84900459 | DKY0120486 | 38820990C40216 |  | 3200302-BELFRY / TOLER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 187 Old Hardy Rd, Toler, KY 41514, USA
2023 | 2023-04-24 | Pikeville | 84893314 | DKY0120689 | 37820035A00015 | TRUE | 3200202-BARRENSHE / VULCAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace bad pole per Mike Bowyer, CRT tech. Rotten @ ground level. On hill on right, @ abandoned trailer. | 933 Camp Branch, Stopover, Ky.
2023 | 2023-04-24 | Pikeville |  |  | 37830335A00061 |  | 3409502-BURDINE / LEVISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace pole installed in 1945 per Mike Bowyer CRT tech. I checked pole, has a little early rot around outer shell. | 103 Contrary Hollow Rd, Jenkins, KY 41537, USA
2023 | 2023-04-24 | Pikeville |  |  | 37830335A00176 |  | 3409502-BURDINE / LEVISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace pole installed 1958 per Mike Bowyer, CRT tech. I checked pole, looks fine but it is 65 years old | 43 Contrary Hollow Rd, Jenkins, KY 41537, USA
2023 | 2023-04-25 | Pikeville |  |  | 37830040C40020 |  | 3413401-GARRETT / GARRETT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Baptist Bottom, Garrett, Ky. | 2023-04-25
2023 | 2023-04-25 | Pikeville |  |  | 37830041B00070 |  | 3413401-GARRETT / GARRETT | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 791 Ky. Rte. 7, Lackey, Ky.
2023 | 2023-04-25 | Pikeville |  |  | 37830065A00067 |  | 3413401-GARRETT / GARRETT | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1260 Ky Rte 7, Lackey, Ky.
2023 | 2023-04-25 | Pikeville |  |  | 37830065A00074 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteoriated pole installed in 1937 | George Road, Estill, Ky.
2023 | 2023-04-25 | Pikeville |  |  | 37830065A00075 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteoriated pole installed in 1937 | 330 Estill Bottom, Estill, KY 41666, USA
2023 | 2023-04-25 | Pikeville |  |  | 37830065A00076 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Remove deteriorating pole installed in 1961 | 330 Estill Bottom, Estill, KY 41666, USA
2023 | 2023-04-25 | Pikeville |  |  | 37830065A00084 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteoriated pole installed in 1961 | 311 Estill Bottom, Estill, KY 41666, USA
2023 | 2023-04-25 | Pikeville |  |  | 37830065A00147 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorating pole installed in 1947 | 110 George Road, Lackey, Ky.
2023 | 2023-04-25 | Pikeville |  |  | 37830065A00148 |  | 3413401-GARRETT / GARRETT | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm deteoriated | 40 George Road, Lackey, Ky.
2023 | 2023-04-25 | Pikeville |  |  | 37830065D00011 |  | 3413401-GARRETT / GARRETT | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 505 Clear Water Rd, Wayland, KY 41666, USA
2023 | 2023-04-25 | Pikeville |  |  | 37830065D00012 |  | 3413401-GARRETT / GARRETT | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 505 Clear Water Rd, Wayland, KY 41666, USA
2023 | 2023-04-26 | Pikeville |  |  | 37830041D00156 |  | 3413401-GARRETT / GARRETT | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ last pole in Martin Branch. No truck | Martin Branch, Wayland, KY 41666, USA
2023 | 2023-04-26 | Pikeville |  |  | 37830065A00030 |  | 3413401-GARRETT / GARRETT | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. No truck | KY-7, Wayland, KY, USA
2023 | 2023-04-26 | Pikeville | 85507033 | DKY0121342 | 37830065D00196 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteoriated pole installed in 1948. May be truck accessible. Old car in driveway. | 65 Stampers Branch Rd, Wayland, KY 41666, USA | 2023-09-25
2023 | 2023-04-26 | Pikeville |  |  | 37830065D00259 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteoriated pole installed in 1949 | Springfield Drive, Wayland, Ky. 41666
2023 | 2023-04-27 | Pikeville | 86214148 | DKY0122441 | 37830016C00152 |  | 3413401-GARRETT / GARRETT | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Rayburn Road, Hueysville, Ky. | 2023-12-07
2023 | 2023-04-27 | Pikeville | 86459280 | DKY0122858 | 37830040C30112 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteoriated pole installed in 1962. Pole sounds hollow just above ground level. Across from marathon station. | Main Street, Garrett, Ky.
2023 | 2023-04-28 | Pikeville | 86214148 | DKY0122441 | 37830016C00297 |  | 3413401-GARRETT / GARRETT | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Raccoon Rd & Salt Lick Rd, Kentucky 41640, USA | 2023-12-07
2023 | 2023-04-28 | Pikeville | 86214148 | DKY0122441 | 37830016C00330 |  | 3413401-GARRETT / GARRETT | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Cemetery Road, Hueysville, Ky.. | 2023-12-07
2023 | 2023-04-28 | Pikeville | 86214148 | DKY0122441 | 37830016C40355 |  | 3413401-GARRETT / GARRETT | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Raccoon Road, Salt Lick, Hueysville, Ky. | 2023-12-07
2023 | 2023-05-01 | Pikeville | 85367046 | DKY0121124 | 37830234000029 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteoriated pole installed in 1948. Pole is hollow. | Golden Rod Drive, Kite, Ky. | 2023-07-20
2023 | 2023-05-01 | Pikeville |  |  | 37830235000085 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1062 Arnold Fork, Kite, Ky.
2023 | 2023-05-01 | Pikeville |  |  | 37830258000019 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Willow Lane, Kite, Ky.
2023 | 2023-05-01 | Pikeville |  |  | 37830258000020 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary pole 258-115 | Willow Lane, Kite, Ky.
2023 | 2023-05-01 | Pikeville |  |  | 37830258000059 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary pole 258-107 | West Fork, Kite, Ky.
2023 | 2023-05-01 | Pikeville |  |  | 37830258000105 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH |  |  |  | KPC | NO | Satellite dish on pole | 108 West Fork, Kite, Ky.
2023 | 2023-05-01 | Pikeville |  |  | 37830258000133 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Willow Lane, Kite, Ky.
2023 | 2023-05-01 | Pikeville |  |  | 37830258D30140 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Willow Lane, Kite, Ky.
2023 | 2023-05-01 | Pikeville |  |  | 37830259000016 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer and secondary pole 259-60 | 1062 Arnold Fork, Kite, Ky.
2023 | 2023-05-01 | Pikeville |  |  | 37830259000025 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1700 Arnold Fork, Kite, Ky.
2023 | 2023-05-01 | Pikeville |  |  | 37830259000037 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 2010 Arnold Fork, Kite, Ky.
2023 | 2023-05-02 | Pikeville |  |  | 37830188B00083 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken, hanging down pole on GOAB SWITCH. @ open point with Burton/Wheelwright circuit. | Ky. Rte. 466, Melvin, Ky.
2023 | 2023-05-02 | Pikeville |  |  | 37830188B00164 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1144 Ky. 466, Melvin, Ky.
2023 | 2023-05-02 | Pikeville |  |  | 37830188B00236 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 240 Muddy Gut Branch, Melvin, Ky.
2023 | 2023-05-02 | Pikeville |  |  | 37830188B00247 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Muddy Gut Branch, Melvin, Ky.
2023 | 2023-05-02 | Pikeville |  |  | 37830235000028 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Skull Fork, Weeksbury, Ky.
2023 | 2023-05-03 | Pikeville |  |  | 37830212D00134 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Yellow Flats, Weeksbury, Ky.
2023 | 2023-05-03 | Pikeville |  |  | 37830212D00281 |  | 3412901-WEEKSBURY / DISTRIBUTION | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Shop Fork, Weeksbury, Ky.
2023 | 2023-05-04 | Pikeville |  |  | 38831146000087 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Hayes Branch, Maytown, Ky.
2023 | 2023-05-08 | Pikeville |  |  | 37830018000237 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 2880 Turkey Creek, Maytown, Ky.
2023 | 2023-05-08 | Pikeville |  |  | 38831146000109 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer.@ small hollow on left just above 1931 | 1931 Turkey Creek, Maytown, Ky.
2023 | 2023-05-09 | Pikeville | 86247988 | DKY0122525 | 38831121000230 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 100 Big Fork Wilson Creek, Langley, Ky. | 2023-12-18
2023 | 2023-05-09 | Pikeville | 86449463 | DKY0122833 | 38831121C00008 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole installed in 1942 | 52 Doc Allen Branch, Langley, KY 41645, USA
2023 | 2023-05-09 | Pikeville |  |  | 38831121C00096 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole installed 1945 | 86 Doc Allen Branch, Langley, KY 41645, USA
2023 | 2023-05-09 | Pikeville | 86482340 | DKY0122910 | 38831121C00106 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated secondary pole installed 1945 | 188 Doc Allen Branch, Langley, KY 41645, USA | 2024-01-15
2023 | 2023-05-09 | Pikeville |  |  | 38831121C00201 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole installed 1945 | 86 Doc Allen Branch, Langley, KY 41645, USA
2023 | 2023-05-09 | Pikeville | 86247988 | DKY0122525 | 38831121D00248 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 97 Wilson Creek, Langley, Ky. | 2023-12-18
2023 | 2023-05-10 | Pikeville | 86247988 | DKY0122525 | 38831097000033 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 2495 Wilson Creek, Langley, Ky. | 2023-12-18
2023 | 2023-05-10 | Pikeville | 86247988 | DKY0122525 | 38831121D00344 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 391 Three Oaks Subdivision, Wilson Creek , Langley, Ky. | 2023-12-18
2023 | 2023-05-10 | Pikeville |  |  | 38831145C00049 |  | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Bailey Addition, Langley, Ky. 41645
2023 | 2023-05-10 | Pikeville |  |  | 38831145C00212 | TRUE | 3402204-MCKINNEY / MAYTOWN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Ousley Dr, Eastern, KY, USA
2023 | 2023-05-11 | Pikeville | 85652742 | DKY0121563 | 38821038D00233 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1479 Pond Creek Rd, Stone, KY 41567, USA | 2023-12-14
2023 | 2023-05-11 | Pikeville | 85652742 | DKY0121563 | 38821062A00379 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. Might be able to reach with truck but questionable. | 539 Davis Branch, Stone, Ky. | 2023-12-14
2023 | 2023-05-11 | Pikeville | 85652742 | DKY0121563 | 38821062A00465 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 91 Davis Branch, Stone, Ky. | 2023-12-14
2023 | 2023-05-11 | Pikeville | 85652742 | DKY0121563 | 38821062B00170 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1174 Mullen Fork, Stone, Ky. | 2023-12-14
2023 | 2023-05-11 | Pikeville |  |  | 38821062C00289 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove 3 spans of inactive single line beginning @ 1062-289 to 1038D-234. Total of 4 poles, 3 spans of wire and 2 xformer s. | 1479 Pond Creek Rd, Stone, KY 41567, USA
2023 | 2023-05-11 | Pikeville | 85652742 | DKY0121563 | 38821062C00290 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. Atlas doesn’t show this xformer | 1479 Pond Creek Rd, Stone, KY 41567, USA | 2023-12-14
2023 | 2023-05-11 | Pikeville | 85026766 | DKY0120678 | 38831077A20707 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES |  | 136 Coleman St | 2023-05-23
2023 | 2023-05-15 | Pikeville | 85428336 | DKY0121217 | 38821062B00150 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole installed in 1958 | 561 Pinsonfork Road, McAndrews, Ky. | 2023-08-04
2023 | 2023-05-15 | Pikeville |  |  | 38821062D00048 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer is covered with vines | Pinsonfork Road, McAndrews, Ky.
2023 | 2023-05-15 | Pikeville | 85449612 | DKY0121255 | 38821062D00126 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole installed in 1937 | Burgraff Road, McAndrews, Ky. | 2023-08-04
2023 | 2023-05-15 | Pikeville | 85499177 | DKY0121330 | 38821062D00128 | TRUE | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole installed in 1937 | Burgraff Road, McAndrews , Ky. | 2023-08-04
2023 | 2023-05-15 | Pikeville | 85499177 | DKY0121330 | 38821062D00128 | TRUE | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole installed in 1937 | Burgraff Road, McAndrews , Ky. | 2023-08-04
2023 | 2023-05-15 | Pikeville | Outage # 4108411 |  | 38821086A00134 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm is broken. Contacted SDS to have crew make repairs asap. Repaired same day. | 643 Pinsonfork Road, McAndrews, Ky. | 2023-05-15
2023 | 2023-05-15 | Pikeville |  |  | 38821109D00021 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Cow Hollow, Pinsonfork, McAndrews, Ky.
2023 | 2023-05-16 | Pikeville |  |  | 38821086C00019 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarms are deteoriated. On hill behind Upper Pond Creek Fire Dept. | 3663 Pond Creek Road, McAndrews, Ky.
2023 | 2023-05-16 | Pikeville |  |  | 38821110A00051 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm is twisted badly. Need to replace. | 958 Runyon Fork, McAndrews, Ky.
2023 | 2023-05-17 | Pikeville |  |  | 38821111A20112 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 233 Homemade Hollow, McVeigh, Ky.
2023 | 2023-05-17 | Pikeville |  |  | 38821135A00003 |  | 3201001-TOM WATKINS / POND CREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarms are rotten/deteoriated. Pole was installed in 1967, seems solid but might want to consider replacing pole also. Probably use truck when dry if you go through the gate. | 6639 Straight Hollow, Upper Pond Creek, McAndrews, Ky.
2023 | 2023-05-18 | Pikeville | 85096065 | DKY0120765 | 37830187D00184 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2023-05-31
2023 | 2023-05-18 | Pikeville |  |  | 38831127B00377 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Weddington Branch, Pikeville, Ky. | 2023-05-18
2023 | 2023-05-22 | Pikeville |  |  | 38831127A00163 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Mullins Addition, Pikeville, Ky. | 2023-05-22
2023 | 2023-05-22 | Pikeville | 85373771 | DKY0121137 | 38831127B00279 |  | 3402003-KEYSER / MULLINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line | 20 First Street, Mossy Bottom, Pikeville, Ky. | 2023-08-23
2023 | 2023-05-22 | Pikeville |  |  | 38831127B00324 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Pikeville, Ky. | 2023-05-22
2023 | 2023-05-22 | Pikeville |  |  | 38831151A00224 |  | 3402003-KEYSER / MULLINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Middle Street, Coal Run Village, Ky. | 2023-05-22
2023 | 2023-05-22 | Pikeville | 86329143 | DKY0122619 | 38831151A00226 |  | 3402003-KEYSER / MULLINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated/rotten pole installed 1955. @ In front of KSP building. | 3483 N Mayo Trail, Pikeville, Ky.
2023 | 2023-05-22 | Pikeville |  |  | 38831151A00442 |  | 3402003-KEYSER / MULLINS | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. No truck. | Rural King Plaza, Pikeville, Ky. @ between Rural King and McDonalds on 3 phase.
2023 | 2023-05-22 | Pikeville | 85389276 | DKY0121159 | 38831151A00446 |  | 3402003-KEYSER / MULLINS | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. Behind Dollar General. | N Mayo Trail, Pikeville, Ky. | 2023-07-10
2023 | 2023-05-23 | Pikeville | 85400363 | DKY0121184 | 38831077A00275 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bracket | 620 Conn St, Ivel, KY 41642, USA | 2023-07-10
2023 | 2023-05-23 | Pikeville |  |  | 38831103000054 |  | 3402003-KEYSER / MULLINS | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Adkins Branch, Cowpen Road, Pikeville, Ky. | 2023-05-23
2023 | 2023-05-24 | Pikeville |  |  | 38831128B10641 |  | 3402002-KEYSER / STONECOAL | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken hanging down the pole. Last transformer in Mims Branch. | 381 Mims Branch, Pikeville, Ky.
2023 | 2023-05-24 | Pikeville | 85445563 | DKY0121248 | 38831152000163 |  | 3402002-KEYSER / STONECOAL | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer @ lay down yard on tollage creek | Tollage Creek, Pikeville, Ky. | 2023-08-22
2023 | 2023-05-24 | Pikeville | 85445563 | DKY0121248 | 38831152000189 |  | 3402002-KEYSER / STONECOAL | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 487 Tollage Creek, Pikeville, Ky. | 2023-08-22
2023 | 2023-05-30 | Pikeville |  |  | 38821105B00047 |  | 3402002-KEYSER / STONECOAL | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 890 Knob Fork, Zebulon, Ky.
2023 | 2023-05-30 | Pikeville |  |  | 38821105B30467 |  | 3402002-KEYSER / STONECOAL | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive duplex hanging down pole. | 890 Knob Fork, Zebulon, Ky.
2023 | 2023-05-30 | Pikeville |  |  | 38821105D00062 |  | 3402002-KEYSER / STONECOAL | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 229 Taylor Road, Zebulon, Ky.
2023 | 2023-05-30 | Pikeville |  |  | 38821105D00346 | TRUE | 3402002-KEYSER / STONECOAL | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 229 Taylor Road, Zebulon, Ky.
2023 | 2023-05-31 | Pikeville | 85167766 | DKY0120879 | 38820966A20596 |  | 3417601-NEW CAMP / SOUTH SIDE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 620 New Camp Rd, South Williamson, KY 41503, USA | 2023-06-13
2023 | 2023-05-31 | Pikeville | 86445195 | DKY0122842 | 38821129B00008 |  | 3402002-KEYSER / STONECOAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten at ground line. @ Old Dils Mobile Home Supply | 2359 Town Mountain Rd, Pikeville, KY 41501, USA | 2024-01-08
2023 | 2023-06-01 | Pikeville |  |  | 38831151D00123 |  | 3402001-KEYSER / THOMPSON RD | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 626 Lykins Creek, Pikeville, KY 41501, USA
2023 | 2023-06-02 | Pikeville | 85172639 | DKY0120905 | 37820009C00086 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 166 Abes Branch, Jamboree, KY 41553, USA | 2023-07-06
2023 | 2023-06-05 | Pikeville |  |  | 38821083D00049 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken.@ just above the station.. | 3779 KY-194, Kimper, KY 41539, USA
2023 | 2023-06-05 | Pikeville |  |  | 38821107000095 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken. Hanging down pole. Will probably need to install new anchor. | 4104 State Hwy 194 E, Kimper, KY 41539, USA
2023 | 2023-06-05 | Pikeville |  |  | 38821107000096 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire rusted in two. Don’t see an anchor. Will need to install one. | 4104 State Hwy 194 E, Kimper, KY 41539, USA
2023 | 2023-06-05 | Pikeville |  |  | 38821108000176 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Gannon Lane, Kimper, Ky. | 2023-06-05
2023 | 2023-06-05 | Pikeville |  |  | 38821108D30001 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 510 Trap Fork, Kimper, Ky.
2023 | 2023-06-06 | Pikeville |  |  | 38821108000186 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 7673 Ky 194 E, Kimper, Ky.
2023 | 2023-06-06 | Pikeville |  |  | 38821108000187 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. No truck. Service drop hanging down pole | 7673 Ky 194 E, Kimper, Ky.
2023 | 2023-06-06 | Pikeville |  |  | 38821108000197 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Kentucky, USA
2023 | 2023-06-06 | Pikeville |  |  | 38821131000029 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Guy wire broken. Another slacked. Need reattached and tightened. | 1374 Sunshine Lane, Kimper, Ky.
2023 | 2023-06-06 | Pikeville |  |  | 38821132000048 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 853 Varney Branch, Kimper, Ky.
2023 | 2023-06-06 | Pikeville | 86443965 | DKY0122816 | 38821132000105 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace pole badly burned by fire. It’s pole next to 105 inside the fence..@ Kimper Grade School | 8223 Ky 194 E, Kimper, Ky.
2023 | 2023-06-06 | Pikeville |  |  | 38821132000151 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Hurricane Branch, Kimper, Ky.
2023 | 2023-06-08 | Pikeville | 86515890 |  | 37820004000004 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 105 Layne Branch, Kimper, Ky.
2023 | 2023-06-08 | Pikeville |  |  | 37820029000007 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. About mile up holler. | Layne Branch, Kimper, Ky.
2023 | 2023-06-08 | Pikeville |  |  | 38821132000039 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. Last pole in Rattlesnake Br | Rattlesnake Branch, Kimper, Ky.
2023 | 2023-06-08 | Pikeville |  |  | 38821133000018 |  | 3411802-JOHNSCREE / RACCOON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1075 Pritchard Fork, Kimper, Ky.
2023 | 2023-06-08 | Pikeville |  |  | 38821134000013 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Gabriel Fork, Kimper, Ky. | 2023-06-08
2023 | 2023-06-08 | Pikeville |  |  | 38821134000013 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Gabriel Fork, Kimper, Ky. | 2023-06-08
2023 | 2023-06-08 | Pikeville |  |  | 38821134000013 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Gabriel Fork, Kimper, Ky. | 2023-06-08
2023 | 2023-06-09 | Pikeville |  |  | 37820031B00006 |  | 3411802-JOHNSCREE / RACCOON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Long Fork, Kimper, Ky | 2023-06-09
2023 | 2023-06-12 | Pikeville | 85258014 | DKY0120999 | 37820009C00121 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | Phelps, KY, USA | 2023-12-04
2023 | 2023-06-12 | Pikeville | 85258205 | DKY0121008 | 38821111D00160 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 3241 Left Fork Blackberry Rd, Ransom, KY 41558, USA | 2023-07-10
2023 | 2023-06-14 | Pikeville |  |  | 38820845A00156 |  | 2150501-BORDERLAND / NOLAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral conductor down. | 11565 State Hwy 292 W, Belfry, Ky.
2023 | 2023-06-14 | Pikeville |  |  | 38820845B00232 |  | 2150501-BORDERLAND / NOLAN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Pole top pin/ insulator damage | 12258 State Hwy 292 W, Belfry, Ky
2023 | 2023-06-14 | Pikeville | 85488817 | DKY0121307 | 38820869B00282 |  | 2150501-BORDERLAND / NOLAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. May need to cut a few limbs to get to the pole with bucket | 7514 State Hwy 292 W, Belfry, Ky. | 2023-07-21
2023 | 2023-06-15 | Pikeville |  |  | 38820868D00043 |  | 2150501-BORDERLAND / NOLAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ Marcum Bottom | N Big Creek Road, Belfry, Ky.
2023 | 2023-06-15 | Pikeville |  |  | 38820892A00035 |  | 2150501-BORDERLAND / NOLAN | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer are covered with vines | N Big Creek Rd & Bent Branch Rd, Kentucky 41514, USA
2023 | 2023-06-16 | Pikeville |  |  | 38820869B00211 |  | 2150502-BORDERLAND/CHATTAROY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 6786 State Hwy 292 W, Belfry, Ky.
2023 | 2023-06-16 | Pikeville |  |  | 38820869B00385 |  | 2150502-BORDERLAND/CHATTAROY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer | 6786 State Hwy 292 W, Belfry. Ky.
2023 | 2023-06-16 | Pikeville |  |  | 38820917B00140 |  | 2150502-BORDERLAND/CHATTAROY | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down the pole | 658 Slaters Branch, Belfry, KY 41514, USA
2023 | 2023-06-16 | Pikeville |  |  | 38820917C00416 |  | 2150502-BORDERLAND/CHATTAROY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 4276 State Hwy 292 W, Belfry, Ky.
2023 | 2023-06-19 | Pikeville |  |  | 38820963A00037 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Rockhouse Fork, Big Creek, Sidney, Ky. | 2023-06-19
2023 | 2023-06-19 | Pikeville |  |  | 38820963C00011 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ Old Lexington coal entrance about 1/4 mile up. | Rockhouse Fork, N Big Creek, Sidney, Ky.
2023 | 2023-06-19 | Pikeville |  |  | 38820963C00029 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Needs guy protector | N Big Creek Rd & Rockhouse Fork, Kentucky 41514, USA | 2023-06-19
2023 | 2023-06-19 | Pikeville |  |  | 38820963C00029 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Needs guy protector | N Big Creek Rd & Rockhouse Fork, Kentucky 41514, USA | 2023-06-19
2023 | 2023-06-19 | Pikeville |  |  | 38820963C00029 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Needs guy protector | N Big Creek Rd & Rockhouse Fork, Kentucky 41514, USA | 2023-06-19
2023 | 2023-06-19 | Pikeville |  |  | 38820964B00129 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer with service drop hanging down pole. | 2729 N Big Creek Rd, Belfry, KY 41514, USA
2023 | 2023-06-19 | Pikeville |  |  | 38820964B40172 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer bank | 2865 N Big Creek Rd, Belfry, KY 41514, USA
2023 | 2023-06-19 | Pikeville |  |  | 38820964B41041 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 2865 N Big Creek Rd, Belfry, KY 41514, USA
2023 | 2023-06-19 | Pikeville |  |  | 38820988A00018 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. @ just below Smith Loop. | N Big Creek, Sidney, Ky.
2023 | 2023-06-19 | Pikeville |  |  | 38820988A00082 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | N Big Creek, Sidney, Ky. | 2023-06-19
2023 | 2023-06-20 | Pikeville |  |  | 38820963D00084 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | N Big Creek Rd & Rockhouse Fork, Kentucky 41514, USA | 2023-06-20
2023 | 2023-06-20 | Pikeville |  |  | 38820963D00086 |  | 3414301-SIDNEY/BIG CREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop | 1780 Rockhouse Road, Sidney, Ky.
2023 | 2023-06-20 | Pikeville |  |  | 38820987D00022 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 3648 Rockhouse Road, Sidney, Ky.
2023 | 2023-06-20 | Pikeville | 86486126 | DKY0122920 | 38821011C00137 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace rotted pole installed in 1960 | 4491 Rock House Rd, Sidney, Ky.
2023 | 2023-06-20 | Pikeville |  |  | 38821011D00139 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 4708 Rockhouse Road, Sidney, Ky.
2023 | 2023-06-20 | Pikeville |  |  | 38821011D00148 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Pinson Fork, Rockhouse Road, Sidney, Ky.
2023 | 2023-06-20 | Pikeville | 86482784 | DKY0122907 | 38821035000003 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | YES | Replace deteoriated /rotted pole installed 1950. Remove inactive transformer | Pinson Fork, Rockhouse Road, Sidney, Ky.
2023 | 2023-06-20 | Pikeville |  |  | 38821035000005 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Pinson Fork, Rockhouse Road,Sidney, Ky.
2023 | 2023-06-22 | Pikeville |  |  | 38821012D00206 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Did Fork, Sidney, Ky.
2023 | 2023-06-22 | Pikeville |  |  | 38821060C00017 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Dix Fork, Sidney, Ky. | 2023-06-22
2023 | 2023-06-22 | Pikeville |  |  | 38821060C00018 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 2993 Dix Fork, Sidney, KY 41564, USA
2023 | 2023-06-26 | Pikeville |  |  | 38821013B00069 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Meathouse Fork, Sidney, Ky. | 2023-06-26
2023 | 2023-06-26 | Pikeville |  |  | 38821060B00037 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 4119 Dix Fork, Sidney, KY 41564, USA
2023 | 2023-06-27 | Pikeville | 85378069 | DKY0121147 | 37830093000258 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES |  | Kentucky, USA | 2023-07-26
2023 | 2023-06-27 | Pikeville |  |  | 38821037D00046 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Transformer is covered with vines | Thornsberry Hollow, Pigeonroost, Canada, Ky. | 2023-11-08
2023 | 2023-06-27 | Pikeville | 86476136 | DKY0122890 | 38821061A00101 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten @ ground line. | 2239 Meathouse Fork, Canada, KY 41519, USA
2023 | 2023-06-27 | Pikeville | 85373625 | DKY0121135 | 38831027C00546 |  | 3400101-ALLEN / DISTRIBUTION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | other: customer owned attachment | KPC | YES | Call customer to unlock gate Bill Derossett (606)226-8358 | 114 Nelson Dr, Dwale, KY 41621, USA | 2023-07-19
2023 | 2023-06-28 | Pikeville |  |  | 38821013B00267 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 410 Pipeyard Hollow, Canada, KY 41519, USA
2023 | 2023-06-28 | Pikeville |  |  | 38821013D00194 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 198 Groundhog Branch, Canada, Ky.
2023 | 2023-06-28 | Pikeville |  |  | 38821037C10397 |  | 3414302-SIDNEY/COBURN MOUNTAIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | U.S. Hwy 119 N, Sidney, Ky.
2023 | 2023-06-29 | Pikeville | 86463200 | DKY0122884 | 38820967A40167 |  | 2150103-SPRIGG / SPRIGG | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole leaning. Need to replace or straighten. | State Hwy 292 E, Belfry, Ky.
2023 | 2023-06-29 | Pikeville |  |  | 38820967B00140 |  | 2150103-SPRIGG / SPRIGG | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 2802 State Hwy 292 E, Belfry, KY 41514, USA
2023 | 2023-06-29 | Pikeville | 86463005 | DKY0122871 | 38820967D20132 |  | 2150103-SPRIGG / SPRIGG | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole leaning. Need to straighten or replace. | 3403 State Hwy 292 E, Belfry, KY 41514, USA
2023 | 2023-06-29 | Pikeville | 86463110 | DKY0122879 | 38820967D20135 |  | 2150103-SPRIGG / SPRIGG | Line Work | OH |  | pole: leaning, burned more than 50% remaining | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | YES | Pole leaning. Need to straighten or replace. Remove inactive transformer. | 2918 State Hwy 292 E, Belfry, Ky.
2023 | 2023-06-29 | Pikeville |  |  | 38820991C00061 |  | 2150103-SPRIGG / SPRIGG | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Maynard Branch, State Hwy 292 E, Belfry, Ky.
2023 | 2023-06-29 | Pikeville |  |  | 38820991C00065 |  | 2150103-SPRIGG / SPRIGG | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | State Hwy 292 E, Belfry, Ky. | 2023-06-29
2023 | 2023-06-29 | Pikeville |  |  | 38820991D10295 |  | 2150103-SPRIGG / SPRIGG | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer are covered with vines | McCoy Branch, State Hwy 292 E, Belfry, Ky. | 2023-10-10
2023 | 2023-06-29 | Pikeville |  |  | 38821016A00224 |  | 2150103-SPRIGG / SPRIGG | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | State Hwy 292 E, Burnwell, Ky.
2023 | 2023-06-30 | Pikeville |  |  | 38821016C00016 |  | 2150105-SPRIGG / MATEWAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 409 River Road, Buskirk, Ky.
2023 | 2023-07-05 | Pikeville | 85426729 | DKY0121223 | 37830209000138 |  | 3407103-TOPMOST / KITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 9199 Highway 7 S, Kite, KY 41862 | 2023-11-02
2023 | 2023-07-05 | Pikeville | 86529810 | DKY0123004 | 38821058B40942 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. @ old car wash | Ky Hwy 194 E, Meta, Ky. | 2024-01-10
2023 | 2023-07-05 | Pikeville |  |  | 38821082000188 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , Forestry - DESCRIBE IN COMMENTS | KPC | NO | Remove inactive transformer.@ just before Blackburn Bottom on left on hill. Will need some minor tree trimming to get truck to pole. | Ottis Hill, Meta, Ky.
2023 | 2023-07-05 | Pikeville |  |  | 38821082C20349 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 45 Tilden King Road, Meta, Ky.
2023 | 2023-07-05 | Pikeville | 86520405 | DKY0122986 | 38821083B12031 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer bank. @ above Bevins Branch on right. | State Hwy 194 E, Meta, Ky. | 2024-01-05
2023 | 2023-07-06 | Pikeville |  |  | 38820937000002 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Brushy Road, Pikeville, Ky. | 2023-07-06
2023 | 2023-07-06 | Pikeville |  |  | 38820937000031 | TRUE | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 549 Curry Branch, Brushy Road, Pikeville, Ky.
2023 | 2023-07-06 | Pikeville |  |  | 38820961000099 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. @ 1/4 mi up rfk | Rfk Brushy Road, Pikeville, Ky.
2023 | 2023-07-06 | Pikeville |  |  | 38820985000021 |  | 3411801-JOHNSCREE / META | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral conductor down | 3269 Rfk Brushy Road, Pikeville, Ky.
2023 | 2023-07-06 | Pikeville |  |  | 38821058B00334 |  | 3411801-JOHNSCREE / META | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral conductor down/missing | Ford Mountain, Meta, Ky.
2023 | 2023-07-07 | Pikeville |  |  | 38821058B00231 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 38 Meta Lane, Meta, Ky.
2023 | 2023-07-07 | Pikeville |  |  | 38821058B00253 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 77 Deskins Road, Meta, Ky.
2023 | 2023-07-07 | Pikeville |  |  | 38821058B00285 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 9598 Meta Hwy, Meta, Ky.
2023 | 2023-07-07 | Pikeville |  |  | 38821058C00112 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 759 Smith Fork, Meta, Ky.
2023 | 2023-07-10 | Pikeville |  |  | 38820961000012 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 180 Brushy School Road, Pikeville,Ky.
2023 | 2023-07-10 | Pikeville |  |  | 38820961000053 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 219 Gin Fork, Brushy Road, Pikeville, Ky.
2023 | 2023-07-10 | Pikeville |  |  | 38820961000081 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 7786 Brushy Road, Pikeville, Ky.
2023 | 2023-07-10 | Pikeville |  |  | 38820962000048 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 1035 Gin Fork, Brushy Road, Pikeville, Ky.
2023 | 2023-07-10 | Pikeville |  |  | 38820986000049 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 524 Hurricane Branch, Brushy Road, Pikeville,Ky.
2023 | 2023-07-10 | Pikeville | 86486220 | DKY0122924 | 38820986000060 |  | 3411801-JOHNSCREE / META | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteoriated pole installed in 1957 | John Young Branch, Brushy Road, Pikeville, Ky. | 2024-01-08
2023 | 2023-07-10 | Pikeville |  |  | 38820986C10155 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer@ mouth of Hurricane Branch | Hurricane Branch, Brushy Road, Pikeville, Ky.
2023 | 2023-07-11 | Pikeville |  |  | 38821010000040 |  | 3411801-JOHNSCREE / META | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down the pole | 556 Stanley Fork, Rfk Brushy, Pikeville, Ky.
2023 | 2023-07-11 | Pikeville |  |  | 38821010000059 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 326 Wolf Branch, Lfk Brushy, Pikeville, Ky.
2023 | 2023-07-11 | Pikeville |  |  | 38821010000128 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 770 Stanley Fork, Rfk Brushy, Pikeville, Ky.
2023 | 2023-07-11 | Pikeville |  |  | 38821010000145 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 356 Stanley Fork, Rfk Brushy, Pikeville, Ky.
2023 | 2023-07-11 | Pikeville |  |  | 38821011A00037 |  | 3411801-JOHNSCREE / META | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Ray Branch, Lfk Brushy Road, Pikeville, Ky. | 2023-07-11
2023 | 2023-07-11 | Pikeville |  |  | 38821034000011 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. @ head of Stanley Fork. | Stanley Fork, Rfk Brushy, Pikeville, Ky.
2023 | 2023-07-11 | Pikeville |  |  | 38821035000189 |  | 3411801-JOHNSCREE / META | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Bent Mountain, Meta, Ky.
2023 | 2023-07-12 | Pikeville |  |  | 37830047D00024 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 3607 Island Creek, Pikeville, Ky.
2023 | 2023-07-12 | Pikeville | 85489198 | DKY0121306 | 37830048B11119 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm broken. On hill going over to Bob Amos park. 4th pole from station. This is double arm with only one arm broken. STATION ZONE. | Narrows Road, Pikeville, Ky. | 2023-07-26
2023 | 2023-07-12 | Pikeville | 83966882 | DKY0121091 | 37830048B40185 | TRUE | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  | lightning arresters/insulators: damaged | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Epoxilators deteoriated/melting. Pole is covered with vines. | 128 Marion Branch, Pikeville, Ky.
2023 | 2023-07-12 | Pikeville |  |  | 37830072A00460 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH | cutout: damaged |  |  | KPC | NO | Cutout door burned up on transformer bank. @ SGS BLDG. Talked to customer Bob Barringer @ the bldg and he said it would be alright to de-energize the bank because they weren’t doing anything in the bldg at this time.Pole above the regulator bank. Contacted SDS to have de-energized. | 1802 Island Creek, Pikeville, Ky.
2023 | 2023-07-13 | Pikeville | 83966923 | DKY0121419 | 37830072B00069 | TRUE | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilators deteoriated/ melted | 640 Lfk Island Creek, Pikeville, Ky.
2023 | 2023-07-13 | Pikeville |  |  | 37830095000121 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 418 Road Fork, Pikeville, Ky.
2023 | 2023-07-13 | Pikeville |  |  | 37830095000233 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 234 Billy Compton Branch, Pikeville, Ky.
2023 | 2023-07-13 | Pikeville |  |  | 37830095000241 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 1006 Lfk Island Creek, Pikeville, Ky.
2023 | 2023-07-13 | Pikeville |  |  | 37830095000272 |  | 3410502-S.PIKEVIL / ISLANDCRE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Lfk Island Creek, Pikeville, Ky. | 2023-07-13
2023 | 2023-07-17 | Pikeville | 86459551 | DKY0122844 | 37830047B00159 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | UG | UG conduit: damaged or separated |  |  | KPC | YES | Underground junction box rusted out. Needs replaced | 349 Kati Street, Cedar Gap, Pikeville, Ky.
2023 | 2023-07-17 | Pikeville | 86461715 | DKY0122864 | 37830047B00201 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | UG | UG conduit: damaged or separated |  |  | KPC | YES | Underground junction box rusted out. Needs replaced@ corner of Evan st/ Summer St. | 107 Evan Street, Cedar Gap, Pikeville, Ky.
2023 | 2023-07-17 | Pikeville | 76908000 | DKY0110179 | 37830071000026 | TRUE | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten @ ground line | 265 Coon Br, Lfk Island Creek, Pikeville, Ky.
2023 | 2023-07-17 | Pikeville |  |  | 37830094000037 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 179 Ray Branch, Lfk Island Creek, Pikeville, Ky.
2023 | 2023-07-17 | Pikeville |  |  | 37830095000050 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. Truck access through yard with customer permission. | 2239 Lfk Island Creek, Pikeville, Ky.
2023 | 2023-07-17 | Pikeville | COMPLETE IN FIELD | COMPLETE IN FIELD | 37830095000073 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer@ just above Sleepy Hollow on left | Lfk Island Creek, Pikeville, Ky.
2023 | 2023-07-17 | Pikeville |  |  | 37830095000076 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 2886 Lfk Island Creek, Pikeville, Ky.
2023 | 2023-07-17 | Pikeville |  |  | 37830095000081 |  | 3410502-S.PIKEVIL / ISLANDCRE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer@ about 3.2 miles up left fork where house burned on right. | Lfk Island Creek, Pikeville, Ky.
2023 | 2023-07-17 | Pikeville | 85882653 | DKY0121931 | 38831125C40088 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2023 | 2023-07-19 | Pikeville |  |  | 37830139C00140 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Clear Creek, Hi Hat, Ky. | 2023-07-19
2023 | 2023-07-19 | Pikeville |  |  | 37830139C00140 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Clear Creek, Hi Hat, Ky. | 2023-07-19
2023 | 2023-07-19 | Pikeville |  |  | 37830140B00078 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer@ mouth of Reynolds Br. | Reynolds Branch, Ligon, Ky.
2023 | 2023-07-19 | Pikeville |  |  | 37830140B00079 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteoriated pole installed 1946. Arms appear to be rotten, pole sounds hollow. | 68 Reynolds Branch, Hi Hat, Ky.
2023 | 2023-07-19 | Pikeville |  |  | 37830140B00165 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteoriated pole installed 1956 | 68 Reynolds Branch, Hi Hat, Ky.
2023 | 2023-07-19 | Pikeville | Outage # 4485431 |  | 37830140D00012 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | cutout: damaged |  |  | KPC | NO | Transformer cutout broken. Contacted SDS to have crew make repairs. Customer service restored @ 15:15 | 16588 Hwy 979, Ligon, Ky. | 2023-07-19
2023 | 2023-07-20 | Pikeville |  |  | 37830021000044 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 723 Ky 3379, Galveston, Ky.
2023 | 2023-07-20 | Pikeville |  |  | 37830045000033 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Center phase floating | 58 Lee Akers Drive, Branham Creek, Galveston, Ky.
2023 | 2023-07-20 | Pikeville |  |  | 37830069000057 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Ky 3379, Galveston, Ky. | 2023-07-20
2023 | 2023-07-20 | Pikeville |  |  | 37830094000006 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 5171 Ky 3379, Galveston, Ky.
2023 | 2023-07-21 | Pikeville |  |  | 37830044000007 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 206 Lfk Frazier’s Branch, Grethel, Ky.
2023 | 2023-07-21 | Pikeville |  |  | 37830044000085 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 206 Lfk Frazier’s Branch, Grethel, Ky.
2023 | 2023-07-21 | Pikeville |  |  | 37830045000074 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , Forestry - DESCRIBE IN COMMENTS | KPC | NO | Remove inactive transformer. A lot of Cudzu vine around the pole | 203 Newsome Branch, Grethel, Ky.
2023 | 2023-07-21 | Pikeville |  |  | 37830045000242 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Marvin Heights, Grethel, Ky.
2023 | 2023-07-24 | Pikeville |  |  | 37830140C00138 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 14673 KY-979, Beaver, KY 41604, USA
2023 | 2023-07-24 | Pikeville |  |  | 37830140C00333 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Buckhorn Road, Beaver, Ky.
2023 | 2023-07-24 | Pikeville |  |  | 37830140D00283 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. Satellite dish on pole. | 16350 Ky. Rte 979, Ligon, Ky.
2023 | 2023-07-24 | Pikeville |  |  | 37830140D30071 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 15055 KY-979, Beaver, KY 41604, USA
2023 | 2023-07-24 | Pikeville |  |  | 37830141000011 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 14180 KY-979, Beaver, KY 41604, USA
2023 | 2023-07-24 | Pikeville |  |  | 37830141000071 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 382 Beech SPG, Tackett Fk, Beaver, Ky.
2023 | 2023-07-24 | Pikeville |  |  | 37830141000212 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 50 Lfk Moore Branch, Ligon, Ky.
2023 | 2023-07-24 | Pikeville |  |  | 37830164000038 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace is broken@ just past Ligon Camp Rd | KY-979, Kentucky, USA
2023 | 2023-07-25 | Pikeville |  |  | 37830068000004 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 4704 KY-680, Grethel, KY 41631, USA
2023 | 2023-07-25 | Pikeville |  |  | 37830068000059 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 355 Little Branch, Hamilton Branch, Grethel, Ky.
2023 | 2023-07-25 | Pikeville | 85687831 | DKY0121622 | 37830068000083 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 4197 KY-680, Grethel, KY 41631, USA | 2023-08-15
2023 | 2023-07-25 | Pikeville |  |  | 37830068000210 |  | 3403201-BEAVERCRE / LIGON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down the pole. | 3800 Ky 680, Hamilton Branch, Grethel, Ky.
2023 | 2023-07-25 | Pikeville |  |  | 37830069000190 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor broke. No truck. @ Dark Hollow | 8099 KY-979, Grethel, KY 41631, USA
2023 | 2023-07-26 | Pikeville |  |  | 37830068000112 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole is split down to the brace bolt. | 943 Mink Branch, Harold, KY 41635, USA
2023 | 2023-07-26 | Pikeville |  |  | 37830068000125 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 107 Rocky Branch, Mink Branch, Craynor, Ky
2023 | 2023-07-26 | Pikeville |  |  | 37830092000001 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. @ mouth of Rocky Branch | 960 Mink Branch, Harold, KY 41635, USA
2023 | 2023-07-26 | Pikeville |  |  | 37830092000163 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 1823 Mink Branch, Craynor, Ky.
2023 | 2023-07-26 | Pikeville |  |  | 37830093000261 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 11680 KY-979, Teaberry, KY 41660, USA
2023 | 2023-07-26 | Pikeville |  |  | 37830093000270 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 290 Blackberry Lane, Teaberry, Ky.
2023 | 2023-07-26 | Pikeville |  |  | 37830093000337 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 290 Blackberry Lane, Teaberry, Ky
2023 | 2023-07-26 | Pikeville |  |  | 37830093C20394 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 56 Willies Road, Ky 979, Teaberry, Ky.
2023 | 2023-07-26 | Pikeville |  |  | 37830117000134 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer@ just before Tinker Fork on right. | 12160 KY-979, Teaberry, KY 41660, USA
2023 | 2023-07-27 | Pikeville |  |  | 37830141000139 | TRUE | 3403201-BEAVERCRE / LIGON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down the pole | 2718 Tinkerfork, Teaberry, Ky.
2023 | 2023-07-31 | Pikeville |  |  | 37830141000016 | TRUE | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 2026 Tinkerfork, Teaberry, Ky.
2023 | 2023-07-31 | Pikeville |  |  | 37830141000022 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  |  | KPC | NO | Neutral stolen or missing.. 4 copper | 2340 Tinkerfork, Teaberry, Ky.
2023 | 2023-07-31 | Pikeville |  |  | 37830141000111 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 2124 Tinkerfork, Teaberry, Ky.
2023 | 2023-07-31 | Pikeville |  |  | 37830141000239 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 2336 Tinkerfork, Teaberry, Ky.
2023 | 2023-07-31 | Pikeville | 85611039 | DKY0121497 | 38820941D00191 |  | 3417602-NEW CAMP / APPAL. REG. HOSPITAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 1606 Central Ave, South Williamson, KY 41503, USA
2023 | 2023-08-01 | Pikeville |  |  | 37830117000087 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Mitchell Branch, Teaberry, Ky. | 2023-08-01
2023 | 2023-08-01 | Pikeville |  |  | 37830117000087 |  | 3403201-BEAVERCRE / LIGON | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Mitchell Branch, Teaberry, Ky. | 2023-08-01
2023 | 2023-08-02 | Pikeville | 85636619 | DKY0121530 | 37830064000108 |  | 3413402-GARRETT / LACKEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | crossarm/braces: deteriorated, not rotten | Forestry - DESCRIBE IN COMMENTS | KPC | YES | Tress need trimmed and cleaned up front yard. | 13020 KY-550, Lackey, KY 41643, USA | 2023-08-16
2023 | 2023-08-02 | Pikeville |  |  | 37830091A00065 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteoriated pole installed 1954. Switch pole. | Spewing Camp Branch , Price, Ky.
2023 | 2023-08-02 | Pikeville |  |  | 37830115000153 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Spewing Camp Branch, Price, Ky. | 2023-08-02
2023 | 2023-08-02 | Pikeville |  |  | 37830115000153 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Spewing Camp Branch, Price, Ky. | 2023-08-02
2023 | 2023-08-03 | Pikeville |  |  | 37830116000006 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 3645 Frasure Creek, McDowell, Ky.
2023 | 2023-08-04 | Pikeville |  |  | 37830139A10061 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down the pole. | N Locust Road, Hi Hat, Ky.
2023 | 2023-08-04 | Pikeville |  |  | 37830139A30303 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | S Locust Road, Hi Hat, Ky. | 2023-08-04
2023 | 2023-08-07 | Pikeville |  |  | 37830115000107 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm deteoriated. Pole installed 1972 | 32 Tunnel Road, Price, Ky.
2023 | 2023-08-07 | Pikeville |  |  | 37830115000209 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Milan Branch, Price, Ky. | 2023-08-07
2023 | 2023-08-07 | Pikeville |  |  | 37830115000209 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Milan Branch, Price, Ky. | 2023-08-07
2023 | 2023-08-08 | Pikeville |  |  | 37830067B00133 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorating pole installed 1944 | 306 Big Bridg
2023 | 2023-08-08 | Pikeville |  |  | 37830091A00148 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 12093 KY-122, McDowell, KY 41647, USA
2023 | 2023-08-08 | Pikeville |  |  | 37830091A00223 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 12093 KY-122, McDowell, KY 41647, USA
2023 | 2023-08-09 | Pikeville |  |  | 37830115000169 |  | 3403202-BEAVER CRK / PRICE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector (2) | Tunnel Road, Price, Ky | 2023-08-09
2023 | 2023-08-09 | Pikeville |  |  | 37830139A20065 |  | 3403202-BEAVER CRK / PRICE | Forestry | OH |  |  | Circuit has since been sprayed after reported date | KPC | NO | Pole is covered with vines | Rfk Bryant Branch, Price, Ky. | 2023-09-30
2023 | 2023-08-09 | Pikeville | 86467916 | DKY0122866 | 37830139A30397 |  | 3403202-BEAVER CRK / PRICE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 16793 KY-122, Hi Hat, KY 41636, USA
2023 | 2023-08-10 | Pikeville |  |  | 38831099000079 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 1537 KY-122, Martin, KY 41649, USA
2023 | 2023-08-14 | Pikeville |  |  | 38831098D00170 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 1285 KY-122, Martin, KY 41649, USA
2023 | 2023-08-15 | Pikeville |  |  | 38831074C00108 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | N River Street, Martin, Ky. | 2023-08-15
2023 | 2023-08-15 | Pikeville |  |  | 38831075000014 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Pole top pin/insulator bent backwards | 10974 Ky 1428, Main Street, Martin, Ky.
2023 | 2023-08-15 | Pikeville |  |  | 38831075000051 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer | Ky 1428, Main Street, Martin, Ky.
2023 | 2023-08-16 | Pikeville |  |  | 38831074C00222 |  | 3408103-SALISBURY / MARTIN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Cracker Bottom, Martin, Ky. | 2023-08-16
2023 | 2023-08-16 | Pikeville |  |  | 38831074C00234 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 688 Cracker Bottom, Martin, Ky.
2023 | 2023-08-16 | Pikeville |  |  | 38831074C31074 |  | 3408103-SALISBURY / MARTIN | Forestry | OH |  |  | Area has been recleared since reported date | KPC | NO | Pole is covered with vines | 612 Cracker Bottom, Martin, Ky. | 2023-09-30
2023 | 2023-08-16 | Pikeville |  |  | 38831074D00048 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Old Post Office Street, Martin, Ky.
2023 | 2023-08-17 | Pikeville |  |  | 38831074A00182 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Crossarm is rotten. Pole was installed 1968 but still seems to be solid. Might consider changing Pole too while there. | 179 Long Fork, Bucks Branch, Martin, Ky.
2023 | 2023-08-18 | Pikeville |  |  | 38831099000123 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 2002 Hite Road, Martin, Ky.
2023 | 2023-08-18 | Pikeville |  |  | 38831123A00021 |  | 3408103-SALISBURY / MARTIN | Forestry | OH |  |  | Area has been recleared since reported date | KPC | NO | Pole is covered with vines | 3113 Hite Road, Martin, Ky. | 2023-09-30
2023 | 2023-08-18 | Pikeville |  |  | 38831123A00038 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 2893 Hite Road, Martin, Ky.
2023 | 2023-08-18 | Pikeville | 85745220 | DKY0121710 | 38831127A00175 |  | 3402003-KEYSER / MULLINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 78 Mullins School St, Pikeville, KY 41501, USA
2023 | 2023-08-21 | Pikeville |  |  | 38831098C00545 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 88 Charby Hollow, Martin, Ky.
2023 | 2023-08-21 | Pikeville | 85755008 | DKY0121724 | 38831125C30014 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 142 Hale Rd, Harold, KY 41635, USA
2023 | 2023-08-22 | Pikeville | 86228581 | DKY0122485 | 38831098A30843 | TRUE | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 253 Stephens Branch, Martin, Ky. | 2023-12-18
2023 | 2023-08-23 | Pikeville |  |  | 38831098B00600 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. In front of Warco Apts. Pole is tagged 597 , but it’s 600 on Atlas. | Ky Rte 80, Martin, Ky.
2023 | 2023-08-23 | Pikeville |  |  | 38831098D00134 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 131 Red Isom Hollow, Martin, Ky.
2023 | 2023-08-23 | Pikeville |  |  | 38831122000243 |  | 3408103-SALISBURY / MARTIN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 468 Johns Branch, Maytown, Ky.
2023 | 2023-08-25 | Pikeville | 85793162 | DKY0121786 | 38831078000118 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | replace bad pole and transfer transformer | 879 Mare Creek Rd, Stanville, KY 41659, USA | 2023-12-18
2023 | 2023-08-28 | Pikeville |  |  | 37830018D00042 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Cow Hollow, Drift, Ky. | 2023-08-28
2023 | 2023-08-28 | Pikeville |  |  | 37830018D00243 |  | 3402202-MCKINNEY / GIBSON | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | 7056 Ky 122, Drift, Ky.
2023 | 2023-08-28 | Pikeville |  |  | 37830042C00226 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown. No truck | Drift Hill, Drift, Ky.
2023 | 2023-08-29 | Pikeville |  |  | 37830018D40589 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines..after crossing bridge at beginning to Stumbo Hollow | 25 Ky Rte 1101, Drift, Ky.
2023 | 2023-08-29 | Pikeville |  |  | 37830019B00043 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer is covered with vines | 104 Upper Lane Siding Station, Drift, Ky.
2023 | 2023-08-29 | Pikeville |  |  | 37830019B00062 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorating/ rotting pole installed 1956 | 265 Upper Lane Siding Station, Drift, Ky.
2023 | 2023-08-29 | Pikeville |  |  | 37830019B00106 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer is covered with vines | 194 Ky 1101, Drift, Ky.
2023 | 2023-08-30 | Pikeville |  |  | 37830018D00229 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 59 Ky 1101, Drift, Ky.
2023 | 2023-08-30 | Pikeville |  |  | 37830042B00453 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Sizemore Road, Minnie, Ky. | 2023-08-30
2023 | 2023-08-30 | Pikeville |  |  | 37830042D00003 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Minnie Road, Minnie, Ky. | 2023-08-30
2023 | 2023-08-30 | Pikeville |  |  | 37830042D00112 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorating pole installed 1947 | Turner Drive, Sizemore Road, Minnie, Ky.
2023 | 2023-08-30 | Pikeville | 86180888 |  | 37830042D00349 | TRUE | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Old Sizemore Road, Minnie, Ky.
2023 | 2023-08-30 | Pikeville |  |  | 37830066C00042 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 269 Cedarcrest Drive, Minnie, Ky.
2023 | 2023-08-30 | Pikeville |  |  | 37830066C00165 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 269 Cedarcrest Drive, Mi
2023 | 2023-08-31 | Pikeville |  |  | 37830042D00058 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 9497 Ky 122, McDowell, Ky.
2023 | 2023-08-31 | Pikeville |  |  | 37830042D00444 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector 2 | Ky 122, McDowell, Ky. | 2023-08-31
2023 | 2023-08-31 | Pikeville |  |  | 37830066C00061 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorating/rotting pole installed 1954. Recloser pole behind McDowell ARH | Doty Creek, McDowell, Ky.
2023 | 2023-08-31 | Pikeville |  |  | 37830066C00069 |  | 3402202-MCKINNEY / GIBSON | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole and transformer is covered with vines | 727 Doty Creek, McDowell, Ky.
2023 | 2023-08-31 | Pikeville |  |  | 37830066D00131 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 905 Doty Branch, McDowell, Ky.
2023 | 2023-08-31 | Pikeville |  |  | 37830090000018 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 1659 Doty Branch, McDowell, Ky.
2023 | 2023-09-05 | Pikeville |  |  | 37830066C00116 |  | 3402202-MCKINNEY / GIBSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Ky 122 , McDowell, Ky. | 2023-09-05
2023 | 2023-09-05 | Pikeville |  |  | 37830067A00094 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines. @ Ky 122 & Ky 680 intersection. | Ky 122, McDowell, Ky
2023 | 2023-09-05 | Pikeville |  |  | 37830067A00184 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 9986 Ky 122, McDowell, Ky.
2023 | 2023-09-05 | Pikeville |  |  | 37830067D00161 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer.@ Browns Branch | 625 Ky 680, Bill Hall Branch, McDowell, Ky.
2023 | 2023-09-06 | Pikeville |  |  | 37830067D10197 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive pole and transformer,etc. | 458 Frasure Creek, McDowell, Ky.
2023 | 2023-09-06 | Pikeville |  |  | 37830068000100 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive primary conductors hanging down the pole. | 2441 Bill Hall Branch, McDowell, Ky.
2023 | 2023-09-06 | Pikeville |  |  | 37830068000133 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 2530 Ky 680, Bill Hall Branch, McDowell, Ky.
2023 | 2023-09-06 | Pikeville |  |  | 37830091C00153 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | Gearheart Branch, McDowell, Ky.
2023 | 2023-09-07 | Pikeville |  |  | 37830091C00026 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 2191 Frasure Creek, McDowell, Ky.
2023 | 2023-09-07 | Pikeville |  |  | 37830091C00117 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 188 Hood Fork, McDowell, Ky.
2023 | 2023-09-07 | Pikeville |  |  | 37830091C00298 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , Forestry - DESCRIBE IN COMMENTS | KPC | NO | Remove inactive transformer bank. Probably will need ROW cut around pole. | 56 Ramsey Drive, McDowell, Ky.
2023 | 2023-09-07 | Pikeville |  |  | 37830092000148 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 480 Hood Fork, McDowell, Ky.
2023 | 2023-09-07 | Pikeville |  |  | 37830092000177 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 273 Hood Fork, McDowell, Ky.
2023 | 2023-09-07 | Pikeville |  |  | 37830116000030 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 1415 Ned Fork, McDowell, Ky.
2023 | 2023-09-07 | Pikeville |  |  | 37830116000035 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorating/rotting pole installed in 1948. Pole is split at top. Angle pole with broken guy wire. | 1710 Ned Fork, McDowell, Ky.
2023 | 2023-09-07 | Pikeville |  |  | 37830116000038 |  | 3402202-MCKINNEY / GIBSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , Forestry - DESCRIBE IN COMMENTS | KPC | NO | Remove inactive transformer. Probably will need ROW cut around pole. Last pole in Ned Fork. | Ned’s Fork, McDowell, Ky.
2023 | 2023-09-08 | Pikeville |  |  | 38831051C10683 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Ky 1428, Allen, Ky. | 2023-09-08
2023 | 2023-09-08 | Pikeville |  |  | 38831051C10683 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Ky 1428, Allen, Ky. | 2023-09-08
2023 | 2023-09-08 | Pikeville |  |  | 38831051C10683 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Ky 1428, Allen, Ky. | 2023-09-08
2023 | 2023-09-12 | Pikeville |  |  | 38831027B00352 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down the pole | Coon Street, Allen, Ky. | 2023-09-12
2023 | 2023-09-12 | Pikeville | 86428034 | DKY0122815 | 38831027B00436 |  | 3400101-ALLEN / DISTRIBUTION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorating/rotting pole installed 1960 | Beaver Avenue, Allen, Ky. | 2024-01-10
2023 | 2023-09-12 | Pikeville |  |  | 38831027C00615 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down the pole | Cemetery Road Loop, Allen, Ky.
2023 | 2023-09-12 | Pikeville |  |  | 38831027D00241 |  | 3400101-ALLEN / DISTRIBUTION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorating pole installed 1946 | 202 Fourth Street, Allen, Ky.
2023 | 2023-09-12 | Pikeville | 85903240 | DKY0121962 | 38831146C00228 |  | 3408101-SALISBURY / PRINTER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 4255 KY-122, Kentucky 41655, USA | 2023-10-26
2023 | 2023-09-13 | Pikeville | 86497873 | DKY0122937 | 38831003D00015 |  | 3400101-ALLEN / DISTRIBUTION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteoriated/rotten pole installed 1962 | May Drive, Allen, Ky.
2023 | 2023-09-13 | Pikeville |  |  | 38831003D00032 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | May Drive, Allen, Ky. | 2023-09-13
2023 | 2023-09-13 | Pikeville |  |  | 38831003D00287 |  | 3400101-ALLEN / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown on transformer bank. @ in front on Allen Elementary. | 5035 KY-1428, Prestonsburg, KY 41653, USA
2023 | 2023-09-13 | Pikeville |  |  | 38831003D00322 |  | 3400101-ALLEN / DISTRIBUTION | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Transformer bank covered with vines | 5252 KY-1428, Allen City, KY 41601, USA
2023 | 2023-09-13 | Pikeville |  |  | 38831027C00109 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | 2nd Avenue, Dwale, Ky. | 2023-09-13
2023 | 2023-09-13 | Pikeville |  |  | 38831027C20714 |  | 3400101-ALLEN / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown. No truck | 2nd Avenue, Dwale, Ky.
2023 | 2023-09-14 | Pikeville |  |  | 38831027A00506 |  | 3400101-ALLEN / DISTRIBUTION | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken, hanging down the pole. @ R.E. Michel Company. Will need to install anchor. No truck | US-23, Allen City, KY, USA
2023 | 2023-09-14 | Pikeville | 86400553 | DKY0122735 | 38831027C00371 |  | 3400101-ALLEN / DISTRIBUTION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace pole washed out around in the creek. Installed 1966 | 338 May Branch, Allen, Ky. | 2024-01-12
2023 | 2023-09-14 | Pikeville |  |  | 38831027D00037 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down the pole. | 226 Reynolds Hill, Allen City, KY 41601, USA
2023 | 2023-09-14 | Pikeville |  |  | 38831027D00548 |  | 3400101-ALLEN / DISTRIBUTION | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. Can use truck if owner will allow to back through yard. | 107 May Branch, Allen, Ky.
2023 | 2023-09-14 | Pikeville |  |  | 38831028000045 |  | 3400101-ALLEN / DISTRIBUTION | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 44 Hall Addition, Banner, Ky.
2023 | 2023-09-14 | Pikeville |  |  | 38831052A00150 |  | 3400101-ALLEN / DISTRIBUTION | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | 150 Hall Addition, Banner, Ky.
2023 | 2023-09-14 | Pikeville |  |  | 38831052A00226 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Alpike Street, Banner, Ky. | 2023-09-14
2023 | 2023-09-14 | Pikeville |  |  | 38831052C20923 |  | 3400101-ALLEN / DISTRIBUTION | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Cecil Hall Street, Banner, Ky.
2023 | 2023-09-18 | Pikeville |  |  | 37830163D00026 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines. No truck. On hill across road from Dollar General Store. | Ky 122, Bevinsville, Ky.
2023 | 2023-09-18 | Pikeville |  |  | 37830163D00029 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole top is covered with vines. No truck. Buckarm behind new Burton station. | Ky 122, Bevinsville, Ky.
2023 | 2023-09-18 | Pikeville |  |  | 37830187C00037 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteoriated pole installed 1962 | 279 Main Street, Wheelwright, Ky.
2023 | 2023-09-18 | Pikeville |  |  | 37830187C00105 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteoriated pole installed 1962. Next to Wheelwright Freewill Baptist Church | 279 KY-306, Wheelwright, KY 41669, USA
2023 | 2023-09-19 | Pikeville |  |  | 37830211C00307 | TRUE | 3400602-BURTON / WHEELWRIG | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive secondary hanging down the pole | 339 Shop Fork St, Wheelwright, KY 41669, USA
2023 | 2023-09-19 | Pikeville |  |  | 37830211C00318 |  | 3400602-BURTON / WHEELWRIG | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop low clearance. Only 6 ft above ground. I think servicer can take 2-3 ft of slack out temporarily but secondary pole needs to be installed. | 255 Hall St, Wheelwright, KY 41669, USA
2023 | 2023-09-20 | Pikeville |  |  | 37830164000115 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 22178 KY-122, Bypro, KY 41612, USA
2023 | 2023-09-21 | Pikeville | 85971925 | DKY0122073 | 37830048D10094 |  | 3410503-S.PIKEVIL / HOSPITAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | STATION ZONE |  | 2023-10-26
2023 | 2023-09-21 | Pikeville |  |  | 37830188C00037 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. | 24520 Abner Mtn, Melvin, Ky.
2023 | 2023-09-21 | Pikeville |  |  | 37830188C00263 |  | 3400602-BURTON / WHEELWRIG | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 24237 Abner Mtn, Melvin, Ky.
2023 | 2023-09-21 | Pikeville |  |  | 37830189A00288 |  | 3400602-BURTON / WHEELWRIG | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop laying on top of building. Can take slack out at service pole | 292 Lower Coal Hollow, Melvin, Ky.
2023 | 2023-09-25 | Pikeville |  |  | 37830139B00079 |  | 3400601-BURTON / LIGON-CLE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck. @ Meade Hill. Across from church. | 19153 KY-122, Hi Hat, KY 41636, USA
2023 | 2023-09-25 | Pikeville | 86096222 | DKY0122244 | 37830162000043 |  | 3400601-BURTON / LIGON-CLE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | YES | Replace rotted/deteoriated pole installed 1947.. Crossarm brace broken. Arm standing up in air. Needs immediate attention. Could cause outage. No truck. | 1021 Wolfpen Road, Buckingham, Hi Hat, Ky. | 2023-11-02
2023 | 2023-09-25 | Pikeville |  |  | 37830163A00118 |  | 3400601-BURTON / LIGON-CLE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | Wolfpen Road, Buckingham, Hi Hat, Ky.
2023 | 2023-09-26 | Pikeville |  |  | 37830163A00100 |  | 3400601-BURTON / LIGON-CLE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 20138 KY-122, Bevinsville, KY 41606, USA
2023 | 2023-09-26 | Pikeville |  |  | 37830163A00321 |  | 3400601-BURTON / LIGON-CLE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 20126 KY-122, Bevinsville, KY 41606, USA
2023 | 2023-09-26 | Pikeville |  |  | 37830187A20428 |  | 3400601-BURTON / LIGON-CLE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 182 Blue Branch, Bevinsville, Ky 41606
2023 | 2023-09-26 | Pikeville |  |  | 37830235000014 |  | 3400601-BURTON / LIGON-CLE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken@ top of hill on Jacks Creek | Ky 1428, Bevinsville, Ky.
2023 | 2023-09-28 | Pikeville |  |  | 37830187B00274 |  | 3400601-BURTON / LIGON-CLE | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm is split on end. | 2134 Jacks Creek, Bevinsville, Ky. 41606
2023 | 2023-09-28 | Pikeville |  |  | 37830211A00134 |  | 3400601-BURTON / LIGON-CLE | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | End of crossarm is split. Could cause outage.@ Bevinsville First Baptist Church. | 2899 Jacks Creek, Bevinsville, Ky. 41606
2023 | 2023-09-28 | Pikeville |  |  | 37830211D00148 | TRUE | 3400601-BURTON / LIGON-CLE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. No truck | Frozen Fork, Jacks Creek, Bevinsville, Ky.
2023 | 2023-09-28 | Pikeville |  |  | 37830211D00148 | TRUE | 3400601-BURTON / LIGON-CLE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. No truck | Frozen Fork, Jacks Creek, Bevinsville, Ky.
2023 | 2023-09-28 | Pikeville | 86417743 | DKY0122764 | 38831126C00154 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole in poor shape/rotten at top/cracking/50 years old | 1058 Broadbottom Rd
2023 | 2023-09-29 | Pikeville | 86107053 | DKY0122262 | 38831126C00732 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 889 Broad Bottom Rd, Kentucky 41501, USA
2023 | 2023-10-02 | Pikeville | 85756903 | DKY0121727 | 37820008A00038 | TRUE | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 1292 Calloway Branch, Phelps, Ky. | 2023-12-12
2023 | 2023-10-02 | Pikeville |  |  | 38821111D00006 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. 1st pole past step down. | 2717 Lfk Blackberry, McVeigh, Ky.
2023 | 2023-10-02 | Pikeville |  |  | 38821111D00087 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 274 Calloway Branch, Blackberry, Ky.
2023 | 2023-10-03 | Pikeville |  |  | 38821112B10212 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 1991 Lfk Blackberry, McVeigh, Ky.
2023 | 2023-10-04 | Pikeville |  |  | 38821088A00033 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 310 Little Blue Springs Road, McVeigh, Ky.
2023 | 2023-10-04 | Pikeville |  |  | 38821088A00156 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer@ just before Big Blue Springs Branch. | 5013 Hwy 1056, McVeigh, Ky.
2023 | 2023-10-04 | Pikeville |  |  | 38821088B00047 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 891 Little Blue Springs Branch, Blackberry, Ky.
2023 | 2023-10-04 | Pikeville |  |  | 38821088B00050 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 1109 Little Blue Springs Branch, Blackberry, Ky.
2023 | 2023-10-04 | Pikeville |  |  | 38821088B00076 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 1223 Little Blue Springs Branch, Blackberry, Ky.
2023 | 2023-10-05 | Pikeville |  |  | 38821087D30495 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 3583 Ky 1056, McCarr, Ky.
2023 | 2023-10-05 | Pikeville |  |  | 38821088A00151 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 4644 Ky 1056, McCarr, Ky.
2023 | 2023-10-06 | Pikeville |  |  | 38821087B00094 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer. No truck | 435 Smith Fork, Blackberry, Ky.
2023 | 2023-10-06 | Pikeville |  |  | 38821087D00046 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer | 48 Smith Fork, Blackberry, Ky.
2023 | 2023-10-09 | Pikeville |  |  | 38811111C00063 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 245 Middle Fork, Ransom, Ky.
2023 | 2023-10-09 | Pikeville |  |  | 38821111B00055 | TRUE | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 1900 Upper Blackberry Rd, Ransom, KY 41558, USA
2023 | 2023-10-09 | Pikeville |  |  | 38821111B00094 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Upper Blackberry Rd, Kentucky 41558, USA
2023 | 2023-10-09 | Pikeville |  |  | 38821111C00071 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 354 Middle Fork, Ransom, Ky.
2023 | 2023-10-09 | Pikeville |  |  | 38821111C00144 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 161 Middle Fork, Ransom, Ky.
2023 | 2023-10-09 | Pikeville |  |  | 38821111D00052 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Pickle Bean Hollow & Upper Blackberry Rd, Kentucky 41558, USA
2023 | 2023-10-09 | Pikeville |  |  | 38821111D00181 |  | 3408304-COLEMAN / CALLOWAY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Pickle Bean Hollow & Upper Blackberry Rd, Kentucky 41558, USA
2023 | 2023-10-11 | Pikeville |  |  | 37820032A00042 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole installed in 1946…No truck | 949 Ash Lick Fork, Phelps, KY 41553, USA
2023 | 2023-10-11 | Pikeville |  |  | 37820032A00051 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorating pole installed in 1946 | 331 Cow Branch, Phelps, Ky.
2023 | 2023-10-11 | Pikeville |  |  | 37820032C00046 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Smith Fork, Phelps, Ky. | 2023-10-11
2023 | 2023-10-12 | Pikeville |  |  | 37820008B00161 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Needs guy protector | KY-632, Phelps, KY, USA | 2023-10-12
2023 | 2023-10-12 | Pikeville |  |  | 37820008B00161 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Needs guy protector | KY-632, Phelps, KY, USA | 2023-10-12
2023 | 2023-10-16 | Pikeville |  |  | 37820008C00116 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Needs guy protector | Ky 632, Phelps, Ky. | 2023-10-16
2023 | 2023-10-16 | Pikeville |  |  | 37820008D00119 |  | 3408303-COLEMAN / PETERCRK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Needs guy protector | Ky 632, Phelps, Ky. | 2023-10-16
2023 | 2023-10-16 | Pikeville |  |  | 38821137A00417 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown | 296 Gregory Street, Phelps, Ky
2023 | 2023-10-17 | Pikeville | 86143712 | DKY0122345 | 37820125000164 |  | 3409402-FEDSCREEK / LICKCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 370 Riles Br, Lick Creek, KY 41540-8105
2023 | 2023-10-17 | Pikeville |  |  | 38821137A00326 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer.@ Phelps football field | 38175 Ky 194 E, Phelps, Ky.
2023 | 2023-10-17 | Pikeville |  |  | 38821137A00485 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer @ Phelps football field | 38175 Ky 194E, Phelps, Ky.
2023 | 2023-10-17 | Pikeville |  |  | 38821137C00546 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 781 Bone Branch, Phelps, Ky.
2023 | 2023-10-18 | Pikeville |  |  | 37820009C00123 |  | 3408303-COLEMAN / PETERCRK | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole covered with vines | 524 Phillips Branch, Phelps, Ky. | 2024-01-17
2023 | 2023-10-18 | Pikeville |  |  | 37820009C00221 |  | 3408303-COLEMAN / PETERCRK | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole is covered with vines | 458 Phillips Branch, Phelps, Ky. | 2024-01-17
2023 | 2023-10-18 | Pikeville |  |  | 38821138C00129 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 2841 Widows Branch, Phelps, Ky.
2023 | 2023-10-19 | Pikeville |  |  | 37820057A00054 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer@ end of Peter Creek circuit on 194. Last pole. | 31550 KY-194 j, Jamboree, KY 41553, USA
2023 | 2023-10-19 | Pikeville |  |  | 37820058B00106 |  | 3408303-COLEMAN / PETERCRK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 2269 Rockhouse Road, Phelps, Ky.
2023 | 2023-10-19 | Pikeville | 86360700 | DKY0122672 | 37830048A40387 | TRUE | 3410501-S.PIKEVIL / PIKEVILLE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorating pole. Pole sounds hollow. | Jefferson St, Pikeville, KY 41501, USA
2023 | 2023-10-23 | Pikeville |  |  | 38831052A00047 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | S Rice Road, Banner, Ky. | 2023-10-23
2023 | 2023-10-23 | Pikeville |  |  | 38831052B00256 | TRUE | 3120101-STANVILLE/MUD CREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop hanging down pole | 223 Gunnell Branch, Banner, Ky.
2023 | 2023-10-23 | Pikeville |  |  | 38831052B00437 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 223 Gunnell Branch, Banner, Ky.
2023 | 2023-10-23 | Pikeville |  |  | 38831052D00328 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 300 Green Hall Branch, Banner, Ky.
2023 | 2023-10-23 | Pikeville |  |  | 38831075C30025 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | 1023 Haus Branch, Banner, Ky. | 2023-10-23
2023 | 2023-10-23 | Pikeville | Trouble ticket 4932301 |  | 38831076000141 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop laying on ground energized. Customer service pole rotted and fell over. Contacted DDC to create trouble ticket for servicer to disconnect. Talked to customer to make him aware of it and told him we would need to disconnect him until repairs are made. | 534 Orchard Branch, Banner, Ky. | 2023-10-23
2023 | 2023-10-24 | Pikeville |  |  | 38831076000063 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. Will need pads and backyard machine. | 2911 Prater Creek Road, Banner, Ky.
2023 | 2023-10-24 | Pikeville |  |  | 38831076000180 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 2911 Prater Creek Road, Banner, Ky.
2023 | 2023-10-24 | Pikeville |  |  | 38831100000084 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Akers Branch, Banner, Ky. | 2023-10-24
2023 | 2023-10-24 | Pikeville |  |  | 38831123000235 | TRUE | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 360 Nicholas Drive, Spurlock Fk, Banner, Ky.
2023 | 2023-10-24 | Pikeville |  |  | 38831123000235 | TRUE | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 360 Nicholas Drive, Spurlock Fk, Banner, Ky.
2023 | 2023-10-26 | Pikeville |  |  | 38831124C00037 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop is only 6.5 ft off the ground. Probably need to install secondary pole for clearance. | 213 Jordan Fork/ Justice Branch, Banner, Ky.
2023 | 2023-10-26 | Pikeville |  |  | 38831124C00095 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 5653 Ky 1426, Harold, Ky.
2023 | 2023-10-26 | Pikeville |  |  | 38831125B20976 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Neutral conductor down/missing. 2 spans.@ mouth Frog Branch | Frog Branch, Little Mud Crk, Harold, Ky.
2023 | 2023-10-26 | Pikeville |  |  | 38831148A30325 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive secondary pole and services | 1200 Big Branch, Honaker, Ky.
2023 | 2023-10-27 | Pikeville | 86179527 |  | 37820243D00352 | TRUE | 3421001-BREAKS/CITY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | YES | Replace pole for clearance per Steven Chinn, TRC Group. Secondary conductor low clearance over driveway. | 3228 Ky 197 Elkhorn Creek, Elkhorn City, Ky.
2023 | 2023-10-27 | Pikeville |  |  | 37830020000152 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 1322 Morgan Fork Little Mud Creek, Harold, Ky.
2023 | 2023-10-27 | Pikeville | 86186026 |  | 37830336000077 | TRUE | 3409502-BURDINE / LEVISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Per Steven Chinn, TRC group, says pole is very bad shape and needs to be replaced. Pole installed 1989, AT&T pole. I checked pole, solid @ ground level, outer shell does have some deterioration due to weather cracks and climbing. I recommend to hold for few years before changing. | 14195 Ky 197 Elkhorn Creek, Ashcamp, Ky.
2023 | 2023-10-27 | Pikeville | 86198009 | DKY0122426 | 38831126A00081 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 199 Zeigler Rd, Pikeville, KY 41501, USA | 2023-12-12
2023 | 2023-10-27 | Pikeville | 86197909 | DKY0122420 | 38831126A00170 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 44 Zeigler Rd, Pikeville, KY 41501, USA | 2023-12-12
2023 | 2023-10-27 | Pikeville |  |  | 38831148000011 |  | 3120101-STANVILLE/MUD CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Little Mud Creek, Harold, Ky. | 2023-10-27
2023 | 2023-10-27 | Pikeville |  |  | 38831148000017 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 2235 Ky 2030, Little Mud Creek, Harold, Ky.
2023 | 2023-10-27 | Pikeville |  |  | 38831148C30336 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 6340 Ky 2030 Little Mud Creek, Harold, Ky.
2023 | 2023-10-30 | Pikeville |  |  | 38831101D20481 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Top of pole is rotten. Primary dead-end should be lowered or replace pole entirely. Installed 1978 | Lakeview Lane, Salem Church Road, Harold, Ky.
2023 | 2023-10-30 | Pikeville |  |  | 38831125A00590 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer bank | Salem Church Road, Harold, Ky.
2023 | 2023-10-30 | Pikeville |  |  | 38831125C30009 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Salem Church Road, Harold, Ky.
2023 | 2023-10-31 | Pikeville |  |  | 38831123B00236 |  | 3408101-SALISBURY / PRINTER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 53 Woody Ln, Printer, KY 41655, USA
2023 | 2023-10-31 | Pikeville |  |  | 38831125C30012 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 142 Hale Road, Harold, Ky.
2023 | 2023-10-31 | Pikeville |  |  | 38831125C30022 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Rfk Track Road, Harold, Ky.
2023 | 2023-11-01 | Pikeville |  |  | 38831125D00577 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer.@ around curve past Toler Creek. | 1630 Ky 979, Harold, Ky.
2023 | 2023-11-01 | Pikeville |  |  | 38831149000116 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Pole top pin is bent over. | 2639 Ky 979, Harold, Ky.
2023 | 2023-11-01 | Pikeville |  |  | 38831149000280 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken | 463 Webster Akers Cemetery Road, Harold, Ky.
2023 | 2023-11-02 | Pikeville |  |  | 38831149000106 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken, hanging down pole | King Drive/Toler Creek, Harold, Ky.
2023 | 2023-11-02 | Pikeville |  |  | 38831149000109 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | King Drive, Toler Creek, Harold, Ky.
2023 | 2023-11-02 | Pikeville |  |  | 38831149000210 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck.@ Meade Branch | 683 Toler Creek, Harold, Ky.
2023 | 2023-11-02 | Pikeville |  |  | 38831149000277 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | King Drive, Toler Creek, Harold, Ky.
2023 | 2023-11-03 | Pikeville |  |  | 37830022000071 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 393 Lfk Toler Creek, Harold, Ky.
2023 | 2023-11-03 | Pikeville |  |  | 37830022000112 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. No truck | 2706 Lfk Toler, Harold, Ky.
2023 | 2023-11-03 | Pikeville |  |  | 37830022000143 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 171 S Floyd Hlw/ Lfk Toler Creek, Harold, Ky.
2023 | 2023-11-03 | Pikeville |  |  | 37830046000016 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 2706 Lfk Toler Creek, Harold, Ky.
2023 | 2023-11-03 | Pikeville |  |  | 37830046000018 |  | 3120101-STANVILLE/MUD CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 2706 Lfk Toler Creek, Harold, Ky.
2023 | 2023-11-07 | Pikeville |  |  | 38831077C00174 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | YES | Replace deteriorating / rotten pole installed 1957 | 242 Jim Maynard Branch, Stanville, Ky.
2023 | 2023-11-07 | Pikeville |  |  | 38831077C00175 |  | 3120102-STANVILLE/TRAM | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. No truck | Jim Maynard Branch, Stanville, Ky.
2023 | 2023-11-07 | Pikeville |  |  | 38831077C00365 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorating/rotting pole installed 1972 | 588 Jim Maynard Branch, Stanville, Ky.
2023 | 2023-11-07 | Pikeville |  |  | 38831077D00158 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace rotten pole.@ mouth Linden Branch | 123 Mare Creek, Stanville, Ky.
2023 | 2023-11-07 | Pikeville |  |  | 38831077D00498 |  | 3120102-STANVILLE/TRAM | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 359 Marecreek, Stanville, Ky.
2023 | 2023-11-07 | Pikeville |  |  | 38831078000047 |  | 3120102-STANVILLE/TRAM | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. No truck | 1977 Marecreek, Stanville, Ky.
2023 | 2023-11-07 | Pikeville |  |  | 38831078000058 |  | 3120102-STANVILLE/TRAM | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 2431 Marecreek, Stanville, Ky.
2023 | 2023-11-07 | Pikeville |  |  | 38831078000073 |  | 3120102-STANVILLE/TRAM | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 3243 Marecreek, Stanville, Ky.
2023 | 2023-11-07 | Pikeville |  |  | 38831078000149 |  | 3120102-STANVILLE/TRAM | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 1820 Marecreek, Stanville, Ky.
2023 | 2023-11-08 | Pikeville |  |  | 38831077D00086 |  | 3120102-STANVILLE/TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | E Main Street, Stanville, Ky. | 2023-11-08
2023 | 2023-11-08 | Pikeville |  |  | 38831101C10480 |  | 3120102-STANVILLE/TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Bobcat Blvd, Stanville, Ky. | 2023-11-08
2023 | 2023-11-08 | Pikeville |  |  | 38831101C10480 |  | 3120102-STANVILLE/TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Bobcat Blvd, Stanville, Ky. | 2023-11-08
2023 | 2023-11-08 | Pikeville |  |  | 38831101C10495 |  | 3120102-STANVILLE/TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Néeds guy protector | Allen Lane, Stanville, Ky | 2023-11-08
2023 | 2023-11-09 | Pikeville |  |  | 38831052C00135 |  | 3120102-STANVILLE/TRAM | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | Davison Branch, Ivel, Ky.
2023 | 2023-11-09 | Pikeville |  |  | 38831052D00002 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | crossarm/braces: deteriorated, not rotten |  | KPC | YES | Replace rotten pole/ deteoriated arms installed 1967 | 109 Stratton Street, Ivel, Ky.
2023 | 2023-11-09 | Pikeville |  |  | 38831052D00267 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace rotten pole installed 1975. Sounds hollow @ ground level | 211 Mockinbird Lane, Ivel, Ky.
2023 | 2023-11-09 | Pikeville |  |  | 38831052D00351 |  | 3120102-STANVILLE/TRAM | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 694 Lfk Lower Stratton Branch, Ivel, Ky.
2023 | 2023-11-09 | Pikeville |  |  | 38831052D00408 |  | 3120102-STANVILLE/TRAM | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Stratton Street, Ivel, Ky. | 2023-11-09
2023 | 2023-11-09 | Pikeville |  |  | 38831053A00052 |  | 3120102-STANVILLE/TRAM | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | Dillon Branch, Ivel, Ky.
2023 | 2023-11-09 | Pikeville |  |  | 38831053A00156 |  | 3120102-STANVILLE/TRAM | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | Spicewood Ln, Ivel, Kentucky 41642, USA
2023 | 2023-11-10 | Pikeville |  |  | 38831053B00020 |  | 3120102-STANVILLE/TRAM | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 625 Tom’s Creek, Ivel, Ky.
2023 | 2023-11-10 | Pikeville |  |  | 38831074D00009 |  | 3408103-SALISBURY / MARTIN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Has flood light to transfer | Cummings St, Martin, KY 41649, USA
2023 | 2023-11-10 | Pikeville |  |  | 38831077A00072 |  | 3120102-STANVILLE/TRAM | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 102 Tom’s Creek, Ivel, Ky.
2023 | 2023-11-10 | Pikeville |  |  | 38831077A00221 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace rotten/deteoriated pole installed 1958 | 106 Carlisle Hollow Rd, Ivel, KY 41642, USA
2023 | 2023-11-15 | Pikeville | 86392359 | DKY0122717 | 38831126C00145 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Extremely rotten at bottom | 1115 Broad Bottom Rd, Pikeville, KY
2023 | 2023-11-15 | Pikeville |  |  | 38831126C10947 | TRUE | 3120103-STANVILLE/HAROLD | Line Work | UG | UG conduit: damaged or separated |  |  | KPC | NO | Pad for padmount transformer damaged. Transformer tilted backwards. | 25 Crossrock Court, Venters Lane, Pikeville, Ky.
2023 | 2023-11-16 | Pikeville | 86429073 | DKY0122787 | 38831101C20080 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , guys/anchors: broken or missing |  |  | KPC | YES |  |  | 2024-01-12
2023 | 2023-11-21 | Pikeville | 86359740 | DKY0122667 | 37830016C00174 |  | 3413401-GARRETT / GARRETT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 112 Raburn Rd, Hueysville, KY 41640, USA
2023 | 2023-11-21 | Pikeville |  |  | 38831101C20062 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | S Bailey Rd, Betsy Layne, KY 41605, USA
2023 | 2023-11-21 | Pikeville |  |  | 38831101C40563 | TRUE | 3120103-STANVILLE/HAROLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Epoxilator broken on step down pole | School St, Betsy Layne, KY 41605, USA
2023 | 2023-11-21 | Pikeville |  |  | 38831101D30608 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck. | Branham Hill Rd, Betsy Layne, KY 41605, USA
2023 | 2023-11-27 | Pikeville |  |  | 38831101D40169 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 320 Coldwater Branch, Harold, Ky.
2023 | 2023-11-27 | Pikeville |  |  | 38831102000037 | TRUE | 3120103-STANVILLE/HAROLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace pole. Split at the top, down to x braces. | 794 Coldwater Branch Rd, Harold, KY 41635, USA
2023 | 2023-11-28 | Pikeville |  |  | 38831125C40280 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 201 Old County Road, Harold, Ky.
2023 | 2023-11-28 | Pikeville |  |  | 38831125C40615 | TRUE | 3120103-STANVILLE/HAROLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown on step down. | 120 Old County Road, Harold, Ky.
2023 | 2023-11-28 | Pikeville |  |  | 38831126B10034 |  | 3120103-STANVILLE/HAROLD | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken. Hanging down pole. | 86 Main Street, Harold, Ky.
2023 | 2023-11-29 | Pikeville | 86396351 | DKY0122723 | 37820001000131 |  | 3403001-PIKEVILLE / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2023 | 2023-11-29 | Pikeville | 86393830 | DKY0122720 | 38831077B00440 |  | 3120102-STANVILLE/TRAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 137 N Steffy St, Tram, KY 41663, USA | 2023-12-04
2023 | 2023-11-29 | Pikeville |  |  | 38831126A00159 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | Porter Lane, Boldman, Ky.
2023 | 2023-11-29 | Pikeville |  |  | 38831126B00566 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 5509 Hurricane Creek, Boldman, Ky.
2023 | 2023-11-29 | Pikeville |  |  | 38831126B10186 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Elkins Drive, Boldman, Ky. | 2023-11-29
2023 | 2023-11-29 | Pikeville |  |  | 38831126B10886 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | Red Bird Lane, Boldman, Ky.
2023 | 2023-11-29 | Pikeville |  |  | 38831150000076 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  |  |  | KPC | NO | Remove inactive transformer | 519 Spring Branch, Boldman, Ky.
2023 | 2023-11-30 | Pikeville |  |  | 38831150000016 |  | 3120103-STANVILLE/HAROLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Bear Fork, Hurricane Crk, Pikeville, Ky. | 2023-11-30
2023 | 2023-11-30 | Pikeville |  |  | 38831150000175 |  | 3120103-STANVILLE/HAROLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | Davis Road, Hurricane Creek, Pikeville, Ky.
2023 | 2023-12-04 | Pikeville |  |  | 37830023000033 |  | 3411702-CEDAR CREEK/IVY COURT | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 940 Elisha Fork, Pikeville, KY 41501, USA
2023 | 2023-12-04 | Pikeville |  |  | 37830023000140 |  | 3411702-CEDAR CREEK/IVY COURT | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor blown. Epoxilator deteoriated | 167 Elisha Fork, Pikeville, KY 41501, USA
2023 | 2023-12-04 | Pikeville |  |  | 37830023000273 |  | 3411702-CEDAR CREEK/IVY COURT | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. No truck | 836 Elisha Fork p, Pikeville, KY 41501, USA
2023 | 2023-12-05 | Pikeville |  |  | 37830022000182 |  | 3411702-CEDAR CREEK/IVY COURT | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 978 Dog Fork, Pikeville, Ky.
2023 | 2023-12-11 | Pikeville | 86463528 | DKY0122868 | 37830237B00094 |  | 3401002-ELWOOD / VIRGIE-IN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 5360 Longfork Rd, Virgie, KY 41572, USA
2023 | 2023-12-12 | Pikeville | 86470072 | DKY0122875 | 38820967D20133 |  | 2150103-SPRIGG / SPRIGG | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 3403 State Hwy 292 E, Belfry, KY 41514, USA
2023 | 2023-12-15 | Pikeville | 86490131 | DKY0122926 | 38821011D00145 |  | 3414301-SIDNEY/BIG CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2023 | 2023-12-20 | Pikeville |  |  | 37820197000029 |  | 3421002-BREAKS/GRASSY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is in a slide location. Needs to be relocated. | 1218 Rfk Little Beaver, Elkhorn City, Ky.
2023 | 2023-12-27 | Pikeville |  |  | 37820220C20147 |  | 3421001-BREAKS/CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten @ ground level | 351 E Russell St, Elkhorn City, KY 41522, USA
2023 | 2023-12-27 | Pikeville |  |  | 37820220D00429 |  | 3421001-BREAKS/CITY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer | 336 Ohio St, Elkhorn City, KY 41522, USA
2023 | 2023-12-28 | Pikeville |  |  | 37820197000003 |  | 3421001-BREAKS/CITY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy protector | Little Beaver Creek, Elkhorn City, Ky. | 2023-12-28
2023 | 2023-12-28 | Pikeville |  |  | 37820197000144 |  | 3421001-BREAKS/CITY | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer | 609 Rfk Little Beaver, Elkhorn City, Ky.
2023 | 2023-12-29 | Pikeville |  |  | 37820220A00129 |  | 3421001-BREAKS/CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is hollow about 2 ft from ground level. | 246 Elkhorn St, Elkhorn City, KY 41522, USA
2023 | 2023-12-29 | Pikeville |  |  | 37820220C20310 |  | 3421001-BREAKS/CITY | Line Work | OH |  |  |  | KPC | NO | Neutral conductor down/stolen. #4 copper | 156 Rush Street, Elkhorn City, Ky.

## Ckt Defects Reported 2019 HAZ
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2019 | 2019-01-04 | Hazard |  |  | 37830345C00043 |  | 3309002-JEFF / JEFF | Line Work | OH | guys/anchors: broken or missing | pole: leaning, burned more than 50% remaining |  | KPC |  | Primary and secondary guy wire broken. No anchors visible. Install: 1999 | Kenmont Rd, Kentucky 41751, USA
2019 | 2019-01-04 | Hazard |  |  | 37830442000055 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Might be able to reach with material handler? If they can get truck down rd. Across rd from depot br. | Ky. Highway 699, Slemp ky.
2019 | 2019-01-07 | Hazard |  |  | 37830442000138 |  | 3309902-SLEMP / LEATHERWOOD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | At switch pole at end of leatherwood circuit. Towards Daisy. Old road goes to it but is wet. | Hwy. 699, Slemp Ky.
2019 | 2019-01-07 | Hazard | 81557481 |  | 37830466000123 |  | 3309902-SLEMP / LEATHERWOOD | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Xfmr open, service hanging down pole, trailer gone. Needs removed | Bob hollow road, off hwy. 699 Slemp, Ky. | 2022-03-10
2019 | 2019-01-07 | Hazard |  |  | 37830491000081 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Rem. Xfmr and secondary and secondary pole 491-49. | Lost fork road, little leather wood
2019 | 2019-01-07 | Hazard |  |  | 37830491000197 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr, manual | Lost fork Rd. little leather Ky.
2019 | 2019-01-08 | Hazard |  |  | 378303490000069 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | Open secondary that serves Halcomb’s grocery, insulation falling off conductors! Needs changed out | Hwy. 699, Owens Branch, Ky.
2019 | 2019-01-08 | Hazard |  |  | 37830465000009 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Low conductors, neutral cover up with vines. Tech. Needs to look at. | Owens Branch, Slemp, Ky.
2019 | 2019-01-08 | Hazard |  |  | 37830489000003 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Manual but not extreme! | Richie Hollow, Owens Branch, Slemp, Ky.
2019 | 2019-01-08 | Hazard | 75737855 | DKY0108404 | 37830490000127 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Secondary pole, has been braced. This is also span guy pole. | Owens’s Branch Rd. Slemp, Ky. | 2020-06-24
2019 | 2019-01-08 | Hazard |  |  | 37830539000038 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | End of line up 463, old burnt church on left. Secondary and secondary pole 539-63 needs removed too. | Ky. Highway 463, Slemp, Ky.
2019 | 2019-01-09 | Hazard |  |  | 37830513B00016 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Drive way gated and locked. Driveway goes near pole | Hwy. 699, Clover Fork , Slemp, Ky.
2019 | 2019-01-09 | Hazard |  |  | 37830559000018 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | There are two 1 pole taps off 559-18, remove both, poles 559-41 and 559-38. Inactiv | Head of Cutshin Creek, Yeaddis, Ky.
2019 | 2019-01-11 | Hazard |  |  | 37830463000089 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Shows two pole tap, off line not in use | Gas rd. Yeaddiss Rd, Yeaddiss, Ky.
2019 | 2019-01-11 | Hazard | 72326220 | 04/17/19 | 37830464000006 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Osmose marked pole for bad. // WR#72326220 / DKY0103595 is on the asset pole sheet to replace this pole - PRB 2/1/19 | Yeaddiss Rd. Yeaddiss, Ky. | 2020-02-03
2019 | 2019-01-11 | Hazard | 72326234 | DKY0103602 | 37830464000007 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Osmose has marked pole for bad. ///WR #72326234 / DKY0103602 is on asset pole sheet to replace this pole / PRB 2/1/2019 | Yeaddiss Rd. Yeaddiss, Ky. | 2019-04-17
2019 | 2019-01-11 | Hazard | 72326247 | DKY0103605 | 37830464000009 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Osmose has marked pole for change out. Rotten //WR #72326247 / DKY0103605 on asset pole sheet to replace this pole / PRB 2/1/19 | Yeaddiss Road, Yeaddiss, Ky. | 2019-04-25
2019 | 2019-01-11 | Hazard |  |  | 37830464000020 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole filled around, needs checked by tech. | Coots Hollow, Yeaddiss, Ky. | 2019-03-15
2019 | 2019-01-11 | Hazard | 72324310 | DKY0103591 | 37830464000023 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Osmose has marked pole to get changed out | Coots Hollow, Yeaddiss, Ky. | 2019-04-29
2019 | 2019-01-11 | Hazard | 72316653 | DKY0103578 | 37830464000025 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Osmose has pole marked for bad, needs changed out | Coots Hollow rd. Yeaddiss, Ky. | 2019-04-25
2019 | 2019-01-11 | Hazard | 72338586 | DKY0103613 | 37830464000068 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Below road about 90ft. Pole rotten at the top. | Coots Hollow, Yeaddiss, Ky. | 2019-05-06
2019 | 2019-01-11 | Hazard |  |  | 37830487000046 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | 2nd tap to right up Yeaddiss Rd. from 699 before step down. | Yeaddiss Rd. Yeaddiss, Ky.
2019 | 2019-01-11 | Hazard | 75739571 | DKY0109371 | 37830488000003 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Trace br. Behind house, shelled bad, needs changed | 75 Trace Br. Yeaddiss, Ky | 2021-01-07
2019 | 2019-01-14 | Hazard |  |  | 37830391000054 |  | 3309003-JEFF / VIPER | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Ina. Xfmr. On right near head of wells fk. Big bucket might reach. | Wells fork rd. Viper ky
2019 | 2019-01-14 | Hazard |  |  | 37830391000056 |  | 3309003-JEFF / VIPER | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Located at last line fuse in wells fork. 8 pole tap, span missing crossing rd. Line fuse open. INA. | Wells Fork Rd. Viper Ky.
2019 | 2019-01-15 | Hazard |  |  | 37830369B00166 |  | 3309003-JEFF / VIPER | Line Work | OH | guys/anchors: broken or missing |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Guy rod visible, guy wire broken. | Holly Hill Drive, Right Fork Maces Creek, Viper Ky.
2019 | 2019-01-15 | Hazard |  |  | 37830392000120 |  | 3309003-JEFF / VIPER | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign |  | Secondary guy, road crossing | Pine Patch Rd. Right Fork Maces Creek,, Viper, Ky.
2019 | 2019-01-15 | Hazard |  |  | 37830416000036 |  | 3309003-JEFF / VIPER | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Primary tap guy wire loose could be broken, dirt piled on top. | 471 Fields Fork Rd. Viper Ky.
2019 | 2019-01-15 | Hazard | 75728566 |  | 37830416000105 |  | 3309003-JEFF / VIPER | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | INA service, meter blanked | Fields Fork, Stratton Fork, Viper, Ky | 2020-02-03
2019 | 2019-01-16 | Hazard |  |  | 37830393B00297 |  | 3309003-JEFF / VIPER | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | If you can get the gate open it’ll be bucket work. Blue diamond mine 75 | Middle Fork, Viper, Ky.
2019 | 2019-01-16 | Hazard |  |  | 378304170000102 |  | 3309003-JEFF / VIPER | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Big material handler will work. | Lick Branch, Middle Fork, Viper, Ky.
2019 | 2019-01-16 | Hazard |  |  | 37830417000125 |  | 3309003-JEFF / VIPER | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen. | Robert Brashear Rd. Middle Fork, Viper, Amy.
2019 | 2019-01-16 | Hazard |  |  | 37830417000180 | TRUE | 3309003-JEFF / VIPER | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Narrow road in head if lick br. | Lick Branch, Middle Fork, Viper Ky.
2019 | 2019-01-16 | Hazard |  |  | 37830417000272 |  | 3309003-JEFF / VIPER | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | INA. One pole tap with xfmr. | Robert Brashear Road, Middle Fork, Viper, Ky.
2019 | 2019-01-16 | Hazard |  |  | 37830418000035 |  | 3309003-JEFF / VIPER | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Primary guy broken and laying over lash. | America Ln.,Campbell’s Branch Viper, Ky.
2019 | 2019-01-17 | Hazard |  |  | 37830417000181 |  | 3309003-JEFF / VIPER | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Primary guy broken | PrimroseLn. Right Fork Maces Creek, Viper, Ky.
2019 | 2019-01-17 | Hazard |  |  | 37830441000042 |  | 3309003-JEFF / VIPER | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | A dry time a material handler will work. In the very head, last pole. | Left Fork, Maces Creek, Viper, Ky.
2019 | 2019-01-17 | Hazard | 75714525 |  | 37830441000064 |  | 3309003-JEFF / VIPER | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service rolled up on pole. Bucket access | Left Fork Maces Creek, Viper, Ky. | 2020-01-31
2019 | 2019-01-18 | Hazard | 80499732 | DKY0114699 | 37830277000119 |  | 3309301-VICCO / REDFOX | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire broken on secondary pole. | 5385 Big Branch Road, Aburgey, Ky. | 2021-10-21
2019 | 2019-01-18 | Hazard | 75717324 | DKY0108362 | 37830325C00274 | TRUE | 3309301-VICCO / REDFOX | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | At hwy. 160 exit on hwy. 15 on right above Hwy. 15 | Hwy. 15,Red Fox, Ky. | 2023-08-31
2019 | 2019-01-18 | Hazard | 79757096 | DKY0114059 | 37830326D00088 |  | 3309301-VICCO / REDFOX | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | INA. Xfmr and secondary pole. 326-334 remove | Wolf pen Creek Road, Red Fox, Ky. | 2022-02-02
2019 | 2019-01-18 | Hazard | 79757096 | DKY0114059 | 37830326D00089 |  | 3309301-VICCO / REDFOX | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Manual pole, service laying on telephone cable. | WolfpenCreek Rd. Red Fox, Ky. | 2022-02-02
2019 | 2019-01-18 | Hazard |  |  | 37830326D40373 |  | VICCO - RED FOX / 3093-01 | Forestry | OH |  |  | FORESTRY ISSUE (see comments) | KPC |  | Small pine tree laying on secondary at secondary pole. | 360 Poplar Hollow, Red Fox, Ky. | 2018-11-10
2019 | 2019-01-18 | Hazard | 79757096 | DKY0114059 | 37830349000125 |  | 3309301-VICCO / REDFOX | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | INA. One pole tap and xfmr. Pole 349-146 | Defeated Creek, Red Fox, Ky. May need forestry to cut path? | 2022-02-02
2019 | 2019-01-21 | Hazard |  |  | 37830296C20511 |  | 3302704-HAZARD / KENMONT | Line Work | OH | guys/anchors: broken or missing | pole: leaning, burned more than 50% remaining |  | Foreign |  | Guys missing and pole leaning. Install: 1938 | East Main Street, Hazard, Ky | 2020-06-02
2019 | 2019-01-21 | Hazard |  |  | 37830296C20971 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign |  | Secondary pole, Shelly and looks Broke. | Locust Street, Hazard, Ky. | 2019-11-11
2019 | 2019-01-21 | Hazard | 75702091 | G0000110 | 37830320C00040 |  | 3302704-HAZARD / KENMONT | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | House nob broken. Behind apartment building , were you turn into Cornett hill drive. | Cornett Hill Dr. Hazard, Ky.
2019 | 2019-01-21 | Hazard | 79757096 | DKY0114059 | 37830325B00066 |  | 3309301-VICCO / REDFOX | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | On right before Argon Hollow | Big Smith Branch Rd, Kentucky, USA | 2022-02-02
2019 | 2019-01-22 | Hazard | 75700075 |  | 37830321A40562 |  | 3309001-JEFF / BOONE LEDGE | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign |  | Pole ground stolen | Hwy. 15, Booneledge, Jeff, Ky. | 2020-01-30
2019 | 2019-01-22 | Hazard | 75699950 |  | 37830321A40563 |  | 3309001-JEFF / BOONE LEDGE | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen | Hwy 15, Booneledge, Jeff, Ky. | 2020-01-30
2019 | 2019-01-22 | Hazard |  |  | 37830321B00139 | TRUE | 3309001-JEFF / BOONE LEDGE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Two pole tap with xfmr.. cross rr tracts. R/W bad | Glomawr, Stormking, Rd. Hazard, Ky.
2019 | 2019-01-22 | Hazard |  |  | 37830321B00376 | TRUE | 3309001-JEFF / BOONE LEDGE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightening arrestors broken, but off line, needs removed or replaced. | Glomawr,, Stormking, Rd. Hazard, Ky.
2019 | 2019-01-23 | Hazard | 72506900 | DKY0103881 | 37830127000027 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | already written to EDN100577 FOREIGN | Pole leaning bad,needs changed. | Lost Creek, KY, USA | 2022-10-20
2019 | 2019-01-23 | Hazard |  |  | 37830127000045 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Rem. Inactive two pole tap,, two poles to be removed are KPC owned. 127-147, 127-148. | Lost Creek Rd. LostCreek, Ky.
2019 | 2019-01-23 | Hazard |  |  | 37830151000025 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH |  | pole: leaning, burned more than 50% remaining | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Inactive xfmr and two secondary poles, 151-210, 151-277, primary pole leaning. Install: 1973 | 16 Mile Creek Rd. Lost Creek, Ky.
2019 | 2019-01-23 | Hazard |  |  | 37830151000103 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Across creek, on 15 mile, remove Ina xfmr and secondary poles | KY-15, Lost Creek, KY, USA
2019 | 2019-01-23 | Hazard |  |  | 37830151000193 | TRUE | 3311701-SHAMROCK / SHAMROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Inactive xfmr | Rowdy Low Gap Rd. Lost Creek, Ky.
2019 | 2019-01-23 | Hazard |  |  | 37830151000213 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Inactive one pole tap with xfmr, needs removed. | 16 Mile Creek, Lost Creek, Ky.
2019 | 2019-01-23 | Hazard |  |  | 37830151000261 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Ina xfmr and secondary pole | 15 Mile Creek, Lost Creek, Ky.
2019 | 2019-01-23 | Hazard |  |  | 37830151A30331 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr, | Lost Creek Rd. Lost Creek, Ky.
2019 | 2019-01-23 | Hazard |  |  | 37830151D30300 |  | 3311701-SHAMROCK / SHAMROCK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Ground wire stolen. | Millie Ann Dr. Lost Creek, Ky.
2019 | 2019-01-23 | Hazard | 75288532 | DKY0107611 | 37830183C00069 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr and secondary pole 183-313 remove | Spruce Pine Rd. Garner, Ky. | 2020-05-28
2019 | 2019-01-25 | Hazard |  |  | 37830181C20172 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Secondary laying on telephone. | Owens Branch Rd, Hindman, KY 41822, USA | 2019-12-10
2019 | 2019-01-25 | Hazard | 75316705 | DKY0107683 | 37830181D00113 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy wire broken | Short Branch Rd, Hindman, KY 41822, USA | 2020-02-12
2019 | 2019-01-25 | Hazard |  |  | 37830182000127 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | 4/2 duplex. In between and laying on communication cables | Upper Mill Crk | 2019-11-25
2019 | 2019-01-25 | Hazard |  |  | 37830182B00108 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | FORESTRY ISSUE (see comments) | KPC |  | Pole needs attn | Upper Mill Creek Rd, Kentucky, USA | 2019-11-25
2019 | 2019-01-25 | Hazard | 75300095 | DKY0107632 | 37830182B00215 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | already written to EDN100577 KPC pole | Pole needs replaced, rotten | Upper Mill Creek, Leburn, Ky | 2020-06-03
2019 | 2019-01-25 | Hazard |  |  | 37830182D00126 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign |  | Also secondary pole needs removed [pole 182-252] | Upper Mill Creek, Leburn, Ky | 2019-11-25
2019 | 2019-01-25 | Hazard |  |  | 37830182D00130 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Conductors May be too close too structure | 1330 Upper Mill Creek, Leburn, Ky.
2019 | 2019-01-25 | Hazard | 75610147 | DKY0108169 | 37830206000139 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is bad and needs replaced | 2043 Upper Mill Creek Leburn Ky | 2020-01-30
2019 | 2019-01-28 | Hazard |  |  | 37830296D11447 |  | 3302704-HAZARD / KENMONT | Line Work | UG |  | transformers: leaking, damaged |  | KPC |  | Underground xfmr looks to be leaking | KY-15, Hazard, KY, USA
2019 | 2019-01-29 | Hazard |  |  | 37830271C00111 |  | 3301401-COMBS / COMBS | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | Clearance, primary and neutral over house | Adams Ridge Rd. Combs, Ky
2019 | 2019-01-30 | Hazard | 76778103 | DKY0110112 | 37830296D40472 |  | 3302704-HAZARD / KENMONT | Line Work | OH | crossarm/braces: broken/split , guys/anchors: broken or missing |  |  | KPC |  | Back parking lot, at Cardinal Dealership. | Hwy. 15 South, Hazard, Ky.
2019 | 2019-01-30 | Hazard |  |  | 37830296D41134 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | already written to EDN100577 FOREIGN |  | Hwy. 15 South, Hazard, Ky.
2019 | 2019-01-30 | Hazard | 76778103 | DKY0110112 | 37830297000182 |  | 3302704-HAZARD / KENMONT | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Head of Stormking Rd. Across from Pearl Campbell garage. | Christopher Hill Rd, Kentucky 41701, USA
2019 | 2019-01-30 | Hazard | 76778103 | DKY0110112 | 37830320B00133 |  | 3302704-HAZARD / KENMONT | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Just pass serenity lane, fourseam rd. | Fourseam Buffalo Rd, Kentucky, USA
2019 | 2019-01-30 | Hazard |  |  | 37830321A00535 |  | 3302704-HAZARD / KENMONT | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Low service drop, may need pole. 321-406, 321-535 | 84 Boothe Ridge Rd, Hazard, KY 41701, USA
2019 | 2019-01-31 | Hazard |  |  | 37830223D21081 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Tech. Needs to check clearance over road. | 179 Happy Valley Ln, Hazard, KY 41701, USA
2019 | 2019-01-31 | Hazard | N/A |  | 37830247C21549 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr, beside gospel light Baptist church. | Independence Dr, Hazard, KY 41701, USA | 2023-10-06
2019 | 2019-01-31 | Hazard | 74827737 |  | 37830271C00060 |  | 3301401-COMBS / COMBS | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign |  | Inactive services, two services needs remove. No truck access | Elm Shoal Branch, Combs, Ky | 2019-10-14
2019 | 2019-01-31 | Hazard | 74827494 |  | 37830271D00239 |  | 3307302-BULAN / AJAX-DWAR | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign |  | Inactive service been cut on pole, needs removed. | Lick Branch Rd, Combs, KY 41701, USA | 2019-10-14
2019 | 2019-02-01 | Hazard |  |  | 37830175000086 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Inactive xfmr | Mount Zion Rd. Sixteen Mile Crk. Lost Creek, Ky.
2019 | 2019-02-01 | Hazard | 68386618 | DKY0098056 | 37830199000120 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | already written to EDN100577 KPC pole | found in STORMS on 2/1/19 - from 2017 inspection - PRB | Napier Hollow Road, Dice KY | 2022-04-08
2019 | 2019-02-01 | Hazard | 75885445 | Ops# 036348258 | 37830199C00091 |  | 3308502-BONNYMAN / HAZARD | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , service: unused or abandoned, blanked meter base |  |  | Foreign |  | Meter base and meter fallen off wall, house falling down. | Lost Creek, KY, USA | 2020-02-21
2019 | 2019-02-01 | Hazard | 75817835 | Ops# 031189443 | 37830199C00112 |  | 3308502-BONNYMAN / HAZARD | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | House knob broke | Noble Br., lost Creek, Ky. | 2020-02-13
2019 | 2019-02-01 | Hazard |  |  | 37830223A00136 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC |  | Inactive xfmr | Harveyton Rd, Kentucky, USA
2019 | 2019-02-01 | Hazard | N/A |  | 37830223B00015 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Mouth of old mill ridge hill. Tech needs to check for clearance | Old Mill Ridge Hill Rd, Kentucky 41719, USA | 2023-10-05
2019 | 2019-02-01 | Hazard |  |  | 37830223B00502 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | 60ft from road | Herald Heights, Kentucky 41719, USA
2019 | 2019-02-01 | Hazard | 75657451 | DKY0108240 | 37830247A00410 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole looks split at top. | Crawford Valley Dr., Bonnyman, Ky | 2020-09-15
2019 | 2019-02-04 | Hazard |  |  | 37830198C00044 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive one pole tap with xfmr. Pole#. 198-203 not shone on field view. | Pvt. Darren K Dr. Grapevine, Ky. | 2019-03-15
2019 | 2019-02-04 | Hazard |  |  | 37830198C00083 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Pvt. Darren K Dr. Grapevine, Ky.
2019 | 2019-02-04 | Hazard |  |  | 37830198C00148 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Hoss Cat Ln. Grapevine, Ky.
2019 | 2019-02-04 | Hazard | 75824675 | Ops# 039865644 | 37830199A00010 |  | 3308502-BONNYMAN / HAZARD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Xfmr pole. | Little Grapevine Creek Rd, Kentucky 41701, USA | 2020-02-14
2019 | 2019-02-04 | Hazard |  |  | 37830223B00414 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive 3 pole tap, xfmr pole on end leaning bad held up by guys. | Middle Ridge Rd, Kentucky 41719, USA
2019 | 2019-02-04 | Hazard | N/A |  | 37830247A00613 |  | 3308502-BONNYMAN / HAZARD | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Top of nascar dr. Turn left to trl. | Nascar Ln, Kentucky 41719, USA | 2023-10-04
2019 | 2019-02-05 | Hazard | 75659709 | DKY0108253 | 37830199B00027 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole needs changed out, weather damage flaking bad. 35/5 pole. | Condy Ln, Kentucky 41701, USA | 2021-01-13
2019 | 2019-02-05 | Hazard | 75659869 | DKY0108257 | 37830222A00282 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole extension. Near end of line | Flat Gap Rd. Bonnyman, Amy. | 2020-03-30
2019 | 2019-02-05 | Hazard |  |  | 37830222B00305 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive 4 pole tap | Shingle-in Dr. Bonnyman, Ky. | 2019-02-05
2019 | 2019-02-05 | Hazard | 78409668 | 034344797 | 37830222D00284 |  | 3308502-BONNYMAN / HAZARD | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Inactive service, rolled up on pole. Mouth of oak point ln. on left. Flat tap rd. | Bonnyman, KY 41719, USA | 2020-12-16
2019 | 2019-02-05 | Hazard | N/A |  | 37830246C00190 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  |  | KPC | NO | Neutral down, below flat gap on right. 6A CU. | Lower Second Crk. Bonnyman, Ky. | 2023-10-02
2019 | 2019-02-05 | Hazard |  |  | 37830269D20909 |  | 3302704-HAZARD / KENMONT | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Upon hill across from Cardinal dealership. | KY-15, Hazard, KY, USA | 2020-06-02
2019 | 2019-02-06 | Hazard |  |  | 37830224A00353 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH |  | pole: leaning, burned more than 50% remaining | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Rem. Inactive xfmr and secondary pole no in use. Pole# 224-434. Install: 1985 | Winter Way, Kentucky 41719, USA
2019 | 2019-02-06 | Hazard |  |  | 37830225D00218 | TRUE | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | already written to EDN100577 FOREIGN | Pole has holes in the top and leaning. | Grigsby Branch Rd, Kentucky 41701, USA
2019 | 2019-02-06 | Hazard |  |  | 37830225D00219 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Inactive xfmr and open secondary and secondary pole needs removed. Pole#225-239 | Grigsby Branch Rd, Kentucky 41701, USA
2019 | 2019-02-06 | Hazard |  |  | 37830225D00456 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Head of grigsby br. Inactive xfmr | Grigsby Branch Rd, Kentucky 41701, USA
2019 | 2019-02-06 | Hazard |  |  | 37830249A00341 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Lines low over garden. Neutral about 9ft off ground. | Darfork, KY 41701, USA
2019 | 2019-02-06 | Hazard |  |  | 37830249C00044 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  |  | Grigsby Branch Rd, Kentucky 41701, USA
2019 | 2019-02-06 | Hazard |  |  | 37830249C00045 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Rem. Inactive xfmr and secondary and secondary pole. Pole# 249-283 | Penn Ln, Kentucky 41701, USA | 2019-02-06
2019 | 2019-02-06 | Hazard |  |  | 37830249C00296 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. | Penn Ln, Kentucky 41701, USA
2019 | 2019-02-07 | Hazard |  |  | 37830250A00015 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr, secondary and 2 secondary poles. Pole# 250-119, 250-216 | Keller Hollow Rd, Kentucky 41701, USA
2019 | 2019-02-07 | Hazard |  |  | 37830250A00059 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole rotten and pole top pin pulled thru pole. Needs changed. | Clear Fork Rd, Kentucky 41701, USA | 2019-02-07
2019 | 2019-02-07 | Hazard | 75635558 | DKY0108213 | 37830250B00038 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole split and PTP leaning towards angle. | Woodys Ln, Kentucky 41701, USA
2019 | 2019-02-07 | Hazard |  |  | 37830251000108 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive one pole tap and xfmr, lash and sec. pole. Primary neutral laying on comm. cable. Needs removed. Top of mountain on left | KY-721, Kentucky 41701, USA
2019 | 2019-02-11 | Hazard |  |  | 37640288000061 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr and Open secondary needs removed, secondary pole. 288-62 | Ky. Highway 2022,Saul, Ky.
2019 | 2019-02-11 | Hazard |  |  | 37830247C31296 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. | Combs Ln, Hazard, Ky. | 2021-02-01
2019 | 2019-02-11 | Hazard |  |  | 37830248A00752 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive one pole tap | Sonny Dr, Kentucky 41701, USA
2019 | 2019-02-12 | Hazard | N/A |  | 37840264000026 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr. | Dusty Rd. Saul, Ky. | 2023-06-07
2019 | 2019-02-12 | Hazard | 75603936 | DKY0108156 | 37840288C00043 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole in bad shape | Couch Hollow Rd., Saul, Ky. | 2020-03-17
2019 | 2019-02-12 | Hazard |  |  | 37840288C00050 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. | Ky. Highway 2022, Saul, Ky.
2019 | 2019-02-12 | Hazard |  |  | 37840288C00093 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. | Ky. Highway 2022, Saul, Ky.
2019 | 2019-02-12 | Hazard |  |  | 37840288C00152 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. | Ky. Highway 2022, Saul, Ky.
2019 | 2019-02-12 | Hazard |  |  | 37840288D00113 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Secondary tap and light pole 288-124 removed from xfmr pole 288-112. Secondary pole and light pole needs removed. | Ky. Highway 484, Saul, Ky.
2019 | 2019-02-13 | Hazard | 75739484 | DKY0108659 | 37830170000011 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | service: unused or abandoned, blanked meter base |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr. Open secondary pole to pole one wire broken. Cutout open. | Feb Fork Rd, Kentucky 41745, USA
2019 | 2019-02-13 | Hazard | 75739484 | DKY0108659 | 37830171000020 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Braces broke, can take atv and get near it. | Hwy. 28, Chavies, Ky.
2019 | 2019-02-13 | Hazard | N/A |  | 37830194000139 |  | 3301101-CHAVIES / CHAVIES | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Service house knob broke | Stable Fk. Chavies, Ky. | 2023-06-13
2019 | 2019-02-13 | Hazard | N/A |  | 37830195000110 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr. Old road needs to be dry time. | Raleigh Rd, Chavies, Ky. | 2023-06-06
2019 | 2019-02-13 | Hazard | 75653078 | DKY0108237 | 37830195000111 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole split out and rotten. Can possibly get bucket to it in dry time. Take gloryland way to line, second pole to right. | Gloryland Way Rd. Chavies, Ky. | 2020-04-08
2019 | 2019-02-13 | Hazard | 83370714 | DKY0117977 | 37830196B30263 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. | MaggardRidge, Chavies, Ky.
2019 | 2019-02-14 | Hazard |  |  | 37830121000073 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. Can get atv to xfmr pole. | Bowling’s Creek Rd. Altro, Ky.
2019 | 2019-02-14 | Hazard | 72287279 | DKY0103529 | 37830122000002 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign |  | Pole rotten, been marked by osmose | Bowling’s Creek Rd. Altro, Ky. | 2019-03-11
2019 | 2019-02-14 | Hazard |  |  | 37830122000003 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. Atv possible | Bowling’s Creek Rd. Altro, Ky
2019 | 2019-02-14 | Hazard | 75659315 | DKY0108241 | 37830122000012 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole washed out. | Bowling’s Creek, Altro, Ky. | 2020-06-16
2019 | 2019-02-14 | Hazard | N/A |  | 37830122000032 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | 3 pole tap, up rock house Hollow. De-energized | Bowling’s Creek Rd. Altro, Ky. | 2023-06-14
2019 | 2019-02-14 | Hazard | 75633293 | DKY0108214 | 37830146000020 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole been braced. | Bowling’s Creek Rd. Altro, Ky. | 2020-03-26
2019 | 2019-02-14 | Hazard | 75611381 | DKY0108205 | 37830146000021 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole has been braced. | Bowling’s Creek Rd. Altro, Ky. | 2020-03-24
2019 | 2019-02-14 | Hazard | 74698230 |  | 37830146000098 |  | 3301101-CHAVIES / CHAVIES | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Looks like this has been de-energized and let down for customer to cut tree. Light secondary. Needs removed or resagged to pole | Bowling’s Creek Rd. Altro, Ky. | 2019-10-14
2019 | 2019-02-14 | Hazard | N/A |  | 37830146A30151 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr. | Bowling Creek, Kentucky 41339, USA | 2023-06-14
2019 | 2019-02-14 | Hazard | N/A |  | 37830171000192 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning bad, needs straighten. Install: 2019 | Ky. Highway 28, Chavies, Ky. | 2023-06-08
2019 | 2019-02-14 | Hazard | 83370714 | DKY0117977 | 37830196B30261 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. | Maggard Ridge, Chavies, Ky.
2019 | 2019-02-14 | Hazard | 83370714 | DKY0117977 | 37830196B30284 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. | Maggard Ridge, Chavies, Ky.
2019 | 2019-02-14 | Hazard |  |  | 38831083C30248 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Need to remove 1/0 lash and pole. Leaning bad | Main St, Jackson, Ky.
2019 | 2019-02-14 | Hazard | 75659490 | DKY0108248 | 38831083C40430 |  | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole rotten. Off picnic hill. | 65 State Dr, Jackson, KY 41339, USA | 2020-03-16
2019 | 2019-02-14 | Hazard |  |  | 38831083D10677 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Inactive xfmr. Two pole tap needs removed. 1083-677, 1083-678.
2019 | 2019-02-14 | Hazard | 75739496 | DKY0108926 | 38831083D30020 |  | 3308001-JACKSON / S.JACKSON | Line Work | OH | guys/anchors: broken or missing | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Guy wire broke, needs removed or replaced. | Railroad St, Kentucky 41339, USA | 2020-04-03
2019 | 2019-02-14 | Hazard |  |  | 38831083D41002 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. | Armory Dr. Jackson, Ky.
2019 | 2019-02-14 | Hazard |  |  | 38831084B00149 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Inactive xfmr | Shucks Bean Hollow, Jackson, Ky.
2019 | 2019-02-14 | Hazard | 75739496 | DKY0108926 | 38831084B00150 |  | 3308001-JACKSON / S.JACKSON | Line Work | OH | guys/anchors: broken or missing | pole: leaning, burned more than 50% remaining |  | Foreign |  | Guy wire missing. Install: 1960 | Shucks Bean Hollow, Jackson, Ky. | 2020-04-03
2019 | 2019-02-14 | Hazard | 85691772 | DKY0122314 | 38831107000029 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | cutout: damaged , service: unused or abandoned, blanked meter base | lightning arresters/insulators: damaged | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , Forestry - DESCRIBE IN COMMENTS | KPC |  | R/W To cut path to pole. Retire secondary pole 1108-491 | Stray Branch Rd. Jackson, Ky.
2019 | 2019-02-14 | Hazard | UNKNOWN | UNKNOWN | 38831108A00153 |  | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | Foreign | YES | COMPLETE IN FIELD. Install: 2015 | Adams Dr. Jackson, Ky. | 2020-01-18
2019 | 2019-02-14 | Hazard | 72794754 | DKY0104303 | 38831108A00154 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | already written to EDN100577 FOREIGN | Bad pole. Off armory dr. Install: 1947 | Adams Dr. Jackson, Ky. | 2022-10-19
2019 | 2019-02-14 | Hazard | 72794754 | DKY0104303 | 38831108A00155 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | already written to EDN100577 FOREIGN | Bad pole. Off armory dr. Install: 1947 | Adams Dr. Jackson, Ky. | 2023-04-06
2019 | 2019-02-14 | Hazard |  |  | 38831108A00401 | TRUE | 3308001-JACKSON / S.JACKSON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign |  | Needs big bucket, three phase service rolled up on pole. Heavy! | Old Quicksand Rd. Jackson, Ky.
2019 | 2019-02-14 | Hazard | 70009056 | DKY0100212 | 38831108B00253 |  | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | already written to EDN100577 FOREIGN | Pole rotten. Might have job on this. Pole stake is there. | 151 Turner Dr, Jackson, KY 41339, USA | 2022-03-17
2019 | 2019-02-15 | Hazard | 75739484 | DKY0108659 | 37830147000035 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Primary guy broke. On bank above driveway. | 99 Big Fork Rd. Altro, Ky
2019 | 2019-02-15 | Hazard |  |  | 37830147000140 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. | Highway 1110, Altro, Ky
2019 | 2019-02-15 | Hazard |  |  | 37830147B30193 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. Driveway a little rough to pole. | Dange Creek, Altro, Ky.
2019 | 2019-02-15 | Hazard | 75604681 | DKY0108163 | 37830171000108 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole has be stubbed | Hwighway 1110, Altro, Ky. | 2020-12-09
2019 | 2019-02-18 | Hazard | 83423522 | DKY0118062 | 37830246A00330 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Inactive xfmr,beside road in curve. | Couchtown Rd, Kentucky 41723, USA | 2023-01-05
2019 | 2019-02-18 | Hazard |  |  | 37830246B00137 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Inactive xfmr, and secondary and secondary pole. Sec. pole 246-B-342 remove | Couchtown Rd, Kentucky 41723, USA
2019 | 2019-02-18 | Hazard |  |  | 37830246D00544 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive tap and xfmr. Old driveway going to property but not been used in awhile. | Eversole Rd, Kentucky 41723, USA
2019 | 2019-02-18 | Hazard |  |  | 37830270C00047 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr, | W Ky. Highway 80, Avawam, Ky
2019 | 2019-02-18 | Hazard |  |  | 37830270C00128 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr, secondary pole, 4/2 secondary. Sec. pole 270-C-266 remove
2019 | 2019-02-18 | Hazard |  |  | 37830270C00408 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Secondary pole leaning. Install: 1995 | Couchtown Rd & Fields Ln, Kentucky 41723, USA
2019 | 2019-02-18 | Hazard |  |  | 37830295B00283 |  | 3308503-BONNYMAN / BIGCREEK | Service Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Broken guy wire, anchor there. | Browns Fork Rd, Kentucky 41701, USA
2019 | 2019-02-18 | Hazard | 83423522 | DKY0118062 | 37830319000165 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Inactive xfmr | Browns Fork, Hazard, Ky. | 2023-01-05
2019 | 2019-02-18 | Hazard | 83423522 | DKY0118062 | 37830319D30239 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Melton Dr. Browns Fk. Hazard, Ky. | 2023-01-05
2019 | 2019-02-18 | Hazard | 72783005 | DKY0104321 | 37830320B00185 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | already written to EDN100577 FOREIGN | Bad stubbed pole, head of Browns Fork.WS has set pole | Floyd Dr. Browns Fk. Rd. Hazard, Ky. | 2022-02-22
2019 | 2019-02-19 | Hazard | 83423522 | DKY0118062 | 37830244000173 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr, and sec. pole 244-198 needs removed | Walker Ln. Yerkes, Ky | 2023-01-05
2019 | 2019-02-19 | Hazard | 75652490 | DKY0108228 | 37830246B00022 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | YES | Inactive xfmr, pole in bad shape, needs changed. | Snatch Creek Rd. Busy, Ky. | 2020-11-30
2019 | 2019-02-19 | Hazard | 83423522 | DKY0118062 | 37830246B00224 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr, 2 secondary poles and secondary needs removed. Pole 246-B-366, 246-B-380 | Snatch Creek, Busy, Ky. | 2023-01-05
2019 | 2019-02-19 | Hazard |  |  | 37830246B00426 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Ky. Highway, 451, Busy, Ky.
2019 | 2019-02-19 | Hazard |  |  | 37830246D00161 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Tap that goes up from this pole needs to be de-energized and removed. Trees grow thru lines. Does not serve anyone. | Snatch Creek Rd. Busy, Ky
2019 | 2019-02-19 | Hazard |  |  | 37830269C00058 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | 4 pole tap and xfmrs not in use needs removed. Road is rough and has ruts. In the head of Laurel. | Laurel Mt. Rd. Yerkes, Ky.
2019 | 2019-02-19 | Hazard | 75739524 | DKY0109106 | 37830270A00094 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarm split, bad shape | Ky. Highway 451, Busy, Ky. | 2023-10-31
2019 | 2019-02-19 | Hazard | 75739524 | DKY0109106 | 37830270A00098 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarm split | Ky. Highway 451, Busy, Ky. | 2023-10-31
2019 | 2019-02-19 | Hazard |  |  | 37830270A00100 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  | crossarm/braces: deteriorated, not rotten | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Cross arm in bad shape. Inactive one pole tap and inactive xfmr. Pole 270-A-348 | Sunlight Ln., Busy, Ky.
2019 | 2019-02-19 | Hazard |  |  | 37830270A00197 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. On right before Morris dr. | Ky. Highway 451, Busy, Ky.
2019 | 2019-02-19 | Hazard | 78733527 | DKY0112635 | 37830270A00355 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Stallings Mt. Rd. Busy, Ky. | 2021-06-22
2019 | 2019-02-19 | Hazard | 78727187 | DKY0112618 | 37830270C00020 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive Secondary and poles, poles that need removed 270-C-20, 270-C-432, 270-C-381. Near old fields store. | Jess Fields Ln. Busy, Ky. | 2021-07-09
2019 | 2019-02-20 | Hazard | 83431689 | DKY0118070 | 37830269A00204 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Forked Mouth Br Rd, Kentucky 41723, USA
2019 | 2019-02-20 | Hazard |  |  | 37830269B00068 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr and 2 secondary pole and secondary, pole 269-B-262, 269-B-341. Remove | Forked Mouth Br Rd, Kentucky 41723, USA
2019 | 2019-02-20 | Hazard |  |  | 37830269B00069 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr and secondary pole and secondary, pole 269-B-221, 269-B-320. Removed | Forked Mouth Br Rd, Kentucky 41723, USA
2019 | 2019-02-20 | Hazard |  |  | 37830269B00275 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr and secondary pole and secondary. Remove | Forked Mouth Br Rd, Kentucky 41723, USA
2019 | 2019-02-20 | Hazard |  |  | 37830269B00289 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Bean Eye Ln, Kentucky 41723, USA
2019 | 2019-02-20 | Hazard |  |  | 37830269C00100 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr and secondary 1/0 lash and sec. pole 269-C-324 remove | Pomp Hollow Rd. Busy, Ky.
2019 | 2019-02-20 | Hazard | 75580543 | DKY0108123 | 37830270B00082 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr, missing ground been stolen. Also sec. pole 270-B-410 needs removed with secondary. | Briar Fork Circle Rd, Kentucky, USA | 2020-02-25
2019 | 2019-02-20 | Hazard | 75739524 | DKY0109106 | 37830293000052 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr, pole ground stolen. | Beech Oak Rd. Busy, Ky. | 2023-10-31
2019 | 2019-02-20 | Hazard |  |  | 37830293000172 |  | 3308503-BONNYMAN / BIGCREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service rolled up on pole. Near head of ROCKHOUSE fork. | Rockhouse Fork Rd, Kentucky 41723, USA
2019 | 2019-02-21 | Hazard |  |  | 37830268000037 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Toulouse Rd. Busy, Ky
2019 | 2019-02-21 | Hazard |  |  | 37830268000044 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr and secondary pole 268-73 and secondary needs removed. | John Blood Hollow, Kentucky 41723, USA
2019 | 2019-02-21 | Hazard | 75739524 | DKY0109106 | 37830268A20191 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr and secondary pole 268-A-192 and secondary. | Toulouse Rd. Busy, Ky. | 2023-10-31
2019 | 2019-02-21 | Hazard |  |  | 37830269C00006 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Big Willard Rd, Busy, Ky.
2019 | 2019-02-21 | Hazard |  |  | 37830270A00103 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  | crossarm/braces: deteriorated, not rotten | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr, crossarm bowed | 6242 Highway 451, Busy, Ky.
2019 | 2019-02-21 | Hazard |  |  | 37830270A00363 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Arm pin bolt loose, insulator laying on arm. | Highway 451, Busy, Ky.
2019 | 2019-02-21 | Hazard | 75659482 | DKY0108246 | 37830292000067 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole been stubbed. | Pepper Rd, Kentucky 41723, USA | 2020-11-19
2019 | 2019-02-21 | Hazard | 77216127 | DKY0110512 | 37830292D30239 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole in a slip, leaning a little. Cracks in ground behind pole. Might need too send tech. Out to look at. Cell tower | Pepper Rd, Kentucky 41723, USA | 2020-11-19
2019 | 2019-02-22 | Hazard | 75659636 | DKY0108251 | 37830247A00455 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole split at the top | Marcus Hollow, Bonnyman, Ky. | 2020-03-17
2019 | 2019-02-22 | Hazard |  |  | 37830247A00462 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service laying on communication cable | Typo Rd, Bonnyman, Ky.
2019 | 2019-02-22 | Hazard |  |  | 37830247A01117 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Marcus Hollow, Kentucky 41719, USA
2019 | 2019-02-22 | Hazard |  |  | 37830247B00103 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning bad! Install: 1995 | Typo Rd. Bonnyman, Ky.
2019 | 2019-02-22 | Hazard | 74729757 |  | 37830247B01121 |  | 3308503-BONNYMAN / BIGCREEK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Rolled up service | Typo Rd. Bonnyman, Ky. | 2019-10-25
2019 | 2019-02-22 | Hazard |  |  | 37830296B10356 |  | 3300602-BLUEGRASS / HAZARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign |  | Messer br. Vines have neutral pulled down in reaching distance. | Messer Br. Hazard, Ky. | 2020-06-02
2019 | 2019-02-25 | Hazard | N/A |  | 37830249B00144 |  | 3300601-BLUEGRASS / WALKERTOW | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Unused service, upper second Crk. | Morgan Dr. Hazard, Ky. | 2023-06-02
2019 | 2019-02-25 | Hazard | N/A |  | 37830272B31565 |  | 3300601-BLUEGRASS / WALKERTOW | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Unused service | Combs St. Hazard, Ky. | 2023-06-02
2019 | 2019-02-25 | Hazard |  |  | 37830272B40085 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground missing | 163 Deaton St. Hazard, Ky.
2019 | 2019-02-25 | Hazard | 76778975 | DKY0110111 | 37830272B40095 |  | 3300602-BLUEGRASS / HAZARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Low wires | 116 Hill St. Hazard, Ky.
2019 | 2019-02-25 | Hazard | N/A |  | 37830272C21116 |  | 3300601-BLUEGRASS / WALKERTOW | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Unused service | 511 Young St. Hazard, Ky. | 2023-06-02
2019 | 2019-02-25 | Hazard | 76778975 | DKY0110111 | 37830295D00084 |  | 3300602-BLUEGRASS / HAZARD | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign |  | Xfmr leaking oil | 488 Messer Br. Hazard, Ky.
2019 | 2019-02-25 | Hazard |  |  | 37830295D00137 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Eldorado Dr. hazard, Ky.
2019 | 2019-02-25 | Hazard |  |  | 37830295D00140 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND , guys/anchors: broken or missing |  |  | Foreign |  | Guys broken and pole ground missing. | Fred Combs Dr. Hazard, Ky.
2019 | 2019-02-25 | Hazard | 76778975 | DKY0110111 | 37830296A30464 |  | 3300602-BLUEGRASS / HAZARD | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Blown arrester | High St. Hazard, Ky.
2019 | 2019-02-25 | Hazard | 74729777 |  | 37830296A31121 |  | 3300601-BLUEGRASS / WALKERTOW | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Service unused, near beams electric. | Town Mt Rd. Hazard, Ky. | 2019-10-25
2019 | 2019-02-26 | Hazard | 75290156 | Dky0107620 | 37830134C00042 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC |  | Inactive xfmr near Crk. | 750 Wiley Fork Rd. Soft shell, Ky. | 2019-12-18
2019 | 2019-02-26 | Hazard | 75216299 | DKY0107551 | 37830134C00058 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | already written to EDN100577 KPC pole | Pole rotten and inactive xfm. | Ratliff School Rd. Lebrun, Ky. | 2020-03-04
2019 | 2019-02-26 | Hazard | 75293006 | DKY0107622 | 37830134D00083 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Inactive xfmr and 1 pole tap needs removed 134-D-167 company pole. | Hicks Branch Rd. Soft shell, Ky. | 2019-12-20
2019 | 2019-02-26 | Hazard | 72258254 | Dky0103461 | 37830135000201 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | already written to EDN100577 KPC pole | Pole rotten. | Ratliff School Rd. Lebrun, Ky. | 2019-05-15
2019 | 2019-02-26 | Hazard |  |  | 37830153A00026 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | guys/anchors: broken or missing |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr and primary guy broke. | Jake Ridge Rd. Ary, Ky.
2019 | 2019-02-26 | Hazard |  |  | 37830153B00189 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Coal stone Rd. Ary, Ky.
2019 | 2019-02-26 | Hazard |  |  | 37830153D00191 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive 2 pole tap and xfmr needs removed. | Ky. Hwy. 476, Ary, Ky.
2019 | 2019-02-26 | Hazard |  |  | 37830153D00246 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Lash been cut down off xfmr pole. Remove secondary pole and secondary. | Laurel Lick Br. Ary, Ky.
2019 | 2019-02-26 | Hazard |  |  | 37830153D10319 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Slide behind pole, tech. needs to check. Mouth of laurel lick br. 3 phase. | Ky. Highway 476, Ary, Ky. | 2020-01-18
2019 | 2019-02-26 | Hazard | 75221647 | Dky0107557 | 37830157000151 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive 1 pole tap and xfmr. Remove | Chimney Rock Road, Lebrun, Ky | 2019-02-07
2019 | 2019-02-26 | Hazard |  |  | 37830172B00093 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy broken | Chavies Dunraven Rd. Chavies, Ky.
2019 | 2019-02-26 | Hazard |  |  | 37830172B00094 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | pole needs straightened. Between RR tracks and Creek. Install: 1988 | Hwy. 451, Chavies, Ky.
2019 | 2019-02-26 | Hazard | 75659381 | DKY0108243 | 37830172B00115 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy. 451, Chavies, Ky.
2019 | 2019-02-26 | Hazard | 75659301 | DKY0108239 | 37830177A00127 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad stubbed pole. | Wolf Pen Rd. Ary, Ky. | 2020-12-07
2019 | 2019-02-26 | Hazard | 75659778 | DKY0108254 | 37830177B00084 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad stubbed pole. | Dogwood View Ln. Bulan, Ky. | 2020-03-09
2019 | 2019-02-26 | Hazard |  |  | 37830177B00264 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Dogwood View, Ln. Bulan, Ky.
2019 | 2019-02-26 | Hazard |  |  | 37830196A00107 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr and 1 pole tap, needs removed. | Napier Br. Krypton, Ky.
2019 | 2019-02-26 | Hazard |  |  | 38831036000009 | TRUE | 3308002-JACKSON / PANBOWL | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 , Forestry - DESCRIBE IN COMMENTS | Foreign |  | Inactive tap.trees grower up in r/w | Frozen Mt. Jackson, Ky.
2019 | 2019-02-26 | Hazard |  |  | 38831036000019 |  | 3308002-JACKSON / PANBOWL | Line Work | OH | service: unused or abandoned, blanked meter base |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr and secondary and secondary pole 1036-20. Remove. | Frozen Mt. Jackson, Ky.
2019 | 2019-02-26 | Hazard |  |  | 38831060C00069 |  | 3308002-JACKSON / PANBOWL | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | Inactive service | Tower Mt. Rd. Jackson, Ky.
2019 | 2019-02-26 | Hazard |  |  | 38831083A30902 |  | 3308002-JACKSON / PANBOWL | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign |  | Service cut dead | Park Road, Jackson, Ky.
2019 | 2019-02-26 | Hazard |  |  | 38831083C20411 |  | 3308002-JACKSON / PANBOWL | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property , service: unused or abandoned, blanked meter base |  |  | KPC |  | Inactive xfmr | Combs St. Jackson, Ky.
2019 | 2019-02-26 | Hazard |  |  | 38831083C30202 |  | 3308002-JACKSON / PANBOWL | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign |  | Lot of slack in line. Hardee’s parking lot. | Hwy. 15. Jackson, Ky.
2019 | 2019-02-26 | Hazard |  |  | 38831084A00040 |  | 3308002-JACKSON / PANBOWL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , cutout: damaged |  | Forestry - DESCRIBE IN COMMENTS | Foreign | YES | Tree between phases. Tech. Needs to check. | LBJ Rd. Jackson, Ky.
2019 | 2019-02-26 | Hazard |  |  | 38831084A00098 |  | 3308002-JACKSON / PANBOWL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign |  | Bad pole | Tin her Ln. Jackson, Ky. | 2019-04-11
2019 | 2019-02-26 | Hazard |  |  | 38831084A00248 |  | 3308002-JACKSON / PANBOWL | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign |  | Braces broken | Hwy. 15, Jackson, Ky.
2019 | 2019-02-26 | Hazard |  |  | 38831084A00310 |  | 3308002-JACKSON / PANBOWL | Line Work | OH | cutout: damaged , UG conduit: damaged or separated |  |  | Foreign |  | C/0 bad, conduit Bracket broken on pole. Behind IGA store | Meeting House Br. Jackson, Ky.
2019 | 2019-02-27 | Hazard |  |  | 37830129D00051 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive 1 pole tap. With xfmr. Doesn’t show on map. May need Asplundh manual crew to cut trees to remove wires, Road crossing | Ball Fork Rd. Ary, Ky.
2019 | 2019-02-27 | Hazard |  |  | 37830130000001 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  |  | Vest Talcum Rd, Kentucky, USA
2019 | 2019-02-27 | Hazard |  |  | 37830130000094 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive 4 pole tap thru trees needs removed | Laura Surilda Ln, Kentucky, USA
2019 | 2019-02-27 | Hazard | 72650554 | DKY0104096 | 37830131000062 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | YES | Thacker Grigsby has set new pole. Other pole in slide. Line inactive from this pole on, needs removed. | Vest, KY 41831, USA | 2019-03-06
2019 | 2019-02-27 | Hazard | 75659940 | DKY0108266 | 37830131000074 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole broken off use a pole extension, may need changed out. | Vest Talcum Rd, Kentucky, USA | 2020-02-18
2019 | 2019-02-27 | Hazard |  |  | 37830131000082 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Retro Ritchie Rd. Talcum, Ky.
2019 | 2019-02-27 | Hazard |  |  | 37830131000094 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Estep Ritchie Rd. Talcum, Ky.
2019 | 2019-02-27 | Hazard |  |  | 37830153C00012 | TRUE | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 3phase pole, split at top, 1941 vintage. Just below laurel fk. around curve on right on cliff. 37830153C00012 | Hwy. 476, Dwarf, Ky
2019 | 2019-02-27 | Hazard | 73087241 | 033843873 | 37830153C00208 |  | 3307301-BULAN / ARY-HEINE | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Unused service, remove | Hwy. 476, Ary, Ky. | 2019-04-12
2019 | 2019-02-27 | Hazard | DKY0106607 |  | 37830154000084 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad stubbed secondary pole | Vest Talcum Rd, Kentucky, USA | 2019-09-16
2019 | 2019-02-28 | Hazard | 79947034 | DKY0114358 | 37830330000005 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Milstone Rd. Milstone, Ky. | 2021-09-16
2019 | 2019-02-28 | Hazard |  |  | 37830330000056 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. | Milstone Rd. Milstone, Ky. | 2021-07-06
2019 | 2019-02-28 | Hazard | 75729006 | DKY0108391 | 37830331B00141 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole cutoff | Meadow Fork, Milstone, Ky. | 2020-06-23
2019 | 2019-02-28 | Hazard |  |  | 37830354000096 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning bad. May want to reroute line up road. Install: 1972 | Millstone Rd. Milestone, Ky. | 2021-07-06
2019 | 2019-02-28 | Hazard | N/A |  | 37830355A00212 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH |  | transformers: leaking, damaged |  | KPC | NO | CSP xfmr, May want to change out. | Lick Fork, Milstone, Ky. | 2023-08-23
2019 | 2019-02-28 | Hazard | 86298281 |  | 37830355A00304 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property , conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive 6 pole three phase tap. 2 inactive xfmrs. Pole 355-A-585 and 355-A-538 | Millstone Rd, Kentucky 41838, USA
2019 | 2019-02-28 | Hazard | 79947034 | DKY0114358 | 37830355A00629 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Milstone Rd. Milstone, Ky. | 2021-09-16
2019 | 2019-02-28 | Hazard | 85681127 | DKY0122323 | 37830355B00325 | TRUE | 3314402-MAYKING / MILLSTONE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC |  | Inactive xfmr | Board Rd, Kentucky 41838, USA
2019 | 2019-02-28 | Hazard | 85681127 | DKY0122323 | 37830355B00413 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr, manual | Hickery Dr. Milstone, Ky.
2019 | 2019-02-28 | Hazard | 85681127 | DKY0122323 | 37830355B00557 | TRUE | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 , Forestry - DESCRIBE IN COMMENTS | KPC |  | Inactive one pole tap and xfmr. Pole 355-B-615. R/w crew manual to cut path and around pole. | Millstone, KY 41837, USA
2019 | 2019-03-01 | Hazard |  |  | 37830378B00104 | TRUE | 3314402-MAYKING / MILLSTONE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Inactive 4 pole tap and 3 xfmrs. Line cut dead on pole 378-104, line down to spans up. Retire line and xfmrs. Road there but bad shape. | Gazelle Dr, Kentucky 41855, USA
2019 | 2019-03-01 | Hazard | 74794206 |  | 37830378D00080 |  | 3314402-MAYKING / MILLSTONE | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Inactive service | High Knob Dr, Kentucky 41837, USA | 2019-10-09
2019 | 2019-03-01 | Hazard | N/A |  | 37830378D00096 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive one pole tap. Wires already off take off pole. Need to retire line. | Buster Rd, Kentucky, USA | 2023-08-18
2019 | 2019-03-04 | Hazard |  |  | 37830128000059 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive 4 pole tap, fuse open lines down. | Ollie Ln. Ary, Ky.
2019 | 2019-03-04 | Hazard |  |  | 37830128000070 |  | 3307301-BULAN / ARY-HEINE | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Low inactive service. Needs removed. | Campbell’s Branch Rd. Ary, Ky
2019 | 2019-03-04 | Hazard | 75659357 | DKY0108245 | 37830128000093 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is slide. | McKinley Branch, Ary, Ky. | 2020-03-16
2019 | 2019-03-04 | Hazard |  |  | 37830128000197 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | service: unused or abandoned |  | conductors: excessive splices, deteriorated conductors , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive service. Just below Ollie ln. on left, old double wide trl. 4/0 secondary and secondary pole 129-197 needs removed trees growing thru sec. '37830128000197 | Hwy. 476, Ary, Ky.
2019 | 2019-03-04 | Hazard |  |  | 37830129A00178 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive 3phase bank, yard pads will work here | Willie Fay Dr. Ary, Ky.
2019 | 2019-03-04 | Hazard |  |  | 37830129A00180 | TRUE | 3307301-BULAN / ARY-HEINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Willie Fay Dr. Ary, Ky.
2019 | 2019-03-04 | Hazard |  |  | 37830129A00182 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr and secondary and secondary pole 129-A-183. Yard pads will probably work here. | Willie Fay Dr. Ary, Ky.
2019 | 2019-03-06 | Hazard | 77618324 | DKY0111023 | 37830370000038 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Old cracked pole, csp xfmr there to. | 7150 Ky. Hwy. 7, Fusonia, Ky. | 2020-12-03
2019 | 2019-03-06 | Hazard | 76779279 | DKY0110060 | 37830371000044 | TRUE | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr and secondary pole 371-B-398 and 2/4 secondary. |  | 2022-06-22
2019 | 2019-03-06 | Hazard |  |  | 37830371000049 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr and secondary and secondary pole 371-158. | Big Branch Rd. Fusonia, Ky. | 2020-06-02
2019 | 2019-03-07 | Hazard |  |  | 37830419C00227 | TRUE | 3301701-DAISY / DAISY | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Arms swayed and splintered | Gas Rd, Ulva, Ky.
2019 | 2019-03-07 | Hazard |  |  | 37830420A40530 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Talent Branch, Kentucky 41731, USA | 2020-06-02
2019 | 2019-03-07 | Hazard |  |  | 37830450000096 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH | guys/anchors: broken or missing |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove xfmr and service, cutout, arrestor | 1123 State Hwy 3410, Mayking, KY 41837, USA
2019 | 2019-03-14 | Hazard | 77616520 | DKY0111020 | 37830394C00148 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | YES | Pole rotten at top. Open secondary and pole needs removed. | Dykes Branch Rd, Fusonia, Ky. | 2020-12-08
2019 | 2019-03-14 | Hazard | 75713880 |  | 37830394D00030 |  | 3301701-DAISY / DAISY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Ground wire missing | Dykes Branch Rd, Kentucky 41774, USA | 2020-01-31
2019 | 2019-03-14 | Hazard |  |  | 37830418C20328 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole in slide. | Campbell Branch Rd. Cornettsville, Ky. | 2020-09-01
2019 | 2019-03-18 | Hazard |  |  | 37830444000060 | TRUE | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Inactive 3 pole tap, 2 inactive xfmrs needs removed. Side by side would be useful. | Hoot Owl Hollow, Hallie, Ky.
2019 | 2019-03-18 | Hazard |  |  | 37830444000065 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Inactive one pole tap. R/w bad | Dead End Rd. Hallie, Ky. | 2019-03-18
2019 | 2019-03-18 | Hazard | 76779178 | DKY0110231 | 37830444000106 | TRUE | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Inactive xfmr and secondary and secondary pole 444-132. Remove | Iron Wood Dr. Hallie, Ky. | 2022-03-21
2019 | 2019-03-18 | Hazard | 76779279 | DKY0110060 | 37830467C40118 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Long Branch, Hallie, Ky. | 2022-06-22
2019 | 2019-03-18 | Hazard | 76779178 | DKY0110231 | 37830468000062 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Inactive one pole. | Long Branch, Hallie, Ky. | 2022-03-21
2019 | 2019-03-18 | Hazard |  |  | 37830469000030 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Inactive 5 pole tap and xfmr. Trees grower up thru lines | Lilley Cornett Br. Hallie, Ky. | 2020-06-02
2019 | 2019-03-18 | Hazard | 76779279 | DKY0110060 | 37830469B30255 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Lilly Cornett Br. Hallie, Ky. | 2022-06-22
2019 | 2019-03-18 | Hazard | 76779279 | DKY0110060 | 37830492000091 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Bates Fork, Hallie, Ky. | 2022-06-22
2019 | 2019-03-19 | Hazard | 76779178 | DKY0110231 | 37830444000011 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Inactive xfmr. May need pads to cross ditch line, old rd.. | Hwy.1103, Hallie, Ky. | 2022-03-21
2019 | 2019-03-19 | Hazard |  |  | 37830493000042 |  | 3301701-DAISY / DAISY | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Ground wire missing. | Big Branch Rd. Hallie, Ky.
2019 | 2019-03-19 | Hazard |  |  | 37830493000046 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole missing got pole extension. | Big Branch Rd. Hallie, Ky | 2021-10-21
2019 | 2019-03-19 | Hazard |  |  | 37839494000135 |  | 3301701-DAISY / DAISY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground missing. Gas rd. In head of big br. | Big Branch Rd. Hallie, Ky
2019 | 2019-03-27 | Hazard | 76779353 | DKY0110146 | 37830201B00202 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr and inactive one pole tap | Ky, Highway 476, Dwarf, Ky. | 2021-02-10
2019 | 2019-03-28 | Hazard | 75659541 | DKY0108249 | 37830176000049 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole old and in bad shape | 33 Mahogany Hill Dr, Hazard, KY 41701, USA | 2020-05-04
2019 | 2019-03-28 | Hazard |  |  | 37630176000140 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive one pole tap and xfmr. Needs removed. | Maple Branch Ln. Bulan, Ky. | 2021-03-11
2019 | 2019-03-28 | Hazard | 76779353 | DKY0110146 | 37830176000136 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. | Riley Gayheart Cemetery Rd. Bulan, Ky. | 2021-02-10
2019 | 2019-03-28 | Hazard | 76778487 | DKY0110155 | 37830225B00028 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr and secondary and secondary poles 225-B-464 and 225-B-520 Needs removed. | 565 Hardburly Rd, Bulan, KY 41722, USA | 2020-12-17
2019 | 2019-03-28 | Hazard | 75652906 | DKY0108235 | 37830225B00037 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Low clearance and leaning. Install: 1962 | 911 Hardburly Rd, Bulan, KY 41722, USA | 2022-05-24
2019 | 2019-03-28 | Hazard | 76778487 | DKY0110155 | 37830225B00038 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning bad. Install:1991 | 911 Hardburly Rd, Bulan, KY 41722, USA | 2020-12-17
2019 | 2019-03-28 | Hazard | 73089981 | DKY0104734 | 37830225D00126 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | already written to EDN100577 FOREIGN | Bad pole needs changed | Muddy Hollow Rd, Kentucky 41722, USA | 2021-01-11
2019 | 2019-04-09 | Hazard | 73058968 | DKY0104710 | 37830177D00051 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Three phase broke at telephone lines | Hwy. 476, Dwarf, Ky. | 2019-04-30
2019 | 2019-04-09 | Hazard | 76779238 | DKY0113097 | 37830201B00005 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | One pole tap and xfmr remove. xfmr Pole 201-B-244 | KY-476, Kentucky, USA | 2021-12-10
2019 | 2019-04-23 | Hazard | 80455207 | DKY0114634 | 37830248A00677 | TRUE | 3301402-COMBS / AIRPORTGA | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | crossarms in bad shape! | Combs Rd, Kentucky 41729, USA | 2023-04-13
2019 | 2019-05-20 | Hazard |  |  | 37830491000093 | TRUE | 3309902-SLEMP / LEATHERWOOD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Located in yard, loose secondary guy, pole leaning. | 4271 Little Leatherwood Creek, Daisy, Ky.
2019 | 2019-05-23 | Hazard | 85788306 | DKY0122362 | 37830299D00078 | TRUE | 3309302-VICCO / JEFF | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr, conductors cut dead at this pole, need to remove in trees. | Rowdy Hollow Rd, Kentucky, USA
2019 | 2019-05-23 | Hazard |  |  | 37830346A00389 | TRUE | 3309302-VICCO / JEFF | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr bank, behind A&T Construction. | Browder Ln, Kentucky, USA
2019 | 2019-05-28 | Hazard | 74698412 |  | 37830347A00172 |  | 3309302-VICCO / JEFF | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Inactive service, rolled upon pole | George's Branch Rd, Kentucky, USA | 2019-09-30
2019 | 2019-05-28 | Hazard | N/A |  | 37830347A00185 |  | 3309302-VICCO / JEFF | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive one pole tap and xfmr. Take off pole 347-A-90. | George's Branch Rd, Kentucky, USA | 2023-08-02
2019 | 2019-05-29 | Hazard |  |  | 37830251000091 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Low clearance over roof and porch. | Buck Branch Rd, Kentucky 41701, USA
2019 | 2019-05-29 | Hazard |  |  | 37830348A00280 |  | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Creek has washed bank away from pole, may need to change. | Montgomery Creek Rd, Vicco, KY 41773, USA | 2020-01-18
2019 | 2019-05-29 | Hazard | 74711648 |  | 37830348A10282 |  | 3309302-VICCO / JEFF | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground missing | Montgomery Creek Rd, Vicco, KY 41773, USA | 2019-09-30
2019 | 2019-05-30 | Hazard | 75698452 | DKY0108321 | 37830372000093 |  | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Manual pole, poles been stubbed. Across creek on bank. | Roark Ln. Vicco, Ky. | 2020-11-06
2019 | 2019-05-30 | Hazard | 75698377 | DKY0108319 | 37830372000095 |  | 3309302-VICCO / JEFF | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive xfmr and secondary pole needs removed. Secondary pole 372-135 | Roark Ln. Vicco, Ky. | 2020-11-19
2019 | 2019-05-30 | Hazard |  |  | 37830373000121 |  | 3309302-VICCO / JEFF | Line Work | OH | cutout: damaged |  |  | KPC |  | One pole tap line fuse C/O is loose or bent. | Carcassonne Rd, Kentucky, USA | 2021-06-07
2019 | 2019-06-03 | Hazard | 74713321 | 037301287 | 37830323D00648 |  | 3309302-VICCO / JEFF | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen | Montgomery Creek Rd. Vicco, Ky. | 2019-11-17
2019 | 2019-06-03 | Hazard | 74700958 |  | 37830348A00155 |  | 3309302-VICCO / JEFF | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen | Montgomery Creek Rd. Vicco, Ky. | 2019-10-07
2019 | 2019-06-03 | Hazard | 74708395 |  | 37830348D00324 |  | 3309302-VICCO / JEFF | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen | Montgomery Creek Rd, Vicco, KY 41773, USA | 2019-10-07
2019 | 2019-06-03 | Hazard | 74708835 |  | 37830348D40413 |  | 3309302-VICCO / JEFF | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen | Montgomery Creek Rd, Vicco, KY 41773, USA | 2019-10-07
2019 | 2019-06-03 | Hazard |  |  | 37830370000024 | TRUE | 3309302-VICCO / JEFF | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive xfmr and secondary and two secondary poles.# 370-155 and 370-207 | 5308 Upper River Rd, Jeff, KY 40207, USA
2019 | 2019-06-03 | Hazard | 74709476 |  | 37830372C30195 |  | 3309302-VICCO / JEFF | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen | Montgomery Creek Rd, Vicco, KY 41773, USA | 2019-10-07
2019 | 2019-06-03 | Hazard |  |  | 37830372C30197 |  | 3309302-VICCO / JEFF | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen | Montgomery Creek Rd, Vicco, KY 41773, USA | 2019-06-03
2019 | 2019-06-03 | Hazard | 74710708 |  | 37830372C30200 |  | 3309302-VICCO / JEFF | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen | Montgomery Creek Rd, Vicco, KY 41773, USA | 2019-09-30
2019 | 2019-06-03 | Hazard | 74709920 |  | 37830372C40203 |  | 3309302-VICCO / JEFF | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen | Montgomery Creek Rd, Vicco, KY 41773, USA | 2019-09-30
2019 | 2019-06-03 | Hazard | 75693984 | DKY0108318 | 37830373000094 |  | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at ground level. Located across road from Jent cemetery sign. | Carcassonne Rd, Kentucky, USA | 2020-09-28
2019 | 2019-06-03 | Hazard | 85794918 |  | 37830373000199 | TRUE | 3309302-VICCO / JEFF | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive one pole tap, take off pole# 373-111 | Square Dance Rd, Kentucky 41804, USA
2019 | 2019-06-04 | Hazard |  |  | 37830346B00084 | TRUE | 3309302-VICCO / JEFF | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Remove inactive 4 pole tap and xfmr. | Upper River Rd, Kentucky, USA
2019 | 2019-06-10 | Hazard | N/A |  | 37830246C00194 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | 6A cu. primary unraveling | Lower 2nd Creek Rd, Kentucky 41719, USA | 2023-10-02
2019 | 2019-06-11 | Hazard |  |  | 37830151000193 | TRUE | 3311701-SHAMROCK / SHAMROCK | Line Work | OH | guys/anchors: broken or missing , transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign |  | Primary guy broken, probably will need a new ancho and rod installed. Inactive xfmr also and C/O. | Rowdy Low Gap, Lost Creek, Ky.
2019 | 2019-06-11 | Hazard |  |  | 37830152000115 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | One pole inactive tap. Take off pole 152-20 | Hunter Church Rd. Lost Creek, Ky.
2019 | 2019-06-11 | Hazard |  |  | 37830198A00152 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | UG | UG conduit: damaged or separated |  |  | KPC |  | Pad mount xfmr partially off pad and secondary pedestal nocked over needs reburied. | Spencer Branch Rd, Kentucky 40914, USA
2019 | 2019-06-13 | Hazard |  |  | 37830151000251 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | Neutral sagged to tight, between phases. | Hooterville Rd. Lost Creek, Ky
2019 | 2019-06-17 | Hazard |  |  | 37830102000123 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning, ear edge of bank. Install: 1976 | Cockerell Fork Road, Lost Creek, Ky. | 2023-03-17
2019 | 2019-06-17 | Hazard | N/A |  | 37830150000053 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr bank | Coal fields industrial Drive, Chavies, Ky. | 2023-06-21
2019 | 2019-06-17 | Hazard | 75660007 | DKY0108259 | 37830150000109 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole split out | KY-15, Kentucky, USA | 2020-06-04
2019 | 2019-06-25 | Hazard |  |  | 37830149B00019 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC |  | Inactive xfmr, | KY-28, Kentucky, USA
2019 | 2019-06-25 | Hazard |  |  | 37830149C40153 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr, end of line up Davidson Br. | Davidson Branch Rd, Kentucky, USA
2019 | 2019-06-25 | Hazard | 80817724 | DKY0115267 | 37830172C00147 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Broken guy needs to be removed or replaced. | Deaton Park Dr, Kentucky 41701, USA | 2022-05-13
2019 | 2019-06-25 | Hazard |  |  | 37830172C00324 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Bad stacked arms, just above Spencer fk. | KY-28, Kentucky, USA
2019 | 2019-06-25 | Hazard |  |  | 37830172C00325 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Stacked arms bad, mouth of Spencer fk. | KY-28, Kentucky, USA
2019 | 2019-06-25 | Hazard | 73997889 | DKY0105872 | 37830172C00328 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole is stressed and slabbed at stress point, need changed out before it breaks. Just above noodle creek rd. | KY-28, Kentucky, USA | 2019-08-06
2019 | 2019-06-25 | Hazard |  |  | 37830173C00008 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Primary guy broken, mouth of Davidson Br. | Davidson Branch Rd, Kentucky, USA
2019 | 2019-06-25 | Hazard |  |  | 37830174A00092 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive 5 pole at the end of Pads Branch, cut dead on pole 174-A-92. Trees are grown up thru lines. | 286 Pads Branch Rd, Hazard, KY 41701, USA
2019 | 2019-06-26 | Hazard | N/A |  | 37830147000016 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive 4 pole tap. Been cut dead needs removed and anchor and guy installed on pole 147-16. | Ashana Rd, Kentucky 41339, USA | 2023-06-28
2019 | 2019-06-26 | Hazard |  |  | 37830171000057 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive 8 pole tap, trees grown up thru lines. Needs removed. | Strong Branch, Kentucky 41339, USA
2019 | 2019-06-27 | Hazard |  |  | 37830196C00015 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  |  | KPC |  | Neutral Down, cross R/R tracks from Carnagie Branch Loop. | Ky. Hwy. 451, Krypton, Ky.
2019 | 2019-06-27 | Hazard |  |  | 37830197000023 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive line, needs removed, primary down betwee poles 197-24 and 197-25. From 197-25 to 197-114 is already removed. This is up Spencer Fork rd. Off Chavies dunraven rd. | Chavies Dunraven Rd, Kentucky, USA
2019 | 2019-06-27 | Hazard |  |  | 37830197000108 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Cross arms bad | Tunnel Hill Cementary Rd, Chavies, Ky
2019 | 2019-06-27 | Hazard |  |  | 37830220000001 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarms bad | Krypton-Napfor Rd, Kentucky 41754, USA | 2023-03-17
2019 | 2019-06-27 | Hazard |  |  | 37830220000048 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Crossarm braces broken. | 685 Krypton-Napfor Rd, Krypton, KY 41754, USA | 2023-03-17
2019 | 2019-07-03 | Hazard | Trouble ticket# 4646011 |  | 37830230D00224 |  | 3308404-BECKHAM/PIPPA PASSES | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | 2/4 duplex rolled up on pole | Sams Branch Rd. Millie, Ky. | 2019-07-03
2019 | 2019-07-08 | Hazard |  |  | 37830230C40373 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr and C/O, Brkt. | Pine Dr. Mallie, Ky.
2019 | 2019-07-08 | Hazard | 75659383 | DKY0108244 | 37830244000039 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1949 pole looks bad at the top of pole. 35/7 | Lost Hollow Rd. Confluence, Ky. | 2020-12-09
2019 | 2019-07-09 | Hazard |  |  | 37830160000039 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Crossarms splintered and cracked, just above Road on Hemp Patch. | Hemp Patch Rd. Pippa Passes, Ky.
2019 | 2019-07-09 | Hazard | N/A |  | 37830244000095 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral down 6Acu, near Campbell Ln. | Trace Branch, Conflunce, Ky. | 2023-07-10
2019 | 2019-07-10 | Hazard | 82262172 | DKY0116920 | 37830113000163 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr and secondary pole 113-B-346. Need r/w crew to cut path to pole. | Highway 899, Pippa Passes, Ky. | 2022-10-21
2019 | 2019-07-12 | Hazard | 74341406 | DKY0106415 | 37830208000020 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole leaning needs replaced. Install: 1948 | Hollybush Rd. Pippa Passes, Ky. | 2022-03-17
2019 | 2019-07-12 | Hazard | 74698795 | 031514856 | 37830208000030 |  | 3308502-BONNYMAN / HAZARD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground broken. Xfmr pole | Hollybush Rd. Pippa Passes, Ky. | 2019-11-17
2019 | 2019-07-12 | Hazard | 75621609 | DKY0108181 | 37830255C00087 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten, ground level (35'6, 1949) | 1086 Mallet Fork Rd. Pine Top, Ky. | 2020-02-20
2019 | 2019-07-12 | Hazard |  |  | 37830255C00142 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Mallet Fork Rd. Pine Top, Ky.
2019 | 2019-07-12 | Hazard | N/A |  | 37830255C00164 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive line one pole, clamp removed. Tree limb on inactive line. | Daisy Ln. Pine Top, Ky. | 2023-09-15
2019 | 2019-07-12 | Hazard |  |  | 37830255D00291 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Pine Top Ln. Pine Top,Ky.
2019 | 2019-07-12 | Hazard |  |  | 37830255D00298 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Pine Top Ln. Pine Top, Ky
2019 | 2019-07-15 | Hazard | N/A |  | 37830256000033 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Primary guy broken strands needs replaced | 6920 Highway 542, Pine Top, Ky. | 2023-09-19
2019 | 2019-07-15 | Hazard |  |  | 37830256000102 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive one pole tap. End pole 256-175 | Meadow Branch, Kentucky 41843, USA
2019 | 2019-07-15 | Hazard | N/A |  | 37830257000026 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral laying on communication cables | 290 Camp Rock Rd, Pine Top, KY 41843, USA | 2023-09-19
2019 | 2019-07-15 | Hazard |  |  | 37830257000038 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Primary loop on double dead end pole laying close to pole. Needs reworked. | Highway 582, Pine Top, Ky.
2019 | 2019-07-15 | Hazard |  |  | 37830279000028 | TRUE | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive 3 pole tap. Needs removed | 1044 Steer Fork Rd, Mallie, KY 41836, USA
2019 | 2019-07-15 | Hazard |  |  | 37830281A30061 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive 4 pole tap, trees growed up around wires. End pole 281-A-65 | Upper Carr Rd. Pine Top, Ky.
2019 | 2019-07-16 | Hazard |  |  | 37830206B00012 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , crossarm/braces: broken/split |  |  | KPC |  | Double circuit pole rotten, arms bad. | Hwy. 899, Mallie, Ky. | 2019-11-11
2019 | 2019-07-16 | Hazard |  |  | 37830279000218 | TRUE | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr | Steer Fork Rd, Kentucky, USA
2019 | 2019-07-17 | Hazard | N/A |  | 37830206000011 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double circuit pole, arms deteriorated! | Hwy. 899, Mallie, Ky. | 2023-08-28
2019 | 2019-07-17 | Hazard | N/A |  | 37830230A00039 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Very Long span, conductors close to telephone pole. Tech. Greg Fugate came and looked at this and will write job up to have this corrected. 7/17/19 | Crimson Rd, Kentucky 41822, USA | 2023-08-28
2019 | 2019-07-17 | Hazard | 75611400 | DKY0108170 | 37830230A00100 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole in bad shape. Needs changed. | 22 Francis Hollow Rd, Brinkley, KY 41822, USA | 2020-02-19
2019 | 2019-07-17 | Hazard | N/A |  | 37830230C00011 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarms deteriorated |  | 2023-08-28
2019 | 2019-07-17 | Hazard |  |  | 37830469000169 | TRUE | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole has been broken or burnt off and use arm for pole extension. Cemetery rd. Gated, pole above house on left of rd. | 6965 Hwy.1103, Hallie, Ky.
2019 | 2019-07-18 | Hazard | N/A |  | 37830230B00158 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Arm split and pin layer over | Herlin Holcomb Rd. Brinkley, Ky. | 2023-08-28
2019 | 2019-07-19 | Hazard |  |  | 37830279000191 | TRUE | 3308402-BECKHAM / CARRSFORK | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign |  | Primary deadend guy broken. | Wolf Rd. Mallie, Ky.
2019 | 2019-07-19 | Hazard |  |  | 37830302D00085 | TRUE | 3308402-BECKHAM / CARRSFORK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Doublearms angle bad. | Burgeys Creek Rd, Kentucky, USA
2019 | 2019-07-19 | Hazard | N/A |  | 37830303000060 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Broken side guy. Needs replaced or removed | Burgeys Creek Rd, Kentucky, USA | 2023-09-08
2019 | 2019-07-22 | Hazard |  |  | 37830296D10084 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten at ground level. | Hemlock St, Hazard, KY 41701, USA
2019 | 2019-07-22 | Hazard | 67366817 | DKY0096966 | 37830320C00267 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Pole rotten. Buckarm pole, osmose has pole marked | Fourseam Buffalo Rd, Kentucky, USA | 2019-09-04
2019 | 2019-07-23 | Hazard | 76778103 | DKY0110112 | 37830297000060 |  | 3302704-HAZARD / KENMONT | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign |  | Pole leaning. Need r/w to cut out secondary, to take weight off lines to straighten pole. Install: 1983 | Gregory Branch Rd, Kentucky 41701, USA
2019 | 2019-07-23 | Hazard | 73989603 | DKY0105856 | 37830296C20507 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole at ground level. Osmose marked pole. | S Main St, Hazard, KY 41701, USA | 2020-01-20
2019 | 2019-07-23 | Hazard | 75603940 | DKY0108157 | 37830296D10167 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Secondary pole in bad shape. Parking lot of Lothair community church. | 316 Reed St. Hazard, Ky. | 2021-01-21
2019 | 2019-09-23 | Hazard | 76779480 | DKY0110092 | 37830272B41228 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightening arrestor broken, big bucket would reach. Need to change out both c/os, arrs, bkts. | L and N Dr, Hazard, KY 41701, USA | 2021-01-04
2019 | 2019-09-23 | Hazard | 76114165 | DKY0108957 | 37830296A11200 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Manual pole, lightening arrestor bad | Mountain Shadows Dr, Hazard, KY 41701, USA | 2020-06-17
2019 | 2019-09-23 | Hazard | 85680264 |  | 37830343D00024 | TRUE | 3302701-HAZARD / BLACKGOLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten at ground level | Jacks Branch Rd, Kentucky 41701, USA
2019 | 2019-09-24 | Hazard |  |  | 37830319000162 |  | 3302701-HAZARD / BLACKGOLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Guy took loose, needs put back up . | Tackett Branch Rd, Kentucky 40351, USA
2019 | 2019-09-24 | Hazard | 74927602 | DKY0107172 | 37830342C20220 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Arm braces broke,manual pole. May needR/W to cut path. Near gas compressor station on strip on left fork big creek. | Polly Hollow, Kentucky 41701, USA | 2019-12-30
2019 | 2019-09-24 | Hazard | 76779480 | DKY0110092 | 37830343B30348 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Lines low needs resagged, between poles 348 and 357 | Avawam, KY 41701, USA | 2021-01-04
2019 | 2019-09-27 | Hazard |  |  | 37830344000053 | TRUE | 3302701-HAZARD / BLACKGOLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole split at top, repairs needed. Manual | Black Gold Haul Rd. Hazard, Ky.
2019 | 2019-09-27 | Hazard | 76779480 | DKY0110092 | 37830344000142 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Lightening arrestor bad on road side phase on stepdown pole. | Black Gold Haul Rd. Hazard, KY, USA | 2021-01-04
2019 | 2019-09-27 | Hazard | 74924004 | DKY0107166 | 37830344A20180 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole split at the top, needs repaired. | Black Gold Haul Rd. Hazard, Ky. | 2019-11-21
2019 | 2019-10-02 | Hazard |  |  | 37830108000067 | TRUE | 3420001-SOFT SHELL / VEST | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Ground wire missing. | Vest Talcum Rd, Kentucky, USA
2019 | 2019-10-02 | Hazard | N/A |  | 37830108000116 | TRUE | 3420001-SOFT SHELL / VEST | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Recloser pole leaning needs straightened. Install: 1999 | Vest Talcum Rd, Kentucky, USA | 2023-09-22
2019 | 2019-10-03 | Hazard |  |  | 37830156000218 | TRUE | 3420001-SOFT SHELL / VEST | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign |  | Inactive 3 pole tap, needs removed. | Sylvester Branch Rd, Kentucky, USA
2019 | 2019-10-04 | Hazard |  |  | 37830109C30114 | TRUE | 3420001-SOFT SHELL / VEST | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Conductors might be low. Pratt family farm dr. Last span. R/W bad here. | Yellow Mountain Rd, Kentucky 41831, USA
2019 | 2019-10-04 | Hazard |  |  | 37830133000034 |  | 3420001-SOFT SHELL / VEST | Line Work | OH | guys/anchors: broken or missing , conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Low conductor, no guys on pole, inactive line on pole | Patrick Ln. Vest, Ky.
2019 | 2019-10-04 | Hazard | 76127552 | DKY0108965 | 37830133000077 |  | 3420001-SOFT SHELL / VEST | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Primary guy broken. | Vest Talcum Rd, Kentucky, USA | 2020-04-01
2019 | 2019-10-08 | Hazard |  |  | 37830339000113 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Telephone pole set close to our primary pole. | Bull Creek Rd. Thousandsticks, Ky.
2019 | 2019-10-08 | Hazard | 76130519 | DKY0108973 | 37830362000178 |  | 3303903-LESLIE / HALSFORK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning bad. Install: 1990 | Bell Branch Rd. Hyden, Ky | 2020-04-22
2019 | 2019-10-08 | Hazard | 75604825 | DKY0108199 | 37830362000179 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole bad, top split. Will have to block rd. To change. | Bell Branch Rd. Hyden, Ky. | 2020-02-27
2019 | 2019-10-08 | Hazard | 75587327 | DKY0108140 | 37830387C00351 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Arms split. | Berry Branch Rd. Hyden, Ky.
2019 | 2019-10-08 | Hazard | 81776146 | G0000110 | 37830387C10753 |  | 3303903-LESLIE / HALSFORK | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | House knob pulled out of pole. Cell tower in head of Maggard Ln. | Maggard Ln. Hyden, Ky. | 2022-03-09
2019 | 2019-10-08 | Hazard | 77496629 | DKY0111434 | 37830388B00082 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Two pole structure, has splits at top and woodpecker holes. | Ash Ln. Hyden, Ky. | 2022-08-25
2019 | 2019-10-08 | Hazard | 77392423 | DKY0111368 | 37830388B30083 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Two pole structure, leaning bad. Install: unknown | Highway 80, Hyden, Ky. | 2022-07-25
2019 | 2019-10-09 | Hazard | N/A |  | 37830338000031 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Lash secondary needs better clearance off ground, needs resagged. May need r/w to cut limbs off sec. to resag. | Osborne Fork Rd. Thousandsticks, Ky | 2023-11-03
2019 | 2019-10-09 | Hazard | N/A |  | 37830338000140 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Line needs resaged, primary close to neutral. | Bowling Branch Rd, Kentucky 41766, USA | 2023-11-03
2019 | 2019-10-09 | Hazard |  |  | 37830362000056 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Needs 3 guy insulators installed in the three primary guys. | Davidson Fork Rd, Kentucky, USA
2019 | 2019-10-09 | Hazard | 75604831 | DKY0108203 | 37830362000201 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole has some damage at top of pole, ptp bolts pulled thru and leaning also line cutout needs added to this pole. | Osborne Fork Rd, Kentucky 41766, USA | 2020-02-25
2019 | 2019-10-09 | Hazard | 75604839 | DKY0108220 | 37830410B00051 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at top and bottom. (40'5, 1977) | 344 Laurel Fork Ln, Hyden, KY 41749, USA | 2020-03-05
2019 | 2019-10-10 | Hazard | 75652373 | DKY0108225 | 37830384000042 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole starting to rot. Near cell tower chandler creek. | Ottis Sizemore Rd., Bear Branch, Ky. | 2021-01-04
2019 | 2019-10-10 | Hazard | 81776169 |  | 37830385000116 |  | 3303903-LESLIE / HALSFORK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Inactive service | Cane Fork Rd, Kentucky 41749, USA | 2022-03-09
2019 | 2019-10-10 | Hazard | 75652377 | DKY0108236 | 37830409000108 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole split out and span guy pull downward towards primary deadend. | Read Leaf Ln. Hyden, Ky. | 2020-03-11
2019 | 2019-10-10 | Hazard | 85793765 | DKY0123058 | 37840360000004 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | YES | Arms splintered and bent. | Ulysses Branch Rd. Bear Branch, Ky.
2019 | 2019-10-10 | Hazard | 75621039 | DKY0108190 | 37840360000013 |  | 3303903-LESLIE / HALSFORK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Bad location and bad shape! Install: 1956 | Ulysses Branch Rd. Bear Branch, Ky. | 2020-07-15
2019 | 2019-10-10 | Hazard | 75604851 | DKY0108221 | 37840384000064 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | guys/anchors: broken or missing | pole: leaning, burned more than 50% remaining |  | KPC | YES | Needs a couple of guys and anchors backing up angle. Install: 1954 | Ulysses Creek Rd, Kentucky 41714, USA | 2020-09-02
2019 | 2019-10-14 | Hazard |  |  | 37840336000037 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | 1/0 secondary lash, low laying in trees, needs removed. Not in use, doesn’t show on map. | Woods Branch Ln, Kentucky 41762, USA
2019 | 2019-10-14 | Hazard |  |  | 37840336000058 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , joint use attachments: clearance issues | guys/anchors: loose, damaged, need insulator/marker |  | KPC | YES | Check clearance over rd., primary guy wire, oat treegrowed around it. | Size rock, Bear Branch, Ky.
2019 | 2019-10-14 | Hazard | N/A |  | 37840336000123 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Communication cable in between primary and neutral. Needs resagged. | Rush Creek Rd, Kentucky, USA | 2023-10-26
2019 | 2019-12-02 | Hazard | 75624812 | DKY0108193 | 37830278A00029 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole split at top, needs changed. Manual, yard dog. | KY-160 & Tolliver Mountain Rd, Kentucky 41773, USA | 2020-09-24
2019 | 2019-12-03 | Hazard | N/A |  | 37830326A20370 |  | 3308402-BECKHAM / CARRSFORK | Service Work | OH | service: unused or abandoned, blanked meter base | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Unused service, de-energized and hanging down pole. | Hwy. 15, Pioneer Village, Redfox, Ky. | 2023-08-29
2019 | 2019-12-09 | Hazard | 85690253 |  | 37830381C00289 | TRUE | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Inactive 3 phase one pole tap needs removed. Doesn’t show on map. | Smokey Row, Jenkins,Ky.
2019 | 2019-12-09 | Hazard | 76131475 | DKY0108982 | 37830381C00629 |  | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr, C/O, arrestorbrkt. Needs removed. Doesn’t show on field view. | Hwy. 23, Jenkins, Ky. | 2020-10-20
2019 | 2019-12-09 | Hazard | 85690371 | DKY0122509 | 37830381C00711 |  | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive xfmr. c/o, arrestor, Brit. Needs removed. | Hwy. 23, Jenkins, Ky. | 2023-12-28
2019 | 2019-12-09 | Hazard | 80529841 | DKY0114746 | 37830381C00788 | TRUE | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole leaning, has a 500kv stepdown on pole, needs straightened. Install: 1994 | C and O Railroad Road, Jenkins, Ky.
2019 | 2019-12-18 | Hazard |  |  | 37830272B40324 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign | NO | Spans on either side of pole needs resaged. Very loose | Pine St, Hazard, KY 41701, USA
2019 | 2019-12-18 | Hazard | N/A |  | 37830272D10460 |  | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole looks broke at telephone attachment. Bent bad | Skyline Dr, Hazard, KY 41701, USA | 2023-12-26
2019 | 2019-12-18 | Hazard | N/A |  | 37830272D11021 |  | 3302703-HAZARD / HAZARD | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Concrete pole leaning, needs straightened. Install: 1984 | Skyline Dr, Hazard, KY 41701, USA | 2023-12-26
2019 | 2019-12-18 | Hazard | 75717312 | DKY0108361 | 37830272D20986 |  | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten at top. Hole just under tap going left up hill. Needs changed. | Skyline Dr, Hazard, KY 41701, USA | 2023-04-06
2019 | 2019-12-18 | Hazard | 75603931 | DKY0108159 | 37830296C10210 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten, split at top. Needs replaced. R/w may be needed to cut limbs off span guy to transfer. | Kentucky Blvd, Hazard, KY 41701, USA | 2021-12-01
2019 | 2019-12-18 | Hazard | 75603931 | DKY0108159 | 37830296C30206 |  | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at top, needs replaced. R/w my need to cut around pole. | Parkway St, Hazard, KY 41701, USA | 2021-12-01
2019 | 2019-12-18 | Hazard | 80082951 | DKY0114279 | 37830296C30952 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Secondary light and span guy pole | Kentucky Blvd, Hazard, KY 41701, USA
2019 | 2019-12-19 | Hazard |  |  | 37830155000027 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove one span in head of hollow, inactive | Big Branch Ball Rd, Kentucky 41740, USA
2019 | 2019-12-19 | Hazard | 75597169 | DKY0108155 | 37830155000049 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole needs replaced | Sand lick br, Bearville Ky | 2020-02-03
2019 | 2019-12-19 | Hazard |  |  | 37830155000051 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | CSP xfmr old and needs replaced. | Sandlick Branch, Bearville, Ky.
2019 | 2019-12-19 | Hazard |  |  | 37830230C00276 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Primary guy broken. (Wrong pole had previously been reported. Another defect had been reported) | Pigman Br Rd, Kentucky 41822, USA | 2023-11-27

## Ckt Defects Reported 2020 HAZ
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2020 | 2020-01-02 | Hazard |  |  | 37830206B00114 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr and c/o, arr, brkt. | Gus Hays Path,Hindman Ky.
2020 | 2020-01-02 | Hazard |  |  | 37830229C10184 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr and c/o, brkt. | Perkins Madden Rd, Kentucky, USA
2020 | 2020-01-03 | Hazard | 75516886 | DKY0107978 | 37830204000041 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , crossarm/braces: broken/split |  |  | KPC | YES | Arms double stacked needs changed! Pole needs changed. Can probable use yard dog on this. | Dogwood Dr, Kentucky 41822, USA | 2020-02-01
2020 | 2020-01-06 | Hazard | 76778994 | DKY0110113-CANCEL | 37830178B00026 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Arms split and rotten, needs changed | Wetmore Ln, Kentucky 41701, USA | 2022-03-10
2020 | 2020-01-07 | Hazard | 75531738 | 108075 | 37830204000049 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Single arm split on end. Needs changed. | Hwy. 550 W, Carrie, Ky. | 2020-02-01
2020 | 2020-01-07 | Hazard |  |  | 37830205A00035 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NEEDS ADDITIONAL CHECK | Arms need changed | Hwy. 550 Main Street, Hindman, Ky.
2020 | 2020-01-07 | Hazard |  |  | 37830205A00037 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Top set of arms bowed needs changed. | Hwy. 550 Main St. Hindman, Ky.
2020 | 2020-01-07 | Hazard |  |  | 37830205A00359 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Stacked arms needs changed. | Hwy. 550 Main Street, Hindman, Ky.
2020 | 2020-01-07 | Hazard |  |  | 37830228000048 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Need a guy and anchor installed. Manual, last house in hollow. | Lower Mill Creek, Carrie, Ky.
2020 | 2020-01-07 | Hazard |  |  | 37830228000150 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive 2 pole tap needs removed. May need r/w for removal. | Lower Mill Creek, Carrie, Ky.
2020 | 2020-01-08 | Hazard | N/A |  | 37830181D00207 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad arms on buck pole. Both sets. | Hwy. 160, Hindman, Ky | 2023-11-29
2020 | 2020-01-08 | Hazard | 75659803 | DKY0108256 | 37830202000028 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole split out at top needs changed | Cockerels Trace Rd. Fisty, Ky. | 2020-03-12
2020 | 2020-01-08 | Hazard | 75659511 | DKY0108247 | 37830202000117 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at ground level | Longhorn Br. Fisty, Ky. | 2020-02-20
2020 | 2020-01-08 | Hazard | 75659996 | DKY0108267 | 37830227B00032 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole been cutoff at top, needs changed. | Dix Fork Rd. Fisty, Ky. | 2020-03-10
2020 | 2020-01-08 | Hazard | 75620574 | DKY0108174 | 37830227D00075 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole cut off, needs changed. | Clear Creek Rd. Fisty, Ky. | 2020-03-05
2020 | 2020-01-08 | Hazard | 76778092 | DKY0110114 | 37830251000164 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Low conductors over road. | Shekinah Ln. Fisty, Ky. | 2020-10-23
2020 | 2020-01-13 | Hazard |  |  | 37830448C30018 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Double stacked and double arms need to be changed. The lower set of arms only one phase is hot, can be made into a single phase tap. | Hazard Rd. Whitesburg, Ky
2020 | 2020-01-13 | Hazard |  |  | 37830448C30355 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Stacked arms, needs changed. | Hazard Rd. WHITESBURG, Ky.
2020 | 2020-01-13 | Hazard |  |  | 37830448C30356 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Double stacked arms, need changed. | Hazard Rd, Whitesburg, KY 41858, USA
2020 | 2020-01-13 | Hazard |  |  | 37830448C30357 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Double stacked arms, needs changed. | Hazard Rd. WHITESBURG, Ky.
2020 | 2020-01-13 | Hazard | N/A |  | 37830448C30380 |  | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Stacked arms needs changed. (Wrong pole number previously reported, 380 should have been 360) | Hwy 931, WHITESBURG, Ky. | 2024-01-04
2020 | 2020-01-13 | Hazard |  |  | 37830449A10019 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Stacked arms needs changed. | Hazard Rd. WHITESBURG, Ky.
2020 | 2020-01-13 | Hazard |  |  | 37830449A10020 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Stacked arms needs changed | Hazard Rd, Whitesburg, KY 41858, USA
2020 | 2020-01-14 | Hazard |  |  | 37830449A10023 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Buck pole, stacked arms need changed. | Hazard Rd. WHITESBURG, Ky.
2020 | 2020-01-14 | Hazard | 76230460 | DKY0109164 | 37830449A10026 |  | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , crossarm/braces: broken/split |  |  | KPC | YES | Buck pole and arms needs changed. | Hazard Rd. WHITESBURG, Ky.
2020 | 2020-01-14 | Hazard | 76194670 | DKY0109100 | 37830449A20232 |  | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole, needs changed. | Main St, Whitesburg, KY 41858, USA | 2020-12-30
2020 | 2020-01-14 | Hazard |  |  | 37830449A20408 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Top set of arms needs changed | Broadway St. WHITESBURG, Ky.
2020 | 2020-01-14 | Hazard |  |  | 37830449A20496 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Stacked arms need changed. | Hwy 15, WHITESBURG, Ky.
2020 | 2020-01-14 | Hazard |  |  | 37830449A20678 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Arms need changed | Broadway St. WHITESBURG, Ky.
2020 | 2020-01-15 | Hazard |  |  | 37830242000129 |  | 3309103-WHITESBUR / COWAN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Primary guy broken. | Brian Baker Dr. Whitesburg, Ky.
2020 | 2020-01-15 | Hazard |  |  | 37830448C10087 |  | 3309103-WHITESBUR / COWAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Arm bad. | 3125 S State Hwy 931, Whitesburg, KY 41858, USA
2020 | 2020-01-15 | Hazard | 75829021 | DKY0108535 | 37830472000113 |  | 3309103-WHITESBUR / COWAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole been cut off, needs replaced. | Donnie Banks Rd. WHITESBURG, Ky. | 2020-10-22
2020 | 2020-01-15 | Hazard |  |  | 37830496000025 |  | 3309103-WHITESBUR / COWAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral and hot secondary wire low and close over driveway. Needs resagged. | Hwy. 931S, WHITESBURG, Ky.
2020 | 2020-01-15 | Hazard | 76190500 | DKY0109090 | 37830496000027 |  | 3309103-WHITESBUR / COWAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , crossarm/braces: broken/split |  |  | KPC | YES | Pole needs changed | Chelsea Hl. Cowan, Ky. | 2021-07-22
2020 | 2020-01-15 | Hazard |  |  | 37830496000055 |  | 3309103-WHITESBUR / COWAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr and c/o, arr. brkt. Needs removed | Sturgill Br. Cowan, Ky.
2020 | 2020-01-15 | Hazard | 76048648 | DKY0108854 | 37830496000193 |  | 3309103-WHITESBUR / COWAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole split at the top. | Chelsea HL. Cowan, Ky. | 2020-11-04
2020 | 2020-01-15 | Hazard | 76050774 | DKY0109076 | 37830496000256 |  | 3309103-WHITESBUR / COWAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole cut off. Needs changed | Hwy. 931S, Cowan, Ky. | 2020-11-04
2020 | 2020-01-15 | Hazard |  |  | 37830520000020 |  | 3309103-WHITESBUR / COWAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Arm is rotten, needs changed. Pole not in the best shape. Scaling off. | Hwy. 931S, Cowan, Ky.
2020 | 2020-01-17 | Hazard |  |  | 37830400A00013 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Cross-arms bad | Smoot Crk. Isom, Ky
2020 | 2020-01-17 | Hazard | 76015463 | DKY0108797 | 37830401B00074 | TRUE | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , crossarm/braces: broken/split |  |  | Foreign | YES | Bad pole needs replaced | Hwy. 931N, WHITESBURG, Ky.
2020 | 2020-01-17 | Hazard |  |  | 37830401B00126 | TRUE | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole
2020 | 2020-01-17 | Hazard |  |  | 37830425D00149 |  | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Crafts Colly Rd. WHITESBURG, Ky.
2020 | 2020-01-17 | Hazard |  |  | 37830449C30508 |  | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole, washed out. | Craft Colly Rd. WHITESBURG, Ky.
2020 | 2020-01-21 | Hazard |  |  | 37830401C00095 |  | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Craft Colly Rd. WHITESBURG, Ky.
2020 | 2020-01-22 | Hazard | 77766494 | DKY0111209 | 37830381D40069 |  | 3312902-JENKINS / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at ground level, hollow in the center | Lakeside Dr. Jenkins, Ky.
2020 | 2020-01-22 | Hazard | 85690451 | DKY0122238 | 37830381D40496 |  | 3312902-JENKINS / JENKINS | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm needs changed. | Lakeside Dr. Jenkins, Ky.
2020 | 2020-01-22 | Hazard | 85690780 | DKY0123052 | 37830382A10167 | TRUE | 3312902-JENKINS / JENKINS | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Arm bad | Cane Br. Jenkins, Ky.
2020 | 2020-01-22 | Hazard | 76215104 | DKY0109175 | 37830382A30152 |  | 3312902-JENKINS / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole and crossarm bad. | Lemon Dr. Jenkins, Ky. | 2020-12-09
2020 | 2020-01-22 | Hazard | 76215110 | DKY0109178 | 37830382A30153 |  | 3312902-JENKINS / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole and crossarm bad. | Lemon Dr. Jenkins, Ky. | 2020-12-09
2020 | 2020-01-22 | Hazard | 85689803 | DKY0123125 | 37830405A00456 |  | 3312902-JENKINS / JENKINS | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Middle phase ptp insulator is broken. | Gateway Industrial Park, Jenkins, Ky.
2020 | 2020-01-22 | Hazard | 75692254 | DKY0108315 | 37830405C00296 |  | 3312902-JENKINS / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at ground level. | Little Oak St. Jenkins, Ky. | 2020-07-01
2020 | 2020-01-28 | Hazard |  |  | 37830380D00279 |  | 3312901-JENKINS / KONA | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive xfmr and pole needs to be removed. | Fish Pond Rd. Mayking, Ky. | 2021-06-07
2020 | 2020-01-28 | Hazard |  |  | 37830380D00281 |  | 3312901-JENKINS / KONA | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Pole has underground on it which I suspect is de-energized. Primary and neutral wires hanging down pole almost to ground.need to remove wires hanging down and clean pole up. | Fish Pond Rd. Mayking, Ky. | 2021-06-07
2020 | 2020-01-28 | Hazard | 79756217 | DKY0114080 | 37830404B00068 |  | 3312901-JENKINS / KONA | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service contacting roof, may need to set secondary pole to get clearance off roof. | Hwy. 3406, Mayking, Ky. | 2021-09-13
2020 | 2020-01-28 | Hazard |  |  | 37830404B00069 | TRUE | 3312901-JENKINS / KONA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole bad needs changed, dry time may get truck to but can use yard or track. | Hwy. 119, Mayking, Ky.
2020 | 2020-01-30 | Hazard |  |  | 37830400B00020 | TRUE | 3308603-COLLIER / SMOOTCR | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property , service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Inactive xfmr, secondary pole and secondary and service needs removed, secondary crosses road and is under pressure from tree limb on secondary. | Smoot Crk. Rd. Isom, Ky.
2020 | 2020-01-30 | Hazard |  |  | 37830446000078 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Top arms broken on buck pole! | Hwy. 160, Premium, Ky.
2020 | 2020-01-30 | Hazard |  |  | 37830446000125 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Cross arms bowed on buck pole | Hwy. 160, Premium, Ky.
2020 | 2020-01-30 | Hazard | 75849794 | DKY0108567 | 37830518000025 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole needs changed - 37830518000025 | Boggs Hollow, Premium, Ky
2020 | 2020-01-30 | Hazard | 70873571 | DKY0101529 | 37830518000038 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole cut off. | Ingram Crk. Premium, Ky. | 2019-01-21
2020 | 2020-01-31 | Hazard |  |  | 37830445000105 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Primary guy needs resagged or removed, low over road. | Hwy. 588, Roxanne, Ky.
2020 | 2020-01-31 | Hazard |  |  | 37830446000051 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarms broken. Needs replaced. Behind George Whitaker’s house on hill. | Hwy. 2036, Roxanne, Ky.
2020 | 2020-01-31 | Hazard |  |  | 37830446000261 |  | 3308603-COLLIER / SMOOTCR | Service Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Anchor is there but guy needs put back. | Hwy. 160, Roxanne, Ky.
2020 | 2020-01-31 | Hazard |  |  | 37830447000004 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm split on end | Jasper Dr. Premium, Ky
2020 | 2020-01-31 | Hazard |  |  | 37830447009007 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Pin about out of arm and cracked. | Jasper Dr. Premium, Ky.
2020 | 2020-01-31 | Hazard |  |  | 37830496000073 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral and primary low over rd. Best to go in from Henry Isom Hollow | Kingdom Come Creek, Whitesburg, Ky.
2020 | 2020-02-03 | Hazard |  |  | 3&830400C00075 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten ground level. | Charlie Cornett Rd. Whitesburg, Ky.
2020 | 2020-02-03 | Hazard |  |  | 37830400C00066 |  | 3308603-COLLIER / SMOOTCR | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Inactive service. House falling down | Little Dry Fork, Whitesburg, Ky
2020 | 2020-02-03 | Hazard | 75845734 | DKY0108562 | 37830400D00059 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten ground level | Little Dry Fork, Whitesburg, Ky | 2021-05-21
2020 | 2020-02-03 | Hazard | 75835372 | DKY0108546 | 37830424000084 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Big cracks in pole, needs changed | Little Dry Fork, Whitesburg, Ky. | 2021-04-08
2020 | 2020-02-04 | Hazard |  |  | 37830435000013 |  | 3311103-STINNETT / WENDOVER | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Stacked crossarm | Hwy. 421, Hyden, Ky.
2020 | 2020-02-04 | Hazard |  |  | 37830435000111 |  | 3311103-STINNETT / WENDOVER | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Stacked crossarm | Hwy. 421, Hyden, Ky.
2020 | 2020-02-04 | Hazard | 75926435 | DKY0108682 | 37830436000042 |  | 3311103-STINNETT / WENDOVER | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole leaning bad, needs changed. | 2029 Hurricane Creek, Hyden, Ky. | 2020-12-09
2020 | 2020-02-04 | Hazard |  |  | 37830459A00113 |  | 3311103-STINNETT / WENDOVER | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Tap guy broken, needs replaced. Burley Roberts Cemetery Road | Flat Hollow Rd. Stinnett, Ky.
2020 | 2020-02-04 | Hazard | 71226064 | DKY0102017 | 37830459C00130 | TRUE | 3311103-STINNETT / WENDOVER | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Braces broke, remaining braces under a lot of stress. | Hwy. 421, STINNETT, Ky. | 2020-07-16
2020 | 2020-02-05 | Hazard | 76181448 | DKY0109074 | 37830436000006 |  | 3311103-STINNETT / WENDOVER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole Bad. | Camp Creek Rd. Wendover, Ky. | 2020-12-15
2020 | 2020-02-05 | Hazard | 76515762 | DKY0109549 | 37830436000031 |  | 3311103-STINNETT / WENDOVER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Not much dirt holding, could kick out. | Camp Creek Rd. Wendover, Ky | 2020-12-15
2020 | 2020-02-05 | Hazard | 76262774 | DKY0109231 | 37830461000006 |  | 3311103-STINNETT / WENDOVER | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole leaning bad. | Camp Creek Rd. Wendover, Ky. | 2020-12-15
2020 | 2020-02-05 | Hazard | 74010971 | DKY0105889 | 37830485000045 |  | 3311103-STINNETT / WENDOVER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole split out, needs changed. | Lower Bad Creek Rd. Stinnett, Ky. | 2020-03-09
2020 | 2020-02-07 | Hazard | 80136023 | DKY0114474 | 37830375C00080 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Stacked arms | Hwy. 1148, Isom, Ky
2020 | 2020-02-07 | Hazard | 80136023 | DKY0114474 | 37830375C00081 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Stacked arms | Hwy. 1148, Isom, Ky
2020 | 2020-02-07 | Hazard | 75884877 | DKY0108685 | 37830375C00085 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Stubbed pole | Hwy. 1148, Isom, Ky.
2020 | 2020-02-07 | Hazard |  |  | 37830375C00087 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Stacked arms | Hwy. 1148, Isom, Ky
2020 | 2020-02-07 | Hazard |  |  | 37830375C00088 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Stacked arms | Hwy. 1148, Isom, Ky.
2020 | 2020-02-07 | Hazard | 75888075 | DKY0108607 | 37830375C00101 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole burnt near top of pole | Lad Dr, Kentucky, USA | 2021-04-09
2020 | 2020-02-07 | Hazard | 80136023 | DKY0114474 | 37830375C00291 | TRUE | 3308602-COLLIER / LOWERROCK | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Stacked arms, driveway near but rough, might can reach with truck? | Hwy. 1148, Isom,Ky.
2020 | 2020-02-07 | Hazard |  |  | 37830376A00105 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Stacked arms | Hwy. 1148, Isom, Ky.
2020 | 2020-02-07 | Hazard | 85794451 | DKY0122421 | 37830376A00321 | TRUE | 3308602-COLLIER / LOWERROCK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Stacked arms | Hwy. 1148, Isom, Ky. | 2023-10-26
2020 | 2020-02-07 | Hazard | 76471327 | DKY0110762 | 37830376C00023 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | YES | Pole been filled around needs changed | Allen Hollow, Hwy. 1148, Isom, Ky. | 2021-04-13
2020 | 2020-02-07 | Hazard | 75883465 | DKY0108599 | 37830376D00188 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at ground level needs changed. | 532 Cinnamon Dr. Isom, Ky. | 2021-04-07
2020 | 2020-02-07 | Hazard |  |  | 37830400A00088 | TRUE | 3308602-COLLIER / LOWERROCK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm braces broken | Cinnamon Dr. Isom, Ky.
2020 | 2020-02-10 | Hazard | 75915454 | DKY0108646 | 37830328B00035 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole been cut off. | Mack Dr. Isom, Ky
2020 | 2020-02-10 | Hazard | 75893912 | DKY0108627 | 37830352B00344 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole been cut off. | 1165 Race Track Hollow, Isom, Ky. | 2020-10-20
2020 | 2020-02-10 | Hazard |  |  | 37830352D00129 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Inactive 2 pole tap. May need r/w cut to remove line. | Midland Dr. Isom, Ky
2020 | 2020-02-11 | Hazard | 75916782 | DKY0108652 | 37830352A00093 | TRUE | 3308601-COLLIER / UPPERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole rotten, big hole below braces and braces broke. | Rockhouse Creek, Isom, Ky. | 2020-10-20
2020 | 2020-02-11 | Hazard |  |  | 37830352A00105 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Primary guy broken. May need r/w cut around pole. | Rockhouse Creek, Isom, Ky.
2020 | 2020-02-11 | Hazard |  |  | 37830353A00105 | TRUE | 3308601-COLLIER / UPPERROCK | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Top set of crossarms bad. 1979 ATT pole | Hwy. 931N, Thornton, Ky
2020 | 2020-02-11 | Hazard |  |  | 37830375C00086 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Stacked crossarms. | Hwy. 1148, Kiona Dr. Isom, Ky.
2020 | 2020-02-12 | Hazard | 80341716 | DKY0114880 | 37830328B00336 (0306 IN FIELD) |  | 3308601-COLLIER / UPPERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , guys/anchors: broken or missing |  |  | KPC | YES | Pole is losing ground to the river, need to check about rerouting? One anchor is washed out completely. | Hwy 7, Isom,Ky.
2020 | 2020-02-12 | Hazard | 75835770 | DKY0108548 | 37830329000275 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole cut off | Mandrill Dr. Thornton, Ky | 2020-12-03
2020 | 2020-02-12 | Hazard |  |  | 37830353C00229 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Need to remove hot line clamp and de-energize last span. Xfmr on last pole is de-energized. Been logging around it. | Nashville Dr. Thornton, Ky.
2020 | 2020-02-13 | Hazard |  |  | 37830367000023 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning needs to be straighten | Pole cat hollow wootons cr
2020 | 2020-02-13 | Hazard | 77625909 | DKY0111032 | 37830367000026 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Pole at hollow Wootons cr | 2020-10-12
2020 | 2020-02-14 | Hazard |  |  | 37830375A00066 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Top crossarms bad, need changed. | Hwy. 15, Isom, Ky.
2020 | 2020-02-14 | Hazard |  |  | 37830375D00255 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive 3 phase 4 pole tap needs removed. | Hwy. 15, Isom, Ky.
2020 | 2020-02-17 | Hazard | 76254834 | DKY0109224 | 37830331C00246 |  | 3401301-FLEMING / NEON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole cut off. | Goose Crk. Rd. Neon, Ky | 2020-11-12
2020 | 2020-02-17 | Hazard | 86206082 | DKY0122425 | 37830355D30089 |  | 3401301-FLEMING / NEON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bottom arms split and cracked. | Second St. Neon, Ky. | 2023-10-23
2020 | 2020-02-17 | Hazard |  |  | 37830355D30333 |  | 3401301-FLEMING / NEON | Line Work | OH | crossarm/braces: broken/split , conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Primary pretty close to road above pole. | Second St. Neon, Ky. | 2021-06-07
2020 | 2020-02-17 | Hazard | 80542771 | DKY0114776 | 37830355D30334 |  | 3401301-FLEMING / NEON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Top arms bad. | Second St. Neon, Ky. | 2022-12-21
2020 | 2020-02-17 | Hazard | 78199396 | DKY0111754 | 37830356B00187 |  | 3401301-FLEMING / NEON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole stubbed. | Fleming Rd. Neon, Ky. | 2021-07-09
2020 | 2020-02-17 | Hazard | 77837211 | DKY0111461 | 37830356B00190 |  | 3401301-FLEMING / NEON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Bad pole, truck access? Yard dog yes | Fleming Rd. Neon, Ky.
2020 | 2020-02-18 | Hazard |  |  | 37830282000069 |  | 3311401-REEDY / DEANE | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service hanging down, not in use | Shelby Frk. Dean, Ky.
2020 | 2020-02-18 | Hazard |  |  | 37830283000148 |  | 3311401-REEDY / DEANE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Inactive xfmr and secondary and secondary pole. | Oasis Frk. Dean,Ky. | 2021-07-06
2020 | 2020-02-18 | Hazard | 76249420 | DKY0109183 | 37830306000036 |  | 3311401-REEDY / DEANE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole cut off | Mill Crk. Dean, Ky. | 2020-12-21
2020 | 2020-02-18 | Hazard |  |  | 37830306000117 |  | 3311401-REEDY / DEANE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Inactive xfmr | Hwy.317, Dean, Ky.
2020 | 2020-02-18 | Hazard | 77760956 | DKY0111202 | 37830331C00112 |  | 3401301-FLEMING / NEON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at bottom. | Quilled Frk. Jackhorn, Ky. | 2020-12-01
2020 | 2020-02-18 | Hazard | 77763227 | DKY0111206 | 37830331C00116 |  | 3401301-FLEMING / NEON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole cut off. | Quilled, Frk. Jackhorn, Ky. | 2020-12-01
2020 | 2020-02-18 | Hazard | 78185353 | DKY0111737 | 37830332A00027 |  | 3401301-FLEMING / NEON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole. | Tony’s Frk. Jackhorn, Ky. | 2020-12-02
2020 | 2020-02-18 | Hazard | 78193483 | DKY0111746 | 37830332A00039 |  | 3401301-FLEMING / NEON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Grassy Fork, Jackhorn, Ky. | 2020-12-21
2020 | 2020-02-18 | Hazard | 85679816 | DKY0122415 | 37830332B00015 |  | 3401301-FLEMING / NEON | Line Work | OH | crossarm/braces: broken/split |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Crossarm brace broke. Also 2 pole inactive needs removed | Hwy. 317, Jackhorn, Ky.
2020 | 2020-02-18 | Hazard | 85679906 |  | 37830332B00280 |  | 3401301-FLEMING / NEON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm split. | Hwy. 317, Jackhorn, Ky.
2020 | 2020-02-18 | Hazard |  |  | 38831060D00007 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive two pole tap needs removed, trees growed up into conductors. | Roark Br. Quicksand, Ky.
2020 | 2020-02-19 | Hazard |  |  | 38830992000045 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten ground level | Wolf Creek Rd. Rousseau, Ky.
2020 | 2020-02-19 | Hazard |  |  | 38831016000059 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten ground level, needs done ASAP | Wolf Creek Rd. Rousseau, Ky
2020 | 2020-02-19 | Hazard |  |  | 38831038000043 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten ground level | Meatscaffold Rd. No tot, Ky.
2020 | 2020-02-19 | Hazard |  |  | 38831060D00010 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Inactive xfmr and secondary and secondary pole 1060-196 | Roark Br. Quicksand, Ky.
2020 | 2020-02-19 | Hazard |  |  | 38831060D00177 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Inactive xfmr | Roark Br. Quicksand,Ky.
2020 | 2020-02-20 | Hazard |  |  | 38830992000008 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive one pole tap low lines over driveway | Hwy 30E, Gauge, Ky.
2020 | 2020-02-20 | Hazard |  |  | 38831016000013 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Hwy 30E, Gauge, Ky.
2020 | 2020-02-20 | Hazard |  |  | 38831016000015 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Hwy. 30E, Gauge, Ky.
2020 | 2020-02-20 | Hazard |  |  | 38831040000029 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Remove secondary and secondary pole. Vines making xfmr pole lean. | Hwy 30E, gauge, Ky.
2020 | 2020-02-20 | Hazard |  |  | 38831059000056 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive xfmr | Quicksand Creek Rd, Lambrick, Ky.
2020 | 2020-02-20 | Hazard |  |  | 38831064000007 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole cut off | Hwy. 542, Gauge, Ky.
2020 | 2020-02-20 | Hazard |  |  | 38831064000023 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | guys/anchors: broken or missing |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | One pole tap needs to be removed pole 1064-73, guy broke and pole leaning. | Hwy. 542, Gauge, Ky.
2020 | 2020-02-20 | Hazard |  |  | 38831064000056 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Hwy. 542, Gauge, Ky.
2020 | 2020-02-20 | Hazard |  |  | 38831065000005 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive xfmr | Hwy 542, Lambrick, Ky
2020 | 2020-02-20 | Hazard |  |  | 38831065000006 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive xfmr | Hwy 542, Lambrick, Ky.
2020 | 2020-02-20 | Hazard |  |  | 38831065000029 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Pole leaning, needs an anchor and guy. | Hwy 542, Gauge, Ky.
2020 | 2020-02-20 | Hazard |  |  | 38831065000032 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive xfmr | Hwy 542, Lambrick, Ky.
2020 | 2020-02-20 | Hazard | 78392776 | DKY0112046 | 38831065000055 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | YES | Telephone pole close to conductor | Hwy. 542, Gauge, Ky. | 2021-04-28
2020 | 2020-02-20 | Hazard |  |  | 38831089000012 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Quicksand Creek Rd, Lambrick, Ky.
2020 | 2020-02-20 | Hazard |  |  | 38831089000031 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Span guy close to primary. | 3731 Quicksand Road, Lambrick, Ky.
2020 | 2020-02-20 | Hazard |  |  | 38831089000049 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole rotten | 3595 Quicksand Creek Rd. Lambrick,Ky.
2020 | 2020-02-20 | Hazard |  |  | 38841064000104 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive xfmr | Hwy. 542, Gauge, Ky.
2020 | 2020-02-24 | Hazard |  |  | 37830305000008 |  | 3311401-REEDY / DEANE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Pole leaning bad | Beaver Dam Rd, Colson, Ky.
2020 | 2020-02-24 | Hazard | 85788353 |  | 37830328C00130 | TRUE | 3311401-REEDY / DEANE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole bad at bottom. | Buck Crk. Dean, Ky
2020 | 2020-02-24 | Hazard | 76498093 | DKY0109505 | 37830329000047 | TRUE | 3311401-REEDY / DEANE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole washed out, looks like it is. | Hwy. 7, Colsom,Ky. | 2022-08-25
2020 | 2020-02-26 | Hazard |  |  | 38831084C00056 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Stacked crossarms | KY-30, Jackson, KY, USA
2020 | 2020-02-26 | Hazard |  |  | 38831084D00024 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Stacked crossarms | Hwy. 30E, Jackson, Ky.
2020 | 2020-02-26 | Hazard |  |  | 38831108C00313 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Leaning bad pole, may need r/w to cut trail f0r pole replacement. | 460 Big Branch Southfork Rd, Jackson, KY 41339, USA
2020 | 2020-02-26 | Hazard |  |  | 38831110000012 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole bad at top, yard dog | Jackson, KY 41339, USA
2020 | 2020-02-26 | Hazard | 76260893 | DKY0109225 | 38831110000089 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole cut off. | South Quicksand, Jackson, Ky. | 2020-06-01
2020 | 2020-02-27 | Hazard |  |  | 38831108B00075 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Bad xfmr,needs removed | Robinson Rd. Jackson, Ky.
2020 | 2020-02-27 | Hazard |  |  | 38831108C00055 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , crossarm/braces: broken/split |  |  | Foreign | YES | Pole bad | Woodcenter Dr, Jackson, KY 41339, USA
2020 | 2020-02-27 | Hazard |  |  | 38831108C00093 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bottom set of arms are stacked. | KY-1098, Jackson, KY 41339, USA
2020 | 2020-02-27 | Hazard |  |  | 38831108C00137 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole, might can use truck. | South Fork Quicksand Creek, Kentucky 41339, USA
2020 | 2020-02-27 | Hazard |  |  | 38831108C00303 |  | 3451202-BEEFHIDE / DUNHAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole in bad shape | Rose Fork, Kentucky 41301, USA | 2020-10-01
2020 | 2020-02-27 | Hazard |  |  | 38831108C10712 |  | 3310501-HADDIX / QUICKSAND | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Ground wire missing from regulator pole | South Fork, Jackson, Ky.
2020 | 2020-02-27 | Hazard | 77917495 | DKY0111409 | 38831109000020 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole bad | Smith Branch Rd. Jackson, KY | 2021-01-14
2020 | 2020-02-27 | Hazard |  |  | 38831109000021 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten | Smith Branch Rd. Jackson, Ky
2020 | 2020-02-27 | Hazard |  |  | 38831109000059 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole bad | Smith Branch Rd. Jackson, Ky.
2020 | 2020-02-27 | Hazard |  |  | 38831109000074 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten | Smith Branch Rd, Kentucky 41339, USA
2020 | 2020-02-27 | Hazard |  |  | 38831110000069 | TRUE | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole bad | South. Fork, Jackson, Ky
2020 | 2020-02-27 | Hazard |  |  | 38831111000022 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | South Fork Quicksand, Jackson, Ky
2020 | 2020-02-27 | Hazard |  |  | 38831111000037 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Jackson, KY 41339, USA
2020 | 2020-02-27 | Hazard | 77927555 | DKY0111419 | 38831133000014 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole bad | SmithBranch Rd. Jackson, Ky | 2021-01-14
2020 | 2020-02-28 | Hazard | 86290367 |  | 37830004D00052 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Falcon Rd. Haddix, Ky.
2020 | 2020-02-28 | Hazard |  |  | 37830056000032 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Tap needs resagged | Buckhorn Crk. Troublesome Crk. Ky.
2020 | 2020-02-28 | Hazard |  |  | 38831037000001 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Lick Branch-Noctor Rd, Kentucky 41339, USA
2020 | 2020-02-28 | Hazard |  |  | 38831037000028 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Neutral sagged to close to primary. | Airport Rd, Kentucky 41339, USA
2020 | 2020-02-28 | Hazard |  |  | 38831037000030 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Anchor pulled out, needs replaced | Airport Rd, Kentucky 41339, USA
2020 | 2020-02-28 | Hazard |  |  | 38831038000058 |  | 3310501-HADDIX / QUICKSAND | Line Work | UG | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Neutral wrapped in telephone cable | 10461 KY-30, Jackson, KY 41339, USA
2020 | 2020-02-28 | Hazard |  |  | 38831038000074 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Secondary pole leaning, needs straightened | Meat Scaffold Rd, Kentucky 41339, USA
2020 | 2020-02-28 | Hazard | 77931596 | DKY0111425 | 38831039000028 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | YES | Pole bad and inactive one pole tap 1039-29 needs removed. | Hunting Creek Rd, Kentucky, USA
2020 | 2020-02-28 | Hazard | 63581663 | DKY0093372 THIS WORK REQUEST HAS BEEN CANCELLED - NEED TO UPDATE DEFECT TRACKER | 38831039000041 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | YES | Pole leaning needs replaced, maybe move up closer to road. This pole was replaced on trouble 03/04/2020. | KY-30, Jackson, KY, USA | 2022-02-21
2020 | 2020-02-28 | Hazard |  |  | 38831039000045 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | KY-30, Jackson, KY, USA
2020 | 2020-02-28 | Hazard |  |  | 38831039000050 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Neutral wire down across creek. Need a boat and r/w crew to cut path. | KY-30, Jackson, KY, USA
2020 | 2020-02-28 | Hazard |  |  | 38831039000052 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive xfmr | KY-30, Kentucky, USA
2020 | 2020-02-28 | Hazard |  |  | 38831039000078 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | KY-30, Kentucky, USA
2020 | 2020-02-28 | Hazard |  |  | 38831040000010 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , crossarm/braces: broken/split |  |  | Foreign | YES | Pole bad | KY-30, Kentucky, USA
2020 | 2020-02-28 | Hazard | 84355287 | DKY0119497 | 38831040000016 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Crossarms bad on pole16 and another pole that’s not on map. Cross creek before hwy 542 | KY-30, Kentucky, USA | 2023-03-30
2020 | 2020-02-28 | Hazard | 85142372 | DKY0120838 | 38831060C40328 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr and secondary and secondary pole | Carpenter Br. Jackson, Ky. | 2023-06-22
2020 | 2020-02-28 | Hazard |  |  | 38831062000003 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive xfmr and secondary and secondary pole | 7079 KY-30, Jackson, KY 41339, USA
2020 | 2020-02-28 | Hazard |  |  | 38831062000013 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Crossarms bad | KY-30, Jackson, KY, USA
2020 | 2020-02-28 | Hazard | 84615817 | DKY0120001 | 38831062000029 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | crossarm/braces: broken/split |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Crossarm braces broken and remove inactive xfmr | KY-30, Jackson, KY, USA | 2023-03-30
2020 | 2020-02-28 | Hazard |  |  | 38831062000073 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive xfmr and secondary and secondary pole | 9421 KY-30, Jackson, KY 41339, USA
2020 | 2020-02-28 | Hazard |  |  | 38831062000076 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive xfmr | 9981 KY-30, Jackson, KY 41339, USA
2020 | 2020-02-28 | Hazard |  |  | 38831062B20090 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive xfmr, can get side/side to pole | KY-30, Kentucky, USA
2020 | 2020-02-28 | Hazard |  |  | 38831084C00054 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | cutout: damaged |  |  | Foreign | NO | One pole tap off pole 1184-54, needs a line C/O installed and show on maps. | 1225 KY-30, Jackson, KY 41339, USA
2020 | 2020-02-28 | Hazard |  |  | 38831084C00055 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Need to remove inactive xfmr and secondary and secondary pole | KY-30, Jackson, KY, USA
2020 | 2020-02-28 | Hazard |  |  | 38831109000043 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Remove one pole tap and xfmr on pole 1109-48
2020 | 2020-02-28 | Hazard |  |  | 38831132000030 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive xfmr | 6665 KY-15, Jackson, KY 41339, USA
2020 | 2020-02-28 | Hazard |  |  | 38831132000139 | TRUE | 3310501-HADDIX / QUICKSAND | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | YES | Primary guy broken | KY-15, Jackson, KY, USA
2020 | 2020-02-28 | Hazard | 85203287 | DKY0120927 | 38831132000174 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | 588 Big Branch Rd, Jackson, KY 41339, USA | 2023-06-12
2020 | 2020-02-28 | Hazard |  |  | 38831133000002 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive xfmr and secondary and secondary pole 1133-28. This also needs a PTP and insulator for loop on double deadend for 19.9 | 705 Big Branch Rd, Jackson, KY 41339, USA
2020 | 2020-03-02 | Hazard | 85182569 |  | 37830056000033 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten at ground level | Buckhorn Crk. Troublesome, Ky
2020 | 2020-03-03 | Hazard | 76263862 | DKY0109238 | 37830053000035 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole top | Leatherwood Rd. Watts, Ky | 2020-12-10
2020 | 2020-03-03 | Hazard |  |  | 37830100000091 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy broken, may not need it, may just need to remove it from pole. | Mcintosh Rd. Watts, Ky.
2020 | 2020-03-03 | Hazard |  |  | 37830101000004 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten ground level | Leatherwood Rd. Watts, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830374B00142 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole was out, needs replaced. | Carbon Glow, Jeremiah, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830374B00147 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | 3 pole 3 phase tap needs removed. Inactive | Carbon Glow, Jeremiah, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830374B00150 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Crossarms bad. | Carbon Glow, Jeremiah, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830374C00015 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten at ground level. | 180 Doty Creek Rd. Jeremiah, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830374D00185 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten and hollow at ground level. Near Jeremiah Baptist Church. | Hwy 7, Jeremiah, Ky
2020 | 2020-03-05 | Hazard | 80136286 | DKY0114478 | 37830375B00417 | TRUE | 3308602-COLLIER / LOWERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive xfmr and c/o and brkt. | Arthur’s Loop, Blair Branch, Isom, Ky. | 2022-02-23
2020 | 2020-03-05 | Hazard |  |  | 37830397000003 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Xfmr leaking oil | Crases Branch, Jeremiah, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830397000020 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole removed, pole fire, needs replaced. | 507 Crases Branch, Jeremiah, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830397000021 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten at ground level. | 546 Crases Branch, Jeremiah, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830397000025 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten ground level | Crases Branch, Jeremiah, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830397000027 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten ground level. | Crashes Branch, Jeremiah, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830397000125 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Secondary pole rotten. Bad shape needs ASAP | Mushroom Rd. Elk Crk. Blacky, Ky.
2020 | 2020-03-05 | Hazard | 76214971 | DKY0109151 | 37830397000154 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole cut off because of c/o breakdown | Elk Creek, Blacky, Ky | 2020-12-11
2020 | 2020-03-05 | Hazard |  |  | 37830398B00316 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten at ground level. | Crashes Branch, Jeremiah, Ky.
2020 | 2020-03-05 | Hazard | 76215006 | DKY0109423 | 37830398C00020 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole stubbed needs replaced. | Letcher High School, Letcher, Ky. | 2020-12-21
2020 | 2020-03-05 | Hazard |  |  | 37830399000016 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotted off ground level. | Spring Branch, Letcher, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830420D00003 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten ground level | Old Dixon Rd., Blacky, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830421A20124 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive xfmr and c/o, brkt, needs removed. | Canoe Rd. Blacky, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830421A20128 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Neutral stolen #4 solid copper | Canoe Rd. Blacky, Ky.
2020 | 2020-03-05 | Hazard |  |  | 37830421A40133 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | 25kva xfmr leaking oil | Arnold Fork, Blacky, Ky.
2020 | 2020-03-05 | Hazard | 76214989 | DKY0109159 | 37830421C30236 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at ground level. | Woodrock Rd, Blacky, Ky | 2020-11-30
2020 | 2020-03-05 | Hazard | 76214984 | DKY0109155 | 37830421C30300 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Secondary pole rotten at ground level | Woodrock Rd. Blacky, Ky. | 2020-10-02
2020 | 2020-03-05 | Hazard |  |  | 37830445000089 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Pole leaning over rd. | Old Dixon Rd. Blacky, Ky.
2020 | 2020-03-06 | Hazard | 76370826 | DKY0109318 | 37830317000025 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , crossarm/braces: broken/split |  |  | KPC | YES | Access road goes through creek. Need dry time when water isn’t up to access. | Lower McIntosh bout 1.5 miles up | 2020-10-19
2020 | 2020-03-06 | Hazard |  |  | 37830317000064 |  | 3303902-LESLIE / WOOTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Repull guy | Hwy 80 by bowling’s hollow
2020 | 2020-03-06 | Hazard |  |  | 37830341000106 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Ky-3425, Kentucky 41749, USA
2020 | 2020-03-06 | Hazard |  |  | 37830365000009 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove primary tap with 3 sec poles 1/0 lash | Across from mallard lane
2020 | 2020-03-06 | Hazard |  |  | 37830365000194 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | By 4 wheeler shop | 5923 KY-80, Wooton, KY 41776, USA
2020 | 2020-03-06 | Hazard |  |  | 37830365000323 |  | 3303902-LESLIE / WOOTON | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Neutral wrapped up in telephone cable | Mallard dr. Wooton
2020 | 2020-03-06 | Hazard |  |  | 37830366000017 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove xfmr | On left past bailey br wooton
2020 | 2020-03-06 | Hazard |  |  | 37830366000106 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr and cutout | Tao to left .7 miles up woot on rd.
2020 | 2020-03-06 | Hazard |  |  | 37830366000296 |  | 3303902-LESLIE / WOOTON | Line Work | OH | cutout: damaged |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Just past 2nd fork on left on hill
2020 | 2020-03-06 | Hazard | 76383122 | DKY0109339 | 37830366D00118 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 2nd Fork, Kentucky 41776, USA | 2020-10-12
2020 | 2020-03-06 | Hazard |  |  | 37830389000020 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Across cr from dollar store cutshin
2020 | 2020-03-06 | Hazard |  |  | 37830389000275 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | 2nd pole past step down up saw branch
2020 | 2020-03-06 | Hazard |  |  | 37830389000279 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | By old dog pound | Alpha lane
2020 | 2020-03-06 | Hazard |  |  | 37830390000145 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage | conductors: excessive splices, deteriorated conductors | KPC | NO | Primary bout in to | 2nd fork wooton
2020 | 2020-03-06 | Hazard | 76394462 | DKY0109353 | 37830391000013 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace 35/7 May be able to use Yard Dog. Located at the end of a field in a cemetery. | Albert wells fork | 2020-09-24
2020 | 2020-03-06 | Hazard | 76396305 | DKY0109362 | 37830391000015 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace 35/6 | Albert wells fork | 2020-09-29
2020 | 2020-03-06 | Hazard | 81773168 |  | 37830391000074 |  | 3303902-LESLIE / WOOTON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO |  | Albert wells fork | 2022-03-09
2020 | 2020-03-06 | Hazard |  |  | 37830413000355 | TRUE | 3303902-LESLIE / WOOTON | Line Work | OH |  |  |  | KPC | NO |  | 1.5 up coon cr.
2020 | 2020-03-06 | Hazard |  |  | 37830414000013 |  | 3303902-LESLIE / WOOTON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | On hill across from polls cr | Left drive after polls cr
2020 | 2020-03-06 | Hazard | 86293035 |  | 37830414000014 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole in a slide | 3111 hwy 699 before polls cr
2020 | 2020-03-06 | Hazard | 81773182 |  | 37830414000042 |  | 3303902-LESLIE / WOOTON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO |  | 1452 polls cr | 2022-03-09
2020 | 2020-03-06 | Hazard |  |  | 37830414000054 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO |  | On hill across from polls cr
2020 | 2020-03-06 | Hazard |  |  | 37830414000055 |  | 3303902-LESLIE / WOOTON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO |  | On hill across from polls cr
2020 | 2020-03-06 | Hazard | 81773209 |  | 37830414000159 |  | 3303902-LESLIE / WOOTON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO |  | By august lane polls cr | 2022-03-09
2020 | 2020-03-06 | Hazard |  |  | 37830415000026 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO |  | Daley br polls cr
2020 | 2020-03-06 | Hazard | 76093009 | Ops 033017687 | 37830415000056 |  | 3303902-LESLIE / WOOTON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove meter and service | Before granny fork | 2020-03-30
2020 | 2020-03-06 | Hazard |  |  | 37830415000110 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | 2326 polls cr close to mine
2020 | 2020-03-06 | Hazard | 81775134 |  | 37830415000111 |  | 3303902-LESLIE / WOOTON | Service Work | OH | crossarm/braces: broken/split , service: unused or abandoned, blanked meter base |  |  | KPC | NO |  | 3511 polls cr | 2022-03-09
2020 | 2020-03-06 | Hazard | 77801091 | DKY0111256 | 37830437000021 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace pole | 2410 coon cr | 2020-11-03
2020 | 2020-03-06 | Hazard | 77806484 | DKY0111262 | 37830437000049 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | YES |  | 1/2 mile up coon cr after crossing bridge at fire dept | 2020-12-10
2020 | 2020-03-06 | Hazard |  |  | 37830437000053 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Behind coon cr fire dept | 3260 coon cr
2020 | 2020-03-06 | Hazard |  |  | 37830437000124 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Coon cr
2020 | 2020-03-06 | Hazard |  |  | 37830437000352 |  | 3303902-LESLIE / WOOTON | Line Work | OH | service: unused or abandoned, blanked meter base |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Cross bridge before Hensley br Wolfe cr
2020 | 2020-03-06 | Hazard |  |  | 37830438000008 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove tap not in use crossing hwy 699 | By Adams market cutshin
2020 | 2020-03-06 | Hazard |  |  | 37830438000017 |  | 3303902-LESLIE / WOOTON | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove unused open sec and pole | Lillie Engle rd cutshin
2020 | 2020-03-06 | Hazard | 81775153 | G0000110 | 37830438000020 |  | 3303902-LESLIE / WOOTON | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Resag sec | 129 Lillie Engle Rd, Smilax, KY 41764, USA | 2022-03-09
2020 | 2020-03-06 | Hazard |  |  | 37830438000021 |  | 3303902-LESLIE / WOOTON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Remove bad cross arm not in use | Lillie Engle rd cutshin
2020 | 2020-03-06 | Hazard | 76093065 | 034103444 | 37830438000041 |  | 3303902-LESLIE / WOOTON | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO |  | Levi br cutshin | 2020-03-31
2020 | 2020-03-06 | Hazard | 76435803 | DKY0109408 | 37830438000048 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 795 Levi’s br | 2020-10-06
2020 | 2020-03-06 | Hazard | 76437898 | DKY0109414 | 37830438000050 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | Cutshin, KY 41777, USA | 2020-10-15
2020 | 2020-03-06 | Hazard |  |  | 37830438000070 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Beech bottom cutshin
2020 | 2020-03-06 | Hazard | 76093043 | 034652112 | 37830438000144 |  | 3303902-LESLIE / WOOTON | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO |  | Levi br | 2020-03-31
2020 | 2020-03-06 | Hazard | 77819505 | DKY0111277 | 37830461000034 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace 35/5 | 4493 coon cr | 2020-11-09
2020 | 2020-03-06 | Hazard |  |  | 37830461000045 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | 5 miles up coon cr
2020 | 2020-03-06 | Hazard | 77820901 | DKY0111288 | 37830461000047 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad pole | 5120 coon cr | 2020-11-05
2020 | 2020-03-06 | Hazard | 76101947 | 038051299 | 37830461000309 |  | 3303902-LESLIE / WOOTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Repull guys | Copper lane | 2020-03-31
2020 | 2020-03-06 | Hazard | 76093133 | Ops 039200204 | 37830462000025 |  | 3303902-LESLIE / WOOTON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove meter and service | Mouth of Hendrix br | 2020-03-30
2020 | 2020-03-06 | Hazard |  |  | 37830462000044 |  | 3303902-LESLIE / WOOTON | Line Work | OH | crossarm/braces: broken/split | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Bad arm holding cutout | Hummingbird lane cutshin
2020 | 2020-03-06 | Hazard |  |  | 37830462000047 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Hummingbird lane
2020 | 2020-03-06 | Hazard |  |  | 37830462000134 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Before dairy bar | 6897 Cutshin Rd, Smilax, KY 41764, USA
2020 | 2020-03-06 | Hazard | 76093096 | 038016597 | 37830462000151 |  | 3303902-LESLIE / WOOTON | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Line fuse pole | Beech bottom cutshin | 2020-03-31
2020 | 2020-03-06 | Hazard |  |  | 37830462000177 | TRUE | 3303902-LESLIE / WOOTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Straighten pole | Crystal lane cutshin
2020 | 2020-03-06 | Hazard | 76466820 | DKY0109448 | 37830462000195 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Across from pecan ln | 6540 cutshin rd | 2020-09-02
2020 | 2020-03-06 | Hazard |  |  | 37830462000196 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Pole shows 462-280 in field | 116 stidham rd Wolfe cr
2020 | 2020-03-06 | Hazard |  |  | 37830462000323 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | 6340 Wolfe cr rd
2020 | 2020-03-06 | Hazard | 77213262 | DKY0110497 | 37830463000010 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | Longs fork cutshin | 2020-10-22
2020 | 2020-03-06 | Hazard |  |  | 37830463000024 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Need to retire line not in use | Head of crystal lane | 2023-10-30
2020 | 2020-03-06 | Hazard |  |  | 37830463000045 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | 1st right up mud lick cutshin
2020 | 2020-03-06 | Hazard |  |  | 37830463000068 |  | 3303902-LESLIE / WOOTON | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral down | Longs br cutshin
2020 | 2020-03-06 | Hazard |  |  | 37830486000010 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Head of lane br cutshin
2020 | 2020-03-06 | Hazard |  |  | 37830486000216 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Myra br Wolfe cr
2020 | 2020-03-06 | Hazard |  |  | 37830487000227 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | On right past mud lick br cutshin
2020 | 2020-03-06 | Hazard |  |  | 37830487000504 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO |  | Cutshin, KY 41777, USA past mud lick br on left
2020 | 2020-03-06 | Hazard | 81775171 | G0000110 | 37830510000014 |  | 3303902-LESLIE / WOOTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Install guy guard | Mouth of causey lane baker fork | 2022-03-09
2020 | 2020-03-06 | Hazard | 77820008 | DKY0111281 | 37830510000019 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace 35/6 | Causey lane | 2020-12-29
2020 | 2020-03-06 | Hazard | 77826505 | DKY0111294 | 37830510000098 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 538 baker fork | 2020-12-18
2020 | 2020-03-06 | Hazard |  |  | 37830510000116 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | 381 big fork rd
2020 | 2020-03-06 | Hazard | 76165307 | 03322378 | 37830510000157 |  | 3303902-LESLIE / WOOTON | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO |  | Near mouth of baker fork | 2020-04-06
2020 | 2020-03-06 | Hazard |  |  | 37830510000167 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | 3764 Wolfe cr
2020 | 2020-03-06 | Hazard | 81775205 | G0000110 | 37830511000038 |  | 3303902-LESLIE / WOOTON | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO |  | Wolfe cr by old mine entrance | 2022-03-09
2020 | 2020-03-06 | Hazard | 81775226 | G0000110 | 37830511000130 |  | 3303902-LESLIE / WOOTON | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO |  | 1/2 mile up hazelnut rd Wolfe cr | 2022-03-09
2020 | 2020-03-06 | Hazard |  |  | 37830535000001 |  | 3303902-LESLIE / WOOTON | Line Work | OH | service: unused or abandoned, blanked meter base |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | 436 hazelnut Wolfe cr
2020 | 2020-03-09 | Hazard | 77659025 | DKY0111073 | 37830003000011 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole bad been stubbed | Hwy. 1410, Haddix, Ky. | 2020-12-15
2020 | 2020-03-09 | Hazard |  |  | 37830267000127 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Straighten pole | Wilder Branch Rd. confluence, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830315000031 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Bull Creek Rd. Thousandsticks, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830315000071 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace bad pole | Bull Creek Rd. Hyden, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830315000109 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Bull Creek Rd. Thousandsticks,Ky
2020 | 2020-03-09 | Hazard |  |  | 37830316000009 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | 6270 Dry Hill Rd. Hyden, Ky.
2020 | 2020-03-09 | Hazard | 76448206 | DKY0109509 | 37830316000067 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad pole | Dry Hill Rd. Hyden, Ky. | 2021-01-07
2020 | 2020-03-09 | Hazard |  |  | 37830316A10200 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Dry Hill Rd. Hyden, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830339000009 |  | 3303901-LESLIE / HYDEN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Replace bad crossarms | Dry Hill Rd. Hyden, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830339000129 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Straighten pole and center phase needs tied in. | Dry Hill Rd. Hyden, Ky.
2020 | 2020-03-09 | Hazard | 80821461 | DKY0115322 | 37830339000139 | TRUE | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | YES | Remove inactive xfmr and secondary and secondary pole | Bull Creek Rd. Confluence, Ky. | 2022-03-15
2020 | 2020-03-09 | Hazard | 80821461 | DKY0115322 | 37830339000139 | TRUE | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive secondary and secondary pole | Bull Creek Rd. Confluence, Ky. | 2022-03-15
2020 | 2020-03-09 | Hazard |  |  | 37830339A30196 | TRUE | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Bull Creek Rd. Thousandsticks, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830340000018 |  | 3303901-LESLIE / HYDEN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Replace bad crossarms | Dry Hill Rd. Hyden, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830340000020 |  | 3303901-LESLIE / HYDEN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Replace bad crossarms | Dry Hill Rd. Hyden,Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830363000011 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Dry Hill Rd. Hyden, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830363000021 |  | 3303901-LESLIE / HYDEN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Repair guy | Dry Hill Rd. Hyden, Ky.
2020 | 2020-03-09 | Hazard | 76245096 | DKY0109352 | 37830363000058 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad pole | Asher Branch Rd. Hyden, Ky. | 2020-12-14
2020 | 2020-03-09 | Hazard | 76245073 | DKY0109212 | 37830363000156 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad pole | Hickory St. Hyden, Ky. | 2021-01-05
2020 | 2020-03-09 | Hazard | 76215125 | DKY0109489 | 37830364000123 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad pole | Owls Nest Rd. Hyden, Ky. | 2020-12-11
2020 | 2020-03-09 | Hazard |  |  | 37830364000170 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad secondary pole | 2860 Owls Nest Rd. Hyden, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830388A00301 |  | 3303901-LESLIE / HYDEN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Low service, needs secondary pole serves blue castle. | Main St. Hyden, Ky.
2020 | 2020-03-09 | Hazard | 70595829 | DKY0101127 | 37830388A00335 | TRUE | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr and secondary and secondary pole #388-199 | Owls Nest Rd. Hyden, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830388B00062 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Morgan Ln. Hyden, Ky
2020 | 2020-03-09 | Hazard | 85185938 | DKY0120923 | 37830388B30514 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Daisy Ln. Hyden, Ky. | 2023-06-14
2020 | 2020-03-09 | Hazard | 76245054 | DKY0109207 | 37830388C00481 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | YES | Remove inactive secondary tap. | Daisy Lane Pond, Hyden, Ky. | 2020-11-12
2020 | 2020-03-09 | Hazard | 76245008 | DKY0109195 | 37830388D00068 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad pole, | Flackey Rd. Hyden, Ky. | 2021-05-25
2020 | 2020-03-09 | Hazard | 69954195 | DKY0100123 | 37830388D00279 | TRUE | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Hwy. 80, Hyden, Ky. | 2023-01-19
2020 | 2020-03-09 | Hazard | 81773126 | G0000110 | 37830388D00440 |  | 3303901-LESLIE / HYDEN | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Resag service, service low | JC Osborne Blvd. Hyden, Ky. | 2022-03-09
2020 | 2020-03-09 | Hazard | 76245036 | DKY0109200 | 37830388D00467 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole bad | Daisy ln. Hyden, Ky. | 2020-12-22
2020 | 2020-03-09 | Hazard | 75846174 | DKY0108561 | 37830412A00026 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad pole | Morgan Ln. Hyden, Ky.
2020 | 2020-03-09 | Hazard | 75845585 | DKY0108557 | 37830412A00027 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace pole | Morgan Ln. Hyden,Ky. | 2020-04-06
2020 | 2020-03-09 | Hazard |  |  | 37830412A00028 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Installed guy marker | Morgan Ln. Hyden, Ky. | 2020-02-20
2020 | 2020-03-09 | Hazard |  |  | 37830412C00021 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning bad | Primrose Ln. Hyden, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830412C00067 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad pole | Hwy 80, HYDEN, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830412C00068 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy. 80, Hyden, Ky.
2020 | 2020-03-09 | Hazard | 76244965 | DKY0109191 | 37830412C00075 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | G Bad secondary pole | Hwy 80, Hyden, Ky. | 2020-12-21
2020 | 2020-03-09 | Hazard |  |  | 37830412C00228 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Straighten secondary pole | Hwy 80, Hyden, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830412C00265 |  | 3303901-LESLIE / HYDEN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy broken | Hwy 80, Hyden, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830412C00266 |  | 3303901-LESLIE / HYDEN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarm | Van over Rd. Hyden, Ky.
2020 | 2020-03-09 | Hazard |  |  | 37830412D00038 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace secondary pole | Hurricane Creek Rd. Hyden, Ky. | 2020-11-11
2020 | 2020-03-09 | Hazard | 76244931 | DKY0109187 | 37830413B00276 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad pole | Preacher Fork, Hyden, Ky | 2020-07-14
2020 | 2020-03-10 | Hazard |  |  | 37830027000045 |  | 3310502-HADDIX / CANOE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Line down from pole 27-45 up. Needs removed. Tap been lifted off pole 45 | Howard’s Creek, Haddix, Ky. | 2023-10-30
2020 | 2020-03-10 | Hazard |  |  | 37830052000006 |  | 3310502-HADDIX / CANOE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove 5 pole tap, inactive line | South Copeland, Haddix, Ky.
2020 | 2020-03-10 | Hazard |  |  | 37830052000127 | TRUE | 3310502-HADDIX / CANOE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive xfmr | South Copeland, Haddix, Ky.
2020 | 2020-03-10 | Hazard | 77837247 | DKY0111713 | 37830099000039 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Replace bad pole | Hwy. 1110, Haddix, Ky. | 2020-12-11
2020 | 2020-03-16 | Hazard | 77710905 | DKY0111130 | 37830025000055 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Mill Br. Rd. Whick, Ky | 2020-12-18
2020 | 2020-03-16 | Hazard | 77704668 | DKY0111127 | 37830026000028 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Mill Crk. Rd, Whick, Ky. | 2020-12-18
2020 | 2020-03-16 | Hazard | 77701183 | DKY0111123 | 37830050000046 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Buzzard Fork Rd. Whick, Ky | 2021-05-11
2020 | 2020-03-16 | Hazard | 77665395 | DKY0111092 | 37830051000083 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole needs changed | Hwy. 1110, Haddix, Ky. | 2020-12-15
2020 | 2020-03-17 | Hazard | 77543842 | DKY0110967 | 37830001000002 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Canoe Rd, Kentucky, USA | 2020-11-12
2020 | 2020-03-17 | Hazard | 76970463 | DKY0110189 | 37830001000002 (wo #110189 replaces #37830001000001 - #2 was replaced on 11/12/2020) |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Stub pole | Canoe Rd, Kentucky, USA | 2022-02-10
2020 | 2020-03-17 | Hazard | 76216241 | DKY0109139 | 37830025000021 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Canoe Rd, Kentucky, USA | 2020-10-28
2020 | 2020-03-17 | Hazard | 76230920 | DKY0109158 | 37830025000022 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Bad leaning pole | Canoe Rd, Kentucky, USA | 2020-11-12
2020 | 2020-03-17 | Hazard |  |  | 37830073000041 |  | 3310502-HADDIX / CANOE | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Primary side tap guy broken | Stone Coal Creek Rd, Kentucky 41314, USA
2020 | 2020-03-17 | Hazard | 76261500 | DKY0109230 | 37830073000068 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole split at top | Elsome Creek Rd, Kentucky 41314, USA | 2020-12-22
2020 | 2020-03-18 | Hazard |  |  | 37830145000010 |  | 3310502-HADDIX / CANOE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Ground wire stolen | Middle Fork River Rd, Buckhorn, KY, USA
2020 | 2020-03-18 | Hazard | 76226659 | DKY0109182 | 37830145000024 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | YES | Bad pole needs changed and a inactive line needs removed |  | 2022-06-02
2020 | 2020-03-18 | Hazard | 78421462 | DKY0112095 | 37830145000027 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Ad pole | Middle Fork River Rd, Buckhorn, KY, USA | 2022-06-02
2020 | 2020-03-18 | Hazard | 76254702 | DKY0109209 | 37830146000065 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Cam Johnson Branch Rd, Kentucky, USA | 2020-12-09
2020 | 2020-03-18 | Hazard |  |  | 37830169C00031 |  | 3310502-HADDIX / CANOE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarms bad | Buckhorn Ln, Buckhorn, KY 41721, USA
2020 | 2020-03-18 | Hazard | Trouble ticket# 4488371 |  | 37830169C00200 |  | 3310502-HADDIX / CANOE | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Light secondary down, needs to be removed | 72 Buckhorn Clinic Rd, Buckhorn, KY 41721, USA | 2020-03-18
2020 | 2020-03-19 | Hazard | 76209426 | DKY0109126 | 37830193000080 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Otter Crk. Buckhorn, KY. | 2021-04-05
2020 | 2020-03-19 | Hazard | 76221896 | DKY0109141 | 37830217000048 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Abner Fork, Buckhorn, KY. | 2020-12-15
2020 | 2020-03-19 | Hazard | 76816488 | DKY0110007 | 37840215000003 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Otter Creek Rd, Kentucky 41721, USA | 2020-12-07
2020 | 2020-03-19 | Hazard | 76816428 | DKY0109998 | 37840216000094 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Cemetery Rd, Kentucky, USA | 2020-12-04
2020 | 2020-03-19 | Hazard |  |  | 37840240000137 |  | 3310502-HADDIX / CANOE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Inactive xfmr | Otter Crk. Buckhorn, KY.
2020 | 2020-03-20 | Hazard |  |  | 37830004B00289 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive xfmr | 2425 State Hwy 1110, Haddix, KY 41339, USA | 2023-10-30
2020 | 2020-03-20 | Hazard | 85181827 | DKY0121657 | 37830004D00155 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Span of neutral low | Fish Pond Loop, Kentucky 41339, USA
2020 | 2020-03-20 | Hazard |  |  | 37830005000045 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive xfmr and secondary and secondary pole | Hayes Branch Rd, Kentucky 41254, USA | 2023-10-30
2020 | 2020-03-20 | Hazard | 86290259 | DKY0123282 | 37830005000109 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Install guy | KY-476, Kentucky, USA
2020 | 2020-03-20 | Hazard |  |  | 37830006000008 | TRUE | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Riley Branch Rd, Kentucky, USA | 2023-10-30
2020 | 2020-03-20 | Hazard |  |  | 37830006000008 | TRUE | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Riley Branch Rd, Kentucky, USA | 2023-10-30
2020 | 2020-03-20 | Hazard | 86292592 |  | 37830006000016 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive tap | Riley Branch, Kentucky 41317, USA
2020 | 2020-03-20 | Hazard |  |  | 37830006000021 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive xfmr | Riley Branch Rd, Kentucky, USA | 2023-10-30
2020 | 2020-03-20 | Hazard | 77537325 | DKY0110954 | 37830006000030 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad secondary pole. | Riley Branch Rd, Kentucky, USA | 2020-12-17
2020 | 2020-03-20 | Hazard |  |  | 37830006000086 |  | 3451202-BEEFHIDE / DUNHAM | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive xfmr | Riley Branch Rd, Kentucky, USA | 2023-10-30
2020 | 2020-03-20 | Hazard | 77463274 | DKY0110854 | 37830029000005 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad pole | KY-476, Kentucky, USA | 2021-01-20
2020 | 2020-03-20 | Hazard | 85182073 | DKY0121203 | 37830029000031 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Replace bad crossarm | KY-476, Kentucky, USA
2020 | 2020-03-20 | Hazard | 86291508 |  | 37830029000108 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Duck Hollow Rd, Kentucky, USA
2020 | 2020-03-20 | Hazard | 86291508 |  | 37830029000109 |  | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr and secondary and secondary pole | Duck Hollow Rd, Kentucky, USA
2020 | 2020-03-20 | Hazard |  |  | 37830029000127 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm braces broken | Marie Roberts Rd, Kentucky, USA | 2023-06-23
2020 | 2020-03-20 | Hazard | 77532327 | DKY0110941 | 37830029000181 | TRUE | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad pole | KY-476, Kentucky, USA | 2020-11-18
2020 | 2020-03-20 | Hazard | 86290259 | DKY0123282 | 37830030000019 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Anchor and guy needs replaced | KY-476, Kentucky, USA
2020 | 2020-03-20 | Hazard | 86292782 |  | 37830030000021 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr and secondary and secondary poles | I-476, Pennsylvania, USA
2020 | 2020-03-20 | Hazard | 86290259 | DKY0123282 | 37830030000050 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Install guy breakers | Sister Rd, Kentucky 41317, USA
2020 | 2020-03-20 | Hazard | 86292782 |  | 37830030000110 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr and secondary and secondary poles | Russell Branch Rd, Kentucky 41317, USA
2020 | 2020-03-20 | Hazard | 77556928 | DKY0110971 | 37830030000142 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  |  |  | KPC | YES | Pole in creek needs relocated | Barge Creek, Kentucky, USA | 2020-12-23
2020 | 2020-03-20 | Hazard |  |  | 37830030000163 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr and secondary and secondary pole | Riley Branch, Kentucky 41317, USA | 2023-10-30
2020 | 2020-03-20 | Hazard | 76215383 | DKY0109125 | 37830030000171 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad secondary pole | KY-476, Kentucky, USA | 2020-05-01
2020 | 2020-03-20 | Hazard |  |  | 37830030000223 |  | 3310503-HADDIX/TROUBLESOME CREEK | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs guy breaker | Sister Rd, Kentucky 41317, USA
2020 | 2020-03-20 | Hazard |  |  | 37830050000012 |  | 3310502-HADDIX / CANOE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive tap | Canoe Rd, Canoe, Ky.
2020 | 2020-03-20 | Hazard |  |  | 37830050000037 |  | 3310502-HADDIX / CANOE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarms bad | Canoe Rd. Canoe,Ky. | 2023-06-23
2020 | 2020-03-20 | Hazard |  |  | 37830050000109 |  | 3310502-HADDIX / CANOE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Pole needs a guy | Butter Point Rd, Kentucky 41339, USA | 2023-06-23
2020 | 2020-03-20 | Hazard |  |  | 37830054000050 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr | Barge Creek Rd, Kentucky 41317, USA
2020 | 2020-03-20 | Hazard | 83323754 | DKY0117905 | 37830054000051 |  | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr and secondary and secondary poles | Barge Creek Rd | 2022-10-31
2020 | 2020-03-20 | Hazard |  |  | 37830054000079 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive secondary pole and secondary | KY-476, Kentucky, USA
2020 | 2020-03-20 | Hazard |  |  | 37830055000012 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr and straighten pole | KY-476, Kentucky, USA
2020 | 2020-03-20 | Hazard |  |  | 37830079000024 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  |  | conductors: excessive splices, deteriorated conductors , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive secondary and secondary pole | KY-476, Kentucky, USA
2020 | 2020-03-23 | Hazard |  |  | 37830120000036 |  | 3310502-HADDIX / CANOE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning | Burton Rd. Booneville, Ky.
2020 | 2020-03-23 | Hazard |  |  | 37830120000038 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole leaning and in bad shape | Burton Rd. Booneville, Ky.
2020 | 2020-03-23 | Hazard |  |  | 37840144000029 |  | 3310502-HADDIX / CANOE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property , conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive 8 pole tap, several inactive xfmrs. Tree has primary pinned near end of line. Needs removed or fixed. | Ingol Rd. Booneville, Ky.
2020 | 2020-04-07 | Hazard |  |  | 37830449A40298 | TRUE | 3309102-WHITESBUR / HOSPITAL | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Crossarms starting to crack and splinter. | Kentucky Ave, Whitesburg, KY 41858, USA
2020 | 2020-04-07 | Hazard |  |  | 37830449A40590 |  | 3309102-WHITESBUR / HOSPITAL | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm cracked and splintering | Kentucky Ave, Whitesburg, KY 41858, USA
2020 | 2020-04-07 | Hazard | 77424999 | DKY0110896 | 37830449B30668 | TRUE | 3309102-WHITESBUR / HOSPITAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Tennessee Ave, Whitesburg, KY 41858, USA | 2020-12-11
2020 | 2020-04-08 | Hazard |  |  | 37830426B00265 |  | 3314401-MAYKING / ERMINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole needs replaced | 74 Cr-1559, Whitesburg, KY 41858, USA
2020 | 2020-04-08 | Hazard |  |  | 37830426B30794 |  | 3314401-MAYKING / ERMINE | Line Work | UG | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Low conductors | Safari Dr, Kentucky 41858, USA
2020 | 2020-04-08 | Hazard | 85586713 | DKY0122395 | 37830449C30593 |  | 3314401-MAYKING / ERMINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Replace stacked arms. | Hwy 119, WHITESBURG, Ky. | 2023-11-21
2020 | 2020-04-08 | Hazard | 75770628 | DKY0108444 | 37830473000006 |  | 3314401-MAYKING / ERMINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole bad needs replaced. | 1424 State Hwy 2035, Whitesburg, KY 41858, USA | 2020-12-18
2020 | 2020-04-28 | Hazard |  |  | 37830332B00002 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 3409, McRoberts, Ky | 2020-10-23
2020 | 2020-04-28 | Hazard | 78201929 | DKY0111784 | 37830332C00125 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole been stubbed. | Sheas Fk. McRoberts, Ky. | 2021-01-12
2020 | 2020-04-28 | Hazard | 76665284 | DKY0109796 | 37830332D00138 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 343,McRoberts, Ky.
2020 | 2020-04-28 | Hazard | 76665329 | DKY0109800 | 37830332D00147 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 343, McRoberts, Ky. | 2021-01-08
2020 | 2020-04-28 | Hazard | 76686860 | DKY0110070 | 37830332D00148 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole, r/w needs to clear around pole. | Hwy 343, mcRoberts, Ky. | 2021-03-16
2020 | 2020-04-28 | Hazard |  |  | 37830333A00037 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 343, McRoberts, Ky. | 2020-11-11
2020 | 2020-04-28 | Hazard | 78231530 | DKY0111806 | 37830333A00063 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole been stubbed, needs changed. | Bark Camp Br. McRoberts, Ky | 2021-04-06
2020 | 2020-04-28 | Hazard | 76892021 | DKY0110083 | 37830333B00003 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 3409, McRoberts, Ky.
2020 | 2020-04-28 | Hazard | 76892658 | DKY0110088 | 37830333B00004 | TRUE | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 3409, McRoberts, Ky.
2020 | 2020-04-28 | Hazard | 76898983 | DKY0110095 | 37830333B00005 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , joint use attachments: clearance issues |  |  | KPC | YES | Bad pole | Hwy 3409, McRoberts, Ky.
2020 | 2020-04-28 | Hazard | 76899273 | DKY0110098 | 37830333B00006 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 3409, McRoberts, Ky.
2020 | 2020-04-28 | Hazard | 76904769 | DKY0110218 | 37830333B00011 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 3409, McRoberts, Ky. | 2021-12-14
2020 | 2020-04-28 | Hazard | 76929641 | DKY0110257 | 37830333B00012 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 3409, McRoberts, Ky.
2020 | 2020-04-28 | Hazard | 76929661 | DKY0110280 | 37830333B00015 | TRUE | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 3409, McRoberts, Ky.
2020 | 2020-04-28 | Hazard | 76929673 | DKY0110314 | 37830333B00028 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 3409, McRoberts, Ky. | 2021-01-13
2020 | 2020-04-28 | Hazard | 76662616 | DKY0109765 | 37830356C00050 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , crossarm/braces: broken/split |  |  | KPC | YES | Bad pole and crossarm | Hwy 343, Fleming Neon, Ky. | 2021-01-08
2020 | 2020-04-28 | Hazard | 77673990 | DKY0111088 | 37830356C00120 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Bandmill Bottom Rd. McRoberts, Ky.
2020 | 2020-04-28 | Hazard | 85688929 | DKY0121894 | 37830379B00097 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Set of arms bad | Hwy 805, Seco, Ky.
2020 | 2020-04-28 | Hazard | 77687413 | DKY0111102 | 37830380C00048 | TRUE | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole bad, could probably use a yard dog on this. | Hwy 805, Potters Fk. McRoberts, Ky.
2020 | 2020-04-28 | Hazard | 77308824 | DKY0110636 | 37830380C00057 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole bad and split at top of pole, crossarms bad. R/w needs to cut around pole | Hwy 805, Potters Fork, McRoberts, Ky. | 2020-12-22
2020 | 2020-04-29 | Hazard |  |  | 37830473000069 |  | 3314401-MAYKING / ERMINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole cut off with crossarm extension. Needs changed. | Limestone Dr. Whitesburg, Ky. | 2020-12-03
2020 | 2020-04-29 | Hazard | 78334537 | DKY0111949 | 37830473000156 |  | 3314401-MAYKING / ERMINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole has been cut off and lowered needs changed. | Limestone Dr. WHITESBURG, Ky. | 2021-01-07
2020 | 2020-04-29 | Hazard | 78337408 | DKY0111955 | 37830497000142 |  | 3314401-MAYKING / ERMINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole been cut off, extended with crossarm. | Hwy 119S, Whitesburg, Ky. | 2021-01-25
2020 | 2020-04-29 | Hazard | 75915178 | DKY0108644 | 37830497A40910 | TRUE | 3314401-MAYKING / ERMINE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning bad | Little Shepherd Trail, Whitesburg, Ky. | 2023-04-06
2020 | 2020-05-04 | Hazard | 77424977 | DKY0111291 | 37830382A30023 | TRUE | 3409503-BURDINE / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole needs changed. | Hwy 23 S, Jenkins, Ky
2020 | 2020-05-06 | Hazard | 77354686 | DKY0110709 | 37830358D00109 |  | 3409503-BURDINE / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Secondary pole bad | Number Two Bottom, Jenkins, Ky. | 2021-03-17
2020 | 2020-05-06 | Hazard | 77304975 | DKY0110652 | 37830358D00111 |  | 3409503-BURDINE / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole bad | 35 Number Two BTM, Jenkins, Ky. | 2021-03-17
2020 | 2020-05-06 | Hazard | 77372387 | DKY0110721 | 37830358D00115 |  | 3409503-BURDINE / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Adam St. Jenkins, Ky. | 2020-11-25
2020 | 2020-05-06 | Hazard | 77373805 | DKY0110826 | 37830358D00116 |  | 3409503-BURDINE / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Adam St. Jenkins, Ky. | 2020-11-25
2020 | 2020-05-06 | Hazard | 85688488 | DKY0121851 | 37830358D00132 |  | 3409503-BURDINE / JENKINS | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Primary guy broken.. | Number One Hill, Jenkins, Ky. | 2023-10-09
2020 | 2020-05-06 | Hazard | 77460765 | DKY0110832 | 37830358D00316 |  | 3409503-BURDINE / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole split at top of pole | Number Two Bottom, Jenkins, Ky.
2020 | 2020-05-06 | Hazard | 77278730 REPLACEMENT WR#80038340 | DKY0110595 REPLACEMENT WO#DKY0114122 | 37830382A30265 |  | 3409503-BURDINE / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at the top. | Cora Whitaker Dr. Jenkins, Ky. | 2021-07-01
2020 | 2020-05-06 | Hazard | 77280290 | DKY0110600 | 37830382C10037 |  | 3409503-BURDINE / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 146 Rocky Hollow, Jenkins, Ky.vC | 2020-12-02
2020 | 2020-05-27 | Hazard | 77837228 | DKY0111694 | 37830448C30518 |  | 3309103-WHITESBUR / COWAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole cracked and weathered bad, needs changed. | Hwy 931N, Whitesburg, Ky. | 2021-03-10
2020 | 2020-06-12 | Hazard |  |  | 37830128000017 |  | 3307301-BULAN / ARY-HEINE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Missing ground
2020 | 2020-06-12 | Hazard |  |  | 38831084A00258 |  | 3451202-BEEFHIDE / DUNHAM | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Ground not attached to the recloser can
2020 | 2020-08-13 | Hazard |  |  | 37830367000024 |  | 3303902-LESLIE / WOOTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning real bad, needs straightened! | Wooton, KY 41776, USA
2020 | 2020-08-17 | Hazard |  |  | 37830462000177 | TRUE | 3303902-LESLIE / WOOTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning bad | Crystal Lane, Cutshin, Ky.
2020 | 2020-09-01 | Hazard | 85181714 | CANCELLED | 37830004D00028 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarms in bad shape! | Hwy. 1110, Haddix, Ky. | 2023-11-28
2020 | 2020-09-01 | Hazard | 85182722 |  | 37830056000042 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole in bad shape, needs changed! | 3694 Little Buckhorn Rd. Rowdy, Ky.
2020 | 2020-09-15 | Hazard | 77532327 | DKY0110941 | 37830029000181 | TRUE | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at ground level has been reinforced. | 2050 Hwy 476, Clayhole, Ky. | 2020-11-18
2020 | 2020-09-15 | Hazard | 85182469 | DKY0121674 | 37830054000006 | TRUE | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Buck arm pole arms are bad | KY-476, Kentucky, USA
2020 | 2020-10-08 | Hazard |  |  | 37830026000005 |  | 3310502-HADDIX / CANOE | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Strand broke in primary 6A copper wire. | Joe Little Fork Rd, Kentucky 41339, USA | 2023-10-30
2020 | 2020-12-03 | Hazard | 80339718 | DKY0114553 | 37830465000001 | TRUE | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole bad | Owens Br. Rd. Slemp, Ky. | 2021-10-04
2020 | 2020-12-03 | Hazard | 80339774 | DKY0114551 | 37830466000061 | TRUE | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Puncheon Camp Rd. Slemp Ky. | 2021-12-10
2020 | 2020-12-03 | Hazard |  |  | 37830491000093 | TRUE | 3309902-SLEMP / LEATHERWOOD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Secondary guy need tightened pulling pole over | 4271 Little Leatherwood Crk. Slemp, Ky.

## Ckt Defects Reported 2021 HAZ
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2021 | 2021-01-04 | Hazard |  |  | 37830051200001 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr | Big Fork Rd, Kentucky 41777, USA
2021 | 2021-01-04 | Hazard | 80339718 | DKY0114553 | 37830465000001 | TRUE | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Owens Br. Slemp, Ky. | 2021-10-04
2021 | 2021-01-04 | Hazard | 80339774 | DKY0114551 | 37830466000061 | TRUE | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Puncheon Camp Rd. Slemp, Ky. | 2021-12-10
2021 | 2021-01-04 | Hazard | 85157617 | DKY0120856 | 37830512000041 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr | Big Fork Rd, Kentucky 41777, USA | 2023-06-14
2021 | 2021-01-04 | Hazard | 78549099 | DKY0112343 | 37830559000007 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole broke above telephone cable | 15 Coleman Rd, Toler, KY 41514, USA | 2021-01-12
2021 | 2021-01-04 | Hazard |  |  | 37830562000032 |  | 3309902-SLEMP / LEATHERWOOD | Service Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | House knob pulled loose from house. Next to last house in Stoney fk. | Stony Fork Rd, Kentucky 41735, USA
2021 | 2021-01-11 | Hazard | 80499732 | DKY0114699 | 37830276000083 |  | 3309301-VICCO / REDFOX | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole split at top. | Big Branch Rd, Vicco, Ky. | 2021-10-21
2021 | 2021-01-11 | Hazard | 80506972 | DKY0114708 | 37830277000019 |  | 3309301-VICCO / REDFOX | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Perkins Madden Rd. Vicco, Ky. | 2021-10-08
2021 | 2021-01-11 | Hazard | 77586529 | DKY0112391 | 37830301000220 |  | 3309301-VICCO / REDFOX | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Braces broken and arms flipped | Big Branch Rd. Vicco, Ky. | 2023-05-26
2021 | 2021-01-11 | Hazard | 80507141 | DKY0114740 | 37830349000016 | TRUE | 3309301-VICCO / REDFOX | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Pauley Hollow, Big Smith Br, Vicco, Ky.
2021 | 2021-01-13 | Hazard | 80508114 | DKY0114710 | 37830326C00076 | TRUE | 3309301-VICCO / REDFOX | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Breeding Creek Rd. Red Fox, Ky.
2021 | 2021-01-13 | Hazard | 80508604 | DKY0114713 | 37830327000001 |  | 3309301-VICCO / REDFOX | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Horseshoe Bend Rd. Red Fox, Ky. | 2022-02-17
2021 | 2021-01-13 | Hazard | 80501410 | DKY0114703 | 37830350000008 |  | 3309301-VICCO / REDFOX | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hales Br. Red Fox, Ky. | 2021-10-22
2021 | 2021-01-14 | Hazard |  |  | 37830345C00361 |  | 3309002-JEFF / JEFF | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Anchor and guy needs too be installed, pole leaning, to back up tap. | Kenmont Rd., Jeff, Ky.
2021 | 2021-01-14 | Hazard | 80341940 | DKY0114840 | 37830345D00032 |  | 3309003-JEFF / VIPER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | River Rd. Jeff, Ky.
2021 | 2021-01-15 | Hazard |  |  | 37830368000010 |  | 3309003-JEFF / VIPER | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Top set of arms in bad shape, buck pole | Right Forkk Maces Crk. Viper, Ky.
2021 | 2021-01-18 | Hazard |  |  | 37830392000074 |  | 3309003-JEFF / VIPER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Wells Fork, Viper, Ky.
2021 | 2021-01-18 | Hazard |  |  | 37830440000007 |  | 3309003-JEFF / VIPER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Stratton Fork, Viper, KY.
2021 | 2021-01-18 | Hazard | 80822031 | DKY0115368 | 37830440000077 |  | 3309003-JEFF / VIPER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top cut off, needs changed | Stratton Fork, Viper, Ky. | 2022-10-19
2021 | 2021-01-19 | Hazard | 80821728 | DKY0115366 | 37830393B00081 |  | 3309003-JEFF / VIPER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Left Fork Maces Creek Rd, Kentucky 41774, USA
2021 | 2021-01-19 | Hazard | 80340516 | DKY0114611 | 37830393B00086 |  | 3309003-JEFF / VIPER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Middle Fork Maces Creek Rd, Kentucky 41774, USA | 2023-12-07
2021 | 2021-01-19 | Hazard | 80340838 | DKY0114600 | 37830417000014 |  | 3309003-JEFF / VIPER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Left Fork, Maces Creek, Viper, Ky. | 2021-10-01
2021 | 2021-01-19 | Hazard |  |  | 37830417000167 |  | 3309003-JEFF / VIPER | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Road side phase down | Lick Branch, Maces Creek Rd. Viper, Ky.
2021 | 2021-01-19 | Hazard |  |  | 37830417000180 | TRUE | 3309003-JEFF / VIPER | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Conductors down, pole inactive needs removed. | Lick Branch Maces Creek, Viper, Ky.
2021 | 2021-01-19 | Hazard |  |  | 37839394B00159 |  | 3309003-JEFF / VIPER | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Single crossarm bad | Left Fork Maces Creek Rd, Viper, KY 41774, USA
2021 | 2021-01-20 | Hazard |  |  | 37830345A00159 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Fourseam Branch Rd. Hazard, Ky.
2021 | 2021-01-20 | Hazard | 80340360 | DKY0114558 | 37830441000002 |  | 3309003-JEFF / VIPER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Left Fork maces Creek, Viper, Ky. | 2021-10-01
2021 | 2021-01-22 | Hazard | 80341999 | DKY0114843 | 37830320C00048 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Fourseam Buffalo Rd. Hazard, Ky.
2021 | 2021-01-22 | Hazard |  |  | 37830320C00167 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Fourseam Rd. Hazard. Ky.
2021 | 2021-01-22 | Hazard |  |  | 37830320D00144 |  | 3302704-HAZARD / KENMONT | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Pole leaning bad | Fourseam Rd, Hazard, Ky
2021 | 2021-01-25 | Hazard | 80342019 | DKY0114885 | 37830296D40025 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Diablock Rd. Hazard, Ky.
2021 | 2021-01-25 | Hazard |  |  | 37830296D40624 |  | 3302704-HAZARD / KENMONT | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad set of crossarms | Century Circle, Hazard, KY.
2021 | 2021-01-25 | Hazard | 80342040 | DKY0114887 | 37830296D40941 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Christopher Hill Rd. Hazard, Ky.
2021 | 2021-01-25 | Hazard | 80342056 | DKY0114933 | 37830296D40986 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole, narrow driveway near pole | Christopher Rd. Hazard, Ky.
2021 | 2021-01-25 | Hazard |  |  | 37830297000056 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole, r/w bad | Gregory Branch Rd. Hazard, Ky.
2021 | 2021-01-25 | Hazard |  |  | 37830297000057 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Gregory Branch Rd. Hazard, Ky.
2021 | 2021-01-25 | Hazard | 76778103 | DKY0110112 | 37830297000060 |  | 3302704-HAZARD / KENMONT | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Needs secondary guy, pole leaning | Gregory Branch Rd. Hazard, Ky.
2021 | 2021-01-25 | Hazard | 80341971 | DKY0114842 | 37830321A00003 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad leaning pole | Raccoon Creek Rd. Hazard, Ky. | 2022-02-15
2021 | 2021-01-26 | Hazard |  |  | 37830151000061 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 15 Mile Creek, Lost Creek, Ky.
2021 | 2021-01-26 | Hazard |  |  | 37830296C20515 |  | 3302704-HAZARD / KENMONT | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Bad single arm | Locust St. Hazard, Ky.
2021 | 2021-01-26 | Hazard |  |  | 37830296C20529 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Algoma St. Hazard, Ky.
2021 | 2021-01-26 | Hazard |  |  | 37830296C20606 |  | 3302704-HAZARD / KENMONT | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Single crossarm bad, | E Main St. Hazard, Ky.
2021 | 2021-01-26 | Hazard |  |  | 37830296C40548 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Ashley’s St. Hazard, Ky.
2021 | 2021-01-26 | Hazard |  |  | 37830297000002 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Bad pole | Stormking Rd. Hazard, Ky.
2021 | 2021-01-26 | Hazard | 80341957 | DKY0114841 | 37830297000027 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Stormking Rd. Hazard, Ky.
2021 | 2021-02-02 | Hazard | 80817489 | DKY0115238 | 37830151000001 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Lost Creek, Dice,Ky.
2021 | 2021-02-02 | Hazard | 78759173 | DKY0112678 | 37830151000026 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 16 Mile Creek, Dice, Ky. | 2021-11-09
2021 | 2021-02-03 | Hazard |  |  | 37830151000003 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Lost Creek Rd. Dice. Ky.
2021 | 2021-02-03 | Hazard |  |  | 37830175000010 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad leaning pole | Strong Br. Rd. Dice,Ky.
2021 | 2021-02-03 | Hazard |  |  | 37830175000011 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Strong Br. Rd. Dice, Ky.
2021 | 2021-02-03 | Hazard |  |  | 37830175000063 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Timber Wood Br.Dice, Ky..
2021 | 2021-02-03 | Hazard |  |  | 37830175000067 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Rock House Br. Dice, Ky.
2021 | 2021-02-05 | Hazard |  |  | 37830110B20305 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr | Softshell, Lebrun, Ky.
2021 | 2021-02-05 | Hazard |  |  | 37830134B00008 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr | 310 Possum Trot Rd. Leburn, Ky.
2021 | 2021-02-05 | Hazard |  |  | 37830135000208 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr | Wiley Fk. Leburn, Ky.
2021 | 2021-02-05 | Hazard | 80819614 | DKY0115302 | 37830181D00140 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad secondary pole | Hwy. 550, Hindman, Ky. | 2022-05-18
2021 | 2021-02-05 | Hazard |  |  | 37830182A00008 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire missing and anchor washed out | 1870 Hwy. 550E, Leburn, Ky.
2021 | 2021-02-05 | Hazard |  |  | 37830182A00153 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr | Possum Trot Rd. Leburn, Ky
2021 | 2021-02-05 | Hazard |  |  | 37830182C00133 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH |  | transformers: leaking, damaged |  | KPC | NO | Xfmr leaking oil. 15kva, 7200 | 268 Watts Fork Rd. Leburn, Ky.
2021 | 2021-02-05 | Hazard |  |  | 37830183C00069 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr | Spruce Pine Rd. Garner,Ky.
2021 | 2021-02-05 | Hazard |  |  | 38831083C20148 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Hurst Ln. Jackson, Ky
2021 | 2021-02-05 | Hazard |  |  | 38831083C40152 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Hurst Ln. Jackson, Ky.
2021 | 2021-02-05 | Hazard |  |  | 38831083C40201 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole split, needs changed | Washington Ave. Jackson, Ky.
2021 | 2021-02-05 | Hazard | 80822311 | DKY0115392 | 38831083D30063 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Armory Dr. Jackson, Ky. | 2023-08-07
2021 | 2021-02-05 | Hazard |  |  | 38831083D30347 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Quicksand Rd. Jackson, Ky.
2021 | 2021-02-05 | Hazard | N/A |  | 38831083D40662 |  | 3308001-JACKSON / S.JACKSON | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Need to remove 1/0 sec and two poles. 1083-72 and 1083-73 | Kings Branch Rd. Jackson, Ky. | 2023-07-14
2021 | 2021-02-05 | Hazard |  |  | 38831084A00183 |  | 3308002-JACKSON / PANBOWL | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Crossarms bowed | Hwy. 15S, Jackson, Ky.
2021 | 2021-02-05 | Hazard |  |  | 38831107000067 |  | 3309902-SLEMP / LEATHERWOOD | Service Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr. | Fire Trail Rd. Stray Br. Jackson,Ky.
2021 | 2021-02-05 | Hazard | 72794754 | DKY0104303 | 38831108A00154 |  | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Lick Br. Armory Dr. Jackson, Ky. | 2023-04-06
2021 | 2021-02-05 | Hazard | 72794754 | DKY0104303 | 38831108A00155 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Lick Br. Armory Dr. Jackson, Ky. | 2023-04-06
2021 | 2021-02-08 | Hazard |  |  | 37830540000016 |  | 3309901-SLEMP / DEFEATED CREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove ina tap off pole 540-16, remove pole 540-40 and xfmr. Arms twisted could cause outage | 2656 Defeated Creek, Line Fork
2021 | 2021-02-08 | Hazard |  |  | 38831036000009 | TRUE | 3308002-JACKSON / PANBOWL | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive line needs removed, remove pole 1036-104 and 1036-103 and inactive xfmr.
2021 | 2021-02-08 | Hazard |  |  | 38831036000020 |  | 3308002-JACKSON / PANBOWL | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Need to remove open secondary and secondary pole and inactive xfmr | Birch Ln. Jackson, Ky.
2021 | 2021-02-08 | Hazard |  |  | 38831059D00039 |  | 3308002-JACKSON / PANBOWL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 261 Jett Dr. Jackson, Ky.
2021 | 2021-02-08 | Hazard | 80822170 | DKY0115370 | 38831059D00101 |  | 3308002-JACKSON / PANBOWL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad secondary pole | Jett Dr. Jackson, Ky. | 2022-03-29
2021 | 2021-02-08 | Hazard |  |  | 38831059D00130 |  | 3308002-JACKSON / PANBOWL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten pole | Collier Avenue, Jackson, Ky.
2021 | 2021-02-08 | Hazard |  |  | 38831083C30571 |  | 3308002-JACKSON / PANBOWL | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | 1/0 lash low over parking lot entrance | Jett Dr. Jackson, Ky.
2021 | 2021-02-08 | Hazard | 80822228 | DKY0115371 | 38831083C30838 |  | 3308002-JACKSON / PANBOWL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad secondary pole | 35 Collier Avenue, Jackson, Ky. | 2022-03-29
2021 | 2021-02-23 | Hazard | N/A |  | 37830272B30379 |  | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | L and N Drive, Hazard, Ky. | 2023-06-01
2021 | 2021-02-23 | Hazard |  |  | 37830493000029 |  | 3309901-SLEMP / DEFEATED CREEK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral down, cross creek. | Defeated Creek, Line Fork
2021 | 2021-02-24 | Hazard |  |  | 37830272A30644 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | River Rd. Hazard, Ky.
2021 | 2021-02-24 | Hazard |  |  | 37830272A40398 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Elizabeth Street, Hazard, Ky.
2021 | 2021-02-24 | Hazard |  |  | 37830272A40643 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | River Rd. Hazard, Ky.
2021 | 2021-02-24 | Hazard |  |  | 37830272A40685 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Alias Rd. Hazard, Ky.
2021 | 2021-02-24 | Hazard | 80342159 | DKY0114893 | 37830272C30899 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole cut off, needs changed | Docks Hollow Rd. Upper Second Creek | 2023-09-28
2021 | 2021-02-24 | Hazard |  |  | 37830273B00080 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Holland Dr. Walkers Br. Rd. Allias , Ky.
2021 | 2021-02-25 | Hazard | 66156034 | DKY0095946 | 37830248B00199 |  | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Upper Second Creek, Hazard, Ky. | 2022-12-30
2021 | 2021-02-25 | Hazard |  |  | 37830248D00237 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten at top | Docks Hollow Rd. Upper Second Creek
2021 | 2021-02-25 | Hazard |  |  | 37830273A00042 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole split at top | Upper Second Creek Rd, Hazard, Ky
2021 | 2021-02-25 | Hazard |  |  | 37830273B00071 | TRUE | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Upper Second Crk. Hazard, Ky
2021 | 2021-02-25 | Hazard |  |  | 37830273C00025 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES |  | High Rock Rd. Upper Second Creek
2021 | 2021-02-25 | Hazard | N/A |  | 37830273C10324 |  | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Guys needs repulsed and pole needs straightened. | High Rock Rd. Upper Second Creek | 2023-06-02
2021 | 2021-02-25 | Hazard |  |  | 37830273D00032 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | High Rock Rd. Upper Second Creek
2021 | 2021-02-25 | Hazard |  |  | 37830273D00037 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pad pole | High Rock Rd. Upper Second Creek
2021 | 2021-02-25 | Hazard |  |  | 37830296B10356 |  | 3300602-BLUEGRASS / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Messer 👀Branch Rd. Hazard, Ky.
2021 | 2021-02-26 | Hazard |  |  | 37830295D00093 |  | 3300602-BLUEGRASS / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NO | Bad pole | Messer Branch Rd. Hazard, Ky.
2021 | 2021-03-05 | Hazard | 85183113 | DKY0121298 | 37830247B01139 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad top arms, rotten, split. | Roy Campbell Dr. Hazard, Ky
2021 | 2021-03-05 | Hazard |  |  | 37830272B40004 |  | 3300602-BLUEGRASS / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Starting to rott at ground level | Broadway St, Hazard, KY 41701, USA
2021 | 2021-03-05 | Hazard |  |  | 37830272B40044 |  | 3300602-BLUEGRASS / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten at top | Eversole St, Hazard, KY 41701, USA
2021 | 2021-03-05 | Hazard |  |  | 37830272B40094 | TRUE | 3300602-BLUEGRASS / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten at ground level | Cedar St, Hazard, KY 41701, USA
2021 | 2021-03-05 | Hazard |  |  | 3783o272B40073 |  | 3300602-BLUEGRASS / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Hall Street, Hazard, Ky.
2021 | 2021-03-09 | Hazard | 80819883 | DKY0115311 | 37830200B00156 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Harveyton Rd. Bonnyman, Ky. | 2022-05-04
2021 | 2021-03-09 | Hazard | 80820344 | DKY0115312 | 37830222D00168 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Oak Point Ln. Flat Gap, Bonnyman, Ky. | 2022-06-13
2021 | 2021-03-09 | Hazard | 80820478 | DKY0115294 | 37830223B00012 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole split at top | Harveyton Rd. Hazard, Ky. | 2022-11-11
2021 | 2021-03-09 | Hazard | 80820568 | DKY0115296 | 37830223B00014 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole in a slide | Harveyton Rd. Bonnyman, Ky. | 2022-11-08
2021 | 2021-03-09 | Hazard |  |  | 37830247B00576 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Buckarm pole, arms in bad shape | Village Dr. Hazardd, Ky. | 2023-06-23
2021 | 2021-03-10 | Hazard |  |  | 37830198C00044 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Single arm bad | Deesaundra Dr. Grapevine, Ky.
2021 | 2021-03-10 | Hazard | 80819824 | DKY0115277 | 37830198C00084 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole leaning bad | Deesaundra Dr. Grapevine, Ky. | 2023-10-03
2021 | 2021-03-10 | Hazard | 80820215 | DKY0115271 | 37830222B00047 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Lower Pigeon Roost Rd. Bonnyman, Ky. | 2022-05-25
2021 | 2021-03-10 | Hazard | 80820284 | DKY0115297 | 37830222D00103 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Flat Gap Rd. Bonnyman, Ky. | 2022-06-16
2021 | 2021-03-10 | Hazard |  |  | 37830247C00364 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten pole | Crawford Mt. Combs, Ky.
2021 | 2021-03-11 | Hazard | 80820743 | DKY0115317 | 37830224A00431 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole in slide | Pinecone Rd. Hazard, Ky. | 2023-01-30
2021 | 2021-03-11 | Hazard |  |  | 37830238A00750 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole been cut off | Noah Sizemore Hill Rd. Combs, Ky.
2021 | 2021-03-11 | Hazard |  |  | 37830248A00163 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten at ground level | Meadow rook Rd. Combs, Ky.
2021 | 2021-03-11 | Hazard |  |  | 37830248A00344 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Sumac Ave. Combs, Ky
2021 | 2021-03-11 | Hazard |  |  | 37830248A00489 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten and split at top | Medowbrook Rd. Combs, Ky.
2021 | 2021-03-11 | Hazard | 80455207 | DKY0114634 | 37830248A00674 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarms | Combs Rd. Combs, Ky. | 2023-04-13
2021 | 2021-03-11 | Hazard | 80455207 | DKY0114634 | 37830248A00677 | TRUE | 3301402-COMBS / AIRPORTGA | Line Work | OH | crossarm/braces: broken/split , service: unused or abandoned, blanked meter base |  |  | KPC | NO |  |  | 2023-04-13
2021 | 2021-03-11 | Hazard | 80820863 | DKY0115326 | 37830268000015 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Toulouse Rd,Krypton, Ky. | 2022-12-19
2021 | 2021-03-12 | Hazard |  |  | 37830268000036 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning bad | Toulouse Rd. Krypton, Ky.
2021 | 2021-03-12 | Hazard | 80341919 | DKY0114838 | 37830268000051 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole in bad shape | Toulouse Rd. Krypton, Ky. | 2021-11-23
2021 | 2021-03-12 | Hazard | 80810416 | DKY0115115 | 37830269A00081 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten at ground level | Forked Mouth Rd. Yerkes, Ky. | 2023-05-24
2021 | 2021-03-12 | Hazard | 80816423 | DKY0115134 | 37830269B00076 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Forked Mouth Rd. Yerkes, Ky. | 2023-08-01
2021 | 2021-03-12 | Hazard | 80821388 | DKY0115327 | 37830292000066 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Pepper Rd. Krypton, Ky. | 2022-06-06
2021 | 2021-03-12 | Hazard |  |  | 37830319000051 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Browns Fk. Hazard, Ky.
2021 | 2021-03-12 | Hazard |  |  | 37830319000062 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Browns Fk. Hazard, Ky.
2021 | 2021-03-12 | Hazard |  |  | 38831083C20176 |  | 3308002-JACKSON / PANBOWL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 423 Court St. Jackson, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830223B21197 |  | 3308503-BONNYMAN / BIGCREEK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service laying on communication cable. | Nearway Br. Rd. Combs, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830246B00255 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Ina. Xfmr. | Hwy. 451, Combs, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830246D00086 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning bad | Typo Rd. Bonnyman, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830247B00103 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning. R/w needs cut around pole | Typo Rd. Bonnyman, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830248C00498 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Pole leaning bad, needs straightened or changed out | Lott’s Creek Rd. Bulan, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830268000062 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | remove tap and xfmr | Stidham Grocery Ln. Willard, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830269C00005 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Ina. Xfmr | Big Willard Rd. Busy, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830269C00006 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Ina. Xfmr | Big Willard Rd. Busy, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830269C00097 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove Ina xfmr and secondary and poles | Pump Hollow, Busy, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830269C00172 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | UG |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Pad mount has been broken into, needs removed/ located Willard Elementary School | Big Willard Rd. Busy, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830269C00260 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Ina xfmr and secondary needs removed. | PumpHollow, Busy, Ky.
2021 | 2021-03-15 | Hazard | 85121711 | DKY0120797 | 37830270A00348 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr | Sunlight Ln. Busy Ky. | 2023-07-20
2021 | 2021-03-15 | Hazard |  |  | 37830270A00405 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Ina. Xfmr | Pinebrook Rd. Willard, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830270A30659 |  | 3308503-BONNYMAN / BIGCREEK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Inactive service rolled up on pole | Pinebrook Rd. Willard, Ky.
2021 | 2021-03-15 | Hazard | 80821276 | DKY0115309 | 37830270B30669 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , guys/anchors: broken or missing |  |  | KPC | YES | Pole and guys in a slide, will need to move | Coal Harbor Rd. Avawam, Ky. | 2022-09-22
2021 | 2021-03-15 | Hazard |  |  | 37830270C00047 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Ina xfmr | Hwy. 80, Avawam, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830270D00060 |  | 3308503-BONNYMAN / BIGCREEK | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground missing | W. Ky. Highway 80, Avawam, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830270D00308 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Ina xfmr | Hwy. 80, Avawam, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830271C00077 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Missing guy and anchor | Combs Dr. Combs, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830271C00089 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten pole | Combs Dr. Combs, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830271C00127 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Ina. Xfmr | Bailey St. Combs, KY.
2021 | 2021-03-15 | Hazard |  |  | 37830271C00473 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Ina. Xfmr | Adams Ridge, Combs, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830271C00489 |  | 3308503-BONNYMAN / BIGCREEK | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | 294-C-489, 271-C-1035, 271-C-491, all have missing pole grounds. All behind primary care. | Town and Country Ln. Combs, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830271D00261 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Ina. Xfmr | Ladder Br. Combs, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830271D31053 |  | 3308503-BONNYMAN / BIGCREEK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Removed rolled up service | Little Ln. Combs, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830292000003 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove Ina xfmr and secondary | Stidham Grocery Ln. Toulouse, Ky.
2021 | 2021-03-15 | Hazard | 75739524 | DKY0109106 | 37830293000052 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Ina xfmr | Beech Oak Rd. Willard, Ky. | 2023-10-31
2021 | 2021-03-15 | Hazard |  |  | 37830293000143 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Ina xfmr and secondary needs removed. | Toulouse Rd. Willard, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830294000073 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Ina xfmr and service | Hwy. 80, Avawam, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830294000080 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Ina two pole tap, needs removed. Pole 294-C-328 and 294-C-329, primary down on 329. | Hwy. 80, Avawam, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830294000127 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Ina. secondary pole and secondary needs removed. | Hwy. 80, Avawam, Ky.
2021 | 2021-03-15 | Hazard |  |  | 37830318A00182 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Ina xfmr | Hwy. 80, Avawam, Ky.
2021 | 2021-03-15 | Hazard |  |  | 38831083C10868 |  | 3308002-JACKSON / PANBOWL | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Bad crossarms | Bobcat Ln. Jackson, Ky.
2021 | 2021-03-15 | Hazard |  |  | 38831083C10938 |  | 3308002-JACKSON / PANBOWL | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Post top insulators are busted, needs changed | Hwy. 15 S, Jackson, Ky.
2021 | 2021-03-16 | Hazard |  |  | 37830225D00218 | TRUE | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Grigsby Branch, Bulan, Ky.
2021 | 2021-03-16 | Hazard |  |  | 37830249C00049 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Lotts Creek Rd, Kentucky, USA
2021 | 2021-03-16 | Hazard | 80342321 | DKY0114902 | 37830250A00059 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Clear Fork Rd & Lotts Creek Rd, Kentucky 41701, USA | 2022-12-22
2021 | 2021-03-16 | Hazard | 80342385 | DKY0114892 | 37830250A00060 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Clear Fork Rd & Lotts Creek Rd, Kentucky 41701, USA | 2022-12-27
2021 | 2021-03-16 | Hazard | 80342403 | DKY0114894 | 37830250A00064 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Clear Fork Rd & Lotts Creek Rd, Kentucky 41701, USA | 2022-12-21
2021 | 2021-03-16 | Hazard |  |  | 37830274A10123 |  | 3301402-COMBS / AIRPORTGA | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy needs pulled, pulled out of wrap | Elk Fork Rd. Bulan, Ky.
2021 | 2021-03-17 | Hazard | 80342479 | DKY0115140 | 37830153B00073 | TRUE | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Pigeon Roost Rd. Ary,Ky.
2021 | 2021-03-17 | Hazard | 80535006 | DKY0114772 | 37830299C00114 |  | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Yellow Creek, Kentucky, USA | 2021-11-08
2021 | 2021-03-22 | Hazard | 80815839 | DKY0115237 | 37830128000041 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 476, Ary, Ky.
2021 | 2021-03-22 | Hazard | 80815907 | DKY0115204 | 37830128000044 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 476, Ary, Ky.
2021 | 2021-03-22 | Hazard |  |  | 37830128000050 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  | pole: leaning, burned more than 50% remaining , guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs anchor and guy | Hwy 476, Ary, Ky.
2021 | 2021-03-22 | Hazard | 80815968 | DKY0115172 | 37830130000035 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole bad | Vest Talcum Rd. Talcum, Ky
2021 | 2021-03-23 | Hazard | 80342487 | DKY0115143 | 37830129B00010 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Irish Green Ln. Troublesome Creek | 2023-04-11
2021 | 2021-03-23 | Hazard | 80342503 | DKY0115146 | 37830129B00011 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Troublesome Creek, Ary, Ky
2021 | 2021-03-23 | Hazard |  |  | 37830130000003 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Main line neutral laying on service wire. | Laura Surilda Ln. Ball Fork Rd.
2021 | 2021-03-23 | Hazard |  |  | 37830153C00012 | TRUE | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole 37830153C00012 | Troublesome Creek, Ary, Ky.
2021 | 2021-03-23 | Hazard | 80342459 | DKY0115132 | 37830153D00005 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | YES | Bad pole | Troublesome Creek, Ary, Ky.
2021 | 2021-03-23 | Hazard | 80342426 | DKY0115131 | 37830177C00020 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole split at the top | Troublesome Creek, Ary, Ky | 2022-09-19
2021 | 2021-03-23 | Hazard | 76779279 | DKY0110060 | 37830371000044 | TRUE | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr and cutout | Big Branch Rd. Fusonia, Ky. | 2022-06-22
2021 | 2021-03-25 | Hazard | 80342449 | DKY0114983 | 37830177D00028 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 476, Dwarf, Ky.
2021 | 2021-03-25 | Hazard | 80341469 | DKY0114608 | 37830371000058 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Big Branch Rd. Fusonia, Ky. | 2021-10-15
2021 | 2021-03-25 | Hazard | 80340374 | DKY0114612 | 37830394D00030 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Dykes Branch, Fusonia, Ky. | 2021-09-17
2021 | 2021-03-25 | Hazard |  |  | 37830395000094 | TRUE | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Rem. Inactive xfmr and cutout | Fort Branch, Fusonia, Ky.
2021 | 2021-03-25 | Hazard |  |  | 37830418C20360 |  | 3301701-DAISY / DAISY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Low wire needs resagged | Stoney Bump Ln. Pratt Mt. Fusonia, Ky.
2021 | 2021-03-25 | Hazard |  |  | 37830419A00171 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Ina. conductor cut and stapled to pole | Open Doors Children’s Home, Cornettsville, Ky.
2021 | 2021-03-25 | Hazard | 80340614 | DKY0114606 | 37830419A00243 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 274 Klenco Rd. Cornettsville, Ky. | 2021-09-24
2021 | 2021-03-25 | Hazard | 76779178 | DKY0110231 | 37830444000106 | TRUE | 3301701-DAISY / DAISY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive xfmr and secondary and secondary pole. Secondary pole broke and 1/0 lash down needs removed | Hoot Owl Hollow, line Fork, Cornettsville, Ky. | 2022-03-21
2021 | 2021-03-25 | Hazard |  |  | 37830444B30186 |  | 3301701-DAISY / DAISY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Conductors need resagged | Hoot Owl Hollow, line Fork, Cornettsville, Ky.
2021 | 2021-03-25 | Hazard |  |  | 37830492000038 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive xfmr and service hanging down pole | Bates Fork, Line Fork, Cornettsville, Ky.
2021 | 2021-03-25 | Hazard |  |  | 37830493000037 |  | 3301701-DAISY / DAISY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Low wires on both sides of pole | Big Branch, line Fk. Cornettsville, Ky.
2021 | 2021-03-29 | Hazard | 80819989 | DKY0115310 | 37830201B00032 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 7513 Hwy 476, Dwarf, Ky.
2021 | 2021-03-29 | Hazard | 80342422 | DKY0114975 | 37830201C00093 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Bad leaning pole | Combs Branch, Dwarf, Ky.
2021 | 2021-03-29 | Hazard | 80342414 | DKY0114972 | 37830201C00095 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Combs Branch, Dwarf, Ky. | 2023-02-14
2021 | 2021-03-29 | Hazard |  |  | 37830225B00047 | TRUE | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Vermillion Dr. Hardburly, Ky.
2021 | 2021-03-30 | Hazard |  |  | 3783-225C40555 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Secondary pole leaning bad | Groundhog Hollow, Hardburly, Ky.
2021 | 2021-03-30 | Hazard |  |  | 37830225A00294 | TRUE | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Tribbey Camp Rd. Tribbey, Ky.
2021 | 2021-03-30 | Hazard |  |  | 37830225B00242 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Shady Crossing Ln. Hardburly, Ky.
2021 | 2021-03-30 | Hazard |  |  | 37830225C00316 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Secondary pole leaning | Groundhog Hollow, Hardburly, Ky.
2021 | 2021-03-30 | Hazard |  |  | 37830225D00137 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy and anchor needs to be installed | Salyers Ln. Hardburly, Ky.
2021 | 2021-03-30 | Hazard |  |  | 37830225D00181 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten ground level | Groundhog Hollow, Hardburly, Ky.
2021 | 2021-04-01 | Hazard |  |  | 37830273D00033 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | High Rock Rd. Upper Second Crk. Hazard, Ky.
2021 | 2021-04-05 | Hazard | 80819530 | DKY0115240 | 37830176000033 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Lost Creek Rd, Lost Creek, Ky
2021 | 2021-04-05 | Hazard |  |  | 37830176000046 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning | Mahogany Hill Dr. Lost Creek, Ky.
2021 | 2021-04-05 | Hazard |  |  | 37830176000118 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Conductors need resagged on single phase | Mahogany Hill Dr. lost Creek, Ky.
2021 | 2021-04-05 | Hazard |  |  | 37830176000140 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive one pole tap needs removed | Maple Branch, Lost Creek, Ky.
2021 | 2021-04-05 | Hazard |  |  | 37830200A00093 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten | Engle Hollow, Lost Creek, Ky.
2021 | 2021-04-05 | Hazard |  |  | 37830200C00078 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy loose pole leaning | Bowling Trl. Lost Creek, Ky
2021 | 2021-04-05 | Hazard |  |  | 37830220000001 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad set of crossarms | Krypton Napfor Rd. Krypton, Ky. | 2023-03-17
2021 | 2021-04-19 | Hazard |  |  | 37830172B00003 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning | Ky. Hwy. 451, Krypton, Ky.
2021 | 2021-05-03 | Hazard |  |  | 37830296C21094 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 05/03/2021 - pole reported as reject in 2019 by GeoForce - moving to CKT DEFECT TRACKER to allow for retiring asset pole Smartsheet - can not locate work order to replace this pole - needs work order written up - thanks, PRB | Hank Street,Hazard,Ky. | 2021-10-25
2021 | 2021-05-17 | Hazard | 80817644 | DKY0115236 | 37830172B00010 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy. 451, Chavies, Ky. | 2023-09-18
2021 | 2021-06-01 | Hazard | N/A |  | 37830123000090 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning bad | Hwy. 1110, Altro, Ky. | 2023-06-21
2021 | 2021-06-01 | Hazard |  |  | 37830172B00003 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning bad | Hwy. 451 Chavies, Ky.
2021 | 2021-06-01 | Hazard | 80817593 | DKY0115239 | 37830172B00008 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy. 451 Chavies, Ky. | 2023-09-18
2021 | 2021-06-01 | Hazard | 75659381 | DKY0108243 | 37830172B00115 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy. 451 Chavies, Ky.
2021 | 2021-06-01 | Hazard | 80819718 | DKY0115303 | 37830196D00143 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy. 451, Chavies, Ky. | 2022-05-05
2021 | 2021-06-02 | Hazard | 80817066 | DKY0115170 | 37830146000011 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Susan Turner Ln. Bowling Crk. Rd. Altro, Ky. | 2023-02-24
2021 | 2021-06-03 | Hazard |  |  | 37830194000095 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Primary and neutral needs resagged. | Stable Fork Rd. Chavies, Ky.
2021 | 2021-06-04 | Hazard |  |  | 37830323C00413 | TRUE | 3309302-VICCO / JEFF | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Lash laying on communication cable | Yellow Crk. Rd. Sassafras, Ky.
2021 | 2021-06-11 | Hazard | N/A |  | 37830108000116 |  | 3420001-SOFT SHELL / VEST | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Rec. pole leaning needs straightened | Hwy. 1087, Vest, Ky. | 2023-09-22
2021 | 2021-06-23 | Hazard |  |  | 37830248D00225 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Arm bad | 1437 Upper 2nd Creek Rd, Hazard, KY 41701, USA
2021 | 2021-06-23 | Hazard | 80341871 | DKY0114738 | 37830302C00061 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 1085 Burgeys Creek Rd, Mallie, KY 41836, USA | 2021-10-15
2021 | 2021-06-24 | Hazard |  |  | 37830230A00035 | TRUE | 3308402-BECKHAM / CARRSFORK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | We have a 2 pole tap off this pole, that has wire down and isolated but line runs over customers building. Looks like they have graded a house site. | KY-160, Hindman, KY, USA
2021 | 2021-06-24 | Hazard |  |  | 37830230A00172 | TRUE | 3308402-BECKHAM / CARRSFORK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Arms in bad condition | KY-160, Hindman, KY, USA
2021 | 2021-06-24 | Hazard | 80341919 | DKY0114838 | 37830279000051 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 720 Steer Fork Rd, Mallie, KY 41836, USA | 2021-11-23
2021 | 2021-06-28 | Hazard |  |  | 37830126000003 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten ground level, bad shape, angle pole | Lost Creek Rd. Lost Creek, Ky.
2021 | 2021-06-28 | Hazard |  |  | 37830126000004 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | bad pole | Lost Creek Rd. Lost Creek, Ky.
2021 | 2021-06-28 | Hazard |  |  | 37830174A00092 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Line inactive, needs removed | Pads Branch Rd. Grapevine, Ky.
2021 | 2021-06-29 | Hazard | 80817724 | DKY0115267 | 37830172C00147 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Denton Park Dr. Chavies, Ky. | 2022-05-13
2021 | 2021-06-29 | Hazard | 85182781 | DKY0121110 | 37830196D00032 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarms | Firehouse Ln. Krypton, Ky.
2021 | 2021-06-29 | Hazard | 82952069 | DKY0117612 | 37830197000012 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning bad, about 70 ft. On hill above road | Krypton Napfor Rd. Krypton, Ky. | 2023-03-17
2021 | 2021-06-29 | Hazard |  |  | 37830197000108 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarms are bad | Campbell Bend, Meadow Br. Rd. Krypton, Ky.
2021 | 2021-06-29 | Hazard |  |  | 37830220000100 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Needs to resag or natal pole for clearance | Gunner Br. Krypton, Ky.
2021 | 2021-06-29 | Hazard | 85182822 | DKY0121209 | 37830220000117 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarm | Krypton Napfor Rd. Krypton, Ky.
2021 | 2021-06-29 | Hazard |  |  | 37830221000176 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral needs to be resagged | Collins Road, Krypton, Ky.
2021 | 2021-06-30 | Hazard | 80817239 | DKY0115205 | 37830148000013 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole. 70ft from roadway | Barker Bend Rd. Chavies, Ky. | 2022-07-14
2021 | 2021-07-01 | Hazard | 80817153 | DKY0115261 | 37830147000016 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | bad pole. Deadend needs cut and inactive line needs removed. | Davidson And Stidham Drive, Chavies, Ky. | 2022-06-06
2021 | 2021-07-02 | Hazard | 80817343 | DKY0115201 | 37830148000025 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Barwick Rd. Chavies, Ky | 2022-06-29
2021 | 2021-07-12 | Hazard |  |  | 38831083C40243 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten ground level | Main St, Jackson, KY 41339, USA
2021 | 2021-07-12 | Hazard | 80822311 | DKY0115392 | 38831083D30063 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs a guy breaker installed, goes over top xfmr riser | Armory Dr, Jackson, KY 41339, USA | 2023-08-07
2021 | 2021-07-13 | Hazard | N/A |  | 38831107000078 |  | 3308001-JACKSON / S.JACKSON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning may need guy. | Lick Branch Armory Rd. Jackson, Ky. | 2023-07-20
2021 | 2021-07-13 | Hazard |  |  | 38831108A00319 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten at ground level | Lick Branch & Armory Dr, Kentucky 41339, USA
2021 | 2021-07-13 | Hazard | 80822364 | DKY0115372 | 38831108A00320 |  | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole, shows on map to be new pole but it’s not. | Lick Branch & Armory Dr, Kentucky 41339, USA | 2022-12-09
2021 | 2021-07-15 | Hazard | 80035299 | DKY0114128 | 37830348B00096 |  | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten, bad shape | Big Branch Rd. Vicco, Ky. | 2021-08-25
2021 | 2021-07-20 | Hazard | N/A |  | 37830373000076 |  | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Wrong pole # in 2021… Pole top pin twisted and split top of pole, may be able to lower conductor? | Carcassonne Rd. Blackey, ky | 2023-08-08
2021 | 2021-07-20 | Hazard | N/A |  | 37830373000124 |  | 3309302-VICCO / JEFF | Line Work | OH |  | pole: leaning, burned more than 50% remaining | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole leaning, tree has fallen laying against pole. Tree needs removed before pole corrected. | Bull Crk. Rd. Vicco, Ky. | 2023-08-08
2021 | 2021-07-22 | Hazard | N/A |  | 37830347D00181 |  | 3309302-VICCO / JEFF | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Anchor washed out | Left Fork Georges Br. Vicco, Ky. | 2023-08-02
2021 | 2021-07-22 | Hazard |  |  | 37830419C00250 | TRUE | 3309302-VICCO / JEFF | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral low over road, needs resagged, primary and neutral. Last tap to right before end of line, bull Crk. 37830419C00250 | Bull Creek Rd, Cornettsville, KY 41731, USA
2021 | 2021-07-23 | Hazard | 80341539 | DKY0114742 | 37830347D00180 | TRUE | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Left Fork Georges Branch Rd, Kentucky 41773, USA
2021 | 2021-07-23 | Hazard | N/A |  | 37830371000036 |  | 3309302-VICCO / JEFF | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Clearance over roof of house, neutral 3 to 4 ft off edge of roof. Plus service laying on telephone cables. No clearance. | Georges Branch Rd, Kentucky 41773, USA | 2023-08-02
2021 | 2021-07-23 | Hazard | 80340526 | DKY0114747 | 37830371000038 |  | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Georges Branch Rd, Kentucky 41773, USA | 2023-02-02
2021 | 2021-07-26 | Hazard | 80341936 | DKY0114839 | 37830346A00148 |  | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Arrow Wood Drive, Happy, Ky. | 2021-10-09
2021 | 2021-07-28 | Hazard | N/A |  | 37830426C00462 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Bad single arm | Hwy. 19N, Mayking, Ky. | 2023-08-17
2021 | 2021-09-20 | Hazard | 80577913 | DKY0114829 | 37830230B00013 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | YES | Lash laying on top of other lash, could cause outage. Las on top needs resagged | KY-160, Kentucky, USA | 2021-10-05
2021 | 2021-09-20 | Hazard | 80571104 | DKY0114819 | 37830230B00027 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole looks like it’s broken at xfmr | KY-160, Kentucky, USA | 2021-09-30
2021 | 2021-09-20 | Hazard | 80578259 | DKY0114831 | 37830230B00097 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Sec. pole rotten | KY-160, Kentucky, USA | 2021-10-06
2021 | 2021-09-27 | Hazard | 82712311 | DKY0117503 | 37830184A00041 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Onion Blade Br. Pippa Passes, Ky. | 2022-12-27
2021 | 2021-09-27 | Hazard | 74341406 | DKY0106415 | 37830208000020 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole leaning bad | Hollybush Rd. -Pippa Passes, Ky. | 2022-03-17
2021 | 2021-09-27 | Hazard |  |  | 37830208D10226 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Old coal company line has come off pole and laying on our span guy.. near head. | Hawk Rd. Pippa Passes, Ky.
2021 | 2021-09-28 | Hazard |  |  | 37830108000085 | TRUE | 3420001-SOFT SHELL / VEST | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Middle phase pulled off insulator | 150 Vest Talcum Rd. Vest, Ky.
2021 | 2021-09-28 | Hazard | 85586707 | DKY0121686 | 37830109000024 | TRUE | 3420001-SOFT SHELL / VEST | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Yellow Mt. Rd. Vest, ky. | 2023-12-20
2021 | 2021-09-28 | Hazard | 84329635 | DKY0119429 | 37830133000077 |  | 3420001-SOFT SHELL / VEST | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Vest Talcum Rd. Vest, Ky. | 2023-02-20
2021 | 2021-10-21 | Hazard |  |  | 37830313000020 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  |  | KPC | NO | Remove inactive transformer and secondary pole.
2021 | 2021-10-21 | Hazard |  |  | 37830313000046 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2021-11-18
2021 | 2021-10-21 | Hazard | 84336724 | DKY0119455 | 37830336000037 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2021 | 2021-10-21 | Hazard | 85680125 |  | 37830337000034 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2021 | 2021-10-21 | Hazard |  |  | 37830337000042 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  |  | KPC | NEEDS ADDITIONAL CHECK | Several spans of wire down between 337-42 and 337-52. Line is dead. Customer at end of line says they will not need power back. Need tech to look at writing retirement job up. All manual
2021 | 2021-10-21 | Hazard |  |  | 37830337000053 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  |  | KPC | NO | Pole needs retired. Tech required to look at job.
2021 | 2021-10-21 | Hazard | 82592771 | DKY0117888 | 37830361000041 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2023-12-28
2021 | 2021-10-21 | Hazard | 82592632 | DKY0118196 | 37830361000047 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2021 | 2021-10-21 | Hazard | 86177775 | DKY0122381 | 37830361000050 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Manual across creek
2021 | 2021-10-21 | Hazard |  |  | 37830361000133 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Manual under roadway
2021 | 2021-10-21 | Hazard | 84339406 | DKY0119464 | 37830361000136 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2021 | 2021-10-21 | Hazard | 85788672 | DKY0122695 | 37830361000139 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  |  | KPC | YES | Pole is leaning bad and needs guy wire or pole replaced. Tech required to look at
2021 | 2021-10-21 | Hazard | N/A |  | 37840336000034 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Pole is rigged to were bird constantly get into guy wire and blow transformer fuse. Needs 8 ft breaker installed |  | 2023-10-26
2021 | 2021-10-21 | Hazard | 82591313 | DKY0118093 | 37840336000039 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Yard dog when dry. Neutral also down on this pole
2021 | 2021-10-21 | Hazard |  |  | 37840336000042 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  |  | KPC | NO | Pole is manual across Creek. Still has primary attached but needs retired | Whispering pines, Sizerock
2021 | 2021-10-21 | Hazard | 82590961 | DKY0117659 | 37840336000049 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Yard dog access on extremely dry day |  | 2023-08-09
2021 | 2021-10-21 | Hazard | 82590933 | DKY0117800 | 37840336000050 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , guys/anchors: broken or missing , UG conduit: damaged or separated |  |  | KPC | YES | Access through bottom will require yard dog on extremely dry day. | 6787 Hwy 1482 | 2023-08-17
2021 | 2021-10-21 | Hazard |  |  | 37840336000058 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2021 | 2021-10-21 | Hazard | 82591287 | DKY0117583 | 37840336000081 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2023-03-22
2021 | 2021-10-21 | Hazard | 82590865 | DKY0118047 | 37840336000086 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Service coming off pole is to low and pole is rotten. |  | 2023-02-02
2021 | 2021-10-21 | Hazard | N/A |  | 37840336000088 |  | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Wire has been removed from abandoned poles 336-88 and 336-89 are no longer in use and need retired. Will require manual ROW crew to retire. |  | 2023-10-31
2021 | 2021-10-21 | Hazard |  |  | 37840336000115 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  |  | KPC | NEEDS ADDITIONAL CHECK | Customer needs secondary pole added for clearance | 7022 Hwy 1482
2021 | 2021-10-21 | Hazard | 81776202 |  | 37840336000126 |  | 3303903-LESLIE / HALSFORK | Service Work | OH |  |  |  | KPC | NO | Remove service |  | 2022-03-09
2021 | 2021-10-21 | Hazard |  |  | 37840336000136 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | joint use attachments: clearance issues |  |  | Foreign | YES | Cross arm used to gain clearance | Statue Ln, sizerock
2021 | 2021-10-21 | Hazard |  |  | 37840336000143 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  |  | KPC | NO | Needs retired | Rush Creek Rd
2021 | 2021-10-22 | Hazard | 85793765 | DKY0123058 | 37840360000004 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2021 | 2021-10-22 | Hazard | 85793842 | DKY0122812 | 37840360000021 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | ROW will need cut to replace pole
2021 | 2021-10-22 | Hazard | 81776205 | G0000110 | 37840384000001 |  | 3303903-LESLIE / HALSFORK | Service Work | OH |  |  |  | KPC | NO | House knob pulled |  | 2022-03-09
2021 | 2021-10-22 | Hazard | 85793911 |  | 37840384000060 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2021 | 2021-10-22 | Hazard |  |  | 37840384000068 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  |  | KPC | NO | Pole needs removed. Still has primary attached crossing hwy 1482
2021 | 2021-10-22 | Hazard | 82592803 | DKY0118109 | 37840384000096 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole split out
2021 | 2021-10-22 | Hazard | 82592922 | DKY0117766 | 37840408c00031 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2023-01-17
2021 | 2021-10-22 | Hazard | 85794162 |  | 37840408C00124 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2021 | 2021-10-25 | Hazard | 80578603 | DKY0116742 | 37830242000139 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | Access by boat only |  | KPC | YES | Pole rotten. Located on Buckhorn Lake. Access by boat only. | Buckhorn Lake
2021 | 2021-10-25 | Hazard |  |  | 37830385000021 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2021 | 2021-10-25 | Hazard | 82593945 | DKY0118142 | 37830385000022 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2023-08-07
2021 | 2021-10-25 | Hazard | 84375102 | DKY0119543 | 37830385000088 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2023-03-03
2021 | 2021-10-25 | Hazard |  |  | 37830385000088 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2022-04-27
2021 | 2021-10-25 | Hazard | N/A |  | 37830385000113 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Pole is abandoned and no longer in use |  | 2023-10-23
2021 | 2021-10-25 | Hazard | 82594317 | DKY0117837 | 37830409000024 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole has been severely burned |  | 2023-02-09
2021 | 2021-10-25 | Hazard |  |  | 37830409000026 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | UG conduit: damaged or separated |  |  | KPC | NEEDS ADDITIONAL CHECK | Pole is in slide and conduit has pulled apart on underground secondary.
2021 | 2021-10-25 | Hazard |  |  | 37830410A00057 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2021 | 2021-10-25 | Hazard | 82593783 | DKY0118124 | 37840408a00131 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2023-01-30
2021 | 2021-10-26 | Hazard |  |  | 37830386000031 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Primary pole adjacent to pole 386-25 needs replaced. Pole not listed on map.
2021 | 2021-10-26 | Hazard | 84375146 | DKY0119551 | 37830387B00070 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2023-07-19
2021 | 2021-10-26 | Hazard | 81776219 |  | 37830411000099 |  | 3303903-LESLIE / HALSFORK | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Needs pole ground and ground rod replaced |  | 2022-03-09
2021 | 2021-10-26 | Hazard |  |  | 37830411a10060 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace needs replaced
2021 | 2021-10-27 | Hazard | 82599407 | DKY0117658 | 37830338000082 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2023-02-03
2021 | 2021-10-27 | Hazard |  |  | 37830338000120 |  | 3303903-LESLIE / HALSFORK | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NEEDS ADDITIONAL CHECK
2021 | 2021-10-27 | Hazard |  |  | 37830338000485 |  | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  |  | KPC | NEEDS ADDITIONAL CHECK | Pole has been replaced. Old pole is leaning severely. Customer says we were supposed to remove old pole
2021 | 2021-10-27 | Hazard | 85684361 | DKY0121857 | 37830362000128 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2021 | 2021-10-27 | Hazard | 84309271 | DKY0119459 | 37830362000314 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | YES |  |  | 2023-11-02
2021 | 2021-11-03 | Hazard | 85683992 |  | 37830362000114 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2021 | 2021-11-03 | Hazard | 85684565 | DKY0122403 | 37830362000152 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole located on graveyard. Can get truck with 50 feet of pole but will need mud boards to avoid tearing up grass.
2021 | 2021-11-08 | Hazard | N/A |  | 37830362000136 |  | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  |  | KPC | NO |  |  | 2023-11-03
2021 | 2021-11-11 | Hazard | N/A |  | 37830388a00214 |  | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  |  | KPC | NO |  |  | 2023-10-17

## Ckt Defects Reported 2022 HAZ
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2022 | 2022-01-05 | Hazard |  |  | 37830206B00114 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove unused xfmr | Gus Hays path
2022 | 2022-01-05 | Hazard |  |  | 37830296A40594 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | This pole has a large hole in it at ground level. I took a screw drive and dug out rotten wood towards the center of the pole.
2022 | 2022-01-05 | Hazard |  |  | 37830296C10254 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , joint use attachments: clearance issues |  |  | Foreign | NO | We have 1/0 lash on this pole that needs to be re-sagged. Our conductors are below telephone drops. On the opposite side of this pole, the neutral is below a span guy.
2022 | 2022-01-05 | Hazard |  |  | 37830296c10406 |  | 3302703-HAZARD / HAZARD | Line Work | OH |  |  |  | Foreign | NO | Blown fuse on a capacitor bank at this location and a hold tag on the control. I’m assuming this is offline.
2022 | 2022-01-05 | Hazard |  |  | 37830296C10425 | TRUE | 3302703-HAZARD / HAZARD | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Stolen pole ground
2022 | 2022-01-05 | Hazard |  |  | 37830296C10817 |  | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , joint use attachments: clearance issues | pole: leaning, burned more than 50% remaining |  | Foreign | YES | This pole has been washed out around for some time. It is leaning towards a fence and has 4/0 secondary close to another homes roof.
2022 | 2022-01-05 | Hazard |  |  | 37830296C10820 | TRUE | 3302703-HAZARD / HAZARD | Forestry | OH |  |  | Forestry - Numerous requests for an outage to complete this work was denied in 2020. Forestry will complete this work when the line/service group decides it is convenient for them to assist us with taking an outage. | Foreign | NO | This pole is covered to the top in vines and there are trees in the adjacent span in open wire secondary. | 159 Woodland St, Woodland Park
2022 | 2022-01-05 | Hazard | N/A |  | 37830296C10926 |  | 3302703-HAZARD / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive XFMR at this location. |  | 2023-12-19
2022 | 2022-01-05 | Hazard | 81739430 |  | 37830296C11352 |  | 3302703-HAZARD / HAZARD | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Stolen pole ground. |  | 2022-03-04
2022 | 2022-01-05 | Hazard | 81739430 |  | 37830296C20397 |  | 3302703-HAZARD / HAZARD | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Stolen pole ground. |  | 2022-03-04
2022 | 2022-01-05 | Hazard |  |  | 37830296C30570 |  | 3302703-HAZARD / HAZARD | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | This is a leaning angle pole with telephone conductors and neither company have guys installed.
2022 | 2022-01-05 | Hazard |  |  | 37830296C30676 | TRUE | 3302703-HAZARD / HAZARD | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Stolen pole ground.
2022 | 2022-01-05 | Hazard |  |  | 37830296C31015 | TRUE | 3302703-HAZARD / HAZARD | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Stolen pole ground.
2022 | 2022-01-06 | Hazard |  |  | 37830205000097 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Repair pole ground | Hwy 160 by Knott co highway dept
2022 | 2022-01-06 | Hazard |  |  | 37830205D00144 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove xfmr and secondary | Cave Branch Rd, Kentucky 41301, USA
2022 | 2022-01-06 | Hazard |  |  | 37830230C00276 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO |  | Pigman br across from Beckham sta
2022 | 2022-01-06 | Hazard |  |  | 37830272B40314 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NEEDS ADDITIONAL CHECK | I sounded this pole with a hammer and it seems to be hallow.
2022 | 2022-01-06 | Hazard | 81739430 |  | 37830272B40323 |  | 3302703-HAZARD / HAZARD | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Stolen pole ground. |  | 2022-03-04
2022 | 2022-01-06 | Hazard | 81696120 |  | 37830272D20739 |  | 3302703-HAZARD / HAZARD | Service Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | This is a manual service going to a house that is falling in. This de-energized service needs to be removed. |  | 2022-02-28
2022 | 2022-01-06 | Hazard |  |  | 37830296A30255 |  | 3302703-HAZARD / HAZARD | Forestry | OH |  |  | Forestry - Trimmed trees away from secondary and cut vines around pole | Foreign | NO | This pole and the adjacent secondary pole are covered in vines and trees and needs to be trimmed out. Looks like this serves abandoned houses but they are still metered. |  | 2022-02-17
2022 | 2022-01-06 | Hazard | 85679682 | DKY0122912 | 37830296A30444 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | This is the pole at the 11th Hour Worship Center on Main St., one pole behind the open point. The first page of info on our maps says that this is a KY Power owned pole but the 4th page says it’s Windstreams. This pole is rotten at ground level. | 59 E MAIN STREET, HAZARD,KY 41701
2022 | 2022-01-06 | Hazard |  |  | 37830296A30730 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | This pole needs to be reworked. A span was removed but a dead-end wasn’t installed. No anchors or ours on this two way deadend pole.
2022 | 2022-01-06 | Hazard | 81739430 |  | 37830296A30754 |  | 3302703-HAZARD / HAZARD | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Stolen pole ground. |  | 2022-03-04
2022 | 2022-01-06 | Hazard |  |  | 37830296A30801 | TRUE | 3302703-HAZARD / HAZARD | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Our secondary is mounted below an inactive telephone drop which is also laying on our conductors.
2022 | 2022-01-06 | Hazard |  |  | 37930229000068 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | 1095 Perkins Madden Rd, Hindman, KY 41822, USA
2022 | 2022-01-07 | Hazard |  |  | 37830272B40343 |  | 3302703-HAZARD / HAZARD | Forestry | OH |  |  | Forestry - Vines were cut around the guy wires and pole | Foreign | NO | This secondary line and the pole itself is covered in large vines and has trees growing into it. This pole needs cleared of vines and a small tree needs to be cut before it damages this secondary. |  | 2022-02-17
2022 | 2022-01-07 | Hazard |  |  | 37830272D10408 |  | 3302703-HAZARD / HAZARD | Forestry | OH |  | conductors: resag no clearance issue, damaged, could cause an outage | Forestry - Outage required, will work when the servicer is available to open the transformer. | KPC | NO | Trees and vines are laying on open wire secondary that is feeding a light. This needs trimmed out before it burns the secondary down. The forestry needs to work with a servicer to de-energize this light wire to safely cut this out. | Skyline Drive and Daniel Drive Intersection | 2022-04-26
2022 | 2022-01-07 | Hazard |  |  | 37830272D10497 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | A guy wire has been cut/removed above the XFMR on this pole and the tail is hanging within 12” of the riser. This tail needs to be either repaired or removed.
2022 | 2022-01-07 | Hazard | N/A |  | 37830272D11021 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | pole: leaning, burned more than 50% remaining | Forestry - DESCRIBE IN COMMENTS | KPC | NO | This is a concrete pole in the driveway to the right of La Citadel that is leaning over the hill and has conductors nearly 12” from touching trees. This pole needs straightened and tree removed before this causes an outage. |  | 2023-12-26
2022 | 2022-01-07 | Hazard |  |  | 37830272D11272 | TRUE | 3302703-HAZARD / HAZARD | Service Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Remove an inactive DD light from this pole that is hanging from its wires. Manual.
2022 | 2022-01-10 | Hazard | 81698487 |  | 37830272D11169 |  | 3302703-HAZARD / HAZARD | Service Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | This is a span of 4/2 feeding a light that was let down for the City to remove a tree but was never put back. This span needs to be re-installed for this light to work. |  | 2022-02-28
2022 | 2022-01-10 | Hazard |  |  | 37830272D40440 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | This is an inactive XFMR above the cell tower site above LD Gormans house. Truck access but may need a tree crew to cut a path. Needs to be dry.
2022 | 2022-01-10 | Hazard |  |  | 37830296A30710 | TRUE | 3302703-HAZARD / HAZARD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Stolen pole ground.
2022 | 2022-01-10 | Hazard |  |  | 37830296C10429 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Two services at this location are touching a roof. It appears that someone installed Christmas lights over one of the services. | 324 E Main St, Hazard, KY 41701, USA
2022 | 2022-01-10 | Hazard | 81699162 |  | 37830296C10590 |  | 3302703-HAZARD / HAZARD | Service Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | This is an inactive service that has had the meter removed. We need to remove this service. |  | 2022-03-01
2022 | 2022-01-10 | Hazard |  |  | 37830296C10592 |  | 3302703-HAZARD / HAZARD | Forestry | OH |  |  | Forestry - Cut/sprayed vines growing on old secondary pole | Foreign | NO | This secondary pole is covered in vines that need to be cleared. |  | 2022-02-17
2022 | 2022-01-11 | Hazard |  |  | 37830156000239 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO
2022 | 2022-01-12 | Hazard | 84331163 | DKY0119438 | 37830205000072 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | By knott co health dept | Amburgey rd hey 550 | 2023-02-21
2022 | 2022-01-12 | Hazard |  |  | 37830205000164 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Push back br
2022 | 2022-01-12 | Hazard | N/A |  | 37830205000226 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Replace or relocate anchor | Hey 550 by cowtown rd | 2023-12-05
2022 | 2022-01-13 | Hazard |  |  | 37830178A00454 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap and XFMR’s, appears manual.
2022 | 2022-01-13 | Hazard | 81845342 |  | 37830178B00176 |  | 3308401-BECKHAM / HINDMAN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen off of this pole that has a capacitor bank. |  | 2022-03-18
2022 | 2022-01-13 | Hazard | N/A |  | 37830178B00224 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | This guy wire is broken that is backing up 1/0 lash that crosses the road. |  | 2023-12-12
2022 | 2022-01-13 | Hazard |  |  | 37830178B00312 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap and XFMR’s. The road looks overgrown so it’s probably manual. The primary crosses HW 550.
2022 | 2022-01-13 | Hazard |  |  | 37830178D00099 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive XFMR and primary tap that crosses HW 550.
2022 | 2022-01-13 | Hazard |  |  | 37830179B00007 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , joint use attachments: clearance issues |  |  | KPC | NO | The cable company has installed conductors and sagged them so tight that our 1/0 lash is below their wires.
2022 | 2022-01-13 | Hazard |  |  | 37830179B00012 |  | 3308401-BECKHAM / HINDMAN | Forestry | OH |  |  | Update on this location...I am working with the customer, and the two spans associated with this location can be worked as normal ROW (three phase). An outage is tentative for the week of Christmas Break Note: The Emmalena School is on this zone. Associated work should be completed by the end of the year (2022). | KPC | NO | Horrible ROW at this location. Trees growing up into the primary with several overhangs above the 3 phase. |  | 2022-11-29
2022 | 2022-01-13 | Hazard | 81846651 |  | 37830179B00215 |  | 3308401-BECKHAM / HINDMAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | This pole ground is loose at least 15 feet up the pole and needs to be secured. |  | 2022-03-18
2022 | 2022-01-13 | Hazard |  |  | 37830179B00217 | TRUE | 3308401-BECKHAM / HINDMAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Stolen/missing pole ground with washed out ground rods.
2022 | 2022-01-13 | Hazard | N/A |  | 37830180000047 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , service: unused or abandoned, blanked meter base |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | I found an open, energized meter base at this location with a separate energized service on the ground. This XFMR bank feeds no other customers so I de-energized this to make it safe. This needs removed ASAP. |  | 2023-12-07
2022 | 2022-01-13 | Hazard |  |  | 37830180000097 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | A unused but energized span of 4/2 secondary that the telephone company has installed lines over top of. This needs to be removed.
2022 | 2022-01-13 | Hazard |  |  | 37830202000164 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive XFMR and secondary pole. If removed, forestry needs to clear vines from the secondary pole.
2022 | 2022-01-14 | Hazard |  |  | 37830131000116 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive XFMR and service.
2022 | 2022-01-14 | Hazard | 81866253 |  | 37830131B20152 |  | 3308401-BECKHAM / HINDMAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Stolen pole grounds on poles 131-152, 155-312, 155-310. |  | 2022-03-22
2022 | 2022-01-14 | Hazard | 81854331 |  | 37830131B20153 |  | 3308401-BECKHAM / HINDMAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Stolen pole ground. |  | 2022-03-21
2022 | 2022-01-14 | Hazard | N/A |  | 37830155000054 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Manual, inactive XFMR. This serves an outdoor light that also appears inactive. |  | 2023-12-15
2022 | 2022-01-14 | Hazard |  |  | 37830155000133 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Inactive XFMR and secondary circuit.
2022 | 2022-01-14 | Hazard |  |  | 37830155000134 |  | 3308401-BECKHAM / HINDMAN | Forestry | OH |  |  | This tap is de-energized just behind the Bearville Market @ pole 155-134 and hasn't been worked due to this fact. | KPC | NO | There isn’t any ROW at this location. Trees are inside of the ROW and growing above the primary. |  | 2022-01-19
2022 | 2022-01-14 | Hazard | N/A |  | 37830155000139 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign | NO | This pole number in the field is 155-144 but appears to be 155-139 on the map. Primary and neutral are extremely close mid span and needs re-sagged. |  | 2023-12-15
2022 | 2022-01-14 | Hazard | N/A |  | 37830155000153 |  | 3308401-BECKHAM / HINDMAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Damaged 1/2 inch guy wire and pre-form. This either needs a new pre-form or replace the entire guy. |  | 2023-12-15
2022 | 2022-01-14 | Hazard |  |  | 37830155A30271 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | This is a manual, inactive XFMR.
2022 | 2022-01-14 | Hazard |  |  | 37830180000018 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Ogden Vest Rd, Kentucky, USA
2022 | 2022-01-14 | Hazard |  |  | 37830204000023 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Lower mill cr knott co
2022 | 2022-01-14 | Hazard |  |  | 37830204000026 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Head of lower mill cr knott co
2022 | 2022-01-14 | Hazard |  |  | 37830204000027 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Head of lower mill cr knott co
2022 | 2022-01-14 | Hazard | N/A |  | 37830228000022 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Cornett rd off big branch | 2023-12-06
2022 | 2022-01-14 | Hazard |  |  | 37830228000043 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Head of lower mill cr
2022 | 2022-01-14 | Hazard | N/A |  | 37830228000047 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Head of lower mill cr | 2023-12-06
2022 | 2022-01-14 | Hazard |  |  | 37830228000112 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  |  | KPC | NO | Need to install a line fuse | Cornett rd off big branch
2022 | 2022-01-14 | Hazard |  |  | 37830229000006 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove step down not in use | Sweet gum br off big br
2022 | 2022-01-14 | Hazard | N/A |  | 37930228000034 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Lower mill cr by calf hollow | 2023-12-06
2022 | 2022-01-18 | Hazard | 78564119 | DKY0112365 | 37380204000094 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | At Big Branch Baptist church | Big Branch Rd, Hindman, KY, USA | 2023-01-12
2022 | 2022-01-18 | Hazard | 82711297 | DKY0117698 | 37830357C00070 |  | 3451202-BEEFHIDE / DUNHAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | Improvement Branch | 2023-04-10
2022 | 2022-01-18 | Hazard |  |  | 37830357C00131 | TRUE | 3451202-BEEFHIDE / DUNHAM | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO
2022 | 2022-01-18 | Hazard |  |  | 37830357C20237 | TRUE | 3451202-BEEFHIDE / DUNHAM | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO
2022 | 2022-01-18 | Hazard |  |  | 37830357D00245 | TRUE | 3451202-BEEFHIDE / DUNHAM | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO
2022 | 2022-01-18 | Hazard | N/A |  | 37830381C00250 |  | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Insulators going bad |  | 2024-01-02
2022 | 2022-01-18 | Hazard | N/A |  | 37830381C00286 |  | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Insulators going bad |  | 2024-01-02
2022 | 2022-01-18 | Hazard |  |  | 37830381C00287 | TRUE | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Bad dead end insulators
2022 | 2022-01-18 | Hazard | N/A |  | 37830381C00288 |  | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Insulators going bad |  | 2024-01-02
2022 | 2022-01-18 | Hazard | 85690253 |  | 37830381C00289 | TRUE | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Insulators going bad
2022 | 2022-01-18 | Hazard | 82711952 | DKY0117717 | 37830381C00295 |  | 3451202-BEEFHIDE / DUNHAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  |  | 2023-12-04
2022 | 2022-01-18 | Hazard | 86298950 |  | 37830381C00299 | TRUE | 3451202-BEEFHIDE / DUNHAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole
2022 | 2022-01-18 | Hazard | 82711480 | DKY0117617 | 37830381C00300 | TRUE | 3451202-BEEFHIDE / DUNHAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2022 | 2022-01-18 | Hazard | 85789012 | DKY0122681 | 37830381C00301 | TRUE | 3451202-BEEFHIDE / DUNHAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole
2022 | 2022-01-18 | Hazard | 82711351 | DKY0117646 | 37830381C00307 | TRUE | 3451202-BEEFHIDE / DUNHAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole
2022 | 2022-01-18 | Hazard | 86299206 |  | 37830381C00330 | TRUE | 3451202-BEEFHIDE / DUNHAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2022 | 2022-01-18 | Hazard | 86299249 |  | 37830381C00331 | TRUE | 3451202-BEEFHIDE / DUNHAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2022 | 2022-01-18 | Hazard | N/A |  | 37830381C00565 |  | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Insulators going bad |  | 2024-01-02
2022 | 2022-01-18 | Hazard |  |  | 37830381C00584 | TRUE | 3451202-BEEFHIDE / DUNHAM | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO
2022 | 2022-01-18 | Hazard |  |  | 37830381C00584 | TRUE | 3451202-BEEFHIDE / DUNHAM | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO
2022 | 2022-01-18 | Hazard |  |  | 37830381C00612 | TRUE | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Bad dead end insulators
2022 | 2022-01-18 | Hazard | 86299150 |  | 37830381C00703 |  | 3451202-BEEFHIDE / DUNHAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2022 | 2022-01-18 | Hazard | N/A |  | 37830381C10791 |  | 3451202-BEEFHIDE / DUNHAM | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO |  |  | 2024-01-02
2022 | 2022-01-18 | Hazard |  |  | 37830381D10498 | TRUE | 3451202-BEEFHIDE / DUNHAM | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Bad dead end insulators
2022 | 2022-01-19 | Hazard | 81879771 |  | 37830179D0062A |  | 3308401-BECKHAM / HINDMAN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Stolen pole ground on a 3 phase recloser pole |  | 2022-03-23
2022 | 2022-01-19 | Hazard |  |  | 37830179D10531 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive XFMR
2022 | 2022-01-19 | Hazard |  |  | 37830179D10532 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive XFMR.
2022 | 2022-01-19 | Hazard |  |  | 37830202000007 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive XFMR in a bottom. Truck access of customer allows.
2022 | 2022-01-19 | Hazard | 81877205 |  | 37830202000020 |  | 3308401-BECKHAM / HINDMAN | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , service: unused or abandoned, blanked meter base |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | This is an inactive service that has been de-energized at the pole but has been removed from the weather dead due to vandalism. |  | 2022-03-23
2022 | 2022-01-19 | Hazard | N/A |  | 37830202000024 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | This single phase recloser appears to be leaking oil next to a small stream. (Mold/mildew not a leak) |  | 2023-12-27
2022 | 2022-01-19 | Hazard |  |  | 37830202000030 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive XFMR next to a Creek, not leaking. Not sure if a bucket truck can reach this from the road or not.
2022 | 2022-01-19 | Hazard |  |  | 37830202000036 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Open line fuse on this pole feeding an inactive tap.
2022 | 2022-01-19 | Hazard | N/A |  | 37830202000039 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | This is a buckarm pole that has had the dead end guys removed. Someone is doing dozer work here and has the path to the pole blocked at this time. |  | 2023-12-27
2022 | 2022-01-19 | Hazard | 81879704 |  | 37830202000045 |  | 3308401-BECKHAM / HINDMAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | This guy wire in a bottom needs a guy marker. |  | 2022-03-23
2022 | 2022-01-19 | Hazard |  |  | 37830202000146 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive XFMR and primary tap that cross the road at this location.
2022 | 2022-01-19 | Hazard | N/A |  | 37830202D10195 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive XFMR here. Needs flaggers if the primary that crosses the road is removed. |  | 2023-12-27
2022 | 2022-01-19 | Hazard | 81879726 |  | 37830202D40248 |  | 3308401-BECKHAM / HINDMAN | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | This is a low 4/2 light wire circuit that someone has tied a rope to and anchored to a fence for clearance on a roof. |  | 2022-03-23
2022 | 2022-01-19 | Hazard |  |  | 37830226000183 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | service: unused or abandoned, blanked meter base |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Open and energized meter base here that I de-energized to make safe. This inactive XFMR needs removed.
2022 | 2022-01-19 | Hazard | N/A |  | 37830226000212 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive XFMR and secondary. |  | 2023-12-27
2022 | 2022-01-19 | Hazard |  |  | 37830227A00051 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Non-leaking, manual, inactive XFMR.
2022 | 2022-01-19 | Hazard |  |  | 37830227A00248 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive XFMR, appears to be manual.
2022 | 2022-01-19 | Hazard |  |  | 37830227B00021 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive XFMR.
2022 | 2022-01-19 | Hazard |  |  | 37830227B00065 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Broken guy wire wrapped around this pole. Needs a new anchor installed.
2022 | 2022-01-19 | Hazard |  |  | 37830227B00067 |  | 3308401-BECKHAM / HINDMAN | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Broken trailer pole at this location with energized secondary on the roof of the house and laying in the yard. I removed the meter and service to make this safe. |  | 2022-01-19
2022 | 2022-01-19 | Hazard |  |  | 37830227B00255 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive XFMR and secondary.
2022 | 2022-01-19 | Hazard | 81879743 |  | 37830227D00076 |  | 3308401-BECKHAM / HINDMAN | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Low service here, just over 6’ from the ground. |  | 2022-03-23
2022 | 2022-01-19 | Hazard |  |  | 37830227D00086 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Non-leaking, inactive XFMR near a stream. Manual.
2022 | 2022-01-19 | Hazard |  |  | 37830227D40279 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive XFMR and primary tap.
2022 | 2022-01-19 | Hazard |  |  | 37830251000130 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive XFMR.
2022 | 2022-01-20 | Hazard |  |  | 37830425B00350 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO |  | Sandlick Creek Rd, Kentucky 41858, USA
2022 | 2022-01-20 | Hazard | 82600118 | DKY0117481 | 37830448C40048 |  | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | Stone Ave, Whitesburg, KY 41858, USA | 2023-07-27
2022 | 2022-01-20 | Hazard |  |  | 37830449A20012 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO |  | Walnut st
2022 | 2022-01-20 | Hazard | 82600296 | DKY0117575 | 37830449A20240 |  | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2022 | 2022-01-20 | Hazard | 82600149 | DKY0117476 | 37830449A20254 |  | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | Pine St, Whitesburg, KY 41858, USA | 2023-05-23
2022 | 2022-01-20 | Hazard | 82600258 | DKY0117508 | 37830449A20255 |  | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | Pine St, Whitesburg, KY 41858, USA | 2023-05-23
2022 | 2022-01-20 | Hazard | 82600401 | DKY0117512 | 37830449A20277 |  | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | Cowan St.
2022 | 2022-01-20 | Hazard |  |  | 37830449A20408 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO |  | Webb St, Whitesburg, KY 41858, USA
2022 | 2022-01-20 | Hazard | 82600362 | DKY0117597 | 37830449A20466 |  | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 2nd street. Whitesburg
2022 | 2022-01-20 | Hazard |  |  | 37830449A20678 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO
2022 | 2022-01-20 | Hazard |  |  | 37830449A21008 | TRUE | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO |  | Walnut St, Whitesburg, KY 41858, USA
2022 | 2022-01-24 | Hazard |  |  | 37830381000727 |  | 3312902-JENKINS / JENKINS | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Repull 1/4 inch guy wire | Raven rock Jenkins
2022 | 2022-01-24 | Hazard |  |  | 37830381B00353 |  | 3312902-JENKINS / JENKINS | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Jenkins, KY, USA
2022 | 2022-01-24 | Hazard |  |  | 37830405a10846 |  | 3312902-JENKINS / JENKINS | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO |  | 3 poles from Jenkins station
2022 | 2022-01-25 | Hazard |  |  | 37830381D40653 |  | 3312902-JENKINS / JENKINS | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO
2022 | 2022-01-25 | Hazard |  |  | 37830405000818 |  | 3312902-JENKINS / JENKINS | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO
2022 | 2022-01-25 | Hazard | 85691117 | DKY0121953 | 37830405C00255 |  | 3312902-JENKINS / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | Jenkins, KY, USA
2022 | 2022-01-25 | Hazard | 85691211 | DKY0122239 | 37830405C00302 |  | 3312902-JENKINS / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES
2022 | 2022-01-26 | Hazard |  |  | 37830358000340 |  | 3312902-JENKINS / JENKINS | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Joes Branch, Jenkins KY
2022 | 2022-01-26 | Hazard |  |  | 37830358000451 |  | 3312902-JENKINS / JENKINS | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Joes Branch, Jenkins, ky
2022 | 2022-01-26 | Hazard |  |  | 37830381C00371 |  | 3312902-JENKINS / JENKINS | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Jenkins, KY, USA
2022 | 2022-01-27 | Hazard | 69851183 | DKY0099998 | 37830353d00078 | TRUE | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES |  |  | 2023-04-12
2022 | 2022-01-27 | Hazard |  |  | 37830377c00080 |  | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES
2022 | 2022-01-27 | Hazard |  |  | 37830377C00128 |  | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES
2022 | 2022-01-27 | Hazard | 85794881 |  | 37830377C00129 |  | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES
2022 | 2022-01-27 | Hazard |  |  | 37830401000336 |  | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO
2022 | 2022-01-27 | Hazard |  |  | 37830401d00249 |  | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO
2022 | 2022-01-27 | Hazard |  |  | 37830425c00156 |  | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO
2022 | 2022-01-27 | Hazard | 85691363 |  | 37830425D00307 |  | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES |  | Crafts Colley Rd, Kentucky, USA
2022 | 2022-02-09 | Hazard |  |  | 37830328000017 |  | 3308601-COLLIER / UPPERROCK | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO |  | Colson Baptist church
2022 | 2022-02-09 | Hazard |  |  | 37830328000710 |  | 3308601-COLLIER / UPPERROCK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO |  | 456 cane br
2022 | 2022-02-09 | Hazard |  |  | 37830352a00349 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Sexton br/ low gap
2022 | 2022-02-10 | Hazard |  |  | 37830329000012 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Fultz rd Thornton rd
2022 | 2022-02-10 | Hazard |  |  | 37830351B00008 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Highway 15
2022 | 2022-02-10 | Hazard | 85138594 | DKY0120820 | 37830353A00005 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Behind 6867 Thornton rd | 2023-06-14
2022 | 2022-02-10 | Hazard |  |  | 37830353A00105 | TRUE | 3308601-COLLIER / UPPERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Top set of crossarms bad. 1979 ATT pole | 6867 thornton rd
2022 | 2022-02-10 | Hazard |  |  | 37830353A00283 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove primary metering | By 6768 Thornton rd
2022 | 2022-02-10 | Hazard |  |  | 37830400A00088 | TRUE | 3308602-COLLIER / LOWERROCK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO |  | 228 cinnamon dr
2022 | 2022-02-11 | Hazard |  |  | 37830351000191 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Nickels Dr
2022 | 2022-02-11 | Hazard |  |  | 37830351C00059 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Hall’s place Hwy 7
2022 | 2022-02-14 | Hazard | 85794958 | DKY0123119 | 37830376C00118 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | YES | Pole is bad, has inactive xfmr, washed out | 540 E Bethany Dr, Allen, TX 75002, USA
2022 | 2022-02-15 | Hazard |  |  | 37830351D00034 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Conductors crossing over the road need removed | Hwy 7, Isom
2022 | 2022-02-15 | Hazard |  |  | 37830351D00300 |  | 3308601-COLLIER / UPPERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | No flaggers needed
2022 | 2022-02-16 | Hazard |  |  | 37830375B00464 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive xfmr | Arthur’s loop
2022 | 2022-02-17 | Hazard |  |  | 37830374000014 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES |  | Doty Creek
2022 | 2022-02-17 | Hazard |  |  | 37830375000437 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Be careful, no pole ground | Arthur’s Loop
2022 | 2022-02-17 | Hazard |  |  | 37830375B00499 |  | 3308602-COLLIER / LOWERROCK | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove service no longer needed | Arthur’s loop
2022 | 2022-02-17 | Hazard |  |  | 37830398B00047 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Mouth of Carbon Glow | Carbon Glow, letcher
2022 | 2022-02-18 | Hazard |  |  | 37830397000042 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES |  | Elk Creek Rd
2022 | 2022-02-18 | Hazard |  |  | 37830397000068 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Single phase line, needs replaced | Elk Crk
2022 | 2022-02-18 | Hazard |  |  | 37830398A00110 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH |  |  |  | Foreign | NO | Need line fuse on tap | Carbon Glow, Caudill Br
2022 | 2022-02-18 | Hazard |  |  | 37830421A20260 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO |  | Hwy 7 just past steel bridge
2022 | 2022-02-18 | Hazard |  |  | 37830421C20104 | TRUE | 3308602-COLLIER / LOWERROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | High Street, Blackey
2022 | 2022-02-21 | Hazard |  |  | 37830339A30196 | TRUE | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO
2022 | 2022-02-21 | Hazard |  |  | 37830388C00442 |  | 3303901-LESLIE / HYDEN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO
2022 | 2022-02-22 | Hazard |  |  | 37830243000072 |  | 3303901-LESLIE / HYDEN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Main line neutral is down and primary is low over road | Opossum Gap Rd
2022 | 2022-02-24 | Hazard |  |  | 37830399000059 |  | 3308603-COLLIER / SMOOTCR | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Please remove unused service | Last trl in bee tree Branch
2022 | 2022-02-24 | Hazard |  |  | 37830400B00020 | TRUE | 3308603-COLLIER / SMOOTCR | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | St Rt 1811
2022 | 2022-02-24 | Hazard |  |  | 37830423000154 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Johnson Frk, Premium
2022 | 2022-02-24 | Hazard |  |  | 37830423C00135 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Bee tree br
2022 | 2022-02-24 | Hazard |  |  | 37830447000179 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Hwy 588 | The Farm Rd
2022 | 2022-02-28 | Hazard |  |  | 37830052000127 | TRUE | 3310502-HADDIX / CANOE | Line Work | OH |  |  | conductors: excessive splices, deteriorated conductors , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Tap needs removed, neutral missing | N Copeland bridge, turn left
2022 | 2022-02-28 | Hazard |  |  | 37830445D30265 |  | 3308603-COLLIER / SMOOTCR | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Old coal company building | Jewel ln, Tolson
2022 | 2022-03-04 | Hazard |  |  | 37830049C20135 |  | 3310502-HADDIX / CANOE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Neutral down, trl burnt | canoe rd
2022 | 2022-03-07 | Hazard |  |  | 37830026000030 |  | 3310502-HADDIX / CANOE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , joint use attachments: clearance issues |  |  | KPC | YES | Telephone is above neutral and inches from primary | Mill Crk, Canoe Rd | 2023-06-23
2022 | 2022-03-07 | Hazard | 82590782 | DKY0117616 | 37830074000057 |  | 3310502-HADDIX / CANOE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Bad pole, needs replaced | Pipe Mudd Rd | 2023-07-27
2022 | 2022-03-08 | Hazard | 82590820 - WR in status 20 on 01/20/23 - per Rob Pigman on 01/19/2-23 - "Pole # 37830121000055 was replaced on or about 8-2-22 during flood work and it is a 45’4 pole. Thank you for all you do." - CANCELLED WR ON 01/20/23 and closed out this defect - prb | N/A | 37830121000055 - sent email on 01/10/23 requesting info on this pole - may already be replaced - prb |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , pole ground: broken or missing - EQUIPMENT GROUND , guys/anchors: broken or missing |  |  | KPC | YES | Pole needs relocated, washed out bad. POLE WASHED AWAY IN FLOOD, ALREADY SET NEW POLE. per Rob Pigman on 01/19/23 - Pole # 37830121000055 was replaced on or about 8-2-22 during flood work and it is a 45’4 pole. Thank you for all you do. - prb | Jct of 315 and 28 | 2023-01-20
2022 | 2022-03-10 | Hazard |  |  | 37840240000034 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is bad, needs replaced | Otter Crk | 2022-03-10
2022 | 2022-03-11 | Hazard |  |  | 37830052000005 |  | 3310502-HADDIX / CANOE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Buck arm pole is leaning bad, guys are washing out | Hwy 1110, copeland bridge
2022 | 2022-03-16 | Hazard |  |  | 37830355D30088 |  | 3401301-FLEMING / NEON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Sec pole is rotten, no number on pole | Neon fire dept
2022 | 2022-03-16 | Hazard |  |  | 37830356B00330 |  | 3401301-FLEMING / NEON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Pole has been struck by tree, needs removed, close to creek | Hwy 343, Fleming Rd
2022 | 2022-03-18 | Hazard |  |  | 37830307D20193 |  | 3401301-FLEMING / NEON | Service Work | OH |  |  | conductors: excessive splices, deteriorated conductors | KPC | NO | Remove service hanging off pole | Morgan Ln
2022 | 2022-03-18 | Hazard | 82710996 | DKY0117684 | 37830355D40010 |  | 3401301-FLEMING / NEON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Main St, Neon
2022 | 2022-03-21 | Hazard |  |  | 37830283000118 |  | 3311401-REEDY / DEANE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr | Long Fork Rd
2022 | 2022-03-22 | Hazard |  |  | 37830282000002 |  | 3311401-REEDY / DEANE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hwy 7, Deane | 2023-02-13
2022 | 2022-03-23 | Hazard |  |  | 37830329000079 |  | 3311401-REEDY / DEANE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Sec pole is broken, lash in trees, cut hot wires on pole, needs removed | Indian Crk Rd, Deane
2022 | 2022-03-29 | Hazard | 77687413 | DKY0111102 | 37830380C00048 | TRUE | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Very bad pole | Potters Frk, Hwy 805
2022 | 2022-03-29 | Hazard |  |  | 37830380D20638 |  | 3401302-FLEMING / MCROBERTS | Service Work | OH |  |  | conductors: excessive splices, deteriorated conductors | KPC | NO | Inactive service on ground needs removed | Head of Ramey Frk, Hammond
2022 | 2022-03-30 | Hazard | 76498093 | DKY0109505 | 37830329000047 | TRUE | 3311401-REEDY / DEANE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole has washed out, next to creek | Hwy 7, close to Ky may dr | 2022-08-25
2022 | 2022-04-01 | Hazard | 81016478 | DKY0115349 | 37830356C00089 WRITTEN TO PROJECT 000007599 - sent email on 01/10/23 requesting info on this pole - may already be replaced - prb |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole has been hit, big chunk missing | Sheas Frk
2022 | 2022-04-01 | Hazard |  |  | 37830356C00126 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Very bad and old, needs replaced | 120 Chopping Branch Rd, McRoberts, KY 41835, USA
2022 | 2022-04-04 | Hazard | 82711272 | DKY0117706 | 37830309000003 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Across crk | LA-343, Louisiana, USA | 2023-05-25
2022 | 2022-04-04 | Hazard |  |  | 37830333000053 - believe this is 37830333A00053 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | State Hwy 343, Arkansas, USA
2022 | 2022-04-04 | Hazard | 82711173 | DKY0117707 | 37830333A00077 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 4129 Hwy 343 | 2023-10-11
2022 | 2022-04-04 | Hazard | 76892658 | DKY0110088 | 37830333B00004 | TRUE | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Very bad pole, heavy xfmr on it, close to hse | 129 Tom Biggs Rd
2022 | 2022-04-04 | Hazard | 76929661 | DKY0110280 | 37830333B00015 | TRUE | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Very bad pole | Tom Biggs Rd
2022 | 2022-04-04 | Hazard | 85689079 | DKY0123256 | 37830379C00440 |  | 3401302-FLEMING / MCROBERTS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotting at base, high traffic area | Hwy 317, behind double quick
2022 | 2022-04-05 | Hazard | 82599875 | DKY0117467 | 37830448C10073 | TRUE | 3309103-WHITESBUR / COWAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | YES | cross arms are bad, pole is old | High street, Whitesburg
2022 | 2022-04-05 | Hazard | 82599849 | DKY0117433 | 37830448C10074 | TRUE | 3309103-WHITESBUR / COWAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | YES | Cross arms are bad, pole is old | High St
2022 | 2022-04-06 | Hazard |  |  | 37830448B00153 |  | 3309103-WHITESBUR / COWAN | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Needs anchor replaced | LA-931, Louisiana, USA
2022 | 2022-04-06 | Hazard | 82599499 | DKY0117376 | 37830448C20099 |  | 3309103-WHITESBUR / COWAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Very bad secondary pole | Antique Ave | 2022-08-25
2022 | 2022-04-07 | Hazard |  |  | 37830472000062 |  | 3309103-WHITESBUR / COWAN | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Lash is lower than phone cable | Hampton Br
2022 | 2022-04-08 | Hazard |  |  | 37830472000073 |  | 3309103-WHITESBUR / COWAN | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Please remove inactive service hanging off pole | Grapevine Br
2022 | 2022-04-11 | Hazard |  |  | 37830519B00059 |  | 3309103-WHITESBUR / COWAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Up on bank out of reach for truck | Jct of 931 and hwy 160
2022 | 2022-04-11 | Hazard |  |  | 37830519C00182 | TRUE | 3309103-WHITESBUR / COWAN | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Please remove inactive service laying on the ground | Woodside Dr
2022 | 2022-04-11 | Hazard |  |  | 37830519D00023 |  | 3309103-WHITESBUR / COWAN | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Need to repair service neutral on this pole | Bo Fork
2022 | 2022-04-13 | Hazard |  |  | 37830307000109 |  | 3401301-FLEMING / NEON | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Need big bucket to install line fuse on this tap | Steven’s Frk, off Hwy 317
2022 | 2022-04-19 | Hazard |  |  | 37830449D10529 |  | 3314401-MAYKING / ERMINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Arms are very bad | Junction of 2034 and 15 , double quick
2022 | 2022-04-21 | Hazard | 82600458 | DKY0117595 | 37830474000005 |  | 3314401-MAYKING / ERMINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole needs replaced | 1.5 miles up Pert Crk | 2023-02-08
2022 | 2022-04-27 | Hazard |  |  | 38831132000139 | TRUE | 3310501-HADDIX / QUICKSAND | Line Work | OH | guys/anchors: broken or missing | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Main line pole needs anchor replaced, stiff angle, heavy telephone | 5339 Hwy 15, Jackson
2022 | 2022-04-29 | Hazard |  |  | 38831110000066 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotton | South Frk Rd, Quicksand
2022 | 2022-04-29 | Hazard |  |  | 38831110000067 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotton | South Frk Rd, Quicksand
2022 | 2022-04-29 | Hazard |  |  | 38831110000068 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotton pole | South Frk Rd, Quicksand
2022 | 2022-04-29 | Hazard |  |  | 38831110000069 | TRUE | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotton | South Frk Rd, Quicksand
2022 | 2022-04-29 | Hazard |  |  | 38831111000033 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotton pole | South Frk Rd, Quicksand
2022 | 2022-05-03 | Hazard | 82590409 | DKY0117362 | 38831061D00098 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Very bad pole | Slate Br, Hwy 30
2022 | 2022-05-03 | Hazard |  |  | 38831111000035 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole needs replaced | South Frk, Quicksand
2022 | 2022-05-03 | Hazard |  |  | 38831111000036 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Across the creek | South Frk, Quicksand
2022 | 2022-05-04 | Hazard |  |  | 38830992000003 |  | 3310501-HADDIX / QUICKSAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten pole | St Rt 30, Gauge
2022 | 2022-05-12 | Hazard | 82262316 | DKY0116933 | 37830355C00483 |  | 3401301-FLEMING / NEON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 2070 Hwy 317 ,Neon,Ky. | 2022-06-07
2022 | 2022-05-19 | Hazard | 82284561 | DKY0117014 | 37830220000115 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad pole | 557 Krypton-Napfor Rd, Krypton, KY 41754, USA | 2023-01-19
2022 | 2022-05-20 | Hazard |  |  | 37830483C00107 |  | 3311101-STINNETT / REDBIRD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Lower Bad Crk Rd
2022 | 2022-05-20 | Hazard |  |  | 37830483D00147 |  | 3311101-STINNETT / REDBIRD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | conductors: resag no clearance issue, damaged, could cause an outage | conductors: excessive splices, deteriorated conductors , other: customer owned attachment | KPC | NO | Neutral is hung under telephone guy | Victory Rd off Greasy Crk
2022 | 2022-05-24 | Hazard |  |  | 37830458000072 |  | 3311101-STINNETT / REDBIRD | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Anchor is gone | Laurel Br Rd
2022 | 2022-05-27 | Hazard |  |  | 37840624000089 |  | 3311101-STINNETT / REDBIRD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Phillips Frk Rd
2022 | 2022-05-31 | Hazard | 82437399 | DKY0117095 | 37830490000067 |  | 3309902-SLEMP / LEATHERWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Replace bad pole | 15 Charlene Ln.,Slemp,Ky | 2022-10-20
2022 | 2022-06-07 | Hazard |  |  | 37830436000048 |  | 3311101-STINNETT / REDBIRD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO |  | Stinnett Wendover Rd
2022 | 2022-06-09 | Hazard |  |  | 37830412B00135 |  | 3311103-STINNETT / WENDOVER | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Need to remove old arms and install new switch | Camp Creek Rd
2022 | 2022-06-16 | Hazard | 82616054 | DKY0117280 | 37830410C00090 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Replace bad pole | 26117 Hwy 421,Hyden | 2022-09-12
2022 | 2022-06-27 | Hazard | 82761306 | DKY0117429 | 37840288000085 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Replace bad pole | Spruce Pine Dr.,Saul,Ky.
2022 | 2022-07-01 | Hazard | 82761306 | DKY0117429 | 37840288000085 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | MANUAL ASSET POLE | Spruce Pine Dr.,Saul,Ky.
2022 | 2022-07-11 | Hazard |  |  | 37830358D00112 |  | 3409503-BURDINE / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole needs replaced | 77 Number 1 Hill
2022 | 2022-07-13 | Hazard |  |  | 37830405A10517 |  | 3312902-JENKINS / JENKINS | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Braces are there but not attached | Gateway Industrial Park Rd
2022 | 2022-07-14 | Hazard | 82859626 | DKY0117532 | 37830350000016 |  | 3309301-VICCO / REDFOX | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 186 Horseshoe Bend Rd.,Redfox,Ky. | 2022-11-03
2022 | 2022-07-19 | Hazard |  |  | 37830413000355 | TRUE | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr | Coon crk rd | 2022-07-19
2022 | 2022-07-19 | Hazard |  |  | 37830413B00092 |  | 3303902-LESLIE / WOOTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Under road | Big Br Rd
2022 | 2022-07-19 | Hazard |  |  | 37830413D00088 |  | 3303902-LESLIE / WOOTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Need to re-pull guy and re-install guy marker | Big Br Rd
2022 | 2022-07-20 | Hazard |  |  | 37830413000355 | TRUE | 3303902-LESLIE / WOOTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr | Coon Crk Rd
2022 | 2022-07-25 | Hazard | 82918055 | DKY0117610 | 37830377A00155 |  | 3309104-WHITESBUR / CRAFTS COLLEY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Asset Pole | 4222 Hwy 931 N Whitesburg, Ky | 2022-08-29
2022 | 2022-08-15 | Hazard |  |  | 37830404B00069 | TRUE | 3312901-JENKINS / KONA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole, needs replaced | Old 119 Loop
2022 | 2022-08-15 | Hazard | 83485531 | DKY0118188 | 37830405A00465 |  | 3312902-JENKINS / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Slip is very close to pole | Industrial road | 2022-10-06
2022 | 2022-08-16 | Hazard |  |  | 37830403A20312 |  | 3312901-JENKINS / KONA | Line Work | OH |  | pole: leaning, burned more than 50% remaining | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree in creek needs cut off wire so pole can be straightened | Mary Jane Potter elementary school
2022 | 2022-08-29 | Hazard | 86290259 | DKY0123282 | 37830004B30464 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire dozed out | Hwy 1110
2022 | 2022-08-29 | Hazard |  |  | 37830005000161 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy washed out | Riverside Rd | 2022-08-29
2022 | 2022-08-29 | Hazard |  |  | 37830101000003 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole needs straightened | Leatherwood Crk, Watts
2022 | 2022-08-31 | Hazard |  |  | 37830005000167 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Need to retire tap | 450 Hwy 476, Lost Crk | 2023-10-30
2022 | 2022-08-31 | Hazard |  |  | 37830030000060 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarms | Nobles LNDG, Hwy 476 | 2022-08-31
2022 | 2022-09-07 | Hazard |  |  | 37830080000001 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | YES |  | Troublesome Ln
2022 | 2022-09-08 | Hazard |  |  | 37830079000061 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole needs replaced or removed, inactive | Rt 476, Rowdy
2022 | 2022-09-15 | Hazard |  |  | 38831083C40243 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten pole needs replaced | 1212 Main St, Jackson
2022 | 2022-09-19 | Hazard | 83454400 | DKY0118112 | 37830231B00134 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES |  | Ira Lane, Mallie, Ky. | 2023-01-31
2022 | 2022-09-19 | Hazard | 84353604 | DKY0119500 | 37830248B00486 |  | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Fence is holding pole up | 3098 N MainSt | 2023-02-20
2022 | 2022-09-27 | Hazard |  |  | 37840216000041 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Creek has pole washed out | Squabble crk
2022 | 2022-11-08 | Hazard | 83772998 | DKY0118559 | 37830228000159 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | Lower Mill Crk, Carrie | 2022-12-21
2022 | 2022-11-08 | Hazard |  |  | 37830301000292 | TRUE | 3309301-VICCO / REDFOX | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Easy xfmr to remove (still energized) | FlaxPatch Rd

## Ckt Defects Reported 2023 HAZ
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2023 | 2023-01-09 | Hazard | 84342937 | DKY0119484 | 37830321000293 |  | 3309002-JEFF / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Kenmont Rd | 2023-02-15
2023 | 2023-01-10 | Hazard |  |  | 37830345000122 |  | 3309003-JEFF / VIPER | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Good inactive xfmr | Slabtown hollow
2023 | 2023-01-10 | Hazard |  |  | 37830391000004 |  | 3309003-JEFF / VIPER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Wells Frk Rd
2023 | 2023-01-10 | Hazard |  |  | 37830440000033 |  | 3309003-JEFF / VIPER | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES |  | Right frk
2023 | 2023-01-16 | Hazard |  |  | 37830296000871 |  | 3302704-HAZARD / KENMONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad shape | Upper Hickory St, Lothair
2023 | 2023-01-19 | Hazard |  |  | 37830151000068 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH | guys/anchors: broken or missing | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Angle pole needs anchor replaced | 15 mile crk just before Springmint Ln
2023 | 2023-01-20 | Hazard |  |  | 37830127000022 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Across creek | Lost Creek Rd
2023 | 2023-01-20 | Hazard |  |  | 37830174000376 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH | guys/anchors: broken or missing | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Anchor needs replaced | Rhonda’s DR, Grapevine Crk | 2023-01-20
2023 | 2023-01-20 | Hazard |  |  | 37830174B00101 |  | 3311701-SHAMROCK / SHAMROCK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive, easy removal | Spencer Br Rd
2023 | 2023-01-20 | Hazard |  |  | 37830174B34420 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Pole leaning badly | Kennedy Rd | 2023-01-20
2023 | 2023-01-23 | Hazard |  |  | 37830134D00099 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hicks Br, off Wiley Frk
2023 | 2023-01-23 | Hazard |  |  | 37830181000420 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole and xfmr need removed | Last place on Kentucky Dr
2023 | 2023-01-24 | Hazard |  |  | 37830181D00131 |  | 3420002-SOFT SHELL / LEBURN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Poleis in terrible condition | 926 Hwy 550 E
2023 | 2023-01-27 | Hazard |  |  | 38831036000006 |  | 3308002-JACKSON / PANBOWL | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy wire needs repaired | 884 Panbowl Br
2023 | 2023-02-01 | Hazard | 84335081 | DKY0119447 | 37830275000019 |  | 3307303-BULAN / LOTTSCREE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole needs replaced. | Lotts Creek Road | 2023-02-24
2023 | 2023-02-01 | Hazard | 84493528 | DKY0119805 | 37830272B21318 | TRUE | 3302701-HAZARD / BLACKGOLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Replace bad pole | 106 Black Gold Court | 2023-08-15
2023 | 2023-02-08 | Hazard |  |  | 37830540000001 |  | 3309901-SLEMP / DEFEATED CREEK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Pole needs cleaned up, inactive xfmr | Cloverlick Rd
2023 | 2023-02-08 | Hazard |  |  | 37830541000016 |  | 3309901-SLEMP / DEFEATED CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , crossarm/braces: broken/split |  |  | KPC | YES | Very bad pole and arms
2023 | 2023-02-13 | Hazard |  |  | 37830249C00033 |  | 3307303-BULAN / LOTTSCREE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Very bad pole, easy access | Feltner Ln, old trl park
2023 | 2023-02-13 | Hazard |  |  | 37830249C00049 | TRUE | 3307303-BULAN / LOTTSCREE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Very bad pole | 3265 Lotts Crk Rd | 2023-07-26
2023 | 2023-02-20 | Hazard |  |  | 37830295000128 |  | 3300602-BLUEGRASS / HAZARD | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign | NO | Re-sag secondary wrapped in telephone | 85 Fred Combs Dr, Town Mtn
2023 | 2023-02-20 | Hazard | 84468385 | DKY0119726 | 37830296A31355 |  | 3300602-BLUEGRASS / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Wire is only thing holding pole up | Walnut St | 2023-03-03
2023 | 2023-02-21 | Hazard | 68075070 | DKY0097613 | 37830272B40094 | TRUE | 3300602-BLUEGRASS / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Concrete sidewalk | 509 cedar st, Hazard
2023 | 2023-02-22 | Hazard |  |  | 37830271C00089 | TRUE | 3301401-COMBS / COMBS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is very bad | 526 KY-80 Combs, KY
2023 | 2023-02-22 | Hazard |  |  | 37830271C00390 |  | 3301401-COMBS / COMBS | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Replace anchor | 87 Cemetery Rd Combs, KY
2023 | 2023-02-22 | Hazard |  |  | 37830296A30831 |  | 3300602-BLUEGRASS / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace bad pole | 116 Walnut Street Hazard,KY
2023 | 2023-03-01 | Hazard |  |  | 37830248000348 |  | 3301402-COMBS / AIRPORTGA | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad cross arms | Combs Rd
2023 | 2023-03-01 | Hazard |  |  | 37830248001121 |  | 3301402-COMBS / AIRPORTGA | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | dd light circuit needs removed | 25 Spring Ave
2023 | 2023-03-02 | Hazard |  |  | 37830129A00180 | TRUE | 3307301-BULAN / ARY-HEINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr | Home place Clinic
2023 | 2023-03-02 | Hazard | 80342479 | DKY0115140 | 37830153B00073 | TRUE | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 75’ up on bank | Pigeon Roost Rd
2023 | 2023-03-06 | Hazard | 84507016 | DKY0120081 | 37830169D00192 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad Pole | Buckhorn Dam Road,Buckhorn, Ky. | 2023-04-19
2023 | 2023-03-07 | Hazard |  |  | 37830153B00083 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole and bad arm | 2707 Pigeonroost Rd
2023 | 2023-03-08 | Hazard | 84614844 | DKY0119992 | 37830323C00414 |  | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Yellow Creek Road,Sassafras | 2023-04-13
2023 | 2023-03-16 | Hazard |  |  | 37830128000001 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Primary and neutral out of sag | 415 Troublesome Lane Hazard, KY 41701
2023 | 2023-03-16 | Hazard |  |  | 37830128000012 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy has washed out | McGilton Br
2023 | 2023-03-16 | Hazard |  |  | 37830128000013 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Inactive transformer near creek needs removed | Was last single phase pole in McGilton Branch
2023 | 2023-03-16 | Hazard |  |  | 37830129A00019 |  | 3307301-BULAN / ARY-HEINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | No dirt around pole | 121 Williams Br, Ary
2023 | 2023-03-21 | Hazard |  |  | 37830225A00294 | TRUE | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Tribes Camp Rd
2023 | 2023-03-21 | Hazard |  |  | 37830225B00290 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage | conductors: excessive splices, deteriorated conductors | KPC | NO | Neutral looks wrapped in communication | Hardburly Rd and Tribbey Camp Rd
2023 | 2023-03-22 | Hazard |  |  | 37830225B00047 | TRUE | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Pleasant Hill Rd off of Vermillion Dr
2023 | 2023-03-27 | Hazard | 84726496 | DKY0120224 | 37830248A00674 | TRUE | 3301402-COMBS / AIRPORTGA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES |  | Combs Road,Airport Gardens | 2023-04-13
2023 | 2023-03-28 | Hazard |  |  | 37830224C00349 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH |  |  |  | Foreign | NO | Broke cutout on capacitor bank | 131 Bulan Hiner Rd, Bulan, KY 41722
2023 | 2023-04-06 | Hazard |  |  | 37830246D00356 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole split at pole top pin bolts | Woodridge Dr, Busy,KY
2023 | 2023-04-06 | Hazard |  |  | 37830246D00544 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO |  | 283 Eversole Rd, Busy, KY
2023 | 2023-04-11 | Hazard |  |  | 37830270D00068 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | 2 guys are broken | 4235 KY-80 Hazard, KY
2023 | 2023-04-11 | Hazard |  |  | 37830294000029 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Boar Rd off of Hwy 1096, Big Creek
2023 | 2023-04-11 | Hazard |  |  | 37830318A00118 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire broken at anchor | 6729 KY-80 Hazard, KY
2023 | 2023-04-11 | Hazard |  |  | 37830318A10418 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Coal haul road Avawam, KY
2023 | 2023-04-11 | Hazard |  |  | 37830319000051 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad rotted off at ground level | Just past Chowning Way in Browns Fork
2023 | 2023-04-11 | Hazard |  |  | 37830319000062 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 3642 Browns Fork Rd
2023 | 2023-04-12 | Hazard |  |  | 37830247A00875 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and tap | Marcus Hollow off Typo Rd, Hazard, KY
2023 | 2023-04-12 | Hazard |  |  | 37830247A01117 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Marcus Hollow off Typo Rd, Hazard, KY
2023 | 2023-04-13 | Hazard |  |  | 37830246B00084 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Colby Lane Hazard, KY
2023 | 2023-04-13 | Hazard |  |  | 37830246B00255 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 7175 Hwy 451 Busy, KY
2023 | 2023-04-13 | Hazard |  |  | 37830269C00003 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 625 Big Willard Rd Hazard, KY
2023 | 2023-04-13 | Hazard |  |  | 37830269C00005 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 569 Big Willard Hazard, KY
2023 | 2023-04-13 | Hazard |  |  | 37830269C00006 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 569 Big Willard Rd Hazard, KY
2023 | 2023-04-13 | Hazard | 75739524 | DKY0109106 | 37830270A00094 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm spilt at insulator bolt | 6749 Hwy 451, Busy, Ky | 2023-10-31
2023 | 2023-04-13 | Hazard |  |  | 37830270A00097 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  | crossarm/braces: deteriorated, not rotten , lightning arresters/insulators: damaged |  | KPC | NO | Crossarm split at pole top pin bolt, insulator laying on arm | 6608 Hwy 451 Busy, KY
2023 | 2023-04-13 | Hazard | 75739524 | DKY0109106 | 37830270A00098 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  | crossarm/braces: deteriorated, not rotten | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Crossarm split at pole top pin bolt, inactive one pole tap, inactive transformer | 6526 Hwy 451 Busy, KY | 2023-10-31
2023 | 2023-04-13 | Hazard |  |  | 37830270A00100 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten , broken/split |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | YES |  | Sunlight Lane Busy, KY
2023 | 2023-04-13 | Hazard |  |  | 37830270A00103 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive Transformer | 6242 Hwy 451 Busy, KY
2023 | 2023-04-13 | Hazard |  |  | 37830270A00197 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 6312 Hwy 451 Busy, KY
2023 | 2023-04-14 | Hazard |  |  | 37830246A00148 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive transformer | 3180 Couchtown Rd Busy, KY
2023 | 2023-04-14 | Hazard | 85183004 |  | 37830246B00007 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm broken | 7267 Hwy 451 Busy, KY
2023 | 2023-04-14 | Hazard | 84642625 | DKY0120065 | 37830246B00074 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole | 7619 Hwy 451 Busy, KY | 2023-10-04
2023 | 2023-04-14 | Hazard |  |  | 37830246D00161 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive line pass this transformer pole | 62 Whitey Lane off Snatch Creek Rd Busy, KY
2023 | 2023-04-14 | Hazard |  |  | 37830270C00047 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 8001 Hall’s Old Homeplace Busy, KY
2023 | 2023-04-14 | Hazard |  |  | 37830294000073 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 4594 KY-80 Hazard, KY
2023 | 2023-04-17 | Hazard | 85182949 |  | 37830245D00155 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole | 61 Poplar Lane Busy, Ky. Yerkes
2023 | 2023-04-17 | Hazard |  |  | 37830269C00172 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | UG | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Pad mount destroyed, de-energized, but gates still hanging on cutouts | Old Willard Elementary
2023 | 2023-04-18 | Hazard |  |  | 37830269C00097 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and inactive secondary | Pomp Hollow Rd Busy, KY
2023 | 2023-04-18 | Hazard |  |  | 37830269C00100 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and inactive secondary | Pomp Hollow Rd Busy, KY
2023 | 2023-04-18 | Hazard | 85121711 | DKY0120797 | 37830269C00257 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | North Dr off Pomp Hollow Rd Busy, KY | 2023-07-20
2023 | 2023-04-18 | Hazard |  |  | 37830270D00308 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 3 phase behind Double Kwik Busy, KY
2023 | 2023-04-19 | Hazard | 80810416 | DKY0115115 | 37830269A00081 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Forked Mouth Branch Rd Busy, KY | 2023-05-24
2023 | 2023-04-19 | Hazard | 83431689 | DKY0118070 | 37830269A00204 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Forked Mouth Branch Rd Busy, KY
2023 | 2023-04-19 | Hazard | 83431689 | DKY0118070 | 37830269A00204 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Forked Mouth Branch Rd Busy, KY
2023 | 2023-04-19 | Hazard |  |  | 37830269B00068 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Forked Mouth Branch Rd Busy, KY
2023 | 2023-04-19 | Hazard |  |  | 37830269B00069 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Forked Mouth Branch Rd Busy, KY
2023 | 2023-04-19 | Hazard |  |  | 37830269B00275 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Forked Mouth Branch Rd Busy, KY
2023 | 2023-04-19 | Hazard |  |  | 37830269B00289 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Bean Eye Lane Busy, KY
2023 | 2023-04-19 | Hazard | 85183161 | DKY0121295 | 37830293000002 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm split at pole top pin | Coleman/Couch Cemetery Rd Busy, KY
2023 | 2023-04-19 | Hazard | 75739524 | DKY0109106 | 37830293000052 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Beech Oak Rd Budy, KY | 2023-10-31
2023 | 2023-04-20 | Hazard |  |  | 37830293000143 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Toulouse Rd near Luke Lane, Busy, KY
2023 | 2023-04-20 | Hazard |  |  | 37830293000200 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Toulouse, France
2023 | 2023-04-21 | Hazard |  |  | 37830268000013 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 1964 Krypton-Toulouse-Yerkes Rd Busy, KY
2023 | 2023-04-21 | Hazard |  |  | 37830268000037 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NEEDS ADDITIONAL CHECK | Inactive transformer | Grassy Branch Road Busy, KY
2023 | 2023-04-21 | Hazard |  |  | 37830268000044 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | John Blood Hollow Busy, KY
2023 | 2023-04-21 | Hazard |  |  | 37830268000062 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and inactive tap | Stidham Grocery Lane Busy, KY
2023 | 2023-04-21 | Hazard | 75739524 | DKY0109106 | 37830268A20191 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Grassy Branch Road Busy, KY | 2023-10-31
2023 | 2023-04-21 | Hazard |  |  | 37830292000003 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Stidham Grocery Lane Busy, KY
2023 | 2023-04-21 | Hazard |  |  | 37830318A00182 | TRUE | 3308503-BONNYMAN / BIGCREEK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer near step downs | 6700 KY-80, Hazard, KY 41701, USA
2023 | 2023-04-24 | Hazard |  |  | 37830371000065 | TRUE | 3301701-DAISY / DAISY | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy marker - completed on site | 2702 Big Branch Rd Viper, KY | 2023-04-24
2023 | 2023-04-24 | Hazard |  |  | 37830371000065 |  | 3301701-DAISY / DAISY | Service Work | OH |  | need insulator/marker |  | KPC | NO | Guy marker - completed on site | 2702 Big Branch Rd Viper, KY | 2023-04-24
2023 | 2023-04-25 | Hazard | 85183216 |  | 37830370000001 |  | 3301701-DAISY / DAISY | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Cross arms are very bad | 121 Big Branch Road Viper, KY
2023 | 2023-04-25 | Hazard |  |  | 37830395000094 | TRUE | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Fort Branch Rd Viper, KY
2023 | 2023-04-25 | Hazard |  |  | 37830418000050 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Danita Ln, Kentucky 41774, USA
2023 | 2023-04-26 | Hazard |  |  | 37830442000081 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 452 Hicks Branch Cornettsville, KY
2023 | 2023-04-26 | Hazard |  |  | 37830443000111 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Little Leatherwood Creek near Huff Lane Cornettsville, KY
2023 | 2023-04-26 | Hazard |  |  | 37830467D20135 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 3265 Little Leatherwood Creek Cornettsville, KY
2023 | 2023-05-01 | Hazard | 85021435 | DKY0120658 | 37830225B00304 |  | 3307302-BULAN / AJAX-DWAR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | BAD POLE | 1449 HARDBURLEY RD, BULAN, KY. | 2023-06-28
2023 | 2023-05-01 | Hazard |  |  | 37830420A40529 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 993 Strawberry Hill Blackey, KY
2023 | 2023-05-01 | Hazard |  |  | 37830420C00055 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NEEDS ADDITIONAL CHECK | Bad pole | 11110 KY-7 Blackey, KY
2023 | 2023-05-01 | Hazard |  |  | 37830420C00056 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 11110 KY-7 Blackey, KY
2023 | 2023-05-01 | Hazard | 85121436 | DKY0120791 | 37830420C00057 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Inactive transformer on a 1946 pole | 145 Talent Branch Blackey, KY
2023 | 2023-05-02 | Hazard |  |  | 37830419B00033 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Bull Creek Rd Cornettsville, KY
2023 | 2023-05-02 | Hazard |  |  | 37830419C00227 | TRUE | 3301701-DAISY / DAISY | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm is bowing | Gas well off Klenco Rd
2023 | 2023-05-02 | Hazard |  |  | 37830419D00110 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | YES | Bad pole | Gas well road off of Klenco Rd
2023 | 2023-05-04 | Hazard |  |  | 37830444000043 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Ironwood Drive Hallie, KY
2023 | 2023-05-04 | Hazard |  |  | 37830444000060 | TRUE | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive transformer | 1278 Hoot Owl Hollow Hallie, KY
2023 | 2023-05-04 | Hazard |  |  | 37830468000135 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | Near 901 Long Branch Hallie, KY
2023 | 2023-05-04 | Hazard |  |  | 37830492000029 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 2610 Turkey Creek Hallie, KY
2023 | 2023-05-05 | Hazard |  |  | 37830469000082 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 188 Tolby Branch Rd, Hallie, KY
2023 | 2023-05-05 | Hazard |  |  | 37830469000169 | TRUE | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole has been broken or burnt off, crossarm used for pole extension. Cemetery rd | 6965 Hwy 1103 Hallie, KY
2023 | 2023-05-08 | Hazard | 80821928 | DKY0115501 | 37830419A00113 | TRUE | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 2 bad poles with same pole number | 86 Bull Creek Rd Cornettsville, KY
2023 | 2023-05-08 | Hazard |  |  | 37830419D20416 |  | 3301701-DAISY / DAISY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 47 Hwy 1103, Blackey, KY
2023 | 2023-05-08 | Hazard |  |  | 37830493000091 |  | 3301701-DAISY / DAISY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Big Branch Hallie, KY
2023 | 2023-05-10 | Hazard | 85120394 | DKY0120782 | 37830271D31118 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Rambler Rd, Lexington, KY 40503, USA | 2023-06-02
2023 | 2023-05-10 | Hazard |  |  | 37830272B11303 |  | 3302701-HAZARD / BLACKGOLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy markers | 163 Citizens Lane, Hazard, KY 41701, USA | 2023-05-10
2023 | 2023-05-10 | Hazard | 85104694 | DKY0120776 | 37830272B11497 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Between the Eye Care Center and old Primary Care Building | 2023-05-26
2023 | 2023-05-12 | Hazard |  |  | 37830272B21318 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole has been burnt and braced with crossarm | 1st Trust Bank on Hwy 15 Bypass Hazard, KY
2023 | 2023-05-12 | Hazard |  |  | 37830272B21390 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH | cutout: damaged |  |  | KPC | NO | Broken bypass (porcelain) on Recloser pole | Behind Black Gold Plaza Hazard, KY
2023 | 2023-05-12 | Hazard |  |  | 37830296D11052 |  | 3302701-HAZARD / BLACKGOLD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | 1868 KY-15, Hazard, KY 41702, USA | 2023-05-12
2023 | 2023-05-15 | Hazard |  |  | 37830296D10213 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 1845 KY-15, Hazard, KY 41701, USA
2023 | 2023-05-15 | Hazard |  |  | 37830296D10678 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 1845 KY-15, Hazard, KY 41701, USA
2023 | 2023-05-15 | Hazard |  |  | 37830344000053 | TRUE | 3302701-HAZARD / BLACKGOLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole split at insulator bolt | Top of Buffalo Mountain Hazard, KY
2023 | 2023-05-15 | Hazard |  |  | 37830344000137 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  | transformers: leaking, damaged |  | KPC | NO | Inactive transformer has been shot | Buffalo Mountain Hazard, KY, USA
2023 | 2023-05-15 | Hazard |  |  | 37830344000138 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  | transformers: leaking, damaged |  | KPC | NO | Inactive transformer has been shot | Buffalo Mountain Hazard, KY
2023 | 2023-05-15 | Hazard |  |  | 37830344000142 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Damaged lightning arrestor | Step downs on top of Buffalo Mountain Hazard, KY
2023 | 2023-05-15 | Hazard |  |  | 37830344A20186 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Buffalo mountain toward Big Creek Rd, Kentucky 41701, USA
2023 | 2023-05-16 | Hazard |  |  | 37830294000257 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor broken | 145 Dean Town Ln, Hazard, KY 41701, USA
2023 | 2023-05-17 | Hazard | 85680264 |  | 37830343D00024 | TRUE | 3302701-HAZARD / BLACKGOLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 20 Greenwood Lane Hazard, KY (Jacks Branch)
2023 | 2023-05-18 | Hazard |  |  | 37830343D00051 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 4131 Big Creek Rd Hazard, KY
2023 | 2023-05-18 | Hazard |  |  | 37830368000025 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 1179 Buffalo Run Rd, Hazard, KY 41701, USA
2023 | 2023-05-18 | Hazard |  |  | 37830368000070 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Vanover Br Rd, Kentucky 41537, USA
2023 | 2023-05-22 | Hazard |  |  | 37830324000168 |  | 3309301-VICCO / REDFOX | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Sassafras, KY 41759, USA
2023 | 2023-05-22 | Hazard |  |  | 37830325A00151 |  | 3309301-VICCO / REDFOX | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap and transformer | 480 Little Smith Branch Rd, Anco, KY 41759, USA
2023 | 2023-05-22 | Hazard |  |  | 37830325A00331 |  | 3309301-VICCO / REDFOX | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy marker missing | 217 Big Smith Branch Rd, Anco, KY 41759, USA | 2023-05-22
2023 | 2023-05-22 | Hazard |  |  | 37830325A00331 |  | 3309301-VICCO / REDFOX | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy marker missing | 217 Big Smith Branch Rd, Anco, KY 41759, USA | 2023-05-22
2023 | 2023-05-22 | Hazard | 80507141 | DKY0114740 | 37830349000016 | TRUE | 3309301-VICCO / REDFOX | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Pauley Hollow Rd Sassafras, KY
2023 | 2023-05-22 | Hazard | 85213242 | DKY0120951 | 37830388B00368 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole has large crack and needs replaced so telephone can work pole | 92 KY 80,Hyden,Ky | 2023-07-25
2023 | 2023-05-24 | Hazard |  |  | 37830253000091 |  | 3309301-VICCO / REDFOX | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 4643 Big Branch Rd Vicco, KY
2023 | 2023-05-24 | Hazard |  |  | 37830277000073 |  | 3309301-VICCO / REDFOX | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole washed out | 249 Frozen Mill Rd
2023 | 2023-05-24 | Hazard |  |  | 37830301000292 | TRUE | 3309301-VICCO / REDFOX | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive transformer | Mouth of Flax Patch Rd, Vicco, KY
2023 | 2023-05-24 | Hazard |  |  | 37830301000313 |  | 3309301-VICCO / REDFOX | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap and transformer | 880 Flax Patch Rd Vicco, KY
2023 | 2023-05-25 | Hazard | 85178647 | DKY0120904 | 37830322B00010 |  | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten Pole-Telephone Company needing to do work at this pole. | 235 Will Combs Ln.,Happy,Ky.
2023 | 2023-05-26 | Hazard |  |  | 37830326A00064 |  | 3309301-VICCO / REDFOX | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole bad in the middle | 389 Breeding Creek Rd Redfox, KY
2023 | 2023-05-26 | Hazard |  |  | 37830326B00044 |  | 3309301-VICCO / REDFOX | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NEEDS ADDITIONAL CHECK
2023 | 2023-05-30 | Hazard |  |  | 37830272B30382 |  | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive transformer | 266 L and N Drive Hazard, KY
2023 | 2023-05-31 | Hazard |  |  | 37830272A30644 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten pole | 200 River Rd Hazard, KY
2023 | 2023-05-31 | Hazard |  |  | 37830272A40398 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES |  | 417 Elizabeth Drive Hazard, KY
2023 | 2023-05-31 | Hazard |  |  | 37830272A40643 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten pole | 200 River Rd Hazard, KY
2023 | 2023-05-31 | Hazard |  |  | 37830272A40685 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 109 Allias Rd Hazard, KY
2023 | 2023-05-31 | Hazard |  |  | 37830272A40994 |  | 3300601-BLUEGRASS / WALKERTOW | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | 948 Highland Ave Hazard, KY | 2023-05-31
2023 | 2023-05-31 | Hazard |  |  | 37830272A40996 |  | 3300601-BLUEGRASS / WALKERTOW | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | 156 Mountain Ave Hazard, KY | 2023-05-31
2023 | 2023-05-31 | Hazard |  |  | 37830272A40997 |  | 3300601-BLUEGRASS / WALKERTOW | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | 149 Mountain Ave Hazard, KY | 2023-05-31
2023 | 2023-05-31 | Hazard |  |  | 37830272B30483 |  | 3300601-BLUEGRASS / WALKERTOW | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | 1241 N Main Street Hazard, KY | 2023-05-31
2023 | 2023-05-31 | Hazard |  |  | 37830272B30788 |  | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NO | Secondary and pole need removed | 189 L and N Drive Hazard, KY
2023 | 2023-05-31 | Hazard |  |  | 37830272B41129 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Broken guy wire | Hazard City Hall
2023 | 2023-06-01 | Hazard |  |  | 37830248B00251 |  | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 11 Hilton Camp Lane Hazard, KY
2023 | 2023-06-01 | Hazard |  |  | 37830272C10538 |  | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Vocational school | 333 Allais Rd, Hazard, KY 41701, USA
2023 | 2023-06-01 | Hazard |  |  | 37830272C10713 |  | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 125 Rowl St, Hazard, KY 41701, USA
2023 | 2023-06-01 | Hazard |  |  | 37830272C10716 |  | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Bad crossarms | 242 Rowl Street Hazard, KY
2023 | 2023-06-01 | Hazard |  |  | 37830273B00080 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 1393 Walker Branch Rd, Hazard, KY 41701, USA
2023 | 2023-06-02 | Hazard |  |  | 37830248D00225 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Bad crossarms | 1437 Upper 2nd Creek Rd, Hazard, KY 41701, USA
2023 | 2023-06-02 | Hazard |  |  | 37830248D00237 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Docks Hollow Rd and Upper 2nd Creek Rd
2023 | 2023-06-02 | Hazard | 80342159 | DKY0114893 | 37830272C30899 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , guys/anchors: broken or missing |  |  | KPC | YES | Pole top extension and guy wire no longer buried | Docks Hollow Rd, Hazard, KY 41701, USA | 2023-09-28
2023 | 2023-06-02 | Hazard |  |  | 37830273A00042 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole split at pole top pin bolts | Upper 2nd Creek Missionary Baptist Church Hazard, KY
2023 | 2023-06-02 | Hazard |  |  | 37830273B00071 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | YES | Bad pole | 4007 Upper 2nd Creek Rd Hazard, KY
2023 | 2023-06-02 | Hazard |  |  | 37830273B00073 |  | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole burnt off | 4165 Upper 2nd Creek Rd Hazard, KY
2023 | 2023-06-02 | Hazard |  |  | 37830273D00032 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 970 High Rock Rd Hazard, KY
2023 | 2023-06-02 | Hazard |  |  | 37830273D00033 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 970 High Rock Rd Hazard, KY
2023 | 2023-06-02 | Hazard |  |  | 37830273D00037 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 1735 High Rock Rd Hazard, KY
2023 | 2023-06-05 | Hazard | 80817593 | DKY0115239 | 37830172B00008 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | KY Hwy 451 just off KY Hwy 28 Chavies, KY | 2023-09-18
2023 | 2023-06-05 | Hazard | 80817644 | DKY0115236 | 37830172B00010 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Slide and bad pole | KY Hwy 451 just off KY Hwy 28, Chavies, KY | 2023-09-18
2023 | 2023-06-05 | Hazard |  |  | 37830172B00093 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy broken | Chavies-Dunraven Rd, Kentucky, USA
2023 | 2023-06-05 | Hazard | 83370714 | DKY0117977 | 37830196B30284 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 398 Maggard Ridge Rd Hazard, KY
2023 | 2023-06-05 | Hazard |  |  | 37830272A40625 |  | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Both span guy poles are rotten 272-200 and 272-201 (25 ft class 7) | 525 Spring St, Hazard, KY 41701, USA
2023 | 2023-06-05 | Hazard |  |  | 37830273C00025 | TRUE | 3300601-BLUEGRASS / WALKERTOW | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 1125 High Rock Rd Hazard, KY
2023 | 2023-06-06 | Hazard |  |  | 37830172B00003 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Leaning pole | Hwy 451, near Hwy 28 Chavies, KY
2023 | 2023-06-06 | Hazard |  |  | 37830172B00094 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 28 KY-451, Hazard, KY 41701, USA
2023 | 2023-06-06 | Hazard | 75659381 | DKY0108243 | 37830172B00115 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 28 KY-451, Hazard, KY 41701, USA
2023 | 2023-06-07 | Hazard |  |  | 37830169D00195 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | Buckhorn Dam Rd Buckhorn, KY
2023 | 2023-06-07 | Hazard | 86292905 |  | 37840288000061 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | KY Hwy 2022 Saul
2023 | 2023-06-07 | Hazard |  |  | 37840288C00050 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | KY Hwy 2022 Saul
2023 | 2023-06-07 | Hazard |  |  | 37840288C00093 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | KY Hwy 2022 Saul
2023 | 2023-06-07 | Hazard |  |  | 37840288C00152 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | KY Hwy 2022 Saul
2023 | 2023-06-08 | Hazard | 75739484 | DKY0108659 | 37830147000035 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy broken | 102 Big Fork Rd, Jackson, KY 41339, USA
2023 | 2023-06-08 | Hazard |  |  | 37830147000040 |  | 3301101-CHAVIES / CHAVIES | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | 66 Dange Creek, Jackson, KY 41339, USA | 2023-06-08
2023 | 2023-06-08 | Hazard |  |  | 37830147000098 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 13501 KY Hwy 28 Jackson, KY
2023 | 2023-06-08 | Hazard |  |  | 37830147000140 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 14769 KY Hwy 1110 Jackson, KY
2023 | 2023-06-08 | Hazard |  |  | 37830147000154 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Pole washed out | 205 Big Fork Rd Jackson, KY
2023 | 2023-06-08 | Hazard |  |  | 37830147B30193 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 14044 Dange Creek Jackson, KY
2023 | 2023-06-08 | Hazard | 75739484 | DKY0108659 | 37830170000011 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | YES | Inactive transformer and bad pole | Redoak Ln & Feb Fork Rd, Kentucky 41745, USA
2023 | 2023-06-08 | Hazard |  |  | 37830170000012 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Redoak Ln & Feb Fork Rd, Kentucky 41745, USA
2023 | 2023-06-08 | Hazard |  |  | 37830170000017 |  | 3301101-CHAVIES / CHAVIES | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | 653 Feb Fork Rd, Gays Creek, KY 41745, USA | 2023-06-08
2023 | 2023-06-09 | Hazard | 75739484 | DKY0108659 | 37830171000020 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken | Top of Chavies Mountain Chavies, KY 41727, USA
2023 | 2023-06-13 | Hazard |  |  | 37830194000064 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Head of John’s Fork Gays Creek, KY 41745, USA
2023 | 2023-06-13 | Hazard |  |  | 37830194000095 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Primary and neutral need re-sagged or a pole in line 194-95 to 194-C3-164 | 531 Stable Fork Rd, Gays Creek, KY 41745, USA
2023 | 2023-06-13 | Hazard |  |  | 37830194000126 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Head of John’s Fork Rd Gays Creek, KY 41745, USA
2023 | 2023-06-13 | Hazard |  |  | 37830194000140 |  | 3301101-CHAVIES / CHAVIES | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | 201 John’s Fork Rd Gays Creek, KY | 2023-06-13
2023 | 2023-06-14 | Hazard |  |  | 37830122000003 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap and inactive transformer | Near 3827 Bowling Creek Rd Jackson, KY
2023 | 2023-06-14 | Hazard | 75717324 | DKY0108362 | 37830325C00274 |  | 3309301-VICCO / REDFOX | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarms | Hwy 15 and Hwy 160 | 2023-08-31
2023 | 2023-06-14 | Hazard | 80508114 | DKY0114710 | 37830326C00076 | TRUE | 3309301-VICCO / REDFOX | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 1015 Breeding Creek, Redfox, KY 41847, USA
2023 | 2023-06-20 | Hazard | 85720175 | DKY0121666 | 37830103000037 |  | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 103 Noble Branch, Rowdy,Ky. | 2023-08-24
2023 | 2023-06-21 | Hazard |  |  | 37830126000026 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Tenmile Creek Rd Chavies, KY
2023 | 2023-06-21 | Hazard |  |  | 37830126000078 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Crow Creek Rd Chavies, KY
2023 | 2023-06-21 | Hazard |  |  | 37830126000178 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Crow Creek Rd Chavies, KY
2023 | 2023-06-21 | Hazard |  |  | 37830126000179 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | 2 inactive transformers | Crow Creek Rd Chavies, KY
2023 | 2023-06-21 | Hazard |  |  | 37830126000216 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Tenmile Creek Rd Chavies, KY
2023 | 2023-06-21 | Hazard |  |  | 37830126D30270 |  | 3312202-ENGLE / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | Chavies, KY 41727, USA | 2023-06-21
2023 | 2023-06-21 | Hazard |  |  | 37830126D30270 |  | 3312202-ENGLE / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | Chavies, KY 41727, USA | 2023-06-21
2023 | 2023-06-21 | Hazard |  |  | 37830126D30270 |  | 3312202-ENGLE / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | Chavies, KY 41727, USA | 2023-06-21
2023 | 2023-06-22 | Hazard |  |  | 37830102000020 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Perkins Branch Rd Lost Creek, KY
2023 | 2023-06-22 | Hazard | 85373998 | DKY0121133 | 37830102000152 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | YES | Inactive transformer and top of pole split | 95 Lost Creek Rd, Hazard, KY 41701, USA | 2023-12-20
2023 | 2023-06-23 | Hazard |  |  | 37830078B40071 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Ned Branch Rd Lost Creek, KY
2023 | 2023-06-23 | Hazard |  |  | 37830101000058 |  | 3312202-ENGLE / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | 48 Butter Rd, Lost Creek, KY 41348, USA | 2023-06-23
2023 | 2023-06-23 | Hazard |  |  | 37830103000081 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 2501 Cockrell Fork Rd Lost Creek, KY
2023 | 2023-06-23 | Hazard |  |  | 37830150000106 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole has been burnt | KY-15 & Wendell Ford Terminal Rd, Kentucky 41727, USA
2023 | 2023-06-26 | Hazard | 85392745 | DKY0121169 | 37830204000040 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | POLE NEEDS REPLACED | 49 DOGWOOD DRIVE, CARRIE,KY. | 2023-11-08
2023 | 2023-06-26 | Hazard |  |  | 37830126000003 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 8829 Lost Creek Rd Chavies, KY
2023 | 2023-06-26 | Hazard |  |  | 37830126000004 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | Lower Lost Creek near Miller Rd Chavies, KY
2023 | 2023-06-26 | Hazard |  |  | 37830126C30309 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Mountain View Cemetery Rd and Frances Br Rd, Kentucky, USA | 2023-06-26
2023 | 2023-06-26 | Hazard |  |  | 37830174C00408 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Stidham Ln, Kentucky 41701, USA
2023 | 2023-06-27 | Hazard |  |  | 37830149B00019 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Hwy 28 just before tap to old Chavies School
2023 | 2023-06-27 | Hazard |  |  | 37830174A00086 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy broke | 484 Kennedy Ln, Hazard, KY 41701, USA
2023 | 2023-06-27 | Hazard |  |  | 37830174A00092 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive line (5 spans) needs removed | 270 Pads Branch Rd, Hazard, KY 41701, USA
2023 | 2023-06-27 | Hazard |  |  | 37830174B34420 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Lending pole (pole number on pole in field is 4421) | Kennedy Ln, Kentucky 41701, USA
2023 | 2023-06-28 | Hazard |  |  | 37830147000058 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 1576 Miller Branch Barwick Rd, Jackson, KY 41339, USA
2023 | 2023-06-28 | Hazard |  |  | 37830147000063 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 53 Stidham Dr, Jackson, KY 41339, USA
2023 | 2023-06-28 | Hazard |  |  | 37830147000064 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Stidham Dr, Kentucky 41339, USA
2023 | 2023-06-28 | Hazard |  |  | 37830147000080 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 99 Old Railroad Rd Jackson, KY
2023 | 2023-06-28 | Hazard |  |  | 37830147D20227 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 1032 Miller Branch Barwick Rd, Jackson, KY 41339, USA
2023 | 2023-06-28 | Hazard |  |  | 37830171000057 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive primary tap | 1091 Strongs Branch, Hazard, KY 41701, USA
2023 | 2023-06-28 | Hazard |  |  | 37830171000235 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 51 Jacks Drive Jackson, KY
2023 | 2023-06-28 | Hazard |  |  | 37830171C10312 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 51 Jacks Drive Jackson, KY
2023 | 2023-06-28 | Hazard |  |  | 37830172A00279 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 3000 Miller Branch Barwick Rd, Jackson, KY 41339, USA
2023 | 2023-06-28 | Hazard |  |  | 37830173A00111 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Hwy 28 just before Deaton Park Rd Chavies, KY
2023 | 2023-06-28 | Hazard |  |  | 37830196A00107 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and single span tap | 15076 KY-451, Hazard, KY 41701, USA
2023 | 2023-06-28 | Hazard | 83370714 | DKY0117977 | 37830196B30261 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Maggard Ridge Rd, Kentucky 41701, USA
2023 | 2023-06-28 | Hazard | 83370714 | DKY0117977 | 37830196B30263 | TRUE | 3301101-CHAVIES / CHAVIES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Maggard Ridge Rd, Kentucky 41701, USA
2023 | 2023-06-29 | Hazard |  |  | 37830149B00099 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Tranquility Lane Chavies, KY
2023 | 2023-06-29 | Hazard |  |  | 37830149B20191 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Chavies, KY 41727, USA
2023 | 2023-06-29 | Hazard |  |  | 37830149C40153 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  | transformers: leaking, damaged |  | KPC | NO | Inactive transformer has been shot | Last pole on Davidson Branch Rd, Kentucky, USA
2023 | 2023-06-29 | Hazard |  |  | 37830172C00199 |  | 3312202-ENGLE / GRAPEVINE | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | 27 Spencer Fork Loop Rd Hazard, KY
2023 | 2023-06-29 | Hazard |  |  | 37830172C00324 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarms (double arms) | Hwy 28 near Spencer Fork Rd
2023 | 2023-06-29 | Hazard |  |  | 37830172C00325 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarms (double arms) | Mouth Spencer Fork Rd and Hwy 28
2023 | 2023-06-29 | Hazard |  |  | 37830173C00008 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy broken | Mouth of Davidson Branch Rd
2023 | 2023-06-30 | Hazard |  |  | 37830197000108 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarms | Tunnel Hill Cemetery/ Campbell Bend Hazard, KY
2023 | 2023-06-30 | Hazard |  |  | 37830221000176 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Resag neutral 221-176 to 221-27 | 158 Collins Rd, Krypton, KY 41754, USA
2023 | 2023-06-30 | Hazard |  |  | 37830221D10287 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 206 Collins Rd Krypton, KY
2023 | 2023-07-10 | Hazard |  |  | 37830196C00015 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  |  | KPC | NO | Neutral Stolen from 196-15 to pole 196-14 | KY-451, Kentucky, USA
2023 | 2023-07-10 | Hazard | 85532794 | DKY0121374 | 37830425B00219 |  | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 184 Thompson Br.,Whitesburg, Ky. | 2023-09-18
2023 | 2023-07-11 | Hazard |  |  | 37830221000007 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole (1100 ft span crosses RR tracks and river) | 6000 Chavies-Dunraven Rd, Chavies, KY 41727, USA
2023 | 2023-07-12 | Hazard |  |  | 37830197000023 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap (de-energized from 197-17) | Spencer Fork South Rd, Kentucky 41754, USA
2023 | 2023-07-12 | Hazard |  |  | 37830220000039 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Neutral needs re-sagged between 220-39 to 220-90 | 12242 KY-451, Krypton, KY 41754, USA
2023 | 2023-07-12 | Hazard |  |  | 37830220000100 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Need to re-sag line or add pole in line for clearance (220-100 to 220-195) | 196 Gunners Br Rd, Hazard, KY 41701, USA
2023 | 2023-07-13 | Hazard | 85182781 | DKY0121110 | 37830196D00032 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarms (may want to change the pole) | 101 Firehouse Ln, Krypton, KY 41754, USA
2023 | 2023-07-13 | Hazard | 85182822 | DKY0121209 | 37830220000117 | TRUE | 3312202-ENGLE / GRAPEVINE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Krypton-Napfor Rd Krypton, KY
2023 | 2023-07-13 | Hazard |  |  | 37830221000001 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 2 Lewis Ln, Krypton, KY 41754, USA
2023 | 2023-07-13 | Hazard |  |  | 37830221C20272 |  | 3312202-ENGLE / GRAPEVINE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 3099 Krypton-Napfor Rd Krypton, KY
2023 | 2023-07-14 | Hazard |  |  | 38831083D10080 |  | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten pole | 75 Armory Dr Jackson, KY
2023 | 2023-07-14 | Hazard |  |  | 38831083D10677 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Inactive transformer and tap (2 spans) 677 and 678 | 157 Cripple Creek Rd Jackson, KY
2023 | 2023-07-14 | Hazard |  |  | 38831083D30061 |  | 3308001-JACKSON / S.JACKSON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy markers | 17 Davis St, Jackson, KY 41339, USA | 2023-07-14
2023 | 2023-07-14 | Hazard |  |  | 38831083D30063 |  | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | YES | Bad pole and guy needs an insulator at transformer | 77 Armory Dr, Jackson, KY 41339, USA
2023 | 2023-07-14 | Hazard |  |  | 38831083D41002 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformers (3) | 775 Armory Dr, Jackson, KY 41339, USA
2023 | 2023-07-14 | Hazard |  |  | 38831108A00319 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten pole | 1343 Armory Dr, Jackson, KY 41339, USA
2023 | 2023-07-17 | Hazard |  |  | 38831083C30248 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Inactive secondary on a rough 1941 pole | 1218 Main Street Jackson, KY
2023 | 2023-07-18 | Hazard |  |  | 38831083C20148 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 1609 Hurst Ln, Jackson, KY 41339, USA
2023 | 2023-07-18 | Hazard |  |  | 38831083C40152 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 1611 Hurst Ln, Jackson, KY 41339, USA
2023 | 2023-07-18 | Hazard |  |  | 38831083C40201 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole split | 729 Washington Ave, Jackson, KY 41339, USA
2023 | 2023-07-18 | Hazard |  |  | 38831083C40243 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 1212 Main Street Jackson, KY
2023 | 2023-07-18 | Hazard |  |  | 38831083C40289 |  | 3308001-JACKSON / S.JACKSON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | YES | Cross arms used for pole top extension | Jackson, KY 41339, USA
2023 | 2023-07-18 | Hazard |  |  | 38831083D30347 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 188 Quicksand Rd, Jackson, KY 41339, USA
2023 | 2023-07-18 | Hazard |  |  | 38831084B00149 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive transformer | Shucky Bean Hollow Rd, Jackson, KY 41339, USA
2023 | 2023-07-19 | Hazard |  |  | 38831108A00293 |  | 3308001-JACKSON / S.JACKSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole rotten at bottom | 1500 Quicksand Rd, Kentucky 41339, USA
2023 | 2023-07-19 | Hazard |  |  | 38831108A00401 | TRUE | 3308001-JACKSON / S.JACKSON | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Need big bucket to remove inactive multi-phase service rolled up on pole. Heavy! | 2060 Quicksand Rd, Jackson, KY 41339, USA
2023 | 2023-07-24 | Hazard | 85696981 | DKY0121646 | 37830424000015 |  | 3309101-WHITESBUR / WHITESBUR | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 22 Marlow Road, Whitesburg, Ky. | 2023-08-22
2023 | 2023-07-24 | Hazard | 85590628 | DKY0121467 | 37830250D00116 |  | 3307303-BULAN / LOTTSCREE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | POLE IN BAD SHAPE.NEEDS REPLACED SOON. | 15 COLES FORK RD.,HAZARD,KY. | 2023-08-10
2023 | 2023-07-25 | Hazard | 85788306 | DKY0122362 | 37830299D00078 | TRUE | 3309302-VICCO / JEFF | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Inactive transformer by creek | Head of Rowdy Hollow Sassafras, KY
2023 | 2023-07-27 | Hazard |  |  | 37830323B00070 |  | 3309302-VICCO / JEFF | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | In the bottom near Vicco Sewer Plant
2023 | 2023-07-27 | Hazard |  |  | 37830323C00413 | TRUE | 3309302-VICCO / JEFF | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Secondary lash laying on communication cable | 308 Yellow Creek Rd Sassafras, KY
2023 | 2023-07-28 | Hazard |  |  | 37830346A00389 | TRUE | 3309302-VICCO / JEFF | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformers | Browder Lane Happy, KY
2023 | 2023-07-28 | Hazard |  |  | 37830370000024 | TRUE | 3309302-VICCO / JEFF | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and lash | 5308 Upper River Road Happy, KY
2023 | 2023-07-31 | Hazard |  |  | 37830346C00413 |  | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole | 270 Happy Circle Happy, KY
2023 | 2023-08-01 | Hazard |  |  | 37830346B00001 | TRUE | 3309302-VICCO / JEFF | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Low service drop | 4817 Hwy 7 Viper, Ky
2023 | 2023-08-01 | Hazard |  |  | 37830346B00084 | TRUE | 3309302-VICCO / JEFF | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | 4 spans of inactive line and 1 inactive transformer | 205 Denmar Lane Viper, KY
2023 | 2023-08-01 | Hazard |  |  | 37830346C00301 |  | 3309302-VICCO / JEFF | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Bad crossarms | 157 Happy Circle Happy, KY
2023 | 2023-08-01 | Hazard |  |  | 37830346D00178 |  | 3309302-VICCO / JEFF | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 796 Scuddy Branch Rd Scuddy, Ky
2023 | 2023-08-01 | Hazard |  |  | 37830346D00224 |  | 3309302-VICCO / JEFF | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | 3 inactive spans and 2 inactive transformers (346-D0-224 and 346-C0-553) takeoff span is already removed. | Heather Drive off Scuddy Branch Rd, Scuddy, KY
2023 | 2023-08-01 | Hazard |  |  | 37830370B30300 |  | 3309302-VICCO / JEFF | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | 3 inactive transformers | Orchard Branch (coal haul rd) Hwy 7,
2023 | 2023-08-02 | Hazard | 80341539 | DKY0114742 | 37830347D00180 | TRUE | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 100 Left Fork Georges Branch Rd Vicco, KY
2023 | 2023-08-07 | Hazard | 85684466 | DKY0121636 | 37830179C00210 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | ROTTEN POLE | 39 CHEROKEE DR.,EMMALENA,KY. | 2023-09-28
2023 | 2023-08-08 | Hazard |  |  | 37830323D30799 |  | 3309302-VICCO / JEFF | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Reynolds Road Vicco, KY
2023 | 2023-08-08 | Hazard |  |  | 37830348D00207 |  | 3309302-VICCO / JEFF | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy markers in yard | 3869 Montgomery Creek Rd, Vicco, KY 41773, USA | 2023-08-08
2023 | 2023-08-08 | Hazard |  |  | 37830372A10185 |  | 3309302-VICCO / JEFF | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole leaning | 3381 Big Br Rd, Viper, KY 41774, USA
2023 | 2023-08-08 | Hazard |  |  | 37830373000075 |  | 3309302-VICCO / JEFF | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Pole top pine twisted and split | Hwy 3408 Blackey, KY
2023 | 2023-08-08 | Hazard | 85794918 |  | 37830373000199 | TRUE | 3309302-VICCO / JEFF | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap (373-111) | Square Dance Rd, Kentucky 41804, USA
2023 | 2023-08-09 | Hazard |  |  | 37830419C00250 | TRUE | 3309302-VICCO / JEFF | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Primary and neutral needs re-sagged or a pole in line. 37830419C00250 | 2500 Bull Creek Rd, Cornettsville, KY 41731, USA
2023 | 2023-08-11 | Hazard |  |  | 37830450A00096 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and service drop. Guy is loose. | Around the Mountain Rd Whitesburg, KY
2023 | 2023-08-11 | Hazard |  |  | 37830450B00223 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive 3 phase tap | 675 Great Oak Rd Mayking, KY
2023 | 2023-08-11 | Hazard |  |  | 37830450C00038 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive 3 phase tap | Dream Rd Mayking, KY
2023 | 2023-08-11 | Hazard |  |  | 37830450C10331 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | Around the Mountain Rd, Kentucky 41837, USA
2023 | 2023-08-15 | Hazard | 85765460 | DKY0121739 | 37830195000058 |  | 3301101-CHAVIES / CHAVIES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace bad pole | 9155 Ky Hwy 28, Chavies, Ky. | 2023-08-31
2023 | 2023-08-16 | Hazard | 85738669 | DKY0121700 | 37830242000102 |  | 3303901-LESLIE / HYDEN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotted off in bad shape.Crew to replace in next few days.RGP | 3811 Oppossum Bend Rd.,Hyden,Ky. | 2023-08-22
2023 | 2023-08-17 | Hazard |  |  | 37830403B00012 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is broken and a crossarm as a splint | 530 Gose Hollow Rd Mayking, Ky
2023 | 2023-08-17 | Hazard |  |  | 37830426C00448 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 240 Jeff’s Drive Mayking, KY
2023 | 2023-08-17 | Hazard |  |  | 37830427A00031 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Pole is washed out between road and creek (pole not in Atlas) | 345 Bottom Fork-Laurel Fork Rd Mayking, KY
2023 | 2023-08-18 | Hazard |  |  | 37830378B00104 | TRUE | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Line needs retired (4 spans) | 180 Gazelle Dr Thornton, KY
2023 | 2023-08-23 | Hazard |  |  | 37830255A00304 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap (4 spans) | End of three phase Right Fork Millstone
2023 | 2023-08-23 | Hazard |  |  | 37830330000003 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 3185 KY 803 Millstone, KY
2023 | 2023-08-23 | Hazard | 85681127 | DKY0122323 | 37830355B00325 | TRUE | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Near 372 Lizz Cott Dr Millstone, KY
2023 | 2023-08-23 | Hazard |  |  | 37830355B00411 |  | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | 6 spans of inactive primary and inactive transformer | Hickory Dr Millstone, KY
2023 | 2023-08-23 | Hazard | 85681127 | DKY0122323 | 37830355B00557 | TRUE | 3314402-MAYKING / MILLSTONE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and single phase tap | 372 Lizz Cott Dr Millstone, KY
2023 | 2023-08-28 | Hazard |  |  | 37830230A00035 | TRUE | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap off of 3 phase (station zone) | 3350 KY-160, Hindman, KY 41822, USA
2023 | 2023-08-28 | Hazard |  |  | 37830230A00172 | TRUE | 3308402-BECKHAM / CARRSFORK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarms | Appalachia Truss Dr, Kentucky 41822, USA
2023 | 2023-08-29 | Hazard |  |  | 37830254B00065 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Runnells Branch Rd, Littcarr, KY 41834, USA
2023 | 2023-08-29 | Hazard |  |  | 37830254B00066 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Runnells Branch Rd, Kentucky, USA
2023 | 2023-08-29 | Hazard |  |  | 37830279000028 | TRUE | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and 3 span tap | 1044 Steer Fork Rd, Mallie, KY 41836, USA
2023 | 2023-08-29 | Hazard |  |  | 37830279000218 | TRUE | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 1325 Steer Fork Rd, Mallie, KY 41836, USA
2023 | 2023-08-31 | Hazard |  |  | 37830160000101 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 7985 KY-899, Pippa Passes, KY 41844, USA
2023 | 2023-08-31 | Hazard |  |  | 37830184000086 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 437 Hawk Rd, Pippa Passes, KY 41844, USA
2023 | 2023-08-31 | Hazard |  |  | 37830208000128 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive transformer | 1328 Hawk Rd Pippa Passes, KY
2023 | 2023-08-31 | Hazard |  |  | 37830257000038 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Primary loop close to pole | 9902 KY-582 Pine Top, KY
2023 | 2023-09-05 | Hazard |  |  | 37830321B00376 | TRUE | 3309001-JEFF / BOONE LEDGE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrestor broken | Glomawr Stormking Road Hazard, KY
2023 | 2023-09-05 | Hazard |  |  | 37830321D00363 |  | 3309001-JEFF / BOONE LEDGE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarm | 1688 Glomawr Stormking Road Hazard, KY
2023 | 2023-09-06 | Hazard |  |  | 37830326D00116 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Last pole up Wolfpen Creek Rd Mallie, Ky
2023 | 2023-09-08 | Hazard |  |  | 37830279000191 | TRUE | 3308402-BECKHAM / CARRSFORK | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Broken guy | 98 Wolf Rd Mallie, KY
2023 | 2023-09-08 | Hazard |  |  | 37830302D00085 | TRUE | 3308402-BECKHAM / CARRSFORK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad Crossarms | 1952 Burgeys Creek Rd Mallie, KY
2023 | 2023-09-08 | Hazard |  |  | 37830303000008 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole washed out | 347 Big Doubles Branch Road Mallie, KY
2023 | 2023-09-08 | Hazard |  |  | 37830303000010 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | 492 Big Doubles Branch Road Mallie, KY
2023 | 2023-09-08 | Hazard |  |  | 37830303000013 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 760 Big Doubles Branch Road Mallie, KY
2023 | 2023-09-08 | Hazard |  |  | 37830303000168 |  | 3308402-BECKHAM / CARRSFORK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive transformer | 2457 Burgeys Creek Rd Mallie, KY
2023 | 2023-09-11 | Hazard |  |  | 37830321B00139 | TRUE | 3309001-JEFF / BOONE LEDGE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive 2 span primary tap | 1466 Glomawr Stormking Rd Jeff, KY
2023 | 2023-09-11 | Hazard |  |  | 37830321B00475 |  | 3309001-JEFF / BOONE LEDGE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 137 Craft Ln, Hazard, KY 41701, USA
2023 | 2023-09-12 | Hazard | 85913337 | DKY0121980 | 37830026000030 |  | 3310502-HADDIX / CANOE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Mill Creek Rd, Kentucky 41339, USA
2023 | 2023-09-13 | Hazard |  |  | 37830230C40373 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 101 Pine Dr, Pippa Passes, KY 41844, USA
2023 | 2023-09-13 | Hazard |  |  | 37830230D00058 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive transformer | 2 Sam’s Branch Rd Mallie, KY
2023 | 2023-09-13 | Hazard |  |  | 37830231A00162 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and service | Hwy 899 just past Briarwood Lane Phipps Passes, KY
2023 | 2023-09-15 | Hazard |  |  | 37830184A00028 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Booger Branch Rd, Kentucky 41844, USA
2023 | 2023-09-15 | Hazard |  |  | 37830184A00053 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer (across road from mouth of Hollybush) | 6 Cr-1108, Pippa Passes, KY 41844, USA
2023 | 2023-09-15 | Hazard |  |  | 37830207C00014 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 100 Purpose Rd, Pippa Passes, KY 41844, USA
2023 | 2023-09-15 | Hazard |  |  | 37830231D00072 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Head of Mallet Fork Pine Top, KY
2023 | 2023-09-15 | Hazard |  |  | 37830231D00278 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | 11 spans of inactive 3 phase primary line needs retired | From the head of Ellis Bentley Hollow Rd to Head of Mallet Fork Rd
2023 | 2023-09-15 | Hazard |  |  | 37830255C00142 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 1086 Mallet Fork Rd, Pine Top, KY 41843, USA
2023 | 2023-09-15 | Hazard |  |  | 37830255C00154 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | 2 spans of inactive primary and neutral need removed | 321 Walnut Hollow Rd, Pine Top, KY 41843, USA
2023 | 2023-09-15 | Hazard |  |  | 37830255C00211 |  | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 98 Daisy Lane Pine Top, KY
2023 | 2023-09-15 | Hazard |  |  | 37830255D00291 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Pine Top Ln, Kentucky 41754, USA
2023 | 2023-09-15 | Hazard |  |  | 37830255D00298 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Pinetop Ln, Kentucky 41843, USA
2023 | 2023-09-19 | Hazard |  |  | 37830256000102 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive one pole primary tap with a transformer on pole 256-175 | 368 Meadow Lark Rd Pinetop, KY
2023 | 2023-09-19 | Hazard |  |  | 37830281A30061 | TRUE | 3308404-BECKHAM/PIPPA PASSES | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | 4 pole inactive tap | 1000 Upper Carr Rd Pine Top, KY
2023 | 2023-09-20 | Hazard |  |  | 37830579C00179 |  | 3311102-STINNETT / BEECHFK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole has been damaged by fire at the base | 6785 US-421 Mozelle, KY
2023 | 2023-09-21 | Hazard | 85586707 | DKY0121686 | 37830109000024 | TRUE | 3420001-SOFT SHELL / VEST | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 56 Yellow Mountain Rd Hueysville, KY | 2023-12-20
2023 | 2023-09-21 | Hazard |  |  | 37830109C30114 | TRUE | 3420001-SOFT SHELL / VEST | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Need a pole placed in line | 214 Family Farm Rd Hueysville, KY
2023 | 2023-09-21 | Hazard |  |  | 37830109C40112 |  | 3420001-SOFT SHELL / VEST | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy anchor has washed out/ guy laying on secondary | 219 Yellow Mountain Rd Hueysville, KY
2023 | 2023-09-22 | Hazard |  |  | 37830108000067 | TRUE | 3420001-SOFT SHELL / VEST | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen | Vest Talcum Rd
2023 | 2023-09-22 | Hazard |  |  | 37830108000085 | TRUE | 3420001-SOFT SHELL / VEST | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections , conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Middle phase off insulator and pole ground stolen | 150 Vest Talcum Rd Vest, KY
2023 | 2023-09-22 | Hazard |  |  | 37830157000081 |  | 3420001-SOFT SHELL / VEST | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Inactive transformer and secondary | 314 Ogden Gap Rd Hindman, KY
2023 | 2023-09-27 | Hazard |  |  | 37830156000030 |  | 3420001-SOFT SHELL / VEST | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing 2 guy markers | 147 Sylvester Branch Rd, Emmalena, KY 41740, USA | 2023-09-27
2023 | 2023-09-27 | Hazard |  |  | 37830156000218 | TRUE | 3420001-SOFT SHELL / VEST | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive 3 pole tap | Sylvester Branch Rd, Kentucky, USA
2023 | 2023-09-27 | Hazard |  |  | 37830156000239 | TRUE | 3420001-SOFT SHELL / VEST | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive transformer | 100 Montgomery Creek Rd, Emmalena, KY 41740, USA
2023 | 2023-09-27 | Hazard |  |  | 37830181A00308 |  | 3420001-SOFT SHELL / VEST | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarms are deteriorating | 1156 Hindman Bypass, Hindman, KY 41822, USA
2023 | 2023-09-27 | Hazard |  |  | 37830181A00347 |  | 3420001-SOFT SHELL / VEST | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 542 Old Ogden Rd, Hindman, KY
2023 | 2023-10-02 | Hazard |  |  | 37830222B00305 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive primary (4 spans) | 291 Shinglepen Dr Bonnyman, KY
2023 | 2023-10-02 | Hazard |  |  | 37830223B00414 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive primary line (2 spans) | Bourbon Ridge Ln, Kentucky 41719, USA
2023 | 2023-10-02 | Hazard |  |  | 37830247A00209 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 137 Typo Rd, Bonnyman, KY 41719, USA
2023 | 2023-10-03 | Hazard |  |  | 37830198C00044 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm is bad | Deesaundra Dr, Kentucky 41701, USA
2023 | 2023-10-03 | Hazard |  |  | 37830198C00083 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Potential low clearance on single phase tap. Inactive transformer | Deesaundra Dr, Kentucky 41701, USA
2023 | 2023-10-03 | Hazard |  |  | 37830198C00148 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 185 Walton Mt, Hazard, KY 41701, USA
2023 | 2023-10-03 | Hazard |  |  | 37830223A00217 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Sheriff Ct, Kentucky 41701, USA
2023 | 2023-10-04 | Hazard |  |  | 37830223D21081 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Potential low clearance over yard | 185 Happy Valley Ln, Hazard, KY 41701, USA
2023 | 2023-10-04 | Hazard |  |  | 37830247A31292 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer (near substation) | Bonnyman, KY 41719, USA
2023 | 2023-10-04 | Hazard |  |  | 37830247A31333 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Nascar Ln, Kentucky 41719, USA
2023 | 2023-10-04 | Hazard |  |  | 37830247A31334 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Nascar Ln, Kentucky 41719, USA
2023 | 2023-10-05 | Hazard |  |  | 37830175000086 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive transformer | 212 Mount Zion Rd, Hazard, KY
2023 | 2023-10-05 | Hazard |  |  | 37830199C00110 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive transformer | 391 Noble Lane, Bonnyman, KY
2023 | 2023-10-05 | Hazard |  |  | 37830199D30447 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 477 Noble Ln, Bonnyman, KY
2023 | 2023-10-05 | Hazard |  |  | 37830223A00136 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Inactive transformer | Harveyton Rd, Kentucky, USA
2023 | 2023-10-05 | Hazard |  |  | 37830223B00119 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Harveyton Rd, Kentucky, USA
2023 | 2023-10-05 | Hazard |  |  | 37830223B00483 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Un-mapped inactive primary tap and transformer | Heralds Heights, Kentucky 41719, USA
2023 | 2023-10-05 | Hazard |  |  | 37830223C00001 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive primary tap | Harveyton Rd, Kentucky, USA
2023 | 2023-10-05 | Hazard |  |  | 37830223C00466 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 2230 Harveyton Rd, Bonnyman, KY 41719, USA
2023 | 2023-10-05 | Hazard |  |  | 37830223C00469 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 2148 Harveyton Rd, Bonnyman, KY 41701, USA
2023 | 2023-10-05 | Hazard | 86071705 | DKY0122223 | 37830270A00099 |  | 3308503-BONNYMAN / BIGCREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | VERY BAD POLE NEEDS REPLACED SOON. | 10 APPLE LN, BUSY,KY.
2023 | 2023-10-06 | Hazard |  |  | 37830247B00576 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 586 Village Lane, Hazard, KY
2023 | 2023-10-06 | Hazard |  |  | 37830247B00961 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 882 Dawahare Dr, Hazard, KY
2023 | 2023-10-06 | Hazard |  |  | 37830247B41293 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer (New Beginnings Day Care) | 151 Miss Edna Lane, Hazard, KY 41701, USA
2023 | 2023-10-06 | Hazard |  |  | 37830247C11619 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | End of Ridgeview Way, Hazard, KY
2023 | 2023-10-06 | Hazard |  |  | 37830247D11732 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | 3 inactive transformers | 792 Morton Blvd, Hazard, KY 41701, USA
2023 | 2023-10-09 | Hazard |  |  | 37830224B10481 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer (Fazoli’s) | 47 Commodore Street, Hazard, Ky
2023 | 2023-10-09 | Hazard |  |  | 37830247C00507 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer (near Boone Ridge Rd) | KY-15, Kentucky, USA
2023 | 2023-10-10 | Hazard |  |  | 37830247D31869 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 15 Morton Blvd, Bradenton, FL 34210, USA
2023 | 2023-10-11 | Hazard | 85183113 | DKY0121298 | 37830247B01139 | TRUE | 3308502-BONNYMAN / HAZARD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarms | 414 Roy Campbell Dr, Hazard, KY 41701, USA
2023 | 2023-10-11 | Hazard |  |  | 37830247D00976 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 276 Roy Campbell Dr, Hazard, KY 41701, USA
2023 | 2023-10-11 | Hazard |  |  | 37830247D21709 |  | 3308502-BONNYMAN / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 181 Roy Campbell Dr, Hazard, KY 41701, USA
2023 | 2023-10-17 | Hazard |  |  | 37830386000031 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 25491 US-421, Hyden, KY 41749, USA
2023 | 2023-10-17 | Hazard |  |  | 37830410A00057 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Puncheoncamp Branch Rd, Kentucky 41749, USA
2023 | 2023-10-17 | Hazard |  |  | 37830411A10060 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace broken | Baywood Ln, Kentucky 41749, USA
2023 | 2023-10-23 | Hazard |  |  | 37830384B30150 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Improper clearance (needs a pole in line) | Chandler Creek Rd, Bear Branch, KY (tower road)
2023 | 2023-10-23 | Hazard |  |  | 37830385000021 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Cane Fork Rd, Hyden, KY
2023 | 2023-10-23 | Hazard |  |  | 37830409000026 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | UG conduit: damaged or separated |  |  | KPC | NO | UG conduit is separated at ground. | Dobber Hollow Hyden, KY
2023 | 2023-10-23 | Hazard | 85793765 | DKY0123058 | 37840360000004 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Ulysses Creek Rd, Bear Branch, KY
2023 | 2023-10-23 | Hazard | 85793842 | DKY0122812 | 37840360000021 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Ulysses Creek Rd, Bear Branch, KY
2023 | 2023-10-23 | Hazard | 85793911 |  | 37840384000060 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Ulysses Creek Rd, Bear Branch, KY
2023 | 2023-10-23 | Hazard |  |  | 37840384000066 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Ulysses Creek Rd, Bear Branch, KY
2023 | 2023-10-23 | Hazard |  |  | 37840408D00005 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is washing out | Hwy 421 at Henry Fork Rd, Hyden, KY
2023 | 2023-10-25 | Hazard | 85182469 | DKY0121674 | 37830054000006 | TRUE | 3310503-HADDIX/TROUBLESOME CREEK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole per TRC | Hwy 476 and Harvey Bend Rd
2023 | 2023-10-26 | Hazard |  |  | 37830312000016 |  | 3303903-LESLIE / HALSFORK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Insulator broken | Rush Creek Rd, Sizerock, KY
2023 | 2023-10-26 | Hazard |  |  | 37830313000020 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | YES | Bad pole and inactive transformer/secondary | Hell for Certain Rd, Bear Branch, KY
2023 | 2023-10-26 | Hazard |  |  | 37830337000009 |  | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap and transformer (off 337-10) | Bullskin Rd, Bear Branch, KY
2023 | 2023-10-26 | Hazard |  |  | 37830337000072 |  | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap and transformer (337-74 ) | Bullskin Rd, Bear Branch, KY
2023 | 2023-10-26 | Hazard |  |  | 37840336000037 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | YES | Bad pole and inactive lash | Woods Branch Rd, Sizerock, KY
2023 | 2023-10-26 | Hazard |  |  | 37840336000143 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive secondary pole and lash | Rush Creek Rd, Sizerock, KY
2023 | 2023-10-26 | Hazard |  |  | 37840384000068 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive single tap and transformer (needs retired) comes off 384-95 | Bullskin Rd, Bear Branch, KY
2023 | 2023-10-26 | Hazard | 82592803 | DKY0118109 | 37840384000096 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole split | Bullskin Rd, Bear Branch, KY
2023 | 2023-10-26 | Hazard | 85794162 |  | 37840408C00124 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | other: customer owned attachment | KPC | NO | Bad abandoned secondary pole | 329 Bob’s Fork, Bear Branch, KY
2023 | 2023-10-31 | Hazard | 85680125 |  | 37830337000034 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hollins Fork Rd, Bear Branch, KY
2023 | 2023-10-31 | Hazard |  |  | 37830337000042 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive line needs retired (10 spans) | Hollins Fork Rd, Bear Branch, KY
2023 | 2023-10-31 | Hazard |  |  | 37830337000053 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive line not on map needs retired | Hollins Fork Rd, Bear Branch, KY
2023 | 2023-10-31 | Hazard | 82592771 | DKY0117888 | 37830361000041 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 835 Hollins Fork Rd, Bear Branch, KY | 2023-12-28
2023 | 2023-10-31 | Hazard | 82592632 | DKY0118196 | 37830361000047 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hollins Fork Rd, Bear Branch, KY
2023 | 2023-10-31 | Hazard | 86177775 | DKY0122381 | 37830361000050 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hollins Fork Rd, Bear Branch, KY
2023 | 2023-10-31 | Hazard |  |  | 37830361000133 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hollins Fork, Bear Branch, KY
2023 | 2023-10-31 | Hazard | 84339406 | DKY0119464 | 37830361000136 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Hollins Fork, Bear Branch, KY
2023 | 2023-10-31 | Hazard | 85788672 | DKY0122695 | 37830361000139 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Leaning pole | Pine Rock Dr, Hollins Fork
2023 | 2023-10-31 | Hazard | 82591313 | DKY0118093 | 37840336000039 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole and neutral down in both directions. | 6045 Bullskin Rd, Sizerock, KY
2023 | 2023-10-31 | Hazard |  |  | 37840336000042 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Span of primary and 1949 pole needs retired | 136 Whispering Pines Lane, Sizerock, KY
2023 | 2023-10-31 | Hazard |  |  | 37840336000058 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker |  | KPC | YES | Bad pole and guy is going through the middle of an oak tree. | County Line Rd, Sizerock, KY
2023 | 2023-10-31 | Hazard |  |  | 37840336000136 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | joint use attachments: clearance issues |  |  | Foreign | YES | Crossarm used as extension to obtain clearance | Statue Lane, Sizerock, KY
2023 | 2023-11-01 | Hazard | 85691003 | DKY0122568 | 37830382A20235 |  | 3409503-BURDINE / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole (per TRC) | Forest Hill Cir, Jenkins, KY 41537, USA | 2023-08-10
2023 | 2023-11-01 | Hazard | 75587327 | DKY0108140 | 37830387C00351 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm split | 75 Berry Branch Rd, Hyden, KY
2023 | 2023-11-01 | Hazard |  |  | 37840336000115 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Secondary needs a pole for clearance | 7022 Bullskin Rd, Sizerock, KY 41762, USA
2023 | 2023-11-02 | Hazard |  |  | 37830339000061 |  | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole top split | Bull Creek Rd, Kentucky, USA
2023 | 2023-11-02 | Hazard |  |  | 37830339000113 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Communication pole close to primary lines | 1615 Bull Creek Rd, Hyden, KY
2023 | 2023-11-02 | Hazard | 85684361 | DKY0121857 | 37830362000128 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Bull Creek Rd, Kentucky, USA
2023 | 2023-11-02 | Hazard |  |  | 37830362000179 |  | 3303903-LESLIE / HALSFORK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | 3 spans of inactive primary and an inactive transformer | 241 Bell Branch Rd, Hyden, KY
2023 | 2023-11-02 | Hazard |  |  | 37830386000010 |  | 3303903-LESLIE / HALSFORK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole in slide and leaning | 979 Thousandsticks Branch Rd, Hyden, KY 41749, USA
2023 | 2023-11-03 | Hazard |  |  | 37830362000056 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | 3 guys need insulators installed | Davidson Fork Rd, Kentucky, USA
2023 | 2023-11-03 | Hazard | 85683992 |  | 37830362000114 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Bowling Branch Rd, Osborne Fork
2023 | 2023-11-03 | Hazard | 85684565 | DKY0122403 | 37830362000152 | TRUE | 3303903-LESLIE / HALSFORK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 1398 Upper Bull Creek Rd, Thousandsticks, KY 41766, USA
2023 | 2023-11-13 | Hazard | 86206082 | DKY0122425 | 37830355D30089 |  | 3401301-FLEMING / NEON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole (per TRC) | 2nd St, Fleming-Neon, KY 41840, USA
2023 | 2023-11-13 | Hazard | 85794451 | DKY0122421 | 37830376A00321 |  | 3308602-COLLIER / LOWERROCK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole (per TRC) | 2009 KY-1148, Isom, KY
2023 | 2023-11-13 | Hazard | 85789012 | DKY0122681 | 37830381C00301 | TRUE | 3451202-BEEFHIDE / DUNHAM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole (per TRC) | 51 No 6 Hollow Rd, Jenkins, KY 41537, USA
2023 | 2023-11-13 | Hazard | 85690780 | DKY0123052 | 37830382A10167 | TRUE | 3312902-JENKINS / JENKINS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole (per TRC) | 410 Cane Branch Rd, Jenkins, KY
2023 | 2023-11-27 | Hazard |  |  | 37830206B00014 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm brace is broken and hanging down | Zane Dr, Kentucky 41822, USA
2023 | 2023-11-27 | Hazard |  |  | 37830230C00276 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Guy broken and wrapped around pole | Pigman Br Rd, Kentucky 41822, USA
2023 | 2023-11-28 | Hazard |  |  | 37830205D00144 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 , transformers: inactive , NOT near waterway or drainage , NOT damaged or leaking | KPC | NO | Inactive transformer and secondary | 72 Cave Branch Rd, Hindman, KY 41822, USA
2023 | 2023-11-28 | Hazard |  |  | 37830206B00114 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Gus Hays Path, Kentucky 41822, USA
2023 | 2023-11-28 | Hazard |  |  | 37830229000068 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 1004 Perkins Madden Rd, Hindman, KY 41822, USA
2023 | 2023-11-28 | Hazard |  |  | 37830229C10184 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer (rough road) | 1004 Perkins Madden Rd, Hindman, KY 41822, USA
2023 | 2023-11-29 | Hazard |  |  | 37830205C00406 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | 2 inactive transformers | Beech St, Hindman, KY 41822, USA
2023 | 2023-12-04 | Hazard | 86508463 | DKY0122956 | 37830319000158 |  | 3302701-HAZARD / BLACKGOLD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES |  | 1494 BIG CREEK RD.,HAZARD,KY.
2023 | 2023-12-05 | Hazard |  |  | 37830180000018 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Old Ogden Branch Rd, Hindman, KY 41740, USA
2023 | 2023-12-05 | Hazard |  |  | 37830204009003 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 1401 W Main St, Hindman, KY 41822, USA
2023 | 2023-12-05 | Hazard |  |  | 37830205A00035 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Bad crossarms | 164 W Main St, Hindman, KY 41822, USA
2023 | 2023-12-05 | Hazard |  |  | 37830205A00037 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Bad crossarms | 169 W Main St, Hindman, KY 41822, USA
2023 | 2023-12-05 | Hazard |  |  | 37830205A00039 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy broken and needs a new anchor | 333 Charles Town Heights, Hindman, KY
2023 | 2023-12-05 | Hazard |  |  | 37830205A00222 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten at ground | 841 W Main St, Hindman, KY 41822, USA
2023 | 2023-12-05 | Hazard |  |  | 37830205A00359 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Stacked arms bad | 169 W Main St, Hindman, KY 41822, USA
2023 | 2023-12-05 | Hazard |  |  | 37830205A00517 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Mountain Memory Gardens, Hindman, KY
2023 | 2023-12-05 | Hazard |  |  | 37830205B00161 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformers | 588 Push Back Branch, Hindman, KY 41822, USA
2023 | 2023-12-05 | Hazard |  |  | 37830205D00095 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Needs an anchor installed | 1970 KY-160, Hindman, KY 41822, USA
2023 | 2023-12-05 | Hazard |  |  | 37830205D00097 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground needs repaired | Cave Branch Rd, Kentucky 41822, USA
2023 | 2023-12-06 | Hazard |  |  | 37830180000077 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Wager Branch Rd, Kentucky 41822, USA
2023 | 2023-12-06 | Hazard |  |  | 37830180000078 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Wager Branch Rd, Kentucky 41822, USA
2023 | 2023-12-06 | Hazard |  |  | 37830204000023 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 1008 Lower Mill Creek Rd, Hazard, KY 41701, USA
2023 | 2023-12-06 | Hazard |  |  | 37830204000026 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 46 Creighton Lane, Carrie, KY
2023 | 2023-12-06 | Hazard |  |  | 37830204000027 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 33 Grandpa Dr, Emmalena, KY 41740, USA (pole entered wrong first)
2023 | 2023-12-06 | Hazard |  |  | 37830204000108 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | Wager Branch Rd, Kentucky 41822, USA
2023 | 2023-12-06 | Hazard |  |  | 37830228000014 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 1868 Lower Mill Creek Rd, Carrie, KY
2023 | 2023-12-06 | Hazard |  |  | 37830228000023 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 680 Cornett Rd, Hindman, KY 41822, USA
2023 | 2023-12-06 | Hazard |  |  | 37830228000043 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary drops | 2889 Lower Mill Creek Rd, Carrie, KY
2023 | 2023-12-06 | Hazard |  |  | 37830228000044 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 2343 Lower Mill Creek Rd, Carrie, KY
2023 | 2023-12-06 | Hazard |  |  | 37830228000055 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | Camp Branch, Kentucky, USA
2023 | 2023-12-06 | Hazard |  |  | 37830228000057 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Camp Branch, Kentucky, USA
2023 | 2023-12-06 | Hazard |  |  | 37830228000150 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive 2 spans of primary | 1638 Lower Mill Creek Rd, Carrie, KY
2023 | 2023-12-06 | Hazard |  |  | 37830229000003 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive stepdown transformer | 80 Sweet Gum Branch Rd, Hindman, KY
2023 | 2023-12-06 | Hazard |  |  | 37830229000146 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive transformer | 2690 Big Branch Rd, Hindman, KY
2023 | 2023-12-07 | Hazard |  |  | 37830179B00007 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | 1/0 lash is sagged below other cables attached to same poles | 8334 KY-550, Emmalena, KY 41740, USA
2023 | 2023-12-07 | Hazard |  |  | 37830179B00027 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 7901 KY-550, Emmalena, KY 41740, USA
2023 | 2023-12-07 | Hazard |  |  | 37830179B00217 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen and ground rod is washing out | Camp Nathanael Rd, Emmalena, KY 41740, USA
2023 | 2023-12-07 | Hazard |  |  | 37830179D00161 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Bad pole | 6550 KY-550, Emmalena, KY
2023 | 2023-12-07 | Hazard |  |  | 37830180000097 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Secondary unused and runs underneath telephone cables | Lick Branch Rd, Kentucky 41740, USA
2023 | 2023-12-12 | Hazard |  |  | 37830178A00454 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and primary lines | 700 KY-550, Bulan, KY 41722, USA
2023 | 2023-12-12 | Hazard |  |  | 37830178B00079 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 533 KY-550, Bulan, KY 41722, USA
2023 | 2023-12-12 | Hazard |  |  | 37830178B00312 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and primary lines | 700 KY-550, Bulan, KY 41722, USA
2023 | 2023-12-12 | Hazard |  |  | 37830178D00099 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Drift Branch Rd
2023 | 2023-12-14 | Hazard |  |  | 37830154000040 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Trace Branch Rd, Kentucky 41701, USA
2023 | 2023-12-14 | Hazard |  |  | 37830154000041 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | 211 Trace Branch Rd, Hazard, KY
2023 | 2023-12-14 | Hazard |  |  | 37830178A00179 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 290 Ridgewater Rd, Hazard, KY
2023 | 2023-12-14 | Hazard |  |  | 37830178B00057 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 11460 KY-550, Fisty, KY 41743, USA
2023 | 2023-12-15 | Hazard |  |  | 37830131000116 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | Wls Mountain, Kentucky 41740, USA
2023 | 2023-12-15 | Hazard |  |  | 37830155000027 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive 1 span primary tap | Big Branch Ball Rd, Kentucky 41740, USA
2023 | 2023-12-15 | Hazard |  |  | 37830155000133 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Inactive transformer and secondary lines | 4885 KY-80, Emmalena, KY 41740, USA
2023 | 2023-12-15 | Hazard |  |  | 37830155000134 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap and transformers (13 spans of primary and 2 transformers) | 4885 KY-80, Emmalena, KY 41740, USA
2023 | 2023-12-15 | Hazard |  |  | 37830155A30271 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Recovery Wy, Kentucky 41740, USA
2023 | 2023-12-15 | Hazard |  |  | 37830179D00064 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 2211 Montgomery Creek Rd, Emmalena, KY 41740, USA
2023 | 2023-12-15 | Hazard |  |  | 37830179D10531 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 2211 Montgomery Creek Rd, Emmalena, KY 41740, USA
2023 | 2023-12-15 | Hazard |  |  | 37830179D10532 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 2211 Montgomery Creek Rd, Emmalena, KY 41740, USA
2023 | 2023-12-19 | Hazard |  |  | 37830296C30676 | TRUE | 3302703-HAZARD / HAZARD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Stolen pole ground (Dipsey Doodle) | 801 E. Main Street, Hazard, KY
2023 | 2023-12-19 | Hazard |  |  | 37830296C31015 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer and stolen pole ground (Dipsey Doodle) | 801 E. Main Street, Hazard, KY
2023 | 2023-12-20 | Hazard |  |  | 37830296C10254 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Lash needs re- sagged | 168 Woodland Ave, Hazard, KY
2023 | 2023-12-20 | Hazard |  |  | 37830296C10422 |  | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten at ground | 524 E. Main Street, Hazard, KY
2023 | 2023-12-20 | Hazard |  |  | 37830296C10428 |  | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 340 E. Main Street, Hazard, KY
2023 | 2023-12-20 | Hazard |  |  | 37830296C10429 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Service drop appears to be laying on the roof. | 340 E. Main Street, Hazard, KY
2023 | 2023-12-20 | Hazard |  |  | 37830296C10820 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH |  |  |  | Foreign | NO | Blown fuse on a capacitor bank at this location and a hold tag on the control. | 400 Kentucky Blvd, Hazard, KY
2023 | 2023-12-20 | Hazard |  |  | 37830296C30827 |  | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 740 Kentucky Blvd, Hazard, KY
2023 | 2023-12-20 | Hazard |  |  | 37830296C30952 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 709 Kentucky Blvd, Hazard, KY
2023 | 2023-12-21 | Hazard |  |  | 37830296A30444 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole (11th Hour Worship) | 67 E. Main Street, Hazard, KY
2023 | 2023-12-21 | Hazard |  |  | 37830296A31095 |  | 3302703-HAZARD / HAZARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | 2 Inactive transformers | 225 Liberty Street, Hazard, KY
2023 | 2023-12-21 | Hazard |  |  | 37830296A40594 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 217 Maple Street, Hazard, KY
2023 | 2023-12-21 | Hazard |  |  | 37830296C10425 | TRUE | 3302703-HAZARD / HAZARD | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Stolen pole ground | 440 E. Main Street, Hazard, KY
2023 | 2023-12-21 | Hazard |  |  | 37830296C10814 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Bad crossarms (Maple Street) | 441 E. Main Street, Hazard, KY
2023 | 2023-12-21 | Hazard |  |  | 37830296C20566 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Bad crossarms | 317 Maple Street, Hazard, KY
2023 | 2023-12-26 | Hazard |  |  | 37830272B40314 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 141 Cedar Street, Hazard, KY
2023 | 2023-12-26 | Hazard |  |  | 37830272B40315 |  | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 157 Cedar Street, Hazard, KY
2023 | 2023-12-26 | Hazard |  |  | 37830272B40324 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign | NO | Primary and neutral needs resagged | 232 Pine Street, Hazard, KY
2023 | 2023-12-26 | Hazard |  |  | 37830272D10497 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy wire has been cut above transformer and the tail is hanging near leads. | Skyline Drive and Daniel Drive, Hazard, KY
2023 | 2023-12-26 | Hazard |  |  | 37830272D11272 | TRUE | 3302703-HAZARD / HAZARD | Service Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Inactive DD light hanging off pole by wire | 221 Gorman Ridge Road, Hazard, KY
2023 | 2023-12-26 | Hazard |  |  | 37830272D40440 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer | Tower Ridge Rd, Hazard, KY
2023 | 2023-12-26 | Hazard |  |  | 37830296A30730 | TRUE | 3302703-HAZARD / HAZARD | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign | NO | Span has been removed, but no dead end was installed | 799 Walnut Street, Hazard, KY
2023 | 2023-12-26 | Hazard |  |  | 37830296A30734 |  | 3302703-HAZARD / HAZARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Service appears to be against roof | 149 Ward Street, Hazard, KY
2023 | 2023-12-26 | Hazard |  |  | 37830296A30748 |  | 3302703-HAZARD / HAZARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Bad pole | 100 Craig Street, Hazard, KY
2023 | 2023-12-26 | Hazard |  |  | 37830296A30801 | TRUE | 3302703-HAZARD / HAZARD | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Inactive communication wire is above our active secondary. | 816 Walnut Street, Hazard, Ky
2023 | 2023-12-27 | Hazard |  |  | 37830202000007 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer (just past 39 Ned’s Rough Rd) | Clear Creek Rd, Hazard, KY
2023 | 2023-12-27 | Hazard |  |  | 37830202000030 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | Cockrells Trace Rd, Hazard, KY
2023 | 2023-12-27 | Hazard |  |  | 37830202000036 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap (6 spans) and 3 transformers | Honeysuckle Lane, Hazard, KY
2023 | 2023-12-27 | Hazard |  |  | 37830202000127 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Guy broken and very close to secondary loops | 625 KY-721, Hazard, KY
2023 | 2023-12-27 | Hazard |  |  | 37830202000146 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 721 KY-721, Emmalena, KY
2023 | 2023-12-27 | Hazard |  |  | 37830202000164 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | Clear Creek Rd, Hazard, KY
2023 | 2023-12-27 | Hazard |  |  | 37830226000035 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 148 Gearheart Fork Rd, Hazard, KY
2023 | 2023-12-27 | Hazard |  |  | 37830226000064 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer (mouth of John Ritchie Branch) | 2331 KY-721, Hazard, KY
2023 | 2023-12-27 | Hazard |  |  | 37830226000172 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Cockrells Trace Rd, Hazard, KY
2023 | 2023-12-27 | Hazard |  |  | 37830226000183 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Cockrells Trace Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830203000027 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | Hickory Withe Branch Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830203B30144 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Head of Hickory Withe Branch Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830203B40155 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Hickory Withe Branch Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830203B40162 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | Foreign | NO | Inactive transformer and secondary | Hickory Withe Branch Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830227A00051 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 489 Clear Creek Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830227A00052 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | Chestnut Log Branch Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830227A00248 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Johnna Haley Drive, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830227B00021 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | Mouth of Buzzard Den Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830227B00065 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH | guys/anchors: broken or missing | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Broken guy | 1180 Clear Creek Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830227B00255 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | Clear Creek Rd and Singleton Branch Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830227D00060 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral needs resagged | 161 Singleton Branch Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830227D00086 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 2174 Clear Creek Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830227D40279 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive primary tap and transformer | 2311 Clear Creek Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830251000034 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | 146 Burley Combs Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830251000128 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | Burley Combs Rd, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830251000130 | TRUE | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive transformer and secondary | 228 Shekinah Lane, Hazard, KY
2023 | 2023-12-28 | Hazard |  |  | 37830251000163 |  | 3308401-BECKHAM / HINDMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive transformer | 146 Burley Combs Rd, Hazard, KY

## Ckt Defects Reported 2019 ASH
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2019 | 2019-01-14 | Ashland | 72782771 |  | 38830501000198 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Bad lightning arrester to transformer (34 KV). | 372 Wexford Dr, Kentucky 41230, USA | 2021-01-26
2019 | 2019-01-14 | Ashland | 72744226 |  | 38830501000310 |  | 3007904-BUSSEYVILLE / TORCHLITE | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. | Issac Park Rd, Louisa, KY 41230, USA | 2019-03-07
2019 | 2019-01-14 | Ashland | 72743985 |  | 38830501000312 |  | 3007904-BUSSEYVILLE / TORCHLITE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen. | 758 Issac Park Rd, Louisa, KY 41230, USA | 2019-03-07
2019 | 2019-01-14 | Ashland | 76350569 | DKY0109685 | 38830501000313 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. | 758 Issac Park Rd, Louisa, KY 41230, USA | 2022-02-24
2019 | 2019-01-14 | Ashland | 72743378 |  | 38830501000315 |  | 3007904-BUSSEYVILLE / TORCHLITE | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. | Issac Park Rd, Louisa, KY 41230, USA | 2019-03-07
2019 | 2019-01-14 | Ashland | 72744905 |  | 38830501000316 |  | 3007904-BUSSEYVILLE / TORCHLITE | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. Pole is next to intersection of Issac Park Rd. & Clayton Br. Rd. | Isaac Branch Rd, Kentucky 41230, USA | 2019-03-07
2019 | 2019-01-14 | Ashland | 72048948 | DKY0103125 | 38830525000247 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Roadway is made for one vehicle at a time. | Dogwood Dr, Kentucky 41230, USA | 2021-08-18
2019 | 2019-01-15 | Ashland | 76350587 | DKY0109629 | 38830525000211 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen. Truck accessible at pole 525-211. Will need to climb pole 526-2. Notified DDC to put in abnormal. | Torchlight Rd, Louisa, Kentucky 41230, USA | 2020-08-20
2019 | 2019-01-15 | Ashland |  |  | 38830525000219 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | Customers TV antenna on KPC pole. THIS NEEDS TO GO TO KPC ENGINEERING/prb. Dish 1000 satellite | 20 Hylton Rd, Louisa, KY 41230, USA
2019 | 2019-01-15 | Ashland | 76350569 | DKY0109685 | 38830549000089 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Across from Box 5885. Remove inactive transformer. Neutral has broken away from tie wire and is laying on metal of clevis. | Mc Clure Branch Rd, Kentucky 41230, USA | 2022-02-24
2019 | 2019-01-17 | Ashland | 72219286 | DKY0103478 | 38830642000046 | TRUE | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Right Fork Georges Creek, Louisa KY | 2021-05-13
2019 | 2019-01-22 | Ashland | '72312614. 72788144 |  | 38830596000153 |  | BUSSEYVILLE - TORCHLITE / 0079-04 | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Remove service drop to vacant trailer. Meter has been removed and blanked off. | 515 Meades Branch Road, Louisa, KY 41230, USA | 2018-03-14
2019 | 2019-01-22 | Ashland | 72313216 |  | 38830620000137 |  | 3007904-BUSSEYVILLE / TORCHLITE | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | House knob has pulled loose from pole. Pole is located in Belles Chapel Freewill Baptist Church front parking lot. No danger to the public at this time. Meter # 190 410 323 | 1788 US-23, Louisa, KY 41232, USA | 2019-02-07
2019 | 2019-01-22 | Ashland | 76350569 | DKY0109685 | 3883620B10335 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign |  | Xarm is split. | 7507 KY-1760, Louisa, KY 41230, USA | 2022-02-24
2019 | 2019-01-23 | Ashland | 7278849 |  | 38830644000030 |  | 3007904-BUSSEYVILLE / TORCHLITE | Service Work | OH | cutout: damaged |  |  | KPC |  | Silver-top cutout (cutout is not damaged) | 70 Elwood Dr., Ulysses, KY 41264 | 2019-03-13
2019 | 2019-01-24 | Ashland | 76350572 | DKY0109640 | 38830477000126 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | 34 KV arrester is damaged. | 28 Pearl Ln, Louisa, KY 41230, USA | 2020-08-20
2019 | 2019-01-25 | Ashland | 72352480. 72822779 |  | 38830453000363 |  | 3007903-BUSSEYVILLE / LOUISA | Service Work | UG | UG conduit: damaged or separated |  |  | KPC |  | UG conduit has come loose at base of pole. Wrapped yellow caution tape around pole. | 190 Carter Rd, Louisa, KY 41230, USA | 2019-03-15
2019 | 2019-01-25 | Ashland |  |  | 38830477000042 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive transformer | 1577 KY-32, Louisa, KY 41230, USA
2019 | 2019-01-25 | Ashland | 72744649 |  | 38830477000075 |  | 3007903-BUSSEYVILLE / LOUISA | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Customers service drop is 7’ from deck. Meter # 533 517 296 - Notified DDC. | 68 Crooked Hill Dr, Louisa, KY 41230, USA | 2019-03-07
2019 | 2019-01-25 | Ashland | 72027630 | DKY0103042 | 38830477000238 | TRUE | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole is leaning (pole passed sound test). Concerned about tension on primary & neutral wires. Install: 1985 | 6 Greenbriaar Rd, Kentucky 41230, USA | 2022-09-04
2019 | 2019-01-25 | Ashland |  |  | 38830477A10358 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | 2 TV antennas on company pole. Dish and Direct TV Satellites. Direct tv connected | 350 Timberlake Dr, Louisa, KY 41230, USA
2019 | 2019-01-25 | Ashland |  |  | 38830477A40503 | TRUE | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | other: customer owned attachment | KPC |  | Customer owned OL and receptacle on company pole. | 110 Victory Ln, Louisa, KY 41230, USA | 2023-10-25
2019 | 2019-01-28 | Ashland |  |  | 38830453000074 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Cust. service drop is close to cust. rear deck. Several feet away from edge of deck. Can we get proper clearance by raising up service drop or installing a taller service pole? | 208 Chapel Rd, Louisa, KY 41230, USA
2019 | 2019-01-28 | Ashland | 71943085 | DKY0103029 | 38830453000121 | TRUE | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Inactive transformer. Cust. would like to have transformer removed. | 944 Two Mile Creek Rd, Louisa, KY 41230, USA | 2022-08-22
2019 | 2019-01-29 | Ashland | 77422494 | DKY0111207 | 38830429B00324 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | YES | Pole appears split or cracked close to transformer. Needs to be checked out. Remove inactive transformer. | 221 Bear Ln, Louisa, KY 41230, USA | 2020-12-21
2019 | 2019-01-29 | Ashland | 72219099 | DKY0103430 | 38830429D00140 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer, secondary and service pole (38830429D00317). Poles are close to Hwy 23 on Chestnut Dr. | Chestnut Dr, Kentucky 41230, USA | 2021-10-13
2019 | 2019-01-29 | Ashland | 72283135 | DKY0103627 | 38830429D00276 | TRUE | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Location of pole is close to Hwy 23 on Chestnut Dr. | Chestnut Dr, Kentucky 41230, USA | 2021-08-18
2019 | 2019-01-29 | Ashland | 72283135 | DKY0103627 | 38830429D06024 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. In field next to Hardee’s restaurant. | US-23, Louisa, KY, USA | 2021-08-18
2019 | 2019-01-29 | Ashland | 85541500 | DKY0121889 | 38830453000371 | TRUE | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Be cautious of dogs on property. | 863 Chapel Rd, Louisa, KY 41230, USA | 2023-12-04
2019 | 2019-01-30 | Ashland | 72283232 | DKY0103733 | 38830454A20127 | TRUE | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | US-23, Louisa, KY, USA | 2022-09-01
2019 | 2019-01-31 | Ashland | 72283166 | DKY0103638 | 38830430B00011 | TRUE | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer and OL. | Mimosa Rd, Kentucky 41230, USA | 2022-06-06
2019 | 2019-01-31 | Ashland |  |  | 38830430B09001 | TRUE | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Customers service drop houseknob is 6 feet from ground. Customer (Mrs. May) informed me that her service drop has been this way since the 1960s and that she stays away from it. On Fieldview pole # is 430-1. Meter # 533 677 644 | 658 Mimosa Rd, Louisa, KY 41230, USA
2019 | 2019-01-31 | Ashland |  |  | 38830453000287 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Xarm brace is broken. | US-23, Louisa, KY, USA
2019 | 2019-01-31 | Ashland |  |  | 38830454B22503 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | 608 KY-32, Louisa, KY, USA
2019 | 2019-02-01 | Ashland | 72219014 | DKY0103441 | 38830429C00424 | TRUE | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | US-23, Louisa, KY, USA | 2022-06-21
2019 | 2019-02-01 | Ashland | 72219014 | DKY0103441 | 38830429C00425 | TRUE | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer, 1/0 secondary and service pole (38830429C00426). Weigh station is torn down. | US-23, Louisa, KY, USA | 2022-06-21
2019 | 2019-02-01 | Ashland | 72219014 | DKY0103441 | 38830429C04017 | TRUE | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Loose 1/2” guy wire. Gate has company lock. | US-23, Louisa, KY, USA | 2022-06-21
2019 | 2019-02-07 | Ashland |  |  | 38830405000071 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Hewlet Branch Rd, Kentucky 41230, USA
2019 | 2019-02-08 | Ashland |  |  | 38830254D00459 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign |  | Pole appears split/cracked. Unable to sound pole because problem is to high to reach. Next to Dollar General store. Is there a problem here? | 3705 Highway 1 Hitchins, Ky. | 2019-02-20
2019 | 2019-02-11 | Ashland | 72743003 | DKY0104581 | 38830254D00161 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | Foreign |  | 2 spans of neutral stolen from pole # 254-161 to 254-282. | 109 Fraley Br., Hitchens, KY | 2021-01-26
2019 | 2019-02-11 | Ashland |  |  | 38830254D00424 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole set next to creek and soil appears washed out on creekside of pole. Pole needs to be looked at to check for proper pole depth. | 64 Bobcat Rd., Hitchens, KY | 2023-01-24
2019 | 2019-02-12 | Ashland | 83739489 |  | 38830254D00135 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | Foreign |  | 1 span of stolen neutral. | 4028 Hitchens Rd., Hitchens, KY | 2022-11-03
2019 | 2019-02-12 | Ashland |  |  | 38830278000021 |  | 3001002-HITCHINS / WILLARD | Service Work | OH | cutout: damaged |  |  | KPC |  | Silver-top cutout (12kv) - cutout is not damaged. | 298 Menifee Rd., Hitchens, KY | 2019-03-11
2019 | 2019-02-13 | Ashland | 72555385 | 103999 | 38830303000058 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | STOLEN NEUTRAL | KPC |  | 2 spans of neutral stolen (303-58 to 303-212). THIS IS ALREADY IN THE ABNORMAL AND SHOULD NOT HAVE BEEN ADDED IN HERE ABNORMAL #KY062617-1033-9035 | 425 Blue Bird Dr., Willard, KY | 2019-04-04
2019 | 2019-02-13 | Ashland |  |  | 38830303000062 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | lightning arresters/insulators: damaged |  | KPC |  | Customers service drop is 9’2” from ground. Arrester is damaged - arrester is attached to transformer. Dog on premise. | 239 EK Mines Branch Rd., Willard, KY | 2020-03-06
2019 | 2019-02-14 | Ashland | 76350432 | DKY0110053 | 38830278000088 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | cutout: damaged |  |  | KPC |  | 12 KV silver top cutout (cutout is not damaged). | 1042 Huffs Run, Willard, KY | 2020-06-23
2019 | 2019-02-14 | Ashland | 75091413 | DKY0108443 | 38830302000047 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer and OL. | Fields Branch Rd., Willard, KY | 2021-09-08
2019 | 2019-02-14 | Ashland | 73128425 | DKY0104967 | 38830326000113 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Primary guy wire broken and needs anchor. Do we need a guy wire here? Customers TV antenna on service pole (326-150). Dish HD Satellite | 5742 Hwy 1496, Willard, KY | 2022-05-13
2019 | 2019-02-14 | Ashland | 72537301 |  | 38830327A00135 |  | 3001002-HITCHINS / WILLARD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground missing to transformer. | 35 Duckeye Rd., Willard, KY | 2019-02-19
2019 | 2019-02-14 | Ashland | 75091404 | DKY0108118 | 38830327A40411 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Yellowstone Dr., Willard, KY | 2022-03-01
2019 | 2019-02-18 | Ashland | 84303677 | DKY0119711 | 38830350000021 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen. | State Highway 1122, Hitchens, KY | 2023-07-07
2019 | 2019-02-18 | Ashland | 80555707 | DKY0114802 | 38830326000061 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Soil has washed away around pole. Pole ground rod is exposed. | 484 Hwy 1122, Hitchens, KY | 2021-10-08
2019 | 2019-02-18 | Ashland | 73128433 | DKY0104929 | 38830350000055 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. There are 3 stolen neutrals to this transformer pole (326-82 to 350-55). Abnormal # KY022117-0640-8903. You can drive to the poles with the stolen neutrals. | State Highway 1496, Hitchens, KY | 2020-07-21
2019 | 2019-02-19 | Ashland | 84303735 | DKY0119712 | 38830350000078 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 3 spans of neutral stolen (350-78 to 374-4). | Hilton Branch Rd., Hitchens,KY | 2023-07-07
2019 | 2019-02-19 | Ashland | 73546119 | 0105326 | 38830373000003 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | 2 spans of primary down at 373-3 to 373-4. Broken pole 373-4 (35’ Class 7). Isolated at 374-14. Bre H. writing a WO to remove this entire line from pole #374-14 to 373-5 | Wells Branch Rd., Hitchens, KY | 2019-06-27
2019 | 2019-02-20 | Ashland |  |  | 38830351000090 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 3 spans of neutral stolen (351-90 to 350-15). | 913 Dry Ridge, Hitchens, KY | 2023-01-24
2019 | 2019-02-20 | Ashland |  |  | 38830351000093 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen (351-93 to 350-16). | 1110 Dry Ridge, Hitchens,KY | 2023-01-24
2019 | 2019-02-21 | Ashland | 75091413 | DKY0108443 | 38830327B00191 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive 3 phase bank. Customer that lives here said he would move cars out of the way so we can get company trucks to pole. Old Willard School | Willard School Ave., Willard, KY | 2021-09-08
2019 | 2019-02-21 | Ashland | 78685613 | DKY0112595 | 38830350000048 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen (350-48 to 350-49). | Black Hollow, Willard, KY | 2021-02-05
2019 | 2019-02-21 | Ashland | 78685613 | DKY0112595 | 38830350000050 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 1 span neutral stolen (350-50 to 350-52). | 585 Black Hollow, Willard, KY | 2021-02-05
2019 | 2019-02-21 | Ashland | 73128415 | DKY0104946 | 38830350000059 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Neighbor said that trailer has been vacant for years. Trailer is run down. | 240 Adams Hollow, Willard, KY | 2020-06-08
2019 | 2019-02-21 | Ashland |  |  | 38830350D40173 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen (350-172 to 350-173). | 1274 Dry Ridge, Louisa, KY | 2023-01-24
2019 | 2019-02-28 | Ashland |  |  | 38830327B00079 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 3 spans neutral stolen in the abnormal #KY061517-0423-9023 should not have been added to smartsheet | Willard School Ave., Willard, KY | 2020-11-20
2019 | 2019-02-28 | Ashland | 75091404 | DKY0108118 | 38830327C00110 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Taylor Br., Willard, Ky | 2022-03-01
2019 | 2019-02-28 | Ashland | 72680776 |  | 38830327D00098 |  | 3001002-HITCHINS / WILLARD | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Resag customers service drop (9’5”) to trailer. Meter # 533 584 729 | 2332 EK Mines Br. | 2019-03-11
2019 | 2019-02-28 | Ashland | 75091404 | DKY0108118 | 38830328000129 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Ratliff Number 1 Cem. Rd., Willard, KY | 2022-03-01
2019 | 2019-03-05 | Ashland | 70367202 | 101159 | 38830304000018 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole. Set in 1949. There are 9 stolen neutrals on this line. | 484 Ratliff Branch Rd., Willard, KY | 2019-04-15
2019 | 2019-03-05 | Ashland |  |  | 38830327D00355 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen (327-355 to 328-29). | 8369 Hwy 1496, Willard, KY | 2020-11-20
2019 | 2019-03-05 | Ashland | 72863601 | DKY0106853 | 38830328000054 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen (328-54 to 328-53). | 10317 Hwy 1496, Willard, KY | 2020-04-30
2019 | 2019-03-05 | Ashland | 72719394 |  | 38830328000064 |  | 3001002-HITCHINS / WILLARD | Service Work | UG | UG conduit: damaged or separated |  |  | KPC |  | UG conduit has come loose at ground level. Placed yellow caution tape around pole. | 1110 Reeves Hollow, Hitchins, KY | 2019-03-11
2019 | 2019-03-06 | Ashland | 73128438 | DKY0105103 | 38830329000083 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. 1 span of primary missing (329-82 to 329-83). | Lost Creek, Willard, KY | 2022-02-02
2019 | 2019-03-07 | Ashland | 72744086 |  | 38830351000083 |  | 3001002-HITCHINS / WILLARD | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Resag customers service drop (8’6” from ground). Meter # 533 510 381 | 867 Bells Trace Rd., Willard, KY | 2019-03-11
2019 | 2019-03-07 | Ashland | WR # 72743806 |  | 38830351000115 |  | 3001002-HITCHINS / WILLARD | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Remove service drop to vacant trailer. | 369 Bells Trace Rd., Willard, KY | 2019-03-13
2019 | 2019-03-07 | Ashland |  |  | 38830352000004 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 1 span of stolen neutral (352-4 to 352-5). | 1127 Bells Trace Rd., Willard, KY | 2021-01-20
2019 | 2019-03-07 | Ashland | 78306547 | DKY0111904 | 38830352000019 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen (352-19 to 352-20). | Bells Trace Rd., Willard, KY | 2021-01-06
2019 | 2019-03-07 | Ashland | 75091343 | DKY0108324 | 38830352C30099 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Customer wants transformer and service drop removed to his barn. | Bee Tree Fork, Willard, KY | 2022-01-10
2019 | 2019-03-07 | Ashland | 73211840 | DKY0104892 | 38830376000062 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Cutout open at 376-62. Pole 377-13 broken and laying on ground. 5 spans of neutral missing (377-11 to 377-15). 2 spans of primary laying on ground (377-12 to 377-14). | Bentley Branch Rd., Willard, KY | 2019-07-26
2019 | 2019-03-11 | Ashland | 73251496 | DKY0105067 | 38830375000060 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Xarm is leaning and causing tension and splitting to xarm braces. | 580 Lick Creek Rd., Willard, KY | 2019-09-25
2019 | 2019-03-12 | Ashland | 72801200 |  | 38830376000092 |  | 3001002-HITCHINS / WILLARD | Service Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Transformer ground connection has come loose and lightning arrester is damaged (Maranatha Bible Church). | Maranatha Lane Hwy 201, Willard, KY | 2019-03-13
2019 | 2019-03-12 | Ashland | 78649162 | DKY0112491 | 38830472000039 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 2 spans of neutral stolen (472-43 to 472-44). | 86 Lick Fork Rd, Webbville, KY 41180, USA | 2021-12-15
2019 | 2019-03-13 | Ashland | 75091343 | DKY0108324 | 38830376000017 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Top double xarm is splitting. Bolt going threw bottom double xarm. | Hwy 201 & Maranatha Lane, Webbvile, KY | 2022-01-10
2019 | 2019-03-13 | Ashland |  |  | 38830496000006 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | KPC pole next to roadway. Part of soil shaved off from road travel. Is pole at proper depth? Pole is not leaning. | Parker Fork Rd., Cherokee, KY | 2019-04-26
2019 | 2019-03-18 | Ashland | 73492568 | 105268 | 38830377000059 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen (377-59). Across from 8840 Hwy 1. | Hwy 1, Webville, KY | 2019-06-11
2019 | 2019-03-18 | Ashland | 75091343 | DKY0108324 | 38830401000021 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Across from 8501 Hwy 1. | Hwy 1, Webville, Ky | 2022-01-10
2019 | 2019-03-18 | Ashland | 73492568 | 105268 | 38830401000026 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 7 spans of neutral stolen (401-26 to 401-19). | Hwy 1, Webville, KY | 2019-06-11
2019 | 2019-03-22 | Ashland |  |  | 38830182B43686 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | One of the double xarms (top xarms) is splitting at insulator connection. Will these xarms last another 2 years? Next to trailer park. | N Hord St, Grayson, KY 41143, USA | 2019-04-26
2019 | 2019-03-22 | Ashland | WR# 72887938 |  | 38830182B43738 |  | 3116102-GRAYSON / DIXIEPARK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground to 3 phase transformers stolen. | 493 Carol Malone Blvd, Grayson, KY 41143, USA | 2019-03-26
2019 | 2019-03-22 | Ashland | WR# 72889271 |  | 38830206A31222 |  | 3116102-GRAYSON / DIXIEPARK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground to transformer stolen. | 206 E 2nd St, Grayson, KY 41143, USA | 2019-03-25
2019 | 2019-03-25 | Ashland | 73251624 | 105233 | 38830182B43557 | TRUE | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC |  | Base of pole deteriorated. Has a Pole Enforcer attached to pole. | 315 E 5th St, Grayson, KY 41143, USA | 2019-08-09
2019 | 2019-03-25 | Ashland | 72928077 |  | 38830182B43591 |  | 3116102-GRAYSON / DIXIEPARK | Service Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Damaged arrester | 520 Rupert Ln, Grayson, KY 41143, USA | 2019-03-27
2019 | 2019-03-26 | Ashland | WR # 72915193 |  | 38830206A31157 |  | GRAYSON - DIXIE PARK / 1161-02 | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground to UG primary cutouts. Pole tag has 206-1278 | 102 Carol Malone Blvd, Grayson, KY 41143, USA | 2019-03-28
2019 | 2019-03-26 | Ashland | WR # 72915193 |  | 38830206A31157 |  | 3116102-GRAYSON / DIXIEPARK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground to UG primary cutouts. Pole tag has 206-1278 | 102 Carol Malone Blvd, Grayson, KY 41143, USA | 2019-03-28
2019 | 2019-03-26 | Ashland | 72915346 |  | 38830206A31272 |  | 3116102-GRAYSON / DIXIEPARK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground to 3 phase bank stolen. | 102 Carol Malone Blvd, Grayson, KY 41143, USA | 2019-03-27
2019 | 2019-03-27 | Ashland | 76343767 | DKY0110047 | 38830183A00092 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign |  | Pole is leaning. Primary from pole 183-92 to 183-162 is 1 to 2 feet away from neutral. Pole 183-162 is leaning too. Install: 2002 | 1035 Beckwith Branch Rd, Grayson, KY 41143, USA | 2021-09-07
2019 | 2019-03-27 | Ashland | 76343767 | DKY0110047 | 38830183A00094 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. | Beckwith Branch Rd, Grayson, KY 41143, USA | 2021-09-07
2019 | 2019-03-27 | Ashland | 76343767 | DKY0110047 | 38830183A00095 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Beckwith Branch Rd, Grayson, KY 41143, USA | 2021-09-07
2019 | 2019-03-28 | Ashland | 76343684 | DKY0110041 | 38830183B00042 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | Resag primary & neutral. Distance between pole 183-42 to 183-138 (397 feet). Primary is 15.5’ and neutral 12’ from ground. | 1630 E Midland Trail, Grayson, KY 41143, USA | 2021-12-17
2019 | 2019-03-29 | Ashland | 72982342 |  | 38830206C02025 |  | 3116102-GRAYSON / DIXIEPARK | Service Work | OH | UG conduit: damaged or separated |  |  | KPC |  | UG conduit has come loose at base of pole. I placed yellow caution tape around pole area. | 112 KY-1, Grayson, KY 41143, USA | 2019-04-02
2019 | 2019-04-01 | Ashland | 76343684 | DKY0110041 | 38830206D02314 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign |  | 5/8” guy wire is broken and needs anchor (unable to locate). | Woodmill Dr, Grayson, KY 41143, USA | 2021-12-17
2019 | 2019-04-04 | Ashland |  |  | 38830255000025 | TRUE | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace rotten pole. Large bush next to pole, need to be removed to make work area safer to work. Pole next to 58 Coal CP. Material laying in yard and needs to be cleared out for truck accessibility. | Coal CP, Hitchens, KY
2019 | 2019-04-04 | Ashland | 73129784 |  | 38830255000033 |  | 3001001-HITCHINS / DENTON | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign |  | Resag 2 spans of neutral and 3 wire secondary from pole 255-33 to 255-35. Neutral & secondary same level as telephone and TV cable. These wires are not touching (8-10”) but high wind could cause problems. | 440 Coal CP, Hitchens, KY | 2019-04-17
2019 | 2019-04-04 | Ashland | 76343295 | DKY0110001 | 38830255000090 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign |  | Secondary guy wire (5/8”) is loose. | Clay CP, Hitchens, Ky. | 2022-01-10
2019 | 2019-04-08 | Ashland |  |  | 38830255000137 |  | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace rotten pole. | 749 Katy Br., Hitchens Ky.
2019 | 2019-04-08 | Ashland | 73128452 | DKY0104881 | 38830280000089 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Glancy Fork, Hitchens, Ky. | 2021-08-25
2019 | 2019-04-08 | Ashland | 75986540 |  | 38830280000097 |  | 3001001-HITCHINS / DENTON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Remove service drop. Meter and trailer has been removed.liffed hot tap on Xfr denergizing service and duplex ,,, customer says they gonna put mobile home back | 129 Shop Br., Hitchens, Ky. | 2020-03-05
2019 | 2019-04-08 | Ashland |  |  | 38830280A10232 |  | 3001001-HITCHINS / DENTON | Line Work | OH | joint use attachments: clearance issues |  |  | KPC |  | 2 satellite dishes on KPC pole. Trailer has been removed from premise (vacant). | 129 Shop Br., Hitchens, Ky. | 2021-01-15
2019 | 2019-04-08 | Ashland | 76343295 | DKY0110001 | 38830280D20046 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen. | Allen Rd., Hitchens Ky. | 2022-01-10
2019 | 2019-04-09 | Ashland | 73128555 | DKY0104934 | 38830280000214 | TRUE | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | already written to EDN100577 KPC pole | Replace pole because of pole top extension. This location is on a muddy private drive and is going uphill. There is a pit bull on premise, it acts friendly but use caution, if possible have dog locked up. | 1123 Glancy Fork, Hitchens, Ky. | 2021-02-04
2019 | 2019-04-09 | Ashland | 73128446 | DKY0106059 | 38830305000048 | TRUE | 3001001-HITCHINS / DENTON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Broken xarm brace. | Hwy 773, Hitchens, Ky. | 2020-03-17
2019 | 2019-04-09 | Ashland | 73128446 | DKY0106059 | 38830305000065 | TRUE | 3001001-HITCHINS / DENTON | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | 12 KV arrester damaged. | 10697 Hwy 773, Hitchens Ky. | 2020-03-17
2019 | 2019-04-09 | Ashland | 76343295 | DKY0110001 | 38830306000178 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Behind Bolts Fork Baptist Church. | Bolts Fork Rd, Kentucky 41168, USA | 2022-01-10
2019 | 2019-04-10 | Ashland | 75091248 | DKY0107894 | 38830329000036 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Down over hillside from 4267 Hwy 1496. | Hwy 1496, Hitchens, Ky | 2020-03-27
2019 | 2019-04-15 | Ashland | 73128438 | DKY0105103 | 38830353000030 | TRUE | 3001001-HITCHINS / DENTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer and 1/0 secondary. Possibly remove small trees next to pole you could possible get line truck to pole. | Knotty Poplar Rd., Hitchens, Ky | 2022-02-02
2019 | 2019-04-17 | Ashland | 72048827 | DKY0103235 | 38830502000154 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | West Silver Fox Drive, Kentucky 41230, USA | 2019-11-05
2019 | 2019-04-22 | Ashland | 78676807 | DKY0112535 | 38830357000025 | TRUE | 3000202-BIG SANDY / BURNAUGH NORTH | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen. | 3339 Blaine Creek Rd, Louisa, KY 41230, USA | 2022-08-18
2019 | 2019-04-22 | Ashland | 72048815 | DKY0103100 | 38830502000232 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Honeydew Dr, Kentucky 41230, USA | 2019-09-11
2019 | 2019-04-23 | Ashland | T.T. # 4149591 |  | 38830478C17016 |  | 3007906-Busseyville / Walbridge | Line Work | UG | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC |  | UG transformer moved on its foundation. Small opening in font of transformer. Notified DDC. | 1999 Fern Dr, Louisa, KY 41230, USA | 2019-12-05
2019 | 2019-04-23 | Ashland | T.T. # 4149261. Field generated order 73199980 |  | 38830502000002 |  | 3007906-Busseyville / Walbridge | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Found service drop laying on ground. Transformer fuse is blown. Notified DDC. | 1144 | 2019-04-25
2019 | 2019-04-24 | Ashland | 72317919 | DKY0103752 | 38830478D20158 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. 1626 Hwy 644, Louisa. | Louisa, KY 41230, USA | 2019-08-26
2019 | 2019-04-24 | Ashland | 72048815 | DKY0103100 | 38830502000111 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | 1265 Walbridge Rd, Louisa, KY 41230, USA | 2019-09-11
2019 | 2019-04-25 | Ashland | 72048480 | DKY0103045 | 38830526000045 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Pole 526-89: pole is broken at base and laying on ground. Pole 526-88: remove pole. Pole 526-45: remove inactive transformer and hardware (1/0 secondary). I wrote this up 2 years ago. | Highway 1690, Louisa, KY | 2019-08-19
2019 | 2019-04-25 | Ashland | 74058484 | DKY0105987 | 38830527000029 |  | 3007906-Busseyville / Walbridge | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Damaged 12 KV arrester. Columbia Gas Trans Corp tower. | Threemile Creek Rd, Kentucky 41230, USA | 2020-02-11
2019 | 2019-04-26 | Ashland | 72049068 | DKY0103123 | 38830526000047 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Threemile Creek Rd, Kentucky 41230, USA | 2019-08-19
2019 | 2019-04-26 | Ashland | 75460397 | DKY0107879 | 38830550C30152 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole is leaning possibly due to hill slipping. Down from Emily Northup Missionary Baptist Church. Install: 2006 | Highway 1690, Louisa, KY | 2020-01-21
2019 | 2019-04-29 | Ashland | 74058471 | DKY0106024 | 38830502000178 |  | 3007906-Busseyville / Walbridge | Line Work | OH |  |  |  | KPC |  | 2 spans of neutral stolen (502-178 to 502-43). | Walbridge Rd, Kentucky 41230, USA | 2020-01-09
2019 | 2019-04-30 | Ashland | 77422358 | DKY0110800 | 38830550000069 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | YES | Remove inactive transformer. Next to 2197 Hwy 2037 WO WRITTEN BUT CREW DETERMINED POLE NEEDS REPLACED - REDLINED OFF WORK ON THIS POLE - 04/20/20 NEED WORK ORDER TO REPLACE POLE 1946 model KPC pole 45'4 | Chapman, KY 41230, USA | 2022-04-19
2019 | 2019-04-30 | Ashland | 73266498 |  | 38830550000129 |  | 3007906-Busseyville / Walbridge | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Broken pole ground to transformer. Pole located at Chapman Community Park. | Chapman St, Kentucky 41230, USA | 2019-05-02
2019 | 2019-04-30 | Ashland | 73266548 |  | 38830550B20167 |  | 3007906-Busseyville / Walbridge | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Stolen pole ground. Pole located on Hwy 2037. | Chapman, KY 41230, USA | 2019-05-02
2019 | 2019-05-01 | Ashland | 72133600 | DKY0103417 | 38830599000018 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Walker Fork, Chapman, KY | 2019-11-20
2019 | 2019-05-02 | Ashland | 72317919 | DKY0103752 | 38830478D40332 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | KY-644, Louisa, KY 41230, USA | 2019-08-26
2019 | 2019-05-02 | Ashland | 72426771 | DKY0103934 | 38830479B00010 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Top xarms are splitting and bowing. | KY-3, Louisa, KY, USA | 2019-09-27
2019 | 2019-05-02 | Ashland | 72426771 | DKY0103934 | 38830479B00019 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | KY-3, Louisa, KY, USA | 2019-09-27
2019 | 2019-05-02 | Ashland | 74058471 | DKY0106024 | 38830479B09006 |  | 3007906-Busseyville / Walbridge | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Xarm showing signs of deterioration and splitting. | KY-3, Louisa, KY, USA | 2019-12-05
2019 | 2019-05-03 | Ashland | 72426771 | DKY0103934 | 38830503A30037 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Broken and deteriorated double xarm. Right away is clear but will need manual tree crew to clear path to pole. Pole is on a difficult hillside. If given permission from customer trucks can park and walk to pole from 3350 Hwy 3. I wrote this up 2 years ago. | 3350 KY-3, Louisa, KY 41230, USA | 2019-09-27
2019 | 2019-05-03 | Ashland | 74058484 | DKY0105987 | 38830503C20042 |  | 3007906-Busseyville / Walbridge | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Neutral has come loose and laying below neutral clevis. | Highway 3, Louisa, Ky | 2020-02-11
2019 | 2019-05-06 | Ashland | 72048849 | DKY0103083 | 38830551000029 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Donithon Rd., Louisa, KY | 2019-10-14
2019 | 2019-05-06 | Ashland | 72049234 | DKY0103162 | 38830551000072 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Red Maple Lane, Louisa, KY | 2019-10-30
2019 | 2019-05-06 | Ashland | 74058484 | DKY0105987 | 38830552A00547 |  | 3007906-Busseyville / Walbridge | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | One of the arms of the double xarm is splitting. | Highway 3, Louisa, KY | 2019-12-05
2019 | 2019-05-07 | Ashland | 72219211 | DKY0103615 | 38820577A01011 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | 1291 River Rd., Louisa, KY | 2019-12-16
2019 | 2019-05-07 | Ashland | 72426783 | DKY0103937 | 38830503D10050 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Top double xarm splitting. Next to 4421 Hwy 3. | KY-3, Louisa, KY, USA | 2019-09-18
2019 | 2019-05-07 | Ashland | 72426712 | DKY0103810 | 38830552B00564 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Damaged 34KV arrester. | Maynard Branch Rd., Louisa, KY | 2020-01-23
2019 | 2019-05-08 | Ashland | 73347023 |  | 38830478A47172 |  | 3007906-Busseyville / Walbridge | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Need to raise customers service drop. Service drop is 8’8” over customers rear deck. | 97 E Clayton Ln, Louisa, KY 41230, USA | 2019-05-10
2019 | 2019-05-08 | Ashland | 74058471 | DKY0106024 | 38830479B00001 |  | 3007906-Busseyville / Walbridge | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | 1/2” primary guy wire broken. Unable to locate anchor, will need a new one. | KY-644, Louisa, KY 41230, USA | 2020-01-27
2019 | 2019-05-08 | Ashland | 74058484 | DKY0105987 | 38830599000031 |  | 3007906-Busseyville / Walbridge | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen (599-31 to 600-12). | 12530 Highway 3, Louisa, KY | 2020-02-11
2019 | 2019-05-08 | Ashland | 72133633 | DKY0103284 | 38830600000077 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Broken 5/8” guy wire. Guy anchor is there and in good shape. | 185 Pruitt Branch Rd., Louisa, KY | 2019-11-13
2019 | 2019-05-08 | Ashland | 72133633 | DKY0103284 | 38830600000090 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Highway 3, Louisa, KY | 2019-11-13
2019 | 2019-05-09 | Ashland | 72133600 | DKY0103417 | 38830575000018 | TRUE | 3007906-Busseyville / Walbridge | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Across from 1858 Donithon Rd. | Donithon Road, Louisa, KY | 2019-11-20
2019 | 2019-05-16 | Ashland | 74058471 (completed 8/10) | 106024 | 38830503A30034 |  | 3007906-Busseyville / Walbridge | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Neutral is 3.5’ from ground. I climbed hillside to check out this area. I did not take iPad with me to take pictures in fear of dropping it and also hindering my climb. Can be re sagged mid span from Sourwood Drive | 3540 KY-3, Louisa, KY 41230, USA | 2019-08-10
2019 | 2019-05-20 | Ashland | 73518736 |  | 38830501000439 |  | 3007905-Busseyville / Mattie | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen. | 374 Poor House Hill Rd., Louisa, KY 41230, USA | 2019-05-31
2019 | 2019-05-20 | Ashland | 73458240 |  | 38830501000502 |  | 3007905-Busseyville / Mattie | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Secondary needs to be raised due to it bumping against telephone wire when wind blows. | 568 Red Branch Rd., Louisa, KY | 2019-05-22
2019 | 2019-05-20 | Ashland | 72317956 | DKY0103792 | 38830501B40577 | TRUE | 3007905-Busseyville / Mattie | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Swift Lane, Louisa, KY 41230, USA | 2022-08-22
2019 | 2019-05-21 | Ashland | 76350562 | DKY0109721 | 38830524000188 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. | Left Fork Little Blaine Rd, Kentucky 41230, USA | 2021-10-13
2019 | 2019-05-21 | Ashland | 82418147 | DKY0117063 | 38830524000191 | TRUE | 3007905-Busseyville / Mattie | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. | Left Fork Little Blaine Rd, Kentucky 41230, USA | 2022-07-08
2019 | 2019-05-22 | Ashland | 76350562 | DKY0109721 | 38830548000051 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Left Fork Little Blaine Creek Rd, Kentucky 41230, USA | 2021-10-13
2019 | 2019-05-22 | Ashland | 76350558 | DKY0109643 | 38830572000062 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. | Left Fork Little Blaine Creek Rd, Kentucky 41230, USA | 2021-10-13
2019 | 2019-05-23 | Ashland | 76350579 | DKY0109317 | 38830524000095 |  | 3007905-Busseyville / Mattie | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Replace pole - burning at top of pole from past trouble. Install: 1990 | 30 Ivory Rd, Louisa, KY 41230, USA | 2020-04-21
2019 | 2019-05-23 | Ashland | 72133508 | DKY0103222 | 38830547000135 | TRUE | 3007905-Busseyville / Mattie | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Apple Hollow Rd., Louisa, KY | 2021-10-20
2019 | 2019-05-23 | Ashland | 76350558 | DKY0109643 | 38830572000011 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Left Fork Little Blaine Rd, Kentucky 41230, USA | 2021-10-13
2019 | 2019-05-28 | Ashland |  |  | 38830254D00250 | TRUE | 3001004-HITCHINS / E K ROAD | Line Work | OH |  |  |  | Foreign | NO | 2 spans neutral stolen, 254-250 to 254-251. | 39 Powell Hollow, Grayson, KY 41143, USA
2019 | 2019-05-28 | Ashland | 72283457 | DKY0103719 | 38830547000035 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | 584 Mattie Rd., Mattie, KY | 2021-10-13
2019 | 2019-05-28 | Ashland | 72133475 | DKY0103199 | 38830571000058 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Newcombe Hollow Rd., Mattie, KY | 2021-10-13
2019 | 2019-05-28 | Ashland | 72133475 | DKY0103199 | 38830594000009 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Mattie Rd., Mattie, KY | 2021-10-13
2019 | 2019-05-30 | Ashland | 76095363 |  | 38830499000093 |  | 3007905-Busseyville / Mattie | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Service drop house knob has come loose from customers pole. Need reattached. | 211 Dry Ridge Rd, Adams, KY 41201, USA | 2020-03-19
2019 | 2019-05-31 | Ashland | 76095388 |  | 38830499000132 |  | 3007905-Busseyville / Mattie | Service Work | UG | UG conduit: damaged or separated |  |  | KPC |  | UG conduit has come loose at base of pole. Placed yellow caution tape around area. 50 Lake Ridge Rd. | Lake Ridge Rd, Kentucky 41201, USA | 2020-03-19
2019 | 2019-05-31 | Ashland | 72317932 | DKY0103790 | 38830499A30167 | TRUE | 3007905-Busseyville / Mattie | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Broken 1/2” guy wire. Unable to locate guy anchor. | 1761 Dry Ridge Rd, Adams, KY 41201, USA | 2022-08-22
2019 | 2019-05-31 | Ashland | 72048544 | DKY0103065 | 38830523000144 | TRUE | 3007905-Busseyville / Mattie | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | KY-32, Louisa, KY, USA | 2022-06-13
2019 | 2019-06-03 | Ashland | 84369130 | DKY0119527 | 38830497000100 |  | 3007905-Busseyville / Mattie | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole is leaning toward road. It appears hillside is slipping. Neighbor informed me the pole started leaning about a month ago. Install: unknown | Irish Creek Rd, Kentucky, USA | 2023-05-31
2019 | 2019-06-03 | Ashland | 72317932 | DKY0103790 | 38830522D10225 | TRUE | 3007905-Busseyville / Mattie | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Pole next to 692 Top of the World Dr. | Top of World Dr, Kentucky, USA | 2022-08-22
2019 | 2019-06-04 | Ashland |  |  | 38830473000084 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Oak Hill Rd, Kentucky 41180, USA
2019 | 2019-07-02 | Ashland |  |  | 38830327B00048 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen. | 464 Dry Ridge, Grayson, KY 41143, USA
2019 | 2019-07-03 | Ashland |  |  | 38830547C40168 |  | 3007905-Busseyville / Mattie | Forestry | OH |  |  | Vines at this location appear to be 100% dead at this time (5/12/2020). Will re-evaluate on regular maintenance cycle. | KPC |  | Thick vines growing up pole and on xarms. | 1855 Hwy 1760, Louisa Ky | 2020-05-12
2019 | 2019-07-08 | Ashland | 76343474 | DKY0109949 | 38830254C00148 |  | 3001004-HITCHINS / E K ROAD | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign |  | Broken primary guy wire. Needs to be replaced with 1/2” wire. | 100 Hill Top Dr, Grayson, KY 41143, USA | 2022-02-21
2019 | 2019-07-08 | Ashland | 76343474 | DKY0109949 | 38830254C00149 | TRUE | 3001004-HITCHINS / E K ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 119 Hilltop Dr, Grayson, KY 41143, USA | 2022-02-21
2019 | 2019-07-08 | Ashland | 76343474 | DKY0109949 | 38830254C00314 | TRUE | 3001004-HITCHINS / E K ROAD | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign |  | Broken primary guy wire. Will need guy anchor installed. | 3188 KY-1, Grayson, KY 41143, USA | 2022-02-21
2019 | 2019-07-08 | Ashland | 76350429 | DKY0110256 | 38830254C04019 |  | 3001004-HITCHINS / E K ROAD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Customers service drop is 15 to 16 feet over customers above ground pool. Transformer # 38830254C00283 | 356 Winding Way Ln, Grayson, KY 41143, USA | 2022-02-21
2019 | 2019-07-10 | Ashland | 75048522 | DKY0107341 | 38830254B00238 | TRUE | 3001004-HITCHINS / E K ROAD | Line Work | OH |  |  |  | Foreign |  | 1 span neutral stolen (254-238 to 254-237). Neutral hanging down pole (254-238), called DDC for TT to remove wire or nail to pole. | 1360 State Hwy 1444, Grayson, KY 41143, USA | 2020-02-04
2019 | 2019-07-10 | Ashland | 75091443 | DKY0109032 | 38830254B00316 |  | 3001004-HITCHINS / E K ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 1040 Edison Rd, Grayson, KY 41143, USA | 2021-09-16
2019 | 2019-07-10 | Ashland | 75048522 | DKY0107341 | 38830254D00268 |  | 3001004-HITCHINS / E K ROAD | Line Work | OH |  |  |  | Foreign |  | 1 span neutral stolen (254-268 to 254-269) on Powell Hollow. | Cr-1222, Kentucky 41143, USA | 2020-02-04
2019 | 2019-07-10 | Ashland | 75091432 | DKY0118794 | 38830254D00388 | TRUE | 3001004-HITCHINS / E K ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 601 Powell Hollow, Grayson, Ky
2019 | 2019-07-10 | Ashland | 75091305 | DKY0108070 | 38830254D16053 | TRUE | 3001004-HITCHINS / E K ROAD | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Guy (1/2”) attachment has come loose from guy rod. Need guy marker installed, guy next to road. | 597 State Hwy 1444, Grayson, KY 41143, USA | 2022-02-28
2019 | 2019-07-11 | Ashland | 76343474 | DKY0109949 | 38830230000089 |  | 3001004-HITCHINS / E K ROAD | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC |  | Pole is leaning. Pole pass sound test and is not cracked. Do we need to attach another guy wire to straighten pole? Install: 2002 | 124 Lakewood Dr, Grayson, KY 41143, USA | 2022-02-21
2019 | 2019-07-12 | Ashland | 74262624 | DKY0107058 | 38830206B02097 |  | 3001004-HITCHINS / E K ROAD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Xarms are not deteriorated. Top double xarm - there is space between xarm and pole. There appears a hole below primary guy attachment. Is there a problem here? | Lakepoint Dr, Grayson, KY 41143, USA | 2020-02-17
2019 | 2019-07-12 | Ashland | 75048522 | DKY0107341 | 38830254B00238 | TRUE | 3001004-HITCHINS / E K ROAD | Line Work | OH |  |  |  | Foreign |  | 5 spans of neutral stolen. | 1360 State Hwy 1444, Grayson, KY 41143, USA | 2020-02-04
2019 | 2019-07-15 | Ashland | 76343383 | DKY0109915 | 38830254C00070 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | KY-1, Grayson, KY, USA | 2022-10-05
2019 | 2019-07-16 | Ashland |  |  | 38830206C02263 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | Poplar Heights Dr & Chestnut St, Grayson, KY 41143, USA
2019 | 2019-07-16 | Ashland | 85770339 | DKY0121751 | 38830206C02383 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 222 Poplar Heights Dr, Grayson, KY 41143, USA | 2023-08-22
2019 | 2019-07-16 | Ashland |  |  | 38830206C02445 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Pole is located in Trimble Lodge parking lot. | 981 E US-60, Grayson, KY 41143, USA
2019 | 2019-07-16 | Ashland |  |  | 38830207000255 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole set in creek bed. Soil and rocks appear washed away. Is pole at proper depth? Unable to locate pole birthmark and pole ground is exposed. | 517 Damron Branch Rd, Grayson, KY 41143, USA
2019 | 2019-07-16 | Ashland |  |  | 38830207A00061 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole set in creek bed. Soil appears washed away. Is pole at proper depth? Unable to locate pole birthmark and pole ground is exposed. | 308 Damron Branch Rd, Grayson, KY 41143, USA
2019 | 2019-07-16 | Ashland |  |  | 38830207A00136 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 1096 Charles St, Grayson, KY 41143, USA
2019 | 2019-07-16 | Ashland |  |  | 38830207A00142 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 1105 Charles St, Grayson, KY 41143, USA
2019 | 2019-07-16 | Ashland | 75971949 |  | 38830230000132 |  | 3001003-HITCHINS / GRAYSON | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND , service: unused or abandoned, blanked meter base |  |  | Foreign |  | Pole ground is broken. Meter has been removed and blanked off to trailer pole - need service drop removed. | 50 Damron St, Grayson, KY 41143, USA | 2020-03-04
2019 | 2019-07-16 | Ashland | 75963929 |  | 38830230000133 |  | 3001003-HITCHINS / GRAYSON | Service Work | UG | UG conduit: damaged or separated |  |  | Foreign |  | Bottom UG conduit needs to be lowered down - wires are exposed at ground line. Weed eating could cause a problem. Placed yellow caution tape around area. | 1382 Damron Branch, Grayson, KY 41143, USA | 2020-03-03
2019 | 2019-07-17 | Ashland | 76343383 | DKY0109915 | 38830207000129 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. |  | 2022-10-05
2019 | 2019-07-17 | Ashland | 75975313 |  | 38830207002020 |  | 3001003-HITCHINS / GRAYSON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC |  | Remove inactive service drop. Next to Lot 18 | 1010 Stinson Rd, Grayson, KY 41143, USA | 2020-03-04
2019 | 2019-07-17 | Ashland | 76343383 | DKY0109915 | 38830207A00033 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. Across 1725 Carroll Rd. | Carroll Cir, Grayson, KY 41143, USA | 2022-10-05
2019 | 2019-07-17 | Ashland | 75738966 | 31896789 | 38830207A00230 |  | 3001003-HITCHINS / GRAYSON | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign |  | Customers trailer (vacant) pole is leaning on trailer. Base of trailer pole is deteriorated, could possibly fall to ground. Trailer is next to 205 Stone St. - remove service drop. | Stone St, Grayson, KY 41143, USA | 2020-02-04
2019 | 2019-07-17 | Ashland | 75738465 | 38987943 | 38830231000151 |  | 3001003-HITCHINS / GRAYSON | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign |  | Found small tree laying on neutral. Between pole 231-151 to 231-152. Called DDC for TT. | 1999 Stinson Rd, Grayson, Ky. | 2020-02-04
2019 | 2019-07-17 | Ashland |  |  | 38830231000181 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Customers service drop is going over their above ground swimming pool (14 feet). I did not take pictures because customer came out and told me he was not moving his swimming pool. He was not threatening. He was very nice about it. | 1950 Stinson Rd, Grayson, KY 41143, USA
2019 | 2019-07-19 | Ashland | 76343426 | DKY0110087 | 38830183B00180 |  | 3001003-HITCHINS / GRAYSON | Line Work | UG | guys/anchors: broken or missing , UG conduit: damaged or separated |  |  | Foreign |  | UG conduit has come loose at base of pole. Placed yellow caution tape around pole. Replace broken guy wire and add guy anchor. | 1753 US-60, Grayson, KY 41143, USA | 2022-09-28
2019 | 2019-07-19 | Ashland | 76343383 | DKY0109915 | 38830208000057 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Stinson Rd, Kentucky 41143, USA | 2022-10-05
2019 | 2019-07-19 | Ashland |  |  | 38830232000039 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 2752 Stinson Rd., Grayson, Ky.
2019 | 2019-07-22 | Ashland |  |  | 38830183D00195 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 407 Damron Mayo Rd, Grayson, KY 41143, USA
2019 | 2019-07-23 | Ashland | 76343426 | DKY0110087 | 38830183D00184 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign |  | Tree limbs laying on primary guy wire (tension on guy wire) need to be removed. Guy wire broken on pole and anchor needs to be installed. | 201 Damron Mayo Rd, Grayson, KY 41143, USA | 2022-09-28
2019 | 2019-07-23 | Ashland |  |  | 38830183D00186 |  | 3001003-HITCHINS / GRAYSON | Forestry | OH |  |  |  | Foreign |  | Vines covering pole. Vines have gotten into primary and transformer. Forestry: Location is known and identified - Circuit is on 2021 work plan. | 223 Damron Mayo Rd, Grayson, KY 41143, USA | 2020-12-04
2019 | 2019-07-23 | Ashland | 82106717 | DKY0116760 | 38830208000012 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | lightning arresters/insulators: damaged |  | Foreign | YES | Top of pole burnt (not burning now). Transformer arrester damaged. | 3451 Stinson Rd, Grayson, Ky. | 2022-04-21
2019 | 2019-07-24 | Ashland | 76343426 | DKY0110087 | 38830208000006 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. | Tark Hill Rd, Kentucky 41143, USA | 2022-09-28
2019 | 2019-07-25 | Ashland | 82839366 | DKY0117500 | 38830183D00034 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is set on side of creek bed. Soil appears washed away. Unable to locate pole birthmark and height is not indicated in info box. Is there a problem here? | 434 Tark Hill Rd, Grayson, KY 41143, USA | 2023-12-04
2019 | 2019-07-29 | Ashland | 76344374 | DKY0109349 | 38830206A31166 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole. | 127 E Main St, Grayson, KY 41143, USA | 2020-06-25
2019 | 2019-07-30 | Ashland |  |  | 38830206A22160 |  | 3116101-GRAYSON / LANSDOWNE | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign |  | Heavy vines on pole and covering transformer and up in primary. Forestry: Completed on 2020 circuit clearing. | 271 S Hord St, Grayson, KY 41143, USA | 2020-10-16
2019 | 2019-07-30 | Ashland | 76343606 | DKY0110008 | 38830206A32531 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign |  | Arrester damaged. | 106 Ruth St, Grayson, KY 41143, USA | 2020-07-01
2019 | 2019-07-30 | Ashland | 76343606 | DKY0110008 | 38830206A42522 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign |  | Primary guy wire broken. Guy rod is already there. | Little Sandy Ln & Carol Malone Blvd, Grayson, KY 41143, USA | 2020-07-01
2019 | 2019-07-30 | Ashland | 76343606 | DKY0110008 | 38830206A42544 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Primary pin insulator has come loose from xarm. It is 252 feet from pole 206-2456. Located next to Adams plumbing. I don’t see any danger at this time but it needs to be taken care of when possible. | 236 Carol Malone Blvd, Grayson, KY 41143, USA | 2020-07-01
2019 | 2019-07-31 | Ashland |  |  | 38830206A10104 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 619 Holcomb St, Grayson, KY 41143, USA
2019 | 2019-07-31 | Ashland | 74332672 | DKY0106476 | 38830502000058 |  | 3007906-Busseyville / Walbridge | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Pole is badly bowed, arms are rotten, B phase loop is nearly burned into | Intersection of 644 and 1690 | 2019-09-27
2019 | 2019-08-01 | Ashland | 73128485 | DKY0104902 | 38830181C00151 | TRUE | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Broken guy wire, will need guy rod installed. Upper insulating guy attachment laying on transformer. | 232 Windy Creek, Grayson, KY 41143, USA | 2022-03-11
2019 | 2019-08-02 | Ashland | 75738634 |  | 38830180000044 |  | 3116101-GRAYSON / LANSDOWNE | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Meter removed to trailer and blanked off, remove service drop. | 115 Gilbert Rd, Grayson, KY 41143, USA | 2020-02-04
2019 | 2019-08-02 | Ashland | 85538941 | DKY0121445 | 38830181B00072 | TRUE | 3116101-GRAYSON / LANSDOWNE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Insulator missing in neutral clevis. | Stan Branch Rd, Kentucky 41143, USA | 2023-10-24
2019 | 2019-08-05 | Ashland |  |  | 38830180000010 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | 499 Smith Branch Rd, Olive Hill, KY 41164, USA | 2020-05-19
2019 | 2019-08-06 | Ashland | 73251584 | DKY0105101 | 38830181C00032 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Resag neutral. Neutral touching Service drop, TV and telephone. | 1950 KY-1947, Grayson, KY 41143, USA | 2021-10-13
2019 | 2019-08-12 | Ashland | 76343202 | DKY0109783 | 38830270B02016 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. It might be possible to drive line truck to pole. | Clark Hollow Rd, Kentucky 41164, USA | 2021-05-18
2019 | 2019-08-13 | Ashland |  |  | 38830269D00303 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | YES | Replace deteriorated pole. Remove inactive transformer. | 4568 Mocabee Creek Rd, Olive Hill, KY 41164, USA
2019 | 2019-08-13 | Ashland | 74393620 | DKY0107008 | 38830270B02014 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. There is a possibly that you can drive a line truck to pole. | Buckeye Ln, Kentucky 41164, USA | 2022-03-11
2019 | 2019-08-15 | Ashland | 74393602 | DKY0106934 | 38830269C00152 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer and OL. House has burned down. | 210 Blue Hall Rd, Olive Hill, KY 41164, USA | 2022-03-16
2019 | 2019-08-15 | Ashland | 74393722 | DKY0107117 | 38830269C00157 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Customer (Mr. Blevins) mentioned that he might let line truck drive to pole with caution. | 451 Blue Hall Rd, Olive Hill, KY 41164, USA | 2022-04-12
2019 | 2019-08-16 | Ashland |  |  | 38830246000124 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | guys/anchors: broken or missing | pole: leaning, burned more than 50% remaining |  | Foreign |  | Pole is leaning. Guy anchor has pulled out of ground. Install: 1983 | Boathouse Hill Rd, Kentucky 41164, USA
2019 | 2019-08-16 | Ashland |  |  | 38830246000028 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer. | State Hwy 1626, Kentucky 41164, USA
2019 | 2019-08-16 | Ashland | 73782964 | DKY0105822 | 38830246000038 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. | 2224 State Hwy 1626, Olive Hill, KY 41164, USA | 2022-03-15
2019 | 2019-08-16 | Ashland |  |  | 38830246000063 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO |  | Cr-1399, Kentucky 41164, USA
2019 | 2019-08-16 | Ashland | 73782941 | DKY0105626 | 38830246000119 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. Transformer pole ground is stolen. | 3673 State Hwy 1626, Olive Hill, KY 41164, USA | 2021-08-25
2019 | 2019-08-19 | Ashland | 76343202 | DKY0109783 | 38830269B00144 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign |  | Replace xarm that is splitting. Primary insulator laying on xarm. | Haldeman Rd, Kentucky 40351, USA | 2021-05-18
2019 | 2019-08-19 | Ashland |  |  | 38830269C00261 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | Nut and washer is missing from bolt to primary insulator pin. | Trumbo Hill Rd & Cemetery Cir, Kentucky 40351, USA
2019 | 2019-08-19 | Ashland | 76343202 | DKY0109783 | 38830293000190 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign |  | Guy wire cut. Guy anchor is there and in good condition. | Open Fork Rd, Kentucky 40351, USA | 2021-05-18
2019 | 2019-08-19 | Ashland | 73428771 | DKY0109173 | 38830293000194 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. | Open Fork Rd., Olive Hill, Ky. | 2022-02-24
2019 | 2019-08-21 | Ashland | 74393586 | DKY0107160 | 38830245A00194 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer and OL. 1 span of neutral stolen. Line tap lifted at pole 245-97. | Greasy Creek Rd, Kentucky 41164, USA | 2022-01-14
2019 | 2019-08-21 | Ashland | 75986601 |  | 38830245B00307 |  | 3000801-HAYWARD / HALDEMAN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND , guys/anchors: broken or missing |  |  | KPC | NO | Transformer pole ground is stolen. Primary guy wire is broken and needs a reflective guard installed. Guy anchor is in good condition. | 150 Rock Hill Rd, Olive Hill, KY 41164, USA | 2020-03-05
2019 | 2019-08-21 | Ashland | 4921351 |  | 38830245B00333 |  | 3000801-HAYWARD / HALDEMAN | Service Work | OH |  |  | conductors: excessive splices, deteriorated conductors | KPC | NO | Service drop laying on ground. Cut-out to transformer is open. Called DDC to have service drop removed. | Cr-1885, Kentucky 41164, USA | 2020-03-05
2019 | 2019-08-21 | Ashland | 74393594 | DKY0107419 | 38830269A00432 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | 9175 US-60, Olive Hill, KY 41164, USA | 2022-03-10
2019 | 2019-08-21 | Ashland |  |  | 38830269A00485 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer and OL. Customer, Mrs. Hargett wanted removed. | 9175 US-60, Olive Hill, KY 41164, USA
2019 | 2019-08-22 | Ashland | 74586001 | DKY0106738 | 38830268D00124 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign |  | Replace deteriorated pole. Base of pole completely deteriorated and pole is leaning. Need replaced as soon as possible. | 575 May Rd, Morehead, KY 40351, USA | 2019-12-03
2019 | 2019-08-22 | Ashland |  |  | 38830269B00105 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Damaged 12 KV arrester. | 156 Mabry Cemetery Rd, Morehead, KY 40351, USA
2019 | 2019-08-23 | Ashland | 74393670 | DKY0107065 | 38830268A00070 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. | Little Perry Rd, Kentucky 40351, USA | 2022-03-02
2019 | 2019-08-23 | Ashland | 81756876 | DKY0116514 | 38830268B00055 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign |  | Broken xarm brace. | 1080 Little Perry Rd, Olive Hill, KY. | 2022-04-07
2019 | 2019-08-26 | Ashland | 75730163 |  | 38830292B00098 |  | 3000801-HAYWARD / HALDEMAN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop. Meter removed to vacant (tan) trailer. | Lafayette Dr. & Schoolhouse Br., Olive Hill, Ky | 2020-02-03
2019 | 2019-08-26 | Ashland | 75730840 |  | 38830292B00241 |  | 3000801-HAYWARD / HALDEMAN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Trailer at end of dirt road. | 6070 Hwy 60, Olive Hill, Ky | 2020-02-03
2019 | 2019-08-27 | Ashland | 76344129 | DKY0109574 | 38830292B00064 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole showing deterioration at top of pole. It passed sound test at base of pole. Set in 1945. | Hamilton Rd., Olive Hill, KY | 2020-07-10
2019 | 2019-08-27 | Ashland | 74393662 | DKY0107089 | 38830292B00083 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Customer would like inactive transformer removed. | 150 Baldwin Rd., Olive Hill, KY | 2022-01-13
2019 | 2019-08-28 | Ashland | 84256414 | DKY0119270 | 38830244000043 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Xarm is bowed because of tension from wire. End of xarm splitting. Big bucket truck can take care of this. | Old Holly School Road, Olive Hill, KY | 2023-01-24
2019 | 2019-08-28 | Ashland |  |  | 38830244000045 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Old Holly School Road, Olive Hill, KY
2019 | 2019-08-28 | Ashland |  |  | 38830246000056 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | There appears burning streak under cutout/arrester (porcelain 12 KV) t-bracket. Possible hole behind t-bracket. Line bucket truck can reach this area. | 1193 Douglas Hollow, Olive Hill, KY 41164, USA
2019 | 2019-08-29 | Ashland | 81756876 | DKY0116514 | 38830195000052 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | guys/anchors: broken or missing , conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Repair primary guy wire and install guy anchor. Primary is 15 feet from ground and neutral is 12 feet. Primary tap is lifted at pole 195-34. | Plank Chapel Road, Olive Hill, KY | 2022-04-07
2019 | 2019-08-29 | Ashland |  |  | 38830196000026 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Repair primary guy wire and install guy anchor. | 1260 Dry Branch Road, Olive Hill, KY
2019 | 2019-08-29 | Ashland | 83956026 | DKY0118793 | 38830219000047 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Repair broken primary guy wire and install guy anchor. | 8815 Cranston Rd, Morehead, KY 40351, USA | 2022-12-21
2019 | 2019-08-29 | Ashland | 75880722 |  | 38830219000098 |  | 3000801-HAYWARD / HALDEMAN | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Resag customers service drop (8’11” from ground line). Meter # 190 415 245 | 155 Estepp Road, Olive Hill, KY | 2020-02-21
2019 | 2019-08-30 | Ashland | 75880467 |  | 38830147000013 |  | 3000801-HAYWARD / HALDEMAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC |  | Need guy marker installed. | 12860 Cranston Road, Olive Hill, KY | 2020-02-21
2019 | 2019-08-30 | Ashland | 75874541 |  | 38830147000018 |  | 3000801-HAYWARD / HALDEMAN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Transformer pole ground stolen. | 370 Barn Br., Morehead, KY | 2020-02-20
2019 | 2019-08-30 | Ashland | 73428868 | DKY0105547 | 38830171000001 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Xarm brace split. | Cranston Rd, Olive Hill, KY | 2022-04-07
2019 | 2019-08-30 | Ashland | 73428888 | DKY0105503 | 38830171000078 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Cranston Road, Morehead, KY | 2022-05-10
2019 | 2019-08-30 | Ashland | 73428901 | DKY0105531 | 38830171000090 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | 190 Buckner Br., Morehead, KY | 2022-04-07
2019 | 2019-08-30 | Ashland | 75874868 |  | 38830195000029 |  | 3000801-HAYWARD / HALDEMAN | Service Work | OH |  | lightning arresters/insulators: damaged |  | KPC |  | 12 KV arrester damaged. | 1180 Elklick Rd, Morehead, KY 40351, USA | 2020-02-20
2019 | 2019-09-03 | Ashland | 74393624 | DKY0107019 | 38830270D00030 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Replace deteriorated single 8’ xarm. | 6565 KY-174, Olive Hill, KY 41164, USA | 2022-04-22
2019 | 2019-09-03 | Ashland | 74393624 | DKY0107019 | 38830270D00103 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. | Paradise Lane, Olive Hill, KY | 2022-04-22
2019 | 2019-09-03 | Ashland | 74393624 | DKY0107019 | 38830270D00199 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. | Goodan Ridge Rd, Kentucky 41164, USA | 2022-04-22
2019 | 2019-09-03 | Ashland | 74393723 | DKY0114869 | 38830270D00200 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | Lost Hills Rd, Kentucky 41164, USA | 2022-04-14
2019 | 2019-09-04 | Ashland | 85291502 | DKY0121036 | 38830271000073 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign |  | Small 4 foot double Xarms. Showing deterioration in Xarm bolt holes. | 4740 KY-174, Olive Hill, KY 41164, USA | 2023-12-06
2019 | 2019-09-04 | Ashland |  |  | 38830270D00018 |  | 3000802-HAYWARD / LAWTON | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign |  | This is a short Xarm (4 feet). The Xarm is not rotten or showing much deterioration. If you change the Xarm at pole 270-19 you might as well change Xarm here at 270-18 (one span). Next to junk yard.
2019 | 2019-09-04 | Ashland | 74393624 | DKY0107019 | 38830270D00019 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | This is a short Xarm (4 feet). Looking threw bolt holes of Xarm it’s showing deterioration. Dogs on premise, they act friendly. | 5965 KY-174, Olive Hill, KY 41164, USA | 2022-04-22
2019 | 2019-09-04 | Ashland |  |  | 38830270D00227 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer. | Hickory Flats Rd, Kentucky 41164, USA
2019 | 2019-09-04 | Ashland | 74393629 | DKY0107012 | 38830270D06004 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Hickory Flats Rd, Kentucky 41164, USA | 2022-03-15
2019 | 2019-09-04 | Ashland | 74393629 | DKY0107012 | 38830270D06005 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Hickory Flats Rd, Kentucky 41164, USA | 2022-03-15
2019 | 2019-09-04 | Ashland | 74393629 | DKY0107012 | 38830270D06011 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Transformer pole ground stolen. | Hickory Flats Rd, Kentucky 41164, USA | 2022-03-15
2019 | 2019-09-04 | Ashland |  |  | 38830271000079 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign |  | Short Xarm (4 feet). Showing deterioration in Xarm bolt hole. Be cautious! German shepherds on location. | 4959 Hwy 174, Olive Hill, KY
2019 | 2019-09-05 | Ashland | 75096727 | DKY0107405 | 38830295000061 |  | 3000802-HAYWARD / LAWTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign |  | Remove inactive transformer. 60 Leatherwood Branch, Olive Hill. | Cr-1295, Kentucky 41164, USA | 2022-04-26
2019 | 2019-09-05 | Ashland |  |  | 38830271000058 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Xarm is splitting. | Load Temple Rd, Kentucky 41164, USA
2019 | 2019-09-05 | Ashland |  |  | 38830271000255 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Pole is cracked in several areas. | 1183 State Hwy 955, Olive Hill, KY 41164, USA
2019 | 2019-09-09 | Ashland |  |  | 38830271000187 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | Mushroom Rd, Kentucky 41164, USA
2019 | 2019-09-09 | Ashland |  |  | 38830271C00267 |  | 3000802-HAYWARD / LAWTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer. | Mushroom Rd, Kentucky 41164, USA
2019 | 2019-09-09 | Ashland |  |  | 38830272000111 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is set on side of creek bed. Soil around base of pole is washed away. This is a 35 foot pole. Unable to locate birthmark. Is pole at proper depth? | State Hwy 1620, Kentucky 41164, USA
2019 | 2019-09-09 | Ashland | 74400038 | DKY0106872 | 38830272000131 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace pole. Top of pole is splitting. Change out pole 272-132 one span away from 272-131. I wrote up a defect order on it too. | 2115 Mushroom Rd, Olive Hill, KY 41164, USA | 2020-02-20
2019 | 2019-09-09 | Ashland | 76344208 | DKY0109588 | 38830272000132 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole along with pole 272-131, one span away. | 2115 Mushroom Rd, Olive Hill, KY 41164, USA | 2020-12-02
2019 | 2019-09-09 | Ashland |  |  | 38830296000067 |  | 3000802-HAYWARD / LAWTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer. | Mushroom Rd, Kentucky 41164, USA
2019 | 2019-09-10 | Ashland |  |  | 38830184C00046 |  | 3003701-COALTON / U.S.60W | Line Work | OH |  |  |  | Foreign | NO | One span of neutral stolen from pole 184-46 to 184-28. | 4854 US-60, Grayson, KY 41143, USA
2019 | 2019-09-10 | Ashland |  |  | 38830272000147 |  | 3000802-HAYWARD / LAWTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | State Hwy 1620, Kentucky 41164, USA
2019 | 2019-09-10 | Ashland |  |  | 38830296000001 |  | 3000802-HAYWARD / LAWTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Tick Ridge Fork, Olive Hill, KY
2019 | 2019-09-10 | Ashland | 74400047 | DKY0106874 | 38830296000034 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole. Top of pole splitting. | 582 Hanshaw Rd, Olive Hill, KY 41164, USA | 2020-10-12
2019 | 2019-09-10 | Ashland | 76344330 | DKY0109378 | 38830296000052 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole. Top of pole is starting to split. Two deep woodpecker holes in middle of pole. Steel brace around base of pole. Pole set in 1952. Customer would like to have old pole. | 2882 State Hwy 1620, Olive Hill, KY 41164, USA | 2020-11-24
2019 | 2019-09-10 | Ashland | 77189488 |  | 38830297000003 |  | 3000802-HAYWARD / LAWTON | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC |  | Neutral is broken in two. Pole next to curve going around hillside - need AWP. | Hwy-1620, Olive Hill, KY | 2020-07-17
2019 | 2019-09-10 | Ashland | 74393656 | DKY0107032 | 38830297000028 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property | lightning arresters/insulators: damaged |  | KPC |  | Remove inactive transformer (next to water pond for cows). Primary insulator broken. | Joe Skaggs Rd, Kentucky 41164, USA | 2021-01-19
2019 | 2019-09-11 | Ashland |  |  | 38830271000334 |  | 3000802-HAYWARD / LAWTON | Forestry | OH |  | pole: leaning, burned more than 50% remaining | Pole not found in fieldview. | Foreign |  | This is a Windstream and a Windstream problem, pole is leaning. Several trees are laying on telephone cables. Install: 1992 | KY-174, Kentucky, USA | 2019-09-11
2019 | 2019-09-12 | Ashland | 76350426 | DKY0110045 | 38830271C00043 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign |  | Repair primary guy wire grip (1/2”). Guy anchor is in good condition. | Mushroom Rd, Kentucky 41164, USA | 2020-07-09
2019 | 2019-09-13 | Ashland | 83482440 | DKY0118162 | 38830454B22517 | TRUE | 3001401-LOUISA / CITY | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | One arm of double xarm (top double xarm) is showing deterioration. Pole tag shows 454-50. | 70 Town Hill Rd, Louisa, KY 41230, USA | 2021-10-14
2019 | 2019-09-13 | Ashland |  |  | 38830454B22520 |  | 3001401-LOUISA / CITY | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Double xarm showing deterioration. | 661 Town Hill Rd, Louisa, KY 41230, USA | 2021-10-18
2019 | 2019-09-13 | Ashland |  |  | 38830454B22527 |  | 3001401-LOUISA / CITY | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Double xarm showing deterioration. | Town Hill Rd, Louisa, KY 41230, USA | 2021-10-18
2019 | 2019-09-13 | Ashland |  |  | 38830454B22528 |  | 3001401-LOUISA / CITY | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | One arm of double xarm splitting (bottom double xarm). | Town Hill Rd, Louisa, KY 41230, USA | 2021-10-08
2019 | 2019-09-16 | Ashland |  |  | 38830454A41685 |  | 3001401-LOUISA / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | W Pike St & Pocahontas St, Louisa, KY 41230, USA
2019 | 2019-09-16 | Ashland | 77422484 | DKY0111341 | 38830454B33058 |  | 3001401-LOUISA / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole. | Madison St & Pocahontas St, Louisa, KY 41230, USA | 2021-01-21
2019 | 2019-09-16 | Ashland |  |  | 38830454B33130 |  | 3001401-LOUISA / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | Madison St & Pocahontas St, Louisa, KY 41230, USA
2019 | 2019-09-17 | Ashland | 76139112 |  | 38830454A41523 |  | 3001401-LOUISA / CITY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Transformer pole ground stolen. | 103 Lock St, Louisa, KY 41230, USA | 2020-03-25
2019 | 2019-09-17 | Ashland | 76139019 |  | 38830454A41524 |  | 3001401-LOUISA / CITY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Transformer pole ground stolen. | 103 Lock St, Louisa, KY 41230, USA | 2020-03-25
2019 | 2019-09-17 | Ashland |  |  | 38830454A41534 |  | 3001401-LOUISA / CITY | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Double xarm is deteriorating around xarm bolt holes. | 403 | 2021-10-18
2019 | 2019-09-17 | Ashland |  |  | 38830454A41535 | TRUE | 3001401-LOUISA / CITY | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign |  | Xarm is deteriorating around xarm bolt holes. | 325 N Clay St, Louisa, KY 41230, USA | 2021-10-14
2019 | 2019-09-17 | Ashland |  |  | 38830454A41746 | TRUE | 3001401-LOUISA / CITY | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Replace double xarm. One xarm is showing burning at cutout/arrester bracket attachment. Xarm appears almost cut in two. | 325 N Clay Ave, Kirkwood, MO 63122, USA | 2020-05-18
2019 | 2019-09-17 | Ashland |  |  | 38830454B33131 | TRUE | 3001401-LOUISA / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace rotten pole. Pole has metal bandaid on it. | 102 Pocahontas St, Louisa, KY 41230, USA | 2020-05-18
2019 | 2019-09-17 | Ashland |  |  | 38830454D16002 |  | 3001401-LOUISA / CITY | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Top double Xarm is deteriorated and splitting. Possible deterioration on bottom Xarms. | 117 E Madison St, Louisa, KY 41230, USA | 2021-10-14
2019 | 2019-09-18 | Ashland | 80739292 | DKY0115040 | 38830454A41508 | TRUE | 3001401-LOUISA / CITY | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | Replace double Xarm - deteriorating and splitting. | 110 Public Way, Louisa, KY 41230, USA | 2022-02-27
2019 | 2019-09-18 | Ashland |  |  | 38830454A41514 | TRUE | 3001401-LOUISA / CITY | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Xarm showing deterioration in Xarm bolt holes. Pole was set in 1940 - pole passed sound test. | 924 Adams St, Louisa, KY 41230, USA | 2021-10-18
2019 | 2019-09-19 | Ashland | 85208216 |  | 38830454A41550 | TRUE | 3001401-LOUISA / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. In front of Louisa City Pool. | N Lock Ave & Stewart St, Louisa, KY 41230, USA
2019 | 2019-09-20 | Ashland | 78662364 |  | 38830478A10199 |  | 3001402-LOUISA / HIGHBOTTOM | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Customers OL service drop is 6.5 feet from ground. Vines and tree limbs laying on OL service drop. I tied yellow caution tape around drop and area. Told customer to stay away from area. I wrote this up two years ago. | 2577 KY-2565, Louisa, KY 41230, USA | 2021-01-22
2019 | 2019-09-23 | Ashland | 77422471 | DKY0110873 | 38830454B43622 |  | 3001402-LOUISA / HIGHBOTTOM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole is cracked and splitting at guy attachments. | 220 Northup Blvd, Louisa, KY 41230, USA | 2020-12-04
2019 | 2019-09-23 | Ashland | 76118988 | DKY0109274 | 38830478C14031 | TRUE | 3001402-LOUISA / HIGHBOTTOM | Line Work | OH | crossarm/braces: broken/split , pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Replace deteriorated double xarm (8 feet). Transformer pole ground stolen. | Eloise Church Rd, Louisa, KY 41230, USA | 2022-02-10
2019 | 2019-09-24 | Ashland | 77422381 | DKY0111197 | 38830478C14016 | TRUE | 3001402-LOUISA / HIGHBOTTOM | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | YES | Double xarm is broken and deteriorated. Customer is not here... could use line truck if customer gives permission. | 304 Old River Rd, Louisa, KY 41230, USA | 2021-05-17
2019 | 2019-09-24 | Ashland | 76151073 |  | 38830478C30255 |  | 3001402-LOUISA / HIGHBOTTOM | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Resag - customers service drop is 8 feet 2 inches from rear deck to tan mobile home. | 1398 KY-3, Louisa, KY 41230, USA | 2020-03-26
2019 | 2019-09-24 | Ashland | 76118936 | DKY0109247 | 38830478C30633 | TRUE | 3001402-LOUISA / HIGHBOTTOM | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | 300 Harley Dr, Louisa, KY 41230, USA | 2022-01-25
2019 | 2019-09-25 | Ashland | 76151138 |  | 38830454D16135 |  | 3001402-LOUISA / HIGHBOTTOM | Service Work | UG | UG conduit: damaged or separated |  |  | KPC |  | UG conduit damaged and large chunk of conduit missing. Secondary is not damaged. Water Street Apartments. Wrapped yellow caution tape around damaged area. Pole tag number shows 454-6016 |  | 2020-03-26
2019 | 2019-09-25 | Ashland | 76151101 |  | 38830478C30253 |  | 3001402-LOUISA / HIGHBOTTOM | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Mrs. Preese told me her OL goes off every time her AC comes on. She said her OL comes back on. I checked the transformer pole and the only issue I could see was one of the secondary loops was touching pole. Need to check OL and secondary. | 1080 KY-3, Louisa, KY 41230, USA | 2020-03-26
2019 | 2019-09-26 | Ashland |  |  | 38830454B27794 |  | 3001402-LOUISA / HIGHBOTTOM | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Finch Ln, Louisa, KY 41230, USA
2019 | 2019-09-30 | Ashland | 77535682 |  | 38830021D20095 |  | 3002106-10STREET / FRONT ST | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole next to floodgate at 13th street. | Front St, Ashland, KY 41101, USA | 2020-08-25
2019 | 2019-10-02 | Ashland | 77179938 |  | 38830223000208 |  | 3103101-OLIVEHILL / GLOBE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND | guys/anchors: loose, damaged, need insulator/marker | other: customer owned attachment | KPC |  | TV antenna attached to pole, antenna is not hooked up. Transformer pole ground stolen. Need reflective marker on primary guy wire. | 260 B and H Ln, Olive Hill, KY 41164, USA | 2020-07-16
2019 | 2019-10-03 | Ashland | 76343567 | DKY0110004 | 38830199000012 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign |  | Repair primary guy wire and install new anchor. Old anchor is damaged. | 539 Webb Ln, Olive Hill, KY 41164, USA | 2020-06-25
2019 | 2019-10-03 | Ashland |  |  | 38830199000058 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace pole because top of pole is splitting. | 563 Hawkensmith Rd, Olive Hill, KY 41164, USA
2019 | 2019-10-03 | Ashland |  |  | 38830199000059 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole splitting and primary pole top pen is loose. Neutral tie wire broken and neutral laying on metal of clevis. Old bus next to pole and needs to be moved to install new pole. | 563 Hawkensmith Rd, Olive Hill, KY 41164, USA
2019 | 2019-10-03 | Ashland | 76343567 | DKY0110004 | 38830223000022 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | From ground level primary and neutral appear close together. Need to resag if this is the case. | 335 Lavender Ln, Olive Hill, KY 41164, USA | 2020-06-25
2019 | 2019-10-03 | Ashland | 77180643 |  | 38830223000049 |  | 3103101-OLIVEHILL / GLOBE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Transformer pole ground stolen. | Cr-1354, Kentucky 41164, USA | 2020-07-16
2019 | 2019-10-03 | Ashland |  |  | 38830223000165 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Broken primary guy wire (1/4“). Guy anchor is already here at location. | Lavender Ln, Kentucky 41164, USA
2019 | 2019-10-08 | Ashland | 75755113 |  | 38830247000140 |  | 3103101-OLIVEHILL / GLOBE | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | pole: leaning, burned more than 50% remaining |  | KPC | NO | Resag customers service drop, it is 8 feet 8 inches from ground. | 107 Post Lane, Olive Hill, KY | 2020-02-05
2019 | 2019-10-09 | Ashland |  |  | 38830246000175 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Need manual tree crew to clear path to pole for line truck. | US-60, Olive Hill, KY, USA
2019 | 2019-10-09 | Ashland | 85254943 | DKY0122902 | 38830247000248 | TRUE | 3103101-OLIVEHILL / GLOBE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 19132 US-60, Olive Hill, KY 41164, USA
2019 | 2019-10-09 | Ashland |  |  | 38830247000287 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | 19132 US-60, Olive Hill, KY 41164, USA
2019 | 2019-10-09 | Ashland |  |  | 38830222B20002 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC |  | Line cutout open at pole 222-2 (cutout damaged). Pole 222-61 should be removed, one span of neutral stolen (second picture). Remove transformer pole 222-68 (third picture). Remove secondary pole and secondary (fourth picture). Remove two spans of primary and one span of neutral. I wrote this up two years ago. | Dutchess Ln, Kentucky 41164, USA
2019 | 2019-10-09 | Ashland | 74788145 | BKY0000012 | 38830246000175 | TRUE | 3103101-OLIVEHILL / GLOBE | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Found de-energized service drop laying on ground. Cutout is open to transformer. Called DDC to make out a TT. | US-60, Olive Hill, KY, USA | 2019-10-09
2019 | 2019-10-10 | Ashland |  |  | 38830173000020 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH |  |  |  | Foreign | NO | Two spans of neutral stolen (173-20 to 197-91). | Walnut Grove, Kentucky, USA
2019 | 2019-10-10 | Ashland | 75884545 |  | 38830197000078 |  | 3103101-OLIVEHILL / GLOBE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen to Walnut Grove Community Church. | Walnut Grove, Kentucky, USA | 2020-02-21
2019 | 2019-10-11 | Ashland |  |  | 38830174000043 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer near waterway. Intersection of 1662 & Rose Crk. | Hwy-1662, Olive Hill, KY
2019 | 2019-10-14 | Ashland | 76264046 |  | 38830045A20511 |  | 3002107-10STREET / WEST CENTRAL | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen from transformer pole. | 368 Maynard St, Ashland, KY 41101, USA | 2020-04-08
2019 | 2019-10-14 | Ashland | 76264028 |  | 38830045A20512 |  | 3002107-10STREET / WEST CENTRAL | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen from transformer pole. | 2510 Kirk St, Ashland, KY 41101, USA | 2020-04-08
2019 | 2019-10-14 | Ashland | 76263991 |  | 38830045A20515 |  | 3002107-10STREET / WEST CENTRAL | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen to transformer pole. | 2814 Kirk St, Ashland, KY 41101, USA | 2020-04-08
2019 | 2019-10-14 | Ashland |  |  | 38830045A31030 |  | 3002107-10STREET / WEST CENTRAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 506 9th St, Ashland, KY 41101, USA | 2021-01-26
2019 | 2019-10-14 | Ashland | 76263631 |  | 38830045B12041 | TRUE | 3002107-10STREET / WEST CENTRAL | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen from transformer pole. | 2425-2427 Boone St, Ashland, KY 41101, USA | 2020-04-08
2019 | 2019-10-14 | Ashland |  |  | 38830045B12099 |  | 3002107-10STREET / WEST CENTRAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 2200 Stephens St, Ashland, KY 41101, USA
2019 | 2019-10-14 | Ashland | 76263666 | 0 | 38830045B12117 |  | 3002107-10STREET / WEST CENTRAL | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign |  | Pole ground stolen from transformer pole. | 603 Bradley St, Ashland, KY 41101, USA | 2020-04-08
2019 | 2019-10-14 | Ashland | 76263914 |  | 38830045B12189 |  | 3002107-10STREET / WEST CENTRAL | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen from transformer pole. | 2610 Crawford St, Ashland, KY 41101, USA | 2020-04-08
2019 | 2019-10-15 | Ashland | 81706967 | DKY0116265 | 38830202000015 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | crossarm/braces: deteriorated, not rotten |  | KPC | YES | Double xarms are deteriorating. Pole set in 1946 and has metal bandaid at base. Might as well change out xarms and pole. Customer at 433 Grahn Rd. told me that customer at 361 is difficult to work with. | 361 Grahn Rd, Olive Hill, KY 41164, USA | 2022-03-16
2019 | 2019-10-15 | Ashland |  |  | 38830227000026 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Double xarms showing deterioration. | Aden Rd, Grahn, KY 41142, USA
2019 | 2019-10-15 | Ashland |  |  | 38830227000027 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Double xarms deteriorating. | Aden Rd, Kentucky, USA
2019 | 2019-10-15 | Ashland |  |  | 38830227000045 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Double xarms deteriorating. | Maddox Hollow, Olive Hill, KY
2019 | 2019-10-15 | Ashland |  |  | 38830251000135 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Double xarms deteriorating. | 4496 Aden Rd, Olive Hill, KY 41164, USA
2019 | 2019-10-15 | Ashland |  |  | 38830251000272 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Aden Rd, Olive Hill, KY
2019 | 2019-10-16 | Ashland | 76343074 | DKY0109771 | 38830226000016 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH | guys/anchors: broken or missing | crossarm/braces: deteriorated, not rotten |  | KPC |  | Double xarms deteriorating. Repair broken primary guy wire and needs guy anchor. | 100 Cr-1257B, Olive Hill, KY 41164, USA | 2022-02-23
2019 | 2019-10-16 | Ashland | 76343074 | DKY0109771 | 38830251000095 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Double xarms deteriorating. | Grahn Rd, Olive Hill, KY | 2022-02-23
2019 | 2019-10-16 | Ashland | 82020163 | DKY0116661 | 38830251000124 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Xarm deteriorating. | 152 Grahn Rd, Olive Hill, Ky | 2022-05-11
2019 | 2019-10-17 | Ashland |  |  | 38830251000033 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Xarm is deteriorated from past burning. | 7268 Grahn Rd, Olive Hill, KY
2019 | 2019-10-17 | Ashland | 76344084 | DKY0110046 | 38830251000034 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | pole does not need to be replaced at this time per V Mullins //// There appears that there is some burning at middle t-bracket to porcelain cut-out. I don’t see any smoke but needs to be looked at further to be on the safe side. | 7225 Grahn Rd, Olive Hill, KY | 2020-09-02
2019 | 2019-10-17 | Ashland | 75741741 |  | 38830251000066 |  | 3000601-GRAHN / PLEASANTV | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Customers service drop is 6 feet 6 inches from front deck. Tied yellow on lowest area of service drop. Looks like a new addition of deck. | 518 Nazarene Hollow, Olive Hill, KY | 2020-02-04
2019 | 2019-10-17 | Ashland | 85539987 | DKY0121509 | 38830251000069 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Xarm deteriorating. | Oats Hill Rd, Kentucky 41164, USA
2019 | 2019-10-17 | Ashland |  |  | 38830251000072 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Double xarms deteriorating. Pole passed sound test but was set in 1941. | Oats Hill Rd, Kentucky 41164, USA
2019 | 2019-10-17 | Ashland |  |  | 38830251000172 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  |  |  | KPC |  | One span of neutral stolen (251-171 to 251-172). | Grahn Rd, Olive Hill, KY
2019 | 2019-10-18 | Ashland |  |  | 38830250000099 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Double xarms deteriorating. Remove inactive transformer. | 385 Cory Rd, Olive Hill, KY
2019 | 2019-10-18 | Ashland |  |  | 38830251000081 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Double xarms deteriorating. | 270 Church Ridge, Olive Hill, KY
2019 | 2019-10-18 | Ashland |  |  | 38830251000195 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | crossarm/braces: broken/split |  |  | KPC |  | End of xarm is splitting. | Church Ridge Road, Olive Hill, KY
2019 | 2019-10-18 | Ashland |  |  | 38830251000276 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Church Ridge Rd, Olive Hill, KY
2019 | 2019-10-18 | Ashland | 76343074 | DKY0109771 | 38830275000004 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Primary guy wire is broken. Unable to locate anchor. | Church Ridge Rd, Olive Hill, KY | 2022-02-23
2019 | 2019-10-21 | Ashland |  |  | 38830250000229 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Boggs Rd, Kentucky 41164, USA
2019 | 2019-10-21 | Ashland |  |  | 38830250000120 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Secondary guy wire broken. Unable to locate anchor. | Cory Rd, Olive Hill, KY | 2022-11-30
2019 | 2019-10-21 | Ashland | 85306964 | DKY0121350 | 38830274000009 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC |  | Xarm deteriorating. Pole inside electric fence. Horses inside fence area. | 550 Pipeline Rd, Olive Hill, KY 41164, USA | 2023-09-05
2019 | 2019-10-22 | Ashland |  |  | 38830250000160 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | lightning arresters/insulators: damaged | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Transformer arrester is damaged. Need manual tree crew to clear driving path for line truck. | 386 Boggs Rd, Olive Hill, KY
2019 | 2019-10-22 | Ashland |  |  | 38830251000074 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  |  |  | KPC |  | 1 span of neutral stolen: 251-74 to 251-75. Beware of dogs on premise. | 401 Oats Hill Rd, Olive Hill, KY 41164, USA
2019 | 2019-10-28 | Ashland | 75754497 |  | 38830224000106 |  | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen from solid blade primary switches. Pole located in front of Olive Hill sub-station. | US-60, Olive Hill, KY, USA | 2020-02-05
2019 | 2019-10-28 | Ashland | 77422829 | DKY0111297 | 38830248000021 |  | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole has metal bandaid at base of pole. Noticed small burning from past close to top of pole. Install: 1946. | 168 Dogwood Hollow, Olive Hill, KY 41164, USA | 2020-12-07
2019 | 2019-10-28 | Ashland |  |  | 38830272000214 |  | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. Pole tag is showing 272-213. | Cr-1291C, Kentucky 41164, USA
2019 | 2019-10-29 | Ashland |  |  | 38830272000082 |  | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer. | Frazier Rd, Kentucky 41164, USA
2019 | 2019-10-30 | Ashland | 75751226 | DKY0108490 | 38830248000039 |  | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Line Work | OH |  |  |  | Foreign |  | 3 spans of stolen neutrals from pole 248-36 to 248-39. | KY-174, Kentucky, USA | 2020-03-02
2019 | 2019-10-30 | Ashland | 76265374 |  | 38830273000037 |  | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Resag customers service drop. Service is 8 feet 4 inches from ground. Service goes to shed. | 3970 Hwy 986, Olive Hill, KY | 2020-04-08
2019 | 2019-11-05 | Ashland | 77187945 |  | 38830249D30230 |  | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC |  | Pole ground stolen. | Cr-1283, Kentucky 41164, USA | 2020-07-17
2019 | 2019-11-05 | Ashland | 74132081 | DKY0106398 | 38830273000074 | TRUE | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | Forestry - DESCRIBE IN COMMENTS | KPC | YES | Reclosure open and grounded at pole 273-44. Pole 273-71 is leaning and cracked at top of pole. Two spans of primary missing at poles 273-73 to 273-75. Replace broken pole 273-74. Large tree laying on roadway blocking path to 273-74, reason for manual tree crew. Three spans of neutral missing at poles 273-74 to 273-158. Clevises missing at poles 273-77 and 273-158. One span of neutral missing at poles 273-78 to 273-81. Line cut-out open and grounded at pole 249-31. I drew a map of all the poles and problems that I found on this section of circuit that I will give to Pat Thovson. | Greenhill Rd, Olive Hill, KY | 2020-06-06
2019 | 2019-11-11 | Ashland | 71725229 | DKY0102789 | 38830356000081 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Delong Branch Rd, Louisa, KY | 2021-08-18
2019 | 2019-11-11 | Ashland | 71619393 | DKY0102731 | 38830380000298 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Primary guy wire(1/4 inch) broken. Anchor rod is there and in good condition. Dogs running loose in yard where anchor is located. | Bobcat Ridge Natural Area, 10184 Co Rd 32C, Loveland, CO 80538, USA | 2022-06-17
2019 | 2019-11-11 | Ashland | 76249377 | DKY0109557 | 38830380000299 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer and OL. | Bobcat Ridge Rd, Kentucky 41230, USA | 2022-01-31
2019 | 2019-11-11 | Ashland | 71619393 | DKY0102731 | 38830405000171 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC |  | Remove inactive transformer (transformer damaged from house fire in the past) and remove inactive OL. Customer informed me that OL comes on at night, cutout is open, take CAUTION that cutout might be tracking. | 500 Bobcat Ridge Rd, Louisa, KY 41230, USA | 2022-06-17
2019 | 2019-11-12 | Ashland | 75975271 |  | 38830353000020 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Transformer pole ground stolen. | 5148 Little Cat Fork Rd, Louisa, KY | 2020-03-04
2019 | 2019-11-12 | Ashland | 77422734 | DKY0110878 | 38830356000044 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole 356-44 has metal bandaid at base of pole, set in 1948. Four spans of neutral stolen (356-40 to 356-177). | Long Branch, Kentucky 41250, USA | 2021-01-11
2019 | 2019-11-14 | Ashland | 71725430 | DKY0102860 | 38830331000053 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is set in creek bed, soil is being washed away around pole. Pole is leaning. | Little East Fork Rd, Louisa, KY | 2021-05-26
2019 | 2019-11-14 | Ashland |  |  | 38830331B10165 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Resag - neutral 11 feet and primary 16 1/2 feet from slope of hillside. Goes to barn. | 345 Little East Fork Rd, Louisa, KY
2019 | 2019-11-15 | Ashland | 75975947 |  | 38830379000069 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC |  | Pole ground stolen from transformer pole. | 610 Hwy 1, Louisa, KY | 2020-03-04
2019 | 2019-11-15 | Ashland |  |  | 38830379000117 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer due to trailer fire. Pole ground stolen from transformer pole. | 916 Hwy 1, Louisa, KY
2019 | 2019-11-19 | Ashland | T.T. # 4047351 |  | 38830378000006 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Resag neutral. Neutral is 3 feet at lowest point from ground between pole 378-6 (378-17) to 378-74. There is a new pole tag on pole 378-6, it is 378-17. Notified Ashland DDC. | Woods Branch Rd, Louisa, KY | 2020-03-31
2019 | 2019-11-19 | Ashland |  |  | 38830402000068 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Resag neutral. Neutral is 10 feet at lowest point between 402-68 to 378-3. | Hwy-1 & Woods Branch Rd, Louisa, KY | 2020-03-31
2019 | 2019-11-19 | Ashland | 71859143 | DKY0102921 | 38830425000123 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | 1607 Diamond Ridge Rd, Louisa, KY | 2022-07-20
2019 | 2019-11-20 | Ashland |  |  | 38830377000052 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Forestry | OH |  |  | Must have been entered in error. This is an old trouble ticket and surely these customers have not been out of power for 173 days. | KPC |  | Primary line tap is open and grounded at pole 377-42. Need tree and brush removal between poles 377-42 to 377-58. Tree laying on primary and neutral between poles 377-52 and 377-53. Manual tree crews. | Woods Branch Rd, Louisa, KY | 2019-11-20
2019 | 2019-11-20 | Ashland |  |  | 38830400000069 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole. (35'6, 1951) | 3745 Diamond Ridge Rd, Webbville, KY 41180, USA | 2020-03-31
2019 | 2019-11-21 | Ashland |  |  | 38830379000189 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Line cutout open at 379-101. Primary pole top pen damaged at 379-189. Primary & neutral down between 379-126 (no truck) to 379-189 (large bucket truck). Primary down at 379-189 to 379-190 (no truck). | Roberts Dr, Louisa, KY
2019 | 2019-11-21 | Ashland | 76249377 | DKY0109557 | 38830403B20264 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Shady Grove Rd, Kentucky, USA | 2022-01-31
2019 | 2019-11-21 | Ashland | 76249374 | DKY0109551 | 38830450000126 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Aaron Ridge Rd, Kentucky 41230, USA | 2022-01-31
2019 | 2019-11-22 | Ashland | 76249374 | DKY0109551 | 38830450000083 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Twin Bridge Rd, Louisa, KY | 2022-01-31
2019 | 2019-11-25 | Ashland | 71619321 | DKY0102698 | 38830405000173 |  | 3000203-BIG SANDY/YATESVILLE | Line Work | OH | guys/anchors: broken or missing |  |  | KPC |  | Primary guy wire (1/4”) broken. Guy anchor is good condition. | 356 Victoria Heights Rd, Louisa, KY 41230, USA | 2022-06-17
2019 | 2019-11-25 | Ashland | 75976462 |  | 38830429A00445 |  | 3000203-BIG SANDY/YATESVILLE | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | Resag customers service drop, it is 8 feet 6 inches from rear deck. | 1346 Fullers Ridge Rd, Louisa, KY 41230, USA | 2020-03-04
2019 | 2019-11-26 | Ashland | 71741001 | DKY0102915 | 38830380000245 |  | 3000203-BIG SANDY/YATESVILLE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Buck Branch Rd, Kentucky 41230, USA | 2021-09-15
2019 | 2019-11-26 | Ashland |  |  | 38830404000187 |  | 3000203-BIG SANDY/YATESVILLE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , Forestry - DESCRIBE IN COMMENTS | KPC |  | Remove inactive transformer. Need manual tree crew to clear path for line crew to transformer pole. | Hwy-3, Louisa, KY
2019 | 2019-11-26 | Ashland |  |  | 38830404000289 |  | 3000203-BIG SANDY/YATESVILLE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | One span of primary & neutral down between 404-289 to 404-302. Primary is isolated at 404-289. Remove inactive transformer at 404-302. | McCoy Branch Rd, Kentucky 41230, USA
2019 | 2019-11-27 | Ashland | 76249368 | DKY0109480 | 38830428000170 |  | 3000203-BIG SANDY/YATESVILLE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | YES | Past burning at top of pole from primary pole top pin and primary stirrup close to pole. Pole passed sound test. One span of primary stolen from 428-170 to 428-67. Customer said that it was okay to drive in yard. | 482 Left Fork Morgans Creek Rd, Louisa, KY 41230, USA | 2021-01-06
2019 | 2019-12-02 | Ashland | 71859188 | DKY0102901 | 38830427000051 |  | 3000203-BIG SANDY/YATESVILLE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Raven Rock Fork Rd, Louisa, KY | 2021-09-08
2019 | 2019-12-02 | Ashland | 76249362 | DKY0109333 | 38830451000110 |  | 3000203-BIG SANDY/YATESVILLE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole. | 1686 Raven Rock Fork Rd, Louisa, KY 41230, USA | 2020-08-17
2019 | 2019-12-03 | Ashland |  |  | 38830403000067 |  | 3000203-BIG SANDY/YATESVILLE | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC |  | Remove inactive transformer. | Jerry Riffe Ridge Rd, Kentucky 41230, USA
2019 | 2019-12-03 | Ashland | 76249379 | DKY0109579 | 38830428000253 |  | 3000203-BIG SANDY/YATESVILLE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC |  | One span of neutral missing (cut down and laying rolled up next to transformer pole). Could’ve come down during wind storm and cut down for clearance. Will need AWP. | 609 Deep Hole Branch Rd, Louisa, KY 41230, USA | 2022-02-10
2019 | 2019-12-05 | Ashland | 77422712 | DKY0110883 | 38830355000027 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole is showing deterioration. Pole set in 1945. Pole passed sound test at base. | Hwy-3, Louisa, KY | 2020-12-07
2019 | 2019-12-06 | Ashland | 71859202 | DKY0102918 | 38830426000048 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole at primary pole top pin appears to be splitting. | 3876 Hwy 828, Louisa, KY | 2021-06-02
2019 | 2019-12-18 | Ashland |  |  | 39830901C24529 |  | 3002002-South Shore / Distribution | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 88 Corner St, South Shore, KY 41175, USA | 2023-02-01
2019 | 2019-12-18 | Ashland |  |  | 39830901C48060 |  | 3002002-South Shore / Distribution | Line Work | UG | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | UG transformer needs to be repositioned on its foundation. Small opening under transformer - small animals and snakes can get inside - opening is 2 - 3 inches. Holly Manor Apts. in South Shore. | Eunice St, South Shore, KY 41175, USA
2019 | 2019-12-19 | Ashland | 77423036 | DKY0110955 | 39830901C45504 |  | 3002002-South Shore / Distribution | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole. If line trucks need to get closer to pole running parallel to highway tree trimming might be needed. | James E Hannah Dr, South Shore, KY 41175, USA | 2021-03-16
2019 | 2019-12-20 | Ashland | 74863099 | DKY0108289 | 39830901A18010 | TRUE | 3002002-South Shore / Distribution | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen. | US-23, South Shore, KY, USA | 2020-10-23
2019 | 2019-12-20 | Ashland |  |  | 39830901C24548 |  | 3002002-South Shore / Distribution | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Nut and washer missing on primary pin. Xarm appears splitting at end of arm. | S Shore Dr, South Shore, KY, USA
2019 | 2019-12-20 | Ashland | 74863123 | DKY0108292 | 39830901C24564 | TRUE | 3002002-South Shore / Distribution | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm is deteriorating. | S Shore Rd, South Shore, KY 41175, USA | 2020-03-27
2019 | 2019-12-23 | Ashland |  |  | 39830900C14037 |  | 3002002-South Shore / Distribution | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated brace pole. Top of main pole appears to be deteriorating. | 87 Spruce Alley, South Portsmouth, KY 41174, USA
2019 | 2019-12-23 | Ashland | T.T. # 4177611 |  | 39830900C14038 |  | 3002002-South Shore / Distribution | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | House knob pulled loose from trailer pole. Drop is 7 1/2 feet from ground. Called DDC for T.T. | Spruce Alley, Kentucky 41174, USA | 2019-12-23
2019 | 2019-12-26 | Ashland |  |  | 39830901C45551 |  | 3002002-South Shore / Distribution | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Top double xarms deteriorating. | 5th Ave Alley, South Shore, KY 41175, USA
2019 | 2019-12-26 | Ashland |  |  | 39830901C45552 |  | 3002002-South Shore / Distribution | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Top double xarms deteriorating. | Cecil Robbins Ave, South Shore, KY 41175, USA
2019 | 2019-12-26 | Ashland |  |  | 39830901C45553 |  | 3002002-South Shore / Distribution | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Double xarms deteriorating. | 5th Ave Alley, South Shore, KY 41175, USA
2019 | 2019-12-26 | Ashland |  |  | 39830901C45554 |  | 3002002-South Shore / Distribution | Line Work | OH |  |  |  | Foreign | NO | Double xarms deteriorating. | 5th Ave Alley, South Shore, KY 41175, USA
2019 | 2019-12-26 | Ashland | 74863123 | DKY0108292 | 39830901C45563 | TRUE | 3002002-South Shore / Distribution | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. Pole in alley. | E 3rd Ave, South Shore, KY 41175, USA | 2020-03-27
2019 | 2019-12-30 | Ashland | 74863123 | DKY0108292 | 39830901C24584 | TRUE | 3002002-South Shore / Distribution | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | W 2nd Ave, South Shore, KY 41175, USA | 2020-03-27
2019 | 2019-12-30 | Ashland |  |  | 39830901C24588 | TRUE | 3002002-South Shore / Distribution | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND , service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Trailer is vacant, meter removed and blanked off. Service drop needs to be removed or leads cut at transformer pole. Transformer pole ground stolen. | 52 Hauser Ave, South Shore, KY 41175, USA | 2020-03-04
2019 | 2019-12-30 | Ashland | 78684777 |  | 39830901C24589 |  | 3002002-South Shore / Distribution | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 14 Hauser Ave, South Shore, KY 41175, USA | 2021-01-26
2019 | 2019-12-30 | Ashland | 74863123 | DKY0108292 | 39830901C24625 | TRUE | 3002002-South Shore / Distribution | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 16 W 1st Ave, South Shore, KY 41175, USA | 2020-03-27
2019 | 2019-12-30 | Ashland |  |  | 39830901C24630 |  | 3002002-South Shore / Distribution | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 58 W 1st Ave, South Shore, KY 41175, USA | 2023-02-01
2019 | 2019-12-30 | Ashland |  |  | 39830901C35003 | TRUE | 3002002-South Shore / Distribution | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace rotten pole. | 143 Ridge St, South Shore, KY 41175, USA
2019 | 2019-12-31 | Ashland |  |  | 39830901D37004 |  | 3002001-South Shore / Siloam | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Broken xarm brace. | Happy Corner, South Shore, KY 41175, USA
2019 | 2019-12-31 | Ashland | 74862987 | DKY0108072 | 39830901D37097 | TRUE | 3002001-South Shore / Siloam | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | Happy Corner, South Shore, KY 41175, USA | 2020-02-24
2019 | 2019-12-31 | Ashland | 74862498 | DKY0107694 | 39830902B00425 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten and top of pole appears that it is splitting. | 1212 KY-7, South Portsmouth, KY 41174, USA | 2022-03-01

## Ckt Defects Reported 2020 ASH
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2020 | 2020-01-02 | Ashland |  |  | 39830902B00058 |  | 3002001-South Shore / Siloam | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | End of xarm on roadside is splitting.
2020 | 2020-01-02 | Ashland | 84346291 |  | 39830902B00060 |  | 3002001-South Shore / Siloam | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND , conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Transformer pole ground stolen. Remove service drop to vacant trailer. Meter removed and blanked off. Across from 1365 St. Rt. 7. | KY-7, South Shore, KY, USA | 2023-02-01
2020 | 2020-01-02 | Ashland | 74862978 | DKY0108066 | 39830902B00064 | TRUE | 3002001-South Shore / Siloam | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen (non-equipment). | KY-7, South Shore, KY, USA | 2020-03-17
2020 | 2020-01-02 | Ashland |  |  | 39830926A00033 | TRUE | 3002001-South Shore / Siloam | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. Park in driveway down from pole to fix pole ground if servicer does not want to park on Rt. 784. | KY-784, Kentucky, USA | 2021-01-26
2020 | 2020-01-02 | Ashland | 74862918 | DKY0108063 | 39830926A00082 | TRUE | 3002001-South Shore / Siloam | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 464 Hwy 784, South Shore, KY | 2020-03-23
2020 | 2020-01-02 | Ashland |  |  | 39830926A00172 |  | 3002001-South Shore / Siloam | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. Park in driveway to fix pole ground. | 425 Hwy 784, South Shore, KY | 2023-02-01
2020 | 2020-01-03 | Ashland | 74862877 | DKY0108078 | 39830925000152 |  | 3002001-South Shore / Siloam | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Damaged transformer arrester. | 681 Shultz Ln, South Shore, KY | 2021-01-14
2020 | 2020-01-03 | Ashland | 74862856 | DKY0108060 | 39830926A00046 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | Middleton Ln, South Shore, KY | 2022-01-25
2020 | 2020-01-03 | Ashland | 74862877 | DKY0108078 | 39830926A00048 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Double xarms deteriorating. | 263 Willard Ln, South Shore, KY 41175, USA | 2021-01-14
2020 | 2020-01-03 | Ashland | 74862877 | DKY0108078 | 39830926A00051 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. | Willow Ln, Kentucky 41175, USA | 2021-01-14
2020 | 2020-01-03 | Ashland | 74862856 | DKY0108060 | 39830926A00072 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 844 Hwy 784, South Shore, KY | 2022-01-25
2020 | 2020-01-03 | Ashland | 78684777 |  | 39830926A00117 |  | 3002001-South Shore / Siloam | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 538 Shultz Ln, South Shore, KY | 2021-01-26
2020 | 2020-01-06 | Ashland |  |  | 39830925000016 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Double xarms deteriorating. | Flat Hollow Rd, Kentucky 41174, USA
2020 | 2020-01-06 | Ashland | 74862820 | DKY0108038 | 39830925000020 |  | 3002001-South Shore / Siloam | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 910 Lower White Oak Rd, South Portsmouth, KY 41174, USA | 2020-10-23
2020 | 2020-01-06 | Ashland |  |  | 39830925000064 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. | 1390 Lower White Oak Rd, South Portsmouth, KY 41174, USA
2020 | 2020-01-06 | Ashland |  |  | 39830925000065 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. Will need permission to drive in customer’s front yard. | 1475 Lower White Oak Rd, South Portsmouth, KY 41174, USA
2020 | 2020-01-06 | Ashland |  |  | 39830925000066 |  | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. | 1509 Lower White Oak Rd, South Portsmouth, KY
2020 | 2020-01-06 | Ashland | 74862820 | DKY0108038 | 39830925000114 |  | 3002001-South Shore / Siloam | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen (non-equipment). | Still Hollow, South Shore, KY | 2020-10-23
2020 | 2020-01-06 | Ashland | 84346604 |  | 39830925000127 |  | 3002001-South Shore / Siloam | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Primary guy needs reflective marker installed. | Bonnie Ln, Kentucky, USA | 2023-02-01
2020 | 2020-01-06 | Ashland | 78684777 |  | 39830925000186 |  | 3002001-South Shore / Siloam | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 222 Flat Hollow, South Shore, KY | 2021-01-26
2020 | 2020-01-06 | Ashland | 74862856 | DKY0108060 | 39830926A00056 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 1048 KY-784, South Shore, KY 41175, USA | 2022-01-25
2020 | 2020-01-06 | Ashland | 74862856 | DKY0108060 | 39830926A00075 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 881 KY-784, South Shore, KY 41175, USA | 2022-01-25
2020 | 2020-01-06 | Ashland |  |  | 39830926B00153 |  | 3002001-South Shore / Siloam | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary |  |  | KPC | NO | One span of neutral stolen. | 1145 KY-784, South Shore, KY 41175, USA
2020 | 2020-01-07 | Ashland |  |  | 39830924000005 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarms deteriorating. | 2808 Lower White Oak Rd, South Portsmouth, KY 41174, USA
2020 | 2020-01-07 | Ashland |  |  | 39830924000006 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarms deteriorating. | 2914 Lower White Oak Rd, South Portsmouth, KY 41174, USA
2020 | 2020-01-07 | Ashland | 74862259 | DKY0107658 | 39830924000012 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotted out at base of pole. | Little Kellen Hollow Rd, South Portsmouth, KY | 2022-07-05
2020 | 2020-01-07 | Ashland | 82320353 | DKY0116993 | 39830925000076 |  | 3002001-South Shore / Siloam | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NO | Soil has been washed out around pole. Info Box shows pole as a 40 foot class 3. Pole birthmark is hard to read. Pole is slightly leaning, pole guy wire is preventing pole from coming down. | Buck Hollow, South Portsmouth, KY | 2022-05-16
2020 | 2020-01-07 | Ashland | 74862802 | DKY0108032 | 39830925000079 |  | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. | Buck Hollow, South Portsmouth, KY | 2020-10-26
2020 | 2020-01-07 | Ashland | 74862281 | DKY0110783 | 39830925000083 |  | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. | 541 Buck Hollow, South Portsmouth, KY | 2021-12-13
2020 | 2020-01-07 | Ashland |  |  | 39830925A10378 |  | 3002001-South Shore / Siloam | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NO | Soil is being washed out around pole. Info Box indicates 40 foot class 5 pole. Pole is not leaning. Is pole at proper depth? | Buck Hollow, South Portsmouth, KY
2020 | 2020-01-08 | Ashland | 78684777 |  | 39830901C35038 |  | 3002001-South Shore / Siloam | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground cut. | 46 Melroy Rd, South Shore, KY 41175, USA | 2021-01-26
2020 | 2020-01-08 | Ashland | 74863047 | DKY0108109 | 39830901C45620 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 65 Hammond Ave, South Shore, KY 41175, USA | 2020-06-01
2020 | 2020-01-08 | Ashland | 78684777 |  | 39830901C45621 |  | 3002001-South Shore / Siloam | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 99 Hammond Ave, South Shore, KY 41175, USA | 2021-01-26
2020 | 2020-01-08 | Ashland | 74863030 | DKY0108074 | 39830901D37039 | TRUE | 3002001-South Shore / Siloam | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen. Pole in alley. | Morton St, South Shore, KY 41175, USA | 2020-02-24
2020 | 2020-01-08 | Ashland | 74863030 | DKY0108074 | 39830901D37050 | TRUE | 3002001-South Shore / Siloam | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. Rear apartment. | 84 Morton St, South Shore, KY 41175, USA | 2020-02-24
2020 | 2020-01-08 | Ashland | 83435765 |  | 39830902A00019 |  | 3002001-South Shore / Siloam | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Across from McKell Elementary School. | Kings Addition Ln, Kentucky 41175, USA | 2023-02-01
2020 | 2020-01-08 | Ashland |  |  | 39830902A00166 |  | 3002001-South Shore / Siloam | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. WARNING: pit bull on premise. | 16 Nelroy Rd, South Shore, KY 41175, USA | 2023-02-01
2020 | 2020-01-08 | Ashland |  |  | 39830902A00178 |  | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Double Xarms deteriorating.
2020 | 2020-01-08 | Ashland | 74863047 | DKY0108109 | 39830902B00189 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | Indianola Ave, South Shore, KY 41175, USA | 2020-06-01
2020 | 2020-01-09 | Ashland |  |  | 39830901A20502 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Xarm braces are broken and Xarm appears damaged at attachment to pole. Xarm pointing straight up. Neutral is 4 to 6 inches from pole. I wrote this up 2 years ago. | 647 Flat Hollow Rd, South Portsmouth, KY 41174, USA
2020 | 2020-01-10 | Ashland | 84345503 |  | 39830902A00610 |  | 3002001-South Shore / Siloam | Service Work | OH | service |  |  | Foreign | NO | Remove inactive service drop. Meter is removed and blanked off to trailer pole. Transformer pole number 902-548. | Fargo St, Kentucky 41175, USA | 2023-02-01
2020 | 2020-01-10 | Ashland |  |  | 39830902C00397 |  | 3002001-South Shore / Siloam | Service Work | OH | service |  |  | Foreign | NO | Customers service drop is going over edge of their swimming pool. Service drop is roughly 15 feet over edge of pool. | 89 Keith St, South Shore, KY 41175, USA | 2023-02-01
2020 | 2020-01-10 | Ashland | 74863073 | DKY0107834 | 39830902C00412 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Broken primary guy wire (1/4 inch). Guy anchor is in good condition. | 119 Maple St, South Shore, KY 41175, USA | 2022-01-25
2020 | 2020-01-10 | Ashland | 74863073 | DKY0107834 | 39830902C00416 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Broken primary and secondary guy wires. Will need guy anchor installed. | 350 Mildred Ave, South Shore, KY 41175, USA | 2022-01-25
2020 | 2020-01-10 | Ashland | 74863073 | DKY0107834 | 39830902C00567 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Damaged arrester. | 50 Wright Ln, South Shore, KY 41175, USA | 2022-01-25
2020 | 2020-01-10 | Ashland | 74862701 | DKY0107874 | 39830902C04007 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | One span of neutral needs to be resag. Neutral is sagging below telephone wire. | Little Rocky Rd, Kentucky, USA | 2022-03-01
2020 | 2020-01-13 | Ashland | 72837215 | DKY0104493 | 39830976000011 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer. Pole is located on Columbia Gas Rd. next to Greenup Dam Bridge. | Ohio River Rd, Kentucky 41144, USA | 2022-04-07
2020 | 2020-01-13 | Ashland | 83584354 |  | 39831000A00130 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | service |  |  | Foreign | NO | Meter removed and blanked off to trailer pole. Remove service drop. | 113 Graysbranch Rd, Greenup, KY 41144, USA | 2022-10-13
2020 | 2020-01-14 | Ashland | 72837215 | DKY0104493 | 39830951000033 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove transformer and hardware. Meter is removed and transformer cutout is open. House is falling in. Grey house across RR tracks. | Andrews Pl, Kentucky 41144, USA | 2022-02-11
2020 | 2020-01-14 | Ashland | 85741760 | 038240075 | 39830951000048 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | service |  |  | Foreign | NO | Resag customers service drop (8 feet 6 inches). | 81 Makaria Hollow, Lloyd, KY 41144, USA | 2023-08-17
2020 | 2020-01-14 | Ashland | 85741780 | 031934479 | 39830975000085 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Primary guy wire (1/2 inch) broken. Guy anchor in good condition. | Wells Ln, Kentucky 41144, USA | 2023-08-17
2020 | 2020-01-15 | Ashland | 72837215 | DKY0104493 | 39830927000078 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer. Across from Antique Loop. | US-23, South Shore, KY, USA | 2022-04-07
2020 | 2020-01-15 | Ashland | 78175312 |  | 39831000B00122 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | service |  |  | Foreign | NO | Customer’s service drop is laying against the edge of their tin roof. Resag service drop. | 120 Tipton Dr, South Shore, KY | 2020-11-10
2020 | 2020-01-16 | Ashland | 78174578 |  | 39831000B00203 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | service |  |  | Foreign | NO | Remove service drop. Meter removed and blanked off to trailer pole. | Rupps Way, Lloyd, KY 41144, USA | 2020-11-10
2020 | 2020-01-16 | Ashland | 78174061 |  | 39831024A00241 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | service |  |  | Foreign | NO | Resag service drop. Customer’s service drop rubbing against edge of tin roof. Looks like roofers wrapped plastic tape around service drop. | 55 Brown Ln, Greenup, KY 41144, USA | 2020-11-10
2020 | 2020-01-16 | Ashland | 83584887 |  | 39831024A00293 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | service |  |  | KPC | NO | House knob has come loose from pole. Service goes to City of Greenup Water Dept. water tank. | US-23, Greenup, KY, USA | 2022-10-13
2020 | 2020-01-17 | Ashland | 85741802 | 035787981 | 39831023000056 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | service |  |  | Foreign | NO | Resag customers service drop. Service drop is 8 feet from ground. | 255 McClurg Rd, Greenup, KY | 2023-08-17
2020 | 2020-01-20 | Ashland | 72837349 | DKY0104423 | 39831024B42059 | TRUE | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2020 | 2020-01-20 | Ashland | 72837349 | DKY0104423 | 39831024B42060 | TRUE | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2020 | 2020-01-20 | Ashland | 72837349 | DKY0104423 | 39831024B42061 | TRUE | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2020 | 2020-01-20 | Ashland | 72837349 | DKY0104423 | 39831024B42062 | TRUE | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2020 | 2020-01-20 | Ashland |  |  | 39831047000027 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , washed out |  |  | Foreign | NEEDS ADDITIONAL CHECK | Foreign pole is set in creek bed (washed out). | 2178 Smith Branch Rd, Greenup, KY 41144, USA
2020 | 2020-01-20 | Ashland | 72837349 | DKY0104423 | 39831048A30217 | TRUE | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground cut. | US-23, Greenup, KY, USA | 2022-03-22
2020 | 2020-01-20 | Ashland | 72901121 | DKY0104444 | 39831048C20226 | TRUE | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2020 | 2020-01-20 | Ashland | 72901121 | DKY0104444 | 39831048C20227 | TRUE | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2020 | 2020-01-20 | Ashland | 72901121 | DKY0104444 | 39831048C20228 | TRUE | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2020 | 2020-01-20 | Ashland | 72901121 | DKY0104444 | 39831048C20229 | TRUE | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2020 | 2020-01-20 | Ashland | 72901121 | DKY0104444 | 39831048C20230 | TRUE | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2020 | 2020-01-21 | Ashland | 83537143 |  | 39831071000125 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | service |  |  | KPC | NO | Remove service to vacant trailer. Meter removed and blanked. | 1745 Coal Branch Rd, Greenup, KY 41144, USA | 2022-10-03
2020 | 2020-01-21 | Ashland | 83514303 |  | 39831072000027 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Recloser - ground wire not attached to ground casing lug. | 1858 Short Branch Rd, Greenup, KY 41144, USA | 2022-10-03
2020 | 2020-01-21 | Ashland | T.T. # 4325611 |  | 39831072000096 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary | pole: leaning, burned more than 50% remaining | Forestry - DESCRIBE IN COMMENTS | KPC | NO | 2 spans of primary down at pole 1072-96 (truck OK) to 1048-63. Pole 1048-63 is leaning and has metal brace at base. Need manual tree crew to clear dirt path from trees to vacant trailer. Tony George told me trailer has been vacant for over 3 years, trailer is in bad condition. Hardware and poles 1072-97, 1048-63, and 1048-64 should be removed, these 3 poles are not truck accessible. Called DDC to have primary wire removed. | 1398 Coal Branch Rd, Greenup, KY 41144, USA
2020 | 2020-01-22 | Ashland | 72836873 | DKY0104449 | 39831070000013 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NEEDS ADDITIONAL CHECK | Pole is leaning. Top of pole appears deteriorating. Pole passed sound test. | Hwy-827, Greenup, KY | 2021-08-18
2020 | 2020-01-22 | Ashland | 72836873 | DKY0104449 | 39831070000054 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. | Sugar Creek Rd, Greenup, KY | 2021-08-18
2020 | 2020-01-22 | Ashland |  |  | 39831070D10078 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. | Allcorn Rd, Greenup, KY
2020 | 2020-01-22 | Ashland | 72836873 | DKY0104449 | 39831071000059 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Primary guy wire (1/4) broken and anchor is missing. | 3793 Coal Branch Rd, Greenup, KY 41144, USA | 2021-08-18
2020 | 2020-01-23 | Ashland | 72836968 | DKY0104454 | 39831048000152 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Primary guy wire broken. Unable to locate anchor. Pole next to blue metal building. | US-23, Greenup, KY, USA | 2022-03-01
2020 | 2020-01-23 | Ashland | 76353923 |  | 39831072000158 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | service |  |  | Foreign | NO | Remove service drop to vacant trailer. Meter removed and blanked off. | 98 Sandy Cove Marina Rd, Greenup, KY 41144, USA | 2020-04-17
2020 | 2020-01-27 | Ashland | 74132081 | DKY0106398 | 38830273000074 | TRUE | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | 10/19/18 JOE MORELAND REPORTED 5 SPANS STILL MISSING. R/W HAS BEEN CUT. PRIMARY NEUTRAL MISSING FROM POLE 38830273000074 TO 38830273000081. THIS NEEDS REPLACED ASAP. THIS SECTION OF THE OLIVE HILL/WEST CARTER ELEMENTARY IS TRANSFERED TO THE GHRAN/PLEASANT VALLEY CKT | Greenhill Road, Olive Hill Ky | 2020-06-06
2020 | 2020-01-27 | Ashland |  |  | 39830951000007 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). | Ohio River Rd, Kentucky 41144, USA
2020 | 2020-01-27 | Ashland | 72837124 | DKY0104432 | 39831048000114 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer. | US-23, Greenup, KY, USA | 2020-05-28
2020 | 2020-01-27 | Ashland | 72837124 | DKY0104432 | 39831048000115 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove two inactive transformers. | US-23, Greenup, KY, USA | 2020-05-28
2020 | 2020-01-28 | Ashland |  |  | 39830951000006 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). Large crack (6 to 7 inches). | Ohio River Rd, Kentucky 41144, USA
2020 | 2020-01-28 | Ashland |  |  | 39831000B00103 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Failed sound and screwdriver test. | 47
2020 | 2020-01-28 | Ashland |  |  | 39831024A00158 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | Forestry - DESCRIBE IN COMMENTS | Foreign | YES | Replace deteriorated pole. Failed sound and screwdriver test. Customer’s small trailer will need to be removed in order for line truck to get close to pole. | 55 Church St, Greenup, KY 41144, USA
2020 | 2020-01-30 | Ashland |  |  | 39831071000107 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary |  |  | KPC | NO | Isolation pole 1071-73, there is no primary tap and it is grounded at this location. At pole 1071-107, one span of primary (15 feet) and neutral (10 feet) from the ground. Whenever we decide to energize this circuit this will need to be corrected. Road across from Coal Branch Community Church. | Coal Branch Rd, Kentucky 41144, USA
2020 | 2020-01-31 | Ashland | 76228536 | DKY0109547 | 38830045A31101 |  | 3002103-10STREET / 12STREET | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | YES | Xarm showing deterioration. Pole located in alley off of Lexington Ave. behind Aladdin’s Art Gallery. You might consider changing xarm at pole 45F1100 one span up from 45F1101. | Lexington Ave, Ashland, KY 41101, USA | 2021-07-07
2020 | 2020-02-03 | Ashland | 76365667 |  | 38830045A10017 |  | 3002103-10STREET / 12STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 340 Ferry St, Ashland, KY 41101, USA | 2020-04-20
2020 | 2020-02-03 | Ashland | 76264428 |  | 38830045A20587 |  | 3002103-10STREET / 12STREET | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen. Park in driveway across from pole. | Pollard Rd & Pierce St, Ashland, KY 41101, USA | 2020-04-08
2020 | 2020-02-03 | Ashland | 82586479 | DKY0117275 | 38830045A31008 |  | 3002103-10STREET / 12STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | Delaware St & Marcia St, Ashland, KY 41101, USA | 2022-07-19
2020 | 2020-02-03 | Ashland | 76228536 | DKY0109547 | 38830045A31102 |  | 3002103-10STREET / 12STREET | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Double xarms deteriorating. In alley off of Lexington Ave. Behind Aladdin’s Art Gallery. | Lexington Ave, Ashland, KY 41101, USA | 2021-07-07
2020 | 2020-02-03 | Ashland | 76264711 |  | 38830045A31149 |  | 3002103-10STREET / 12STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 418 Pierce St, Ashland, KY 41101, USA | 2020-04-08
2020 | 2020-02-03 | Ashland |  |  | 38830045A31157 |  | 3002103-10STREET / 12STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 412 Beckett St, Ashland, KY 41101, USA
2020 | 2020-02-03 | Ashland | 76190620 |  | 38830045A41595 |  | 3002103-10STREET / 12STREET | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen (non-equipment). Park truck in parking space next to pole. | Pollard Rd, Ashland, KY 41101, USA | 2020-03-31
2020 | 2020-02-03 | Ashland | 76190620 |  | 38830045A41597 |  | 3002103-10STREET / 12STREET | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. Park in driveway next to pole. | Pollard Rd, Ashland, KY 41101, USA | 2020-03-31
2020 | 2020-02-03 | Ashland | 76365556 |  | 38830045A41599 |  | 3002103-10STREET / 12STREET | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. Park in driveway next to pole. | Pollard Rd, Ashland, KY 41101, USA | 2020-04-20
2020 | 2020-02-03 | Ashland | 76365579 |  | 38830045A41605 |  | 3002103-10STREET / 12STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Park in apartments driveway. | 620 Pollard Rd, Ashland, KY 41101, USA | 2020-04-20
2020 | 2020-02-03 | Ashland | 77462252 |  | 38830045A41658 |  | 3002103-10STREET / 12STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen to OL. Across from tennis courts. | 1477-1481 Oakview Rd, Ashland, KY 41101, USA | 2020-08-17
2020 | 2020-02-03 | Ashland |  |  | 38830045A41660 |  | 3002103-10STREET / 12STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Across from tennis courts. | 1477-1481 Oakview Rd, Ashland, KY 41101, USA
2020 | 2020-02-03 | Ashland | 76264487 |  | 38830045A41671 |  | 3002103-10STREET / 12STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 425 Pollard Rd, Ashland, KY 41101, USA | 2020-04-08
2020 | 2020-02-03 | Ashland | 76365635 |  | 38830045A41672 |  | 3002103-10STREET / 12STREET | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. Park in driveway next to pole. | Pollard Rd, Ashland, KY 41101, USA | 2020-04-20
2020 | 2020-02-03 | Ashland | 76365611 |  | 38830045A41673 |  | 3002103-10STREET / 12STREET | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. Park in driveway next to pole. | Pollard Rd, Ashland, KY 41101, USA | 2020-04-20
2020 | 2020-02-03 | Ashland | 76190620 |  | 38830045A41733 |  | 3002103-10STREET / 12STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 1108 Pollard Rd, Ashland, KY 41101, USA | 2020-03-31
2020 | 2020-02-03 | Ashland | 76190620 |  | 38830045A41795 |  | 3002103-10STREET / 12STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 1203 13th St, Ashland, KY 41101, USA | 2020-03-31
2020 | 2020-02-03 | Ashland | 70940989 | DKY0101783 | 38830045C14489 | TRUE | 3002103-10STREET / 12STREET | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Double xarms deteriorating. In alley off of Montgomery Ave. behind Ashland Children’s Clinic. | Montgomery Ave, Ashland, KY 41101, USA | 2022-04-29
2020 | 2020-02-04 | Ashland | 77533043 |  | 38830045A41534 |  | 3002103-10STREET / 12STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 964 Prospect Ave, Ashland, KY 41101, USA | 2020-08-25
2020 | 2020-02-04 | Ashland |  |  | 38830045A41717 |  | 3002103-10STREET / 12STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). | 915 Chestnut Dr, Ashland, KY 41101, USA
2020 | 2020-02-04 | Ashland | 77534528 |  | 38830045D16060 |  | 3002103-10STREET / 12STREET | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen. | Forest Ave, Ashland, KY 41101, USA | 2020-08-25
2020 | 2020-02-04 | Ashland | 77534493 |  | 38830045D16061 |  | 3002103-10STREET / 12STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen to OL. | Forest Ave, Ashland, KY 41101, USA | 2020-08-25
2020 | 2020-02-04 | Ashland | 77534465 |  | 38830045D16062 |  | 3002103-10STREET / 12STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | Forest Ave, Ashland, KY 41101, USA | 2020-08-25
2020 | 2020-02-04 | Ashland | 77534550 |  | 38830045D16222 |  | 3002103-10STREET / 12STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | Forest Ave, Ashland, KY 41101, USA | 2020-08-25
2020 | 2020-02-06 | Ashland | 70940668 | DKY0101626 | 38830045C24510 | TRUE | 3002104-10STREET / 10-3 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 714 16th St, Ashland, KY 41101, USA | 2020-03-04
2020 | 2020-02-06 | Ashland | 77559886 |  | 38830045C24551 |  | 3002104-10STREET / 10-3 | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 2005 Hilton Ave, Ashland, KY 41101, USA | 2020-08-27
2020 | 2020-02-06 | Ashland | 77499172 |  | 38830045C24556 |  | 3002104-10STREET / 10-3 | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 1909 Hilton Ave, Ashland, KY 41101, USA | 2020-08-20
2020 | 2020-02-06 | Ashland | 76679791 | DKY0109794 | 38830045C24743 |  | 3002104-10STREET / 10-3 | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Replace double xarms (split). Pole on Central Park block and across from King’s Daughters Hospital. There is the possibility not needing flaggers. | 22nd St, Ashland, KY 41101, USA | 2021-01-15
2020 | 2020-02-07 | Ashland |  |  | 38830045C24713 | TRUE | 3002104-10STREET / 10-3 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). | 22nd St & Lexington Ave, Ashland, KY 41101, USA
2020 | 2020-02-10 | Ashland |  |  | 38830045C14953 |  | 3002104-10STREET / 10-3 | Line Work | UG | secondary |  |  | KPC | NO | Secondary UG pedestal latch is damaged. Pedestal located next to small brick theater. Placed yellow caution tape around pedestal. | Chattin Dr, Ashland, KY 41101, USA | 2021-01-22
2020 | 2020-02-10 | Ashland | 78662724 | DKY0112512 | 38830045C24748 |  | 3002104-10STREET / 10-3 | Line Work | UG | secondary |  |  | KPC | NO | Secondary UG pedestal latch is broken off. Pedestal located next to tennis courts. Placed yellow caution tape around pedestal. | Central Ave, Ashland, KY 41101, USA | 2021-02-09
2020 | 2020-02-11 | Ashland | 70938506 | DKY0101660 | 38830021D28376 | TRUE | 3002105-10STREET / MIDTOWN | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to transformer (3 phase bank). Pole in alley. | 1220 Greenup Ave, Ashland, KY 41101, USA | 2022-03-30
2020 | 2020-02-11 | Ashland | 77462440 |  | 38830045C14309 |  | 3002105-10STREET / MIDTOWN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen to transformer. | 1632 Central Ave, Ashland, KY 41101, USA | 2020-08-17
2020 | 2020-02-11 | Ashland | 77547942 |  | 38830045C35041 |  | 3002105-10STREET / MIDTOWN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen. Pole in alley. | 2129 Winchester Ave, Ashland, KY 41101, USA | 2020-08-26
2020 | 2020-02-11 | Ashland | 77547624 |  | 38830045C35044 |  | 3002105-10STREET / MIDTOWN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen to cutout switches. Pole at alley entrance between Winchester Ave. & Greenup Ave. on 21st St. | 21st St, Ashland, KY 41101, USA | 2020-08-26
2020 | 2020-02-11 | Ashland | 77544068 |  | 38830045C35076 |  | 3002105-10STREET / MIDTOWN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen to 3 phase transformers. | 1944 Greenup Ave, Ashland, KY 41101, USA | 2020-08-26
2020 | 2020-02-11 | Ashland | 78164722 |  | 38830045C35186 |  | 3002105-10STREET / MIDTOWN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to transformer. | 2236 Greenup Ave, Ashland, KY 41101, USA | 2020-11-09
2020 | 2020-02-11 | Ashland | 78608843 |  | 38830045C45859 |  | 3002105-10STREET / MIDTOWN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen to transformer. | 2328 Greenup Ave, Ashland, KY 41101, USA | 2021-01-14
2020 | 2020-02-12 | Ashland |  |  | 38830045C14278 |  | 3002105-10STREET / MIDTOWN | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Transformer arrester damaged. Pole next to Masonic Temple. | 15th St, Ashland, KY 41101, USA
2020 | 2020-02-12 | Ashland | 77498983 |  | 38830045C14308 |  | 3002105-10STREET / MIDTOWN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen. | 1617 Bath Ave, Ashland, KY 41101, USA | 2020-08-20
2020 | 2020-02-12 | Ashland | 77498628 |  | 38830045C14342 |  | 3002105-10STREET / MIDTOWN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 1505 Bath Ave, Ashland, KY 41101, USA | 2020-08-20
2020 | 2020-02-13 | Ashland | 72850485 | DKY0105480 | 39831097C00121 | TRUE | 3110902-WURTLAND / GREENUP | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | End of double xarms splitting. Pole next to entrance to gravel plant. Unable to sound pole because water around pole. Pole appears in good shape. | US-23, Greenup, KY, USA | 2022-02-24
2020 | 2020-02-13 | Ashland | 72850448 | DKY0106317 | 39831097D00320 | TRUE | 3110902-WURTLAND / GREENUP | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer and secondary. | Wurtland, KY 41144, USA | 2022-03-29
2020 | 2020-02-13 | Ashland | 76250677 |  | 39831098B11265 |  | 3110902-WURTLAND / GREENUP | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | Wurtland Ave, Kentucky, USA | 2020-04-07
2020 | 2020-02-14 | Ashland |  |  | 39831096000040 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , Forestry - DESCRIBE IN COMMENTS | KPC | NO | Remove transformer and hardware at 1096-40. Primary is open at 1096-40. Large tree laying on primary and neutral between 1096-53 to 1096-54. Remove transformer and hardware at 1096-54. Pole 1096-55 is unused service pole. Should these two spans and service pole be completely removed? | W Hollow Rd, Kentucky 41144, USA
2020 | 2020-02-14 | Ashland | 72850543 | DKY0104827 | 39831097A00203 | TRUE | 3110902-WURTLAND / GREENUP | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. | E Kentucky Rd, Greenup, KY, USA | 2022-04-13
2020 | 2020-02-14 | Ashland | 72850525 | DKY0104920 | 39831097B00261 | TRUE | 3110902-WURTLAND / GREENUP | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Damaged transformer arrester. | 123 Collins Ln, Greenup, KY 41144, USA | 2020-07-22
2020 | 2020-02-14 | Ashland | 76261366 |  | 39831121A00181 |  | 3110902-WURTLAND / GREENUP | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 204 Shepherd Loop Rd, Wurtland, KY 41144, USA | 2020-04-08
2020 | 2020-02-19 | Ashland | 76263467 |  | 39831120000003 |  | 3110902-WURTLAND / GREENUP | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 531 Shackle Run Rd, Greenup, KY | 2020-04-08
2020 | 2020-02-19 | Ashland |  |  | 39831121A00238 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Primary guy is broken. Need anchor installed. | 1054 Plum Grove Rd, Greenup, KY 41144, USA
2020 | 2020-02-19 | Ashland |  |  | 39831121B00102 |  | 3110902-WURTLAND / GREENUP | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Damaged line arrester. | Cedar Riffle Rd, Greenup, KY
2020 | 2020-02-19 | Ashland | 84619979 | DKY0120008 | 39831145A30298 |  | 3110902-WURTLAND / GREENUP | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. | KY-1, Greenup, KY, USA | 2023-04-27
2020 | 2020-02-20 | Ashland |  |  | 39831072C45520 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Pole is located on Main St. rear. | 821 E Main St, Greenup, KY 41144, USA
2020 | 2020-02-20 | Ashland | 78173432 |  | 39831072C45698 |  | 3110902-WURTLAND / GREENUP | Service Work | OH | service |  |  | Foreign | NO | Customer’s service drop is 7.5 feet at lowest point. Customer said service drop has been this way for a number years. | 121 KY-2, Greenup, KY 41144, USA | 2020-11-10
2020 | 2020-02-20 | Ashland | 72850543 | DKY0104827 | 39831072D37005 | TRUE | 3110902-WURTLAND / GREENUP | Line Work | OH |  |  |  | Foreign | NO | Top double xarms deteriorating. Arrester to transformer is broken. Transformer pole ground is broken at ground line. | 928 Seaton Ave, Greenup, KY 41144, USA | 2022-04-13
2020 | 2020-02-20 | Ashland |  |  | 39831072D37023 |  | 3110902-WURTLAND / GREENUP | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. | 929 Winifred St, Greenup, KY 41144, USA
2020 | 2020-02-20 | Ashland | 82057744 | DKY0116707 | 39831072D37070 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 928 Seaton Ave, Greenup, KY 41144, USA | 2022-05-02
2020 | 2020-02-21 | Ashland | 76228551 | DKY0109603 | 38830021B43574 |  | 3002101-10STREET / 6STREET | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | End of Xarm is splitting. | 835 Carter Ave, Ashland, KY 41101, USA | 2022-02-19
2020 | 2020-02-21 | Ashland | 77497233 |  | 38830021B43736 |  | 3002101-10STREET / 6STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole next to 10th Street sub-stationing alley. | 924 Greenup Ave, Ashland, KY 41101, USA | 2020-08-20
2020 | 2020-02-21 | Ashland | 72837297 | DKY0104396 | 39831072C35010 | TRUE | 3110902-WURTLAND / GREENUP | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | Elizabeth St & Chestnut St, Greenup, KY 41144, USA | 2022-07-12
2020 | 2020-02-21 | Ashland |  |  | 39831072C45562 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). | 400 Perry St, Greenup, KY 41144, USA | 2020-07-17
2020 | 2020-02-21 | Ashland |  |  | 39831121A00272 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Primary tap lifted at Iso. pole 1121-14. Primary insulator and transformer cutout are damaged. Inactive transformer. Pole 1121-272, hardware, primary and neutral should be removed. Trailer appears abandoned for a number of years. | 2836 KY-1, Greenup, KY 41144, USA
2020 | 2020-02-24 | Ashland | 77531706 |  | 38830045C24646 |  | 3000103-ASHLAND / 25-14STRE | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen. Pole in alley. | 2009 Central Ave, Ashland, KY 41101, USA | 2020-08-24
2020 | 2020-02-24 | Ashland | 77531706 |  | 38830045C24647 |  | 3000103-ASHLAND / 25-14STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. Pole in alley. | 2001 Central Ave, Ashland, KY 41101, USA | 2020-08-24
2020 | 2020-02-24 | Ashland | 77545470 |  | 38830045C30135 |  | 3000105-ASHLAND / 25-1 | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole in alley. | 2215 Greenup Ave, Ashland, KY 41101, USA | 2020-08-26
2020 | 2020-02-24 | Ashland | 77545008 |  | 38830045C30374 |  | 3000105-ASHLAND / 25-1 | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is in alley. | 2119 Greenup Ave, Ashland, KY 41101, USA | 2020-08-26
2020 | 2020-02-24 | Ashland | 77544562 |  | 38830045C30379 |  | 3000105-ASHLAND / 25-1 | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is located in alley behind Bill Cole Ford. | Greenup Ave, Ashland, KY 41101, USA | 2020-08-26
2020 | 2020-02-24 | Ashland | 78165675 |  | 38830045C35526 |  | 3000105-ASHLAND / 25-1 | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen to switches. | Front St, Ashland, KY 41101, USA | 2020-11-09
2020 | 2020-02-24 | Ashland |  |  | 38830045C45725 |  | 3000103-ASHLAND / 25-14STRE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). At entrance of alley. Pole is leaning slightly. | 22nd St, Ashland, KY 41101, USA
2020 | 2020-02-24 | Ashland | 78632596 |  | 38830045C45793 |  | 3000103-ASHLAND / 25-14STRE | Service Work | OH | UG conduit: damaged or separated |  |  | Foreign | NO | Secondary UG conduit is separated. Placed yellow caution tape around area. | 2550 Winchester Ave, Ashland, KY 41101, USA | 2021-01-19
2020 | 2020-02-24 | Ashland | 77531706 |  | 38830045C45815 |  | 3000103-ASHLAND / 25-14STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 2140 Carter Ave, Ashland, KY 41101, USA | 2020-08-24
2020 | 2020-02-24 | Ashland |  |  | 38830045C45902 |  | 3000103-ASHLAND / 25-14STRE | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Double xarms splitting. Pole at entrance of alley. | 25th St, Ashland, KY 41101, USA
2020 | 2020-02-25 | Ashland | 77544854 |  | 38830045C30381 |  | 3000105-ASHLAND / 25-1 | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is located in alley. | 1841 Greenup Ave, Ashland, KY 41101, USA | 2020-08-26
2020 | 2020-02-25 | Ashland | 81373971 | DKY0117304 | 38830045C30382 |  | 3000105-ASHLAND / 25-1 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | Transmission pole | KPC | YES | Replace deteriorated pole. Pole is in alley. | 1909 Greenup Ave, Ashland, KY 41101, USA | 2023-04-24
2020 | 2020-02-25 | Ashland |  |  | 38830045D37212 |  | 3000101-ASHLAND / 25-25STRE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Top of pole showing deterioration. | 814 24th St, Ashland, KY 41101, USA
2020 | 2020-02-25 | Ashland | 78614186 |  | 38830045D37248 |  | 3000101-ASHLAND / 25-25STRE | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen. Pole is located in alley. | 812 23rd St, Ashland, KY 41101, USA | 2021-01-15
2020 | 2020-02-26 | Ashland | 71110118 | DKY0101944 | 38830045C45558 | TRUE | 3000102-ASHLAND / 25-29STRE | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. Pole is located in alley. Behind Bill Cole Auto. | Greenup Ave, Ashland, KY 41101, USA | 2022-03-24
2020 | 2020-02-26 | Ashland | 71110118 | DKY0101944 | 38830045C45559 | TRUE | 3000102-ASHLAND / 25-29STRE | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. Pole is located in alley. | Greenup Ave, Ashland, KY 41101, USA | 2022-03-24
2020 | 2020-02-26 | Ashland | 77526209 |  | 38830045C45560 |  | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. Pole is located in alley. | 2548 Greenup Ave, Ashland, KY 41101, USA | 2020-08-24
2020 | 2020-02-26 | Ashland | 78614186 |  | 38830045C45582 | TRUE | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is located in alley. | 2701 Winchester Ave, Ashland, KY 41101, USA | 2021-01-15
2020 | 2020-02-26 | Ashland |  |  | 38830045C45732 |  | 3000102-ASHLAND / 25-29STRE | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Double xarms broken. Pole is located in alley next to Subway. | 28th St, Ashland, KY 41101, USA
2020 | 2020-02-26 | Ashland | 48614186 |  | 38830045C45847 | TRUE | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is located in alley. | 2733 Greenup Ave, Ashland, KY 41101, USA | 2021-01-15
2020 | 2020-02-26 | Ashland | 77526510 |  | 38830045C48436 |  | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is located in alley. | 2528 Greenup Ave, Ashland, KY 41101, USA | 2020-08-24
2020 | 2020-02-26 | Ashland | 78614186 |  | 38830045D37080 |  | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. Pole is located in alley. | 600 29th St, Ashland, KY 41101, USA | 2021-01-15
2020 | 2020-02-26 | Ashland | 77525838 |  | 38830046A20550 |  | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is located in alley. | 2777 Winchester Ave, Ashland, KY 41101, USA | 2020-08-24
2020 | 2020-02-26 | Ashland | 77525223 |  | 38830046A20552 |  | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is located in alley. | 2822 Greenup Ave, Ashland, KY 41101, USA | 2020-08-24
2020 | 2020-02-26 | Ashland | 76108282 |  | 38830046A20579 | TRUE | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. Pole is located in alley. | 2932 Greenup Ave, Ashland, KY 41101, USA | 2020-03-22
2020 | 2020-02-26 | Ashland |  |  | 38830046A20613 |  | 3000102-ASHLAND / 25-29STRE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). Pole is located in alley. Next to Subway. | 28th St, Ashland, KY 41101, USA
2020 | 2020-02-26 | Ashland | 71110953 | DKY0101994 | 38830046B12002 | TRUE | 3000102-ASHLAND / 25-29STRE | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Primary guy wire needs reflective marker installed. Pole is located in alley. | 3033 Winchester Ave, Philadelphia, PA 19136, USA | 2022-03-30
2020 | 2020-02-26 | Ashland | 77190442 |  | 38830046B12003 |  | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is located in alley. | 3000 Greenup Ave, Ashland, KY 41101, USA | 2020-07-17
2020 | 2020-02-26 | Ashland | 77190820 |  | 38830046B12004 |  | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is located in alley. | 229 31st St, Ashland, KY 41101, USA | 2020-07-17
2020 | 2020-02-26 | Ashland | 7710442 |  | 38830046B12052 |  | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is located in alley. | 320 32nd St, Ashland, KY 41101, USA | 2020-07-17
2020 | 2020-02-26 | Ashland | 77521123 |  | 38830046B12054 |  | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is located in alley. | 330 Ringo St, Ashland, KY 41101, USA | 2020-08-24
2020 | 2020-02-26 | Ashland | 78614186 |  | 38830046B12103 |  | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is located in alley. | 3020 Winchester Ave, Ashland, KY 41101, USA | 2021-01-15
2020 | 2020-02-26 | Ashland | 77522454 |  | 38830046B12105 |  | 3000102-ASHLAND / 25-29STRE | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service , service |  |  | Foreign | NO | Customer’s house knob has pulled loose from building. | 3050 Winchester Ave, Ashland, KY 41101, USA | 2020-08-24
2020 | 2020-02-26 | Ashland | 78614186 |  | 38830046B12185 |  | 3000102-ASHLAND / 25-29STRE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole is located in alley. | 3127 Central Ave, Ashland, KY 41101, USA | 2021-01-15
2020 | 2020-02-26 | Ashland |  |  | 38830046B12310 |  | 3000102-ASHLAND / 25-29STRE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | This pole is deteriorated and has a metal support band on it. Base of pole is completely deteriorated. I believe pole should be replaced. | 3145 Greenup Ave, Ashland, KY 41101, USA | 2022-09-08
2020 | 2020-02-27 | Ashland |  |  | 38830046B12060 |  | 3000102-ASHLAND / 25-29STRE | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | 420 32nd St, Ashland, KY 41101, USA
2020 | 2020-02-27 | Ashland | 71110118 | DKY0101944 | 38830046B12138 | TRUE | 3000102-ASHLAND / 25-29STRE | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 3500 Winchester Ave, Ashland, KY 41101, USA | 2022-03-24
2020 | 2020-02-27 | Ashland | 71110142 | DKY0102033 | 38830046B12139 | TRUE | 3000102-ASHLAND / 25-29STRE | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 3408 Winchester Ave, Ashland, KY 41101, USA | 2022-03-25
2020 | 2020-02-27 | Ashland |  |  | 38830070A31100 |  | 3000102-ASHLAND / 25-29STRE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | 3 phase primary insulator laying against pole. Pole ground stolen. | 39th Street & Winchester Ave, Ashland, KY 41101, USA
2020 | 2020-02-27 | Ashland |  |  | 39831098B12007 |  | 3110903-WURTLAND / RT.503 | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Xarm brace is split. | 102 Kentucky Ave, Wurtland, KY 41144, USA
2020 | 2020-02-28 | Ashland | 76261184 |  | 39831122A00158 |  | 3110903-WURTLAND / RT.503 | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 245 Rabbitery Rd, Wurtland, KY | 2020-04-08
2020 | 2020-02-28 | Ashland | 72986600 | DKY0104762 | 39831122A00303 | TRUE | 3110903-WURTLAND / RT.503 | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Primary guy wire is broken. Unable to locate anchor. | 267 Yates Rd, Wurtland, KY 41144, USA | 2022-05-12
2020 | 2020-02-28 | Ashland |  |  | 39831122B00049 |  | 3110903-WURTLAND / RT.503 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). | 2372 Uhlens Banch Rd, Greenup, KY 41144, USA
2020 | 2020-02-28 | Ashland | 72986540 | DKY0104666 | 39831146A00119 | TRUE | 3110903-WURTLAND / RT.503 | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Inactive transformer. | Melvin Cemetery Rd, Greenup, KY | 2022-01-31
2020 | 2020-02-28 | Ashland | 72986540 | DKY0104666 | 39831146A00296 | TRUE | 3110903-WURTLAND / RT.503 | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Inactive transformer. | Melvin Cemetery Rd, Greenup, KY | 2022-01-31
2020 | 2020-03-02 | Ashland |  |  | 38830018000095 |  | 3110903-WURTLAND / RT.503 | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer. Pole next to pond. | Pleasant Valley, Wurtland, KY
2020 | 2020-03-02 | Ashland |  |  | 38830018000191 |  | 3110903-WURTLAND / RT.503 | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Remove inactive transformer. Pole next to stream. | Garvin Rd, Wurtland, KY
2020 | 2020-03-02 | Ashland | 84587466 | DKY0119941 | 38830018000217 |  | 3110903-WURTLAND / RT.503 | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. Pole is in field next to stream. | 4094 Hwy 207, Wurtland, KY | 2023-04-10
2020 | 2020-03-02 | Ashland | 72986524 | DKY0105612 | 39831146C20415 | TRUE | 3110903-WURTLAND / RT.503 | Line Work | OH | UG conduit: damaged or separated | pole: leaning, burned more than 50% remaining |  | KPC | NO | UG conduit is separated at base of pole because pole is leaning. Placed yellow caution tape around area. | 290 Gillum Ln, Wurtland, KY 41144, USA | 2020-05-07
2020 | 2020-03-03 | Ashland | 72837453 | DKY0104428 | 38830018000055 |  | 3110903-WURTLAND / RT.503 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Insulator missing in neutral clevis. | Hensley Hollow, Wurtland, KY | 2022-04-18
2020 | 2020-03-03 | Ashland | 72837483 | DKY0104425 | 38830042000093 |  | 3110903-WURTLAND / RT.503 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , guys/anchors: broken or missing |  |  | Foreign | YES | Large chuck of wood missing at base of pole. Also, base of pole is deteriorating. | 6963 Naples Rd, Greenup, KY 41144, USA | 2022-05-31
2020 | 2020-03-03 | Ashland | 72986698 | DKY0104826 | 39831098B43537 | TRUE | 3110903-WURTLAND / RT.503 | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Primary guy wire broken. Anchor is in good condition. | Darius Ct, Wurtland, KY 41144, USA | 2022-03-25
2020 | 2020-03-04 | Ashland | 77424129 | DKY0112460 | 39831098B33011 |  | 3110903-WURTLAND / RT.503 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is showing deterioration at top of pole and wood splitting from surface of pole. Pole has metal band attached at base. I believe this pole should be changed out. | 305 Central Ave, Wurtland, KY 41144, USA | 2022-04-20
2020 | 2020-03-04 | Ashland | 76243026 |  | 39831098B33030 |  | 3110903-WURTLAND / RT.503 | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. Pole is at entrance of alley. | East St, Wurtland, KY 41144, USA | 2020-04-06
2020 | 2020-03-04 | Ashland | 76243148 |  | 39831098B33120 |  | 3110903-WURTLAND / RT.503 | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | 600 East St, Wurtland, KY 41144, USA | 2020-04-06
2020 | 2020-03-04 | Ashland | 76249403 |  | 39831098D06028 |  | 3110903-WURTLAND / RT.503 | Service Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Primary guy wire broken and nailed to pole by customer. Guy wire is not needed here and should be removed. | 968 Madison Ave, Wurtland, KY 41144, USA | 2020-04-07
2020 | 2020-03-05 | Ashland |  |  | 39831098D00249 |  | 3110903-WURTLAND / RT.503 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). Pole failed sound test and is deteriorating. | Cr-1109E, Wurtland, KY 41144, USA
2020 | 2020-03-05 | Ashland |  |  | 39831098D00250 |  | 3110903-WURTLAND / RT.503 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). Pole failed sound test and is deteriorating. | Cr-1109E, Wurtland, KY 41144, USA
2020 | 2020-03-09 | Ashland | 72992764 | DKY0105608 | 39831098B10385 | TRUE | 3110901-WURTLAND / WURTLAND | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole. | Wurtland Ave, Wurtland, KY, USA | 2021-02-03
2020 | 2020-03-09 | Ashland | 76250647 |  | 39831098B10386 |  | 3110901-WURTLAND / WURTLAND | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 400 Harris Rd, Wurtland, KY 41144, USA | 2020-04-07
2020 | 2020-03-09 | Ashland | 76249410 |  | 39831098B33002 |  | 3110901-WURTLAND / WURTLAND | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | Wurts Rd, Wurtland, KY 41144, USA | 2020-04-07
2020 | 2020-03-09 | Ashland | 76250197 |  | 39831098D00353 |  | 3000903-HIGHLAND / WURTLAND | Service Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Primary guy wire is broken. Anchor is in good condition. | Greenup Rd, Wurtland, KY | 2020-04-07
2020 | 2020-03-09 | Ashland | 76240777 |  | 39831098D00357 |  | 3000903-HIGHLAND / WURTLAND | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 1222 Wurtland Ave, Wurtland, KY 41144, USA | 2020-04-06
2020 | 2020-03-10 | Ashland | 76249392 |  | 39831098D00106 |  | 3000903-HIGHLAND / WURTLAND | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground is stolen. | 1214 Riverside Blvd, Wurtland, KY 41144, USA | 2020-04-07
2020 | 2020-03-10 | Ashland | 76240279 |  | 39831098D00307 |  | 3000903-HIGHLAND / WURTLAND | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen. | 100 Highland Ave, Wurtland, KY 41169, USA | 2020-04-06
2020 | 2020-03-11 | Ashland | 76240606 |  | 39831098D00125 |  | 3000903-HIGHLAND / WURTLAND | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen. | 416 Chinn St, Wurtland, KY 41144, USA | 2020-04-06
2020 | 2020-03-11 | Ashland | 73914871 | DKY0106258 | 39831098D00259 | TRUE | 3000903-HIGHLAND / WURTLAND | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Xarm brace broken. |  | 2022-03-30
2020 | 2020-03-11 | Ashland | 76249393 |  | 39831098D00493 |  | 3000903-HIGHLAND / WURTLAND | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground is broken and wrapped around pole. Pole ground should be removed, it is not needed here. | 1014 Scott Ave, Wurtland, KY 41144, USA | 2020-04-07
2020 | 2020-03-11 | Ashland | 76242781 |  | 39831098D00499 |  | 3000903-HIGHLAND / WURTLAND | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 1000 Scott Ave, Wurtland, KY 41144, USA | 2020-04-06
2020 | 2020-03-11 | Ashland | 73914940 | DKY0106074 | 39831122C00276 | TRUE | 3000903-HIGHLAND / WURTLAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer. | KY-693, Wurtland, KY, USA | 2022-03-23
2020 | 2020-03-11 | Ashland |  |  | 39831122D00208 |  | 3000903-HIGHLAND / WURTLAND | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | China’s Br, Wurtland, KY | 2023-01-31
2020 | 2020-03-12 | Ashland | 73914940 | DKY0106074 | 39831098D00701 | TRUE | 3000903-HIGHLAND / WURTLAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. Pole in open field. | Chestnut St, Greenup, KY 41144, USA | 2022-03-23
2020 | 2020-03-12 | Ashland | 73914940 | DKY0106074 | 39831122C00014 | TRUE | 3000903-HIGHLAND / WURTLAND | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Primary guy wire broken. Pole next to Popular St. | Racetrack Hill, Wurtland, KY 41169, USA | 2022-03-23
2020 | 2020-03-12 | Ashland |  |  | 39831122C00221 |  | 3000903-HIGHLAND / WURTLAND | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer. | Thornton St, Kentucky 41169, USA
2020 | 2020-03-13 | Ashland |  |  | 39831122C00074 |  | 3000903-HIGHLAND / WURTLAND | Forestry | OH |  |  |  | Foreign | NO | Tree has rubbed loose tie wire to secondary. Forestry: work is outside scope, secondary conductor: pole to house service drop. Would require outage to work safely. | 910 KY-693, Raceland, KY 41169, USA | 2020-12-04
2020 | 2020-03-17 | Ashland | 73914968 | DKY0106251 | 39831123A28133 | TRUE | 3000901-HIGHLAND / RUSSELL | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Broken Xarm brace. | Caroline Rd, Raceland, KY, USA | 2022-03-25
2020 | 2020-03-18 | Ashland |  |  | 38830069C35105 | TRUE | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). | 2701 Cambridge Dr, Flatwoods, KY 41139, USA
2020 | 2020-03-18 | Ashland |  |  | 39831123B00578 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Arrester damaged. | 1815 Summer St, Flatwoods, KY 41139, USA
2020 | 2020-03-18 | Ashland |  |  | 39831147A01049 | TRUE | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NEEDS ADDITIONAL CHECK | Top of pole is burnt from the past. This is a foreign pole and I believe it should be replaced. | 1618 Valley Dr, Flatwoods, KY 41139, USA
2020 | 2020-03-19 | Ashland | 76091496 | DKY0108901 | 38830403000048 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Ann Campbell found and wrote WR 76091496 DKY0108901. Not in the dae, placed in smartsheet. Down between poles 38830403000048 to 38830403000049 | 2056 Big Cat Fork Rd, Louisa, KY 41230, USA | 2020-06-10
2020 | 2020-03-19 | Ashland |  |  | 39831098C00551 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Deteriorated pole. Pole is leaning. | 1529 Elmhurst Dr, Worthington, KY 41183, USA
2020 | 2020-03-19 | Ashland |  |  | 39831098C00552 | TRUE | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 1632 Gainesway Dr, Worthington, KY 41183, USA
2020 | 2020-03-19 | Ashland | 77424138 | DKY0111308 | 39831098D00710 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of guy pole splitting. | Carolyn St & McCloud Dr, Worthington, KY 41183, USA | 2020-12-04
2020 | 2020-03-19 | Ashland | 73914813 | DKY0106146 | 39831099B10068 | TRUE | 3000901-HIGHLAND / RUSSELL | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarms showing deterioration. Pole located in CSX yard. | Riverside Blvd, Worthington, KY, USA | 2020-06-01
2020 | 2020-03-20 | Ashland |  |  | 39831098C00535 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). | 1493 S Calumet Ave, Chicago, IL 60616, USA
2020 | 2020-03-20 | Ashland |  |  | 39831098C00536 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). | 1497 S Calumet Dr, Worthington, KY 41183, USA
2020 | 2020-03-20 | Ashland |  |  | 39831098C00540 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). | 1508 Elmhurst Dr, Worthington, KY 41183, USA
2020 | 2020-03-20 | Ashland | 82584012 | DKY0117239 | 39831098C00626 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole (foreign). | 1617 Gainesway Dr, Worthington, KY 41183, USA | 2022-06-23
2020 | 2020-03-23 | Ashland |  |  | 39831099B33019 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole that needs replaced is the guy pole (no pole #) across from pole 1099-3019. | 508 2nd St, Worthington, KY 41183, USA | 2020-10-06
2020 | 2020-03-23 | Ashland | 77424710 | DKY0111309 | 39831099B33021 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole. | 3rd Ave Alley, Worthington, KY 41183, USA | 2021-01-12
2020 | 2020-03-23 | Ashland | 77424776 | DKY0111317 | 39831099B33068 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole. | 2nd Ave Alley, Worthington, KY 41183, USA | 2020-12-08
2020 | 2020-03-24 | Ashland | 85724103 | 036981943 | 39831099B30080 |  | 3000901-HIGHLAND / RUSSELL | Service Work | OH | secondary |  |  | KPC | NO | Secondary attachment is coming loose from transformer pole. Needs to be in summer time when very dry | 100 Scott St, Worthington, KY 41183, USA | 2023-08-15
2020 | 2020-03-24 | Ashland | TT # 4505451 |  | 39831099D16037 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Primary has come loose from primary pole top pin. Called DDC for a TT. // Asked Vernon Mullins to field check if this was completed on the trouble ticket. 6/7/2022. BAM | 905 Market St, Worthington, KY 41183, USA
2020 | 2020-03-24 | Ashland | TT # 4505661/ WR#76253914 |  | 39831099D16039 |  | 3000901-HIGHLAND / RUSSELL | Service Work | OH | service |  |  | KPC | NO | Customer’s house knob has come loose from house. Service drop is 5.5 to 6 feet from ground. Called DDC for a TT. | 1001 Market St, Worthington, KY 41183, USA | 2020-04-07
2020 | 2020-03-25 | Ashland |  |  | 39831100B28094 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Xarm brace is missing (broken off). | Russell-Worthington Rd, Russell, KY, USA
2020 | 2020-03-27 | Ashland |  |  | 38830069C35100 | TRUE | 3008002-47TH STREET / 39TH STREET | Service Work | OH | service |  |  | Foreign | NO | Service drop is wrapped to pole (8 feet from ground) and needs to be removed, still energized. Called DDC and they informed me their system is down. Called Gatlin to fix problem. | 3912 Kenney St, Ashland, KY 41101, USA | 2020-03-27
2020 | 2020-03-27 | Ashland |  |  | 38830069C35100 | TRUE | 3008002-47TH STREET / 39TH STREET | Service Work | OH | service |  |  | Foreign | NO | Service drop is wrapped to pole (8 feet from ground) and needs to be removed, still energized. Called DDC and they informed me their system is down. Called Gatlin to fix problem. | 3912 Kenney St, Ashland, KY 41101, USA | 2020-03-27
2020 | 2020-03-27 | Ashland |  |  | 38830069C35100 |  | 3008002-47TH STREET / 39TH STREET | Service Work | OH | service |  |  | Foreign | NO | Service drop is wrapped to pole (8 feet from ground) and needs to be removed, still energized. Called DDC and they informed me their system is down. Called Gatlin to fix problem. | 3912 Kenney St, Ashland, KY 41101, USA | 2020-03-27
2020 | 2020-03-31 | Ashland |  |  | 38830045D47535 |  | 3008002-47TH STREET / 39TH STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Across rom 1016 Belmont St. | Belmont St, Ashland, KY 41101, USA
2020 | 2020-03-31 | Ashland | 71005746 | DKY0101855 | 38830045D47546 | TRUE | 3008002-47TH STREET / 39TH STREET | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | Belmont St, Ashland, KY 41101, USA | 2022-02-16
2020 | 2020-03-31 | Ashland |  |  | 38830069C35081 |  | 3008002-47TH STREET / 39TH STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | Baer St, Ashland, KY 41101, USA | 2021-01-18
2020 | 2020-03-31 | Ashland |  |  | 38830069C35084 |  | 3008002-47TH STREET / 39TH STREET | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections , lightning arresters/insulators: damaged |  | Foreign | NO | Replace damaged arrester (12KV) and stolen pole ground.
2020 | 2020-03-31 | Ashland |  |  | 38830069C35105 | TRUE | 3008002-47TH STREET / 39TH STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 3913 Putnam St, Ashland, KY 41101, USA
2020 | 2020-03-31 | Ashland | 78627576 |  | 38830069C35164 |  | 3008002-47TH STREET / 39TH STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 1713 Nervie St, Ashland, KY 41101, USA | 2021-01-18
2020 | 2020-03-31 | Ashland | 78627576 |  | 38830069C45520 |  | 3008002-47TH STREET / 39TH STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 2020 Belmont St, Ashland, KY 41101, USA | 2021-01-18
2020 | 2020-03-31 | Ashland |  |  | 38830069C45537 |  | 3008002-47TH STREET / 39TH STREET | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen. | 4226 Blackburn Ave, Ashland, KY 41101, USA | 2021-01-18
2020 | 2020-03-31 | Ashland | 78627576 |  | 38830069C45587 |  | 3008002-47TH STREET / 39TH STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 3921 Logan St, Ashland, KY 41101, USA | 2021-01-18
2020 | 2020-04-01 | Ashland |  |  | 38830045D26594 | TRUE | 3008002-47TH STREET / 39TH STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 3221 Newman St, Ashland, KY 41101, USA | 2021-01-18
2020 | 2020-04-01 | Ashland |  |  | 38830045D26597 |  | 3008002-47TH STREET / 39TH STREET | Forestry | OH |  |  | Circuit currently being recleared now. | Foreign | NO | Trees are against pole and in primary area. |  | 2020-05-31
2020 | 2020-04-01 | Ashland |  |  | 38830045D47515 |  | 3008002-47TH STREET / 39TH STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 1040 29th St, Ashland, KY 41101, USA | 2021-01-18
2020 | 2020-04-01 | Ashland |  |  | 38830045D47536 |  | 3008002-47TH STREET / 39TH STREET | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm is twisted at one end of xarm and showing signs of splitting. | Belmont St, Ashland, KY 41101, USA
2020 | 2020-04-01 | Ashland |  |  | 38830045D47562 |  | 3008002-47TH STREET / 39TH STREET | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground is stolen. | Walters St & Simpson Rd, Ashland, KY 41101, USA | 2021-01-18
2020 | 2020-04-01 | Ashland | 71005403 | DKY0101791 | 38830045D47630 | TRUE | 3008002-47TH STREET / 39TH STREET | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 3225 Newman St, Ashland, KY 41101, USA | 2022-02-16
2020 | 2020-04-01 | Ashland |  |  | 38830045D47658 |  | 3008002-47TH STREET / 39TH STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 1109 Belmont St, Ashland, KY 41101, USA | 2021-01-18
2020 | 2020-04-02 | Ashland |  |  | 38830045D26601 |  | 3008002-47TH STREET / 39TH STREET | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. | 2600 Country Club Ct, Ashland, KY 41101, USA | 2020-04-02
2020 | 2020-04-03 | Ashland |  |  | 38830045D26601 |  | 3008002-47TH STREET / 39TH STREET | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. | 2600 Country Club Ct, Ashland, KY 41101, USA
2020 | 2020-04-06 | Ashland | 73915134 | DKY0105983 | 39831099B43558 |  | 3000902-HIGHLAND / FLATWOODS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Brace pole is deteriorating at base. Main pole passed sound test. | Crump St & Chinn St, Raceland, KY 41169, USA | 2021-08-30
2020 | 2020-04-14 | Ashland |  |  | 39831123C24540 |  | 3000902-HIGHLAND / FLATWOODS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Set in 1957. | 712 Winters Dr, Raceland, KY 41169, USA
2020 | 2020-04-14 | Ashland | 73915030 | DKY0108693 | 39831123D16023 | TRUE | 3000902-HIGHLAND / FLATWOODS | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. | 1716 Lexington Ave, Flatwoods, KY 41139, USA | 2022-03-21
2020 | 2020-04-15 | Ashland |  |  | 38830070B33103 |  | 3008001-47TH STREET / 49TH STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | Cordial Dr, Ashland, KY 41101, USA
2020 | 2020-04-20 | Ashland | 71006497 | DKY0101818 | 38830069D28166 |  | 3008001-47TH STREET / 49TH STREET | Line Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground stolen. | Azalea Dr, Ashland, KY 41102, USA | 2022-03-15
2020 | 2020-04-20 | Ashland |  |  | 38830070B12230 | TRUE | 3008001-47TH STREET / 49TH STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 821 Halbert St, Ashland, KY 41101, USA
2020 | 2020-04-21 | Ashland | 77190442 |  | 38830070B12189 |  | 3008001-47TH STREET / 49TH STREET | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Pole ground cut. | Shadowlawn Dr, Ashland, KY 41101, USA | 2020-07-17
2020 | 2020-04-21 | Ashland |  |  | 38830070B12230 | TRUE | 3008001-47TH STREET / 49TH STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | Halbert St & Patton St, Ashland, KY 41101, USA
2020 | 2020-04-23 | Ashland | 78063451 |  | 38830069D37159 |  | 3008001-47TH STREET / 49TH STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 2500 Bradley Dr, Ashland, KY 41101, USA | 2020-10-27
2020 | 2020-04-24 | Ashland | 77424946 | DKY0111645 | 38830070B22574 |  | 3008001-47TH STREET / 49TH STREET | Line Work | OH |  |  |  | KPC | YES | Replace deteriorated pole. | Powers Rd, Ashland, KY 41101, USA | 2020-12-12
2020 | 2020-04-27 | Ashland |  |  | 38830069C45624 |  | 3008001-47TH STREET / 49TH STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 4324 Gartin Ave, Ashland, KY 41101, USA
2020 | 2020-04-29 | Ashland | 71346053 | DKY0102172 | 39831147C24595 |  | 3116701-BELHAVEN / DIEDERICH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 2417 Todd St, Flatwoods, KY 41139, USA | 2021-08-25
2020 | 2020-04-29 | Ashland |  |  | 39831147C45576 |  | 3116701-BELHAVEN / DIEDERICH | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Vines growing on pole and need to be cut. work was completed on 2020 work plan. | 120 Thompson Rd, Russell, KY 41139, USA | 2020-07-22
2020 | 2020-04-30 | Ashland | 71350221 | DKY0102193 | 39831147D40451 |  | 3116701-BELHAVEN / DIEDERICH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 719 Short White Oak Rd, Russell, KY 41169, USA | 2021-08-25
2020 | 2020-05-11 | Ashland | 71445431 | DKY0102520 | 39831147D30299 | TRUE | 3116702-BELHAVEN / INDIAN RUN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 152 Thompson Rd, Russell, KY 41169, USA | 2021-08-25
2020 | 2020-05-12 | Ashland | 76596510 | DKY0109661 | 38830044B00620 |  | 3000303-BELLEFONT / BELLEFONT | Line Work | OH |  |  |  | Foreign | NO | One span of neutral down, 44-620 to 44-621. Bre Howell wrote WO | 4109 Killen Dr, Ashland, KY 41102, USA | 2020-05-22
2020 | 2020-05-12 | Ashland | 71371032 | DKY0102271 | 39831147A00330 | TRUE | 3116702-BELHAVEN / INDIAN RUN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Base of pole is splitting. | 1514 Bellefonte Rd, Flatwoods, KY 41139, USA | 2021-08-25
2020 | 2020-05-12 | Ashland | 71405234 | DKY0102307 | 39831147C14061 | TRUE | 3116702-BELHAVEN / INDIAN RUN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole and push-brace pole. | 2504 Needa St, Flatwoods, KY 41139, USA | 2022-04-25
2020 | 2020-05-12 | Ashland | 85539381 | DKY0121381 | 39831147C24633 | TRUE | 3116702-BELHAVEN / INDIAN RUN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Behind Pleasant View Apts. | 2719 Fields Ave, Flatwoods, KY 41139, USA | 2023-07-19
2020 | 2020-05-13 | Ashland | 71405126 | DKY0102278 | 39831147A00442 | TRUE | 3116702-BELHAVEN / INDIAN RUN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | Cs-2007, Flatwoods, KY 41139, USA | 2021-08-25
2020 | 2020-05-13 | Ashland | 85541214 | DKY0122887 | 39831147C14170 | TRUE | 3116702-BELHAVEN / INDIAN RUN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 1403 Taylor St, Flatwoods, KY 41139, USA
2020 | 2020-05-20 | Ashland | 83955278 | DKY0118792 | 39831123B00570 | TRUE | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Bad arrester. Change out silver-top at the same time. | 2418 Foxmore Ct, Flatwoods, KY 41139, USA | 2023-02-15
2020 | 2020-05-20 | Ashland | 71514845 | DKY0102553 | 39831147C14097 | TRUE | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated (cracked) pole. | 2305 Spring St, Flatwoods, KY 41139, USA | 2022-03-16
2020 | 2020-05-21 | Ashland |  |  | 39831147D10965 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Vines growing up pole in to primary. Two spans out on pole # 1147D186 vines growing up pole to transformer and primary. work will be completed on this years work plan for 2020 crews will be starting work on this circuit. | KY-1458, Flatwoods, KY, USA | 2020-12-04
2020 | 2020-05-22 | Ashland | 71514813 | DKY0102539 | 39831147B00503 | TRUE | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 1291 Reid St, Flatwoods, KY 41139, USA | 2021-08-25
2020 | 2020-05-27 | Ashland | 71445466 | DKY0102397 | 38830019C00043 | TRUE | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | Short White Oak Rd, Russell, KY, USA | 2021-11-01
2020 | 2020-05-28 | Ashland |  |  | 39831124B22503 | TRUE | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 715 Highland Ave, Flatwoods, KY 41139, USA
2020 | 2020-06-01 | Ashland | 71514792 | DKY0102604 | 39831147A00550 | TRUE | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | Brent Ann Dr, Flatwoods, KY 41139, USA | 2022-08-22
2020 | 2020-06-02 | Ashland |  |  | 39830902C00613 |  | 3004301-Siloam / Siloam | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Tree branches and vines laying on neutral and causing dead-end pole to lean along with primary and neutral. tree crew need an outage to work safely. | 115 1st St, South Shore, KY 41175, USA | 2020-12-04
2020 | 2020-06-03 | Ashland | 74862711 | DKY0108022 | 39830903000011 | TRUE | 3004301-Siloam / Siloam | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Replace deteriorated Xarm. | Johnson's Ln, Kentucky 41175, USA | 2022-02-01
2020 | 2020-06-04 | Ashland | 75909420 | DKY0108638 | 39830879D00107 | TRUE | 3004301-Siloam / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. Next to RR tracks on De Antoine Ln. | Cr-1036, Kentucky 41175, USA | 2022-02-14
2020 | 2020-06-05 | Ashland |  |  | 39830879D00054 |  | 3004301-Siloam / Siloam | Line Work | OH |  |  |  | KPC | NO | 3 spans of neutral stolen. I drew a map for technician. | Siloam Rd, Kentucky 41175, USA
2020 | 2020-06-16 | Ashland |  |  | 39831148B10087 | TRUE | 3010601-RUSSELL / KENWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 100 Blantel Dr, Russell, KY 41169, USA
2020 | 2020-06-16 | Ashland | 85440057 | DKY0121640 | 39831148B40363 | TRUE | 3010601-RUSSELL / KENWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 1030 Amherst Dr, Ashland, KY 41101, USA
2020 | 2020-06-17 | Ashland |  |  | 39831124B43544 |  | 3010601-RUSSELL / KENWOOD | Line Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Vines growing around transformer and into primary. Transformer goes to large water tank. | 120 Bear Run Rd, Russell, KY 41169, USA
2020 | 2020-06-17 | Ashland |  |  | 39831148A00334 |  | 3010601-RUSSELL / KENWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Pole tag shows 148-384. | 116 Meadowlark Rd, Russell, KY 41169, USA
2020 | 2020-06-17 | Ashland | 74149512 | DKY0106168 | 39831148A00382 | TRUE | 3010601-RUSSELL / KENWOOD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. | 601 | 2022-03-30
2020 | 2020-06-19 | Ashland |  |  | 39831147C35094 |  | 3010601-RUSSELL / KENWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 1710 Cs-2127, Flatwoods, KY 41139, USA | 2021-08-30
2020 | 2020-06-19 | Ashland |  |  | 39831147C35132 | TRUE | 3010601-RUSSELL / KENWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Pole is next to small shed. | 706 Nash St, Flatwoods, KY 41139, USA | 2022-05-27
2020 | 2020-06-25 | Ashland |  |  | 39831148A00538 |  | 3010601-RUSSELL / KENWOOD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Large tree is dead and close to 3 phase conductors. Across from First Baptist Church of Russell. Should be removed. this tree has been removed. | 901 Ashland Dr, Russell, KY 41101, USA | 2020-11-05
2020 | 2020-06-26 | Ashland | 80430296 | DKY0114585 | 39831124A41508 |  | 3010602-RUSSELL / BEARRUN | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | 323 Ferry St, Russell, KY 41169, USA | 2021-12-21
2020 | 2020-06-29 | Ashland |  |  | 39831124A20599 |  | 3010602-RUSSELL / BEARRUN | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Heavy vines growing up pole and around transformer. Pole is one span down from reclosure pole. vines have been cut and sprayed at transformer pole. | US-23, Russell, KY, USA | 2020-11-03
2020 | 2020-06-29 | Ashland |  |  | 39831124B12071 |  | 3010602-RUSSELL / BEARRUN | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Vines growing up pole (1124B2071) into transformer and tree branches growing around street light pole (1124B8109). vines have been cut and sprayed at transformer pole. Forestry does not trim for street lights. | 901 Poplar St, Flatwoods, KY 41139, USA | 2020-11-10
2020 | 2020-06-29 | Ashland |  |  | 39831124B12081 |  | 3010602-RUSSELL / BEARRUN | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Vines growing up pole and around transformer bank. vines have been cut and sprayed at transformer pole. | 879 Poplar St, Russell, KY 41169, USA | 2020-11-04
2020 | 2020-06-29 | Ashland |  |  | 39831124B18109 |  | 3010602-RUSSELL / BEARRUN | Service Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Customer informed me that street light in front of their home is not working. I have wrote up a separate order to have tree branches removed at this pole blocking light. | 901 Poplar St, Flatwoods, KY 41139, USA | 2023-01-30
2020 | 2020-07-07 | Ashland | 71204149 | DKY0102082 | 38830020A31032 | TRUE | 3000302-BELLEFONT / FLATWOODS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | Forestry - DESCRIBE IN COMMENTS | Foreign | YES | Replace deteriorated pole. | 502 Franklin Ct, Ashland, KY 41101, USA | 2022-02-28
2020 | 2020-07-07 | Ashland |  |  | 38830020C35095 |  | 3000302-BELLEFONT / FLATWOODS | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree branches close to primary conductors. You can see burnt leaves from the past. Next to Bellefonte Sub-station. This work is on the 2020 plan to be done. | US-23, Russell, KY, USA | 2020-12-04
2020 | 2020-07-07 | Ashland |  |  | 39831148B40979 |  | 3000302-BELLEFONT / FLATWOODS | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree branches close to primary conductors. Leaves appear burnt with binoculars. This work is on the 2020 plan to be worked. | 784 Diederich Blvd, Ashland, KY 41101, USA | 2020-12-04
2020 | 2020-07-08 | Ashland | 78660260 |  | 38830305000055 |  | 3001001-HITCHINS / DENTON | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to recloser. | Glenwood Branch Rd, Kentucky, USA | 2021-01-22
2020 | 2020-07-08 | Ashland | 78315621 | DKY0111911 | 38830400000037 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC | NO | One span of neutral stolen at recloser pole. Intersection of Dry Fork Rd. & Needmore Rd. | Willard, KY 41143, USA | 2021-01-06
2020 | 2020-07-13 | Ashland |  |  | 38830118A00017 |  | 3008003-47TH STREET / CATLETTSB | Forestry | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | guys/anchors: loose, damaged, need insulator/marker | Forestry - Need work order to replace pole and guy wires. Will cut limb off guy on DKY or regular maintenance cycle. Which ever one comes first. | KPC | NO | Large tree laying on primary, telephone and TV guy wires. Primary guy wire broken loose from anchor. | 2005 Barbeque Rd, Catletsburg, KY | 2020-07-28
2020 | 2020-07-14 | Ashland |  |  | 38830094B00006 | TRUE | 3008003-47TH STREET / CATLETTSB | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole is leaning and soil is washed out around pole. Unable to locate birthmark. Is pole at proper depth? It is truck accessible with caution. | 7472 Hwy 168, Catletsburg, KY
2020 | 2020-07-14 | Ashland | 77188568 |  | 38830118B00160 |  | 3008003-47TH STREET / CATLETTSB | Service Work | UG | UG conduit: damaged or separated |  |  | KPC | NO | Customer’s UG conduit damaged. Tied yellow caution tape around damaged area. | 7916 Cannonsburg Rd, Catlettsburg, KY | 2020-07-17
2020 | 2020-07-15 | Ashland | 85776094 | DKY0121762 | 38830094D16039 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 2010 Center St, Catlettsburg, KY 41129, USA | 2023-09-11
2020 | 2020-07-15 | Ashland |  |  | 38830094D26624 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Service pole is in alley. | 204 26th St, Catlettsburg, KY 41129, USA
2020 | 2020-07-15 | Ashland |  |  | 38830118B00257 |  | 3008003-47TH STREET / CATLETTSB | Forestry | OH | Sprayed by Progressive. Work complete. |  | Forestry - | KPC | NO | Vines growing up pole and around line regulator. | 8413 36th St, Catlettsburg, KY 41129, USA | 2020-07-28
2020 | 2020-07-15 | Ashland |  |  | 38830118C14022 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH | cutout: damaged |  |  | Foreign | NO | Two porcelain line cut-outs (12KV) broken. “B” and “C” phase. “C” phase hot line tap is lifted. Pole next to alley entrance. | 105 30th St, Catlettsburg, KY 41129, USA
2020 | 2020-07-15 | Ashland | 71006914 | DKY0101814 | 38830118C24586 | TRUE | 3008003-47TH STREET / CATLETTSB | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | End of xarm splitting. | 3301 Oakland Ave, Catlettsburg, KY 41129, USA | 2022-04-29
2020 | 2020-07-16 | Ashland | 77424956 | DKY0111646 | 38830118D26506 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Push brace pole deteriorated at base and attachment at top of pole appears loose. | Valley St & Neal St, Catlettsburg, KY 41129, USA | 2020-12-10
2020 | 2020-07-27 | Ashland |  |  | 38830021B12058 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH | Will cut/spray on regular maintenance cycle. |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Vines growing up pole and around 3 phase transformers. | 111 Armco Blvd, Westwood, KY 41101, USA | 2020-07-28
2020 | 2020-07-27 | Ashland |  |  | 38830021B22579 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH | Will cut/spray on regular maintenance cycle. |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Vines growing up pole and around transformer. | 181 W Central Ave, Ashland, KY 41101, USA | 2020-07-28
2020 | 2020-07-28 | Ashland |  |  | 38830020B43513 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH | Will cut/spray on regular maintenance cycle. |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Vines growing up pole and around transformer. | 2619 Hoods Creek Pike, Ashland, KY 41102, USA | 2020-07-28
2020 | 2020-07-28 | Ashland |  |  | 38830020D26514 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH | Will cut/spray on regular maintenance cycle. |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Vines growing up pole. | Hoods Creek Pike, Westwood, KY, USA | 2020-07-28
2020 | 2020-07-28 | Ashland | 77473410 |  | 38830020D26548 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 2403 4th St W, Ashland, KY 41102, USA | 2020-08-19
2020 | 2020-07-28 | Ashland | 71193525 | DKY0102024 | 38830020D26567 | TRUE | 3000301-BELLEFONT / WESTWOOD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NEEDS ADDITIONAL CHECK | Xarm is deteriorating. Pole passed sound test. Pole was set in 1924. | 2319 Hoods Creek Pike, Ashland, KY 41101, USA | 2021-08-25
2020 | 2020-07-28 | Ashland |  |  | 38830020D37135 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | One arrester (7200 KV) to 3 phase bank is damaged. Pole in Dollar General store parking lot. | 1732 Hoods Creek Pike, Westwood, KY, USA | 2023-11-16
2020 | 2020-07-28 | Ashland |  |  | 38830020D47617 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH | Will cut/spray on regular maintenance cycle. |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Vines growing up pole and around transformer. | 715 Unrue St, Ashland, KY 41102, USA | 2020-07-28
2020 | 2020-07-29 | Ashland | 86352757 | DKY0123286 | 38830020D37045 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole around transformer attachment area appears broken. Unable to tell with binoculars. Needs to be checked out with bucket truck as soon as possible. Base of pole passed sound test. | 1300 Hoods Creek Pike, Ashland, KY 41101, USA
2020 | 2020-07-29 | Ashland | 77471790 |  | 38830020D47502 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to transformer pole. | 1415 High St, Westwood, KY 41101, USA | 2020-08-18
2020 | 2020-07-29 | Ashland | 86353080 | DKY0122789 | 38830020D47536 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | End of xarm splitting. | Collins Ln, Westwood, KY, USA
2020 | 2020-07-29 | Ashland |  |  | 38830020D47561 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Entire circuit needs to be recleared. Will address all vines on regular maintenance schedule then. | 437 Bellefonte Rd, Ashland, KY 41102, USA | 2020-08-10
2020 | 2020-07-29 | Ashland | 77472173 |  | 38830021B22602 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen to non-equipment. | Oakwood Manor, Westwood, KY 41101, USA | 2020-08-18
2020 | 2020-07-29 | Ashland |  |  | 38830021B22616 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Entire circuit needs to be recleared. Will address all vines on regular maintenance schedule then. | 334 W Central Ave, Westwood, KY 41101, USA | 2020-08-10
2020 | 2020-07-30 | Ashland | 71204111 | DKY0102494 | 38830044C35048 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is deteriorated (failed sound test). Needs replaced as soon as possible. | 437 Prichard St, Ashland, KY 41102, USA | 2021-08-25
2020 | 2020-07-31 | Ashland |  |  | 38830044C14074 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Guy pole deteriorated at base and pole is leaning. | Old Buckley Road & Butler St, Westwood, KY 41102, USA
2020 | 2020-07-31 | Ashland |  |  | 38830044C14094 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Entire circuit needs to be recleared. Will address on regular maintenance schedule then. | 605 Zanesville, Ashland, KY 41102, USA | 2020-08-10
2020 | 2020-07-31 | Ashland |  |  | 38830044C24508 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole deteriorated at base. Pole should be replaced as soon as possible. | 911 Old Buckley Road, Ashland, KY 41102, USA
2020 | 2020-07-31 | Ashland | 77532318 |  | 38830044C24521 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen to 3 phase reclosers. | 2731 Main St W, Ashland, KY 41102, USA | 2020-08-25
2020 | 2020-08-03 | Ashland |  |  | 38830044C24571 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Entire circuit needs to be recleared. Will address all vines on regular maintenance schedule then. | Main St W & McKnight St, Westwood, KY 41102, USA | 2020-08-10
2020 | 2020-08-03 | Ashland | 77471250 |  | 38830044C24602 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground cut to transformer pole. | 220 McCown Rd, Ashland, KY 41102, USA | 2020-08-18
2020 | 2020-08-03 | Ashland |  |  | 38830044C24619 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Entire circuit needs to be recleared. Will address all vines on regular maintenance schedule then. | 150 McCown Rd, Ashland, KY 41102, USA | 2020-08-10
2020 | 2020-08-03 | Ashland |  |  | 38830044D16015 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Entire circuit needs to be recleared. Will address all vines on regular maintenance schedule then. | 368 Pine Acres Dr, Ashland, KY 41102, USA | 2020-08-10
2020 | 2020-08-03 | Ashland |  |  | 38830044D16022 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Entire circuit needs to be recleared. Will address all vines on regular maintenance schedule then. | 230 McKnight St, Ashland, KY 41102, USA | 2020-08-10
2020 | 2020-08-03 | Ashland |  |  | 38830044D37100 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Entire circuit needs to be recleared. Will address all vines on regular maintenance schedule then. | 920 Commanche Dr, Ashland, KY 41102, USA | 2020-08-10
2020 | 2020-08-04 | Ashland |  |  | 38830044C14063 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole as soon as possible. Pole is leaning. | Piqua St & Zanesville, Westwood, KY 41102, USA
2020 | 2020-08-04 | Ashland | 78202117 | DKY0111851 | 38830044C45588 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is deteriorated at base. Replace deteriorated pole as soon as possible. | 349 Cr-1044D5, Ashland, KY 41102, USA | 2021-07-22
2020 | 2020-08-04 | Ashland |  |  | 38830044D37054 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Entire circuit needs to be recleared. Will address all vines on regular maintenance schedule then. | 111 McKnight St, Ashland, KY 41102, USA | 2020-08-10
2020 | 2020-08-04 | Ashland |  |  | 38830044D37124 |  | 3000301-BELLEFONT / WESTWOOD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Vines growing up pole and around primary UG. Pole located in trailer park. | McKnight St, Westwood, KY 41102, USA | 2020-08-10
2020 | 2020-08-05 | Ashland | 86350347 |  | 38830020C45519 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. | French Broad St & Price St, Westwood, KY 41101, USA
2020 | 2020-08-05 | Ashland | 86352702 |  | 38830020C45521 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarms deteriorating. | 1301 French Broad St, Westwood, KY 41101, USA
2020 | 2020-08-05 | Ashland | 77508351 |  | 38830020D37017 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Service drop attachment has come loose from secondary. Need bucket truck to make repairs. | 1002 French Broad St, Westwood, KY 41101, USA | 2020-08-21
2020 | 2020-08-10 | Ashland |  |  | 38830020C14005 | TRUE | 3000303-BELLEFONT / BELLEFONT | Line Work | OH | broken/split | lightning arresters/insulators: damaged |  | Foreign | NEEDS ADDITIONAL CHECK | Pole is cracked 10 feet up from ground. Unable to tell if pole is cracked all the way threw the pole. Needs to be checked out by service bucket truck. Pole passed sound test at base. One of the primary insulators (“B” phase) is broken. | Patton Dr & Bellefonte Princess Rd, Westwood, KY 41101, USA
2020 | 2020-08-10 | Ashland | 71271248 | DKY0102109 | 38830020C14027 | TRUE | 3000303-BELLEFONT / BELLEFONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at base. Pole should be replaced this year. | 127 Lycan Rd, Bellefonte, KY 41101, USA | 2021-06-10
2020 | 2020-08-18 | Ashland |  |  | 38830043000066 | TRUE | 3000303-BELLEFONT / BELLEFONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NO | Pole is set on side of creek bed. Soil has been washed away around pole. Is pole set at proper depth? It needs to be checked out as soon as possible. | 427 Rockhouse Rd, Ashland, KY 41102, USA
2020 | 2020-08-18 | Ashland |  |  | 38830044A00109 |  | 3000303-BELLEFONT / BELLEFONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NEEDS ADDITIONAL CHECK | Pole appears cracked at TV and telephone connection. Needs to be looked at with bucket truck as soon as possible. | KY-5 & W Muddy Branch Rd, Kentucky 41102, USA | 2023-11-16
2020 | 2020-08-19 | Ashland | 77506091 |  | 38830043000177 |  | 3000303-BELLEFONT / BELLEFONT | Service Work | OH | secondary |  |  | Foreign | NO | Resag secondary. Secondary is low and touching telephone cable. | 2037 W Hearthstone Ln, Ashland, KY 41102, USA | 2020-08-21
2020 | 2020-08-19 | Ashland | 84301583 | TT 4473411 | 38830043000243 |  | 3000303-BELLEFONT / BELLEFONT | Service Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Arrester is damaged. | 2020 W Hearthstone Ct, Ashland, KY 41102, USA | 2023-01-25
2020 | 2020-08-19 | Ashland | 77520330 |  | 38830044A00602 |  | 3000303-BELLEFONT / BELLEFONT | Service Work | OH | UG conduit: damaged or separated |  |  | Foreign | NO | UG conduit damaged and secondary exposed at ground level. Placed yellow caution tape around damaged area. | KY-5 & Old Buckley Road, Kentucky 41102, USA | 2020-08-24
2020 | 2020-08-20 | Ashland |  |  | 38830044B00514 |  | 3000303-BELLEFONT / BELLEFONT | Forestry | OH |  |  | Field Checked by Dusty - dead tree has been cut back. | Foreign | NO | Dead tree hanging over primary and neutral, needs to be removed as soon as possible. Will have to look at this tree see what forestry can do. | 4401 Kiser Ln, Ashland, KY 41102, USA | 2021-11-11
2020 | 2020-08-24 | Ashland |  |  | 38830067C00224 |  | 3000303-BELLEFONT / BELLEFONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Deteriorated pole needs to be replaced. | 5401 Hill Ave, Ashland, KY 41102, USA
2020 | 2020-08-26 | Ashland | 78482787 | 1121728 | 38830043000128 |  | 3000303-BELLEFONT / BELLEFONT | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen to transformer pole. Cordle’s garage. | 1147 Rockhouse Rd, Flatwoods, KY 41139, USA | 2021-01-08
2020 | 2020-08-26 | Ashland |  |  | 38830251000116 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  |  |  | KPC | NO | Joe Moreland reported one span of neutral stolen at pole 251-116. Pole is five spans away from transformer pole 251-121. | Grahn Rd, Kentucky 41164, USA | 2023-01-24
2020 | 2020-08-27 | Ashland | 77982849 |  | 38830067C00050 |  | 3000303-BELLEFONT / BELLEFONT | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen to transformer pole. | 5319 Daniels Fork, Ashland, KY 41102, USA | 2020-10-16
2020 | 2020-08-31 | Ashland |  |  | 38830069A31048 |  | 3001202-HOWARDCOL / 29STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 2915 Evans St, Ashland, KY 41102, USA
2020 | 2020-08-31 | Ashland |  |  | 38830069A41664 | TRUE | 3001202-HOWARDCOL / 29STREET | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Customer stopped me and would like guy wire fixed. Trailer #6 | 3400 S 29th St, Ashland, KY 41102, USA
2020 | 2020-09-01 | Ashland |  |  | 38830069C24569 |  | 3001202-HOWARDCOL / 29STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole this year. | 2316 Linden Rd, Ashland, KY 41101, USA
2020 | 2020-09-02 | Ashland |  |  | 38830069C24548 | TRUE | 3001202-HOWARDCOL / 29STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | Peacock Rd, Ashland, KY 41102, USA
2020 | 2020-09-02 | Ashland |  |  | 38830069C24669 |  | 3001202-HOWARDCOL / 29STREET | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Circuit is on schedule to be worked in 2021. Vines will be addressed at that time. | 2549 E Euclid Ave, Ashland, KY 41102, USA | 2020-09-16
2020 | 2020-09-02 | Ashland |  |  | 38830069C24686 |  | 3001202-HOWARDCOL / 29STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole this year. Top of pole is cracking. Pole was set in 1941. | Pleasant Ave, Ashland, KY 41102, USA
2020 | 2020-09-03 | Ashland |  |  | 38830069C14048 |  | 3001202-HOWARDCOL / 29STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. Pole located at entrance to alley. | 3300 Pinehaven Dr, Ashland, KY 41101, USA | 2021-01-18
2020 | 2020-09-03 | Ashland |  |  | 38830069C45612 |  | 3001202-HOWARDCOL / 29STREET | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Bottom bolt to primary pole top pin is coming loose. | 3921 Ferguson Dr, Ashland, KY 41101, USA
2020 | 2020-09-08 | Ashland |  |  | 38830045A41512 |  | 3002103-10STREET / 12STREET | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | There was ZERO vegetation at this pole number nor anything around it that I could find. | 1328 Hilton Ct, Ashland, KY 41101, USA | 2020-10-07
2020 | 2020-09-08 | Ashland | 74534751 | DKY0107280 | 38830067D00205 | TRUE | 3001101-HOODSCREE / SUMMIT | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | Ground wire has come loose from bottom of arrester. | 5430 Hill Ave, Ashland, KY 41102, USA | 2022-01-21
2020 | 2020-09-08 | Ashland |  |  | 38830067D00283 |  | 3001101-HOODSCREE / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole this year. | 1004 W Alexander Dr, Ashland, KY 41102, USA
2020 | 2020-09-08 | Ashland |  |  | 38830091C00323 |  | 3001101-HOODSCREE / SUMMIT | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Vines will be cut/sprayed on next regular maintenance schedule. | 1216 W Greenhill Rd, Ashland, KY 41102, USA | 2020-09-16
2020 | 2020-09-09 | Ashland | 77982181 |  | 38830068B00972 |  | 3001101-HOODSCREE / SUMMIT | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to transformer pole. | Bybee Rd, Kentucky 41102, USA | 2020-10-16
2020 | 2020-09-09 | Ashland | 77982020 |  | 38830091C00129 |  | 3001101-HOODSCREE / SUMMIT | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen from transformer pole. | 6528 Hoenig Dr, Ashland, KY 41102, USA | 2020-10-16
2020 | 2020-09-09 | Ashland | 77981830 |  | 38830091C00142 |  | 3001101-HOODSCREE / SUMMIT | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to transformer pole. | 6500 Hoenig Dr, Ashland, KY 41102, USA | 2020-10-16
2020 | 2020-09-10 | Ashland | 77952950 |  | 38830068B00597 |  | 3001101-HOODSCREE / SUMMIT | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen from transformer pole. | 5118 | 2020-10-13
2020 | 2020-09-10 | Ashland | 77689092 | DKY0111104 | 38830068C00213 |  | 3001101-HOODSCREE / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is cracked/split at top of pole. This pole needs to be replaced as soon as possible. | Roberts Dr & Donta Rd, Kentucky 41102, USA | 2021-07-07
2020 | 2020-09-11 | Ashland |  |  | 38830044B00418 | TRUE | 3001101-HOODSCREE / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NO | Pole is set on side of creek bed. Soil around pole is being washed away. Needs to be checked out for proper depth. | 4034 Willow Dr, Ashland, KY 41102, USA
2020 | 2020-09-11 | Ashland |  |  | 38830068A00053 |  | 3001101-HOODSCREE / SUMMIT | Service Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Arrester is damaged and needs changed out. Porcelain cutout. | 1812 Donta Rd, Ashland, KY 41102, USA | 2023-01-25
2020 | 2020-09-15 | Ashland |  |  | 38830067B00035 | TRUE | 3001102-HOODSCREE / RURAL | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | All 4 xarm braces damaged. | 6929 St Rt 5, Ashland, KY
2020 | 2020-09-15 | Ashland | 74535078 | DKY0107284 | 38830067C00216 | TRUE | 3001102-HOODSCREE / RURAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 1915 W Ike Patton Dr, Ashland, KY 41102, USA | 2022-04-12
2020 | 2020-09-15 | Ashland | 77983469 |  | 38830067D00179 |  | 3001102-HOODSCREE / RURAL | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen to transformer pole. | 1720 W Miller Rd, Ashland, KY 41102, USA | 2020-10-16
2020 | 2020-09-16 | Ashland | 78615055 | DKY0112526 | 38830090000139 | TRUE | 3001102-HOODSCREE / RURAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is located at edge of creek. Soil is being washed away. Is pole set at proper depth? | Driller Ln, Kentucky 41121, USA | 2021-08-31
2020 | 2020-09-17 | Ashland |  |  | 38830066000017 |  | 3001102-HOODSCREE / RURAL | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | On regular maintenance schedule for 2021. Will be addressed at that time. <<<Vines growing up pole and around transformer. | 4882 Lost Lick Rd, Argillite, KY 41121, USA | 2021-06-30
2020 | 2020-09-17 | Ashland | 78579619 |  | 38830089000002 |  | 3001102-HOODSCREE / RURAL | Service Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Transformer lightning arrester is damaged. | 3101 | 2021-01-11
2020 | 2020-09-21 | Ashland | 78579401 |  | 38830066000109 |  | 3001102-HOODSCREE / RURAL | Service Work | UG | UG conduit: damaged or separated |  |  | Foreign | NO | UG conduit has separated. Need to be attached. I placed yellow caution tape around the area. | 579 Brookefield Farm Rd, Ashland, KY 41102, USA | 2021-01-11
2020 | 2020-09-28 | Ashland | 82806584 | DKY0117471 | 38830069A31220 |  | 3001203-HOWARDCOL / FLOYD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Service pole is deteriorated and needs replaced. | 2534 Elm St, Ashland, KY | 2022-07-09
2020 | 2020-09-29 | Ashland | 77973623 |  | 38830045B33019 |  | 3001203-HOWARDCOL / FLOYD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 2125 Moore St, Ashland, KY 41101, USA | 2020-10-15
2020 | 2020-09-29 | Ashland |  |  | 38830045D16158 |  | 3001203-HOWARDCOL / FLOYD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 2117 Woodland Ave, Ashland, KY 41101, USA
2020 | 2020-09-29 | Ashland | 77974773 |  | 38830045D26718 |  | 3001203-HOWARDCOL / FLOYD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 2148 Sellars St, Ashland, KY 41101, USA | 2020-10-15
2020 | 2020-09-29 | Ashland | 77974220 |  | 38830045D28346 |  | 3001203-HOWARDCOL / FLOYD | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen to UG primary cutout. | 2420 Moore St, Ashland, KY 41101, USA | 2020-10-15
2020 | 2020-09-29 | Ashland | 77975768 |  | 38830069A31026 |  | 3001203-HOWARDCOL / FLOYD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 2309 Crooks St, Ashland, KY 41101, USA | 2020-10-15
2020 | 2020-09-29 | Ashland | 77927933 |  | 38830069A31029 |  | 3001203-HOWARDCOL / FLOYD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 2341 Crooks St, Ashland, KY 41101, USA | 2020-10-09
2020 | 2020-09-29 | Ashland | 77964822 |  | 38830069C14162 |  | 3001203-HOWARDCOL / FLOYD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. In alley of South Ashland United Methodist Church parking lot. | Barton Ct, Ashland, KY 41101, USA | 2020-10-14
2020 | 2020-09-30 | Ashland |  |  | 38830045D16159 |  | 3001203-HOWARDCOL / FLOYD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 1130 Elmwood Ave, Ashland, KY 41101, USA | 2021-07-13
2020 | 2020-09-30 | Ashland |  |  | 38830045D26550 |  | 3001203-HOWARDCOL / FLOYD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 3227 Hackworth St, Ashland, KY 41101, USA | 2021-01-18
2020 | 2020-09-30 | Ashland |  |  | 38830045D26551 |  | 3001203-HOWARDCOL / FLOYD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 3201 Hackworth St, Ashland, KY 41101, USA | 2021-01-18
2020 | 2020-09-30 | Ashland | 78562911 |  | 38830045D26580 |  | 3001203-HOWARDCOL / FLOYD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 2941 Hampton St, Ashland, KY 41101, USA | 2021-01-08
2020 | 2020-09-30 | Ashland | 78563328 |  | 38830045D26582 |  | 3001203-HOWARDCOL / FLOYD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 3209 Hampton St, Ashland, KY 41101, USA | 2021-01-08
2020 | 2020-09-30 | Ashland | 78563662 |  | 38830045D26583 |  | 3001203-HOWARDCOL / FLOYD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 3231 Hampton St, Ashland, KY 41101, USA | 2021-01-08
2020 | 2020-09-30 | Ashland |  |  | 38830045D26728 |  | 3001203-HOWARDCOL / FLOYD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Pole located in alley. | 2957 Gibbs Ct, Ashland, KY 41101, USA
2020 | 2020-10-02 | Ashland |  |  | 38830068C00987 |  | 3001201-HOWARDCOL / 13STREET | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Double xarms needs to be replaced. One xarm is broken. | 3701 13th St, Ashland, KY 41102, USA
2020 | 2020-10-05 | Ashland |  |  | 38830045B22554 |  | 3001201-HOWARDCOL / 13STREET | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Will trim on regular maintenance schedule. | 1409 Maxwell St, Ashland, KY 41102, USA | 2020-10-06
2020 | 2020-10-05 | Ashland |  |  | 38830045B22608 |  | 3001201-HOWARDCOL / 13STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | 1621 Blackburn Ave, Ashland, KY 41101, USA
2020 | 2020-10-06 | Ashland | 77930051 |  | 38830045B22631 |  | 3001201-HOWARDCOL / 13STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 2616 Lincoln Ave, Ashland, KY 41102, USA | 2020-10-09
2020 | 2020-10-06 | Ashland | 77929677 |  | 38830045B22633 |  | 3001201-HOWARDCOL / 13STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 2620 Lincoln Ave, Ashland, KY 41102, USA | 2020-10-09
2020 | 2020-10-06 | Ashland |  |  | 38830045B22639 |  | 3001201-HOWARDCOL / 13STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Tree limbs close to primary, need to be removed. | 2432 Roosevelt Ave, Ashland, KY 41102, USA | 2021-03-22
2020 | 2020-10-06 | Ashland | 77928773 |  | 38830045B22681 |  | 3001201-HOWARDCOL / 13STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 2632 Lincoln Ave, Ashland, KY 41102, USA | 2020-10-09
2020 | 2020-10-07 | Ashland |  |  | 38830045A41705 |  | 3001201-HOWARDCOL / 13STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NEEDS ADDITIONAL CHECK | Top of pole is splitting - it needs to be looked at further. Pole passed sound test at base of pole. | 1218 Florence St, Ashland, KY 41101, USA
2020 | 2020-10-07 | Ashland | 77972779 |  | 38830045A41721 |  | 3001201-HOWARDCOL / 13STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground cut. | 1521 Sword St, Ashland, KY 41101, USA | 2020-10-15
2020 | 2020-10-07 | Ashland | 77973151 |  | 38830045A41723 |  | 3001201-HOWARDCOL / 13STREET | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 1509 Sword St, Ashland, KY 41101, USA | 2020-10-15
2020 | 2020-10-08 | Ashland |  |  | 38830045B43681 |  | 3001201-HOWARDCOL / 13STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Pole is leaning. Set in 1955. | Altamont Dr & Blackburn Ave, Ashland, KY 41101, USA
2020 | 2020-10-08 | Ashland | 77928421 |  | 38830069A20608 |  | 3001204-HOWARDCOL / SUMMIT | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 4082 Skyline Dr, Ashland, KY 41102, USA | 2020-10-09
2020 | 2020-10-09 | Ashland |  |  | 38830068D00880 | TRUE | 3001204-HOWARDCOL / SUMMIT | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Bolt to primary pole top pin is coming out. | 2865 Stephens Ct, Ashland, KY 41102, USA
2020 | 2020-10-09 | Ashland | 77953894 |  | 38830068D26159 |  | 3001204-HOWARDCOL / SUMMIT | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 1119 Armco Park, Ashland, KY 41102, USA | 2020-10-13
2020 | 2020-10-09 | Ashland | 77961957 |  | 38830069B28092 |  | 3001204-HOWARDCOL / SUMMIT | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen to 3 primary arresters. | Hogsten Dr, Ashland, KY 41102, USA | 2020-10-14
2020 | 2020-10-09 | Ashland | 77962785 |  | 38830069B33029 |  | 3001204-HOWARDCOL / SUMMIT | Service Work | OH |  |  | conductors: excessive splices, deteriorated conductors | Foreign | NO | Neutral laying on metal part of neutral clevis. Tie wire broken. | 3460 Lowman Dr, Ashland, KY 41102, USA | 2020-10-14
2020 | 2020-10-19 | Ashland |  |  | 38830093A00012 |  | 3001204-HOWARDCOL / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Unable to tell if pole is cracked. Needs to be further checked out. | Greenfield Rd & Boy Scout Rd, Ashland, KY 41102, USA | 2022-04-21
2020 | 2020-10-20 | Ashland |  |  | 38830092A00061 |  | 3001204-HOWARDCOL / SUMMIT | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Will trim limbs on regular maintenance cycle. Clearance here is minimal due to City of Ashland Park folks not wanting trees to be removed. This results in continual close limb/power line interactions. | Armco Park, 1119 Armco Park Dr, Ashland, KY 41102, USA | 2020-10-29
2020 | 2020-10-22 | Ashland | 78564295 |  | 38830188C26052 |  | 3008701-CANNONSBU / CANNONSBU | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to 3 primary cutouts. Pole located in front of Cannonsburg sub-station. | Ponderosa Dr, Kentucky 41129, USA | 2021-01-08
2020 | 2020-10-22 | Ashland |  |  | 38830188D00068 | TRUE | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Service drop laying on ground. Service drop and transformer is de-energized, transformer cutout is open. Notified DDC to have service drop removed. | Cannonsburg Rd, Kentucky, USA | 2023-01-30
2020 | 2020-10-22 | Ashland | 78564295 |  | 38830188D00465 |  | 3008701-CANNONSBU / CANNONSBU | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to transformer pole. | Bear Creek Rd, Catlettsburg, KY 41129, USA | 2021-01-08
2020 | 2020-10-23 | Ashland | 84434320 | DKY0119668 | 38830188A00027 | TRUE | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Xarm is splitting. “C” phase primary insulator is leaning. | Bear Creek Rd, Kentucky 41129, USA | 2023-06-30
2020 | 2020-10-23 | Ashland | 78632015 |  | 38830212000049 |  | 3008701-CANNONSBU / CANNONSBU | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Broken pole ground to transformer. | 19124 Bear Creek Rd, Catlettsburg, KY 41129, USA | 2021-01-19
2020 | 2020-10-26 | Ashland |  |  | 38830164A00306 | TRUE | 3008701-CANNONSBU / CANNONSBU | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | One of the arresters to the 3 phase bank is damaged. | 1500 N Big Run Rd, Ashland, KY 41102, USA
2020 | 2020-10-26 | Ashland |  |  | 38830188D00290 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | One span of neutral needs to be resag at pole 188D290. Neutral is 11 feet 8 inches from ground. Primary is at the proper height. Customer would like to be notified first (606-571-2799). Bad dog on premise. /// Neutral height between poles 188D290 and 188D291 is 11 feet 8 inches. Neutral needs to be resag. Primary is at correct height. | 17200 Bear Creek Rd, Catlettsburg, KY 41129, USA | 2022-09-27
2020 | 2020-10-30 | Ashland | TT# 4606091 wr# 78633464 |  | 38830262000263 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Service Work | OH | service |  |  | KPC | NO | I found secondary and meter box laying on ground. Secondary is energized. I called DDC for a trouble ticket order. | 8860 Harmon Ln, Catlettsburg, KY 41129, USA | 2021-01-19
2020 | 2020-11-02 | Ashland | 78632401 |  | 38830262C10320 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen from pole. |  | 2021-01-19
2020 | 2020-11-02 | Ashland | 78643690 |  | 38830287B09001 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | Faulkner Rd, Kentucky 41129, USA | 2021-01-20
2020 | 2020-11-03 | Ashland |  |  | 38830263B00012 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole is splitting and causing primary pole top pin to lean towards xarm. Pole passed sound test. | 29025 Mayo Trail Rd, Catlettsburg, KY 41129, USA | 2022-04-07
2020 | 2020-11-03 | Ashland | 78632401 |  | 38830263B00042 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 29019 Mayo Trail Rd, Catlettsburg, KY 41129, USA | 2021-01-19
2020 | 2020-11-03 | Ashland | 78632401 |  | 38830263B09017 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Transformer pole ground stolen. | 29019 Mayo Trail Rd, Catlettsburg, KY 41129, USA | 2021-01-19
2020 | 2020-11-03 | Ashland | 78644744 |  | 38830286000096 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 28236 Cardinal Ln, Catlettsburg, KY 41129, USA | 2021-01-20
2020 | 2020-11-03 | Ashland | 78644772 |  | 38830286000108 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 7936 Linda Cir, Catlettsburg, KY 41129, USA | 2021-01-20
2020 | 2020-11-03 | Ashland | 78643741 |  | 38830286000215 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 8908 Linda Dr, Catlettsburg, KY 41129, USA | 2021-01-20
2020 | 2020-11-04 | Ashland | 78566481 | DKY0112380 | 38830285000001 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Line Work | OH |  |  |  | KPC | NO | One span of neutral stolen. | Bear Crk Rd, Burnaugh, KY | 2021-01-26
2020 | 2020-11-05 | Ashland | 78566481 | DKY0112380 | 38830309000034 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Line Work | OH |  |  |  | KPC | NO | One span of neutral stolen (309-34 to 309-101). | 7228 Bear Crk Rd, Louisa, KY | 2021-01-26
2020 | 2020-11-06 | Ashland | 78676807 | DKY0112535 | 38830357000025 | TRUE | 3000202-BIG SANDY / BURNAUGH NORTH | Line Work | OH |  |  |  | KPC | NO | One span of neutral down going across creek and hillside (poles 357-25 to 357-24). | 3339 Blaine Creek Rd, Louisa, KY 41230, USA | 2022-08-18
2020 | 2020-11-09 | Ashland |  |  | 38830162C00211 |  | 3003702-COALTON / CANNONSBU | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Primary pole top pin is splitting away from top of pole. Primary insulator might be laying on Xarm ... hard to tell. Three spans from Coalton/Cannnonsburg Sub-station. Pole on hill. | S Big Run Rd, Kentucky, USA
2020 | 2020-11-09 | Ashland |  |  | 38830162C00271 |  | 3003702-COALTON / CANNONSBU | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarms showing deterioration. Pole in front of Hyland Pet Supply. | S Big Run Rd, Kentucky, USA
2020 | 2020-11-11 | Ashland |  |  | 38830140A20552 |  | 3003702-COALTON / CANNONSBU | Service Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Pole is setting in creek. Is pole at proper depth? | 1621 Cannonsburg Rd, Ashland, KY 41102, USA | 2021-01-08
2020 | 2020-11-12 | Ashland | 78564295 |  | 38830188C00392 |  | 3008702-CANNONSBU / ROUTE3 | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to OL. | 16336 Bramble Dr, Catlettsburg, KY 41129, USA | 2021-01-08
2020 | 2020-11-12 | Ashland | 78564295 |  | 38830188C00393 |  | 3008702-CANNONSBU / ROUTE3 | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | Ponderosa Dr & Bramble Dr, Kentucky 41129, USA | 2021-01-08
2020 | 2020-11-12 | Ashland | 78564295 |  | 38830188C00394 |  | 3008702-CANNONSBU / ROUTE3 | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 16336 Ponderosa Dr, Catlettsburg, KY 41129, USA | 2021-01-08
2020 | 2020-11-12 | Ashland | 78564295 |  | 38830188C00500 |  | 3008702-CANNONSBU / ROUTE3 | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 16731 Ponderosa Dr, Catlettsburg, KY 41129, USA | 2021-01-08
2020 | 2020-11-13 | Ashland |  |  | 38830164D00302 |  | 3008702-CANNONSBU / ROUTE3 | Line Work | UG | UG conduit: damaged or separated |  |  | KPC | NO | Service drop wires exposed at bottom of conduit. Soil around pole is washed away. Placed yellow caution tape around area. | 3708 KY-3, Catlettsburg, KY 41129, USA
2020 | 2020-11-17 | Ashland | 83401836 |  | 38830093B00353 |  | 3008702-CANNONSBU / ROUTE3 | Service Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Transformer arrester damaged. | 3330 Holly Ct, Catlettsburg, KY 41129, USA | 2022-10-12
2020 | 2020-11-17 | Ashland | 78600333 | DKY0112503 | 38830118D26545 |  | 3008702-CANNONSBU / ROUTE3 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Pole is deteriorated at base. Set in 1962. It has metal band attached at base. |  | 2021-08-16
2020 | 2020-11-18 | Ashland |  |  | 38830142A00113 |  | 3008702-CANNONSBU / ROUTE3 | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm is deteriorating. Pole is leaning but passed sound test. Pole set in 1939. | 8214
2020 | 2020-11-18 | Ashland |  |  | 38830142A00396 |  | 3008702-CANNONSBU / ROUTE3 | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Top xarm split and broken. | Bryan Rd & Robin Ln, Kentucky 41129, USA
2020 | 2020-11-20 | Ashland | 81481305 | DKY0115965 | 38830190000073 | TRUE | 2206403-SOUTH NEAL / WHITES CREEK RD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is leaning and bowed in middle. Pole failed sound test and has large metal band around base of pole. |  | 2022-02-23
2020 | 2020-12-02 | Ashland |  |  | 38830284000029 |  | 3003703-COALTON / TRACECREE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Xarm braces broken. Xarm looks good. | Bolts Fork Rd, Coalton, KY
2020 | 2020-12-04 | Ashland |  |  | 38830139A00301 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NEEDS ADDITIONAL CHECK | Pole is leaning from heavy phone cables attached to pole. Base of pole is cracked and splitting. Wood breaks away when hit with a hammer. I would replace pole but needs further looked at. | 12139 KY-5, Ashland, KY 41102, USA
2020 | 2020-12-07 | Ashland | 78349797 | DKY0112010 | 39831097B00174 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 30'6 1949 model secondary pole | Bowling Rd, Kentucky 41144, USA | 2020-12-16
2020 | 2020-12-07 | Ashland | 78349840 | DKY0112007 | 39831120000006 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 40'6 1949 model primary pole | Shackle Run Road | 2020-12-30
2020 | 2020-12-07 | Ashland | 78349898 | DKY0112005 | 39831121A00108 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 35'6 1949 model primary pole | Shackle Run Road | 2021-01-28
2020 | 2020-12-07 | Ashland | 78349995 | DKY0112006 | 39831121A00109 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 35'6 1949 model primary pole | Shackle Run | 2021-01-28
2020 | 2020-12-07 | Ashland | 78350036 | DKY0112020 | 39831121B00094 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 35'7 1949 model primary pole | Big Hollow Rd, Kentucky 41175, USA | 2020-12-30
2020 | 2020-12-07 | Ashland | 78350081 | DKY0112023 | 39831121B00096 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 35'7 1949 model primary pole | Big Hollow Rd, Kentucky 41175, USA | 2020-12-16
2020 | 2020-12-14 | Ashland | 78539856 | DKY0112372 | 38830116A00307 |  | 3117601-PRINCESS / MEADE STATION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is broken/split at telephone attachment. | 2315 Booth Quillen Rd, Ashland, KY 41102, USA | 2021-08-31
2020 | 2020-12-14 | Ashland | 77424956 | DKY0111646 | 38830118D26506A |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | this is push brace on pole #38830118D26506 - it's marked "A" pole - John Sode created pole number for this push brace - new pole should be tagged 38830118d26735 | Valley St & Neal St, Catlettsburg, KY 41129, USA | 2020-12-10
2020 | 2020-12-15 | Ashland |  |  | 38830092A00205 |  | 3117601-PRINCESS / MEADE STATION | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Double xarms deteriorating. 1023 Old Summit Rd. | Cr-1344C & Old Summit Rd, Kentucky 41102, USA
2020 | 2020-12-23 | Ashland |  |  | 38830501000198 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrester damaged - 34 KV 14163 Hwy 23, Louisa, KY Dog on premise. | Wexford Dr, Kentucky 41230, USA
2020 | 2020-12-28 | Ashland |  |  | 38830525000113 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | lightning arresters/insulators: damaged |  | KPC | NO | Four span of primary and neutral down from past storm trouble, from 525-110 to 525-109. 525-109 has been turned into a dead-end pole. Primary pole top pin damaged at 525-110. | Rhubens Branch Rd, Kentucky 41230, USA
2020 | 2020-12-28 | Ashland | 78539797 | DKY0112369 | 38830526000010 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | YES | Xarm is deteriorating. Pole should be replaced too - pole has metal brace at base of pole. | 1658 Torchlight Rd, Louisa, KY 41230, USA | 2022-02-21
2020 | 2020-12-28 | Ashland |  |  | 38830526000011 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Xarm is deteriorating and splitting at end of arm. Primary pin is leaning. | 1658 Torchlight Rd, Louisa, KY 41230, USA

## Ckt Defects Reported 2021 ASH
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2021 | 2021-01-07 | Ashland | 78660588 |  | 38830620B10332 |  | 3007904-BUSSEYVILLE / TORCHLITE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to reclosure pole. | 7761 Charley Rd, Louisa, KY | 2021-01-22
2021 | 2021-01-08 | Ashland | 78651940 |  | 38830645000244 |  | 3007904-BUSSEYVILLE / TORCHLITE | Service Work | OH | cutout: damaged |  |  | KPC | NO | Customer informed me that his OL hasn’t been working for a period of time. Fuse is blown to cutout. OL is the only service off of transformer. | 153 Mt Olive Rd, Louisa, KY | 2021-01-21
2021 | 2021-01-11 | Ashland |  |  | 38830645000032 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Transformer arrester damaged. | 12922 Hwy 1690, Louisa, KY 41230, USA
2021 | 2021-01-13 | Ashland | 78648756 | DKY0112586 | 38830597000037 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Burning at arrester/cutout attachment to pole from past trouble. Area appears cracked because weakness from past burning and tension of primary wires. | 178 Wooten Branch Rd, Louisa, KY 41230, USA | 2021-07-06
2021 | 2021-01-21 | Ashland | 78750736 | DKY0112736 | 38830453000078 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Burnt area on pole next to lightning arrester wire from past trouble. Arrester has been disconnected from cutout. | 205 Partridge Rd, Louisa, KY 41230, USA | 2021-10-11
2021 | 2021-01-29 | Ashland | 78737810 | DKY0112737 | 38830405000079 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole has metal bandaid at base of pole and showing deterioration at top of pole. | 20754 US-23, Louisa, KY 41230, USA | 2021-07-07
2021 | 2021-02-03 | Ashland |  |  | 38830254D00424 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NO | Soil has washed away around pole in creek bed. This needs to be fixed as soon as possible. | 64 Bobcat Rd, Grayson, KY | 2023-01-24
2021 | 2021-02-03 | Ashland | 84360014 | DKY0119518 | 38830278000019 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm deteriorating. | Menifee Rd, Grayson, KY | 2023-05-11
2021 | 2021-02-05 | Ashland | 84312116 | DKY0119861 | 38830279000014 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm is deteriorating. | 178 Fields Br, Louisa, KY
2021 | 2021-02-05 | Ashland | 75091413 | DKY0108443 | 38830302000047 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove transformer and OL. | Fields Br, Louisa, KY | 2021-09-08
2021 | 2021-02-10 | Ashland | 78750766 | DKY0113063 | 38830327B00025 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | crossarm/braces: deteriorated, not rotten |  | KPC | YES | Xarm deteriorating. Pole passed sound test but showing deterioration close to xarm. Pole set in 1941. Don’t need yardtrack because pole can be set from road. | 6639 Hwy 1496, Willard, KY | 2021-08-27
2021 | 2021-02-10 | Ashland | 84312027 | DKY0119850 | 38830327B00045 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | 6639 Hwy 1496, Willard, KY
2021 | 2021-03-08 | Ashland | 84304401 | DKY0119715 | 38830327B00072 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Pole has a large deep crack. Pole passed sound test. Pole set in 1945. | Hwy 1496, Willard, KY
2021 | 2021-03-08 | Ashland | 84312067 | DKY0119858 | 38830327B00073 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | Hwy 1496, Willard, KY
2021 | 2021-03-08 | Ashland | 84304822 | DKY0119719 | 38830327B00074 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | Hwy 1496, Willard, KY
2021 | 2021-03-08 | Ashland | 84304882 | DKY0119729 | 38830327B00075 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | Hwy 1496, Willard, KY
2021 | 2021-03-08 | Ashland |  |  | 38830327B00352 |  | 3001002-HITCHINS / WILLARD | Forestry | OH |  |  | Forestry does not clear service drops - will need to be field checked before closing this defect | KPC | NO | Tree limb laying on service drop. | 6101 St Hwy 1496, Willard, KY | 2021-12-21
2021 | 2021-03-08 | Ashland | 84311915 | DKY0119752 | 38830350000001 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | 5591 St Hwy 1496, Willard, KY
2021 | 2021-03-09 | Ashland | 80555707 | DKY0114802 | 38830326000061 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Soil has washed away around pole. Pole is in creek area. | 484 St Hwy 1122, Willard, KY | 2021-10-08
2021 | 2021-03-13 | Ashland |  |  | 38830447000019 |  | 3001002-HITCHINS / WILLARD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree limb hanging on primary and neutral. | Cherokee Gap Ridge Rd, Kentucky 41180, USA | 2023-01-24
2021 | 2021-03-16 | Ashland | 84304287 | DKY0119713 | 38830327B00078 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm deteriorating. | 5868 Hwy 1496, Willard, KY
2021 | 2021-03-22 | Ashland |  |  | 38830182B30281 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Transformer arrester damaged. Porcelain cut-out (7.2 KV) | 611 Prichard St, Grayson, KY 41143, USA
2021 | 2021-03-22 | Ashland | 83544536 |  | 38830182B43509 |  | 3116102-GRAYSON / DIXIEPARK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 404 N Hord St, Grayson, KY 41143, USA | 2022-10-07
2021 | 2021-03-22 | Ashland | TT # 4361801 |  | 38830182B43544 |  | 3116102-GRAYSON / DIXIEPARK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop (energized) has broken loose and laying on sidewalk. Called DDC for trouble ticket. | 210 Park St, Grayson, KY 41143, USA | 2021-03-22
2021 | 2021-03-23 | Ashland |  |  | 38830183B00238 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | Foreign | NO | Small oil leak at secondary bushing. | Mary Ann Ln, Grayson, KY 41143, USA
2021 | 2021-03-23 | Ashland | 76071582 | DKY0109117 | 38830206A31106 | TRUE | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Xarm is splitting. | 206 Robert and Mary St, Grayson, KY 41143, USA | 2022-03-02
2021 | 2021-03-25 | Ashland | 83544207 |  | 38830182D00168 |  | 3116102-GRAYSON / DIXIEPARK | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. | 813 Webster Ave, Grayson, KY 41143, USA | 2022-10-07
2021 | 2021-03-25 | Ashland |  |  | 38830182D06022 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Primary guy wire broken. Needs anchor. | 330 Riverbend Way, Grayson, KY 41143, USA
2021 | 2021-03-25 | Ashland |  |  | 38830183B00271 |  | 3116102-GRAYSON / DIXIEPARK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Found secondary rolled up on pole from ice storm work. Secondary is about 4 feet from ground and still energized. Called DDC for TT (#4372641). I waited on servicer to show up to make area safe. | 88 Karen Cir, Grayson, KY 41143, USA | 2021-03-25
2021 | 2021-04-05 | Ashland |  |  | 38830279000045 |  | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Pole is set next to creek bed. Soil is washed away next to pole. We need to keep an eye on this pole. | Hicks Rd, Hitchens, KY | 2021-05-18
2021 | 2021-04-08 | Ashland | 84286351 |  | 38830330000052 |  | 3001001-HITCHINS / DENTON | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to transformer pole. | Glenwood Branch Rd, Hitchens, KY | 2023-01-23
2021 | 2021-04-12 | Ashland | 84852822 | DKY0120394 | 38830255000160 | TRUE | 3001001-HITCHINS / DENTON | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Xarm is cracked and split. | Hwy 773, Hitchens, KY
2021 | 2021-04-14 | Ashland | 80727685 |  | 38830501000372 |  | 3007906-Busseyville / Walbridge | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to transformer pole. | KY-2565, Louisa, KY 41230, USA | 2021-10-15
2021 | 2021-04-14 | Ashland | 80727672 |  | 38830501000373 |  | 3007906-Busseyville / Walbridge | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to primary arresters (3 arresters). |  | 2021-10-14
2021 | 2021-04-14 | Ashland | 80727672 |  | 38830502000190 |  | 3007906-Busseyville / Walbridge | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to 3 primary arresters. | KY-2565, Kentucky 41230, USA | 2021-10-14
2021 | 2021-04-19 | Ashland | 80737842 |  | 38830478C20602 |  | 3007906-Busseyville / Walbridge | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to recloser. | Old Beech Rd, Louisa, KY 41230, USA | 2021-10-18
2021 | 2021-04-21 | Ashland | 79515745 | DKY0113645 | 38830599000004 |  | 3007906-Busseyville / Walbridge | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Soil washed away around pole in creek bed. Is this pole at the proper depth? | 4459 Walker Fork, Louisa, KY | 2021-07-22
2021 | 2021-04-26 | Ashland | TT# 4480771 |  | 38830502000088 |  | 3007906-Busseyville / Walbridge | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | 1 span of neutral laying on ground. Notified DDC to have repairs made. | Hwy 1690, Kentucky 41230, USA
2021 | 2021-04-26 | Ashland | 80782803 |  | 38830502000223 |  | 3007906-Busseyville / Walbridge | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop needs to be resag (5’). | 724 Bowe Hollow Rd, Louisa, KY 41230, USA | 2021-10-21
2021 | 2021-04-27 | Ashland |  |  | 38830550C10154 |  | 3007906-Busseyville / Walbridge | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Top of pine tree hanging overhead primary and appears to be touching. Before Emily Northup Church (3533 Hwy 1690). FORESTRY COMMENTS: Tree is now gone. | Hwy 1690, Louisa, KY | 2022-02-28
2021 | 2021-04-27 | Ashland | 80782841 |  | 38830574C20201 |  | 3007906-Busseyville / Walbridge | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Recloser pole ground stolen. | 266 Chapman St, LouisaKY | 2021-10-22
2021 | 2021-05-05 | Ashland | 86587010 | DKY0123074 | 38830501000184 | TRUE | 3007905-Busseyville / Mattie | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Is pole cracked? Pole passed sound test. Area circled in red needs to be checked out further by servicer. | 55 Swift Ln, Louisa, KY 41230, USA
2021 | 2021-05-07 | Ashland | 79515639 | DKY0113642 | 38830501000352 |  | 3007905-Busseyville / Mattie | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is cracked. Best location on Hwy 32. | 608 Swift Ln, Louisa, KY | 2021-07-20
2021 | 2021-05-10 | Ashland | 80737752 |  | 38830500000202 |  | 3007905-Busseyville / Mattie | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | Hwy 32, Louisa, KY | 2021-10-18
2021 | 2021-05-10 | Ashland | 80737727 |  | 38830500000204 |  | 3007905-Busseyville / Mattie | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen to transformer pole. | Hwy 32, Louisa, KY | 2021-10-18
2021 | 2021-05-12 | Ashland |  |  | 38830571000094 |  | 3007905-Busseyville / Mattie | Forestry | OH |  |  |  | KPC | NO | Tree overtop primary 2 to 3 feet. Need cleared out of the way. Go out Elk Lane off of Hwy 1760. | Elk Ln, Louisa, KY | 2021-05-20
2021 | 2021-06-01 | Ashland |  |  | 38830473000020 |  | 3007905-Busseyville / Mattie | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Soil has washed away around pole in creek. I was not able to sound test pole. Pole set in 1949. | 1893 Irish Creek Rd, Louisa, KY
2021 | 2021-06-08 | Ashland | 80782750 |  | 38830476000118 |  | 3007905-Busseyville / Mattie | Service Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Pole is splitting and is out of reach for a sound test. Pole passed sound test at base. Need servicer to check out. Pole is close to boat ramp. | Hwy 3215, Louisa, KY | 2021-10-21
2021 | 2021-06-10 | Ashland | 76343474 | DKY0109949 | 38830254C00149 | TRUE | 3001004-HITCHINS / E K ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole failed sound test. Deteriorated at base. | 119 Hilltop Dr, Grayson, KY 41143, USA | 2022-02-21
2021 | 2021-06-11 | Ashland | 83749704 |  | 38830255000050 |  | 3001004-HITCHINS / E K ROAD | Service Work | OH |  |  |  | Foreign | NO | One span of neutral stolen. Be aware there is a difficult customer off of this pole. Pole located at intersection of Crum Rd. & Shaelyn Acres Rd. | Crum Rd, Kentucky 41143, USA | 2022-11-02
2021 | 2021-06-16 | Ashland |  |  | 38830254B00569 |  | 3001004-HITCHINS / E K ROAD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree limb laying on neutral. Manual tree crew needed. FORESTRY COMMENTS: Circuit currently being worked on regular maintenance now. Will be addressed. | Edison Rd, Kentucky 41143, USA | 2022-04-07
2021 | 2021-06-21 | Ashland |  |  | 38830206B28025 | TRUE | 3001004-HITCHINS / E K ROAD | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole is leaning because ground is slipping. This needs to be checked out. Relocate pole? Located at South 7 Storage on Hwy 7. | KY-7, Grayson, KY, USA
2021 | 2021-06-29 | Ashland |  |  | 38830230000194 |  | 3001004-HITCHINS / E K ROAD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Both ends of xarms splitting. | Burton Ln, Grayson, KY 41143, USA
2021 | 2021-06-30 | Ashland |  |  | 38830230000197 |  | 3001004-HITCHINS / E K ROAD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | Cr-1112, Kentucky 41143, USA
2021 | 2021-06-30 | Ashland |  |  | 38830230000198 |  | 3001004-HITCHINS / E K ROAD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Double xarms are deteriorated. Will need customer’s permission to use yard track on premise. | 566 Bucksaw Jct, Grayson, KY 41143, USA
2021 | 2021-07-02 | Ashland |  |  | 38830230000297 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Primary has come loose from primary pole top pin. Hanging above pole. | Kelly Dr, Grayson, KY
2021 | 2021-07-07 | Ashland | 79409597 | DKY0113407 | 38830208000027 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | This looks like a temporary fix from ice storm in February. | Fighting Fork Rd, Kentucky, USA | 2022-05-12
2021 | 2021-07-07 | Ashland | TT# 4865091 |  | 38830208000061 |  | 3001003-HITCHINS / GRAYSON | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Found energized service drop hanging down pole. Notified Ashland DDC. | 4235 Cr-1030, Grayson, KY 41143, USA | 2021-07-07
2021 | 2021-07-12 | Ashland |  |  | 38830206C02263 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Base of pole is rotten. Replace pole. | 232 Poplar Heights Dr, Grayson, KY 41143, USA
2021 | 2021-07-12 | Ashland |  |  | 38830206C02445 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at base. Replace pole. Trimble Grayson lodge | US-60, Grayson, KY, USA
2021 | 2021-07-12 | Ashland | 83084882 | DKY0117691 | 38830207A00122 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole is splitting at primary pin and Xarm attachment. | 397 Damron Branch Rd, Grayson, KY 41143, USA
2021 | 2021-07-12 | Ashland |  |  | 38830207A00136 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten at base. Need replaced. | 1096 Charles St, Grayson, KY 41143, USA
2021 | 2021-07-12 | Ashland |  |  | 38830207A00142 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at base. Need replaced. | 1112 Charles St, Grayson, KY 41143, USA
2021 | 2021-07-12 | Ashland |  |  | 38830230000071 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Xarm is splitting at end of arm. Bad dog on premise. | 1569
2021 | 2021-07-14 | Ashland |  |  | 38830183D00195 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at base. Need replaced. | 407 Damron Mayo Rd, Grayson, KY 41143, USA
2021 | 2021-07-15 | Ashland | 82839366 | DKY0117500 | 38830183D00034 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NEEDS ADDITIONAL CHECK | Pole is in creek bed and soil has washed away from around it. Is this pole at the proper depth? Pole set in 1941. | 434 Tark Hill Rd, Grayson, KY 41143, USA | 2023-12-04
2021 | 2021-07-22 | Ashland |  |  | 38830182B22621 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NEEDS ADDITIONAL CHECK | Pole is leaning because telephone and cable tv pressing on pole. A broken pole is next to it that is causing a problem too. | 260 Cardinal Dr, Grayson, KY 41143, USA
2021 | 2021-07-22 | Ashland |  |  | 38830206A10114 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at base. Failed sound test. Pole is next to a fire hydrant. | Lynnwood Dr & Maple St, Grayson, KY 41143, USA
2021 | 2021-07-23 | Ashland | 83544932 |  | 38830181D00177 |  | 3116101-GRAYSON / LANSDOWNE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground broken. Trailer park on Kitty Lane. | Paradise Hill Rd, Grayson, KY 41143, USA | 2022-10-07
2021 | 2021-07-23 | Ashland |  |  | 38830206A31169 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NO | There has been burning at top of pole located at cutout/arrester t-bracket area. Porcelain cutout & arrester (7200KV) needs to be changed out. | 200 Johnson St, Grayson, KY 41143, USA
2021 | 2021-07-28 | Ashland | 82036870 | DKY0116684 | 38830180000053 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NEEDS ADDITIONAL CHECK | Two spans of neutral down at pole 180-56 to 180-58. Pole 38830180000057 is damaged and needs replaced. This section of circuit is isolated at pole 180-53. This is from the ice storm this year. | 1623 Stan Br, Grayson, KY | 2022-03-29
2021 | 2021-07-29 | Ashland | 82601358 |  | 38830204000148 |  | 3116101-GRAYSON / LANSDOWNE | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Service drop has come loose from house-knob. Service drop goes to garage. | 391 Smith Branch Rd, Olive Hill, KY 41164, USA | 2022-06-15
2021 | 2021-07-29 | Ashland |  |  | 38830205000047 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NEEDS ADDITIONAL CHECK | Remove inactive transformer and hardware. Pole appears cracked at transformer connection. It needs further looked at. Pole is located across from Carter County Fairgrounds. | US-60, Grayson, KY, USA
2021 | 2021-08-03 | Ashland | 76343684 | DKY0110041 | 38830183B00138 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Primary & neutral need to be resag. Primary is 14 feet from ground and neutral is 11 feet. Poles passed sound test. Would need customers permission to drive on their property. | 1630 E Midland Trail, Grayson, KY 41143, USA | 2021-12-17
2021 | 2021-08-03 | Ashland |  |  | 38830206A31170 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Primary & neutral is close to customer’s corner of house. Needs further looked at. Pole passed sound test. | 202 Johnson St, Grayson, KY 41143, USA | 2023-02-27
2021 | 2021-08-03 | Ashland | 74393620 | DKY0107008 | 38830270B02014 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH | transformers: leaking, damaged, unused near waterway/drainage OR school property |  |  | KPC | NO | Remove inactive transformer. | Buckeye Ln, Hayward, KY | 2022-03-11
2021 | 2021-08-04 | Ashland | 83543958 |  | 38830206C02440 |  | 3116102-GRAYSON / DIXIEPARK | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | There is to much tension on service drop going to customer’s newly installed weather-head. The telephone cable connected to the pole is causing the pole to lean and adding tension to customer’s service drop. Telephone company needs to reposition or add another guy wire to take tension off of customer’s service drop. If not taken care of this will cause damage to newly installed meter installation. | 398 Krestview Dr, Grayson, KY 41143, USA | 2022-10-07
2021 | 2021-08-05 | Ashland | 74393600 | DKY0107083 | 38830294000036 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Primary guy wire broken. Anchor is here. | 2336 Austin Rd, Hayward, KY | 2022-10-06
2021 | 2021-08-05 | Ashland | 80698302 | DKY0115230 | 38830317000007 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , crossarm/braces: broken/split |  |  | KPC | YES | Xarm is splitting. Pole has metal band at base of pole. Set in 1949. Pole should be replaced. | Brinegar Rd, Hayward, KY | 2022-02-24
2021 | 2021-08-06 | Ashland |  |  | 38830246000055 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | There are large holes at top of pole next to pole top pin. Pole set in 1948. Open wire secondary coming off pole is low going across field. Pole top pin is leaning because of holes. | Douglas Hollow, Kentucky 41164, USA
2021 | 2021-08-06 | Ashland | 74393722 | DKY0107117 | 38830269C00157 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole failed sound test. Rotten at base. | 451 Blue Hall Rd, Olive Hill, KY 41164, USA | 2022-04-12
2021 | 2021-08-16 | Ashland | 80409091 | DKY0114562 | 38830237000107 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole is rotten. I was not at this location, I entered this for line dept. | 18715 Brooks Dr, Catlettsburg, KY 41129, USA | 2021-10-12
2021 | 2021-08-19 | Ashland | 74393670 | DKY0107065 | 38830268A00070 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive transformer. | Little Perry Rd, Kentucky 40351, USA | 2022-03-02
2021 | 2021-08-23 | Ashland |  |  | 38830196000032 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Resag neutral (11 feet). Resag primary (16 feet). | 1450 Dry Branch Rd, Olive Hill, KY
2021 | 2021-08-25 | Ashland | 79810102 | DKY0113865 | 38830270B00169 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace rotten pole. Pole is across street from Hayward Substation. | 6890 KY-174, Olive Hill, KY 41164, USA | 2023-05-09
2021 | 2021-08-25 | Ashland |  |  | 38830270D00182 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | YES | Replace rotten pole and remove inactive transformer & hardware. Pole is in field and truck accessible. | 547 Lost Hills Rd, Olive Hill, KY 41164, USA
2021 | 2021-08-25 | Ashland | 74393624 | DKY0107019 | 38830270D00199 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Remove inactive transformer. Located on Goodan Ridge Rd. | Olive Hill, KY 41164, USA | 2022-04-22
2021 | 2021-08-25 | Ashland |  |  | 38830270D00235 |  | 3000802-HAYWARD / LAWTON | Line Work | OH |  |  |  | KPC | NEEDS ADDITIONAL CHECK | Customer (Mr. Caudill) would like service pole and service drop removed to his barn. Meter has been removed. | 547 Lost Hills Rd, Olive Hill, KY 41164, USA
2021 | 2021-08-26 | Ashland | 74393624 | DKY0107019 | 38830270D00019 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm is deteriorating. | 5965 KY-174, Olive Hill, KY 41164, USA | 2022-04-22
2021 | 2021-08-26 | Ashland |  |  | 38830271000079 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. Located in field next to metal building. | KY-174, Olive Hill, KY, USA
2021 | 2021-08-26 | Ashland |  |  | 38830271000080 |  | 3000802-HAYWARD / LAWTON | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm deteriorating. Pole is located in field. | KY-174, Olive Hill, KY, USA
2021 | 2021-08-27 | Ashland | 85291502 | DKY0121036 | 38830271000073 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Double xarms deteriorating. | 4740 KY-174, Olive Hill, KY 41164, USA | 2023-12-06
2021 | 2021-08-27 | Ashland |  |  | 38830271000058 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. | Load Temple Rd, Kentucky 41164, USA
2021 | 2021-09-02 | Ashland |  |  | 38830271C00016 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole is rotten. | 3786 KY-174, Olive Hill, KY 41164, USA
2021 | 2021-09-14 | Ashland | 80467552 | DKY0114730 | 38830117A00433 |  | 3008702-CANNONSBU / ROUTE3 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole (40 class 5) at 3401 Helton Ct. - road is off of Graydon Heights Dr. | 3401 Helton Ct, Catlettsburg, KY 41129, USA | 2021-09-24
2021 | 2021-09-15 | Ashland | 83482440 | DKY0118162 | 38830454B22517 |  | 3001401-LOUISA / CITY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | This pole needs further looked at. . . .Is this a new crack below xarm brace? | 706 Town Hill Rd, Louisa, KY 41230, USA | 2022-11-04
2021 | 2021-09-16 | Ashland |  |  | 38830454A41508 |  | 3001401-LOUISA / CITY | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Double xarms splitting. | 114 Public Way, Louisa, KY 41230, USA
2021 | 2021-09-16 | Ashland |  |  | 38830454A41514 |  | 3001401-LOUISA / CITY | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm deteriorating. | 924 Adams St, Louisa, KY 41230, USA
2021 | 2021-09-16 | Ashland |  |  | 38830454A41535 |  | 3001401-LOUISA / CITY | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm is deteriorating. Be aware that pole next to it (38830454A41746) double xarm has a temporary repair next to t-bracket. | 325 N Clay St, Louisa, KY 41230, USA
2021 | 2021-09-16 | Ashland |  |  | 38830454A41570 |  | 3001401-LOUISA / CITY | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Lightning arrester is damaged. | 204 Berry St, Louisa, KY 41230, USA
2021 | 2021-09-20 | Ashland | 80737899 | BKY0000012 | 38830454D16014 |  | 3001402-LOUISA / HIGHBOTTOM | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole in front of old elementary school. | Powhatan St, Louisa, KY 41230, USA | 2021-10-18
2021 | 2021-09-20 | Ashland | 76118988 | DKY0109274 | 38830478C14031 | TRUE | 3001402-LOUISA / HIGHBOTTOM | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Cross RR tracks and pole is in field on left side of road. | Levisa St, Louisa, KY 41230, USA | 2022-02-10
2021 | 2021-09-21 | Ashland |  |  | 38830454D26531 |  | 3001402-LOUISA / HIGHBOTTOM | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | One span of secondary needs to be resag. Secondary is below and touchng telephone cable. | 137 Chapel Rd, Louisa, KY 41230, USA
2021 | 2021-09-30 | Ashland | 84286516 |  | 38830223000026 |  | 3103101-OLIVEHILL / GLOBE | Service Work | OH |  |  | other: customer owned attachment | KPC | NO | Secondary guy attachment has come loose from secondary at customer’s weather-head. | 944 Smith Run, Olive Hill, KY 41164, USA | 2023-01-23
2021 | 2021-09-30 | Ashland |  |  | 38830223000166 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Bad arrester and go ahead and change out porcelain cutout (12kV). | 163 Southpaw Ln, Olive Hill, KY 41164, USA
2021 | 2021-10-04 | Ashland |  |  | 38830197000027 |  | 3103101-OLIVEHILL / GLOBE | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree branches close and hanging over primary line. Can be removed by bucket truck. | 313 Woodrow Rd, Olive Hill, KY 41164, USA
2021 | 2021-10-05 | Ashland |  |  | 38830197000036 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Pole failed sound test. Pole has large cracks.
2021 | 2021-10-08 | Ashland | 81911387 | DKY0116574 | 38830045A10104 | TRUE | 3002107-10STREET / WEST CENTRAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten and needs replaced. Pole is set next to small garage roof. | 108 Hillcrest Ct, Ashland, KY 41101, USA | 2022-05-16
2021 | 2021-10-08 | Ashland |  |  | 38830045A31171 |  | 3002107-10STREET / WEST CENTRAL | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Heavy vines growing up pole and around 3 phase transformers. Transformers service Wendy’s across from Kroger’s. FORESTRY COMMENTS: Will be addressed on regular maintenance. | 711 12th St, Ashland, KY 41101, USA | 2022-04-07
2021 | 2021-10-08 | Ashland | 84285259 |  | 38830150000005 |  | 3103101-OLIVEHILL / GLOBE | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Pole ground stolen to transformer pole. |  | 2023-01-23
2021 | 2021-10-08 | Ashland | 80686768 | DKY0114970 | 38830182B43641 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pre-68 pole that is in bad shape. Pole needs changed out. (John Sodie) | Carol Malone Blvd, Kentucky 41143, USA | 2021-10-15
2021 | 2021-10-08 | Ashland | 80686812 | DKY0114974 | 38830182B43643 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pre-68 pole that is in bad shape. Pole needs to be changed out. (John Sodie) | Carol Malone Blvd, Kentucky 41143, USA | 2021-10-15
2021 | 2021-10-11 | Ashland | 83564608 |  | 38830044C45510 |  | 3002107-10STREET / WEST CENTRAL | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Small tree branch laying on primary loop. Branch is close to telephone cable. Tree branch needs removed. Tree next to pole needs to be trimmed. | County Rd & Iowa St, Westwood, KY 41102, USA | 2022-10-11
2021 | 2021-10-11 | Ashland | 83517476 | G0000110 | 38830044C47680 |  | 3002107-10STREET / WEST CENTRAL | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Recloser pole ground broken at base of pole. Needs repaired. | County Rd & Roberts Dr, Kentucky 41102, USA | 2022-10-11
2021 | 2021-10-12 | Ashland |  |  | 38830044D47599 |  | 3002107-10STREET / WEST CENTRAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | OL pole is rotten and needs replaced. | 3515 Morgan Ave, Ashland, KY 41102, USA
2021 | 2021-10-12 | Ashland |  |  | 38830250000099 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Double xarms deteriorating. Inactive transformer. | Corey Rd, Grahn, KY
2021 | 2021-10-12 | Ashland |  |  | 38830251000095 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | Grahn Rd, Grahn, KY
2021 | 2021-10-13 | Ashland | 82205791 | DKY0116859 | 38830226000016 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | guys/anchors: broken or missing | crossarm/braces: deteriorated, not rotten |  | KPC | YES | Double xarms deteriorating. Broken guy wire is not needed here. | 100 Grahn Rd, Olive Hill, KY 41164, USA | 2022-05-09
2021 | 2021-10-13 | Ashland |  |  | 38830227000026 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | Aden Rd, Kentucky, USA
2021 | 2021-10-13 | Ashland |  |  | 38830227000027 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm deteriorated. | Aden Rd, Kentucky, USA
2021 | 2021-10-13 | Ashland | 82600744 |  | 38830227000037 |  | 3000601-GRAHN / PLEASANTV | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | conductors: resag no clearance issue, damaged, could cause an outage | other: customer owned attachment | KPC | NO | Customer’s service mast and service drop attachment damaged. This has caused customer’s service drop to sag (6.5 feet from ground). Customer informed me its been like this since the ice storm. | 530 Dry Fork Rd, Olive Hill, KY 41164, USA | 2022-06-15
2021 | 2021-10-13 | Ashland | 85539987 | DKY0121509 | 38830251000069 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm deteriorating. | 532 Oats Hill Rd, Olive Hill, KY 41164, USA
2021 | 2021-10-13 | Ashland |  |  | 38830251000072 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | 446 Oats Hill Rd, Olive Hill, KY 41164, USA
2021 | 2021-10-13 | Ashland |  |  | 38830251000081 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm deteriorating. | 270 Church Ridge Rd, Olive Hill, KY
2021 | 2021-10-13 | Ashland |  |  | 38830251000135 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | 4496 Aden Rd, Olive Hill, KY 41164, USA
2021 | 2021-10-13 | Ashland |  |  | 38830275000002 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Xarm splitting. | Church Ridge Rd, Olive Hill, KY
2021 | 2021-10-14 | Ashland | 85306964 | DKY0121350 | 38830274000009 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm deteriorating. Transformer goes to a barn. | 550 Parker Rd, Olive Hill, KY 41164, USA | 2023-09-05
2021 | 2021-10-14 | Ashland | 80739181 | DKY0115036 | 38830454C24557 |  | 3001401-LOUISA / CITY | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Double xarms rotten and need replaced. | E Madison St, Louisa, KY 41230, USA | 2022-02-27
2021 | 2021-11-11 | Ashland |  |  | 38830426000042 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH |  |  |  | KPC | NO | 1 span of neutral stolen. | 3676 Cooksey Fork, Kentucky 41230, USA
2021 | 2021-11-11 | Ashland | Trouble Ticket 4076661 | 123456 | 38830450000018 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | 7655 Hwy 828, Louisa, KY - Customer’s service drop needs to be resag - it is 4 feet from the ground. Notified DDC to make out a TT. | Louisa, KY 41230, USA | 2023-01-23
2021 | 2021-11-19 | Ashland | 84281525 |  | 38830379000083 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen at 333 Little Cat Fork Rd. | Little Cat Fork Rd, Kentucky, USA | 2023-01-23

## Ckt Defects Reported 2022 ASH
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2022 | 2022-01-05 | Ashland |  |  | 39830901A20502 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Xarm braces broken and xarm leaning. Its been this way for 2 years. | Flat Hollow Rd, Kentucky 41174, USA
2022 | 2022-01-05 | Ashland | 74862582 | DKY0107733 | 39830901C24541 | TRUE | 3002002-South Shore / Distribution | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Brace pole is rotten and needs replaced. Single xarm (picture) looks like it is deteriorating. I believe it is in good shape at this time but bucket truck might want to take a closer look. | Ferry Ave & S Shore Dr, Kentucky 41175, USA | 2023-01-09
2022 | 2022-01-05 | Ashland |  |  | 39830901C24549 |  | 3002002-South Shore / Distribution | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Arrester is damaged needs replaced. Porcelain cut-out (12 KV). | S Shore Dr, South Shore, KY, USA
2022 | 2022-01-05 | Ashland |  |  | 39830901C35003 | TRUE | 3002002-South Shore / Distribution | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten. | 143 Ridge St, South Shore, KY 41175, USA
2022 | 2022-01-05 | Ashland |  |  | 39830901C45592 |  | 3002002-South Shore / Distribution | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten. | 5th Ave, South Shore, KY 41175, USA
2022 | 2022-01-05 | Ashland |  |  | 39830902B00425 |  | 3002001-South Shore / Siloam | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is rotten. Pole is next to St. Rt. 7 | Old Sunshine Rd, South Shore, KY 41175, USA | 2022-03-01
2022 | 2022-01-05 | Ashland |  |  | 39830924000005 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating.
2022 | 2022-01-05 | Ashland |  |  | 39830924000006 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Double xarms deteriorating. | 2914 Lower White Oak Rd, South Portsmouth, KY 41174, USA
2022 | 2022-01-05 | Ashland | 74862259 | DKY0107658 | 39830924000012 |  | 3002001-South Shore / Siloam | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace rotten pole. | Pennington Hollow, South Shore, KY | 2022-07-05
2022 | 2022-01-05 | Ashland |  |  | 39830925000016 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Double xarms deteriorating. | Lower White Oak Rd, Kentucky 41174, USA
2022 | 2022-01-05 | Ashland |  |  | 39830925000064 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Xarm deteriorating. | 1390 Lower White Oak Rd, South Portsmouth, KY 41174, USA
2022 | 2022-01-05 | Ashland |  |  | 39830925000065 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Xarm deteriorating. | 1475 Lower White Oak Rd, South Portsmouth, KY 41174, USA
2022 | 2022-01-05 | Ashland |  |  | 39830925000073 |  | 3002001-South Shore / Siloam | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Is pole cracked? Needs to be looked at closer with service truck. | Little White Oak Rd, Kentucky, USA
2022 | 2022-01-05 | Ashland | 82320353 | DKY0116993 | 39830925000076 | TRUE | 3002001-South Shore / Siloam | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NO | Soil washed away around pole. Pole is leaning. | Buck Hollow Rd, Kentucky 41174, USA | 2022-05-16
2022 | 2022-01-05 | Ashland |  |  | 39831000B00066 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten. Failed sound test. Pole next to customer’s fence.
2022 | 2022-01-06 | Ashland |  |  | 39831047000047 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten. Pole is leaning. | 3060 Rice Ln, Greenup, KY
2022 | 2022-01-06 | Ashland | 72901121 | DKY0104444 | 39831048C20228 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Non equipment pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2022 | 2022-01-06 | Ashland | 72901121 | DKY0104444 | 39831048C20229 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Non equipment pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2022 | 2022-01-06 | Ashland | 72901121 | DKY0104444 | 39831048C20230 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Non equipment pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2022 | 2022-01-07 | Ashland | 72837349 | DKY0104423 | 39831024B42059 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2022 | 2022-01-07 | Ashland | 72837349 | DKY0104423 | 39831024B42060 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2022 | 2022-01-07 | Ashland | 72837349 | DKY0104423 | 39831024B42061 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2022 | 2022-01-07 | Ashland | 72837349 | DKY0104423 | 39831024B42062 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2022 | 2022-01-07 | Ashland | 72901121 | DKY0104444 | 39831048C20226 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Pole ground stolen. | US-23, Greenup, KY, USA | 2022-03-22
2022 | 2022-01-07 | Ashland | 81402006 | DKY0115992 | 39831145B00030 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole - replace. (Bre McCoy) | Ek Rd, Kentucky 41143, USA | 2022-03-21
2022 | 2022-01-07 | Ashland | 81402006 | DKY0115992 | 39831145B00031 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole - replace. (Bre McCoy) | Ek Rd, Kentucky 41143, USA | 2022-03-21
2022 | 2022-01-11 | Ashland |  |  | 39831072000033 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NEEDS ADDITIONAL CHECK | Pole appears cracked at neutral connections. | 1415 Short Branch Rd, Greenup, KY 41144, USA
2022 | 2022-01-12 | Ashland | TT # 4339791 WR#81361933 |  | 39830999000039 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Found energized service drop laying on ground. Notified DDC to make out a TT. remark on WR on 01/12/2022 "abandoned trailer service. removed" Mike Phelps - - closing this entry on 07/01/22 - prb | Hall Rd, Kentucky 41144, USA | 2022-01-12
2022 | 2022-01-20 | Ashland |  |  | 38830045C24691 |  | 3002103-10STREET / 12STREET | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Dead tree needs to be removed. FORESTRY COMMENTS: This is a line clearance refusal customer. Tree far enough away that they can hire private company. No work planned. | 1734 Dysard Hill Dr, Ashland, KY 41101, USA | 2022-01-21
2022 | 2022-01-24 | Ashland |  |  | 38830045C24713 | TRUE | 3002104-10STREET / 10-3 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten and needs replaced. | 22nd St & Lexington Ave, Ashland, KY 41101, USA
2022 | 2022-01-24 | Ashland | TT# 4400981 WR#81441643 |  | 38830045C35045 |  | 3002105-10STREET / MIDTOWN | Service Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Xarm brace has come loose and laying transformer primary riser (metal end of brace). Noticed DDC to make out a TT. remark on WR on Jan 24, 2022 "Crossarm brace loose and laying on TR primary riser--truck accessible///repairs made///Complete BR" - closing this entry on Jul 1, 2022 - prb | 2100 Greenup Ave, Ashland, KY 41101, USA | 2022-01-24
2022 | 2022-01-25 | Ashland | 83567364 |  | 38830045C14415 |  | 3002105-10STREET / MIDTOWN | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Transformer pole ground stolen. Pole across from American Legion. | 20th St, Ashland, KY 41101, USA | 2022-10-11
2022 | 2022-01-28 | Ashland | 72850564 | DKY0104492 | 39831073B12149 | TRUE | 3110902-WURTLAND / GREENUP | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Top xarm splitting. Pole is next to Greenup Food Fair. | Walnut St, Greenup, KY 41144, USA | 2022-08-22
2022 | 2022-02-01 | Ashland |  |  | 39831121B00040 |  | 3110902-WURTLAND / GREENUP | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Pole is deteriorated halfway up pole. Metal band at base of pole. Pole was set in 1944 and I believe it should be changed out to a new pole. | 171 Hidden Hollow Rd, Greenup, KY 41144, USA
2022 | 2022-02-07 | Ashland | 81541222 | DKY0116046 | 38830352000048 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace pole - Bre McCoy | Hickory Log Hollow, Kentucky 41143, USA | 2022-03-10
2022 | 2022-02-07 | Ashland | 81542837 | DKY0116049 | 38830116A00553 |  | 3117601-PRINCESS / MEADE STATION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace pole- Bre McCoy | Green Valley Dr, Kentucky 41102, USA | 2022-03-30
2022 | 2022-02-07 | Ashland | 81541173 | DKY0116045 | 38830352000050 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole needs replaced- Bre McCoy | Hickory Log Hollow, Kentucky 41143, USA | 2022-03-09
2022 | 2022-02-07 | Ashland | 81542098 | DKY0116048 | 38830428000083 |  | 3000203-BIG SANDY/YATESVILLE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace pole - Bre McCoy | Rice Br Rd, Kentucky 41653, USA | 2022-04-01
2022 | 2022-02-16 | Ashland |  |  | 39831121C00211 |  | 3110903-WURTLAND / RT.503 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Pole appears cracked or splitting below TV & telephone area. Bucket truck needs to look at this area up closer. | 803 Uhlan Branch Rd, Greenup, KY 41144, USA
2022 | 2022-02-23 | Ashland | 81658723 | DKY0116205 | 38830180000057 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole. | Stan Branch, Kentucky 41143, USA | 2022-03-04
2022 | 2022-03-02 | Ashland |  |  | 39831099B10093 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | cutout: damaged |  |  | KPC | NO | “C” phase cutout is blown to capacitor. Road runs parallel to Riverside Blvd. next to RR tracks. Pole tag has 1099BR98 | Riverside Blvd, Worthington, KY, USA
2022 | 2022-03-03 | Ashland |  |  | 39831099D20074 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Xarm is splitting. Pole tag has B-R79-308
2022 | 2022-03-04 | Ashland | 82921014 | DKY0117856 | 39831099D16099 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is deteriorated and has metal band secured at base. Pole set in 1950 and is located next to baseball field. | Fisher Ave, Worthington, KY 41183, USA | 2022-09-13
2022 | 2022-03-07 | Ashland | 73914968 | DKY0106251 | 39831123A28133 | TRUE | 3000901-HIGHLAND / RUSSELL | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Xarm brace broken. |  | 2022-03-25
2022 | 2022-03-08 | Ashland | 83322346 | DKY0117970 | 39831099B33112 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace deteriorated pole. Metal band on base of pole. Intersection of Riverside Dr. & 3rd Ave. | 3rd St, Worthington, KY, USA | 2022-09-30
2022 | 2022-03-08 | Ashland |  |  | 39831123B00357 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten pole. | 2701 Cambridge Dr, Flatwoods, KY 41139, USA
2022 | 2022-03-14 | Ashland |  |  | 38830069C35105 | TRUE | 3008002-47TH STREET / 39TH STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten. Customer said pole sways when the wind blows. | 3913 Putnam St, Ashland, KY 41101, USA
2022 | 2022-03-17 | Ashland |  |  | 38830045D26597 |  | 3008002-47TH STREET / 39TH STREET | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Tree limbs are in primary area. FORESTRY COMMENTS: This is a line clearance refusal from a code red customer. No work planned. | 1614 Spring Park, Ashland, KY 41101, USA | 2022-03-17
2022 | 2022-03-17 | Ashland |  |  | 38830045D37096 |  | 3008002-47TH STREET / 39TH STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at base. In alley that runs behind Ageless Spa. | 2809 1/2 Lexington Ave, Ashland, KY 41101, USA
2022 | 2022-03-18 | Ashland | 81859536 | DKY0116439 | 38830280000147 | TRUE | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole (1965) - Brent Parsons | Hitchins, KY 41143, USA | 2022-04-14
2022 | 2022-03-23 | Ashland |  |  | 39831123C24590 |  | 3000902-HIGHLAND / FLATWOODS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at base. Large trailer in driveway will need to be moved in order to set pole. | 600 Cherokee Rd, Raceland, KY 41169, USA
2022 | 2022-03-23 | Ashland | 85859281 | DKY0121897 | 39831123D16133 | TRUE | 3000902-HIGHLAND / FLATWOODS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | crossarm/braces: deteriorated, not rotten |  | Foreign | YES | Pole is splitting at top of pole and midway up pole. Xarms are splitting. | 1806 Court St, Flatwoods, KY 41139, USA | 2023-09-21
2022 | 2022-03-28 | Ashland |  |  | 38830069D37078 |  | 3008001-47TH STREET / 49TH STREET | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | Foreign | NO | 1219 Gallaher Dr., Catlettsburg, KY - 1 strand of wire broken on primary. 1 span of neutral missing. | Ashland, KY, USA
2022 | 2022-03-31 | Ashland |  |  | 38830069D47529 |  | 3008001-47TH STREET / 49TH STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten. Top of pole has several woodpecker holes next to the primary pole top pin. 4710 Nottingham Ct., Ashland. | Nottingham Ct, Ashland, KY 41101, USA
2022 | 2022-03-31 | Ashland |  |  | 38830069D47531 |  | 3008001-47TH STREET / 49TH STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  | Forestry - DESCRIBE IN COMMENTS | Foreign | YES | Pole is rotten. | 4716 Nottingham Ct, Ashland, KY 41101, USA
2022 | 2022-04-04 | Ashland | 82022871 | DKY0116681 | 38830226000009 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is over 50 years old and needs replaced - John Sodie | Leadingham Loop, Kentucky 41164, USA | 2022-05-04
2022 | 2022-04-04 | Ashland | 82022756 | DKY0116674 | 38830226000014 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is over 50 years old and needs replaced - John Sodie | Leadingham Loop, Kentucky 41164, USA | 2022-05-05
2022 | 2022-04-04 | Ashland | 82020163 | DKY0116661 | 38830251000124 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is over 50 years old and needs replaced - John Sodie | 152 Clay Dump Rd, Olive Hill, KY 41164, USA | 2022-05-11
2022 | 2022-04-06 | Ashland |  |  | 38830069D28176 |  | 3008001-47TH STREET / 49TH STREET | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Tree branches close to primary line. FORESTRY COMMENTS: Limbs close to the primary isn't a defect. All limbs that are not a refusal get trimmed on scheduled maintenance. In the meantime, limbs get close. It's normal. | 4913 Southern Hills Dr, Ashland, KY 41102, USA | 2022-04-06
2022 | 2022-04-07 | Ashland |  |  | 38830070B12230 | TRUE | 3008001-47TH STREET / 49TH STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Base of pole is rotten. | Halbert St & Patton St, Ashland, KY 41101, USA
2022 | 2022-04-12 | Ashland | 82036231 | DKY0116673 | 38830180000049 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole - Pat Thovson | 1386 Stan Branch Rd, Grayson, KY 41143, USA | 2022-04-28
2022 | 2022-04-12 | Ashland | 82036870 | DKY0116684 | 38830180000053 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole - Pat Thovson | 1623 Stan Branch Rd, Grayson, KY 41143, USA | 2022-04-28
2022 | 2022-04-12 | Ashland | 82050425 | DKY0116815 | 38830181C00014 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole - Tom Huff | Grayson, KY 41143, USA | 2022-05-04
2022 | 2022-04-12 | Ashland | 82110850 | DKY0116776 | 38830206A31066 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole - Tom Huff | Park St, Grayson, KY 41143, USA | 2022-05-03
2022 | 2022-04-12 | Ashland | 82032549 | DKY0116667 | 38830222B00061 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole - Richard Blackshire | Olive Hill, KY 41164, USA | 2022-04-26
2022 | 2022-04-12 | Ashland | 82086673 | DKY0116755 | 38830255B10293 |  | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole - Tom Huff | Hitchins, KY 41143, USA | 2022-05-02
2022 | 2022-04-12 | Ashland | 82037662 | DKY0116682 | 38830268C00036 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace pole with 35’ class 5 pole. - Brent Parsons | Haldeman, KY 41179, USA | 2022-05-16
2022 | 2022-04-12 | Ashland | 81859536 | DKY0116439 | 38830280000147 |  | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace pole with 45’ class 4 - Brent Parsons | Hitchins, KY 41143, USA | 2022-04-14
2022 | 2022-04-12 | Ashland | 82034970 | DKY0116670 | 38830292C00043 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole- Pat Thovson | 615 Haldeman Rd, Morehead, KY 40351, USA | 2022-04-27
2022 | 2022-04-12 | Ashland | 82035746 | DKY0116671 | 38830293000064 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole - Pat Thovson | 875 Haldeman Rd, Morehead, KY 40351, USA | 2022-04-26
2022 | 2022-04-12 | Ashland |  |  | 39831147D31013 |  | 3116701-BELHAVEN / DIEDERICH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NEEDS ADDITIONAL CHECK | Top of pole is splitting beneath double xarms and guy attachment. Needs to be checked out further. | 1600 Bellefonte Rd, Flatwoods, KY 41139, USA
2022 | 2022-04-13 | Ashland | 82042488 | DKY0116685 | 38830269A00182 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole with 40’ class 4 pole. | 8710 E State Rd 60, Bartow, FL 33830, USA | 2022-05-17
2022 | 2022-04-13 | Ashland |  |  | 39831147D40451 |  | 3116701-BELHAVEN / DIEDERICH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is rotten at base. Pole is leaning. | Short White Oak Rd, Flatwoods, KY, USA
2022 | 2022-04-14 | Ashland | 82057789 | DKY0116708 | 38830453000125 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole - Richard Blackshire | Chapel Rd, Louisa, KY 41230, USA | 2022-05-10
2022 | 2022-04-14 | Ashland | 82058478 | DKY0116709 | 38830453000272 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole - Richard Blackshire | Chapel Rd, Louisa, KY 41230, USA | 2022-05-10
2022 | 2022-04-19 | Ashland | 82623347 | DKY0117290 | 38830180000021 | TRUE | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole. | 1243 Smith Branch Rd, Olive Hill, KY 41164, USA | 2022-09-14
2022 | 2022-04-19 | Ashland | 83953021 | DKY0118787 | 38830181B00082 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole. 2299 St. Hwy. 1947 | Grayson, KY 41143, USA | 2022-12-13
2022 | 2022-04-19 | Ashland | 82625880 | DKY0117294 | 38830182B22518 | TRUE | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole. | 105 W 3rd St, Grayson, KY 41143, USA | 2022-07-20
2022 | 2022-04-19 | Ashland | 82624616 | DKY0117292 | 38830182B22519 | TRUE | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole. | 105 W 3rd St, Grayson, KY 41143, USA | 2022-07-20
2022 | 2022-04-19 | Ashland | 83484267 | DKY0118165 | 38830182B22528 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole. | 409 W 2nd St, Grayson, KY 41143, USA | 2022-10-17
2022 | 2022-04-19 | Ashland | 82148000 | DKY0116823 | 38830182B43501 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole. | 104 College St, Grayson, KY 41143, USA | 2022-05-04
2022 | 2022-04-20 | Ashland | 82084837 | DKY0116745 | 38830245C00043 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole. Asset pole 1 Jan 1941 | 22120 W US. Hwy 60, Olive Hill, KY 41164, USA | 2022-05-11
2022 | 2022-04-21 | Ashland | 81982022 | DKY0116607 | 38830181C00020 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole. | 2049 KY-1947, Grayson, KY 41143, USA | 2022-05-19
2022 | 2022-04-21 | Ashland | 82104276 | DKY0116757 | 38830226000052 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace old pole. | Grahn Rd, Kentucky 41164, USA | 2022-05-05
2022 | 2022-04-21 | Ashland |  |  | 39831147C24623 |  | 3116702-BELHAVEN / INDIAN RUN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Replace deteriorated pole. Next to trailer park. | Reed St, Flatwoods, KY 41139, USA
2022 | 2022-04-21 | Ashland | 85539381 | DKY0121381 | 39831147C24633 | TRUE | 3116702-BELHAVEN / INDIAN RUN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Base of pole rotten. Pole next to apartment complex. | Velma Ln, Flatwoods, KY 41139, USA | 2023-07-19
2022 | 2022-04-25 | Ashland |  |  | 38830019A00086 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | Foreign | YES | Top of pole burnt | 710 Indian Run Rd, Flatwoods, KY 41139, USA
2022 | 2022-04-25 | Ashland |  |  | 38830019A00259 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | 2’ pole ground missing near base of pole | 422 Summer Hill Farm Rd, Flatwoods, KY 41139, USA | 2023-01-25
2022 | 2022-04-25 | Ashland |  |  | 38830019C00207 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole rotted out | 1160 Indian Run Rd, Flatwoods, KY 41139, USA
2022 | 2022-04-25 | Ashland | 123456 |  | 38831147D2test |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Test 1 base of pole is rotten.test test | 3200 Indian Run Rd, Flatwoods, KY 41139, USA | 2022-04-25
2022 | 2022-04-25 | Ashland |  |  | 39831147B00503 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotted at base | 1291 Reid St, Flatwoods, KY 41139, USA
2022 | 2022-04-25 | Ashland |  |  | 39831147D20303 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is split , replace xfmr with 15KVA | 189 Barker Ln, Flatwoods, KY 41139, USA
2022 | 2022-04-25 | Ashland |  |  | 39831147D22003 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree in primary | Indian Run Rd, Flatwoods, KY, USA
2022 | 2022-04-26 | Ashland |  |  | 38830019C00051 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole cracked at neutral | 1557 Indian Run Rd, Flatwoods, KY 41139, USA
2022 | 2022-04-26 | Ashland | 86107151 | DKY0122258 | 38830019C00247 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole washed out. Needs relocated | Indian Run Rd, Flatwoods, KY, USA | 2024-01-03
2022 | 2022-04-26 | Ashland | 82140813 | DKY0116808 | 38830247000026 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole 1 Jan 1941 | W US. Hwy 60, Kentucky 41164, USA | 2022-05-11
2022 | 2022-04-26 | Ashland | 82137275 | DKY0116800 | 38830247000063 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole 1 Jan 1941 | State Hwy 1626, Kentucky 41164, USA | 2022-05-05
2022 | 2022-04-26 | Ashland |  |  | 39831147C14099 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten pole 1947 | 1004 Williams St, Flatwoods, KY 41139, USA
2022 | 2022-04-27 | Ashland | 82140441 | DKY0116804 | 38830376000025 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole 1 Jan 1945 J Sode | Bells Trace Rd | 2022-05-09
2022 | 2022-04-27 | Ashland |  |  | 39831123D37119 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten at base | 1137 Crestwood Ct, Flatwoods, KY 41139, USA
2022 | 2022-04-27 | Ashland |  |  | 39831123D47589 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole cracked and rotten on top | 1606 Brenda Sue Dr, Flatwoods, KY 41139, USA
2022 | 2022-04-27 | Ashland |  |  | 39831123D47594 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole cracked in several spots | 1607 Brenda Sue Dr, Flatwoods, KY 41139, USA
2022 | 2022-04-27 | Ashland |  |  | 39831124B22503 | TRUE | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten at base 715 Highland Ave | Flatwoods, KY, USA
2022 | 2022-04-28 | Ashland | 82162393 | DKY0116826 | 38830019C00120 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Clearance issue across driveway | 308 Cherry Hl, Flatwoods, KY 41139, USA | 2022-05-17
2022 | 2022-04-28 | Ashland |  |  | 39831123C24556 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole rotted out; also relocate out of creek | 1710 Beth Ann Dr, Flatwoods, KY 41139, USA
2022 | 2022-04-28 | Ashland |  |  | 39831123D16070 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten at base | 1605 Walnut St, Flatwoods, KY 41139, USA
2022 | 2022-04-28 | Ashland | 84397846 | DKY0119593 | 39831123D47509 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | crossarm/braces: broken/split | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Crossarm split out | 1211 Maple St, Flatwoods, KY 41139, USA | 2023-09-14
2022 | 2022-05-10 | Ashland | 84397846 | DKY0119593 | 39831147C14070 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | crossarm/braces: broken/split | lightning arresters/insulators: damaged |  | Foreign | NO | Broken crossarm brace and blown arrester | 1600 W Collins St, Flatwoods, KY 41139, USA | 2023-09-14
2022 | 2022-05-10 | Ashland |  |  | 39831147C14074 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Vines engulfing bare open wire secondary and pole | 1501 W Collins St, Flatwoods, KY 41139, USA
2022 | 2022-05-10 | Ashland | 82445184 | DKY0117085 | 39831147C14076 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | guys/anchors: broken or missing | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Primary stub guy broken/need anchor | Fannin St, Flatwoods, KY 41139, USA | 2022-07-12
2022 | 2022-05-10 | Ashland |  |  | 39831147C14115 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Vines engulfing pole and xfmr | 1306 Clark St, Flatwoods, KY 41139, USA
2022 | 2022-05-10 | Ashland |  |  | 39831147C14122 |  | 3116703-BELHAVEN / ARGILLITE ROAD | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Broken guy/need anchor | 2503 Fannin St, Flatwoods, KY 41139, USA
2022 | 2022-05-11 | Ashland | 82444150 | DKY0117080 | 39830879B04663 |  | 3004301-Siloam / Siloam | Line Work | OH | crossarm/braces: broken/split | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Rotten crossarm/truck access but need pallets moved | Johnson Ln, south shore | 2022-09-21
2022 | 2022-05-12 | Ashland |  |  | 39830879D00273 |  | 3004301-Siloam / Siloam | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | Foreign | YES | Top of pole rotted out | 335 Siloam Ln, South Shore, KY 41175, USA
2022 | 2022-05-13 | Ashland |  |  | 39830903000058 |  | 3004301-Siloam / Siloam | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | Foreign | YES | Top of pole rotted out | 29 eighth st, south shore ky
2022 | 2022-05-18 | Ashland | 4907401 |  | 39831148A01013 |  | 3010603-RUSSELL / ASHLANDOI | Service Work | OH |  |  |  | Customer | NO | CT meter cabinet hanging off customer meter pole | 2000 Ashland Dr, Russell, KY 41169, USA | 2022-05-18
2022 | 2022-05-24 | Ashland | 82402879 | DKY0117078 | 39831124A20578 |  | 3000901-HIGHLAND / RUSSELL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Rotten pole | 100 Vernon st, Russell, KY 41169, USA | 2022-08-17
2022 | 2022-05-27 | Ashland | 86075745 | DKY0122228 | 38830223000167 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole | 3761 st rt 2078, Olive hill, ky
2022 | 2022-05-27 | Ashland |  |  | 39831148B10087 | TRUE | 3010601-RUSSELL / KENWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Base of pole rotted | 100 Blantel Dr, Russell, KY 41169, USA
2022 | 2022-05-27 | Ashland | 85440057 | DKY0121640 | 39831148B40363 | TRUE | 3010601-RUSSELL / KENWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Whole base of pole rotted out | 1020 Amherst Dr, Ashland, KY 41101, USA
2022 | 2022-05-31 | Ashland | 84397846 | DKY0119593 | 39831124000030 |  | 3010602-RUSSELL / BEARRUN | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Broken crossarm | US-23, Russell, KY, USA | 2023-09-14
2022 | 2022-05-31 | Ashland |  |  | 39831124B43520 |  | 3010602-RUSSELL / BEARRUN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Loose secondary guy | 327 kenwood dr, Russell, ky | 2023-01-30
2022 | 2022-05-31 | Ashland |  |  | 39831148C00069 |  | 3010602-RUSSELL / BEARRUN | Line Work | OH | guys/anchors: broken or missing | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Broken down guy | 1170 Riverview Rd, Russell, KY 41169, USA
2022 | 2022-06-09 | Ashland | 84337962 |  | 39831123C35013 |  | 3010602-RUSSELL / BEARRUN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Remove service drop. It is cut at pole already | 1416 Meade st, Russell, ky | 2023-01-31
2022 | 2022-06-09 | Ashland | 83624495 |  | 39831123C35018 |  | 3010602-RUSSELL / BEARRUN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | House knob pulled out of house; remove abandoned service | 322 Osborne rd, Russell, ky | 2022-10-18
2022 | 2022-06-09 | Ashland | 84397846 | DKY0119593 | 39831123C35090 |  | 3010602-RUSSELL / BEARRUN | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Splitcrossarm | Osbourne St, Russell, ky | 2023-09-14
2022 | 2022-06-09 | Ashland |  |  | 39831124A18005 |  | 3010602-RUSSELL / BEARRUN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | No guy marker on pri guy in yard | Kentucky, USA | 2022-06-09
2022 | 2022-06-09 | Ashland | 83566829 | DKY0118288 | 39831124A20560 |  | 3010602-RUSSELL / BEARRUN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole weakened at joint use attachment, need 50’3 | 523 US 23, Russell,ky | 2023-02-24
2022 | 2022-06-09 | Ashland | 4047611 |  | 39831124B33003 | TRUE | 3010602-RUSSELL / BEARRUN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Open energized mtr base | 439 railroad st, Russell, ky | 2022-06-09
2022 | 2022-06-09 | Ashland |  |  | 39831124B33003 | TRUE | 3010602-RUSSELL / BEARRUN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Blanked mtr base; need hot legs cut at pole | 437 Railroad St, Russell, Ky | 2022-06-09
2022 | 2022-06-09 | Ashland | 83615797 |  | 39831124B33003 |  | 3010602-RUSSELL / BEARRUN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Remove inactive service drop or old sign | 439 RailRoad St, Russell, ky | 2022-10-18
2022 | 2022-06-09 | Ashland |  |  | 39831124B33004 |  | 3010602-RUSSELL / BEARRUN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Blanked out mar base; need hot legs cut at pole | 419 Railroad St, Russell,ky | 2023-01-30
2022 | 2022-06-17 | Ashland | 82623347 | DKY0117290 | 38830180000021 | TRUE | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole. Need 40’4 and long reach digger | Smith Branch Rd, Kentucky, USA | 2022-09-14
2022 | 2022-06-17 | Ashland | 86062282 | DKY0122200 | 38830180000054 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole. Dated 1948 | Stan Branch, Kentucky 41143, USA | 2023-11-20
2022 | 2022-06-17 | Ashland | 82628012 | DKY0117296 | 38830180000055 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole. Dated 1948 | Stan Branch, Kentucky 41143, USA | 2022-07-19
2022 | 2022-06-17 | Ashland | 82627196 | DKY0117295 | 38830180000056 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole. Dated 1948 | Stan Branch, Kentucky 41143, USA | 2022-07-19
2022 | 2022-06-17 | Ashland | 82625880 | DKY0117294 | 38830182B22518 | TRUE | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Potter pole dated 1950. Need 35’5 | 206 W 3rd St, Grayson, KY 41143, USA | 2022-07-20
2022 | 2022-06-17 | Ashland | 82624616 | DKY0117292 | 38830182B22519 | TRUE | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole replace with 35’5 | W 3rd St, Grayson, KY 41143, USA | 2022-07-20
2022 | 2022-06-21 | Ashland |  |  | 38830020A31044 |  | 3000302-BELLEFONT / FLATWOODS | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole rotted out | 616 Amanda Furnace Dr, Ashland, KY 41101, USA
2022 | 2022-06-21 | Ashland | 84397846 | DKY0119593 | 38830020C35059 |  | 3000302-BELLEFONT / FLATWOODS | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Bad crossarm | US-23, Ashland, KY, USA | 2023-09-14
2022 | 2022-06-21 | Ashland | 84397846 | DKY0119593 | 38830020C35095 |  | 3000302-BELLEFONT / FLATWOODS | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Rotten/split crossarm | US-23, Ashland, KY, USA | 2023-09-14
2022 | 2022-06-21 | Ashland | 82728972 | DKY0117393 | 38830287A00109 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten at base. Need 35’5. Reported by Pat Thovson | Runyon rd, burnaugh, ky | 2022-07-14
2022 | 2022-06-22 | Ashland |  |  | 38830094A10065 |  | 3008003-47TH STREET / CATLETTSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy marker missing | 55th St, Catlettsburg, KY, USA | 2022-06-22
2022 | 2022-06-22 | Ashland |  |  | 38830094A10067 |  | 3008003-47TH STREET / CATLETTSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy marker missing | 485 golden oaks dr, Catlettsburg, ky | 2022-06-22
2022 | 2022-06-22 | Ashland | 83687651 | DKY0118448 | 38830094A10213 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Pole needs relocated about 5’ north | 55th St, Catlettsburg, KY, USA | 2022-11-16
2022 | 2022-06-22 | Ashland |  |  | 38830094A31108 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NEEDS ADDITIONAL CHECK | 2 clearance issues, need pole | 535 10th St, Catlettsburg, KY 41129, USA
2022 | 2022-06-22 | Ashland |  |  | 38830094A31114 | TRUE | 3008003-47TH STREET / CATLETTSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy protector | 412 11th St, Catlettsburg, KY 41129, USA | 2022-06-22
2022 | 2022-06-22 | Ashland | 83579031 |  | 38830094A31114 |  | 3008003-47TH STREET / CATLETTSB | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service drop contacting roof | 410 11th St, Catlettsburg, KY 41129, USA | 2022-10-12
2022 | 2022-06-22 | Ashland | 031938861 & 035962871 |  | 38830094A31145 |  | 3008003-47TH STREET / CATLETTSB | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | 2 low service drops, created OPS order for servicer | 630 10th St, Catlettsburg, KY 41129, USA | 2022-06-22
2022 | 2022-06-23 | Ashland | 83578996 |  | 38830094A31058 |  | 3008003-47TH STREET / CATLETTSB | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Point of attachment is off pole | 312 Wadkins St, Catlettsburg, KY 41129, USA | 2022-10-12
2022 | 2022-06-23 | Ashland |  |  | 38830094A31154 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Need lift pole. 9’3” service drop clearance across yard | 355 Grandview dr, Catlettsburg, ky
2022 | 2022-06-24 | Ashland |  |  | 38830094B00006 | TRUE | 3008003-47TH STREET / CATLETTSB | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Straighten pole; pulling over customer meter pole | KY-168, Catlettsburg, KY, USA
2022 | 2022-06-24 | Ashland |  | Not known | 38830094B00034 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage | conductors: excessive splices, deteriorated conductors | Foreign | NO | 2 broken strands on 6a primary | KY-168, Catlettsburg, KY, USA | 2022-06-27
2022 | 2022-06-24 | Ashland | 84455291 | DKY0119690 | 38830094B00082 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Split crossarm | SR 168, Catlettsburg, ky | 2023-09-01
2022 | 2022-06-24 | Ashland |  |  | 38830094B00101 |  | 3008003-47TH STREET / CATLETTSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | KY-168, Catlettsburg, KY, USA | 2022-06-24
2022 | 2022-06-27 | Ashland |  |  | 38830093D00164 |  | 3008003-47TH STREET / CATLETTSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy marker missing | Applewood Dr, Kentucky 41129, USA | 2022-06-27
2022 | 2022-06-27 | Ashland | 83324878 | DKY0117902 | 38830094B00009 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Appears to be cracked at ju attachment | 7616 KY-168, Catlettsburg, KY 41129, USA | 2022-09-19
2022 | 2022-06-27 | Ashland |  |  | 38830094B00129 |  | 3008003-47TH STREET / CATLETTSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy marker missing | 7625 state highway 168, Catlettsburg, ky | 2022-06-27
2022 | 2022-06-27 | Ashland | 83742806 | DKY0118519 | 38830118A00012 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten asset pole, need 45’4 | 7521 Twin Fork Dr, Catlettsburg, KY 41129, USA | 2022-12-13
2022 | 2022-06-27 | Ashland |  |  | 38830118A00017 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Anchor missing | Barbecue Rd, Catlettsburg,ky
2022 | 2022-06-27 | Ashland | 827018267 |  | 38830118A00222 |  | 3008003-47TH STREET / CATLETTSB | Service Work | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree limb on secondary over driveway | Barbeque Rd, Catlettsburg, KY 41129, USA | 2022-06-27
2022 | 2022-06-27 | Ashland | 83504701 |  | 38830118A00255 |  | 3008003-47TH STREET / CATLETTSB | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Hot legs not cut at pole; remove service drop | 7516 Twin Fork Rd, Catlettsburg, KY 41129, USA | 2022-10-03
2022 | 2022-06-28 | Ashland |  |  | 38830094D26686 |  | 3008003-47TH STREET / CATLETTSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | 25th St, Catlettsburg, KY 41129, USA | 2022-06-28
2022 | 2022-06-28 | Ashland |  |  | 38830118B00049 |  | 3008003-47TH STREET / CATLETTSB | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | Cannonsburg Rd, Catlettsburg, KY, USA | 2022-06-28
2022 | 2022-06-28 | Ashland |  |  | 38830118C16647 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH | joint use attachments: clearance issues |  |  | KPC | NO | Pri/neut needs resagged; also telephone needs bellied (no sag in it); 2’ pri to telephone, telephone above neut | Marushi Ln, Catlettsburg, KY 41129, USA
2022 | 2022-06-28 | Ashland | 032751376 |  | 38830118C24546 |  | 3008003-47TH STREET / CATLETTSB | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Blanked mtr base; still energized; remove drop | 3320 Springhaven Dr, Catlettsburg, KY 41129, USA | 2022-06-28
2022 | 2022-06-29 | Ashland | 83689344 | DKY0118451 | 38830118C14156 |  | 3008003-47TH STREET / CATLETTSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1958 asset pole; rotten at base | Lock Ave, Catlettsburg, ky | 2023-05-17
2022 | 2022-07-01 | Ashland |  |  | 38830020C45576 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | UG | UG conduit: damaged or separated |  |  | Foreign | NO | Exposed conductors at mtr base | 1312 Horn St, Westwood, KY 41101, USA
2022 | 2022-07-01 | Ashland |  |  | 38830020D37108 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy markert | Thompson Ln, Westwood, KY 41101, USA | 2022-07-01
2022 | 2022-07-01 | Ashland |  |  | 38830020D47547 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Guy marker missing | Bellefonte Rd, Westwood, KY, USA | 2022-07-01
2022 | 2022-07-01 | Ashland | 86353157 | DKY0122991 | 38830020D47554 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Broken crossarm braces | Bellefonte Rd, Westwood, KY, USA
2022 | 2022-07-01 | Ashland | 83566991 |  | 38830020D47658 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | Collins Ln, Westwood, KY, USA | 2022-10-11
2022 | 2022-07-01 | Ashland | 86353044 |  | 38830020D47717 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Pole leaning pulling secondary pole across road; pole ground twisted into J.U. attachment | W Central Ave, Ashland, KY 41101, USA
2022 | 2022-07-01 | Ashland | 86329625 (1 OF 2) |  | 38830021B12031 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Anchor missing | Stevens Ave, Ashland, KY 41101, USA
2022 | 2022-07-01 | Ashland |  |  | 38830021B22520 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy marker missing | Central Ave, Ashland, KY 41101, USA | 2022-07-01
2022 | 2022-07-01 | Ashland | 86329625 (2 OF 2) |  | 38830021B22527 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Secondary anchor missing | Evans Rd, Ashland, KY 41101, USA
2022 | 2022-07-05 | Ashland |  |  | 38830020D26586 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | Hoods creek pike, Ashland, ky | 2022-07-05
2022 | 2022-07-05 | Ashland | 83565865 |  | 38830020D47666 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH | service: unused or abandoned, blanked meter base |  | other: customer owned attachment | KPC | NO | House knob pulled out of house; abandoned service | Maggard st, Westwood, ky | 2022-10-11
2022 | 2022-07-06 | Ashland |  |  | 38830020B43514 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | 2626 Doyle st, Ashland, ky | 2022-07-06
2022 | 2022-07-06 | Ashland | 86353296 |  | 38830020D26542 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Missing anchor | 3rd st west, Ashland, ky
2022 | 2022-07-06 | Ashland |  |  | 38830020D26624 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | 10’6 to service drop; need secondary pole; also low over pool | 109 pine crest dr, Ashland,ky
2022 | 2022-07-06 | Ashland | 86353249 |  | 38830020D26625 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Anchor pulled out | 2336 3rd st west, Ashland. Ky
2022 | 2022-07-07 | Ashland |  |  | 38830044C14010 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | Main st w, Westwood, ky | 2022-07-07
2022 | 2022-07-07 | Ashland | 83565027 |  | 38830044C24637 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | W old Buckley rd, Westwood, ky | 2022-10-11
2022 | 2022-07-07 | Ashland | 83455202 | DKY0118102 | 38830044C35041 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset 1934 pole, need 40’4 | Prichard st, Westwood, ky | 2022-10-11
2022 | 2022-07-07 | Ashland |  |  | 38830044C35044 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Loose pole ground | Prichard st, Westwood, ky | 2022-07-07
2022 | 2022-07-07 | Ashland | 83517492 | DKY0118212 | 38830044C35045 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset 1958 pole DS101 need 45’4 | Prichard st., Westwood, ky | 2022-10-18
2022 | 2022-07-07 | Ashland |  |  | 38830044C35079 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | Foreign | NO | Loose pole ground | Prichard st, Westwood, ky | 2022-07-07
2022 | 2022-07-08 | Ashland |  |  | 38830044C24605 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Need secondary pole installed to get service drop off roof, Assigned to Ben Wilburn, sent email with details | 2745 Shawnee dr, Ashland, ky
2022 | 2022-07-08 | Ashland | 83564886 |  | 38830044C24645 |  | 3000301-BELLEFONT / WESTWOOD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | McCown rd, Ashland, ky | 2022-10-11
2022 | 2022-07-11 | Ashland |  |  | 38830020C14005 | TRUE | 3000303-BELLEFONT / BELLEFONT | Line Work | OH | cutout: damaged |  |  | Foreign | NEEDS ADDITIONAL CHECK | B phase bell insulator broken | Bellefonte Princess Rd, Bellefonte, ky
2022 | 2022-07-11 | Ashland |  |  | 38830020C14010 |  | 3000303-BELLEFONT / BELLEFONT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | Lycan rd, bellefonte, ky | 2022-07-11
2022 | 2022-07-11 | Ashland |  |  | 38830020D16008 |  | 3000303-BELLEFONT / BELLEFONT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | Oxcart rd, bellefonte, ky | 2022-07-11
2022 | 2022-07-18 | Ashland | 86353380 (2 OF 2) |  | 38830044B00254 |  | 3000303-BELLEFONT / BELLEFONT | Line Work | OH |  |  |  | Foreign | NO | Neutral down | Literal hill, Ashland,ky
2022 | 2022-07-18 | Ashland | 86353961 |  | 38830044B00614 |  | 3000303-BELLEFONT / BELLEFONT | Line Work | OH |  |  | other: customer owned attachment | Foreign | NEEDS ADDITIONAL CHECK | Customer built around Windstream pole; sent picture to CSR and engineering | 3450 emmit dr, Ashland, ky | 2024-01-10
2022 | 2022-07-19 | Ashland |  |  | 38830019D00009 |  | 3000303-BELLEFONT / BELLEFONT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy guard | Hwy 1458, Ashland, ky | 2022-07-19
2022 | 2022-07-19 | Ashland |  |  | 38830019D00266 |  | 3000303-BELLEFONT / BELLEFONT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy guard | W muddy ridge rd, Ashland, ky | 2022-07-19
2022 | 2022-07-19 | Ashland |  |  | 38830019D26035 |  | 3000303-BELLEFONT / BELLEFONT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy guard | Springfield ranch, Ashland, ky | 2022-07-19
2022 | 2022-07-19 | Ashland | 86353682 (2 OF 2) | DKY0122881 | 38830043000374 |  | 3000303-BELLEFONT / BELLEFONT | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Neutral needs resagged, below telephone mid span | Rivendell rd, Ashland, ky
2022 | 2022-07-21 | Ashland |  |  | 38830043000066 | TRUE | 3000303-BELLEFONT / BELLEFONT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole washed out, needs relocated | 427 muddy br, Ashland, ky
2022 | 2022-07-21 | Ashland | 86353682 (1 OF 2) | DKY0122881 | 38830043000289 |  | 3000303-BELLEFONT / BELLEFONT | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Missing anchor | Rockhouse rd, Ashland, ky
2022 | 2022-07-29 | Ashland | 82966648 | DKY0117619 | 38830021B22554 |  | BELLEFONTE - WESTWOOD / 0003-01 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole Rotten, needs replaced | 257 W. Central Ave, Ashland KY | 2022-09-07
2022 | 2022-08-11 | Ashland |  |  | 38830069A20503 |  | 3001202-HOWARDCOL / 29STREET | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | S 29th St, Ashland, KY 41102, USA | 2022-08-11
2022 | 2022-08-11 | Ashland | 83431153 | DKY0118066 | 38830069A31080 |  | 3001202-HOWARDCOL / 29STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1939 Asset pole. Replace w/40’5 | McDowell St, Ashland, KY 41102, USA | 2022-09-30
2022 | 2022-08-11 | Ashland | 83567891 |  | 38830069A31226 |  | 3001202-HOWARDCOL / 29STREET | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy guard | Joel St, Ashland, KY 41102, USA | 2022-10-11
2022 | 2022-08-11 | Ashland | 84455291 | DKY0119690 | 38830069A41553 |  | 3001202-HOWARDCOL / 29STREET | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Split crossarm | 3400 S 29th St, Ashland, KY 41102, USA | 2023-09-01
2022 | 2022-08-11 | Ashland |  |  | 38830069A41593 |  | 3001202-HOWARDCOL / 29STREET | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | YES | Service drop over pool. Need pole relocated | Christy St, Ashland, KY 41102, USA
2022 | 2022-08-11 | Ashland |  |  | 38830069A41596 |  | 3001202-HOWARDCOL / 29STREET | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Straighten pole | Poage Elementary School, Ashland,ky
2022 | 2022-08-11 | Ashland | 83429690 | DKY0118065 | 38830069A41643 |  | 3001202-HOWARDCOL / 29STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole rotted out | Lorraine st, Ashland, ky | 2022-10-20
2022 | 2022-08-11 | Ashland |  |  | 38830069A41664 | TRUE | 3001202-HOWARDCOL / 29STREET | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Missing dwn guy & anchor | S 29th St, Ashland, KY 41102, USA
2022 | 2022-08-11 | Ashland | 83304667 | DKY0117883 | 38830069A41694 |  | 3001202-HOWARDCOL / 29STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten at base. Need 30’6 | Lorraine St, Ashland, KY 41102, USA | 2022-09-27
2022 | 2022-08-16 | Ashland |  |  | 38830069C14135 |  | 3001202-HOWARDCOL / 29STREET | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  | other: customer owned attachment | Foreign | NO | Gutter laying on service drop; sent pic to Debbie Kahn to send customer letter | 2412 Monroe St, Ashland, ky | 2022-08-16
2022 | 2022-08-16 | Ashland |  |  | 38830069C24548 | TRUE | 3001202-HOWARDCOL / 29STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten at base | Peacock Rd, Ashland, KY 41102, USA
2022 | 2022-08-16 | Ashland | 4751321 |  | 38830069C24792 |  | 3001202-HOWARDCOL / 29STREET | Service Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | 4/2 secondary on ground energized; called in trouble ticket | Peacock Rd, Ashland, KY 41102, USA | 2022-08-16
2022 | 2022-08-16 | Ashland | 83145188 | DKY0118367 | 38830195000004 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1948 asset pole; assign to John Sode | Dry Branch Rd, Olive Hill, ky | 2022-11-10
2022 | 2022-08-19 | Ashland |  |  | 38830067D00007 |  | 3001101-HOODSCREE / SUMMIT | Line Work | UG | pole: rotten, washed out, broken/split, burned less than 50% remaining , UG conduit: damaged or separated |  |  | Foreign | NO | Secondary pedestal washed out, needs relocated | St Rt 5, Ashland, ky
2022 | 2022-08-19 | Ashland |  |  | 38830067D00239 |  | 3001101-HOODSCREE / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole in middle of creek, needsrelocated | 5416 state route 5, Ashland, ky
2022 | 2022-08-19 | Ashland | 83407073 | DKY0118034 | 38830068B00118 |  | 3001101-HOODSCREE / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1940 asset pole, 45’4 | Harris rd, summit, ky | 2022-10-05
2022 | 2022-08-19 | Ashland | 83407829 | DKY0118039 | 38830068B00646 |  | 3001101-HOODSCREE / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , joint use attachments: clearance issues |  |  | KPC | YES | 1965 asset pole; also J.U. 11’9 over edge of road; 45’4 will solve clearance issue | Bybee rd, Ashland, ky | 2022-10-18
2022 | 2022-08-19 | Ashland |  |  | 38830068B00732 |  | 3001101-HOODSCREE / SUMMIT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy marker missing | Dog Ridge, Ashland, ky | 2022-08-19
2022 | 2022-08-19 | Ashland | 83401619 | DKY0118023 | 38830068B00829 |  | 3001101-HOODSCREE / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1969 asset pole | Hicks Rd, Ashland, ky | 2022-10-04
2022 | 2022-08-22 | Ashland |  |  | 38830067D00455 |  | 3001101-HOODSCREE / SUMMIT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy guard in yard | Sunrise Ln, Ashland, ky | 2022-08-22
2022 | 2022-08-23 | Ashland |  |  | 38830044D26534 |  | 3001101-HOODSCREE / SUMMIT | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Clearance issue over deck, 9’ to service drop. Need secondary pole to reroute | 3806 hardeman dr, Ashland, ky
2022 | 2022-08-23 | Ashland |  |  | 38830044D40589 |  | 3001101-HOODSCREE / SUMMIT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | Hardeman dr, Ashland, ky | 2022-08-23
2022 | 2022-08-23 | Ashland |  |  | 38830044D40590 |  | 3001101-HOODSCREE / SUMMIT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | Hardeman dr, Ashland, ky | 2022-08-23
2022 | 2022-08-23 | Ashland |  |  | 38830068C00232 |  | 3001101-HOODSCREE / SUMMIT | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage | conductors: excessive splices, deteriorated conductors | KPC | NO | Broken neutral, one span | Rose hill school, Roberts dr, Ashland, ky
2022 | 2022-08-23 | Ashland |  |  | 38830068C00904 |  | 3001101-HOODSCREE / SUMMIT | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Blown arrester | 4533 Roberts Dr, Ashland, ky
2022 | 2022-08-24 | Ashland |  |  | 38830044B00418 | TRUE | 3001101-HOODSCREE / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is in danger of being washed out, pole needs relocated out of ditch | Willow Dr, Ashland, ky
2022 | 2022-08-24 | Ashland | 833250087 | DKY0117904 | 38830068A00257 |  | 3001204-HOWARDCOL / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1948 asset pole, need 45’4 | Pine st, Ashland, ky
2022 | 2022-08-24 | Ashland | 83358551 | DKY0117953 | 38830068A00465 |  | 3001101-HOODSCREE / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1958 asset pole, need 45’4, DS101 | 429 w nunley Ct, Ashland, ky | 2022-09-16
2022 | 2022-08-24 | Ashland | 85267859 | DKY0122226 | 38830068A00468 | TRUE | 3001101-HOODSCREE / SUMMIT | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Need 2 anchors | Willard Dr, Ashland, ky | 2023-11-16
2022 | 2022-08-24 | Ashland |  |  | 38830068A01062 |  | 3001101-HOODSCREE / SUMMIT | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing 2 guy markers | W vine st, Ashland, ky | 2022-08-24
2022 | 2022-08-24 | Ashland |  |  | 38830068A01331 | TRUE | 3001101-HOODSCREE / SUMMIT | Forestry | OH |  |  | Line is de-energized and will require grounds before forestry can remove tree. Contact when grounds are placed and tree can be addressed. | KPC | NO | Tree pinning down pri/neut mid span. Need tree removed; contact property owner prior to coming out | 638 stevens rd, Ashland, ky
2022 | 2022-08-24 | Ashland |  |  | 38830068A01331 | TRUE | 3001101-HOODSCREE / SUMMIT | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Tree pinning pri/neut to ground; need tree trimmers and pole straighted. Span cut in clear for now but customer said he is putting trailer back in in near future, call customer prior to working | 627 stevens rd, Ashland, ky
2022 | 2022-08-26 | Ashland |  |  | 38830067B00035 | TRUE | 3001102-HOODSCREE / RURAL | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Broken arm brace | 6917 state route 5, Ashland,ky
2022 | 2022-08-26 | Ashland |  |  | 38830067C00113 |  | 3001102-HOODSCREE / RURAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | Barnhart Dr, Ashland, ky | 2022-08-26
2022 | 2022-08-26 | Ashland |  |  | 38830067C00216 |  | 3001102-HOODSCREE / RURAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | W Ike Patton Dr, Ashland, ky | 2022-08-26
2022 | 2022-08-26 | Ashland |  |  | 38830067C00416 |  | 3001102-HOODSCREE / RURAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | W Tara Dr, Ashland, ky | 2022-08-26
2022 | 2022-08-26 | Ashland |  |  | 38830067D00220 |  | 3001102-HOODSCREE / RURAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | W ike Patton Dr, Ashland ky | 2022-08-26
2022 | 2022-08-26 | Ashland |  |  | 38830067D00322 |  | 3001102-HOODSCREE / RURAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Missing guy marker | W Miller rd, Ashland, ky | 2022-08-26
2022 | 2022-08-26 | Ashland |  |  | 38830091A00006 |  | 3001102-HOODSCREE / RURAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | State Route 5, Ashland, ky | 2022-08-26
2022 | 2022-08-26 | Ashland | 83556836 | DKY0118292 | 38830091A00021 |  | 3001102-HOODSCREE / RURAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1958 asset pole, need 45’4 | W little garner rd, Ashland, ky | 2022-10-19
2022 | 2022-08-26 | Ashland |  |  | 38830091A00025 |  | 3001102-HOODSCREE / RURAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1939 asset pole, maybe truck not sure if septic, need 45’4 | W little garner rd, Ashland, ky
2022 | 2022-08-26 | Ashland | 83493501 |  | 38830091A00028 |  | 3001102-HOODSCREE / RURAL | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Stolen pole ground, can’t reach it it fix it | W little garner rd, Ashland, ky | 2022-10-04
2022 | 2022-08-26 | Ashland |  |  | 38830091A00030 |  | 3001102-HOODSCREE / RURAL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | W little garner rd, Ashland, ky | 2022-08-26
2022 | 2022-08-26 | Ashland |  |  | 38830091A00160 |  | 3001102-HOODSCREE / RURAL | Line Work | OH | guys/anchors: broken or missing | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing anchor and guy on 3 phase pole | State Route 5, Ashland, ky
2022 | 2022-08-26 | Ashland | 83569451 | DKY0118306 | 38830091A00303 |  | 3001102-HOODSCREE / RURAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1969 asset secondary pole | W little garner rd, Ashland, ky | 2022-10-19
2022 | 2022-08-26 | Ashland | 83516517 | G0000110 | 38830091C00032 |  | 3001102-HOODSCREE / RURAL | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | KPC | NO | Stolen pole ground, can’t reach it to fix it | W little garner rd, Ashland, ky | 2022-10-21
2022 | 2022-08-30 | Ashland | 83463778 | DKY0118130 | 38830091C00208 |  | 3001101-HOODSCREE / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1962 asset pole, 40’4 ok | Lake Mary Carol Rd W, Kentucky 41102, USA | 2022-10-13
2022 | 2022-08-30 | Ashland | 83256471 | DKY0117819 | 38830292B00096 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Reported by Bre Howell | 365 Lafayette Dr, Morehead, KY 40351, USA | 2022-10-27
2022 | 2022-08-31 | Ashland | 85046190 | DKY0120693 | 38830090000004 |  | 3001102-HOODSCREE / RURAL | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Broken crossarm, phase suspended, in cornfield; sent notice to Luke McCoy | KY-5, Ashland, KY, USA | 2023-06-30
2022 | 2022-08-31 | Ashland | 86107545 | DKY0122260 | 38830090000109 |  | 3001102-HOODSCREE / RURAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1947 asset pole, DS101, can be moved to make more truck accessible | KY-5, Ashland, KY, USA | 2024-01-03
2022 | 2022-08-31 | Ashland | 83538096 | DKY0118249 | 38830091A00015 |  | 3001102-HOODSCREE / RURAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1972 asset pole, beef up pole , long spans | KY-5, Ashland, KY, USA | 2023-09-06
2022 | 2022-08-31 | Ashland |  |  | 38830091A00203 |  | 3001102-HOODSCREE / RURAL | Line Work | OH | guys/anchors: broken or missing |  |  | Foreign | NO | Missing anchor | KY-5, Ashland, KY, USA
2022 | 2022-09-01 | Ashland | 83564782 | DKY0118286 | 38830089000009 |  | 3001102-HOODSCREE / RURAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1945 asset pole, need long reach digger | Bush St, Ashland, KY 41101, USA | 2022-11-29
2022 | 2022-09-01 | Ashland | 83453528 | DKY0118098 | 38830090000069 |  | 3001102-HOODSCREE / RURAL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1945 asset pole, 40’4 ok | Lock Hollow Rd, Kentucky, USA | 2022-10-11
2022 | 2022-09-01 | Ashland |  |  | 38830113000043 |  | 3001102-HOODSCREE / RURAL | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole needs straightened | Sparks St, Ashland, KY 41101, USA
2022 | 2022-09-02 | Ashland |  |  | 38830069A10139 |  | 3001203-HOWARDCOL / FLOYD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole rotted out, stiff Hendrix angle pole | May St, Ashland, KY 41102, USA
2022 | 2022-09-02 | Ashland |  |  | 38830069A10295 |  | 3001203-HOWARDCOL / FLOYD | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Split croossarm | 3205 Old 13th St, Ashland, KY 41102, USA
2022 | 2022-09-02 | Ashland | 83454416 | DKY0118100 | 38830069A10322 |  | 3001203-HOWARDCOL / FLOYD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Broken pole, 40’4 | Beech St, Ashland, KY 41102, USA
2022 | 2022-09-23 | Ashland | 83443371 | DKY0118087 | 39831073B20129 |  | WURTLAND - GREENUP / 1109-02 | Line Work | OH |  |  |  | KPC | YES | Replace Rotten KY Power Pole |  | 2022-10-03
2022 | 2022-09-26 | Ashland | 83464298 | DKY0118133 | 38830068D00398 |  | 3001204-HOWARDCOL / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1964 asset pole, need 45’4 | Skyline Dr, Ashland, KY 41102, USA | 2022-12-12
2022 | 2022-09-26 | Ashland |  |  | 38830068D00473 |  | 3001204-HOWARDCOL / SUMMIT | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Stolen pole ground | Skyline Dr, Ashland, KY 41102, USA | 2022-09-26
2022 | 2022-09-26 | Ashland | 86096734 | DKY0122248 | 38830068D00737 |  | 3001204-HOWARDCOL / SUMMIT | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1972 asset pole, replace with 45’4 DS101 | Ashland, KY, USA | 2023-11-13
2022 | 2022-09-26 | Ashland |  |  | 38830068D00880 | TRUE | 3001204-HOWARDCOL / SUMMIT | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Bottom bolt coming out of pole top pin | Ashland, KY, USA
2022 | 2022-09-26 | Ashland |  |  | 38830092A00059 |  | 3001204-HOWARDCOL / SUMMIT | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Missing anchor | KY-176, Kentucky, USA
2022 | 2022-09-26 | Ashland | 83401736 | DKY0118052 | 38830454B22558 |  | 3001402-LOUISA / HIGHBOTTOM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1968 asset pole reported by Bre McCoy | 132 KY-32, Louisa, KY 41230, USA | 2022-10-04
2022 | 2022-09-27 | Ashland |  |  | 38830188B00040 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Broken down guy; too high to reach from ground | Ashland, KY, USA
2022 | 2022-09-28 | Ashland | 83475425 | DKY0118146 | 38830188D00085 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1975 asset pole, need 45’4 | 4219 Friendship Rd, Catlettsburg, KY 41129, USA | 2022-10-14
2022 | 2022-09-28 | Ashland | 83474877 | DKY0118145 | 38830188D00305 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1977 asset pole, need 45’4 DS115 | 5813 Dog Fork Laurel Rd, Catlettsburg, KY 41129, USA | 2022-10-25
2022 | 2022-09-28 | Ashland |  |  | 38830188D00383 |  | 3008701-CANNONSBU / CANNONSBU | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Tighten guy and add guy marker | Kendall Ln, Kentucky 41102, USA | 2022-09-28
2022 | 2022-09-28 | Ashland |  |  | 38830212000035 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Stolen/missing neutral; one span | Bear creek rd, catlettsburg, ky
2022 | 2022-09-28 | Ashland | 83476233 | DKY0118149 | 38830212000094 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1966 asset pole | Blue ribbon ln, catlettsburg, ky | 2022-10-13
2022 | 2022-09-28 | Ashland | 83481370 | DKY0118157 | 38830212000126 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Large crack down middle of pole | 3914 Blue Ribbon Rd, Catlettsburg, KY 41129, USA | 2022-10-10
2022 | 2022-09-28 | Ashland |  |  | 38830213000003 |  | 3008701-CANNONSBU / CANNONSBU | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Can reach abandoned service drop from ground | 4125 Burchett Branch, Catlettsburg, KY 41129, USA | 2022-10-11
2022 | 2022-09-28 | Ashland |  |  | 38830213000061 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Poly pole top pin appears to be ready to break loose also pole is mistagged with 62 | Friendship Rd, Kentucky 41129, USA
2022 | 2022-09-28 | Ashland | 83536025 | DKY0118244 | 38830236000039 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1941 asset pole | Bear creek rd, catlettsburg, ky | 2022-10-12
2022 | 2022-09-28 | Ashland | 83517856 | DKY0118213 | 38830236000088 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1966 asset pole | Bear Creek Rd, Kentucky 41129, USA | 2022-10-19
2022 | 2022-09-30 | Ashland | 84434320 | DKY0119668 | 38830188A00027 | TRUE | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Split crossarm | Bear Creek Rd, Kentucky 41129, USA | 2023-06-30
2022 | 2022-09-30 | Ashland | 84434320 | DKY0119668 | 38830188B00035 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm split | Bear Creek Rd, Kentucky 41129, USA | 2023-06-30
2022 | 2022-10-03 | Ashland | 84415466 | DKY0119612 | 38830164B00264 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole appears to be split below telephone | Catlettsburg, KY 41129, USA | 2023-07-26
2022 | 2022-10-03 | Ashland |  |  | 38830188A00176 |  | 3008701-CANNONSBU / CANNONSBU | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Trees heavy on secondary. Sent text to Jason Bradshaw and Dusty Roll 10/3/2022 | 3006 Bonanza Dr, Catlettsburg, KY 41129, USA | 2022-10-03
2022 | 2022-10-03 | Ashland |  |  | 38830188A00212 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Missing anchor | Hidden Valley Rd, Kentucky 41129, USA
2022 | 2022-10-03 | Ashland |  |  | 38830188A00502 | TRUE | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Missing anchor | Catlettsburg, KY 41129, USA
2022 | 2022-10-03 | Ashland |  |  | 38830188A00502 | TRUE | 3008701-CANNONSBU / CANNONSBU | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Resag primary | Catlettsburg, KY 41129, USA
2022 | 2022-10-04 | Ashland | 83528848 | DKY0118233 | 38830163000029 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1958 asset pole | N Big Run Rd, Kentucky 41102, USA | 2022-11-07
2022 | 2022-10-04 | Ashland | 83525753 | DKY0118229 | 38830163000037 |  | 3008701-CANNONSBU / CANNONSBU | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole. Not a 1980 50’ pole | N Big Run Rd, Kentucky 41102, USA | 2022-11-01
2022 | 2022-10-04 | Ashland |  |  | 38830164A00306 | TRUE | 3008701-CANNONSBU / CANNONSBU | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Blown arrester on c phase | 1701 Central Ave, Ashland, KY 41101, USA
2022 | 2022-10-17 | Ashland | 84434320 | DKY0119668 | 38830164D00112 |  | 3008702-CANNONSBU / ROUTE3 | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | End of crossarm split | Dog fork Laura’s rd & brandy wine Dr, catlettsburg, ky | 2023-06-30
2022 | 2022-10-17 | Ashland | 83628637 | DKY0118364 | 38830188C00184 |  | 3008702-CANNONSBU / ROUTE3 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1972 asset pole | Bramble dr, catlettsburg, ky | 2022-11-07
2022 | 2022-10-17 | Ashland |  |  | 38830188C00225 |  | 3008702-CANNONSBU / ROUTE3 | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Customer complaining tree is knocking out Pwr. Tree in primary, reported to j Bradshaw | 15944 bramble drive, catlettsburg, ky | 2022-10-17
2022 | 2022-10-17 | Ashland | 83692596 | DKY0118455 | 38830188C00296 |  | 3008702-CANNONSBU / ROUTE3 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1977 asset pole | 16036 lone oak dr,catlettsburg, ky | 2023-11-08
2022 | 2022-10-17 | Ashland |  |  | 38830189000127 |  | 3008702-CANNONSBU / ROUTE3 | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Abandoned primary tap. Remove facilities | Lake view drive, catlettsburg, ky
2022 | 2022-10-24 | Ashland | 83665666 | DKY0118409 | 38830182B22661 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at top | N Hord St, Grayson, KY 41143, USA | 2022-11-04
2022 | 2022-10-25 | Ashland |  |  | 38830045A31051 |  | 3002107-10STREET / WEST CENTRAL | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Tree in primary | 1105 Martin Luther king blvd, Ashland, ky | 2022-10-25
2022 | 2022-10-25 | Ashland |  |  | 38830045A31216 |  | 3002107-10STREET / WEST CENTRAL | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Tree limb brushing primary | Behind Gatti Town Ashland Plaza | 2022-10-25
2022 | 2022-11-01 | Ashland | 83723813 | DKY0118498 | 38830326000103 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Assett pole turned in my Micheal Thompson | Grayson, KY 41143, USA | 2022-11-17
2022 | 2022-11-07 | Ashland |  |  | 38830190A46022 |  | 2206403-SOUTH NEAL / WHITES CREEK RD | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Leaning pole | US-23, Catlettsburg, KY, USA
2022 | 2022-11-07 | Ashland |  |  | 38830215B00011 |  | 2206403-SOUTH NEAL / WHITES CREEK RD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Top of pole rotted out | 16439 US-23, Catlettsburg, KY 41129, USA
2022 | 2022-11-07 | Ashland |  |  | 38830215B00033 |  | 2206403-SOUTH NEAL / WHITES CREEK RD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Top of pole rotten | 16439 US-23, Louisa, KY 41230, USA
2022 | 2022-11-07 | Ashland |  |  | 38830215B00066 |  | 2206403-SOUTH NEAL / WHITES CREEK RD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Brace broken | US-23, Louisa, KY, USA
2022 | 2022-11-07 | Ashland | 84379526 |  | 38830238000124 |  | 2206403-SOUTH NEAL / WHITES CREEK RD | Service Work | OH |  | pole ground: broken, missing- NON EQUIPMENT - loose connections |  | Foreign | NO | Stolen pole ground, can’t find ground rod | US-23, Louisa, KY, USA | 2023-02-07
2022 | 2022-11-07 | Ashland |  |  | 38830263A00032 |  | 2206403-SOUTH NEAL / WHITES CREEK RD | Line Work | OH |  | lightning arresters/insulators: damaged |  | Foreign | NO | 2 blown arrestors | US23 Louisa, ky
2022 | 2022-11-18 | Ashland | 83849309 | DKY0118660 | 38830116B00194 |  | 3117601-PRINCESS / MEADE STATION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; reported by Pat Thovson | Tipton Ross Rd, Kentucky 41102, USA | 2022-12-14
2022 | 2022-11-18 | Ashland | 83849598 | DKY0118665 | 38830116B00194A pole to be retagged to 38830116B06117 |  | 3117601-PRINCESS / MEADE STATION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | This is an “A” pole across the street. New pole # assigned 38830116B06117; reported by Pat Thovson | Tipton Ross Rd, Kentucky 41102, USA | 2022-12-14
2022 | 2022-11-18 | Ashland | 83852952 | DKY0118663 | 38830118C24561 | TRUE | 3008003-47TH STREET / CATLETTSB | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1967 asset pole; reported by Micheal Thompson | Oakland Ave, Catlettsburg, KY 41129, USA | 2023-03-21
2022 | 2022-11-23 | Ashland | 83880281 | DKY0118703 | 38830136000028 | TRUE | 3003701-COALTON / U.S.60W | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; reported by Pat Thovson |  | 2023-01-30
2022 | 2022-11-23 | Ashland | 83879559 | DKY0118702 | 38830136000033 | TRUE | 3003701-COALTON / U.S.60W | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; reported by Pat Thovson |  | 2023-01-30
2022 | 2022-12-02 | Ashland |  |  | 38830114000071 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten 1945 pole, may need to relocate and and a secondary pole to make them truck accessible | 2386 W Cobb Fork Rd, Ashland, KY 41102, USA
2022 | 2022-12-02 | Ashland | 84554859 | DKY0119939 | 38830114000074 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1945 asset pole | 2570 W Cobb Fork Rd, Ashland, KY 41102, USA | 2023-03-29
2022 | 2022-12-02 | Ashland | 84618313 | DKY0120006 | 38830114000075 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1045 asset pole | W Cobb Fork Rd, Kentucky 41102, USA | 2023-05-08
2022 | 2022-12-02 | Ashland | 84827920 | DKY0120357 | 38830138C30464 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1965 asset pole; need30’6 | KY-5, Ashland, KY, USA | 2023-05-12
2022 | 2022-12-02 | Ashland |  |  | 38830138C40468 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Need secondary lift pole to reroute service drop; service drop on roof | 11509 KY-5, Ashland, KY 41102, USA
2022 | 2022-12-02 | Ashland |  |  | 38830139A00329 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | End of arm twisted; replace with heavy duty arm, 556 angle pole | Virginia Blvd, Kentucky 41102, USA
2022 | 2022-12-03 | Ashland | 84472022 | DKY0119725 | 38830113000052 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 2 very large and deep woodpecker holes | High knob, Ashland,ky | 2023-03-15
2022 | 2022-12-03 | Ashland | 84588175 | DKY0119945 | 38830137000013 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, this is not a 1993 pole | Moore Branch Rd, Kentucky 41102, USA
2022 | 2022-12-03 | Ashland | 84550433 | DKY0119909 | 38830137000015 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1947 asset pole | Moore Branch Rd, Kentucky 41102, USA
2022 | 2022-12-03 | Ashland |  |  | 38830137000028 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Neutral below telephone cable, needs resagged | Straight Creek Rd, Kentucky, USA
2022 | 2022-12-03 | Ashland |  |  | 38830137C30143 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Arrester hanging off arm | Buena Vista Dr, Bellefonte, KY 41101, USA
2022 | 2022-12-03 | Ashland | 84534509 | DKY0119887 | 38830138A00098 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1947 asset pole | 3201 Straight Creek Rd, Ashland, KY 41102, USA | 2023-04-21
2022 | 2022-12-03 | Ashland |  |  | 38830138A00259 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Ground rod against chain link fence enclosing pool; move ground rod to opposite side of pole
2022 | 2022-12-03 | Ashland | 84831689 | DKY0120362 | 38830138B00101 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at top, long span | Straight Creek Rd, Kentucky, USA
2022 | 2022-12-03 | Ashland | 84492784 | DKY0119775 | 38830138B00143 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Large woodpecker holes at top of pole; also no secondary tap off pole. Pole 38830138B00339 not in field | 3638 Straight Creek Rd, Ashland, KY 41102, USA | 2023-03-20
2022 | 2022-12-03 | Ashland |  |  | 38830161000123 |  | 3117602-PRINCESS / ROUTE 180 | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Anchor missing | Gillium cemetery rd, Ashland,ky
2022 | 2022-12-14 | Ashland | 84012030 | DKY0118872 | 38830091C00182 |  | 3117601-PRINCESS / MEADE STATION | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Broken crossarm | Hall Ridge Rd, Kentucky 41102, USA | 2022-12-28
2022 | 2022-12-14 | Ashland | 84012030 | DKY0118872 | 38830091C00447 |  | 3117601-PRINCESS / MEADE STATION | Line Work | OH | crossarm/braces: broken/split | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Bad crossarm | Hall ridge rd, Ashland,ky | 2022-12-28
2022 | 2022-12-14 | Ashland | 84415494 | DKY0119614 | 38830092A00236 |  | 3117601-PRINCESS / MEADE STATION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1973 asset pole; top of pole rotten | Summit rd, Ashland,ky | 2023-04-25
2022 | 2022-12-14 | Ashland |  |  | 38830092B00217 |  | 3117601-PRINCESS / MEADE STATION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1971asset pole. Split at top | 1926 shores creek rd, Ashland,ky
2022 | 2022-12-14 | Ashland | 86103991 | DKY0122255 | 38830115A00183 |  | 3117601-PRINCESS / MEADE STATION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1963 asset pole | Meade Naples Rd, Kentucky 41102, USA | 2024-01-08
2022 | 2022-12-14 | Ashland |  |  | 38830115D00511 |  | 3117601-PRINCESS / MEADE STATION | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Broken crossarm brace | Paul Coffey Blvd, Kentucky 41102, USA
2022 | 2022-12-14 | Ashland |  |  | 38830115D00596 |  | 3117601-PRINCESS / MEADE STATION | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Large woodpecker holes; pole needs rechecked | Koans dr, Ashland,ky
2022 | 2022-12-16 | Ashland | 84293317 | DKY0119368 | 38830244000033 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Richard Blackshire | Old holly school rd, Lawton, ky | 2023-02-16
2022 | 2022-12-16 | Ashland | 84284874 | DKY0119346 | 38830244000034 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Assetpole; Richard Blackshire | Old holly school rd, Lawton,ky | 2023-02-15
2022 | 2022-12-16 | Ashland | 84282570 | DKY0119341 | 38830244000035 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Richard Blackshire | Old holly school rd, Lawton ky | 2023-02-15
2022 | 2022-12-16 | Ashland | 84281508 | DKY0119334 | 38830244000036 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Richard Blackshire | Old holly school rd, Lawton, ky | 2023-02-14
2022 | 2022-12-16 | Ashland | 84280911 | DKY0119332 | 38830244000037 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Richard Blackshire | Old Holly School Rd, Kentucky 40351, USA | 2023-02-14
2022 | 2022-12-16 | Ashland | 84280604 | DKY0119331 | 38830244000038 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Richard Blackshire | Old Holly School Rd, Kentucky 40351, USA | 2023-02-14
2022 | 2022-12-16 | Ashland | 84270376 | DKY0119295 | 38830244000039 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset ole; Richard Blackshire | Old holly school rd, lawton ,ky | 2023-02-13
2022 | 2022-12-16 | Ashland | 84267252 | DKY0119292 | 38830244000040 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Richard Blackshire | Old holly school rd, Lawton, ky | 2023-02-13
2022 | 2022-12-16 | Ashland | 84256414 | DKY0119270 | 38830244000043 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Richard Blackshire | Old holly school rd, Lawton,ky | 2023-01-24
2022 | 2022-12-16 | Ashland | 84145214 | DKY0118995 | 38830244000047 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Richard blacksh | Holly Fork, Lawton, ky | 2023-02-08
2022 | 2022-12-16 | Ashland | 84143932 | DKY0118993 | 38830244000058 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Richard Blackshire | Holly fork rd, Lawton, ky | 2023-02-08
2022 | 2022-12-16 | Ashland | 84089054 | DKY0118952 | 38830244000064 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Richard Blackshire | Holly Fork rd, Lawton, ky | 2023-01-13
2022 | 2022-12-16 | Ashland | 84290131 | DKY0119356 | 38830292C00105 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Richard Blackshire | Little Perry rd, Morehead, ky | 2023-05-10
2022 | 2022-12-16 | Ashland | 84287628 | DKY0119355 | 38830292C00107 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Richard Blackshire | Little Perry rd,Morehead, ky | 2023-05-22
2022 | 2022-12-16 | Ashland | 84286916 | DKY0119354 | 38830292C00109 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Richard Blackshire | Little Perry rd, Morehead, ky | 2023-05-22
2022 | 2022-12-19 | Ashland | 84226923 | DKY0119218 | 38830171000001 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | 11095 Ky-377, Morehead KY | 2023-05-11
2022 | 2022-12-19 | Ashland |  |  | 38830171000011 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | 11444 KY-377, Morehead Ky
2022 | 2022-12-19 | Ashland | 84455465 | DKY0119693 | 38830171000022 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | 11495 Ky-377, Morehead Ky
2022 | 2022-12-19 | Ashland | 84097106 | DKY0118973 | 38830171000024 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | 11628 Ky-377, Morehead KY | 2023-01-16
2022 | 2022-12-19 | Ashland | 84223332 | DKY0119209 | 38830195000008 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | 9699 Ky-377 Morehead, Ky | 2023-02-21
2022 | 2022-12-19 | Ashland | 84311537 | DKY0119403 | 38830195000038 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | Plank Chapel Road, Morehead Ky | 2023-05-11
2022 | 2022-12-19 | Ashland | 82411791 | DKY0117057 | 38830195000045 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | 10801 Ky-377, Morehead Ky | 2022-05-31
2022 | 2022-12-19 | Ashland |  |  | 38830244000046 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | Holly Fork Road, Morehead Ky | 2023-04-14
2022 | 2022-12-19 | Ashland | 84144359 | DKY0118994 | 38830244000062 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | Holly Fork Road, Morehead Ky | 2023-01-19
2022 | 2022-12-19 | Ashland | 84096390 | DKY0118967 | 38830244000068 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | Holly Fork Road, Morehead KY | 2023-02-09
2022 | 2022-12-19 | Ashland | 84396268 | DKY0119583 | 38830293000062 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | 1164 Ky-174, Morehead Ky | 2023-01-19
2022 | 2022-12-19 | Ashland | 84373739 | DKY0119536 | 38830268D00025 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | 7868 Us-60, Morehead Ky | 2023-04-15
2022 | 2022-12-19 | Ashland |  |  | 38830269D00247 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | 8691 Ky-174, Olive Hill Ky
2022 | 2022-12-19 | Ashland |  |  | 38830269D00255 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | Ky-174, Olive Hill Ky
2022 | 2022-12-19 | Ashland | 84359743 | DKY0119512 | 38830292C00114 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; Michael Thompson | 540 Little Perry Road, Morehead KY | 2023-05-12
2022 | 2022-12-28 | Ashland | 86674017 | DKY0123305 | 38830140B00140 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole split at top | Midland Trail, Kentucky 41102, USA
2022 | 2022-12-28 | Ashland | 86277567 | DKY0122537 | 38830140B00217 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, has mtr brace | E Jackson st, Ashland, ky | 2024-01-03
2022 | 2022-12-28 | Ashland |  |  | 38830140B00224 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; has mtl brace | Music Branch Rd, Kentucky, USA
2022 | 2022-12-28 | Ashland |  |  | 38830140B00276 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Low service drop, 12’ over driveway, 13’ over edge of road; need secondary pole | E Johnson Rd, Kentucky 41102, USA
2022 | 2022-12-28 | Ashland |  |  | 38830140B00283 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, has mtl brace | E Johnson Rd, Kentucky 41102, USA
2022 | 2022-12-28 | Ashland | 84434320 | DKY0119668 | 38830140B00449 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Rotten crossarm | Ashland US Army Reserve Center, Ashland, ky | 2023-06-30
2022 | 2022-12-28 | Ashland | 84378795 | DKY0119540 | 38830140B00472 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Pole appears weak at joint use attachments | Midland trail, Ashland, ky | 2023-05-25
2022 | 2022-12-28 | Ashland |  |  | 38830140B02017 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Missing anchor | Jason Rd, Kentucky 41102, USA
2022 | 2022-12-28 | Ashland |  |  | 38830140D00325 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, has mtr brace; need forestry to cut path to pole | 3710 Melody Ln, Ashland, KY 41102, USA
2022 | 2022-12-28 | Ashland |  |  | 38830140D00370 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Priority asset pole | Music Branch Rd, Kentucky, USA
2022 | 2022-12-28 | Ashland | 84397237 | DKY0119586 | 38830140D00406 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, has mtr brace | Music Branch Rd, Kentucky, USA | 2023-04-21
2022 | 2022-12-28 | Ashland |  |  | 38830140D00432 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, has crack in it and needs guyed | Melody Ln, Kentucky 41102, USA
2022 | 2022-12-28 | Ashland |  |  | 38830140D06006 |  | 3117603-PRINCESS/MIDLAND TRAIL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy guard | Dove Haven Dr, Kentucky 41102, USA | 2022-12-28
2022 | 2022-12-28 | Ashland |  |  | 38830140D07004 |  | 3117603-PRINCESS/MIDLAND TRAIL | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy guard | Willow wood Dr, Ashland, ky | 2022-12-28
2022 | 2022-12-29 | Ashland |  |  | 38830147000013 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | 12860 Cranston Road, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830219000015 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | Holly Fork Road, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830219000016 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | Holly Fork Road, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830219000035 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | 8690 Cranston Road, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830219000059 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | 9510 Cranston Road, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830244000063 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | 1535 Holly Fork Road, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830244000091 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | Near I--64, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830244000092 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | Near I--64, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830247000092 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | Hawk Road, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830247000093 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | Hawk Road, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830247000120 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | Hawk Lane, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830247000121 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | Hawk Lane, Morehead Ky
2022 | 2022-12-29 | Ashland | 84506661 | DKY0119870 | 38830247000122 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | Hawk Lane, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830247000180 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | Globe Hill Circle, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830247000181 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | Globe Hill Circle, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830247000182 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | Globe Hill Circle, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830247000184 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | Globe Hill Circle, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830247000185 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | Globe Hill Circle, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830247000186 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | Globe Hill Circle, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830247000187 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | Globe Hill Circle, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830247000188 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | Globe Hill Circle, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830271000063 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | State Highway 174, Morehead Ky
2022 | 2022-12-29 | Ashland | 84690619 | DKY0120157 | 38830272000049 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | Holbrook Road, Morehead Ky
2022 | 2022-12-29 | Ashland | 84690966 | DKY0120163 | 38830272000050 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | Holbrook Road, Morehead Ky
2022 | 2022-12-29 | Ashland | 82585904 | DKY0117246 | 38830272000052 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | Beathart Road, Morehead Ky | 2022-08-24
2022 | 2022-12-29 | Ashland |  |  | 38830272000060 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | State Highway 1620, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830272000061 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | State Highway 1620, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830272000063 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | State Highway 1620, Morehead Ky
2022 | 2022-12-29 | Ashland | NA | NA | 38830272000118 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Pole does not exist out in the field; it is no longer there. | State Highway 1620, Morehead Ky | 2023-04-13
2022 | 2022-12-29 | Ashland |  |  | 38830296000028 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | State Highway 1620, Morehead Ky
2022 | 2022-12-29 | Ashland | 84434320 | DKY0119668 | 38830116B00558 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Deteriorated crossarm | Oak Hill Dr, Kentucky 41102, USA | 2023-06-30
2022 | 2022-12-29 | Ashland |  |  | 38830140A00133 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Pole and stub guy pole needs straightened | Midland Trail Rd, Kentucky 41102, USA
2022 | 2022-12-29 | Ashland |  |  | 38830140A01003 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | 4/0 secondary—needs guy and anchor | Ashland, KY, USA
2022 | 2022-12-29 | Ashland |  |  | 38830140B00287 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, mtr brace | High Park St, Kentucky 41102, USA
2022 | 2022-12-29 | Ashland | 84151213 | DKY0119046 | 38830140C00045 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, mtl brace | Cannonsburg rd, Ashland, ky | 2023-01-19
2022 | 2022-12-29 | Ashland | 86665671 | DKY0123273 | 38830140D00163 |  | 3117603-PRINCESS/MIDLAND TRAIL | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, mtr brace | Collins rd, Ashland, ky
2022 | 2022-12-29 | Ashland |  |  | 38830245B00177 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | 9110 Us-60, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830268D00031 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | Bradley Hollow Road, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830269B00310 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | State Highway 174, Olive Hill KY
2022 | 2022-12-29 | Ashland |  |  | 38830269B00311 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | State Highway 174, Olive Hill KY
2022 | 2022-12-29 | Ashland |  |  | 38830269D00279 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | State Highway 174, Olive Hill KY
2022 | 2022-12-29 | Ashland |  |  | 38830270B00038 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | State Highway 174, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830270D00013 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | State Highway 174, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830270D00016 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | State Highway 174, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830270D00019 | TRUE | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | 5767 State Highway 174, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830270D00027 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | State Highway 174, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830270D00031 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Derek Null | State Highway 174, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830271C00102 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | State Highway 174, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830271C00164 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | State Highway 174, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830292C00048 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | 567 Ky-174, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | 38830292C00052 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Tom Huff | 415 Ky-174, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | FROM LAT/LON and address - I think this is pole 38830247000188 - not 38830272000064 (see other entry for #64) - NEED FIELD CHECK |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | Globe Hill Circle, Morehead Ky
2022 | 2022-12-29 | Ashland |  |  | FROM LAT/LON and address I think this is 38830272000064 - need to verify in field |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, assigned to Pat Thovson | State Highway 1620, Morehead Ky

## Ckt Defects Reported 2023 ASH
Reported Year | Reported Date | District | WR # or Trouble Ticket # | Work Order | Location Number | Duplicate Pole #? | Circuit Name | Work Type | OH or UG | P1 | P2 | Internal | Pole Owner | Does Pole Need Replaced? | Comments | Address | COMPLETED DATE
2023 | 2023-01-04 | Ashland |  |  | 38830116A00275 |  | 3117601-PRINCESS / MEADE STATION | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | YES | Strained pole over US60, needs replaced | US60, ASHLAND, KY
2023 | 2023-01-11 | Ashland | 84434174 | DKY0119648 | 38830525000082 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1949 asset pole, DS101 | Reuben’s branch rd, Louisa, ky | 2023-02-21
2023 | 2023-01-11 | Ashland |  |  | 38830525000110 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive pri line, wire on ground; pri deadended on 525/109-needs guyed; 4 spans need removed | Reuben’s branch rd, Louisa,ky
2023 | 2023-01-17 | Ashland | 84608657 | DKY0119988 | 38830549000043 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; DS103 | McClure Bridge Rd, Duluth, GA 30096, USA
2023 | 2023-01-17 | Ashland | 84814158 | DKY0120326 | 38830549000071 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; DS101, pole across creek; neutral down | McClure Branch Rd, Kentucky 41230, USA
2023 | 2023-01-17 | Ashland |  |  | 38830572000090 |  | 3007904-BUSSEYVILLE / TORCHLITE | Forestry | OH |  |  | Will address on regular maintenance schedule. | KPC | NO | Xfmr engulfed in vines | End of Shannon branch rd, Louisa, ky
2023 | 2023-01-17 | Ashland |  |  | 38830572D20154 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Duplex twisted in neutral | Blevins Fork rd, Louisa, ky
2023 | 2023-01-18 | Ashland |  |  | 38830596000048 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap; pri/neut on ground | Meades Branch Rd, Kentucky 41230, USA
2023 | 2023-01-18 | Ashland | 84800486 | DKY0120296 | 38830596000105 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced secondary pole | Blevins Fork Rd, Kentucky 41230, USA
2023 | 2023-01-18 | Ashland | 84300564 | DKY0119382 | 38830618000010 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole-braced | Big fork rd, uylesses, ky | 2023-01-31
2023 | 2023-01-18 | Ashland | 84351573 | DKY0119494 | 38830620000090 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, braced | Spaulding Branch Rd, Kentucky 41230, USA | 2023-02-08
2023 | 2023-01-18 | Ashland | 84299319 | DKY0119380 | 38830620000173 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole-braced | US Rt 581, Louisa, ky | 2023-02-13
2023 | 2023-01-18 | Ashland | 84803299 | DKY0120307 | 38830620C30357 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | YES | Need 5’ taller secocondary pole—triplex in joint use midspan | US Hwy 581, Louisa,ky | 2024-01-04
2023 | 2023-01-18 | Ashland | 84614583 | DKY0119993 | 38830642000024 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1949 Asset pole
2023 | 2023-01-18 | Ashland | 84605576 | DKY0119978 | 38830669000012 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1947 asset pole | Hwy 1690, Ulysses, ky
2023 | 2023-01-18 | Ashland | 84447215 | DKY0119671 | 38830669000028 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole scabbed, long spans, down pressure | Nats creek fork, Ulysses, ky | 2023-04-19
2023 | 2023-01-19 | Ashland |  |  | 38830621000012 |  | 3007904-BUSSEYVILLE / TORCHLITE | Forestry | OH |  |  | Will address on regular maintenance schedule. | KPC | NO | Primary pole overtaken by evergreens | Hwy 581, Louisa, ky
2023 | 2023-01-19 | Ashland |  |  | 38830621000068 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap; pri/neut down in several places; also map discrepancy-fuse feeds tap to 621/73 | Tadpole rd, Ulysses, ky
2023 | 2023-01-19 | Ashland | 84434666 | DKY0119651 | 38830645000055 |  | 3007904-BUSSEYVILLE / TORCHLITE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, braced | Hwy 1690, Kentucky 41230, USA | 2023-02-21
2023 | 2023-01-23 | Ashland | 84285599 | DKY0119348 | 38830244000115 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole reported by Richard Blackshire | Old Holly School rd, Cranston, ky | 2023-02-15
2023 | 2023-01-23 | Ashland |  |  | 38830453000091 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole—has a hydrolic recloser | Five Forks Rd, Kentucky 41230, USA
2023 | 2023-01-23 | Ashland | 84626974 | DKY0120034 | 38830453000264 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Scabbed pole | Partridge rd, Louisa,ky
2023 | 2023-01-23 | Ashland |  |  | 38830477000041 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | conductors: excessive splices, deteriorated conductors | KPC | NO | Washer and nut Missing on neutral Clevis, clevis coming out of pole | Hwy 32, Louisa, ky
2023 | 2023-01-23 | Ashland | 84434029 | DKY0119647 | 38830477000052 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1947 asset pole | Greenbrier rd, Louisa, ky | 2023-02-22
2023 | 2023-01-23 | Ashland |  |  | 38830501000526 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Pole leaning, anchor needs replaced | Blue sky drive, Louisa, ky
2023 | 2023-01-24 | Ashland | 84311704 | DKY0119402 | 38830429B00304 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | Wolfe ridge rd, Louis, ky | 2023-02-07
2023 | 2023-01-24 | Ashland |  |  | 38830429B00354 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole rotten at top | 1192 n Hwy 3, Louisa, ky
2023 | 2023-01-24 | Ashland |  |  | 38830429D06007 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH |  |  | conductors: excessive splices, deteriorated conductors | KPC | NO | Separated UG service conduit, exposed UG service | Hardee’s, Louisa ,ky
2023 | 2023-01-24 | Ashland | 84591865 | DKY0119968 | 38830453000130 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | Two mile creek rd, Louisa, ky | 2023-04-13
2023 | 2023-01-24 | Ashland | 84627416 | DKY0120045 | 38830453000151 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | Two mile creek rd, Louisa, ky
2023 | 2023-01-25 | Ashland | 84803869 | DKY0120311 | 38830430B09003 |  | 3007903-BUSSEYVILLE / LOUISA | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | Crab Tree Gap Rd, Louisa, KY 41230, USA
2023 | 2023-01-27 | Ashland |  |  | 38830254D00118 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | 254\118 inactive to 245\115; tree across all 3 phases at 254/117; loops cut at 245/115–fed from 254/54 | Rt 1, Hitchens, ky
2023 | 2023-01-27 | Ashland |  |  | 38830254D00118 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | 254\118 inactive to 245\115; tree across all 3 phases at 254/117; loops cut at 245/115–fed from 254/54 | Rt 1, Hitchens, ky
2023 | 2023-01-27 | Ashland |  |  | 38830254D00205 |  | 3001002-HITCHINS / WILLARD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Danger tree | Fraley br, Hitchens, ky
2023 | 2023-01-27 | Ashland |  |  | 38830254D00211 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | WS pole, rotten at top and large woodpecker holes | Fraley rd, Hitchens, ky
2023 | 2023-01-27 | Ashland |  |  | 38830254D00211 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | WS pole, rotten at top and large woodpecker holes | Fraley rd, Hitchens, ky
2023 | 2023-01-27 | Ashland |  |  | 38830254D00424 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Low service drop across rear deck; secondary pole needed | First trailer on Rt on Bobcat rd, Hitchens, ky
2023 | 2023-01-27 | Ashland |  |  | 38830278000106 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Abandoned secondary pole, 1 conductor of open wire still up, non-AEP lock on gate | Bobcat rd, Hitchens, ky z
2023 | 2023-01-27 | Ashland | 84312116 | DKY0119861 | 38830279000014 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | 178 Fields Br, Louisa, KY
2023 | 2023-01-27 | Ashland | 84312027 | DKY0119850 | 38830327B00045 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | Hwy 1496, Grayson, ky
2023 | 2023-01-27 | Ashland | 84304401 | DKY0119715 | 38830327B00072 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | Hwy 1496, Grayson, ky
2023 | 2023-01-27 | Ashland | 84312067 | DKY0119858 | 38830327B00073 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | Hwy 1496, Grayson, ky
2023 | 2023-01-27 | Ashland | 84304822 | DKY0119719 | 38830327B00074 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | Hwy 1496, Grayson, ky
2023 | 2023-01-27 | Ashland | 84304882 | DKY0119729 | 38830327B00075 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | Hwy 1496, Grayson, ky
2023 | 2023-01-27 | Ashland | 84304287 | DKY0119713 | 38830327B00078 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | Hwy 1496, Grayson, ky
2023 | 2023-01-27 | Ashland | 84311915 | DKY0119752 | 38830350000001 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | Hwy 1496, Grayson, ky
2023 | 2023-01-31 | Ashland | 84360014 | DKY0119518 | 38830279000164 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Rotten crossarm | Hitchens Rd, Kentucky 41143, USA | 2023-05-11
2023 | 2023-01-31 | Ashland | 84360014 | DKY0119518 | 38830279000165 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Rotten crossarm | Hitchens rd, Hitchens,ky | 2023-05-11
2023 | 2023-01-31 | Ashland | 84360014 | DKY0119518 | 38830279000169 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm split on field side | Hitchens rd, Hitchens, ky | 2023-05-11
2023 | 2023-01-31 | Ashland | 84360014 | DKY0119518 | 38830279000182 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Split crossarm | Hitchens Rd, Kentucky 41143, USA | 2023-05-11
2023 | 2023-01-31 | Ashland | 84378651 | DKY0119546 | 38830303000141 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole split at crossarm | Hitchens Rd, Kentucky 41143, USA | 2023-05-24
2023 | 2023-01-31 | Ashland |  |  | 38830303000161 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | NEEDS ADDITIONAL CHECK | Pole is splitting at pri guy attachment | Hardy Branch Rd, Kentucky 41143, USA
2023 | 2023-02-02 | Ashland | 84853242 | DKY0120395 | 38830303000168 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | crossarm/braces: broken/split | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Crossarm splitting | Rt 1, Hitchens, ky | 2023-06-08
2023 | 2023-02-02 | Ashland | 84853675 | DKY0120396 | 38830327A00277 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Broken brace | Kentucky, USA | 2023-06-08
2023 | 2023-02-10 | Ashland |  |  | 38830181C00128 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole—Micheal Thompson | Hwy 1947, Grayson, ky
2023 | 2023-02-10 | Ashland |  |  | 38830244000011 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole-Richard Blackshire | Old Holly school rd, morehead, ky
2023 | 2023-02-10 | Ashland |  |  | 38830244000011 | TRUE | 3000801-HAYWARD / HALDEMAN | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole-Richard Blackshire | Old Holly school rd, morehead, ky
2023 | 2023-02-10 | Ashland | 84468491 | DKY0119722 | 38830327B00248 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | Rt 1, Hitchens, ky | 2023-05-25
2023 | 2023-02-13 | Ashland | 84493659 | DKY0119777 | 38830326000059 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, braced | St Hwy 1122, Willard, ky
2023 | 2023-02-13 | Ashland |  |  | 38830326000108 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole inactive pole, may want to remove? | St Hwy 1122, Willard, ky | 2023-02-14
2023 | 2023-02-13 | Ashland |  |  | 38830326000112 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, cutout open feeding this and 326/112, might remove these two poles? | St Hwy 1122, Willard, ky
2023 | 2023-02-13 | Ashland | 84312027 | DKY0119850 | 38830327B00045 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole 1941 | St Hwy 1496, Willard, ky
2023 | 2023-02-13 | Ashland |  |  | 38830350000064 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO |  | St Hwy 1122, Willard, ky
2023 | 2023-02-13 | Ashland |  |  | 38830350000073 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Missing anchor | St Hwy 1122, Hitchens, ky
2023 | 2023-02-13 | Ashland |  |  | 38830350000108 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Need in-line primary pole, primary 10’ from top of slope | Leadingham branch, Willard, ky
2023 | 2023-02-13 | Ashland |  |  | 38830350000136 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Missing anchor | Leadingham branch, Willard, ky
2023 | 2023-02-13 | Ashland |  |  | 38830351000054 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Poletop rotted out | Bells Trace, Kentucky, USA
2023 | 2023-02-13 | Ashland | 84468423 | DKY0119763 | 38830351000057 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole | Bells trace, Hitchens, ky
2023 | 2023-02-13 | Ashland | 84468423 | DKY0119763 | 38830351000057 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | Stolen neutral - 2 spans | Bells Trace, Kentucky, USA
2023 | 2023-02-13 | Ashland |  |  | 38830351000065 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Split crossarm, also roadside phase off insulator | KY-1, Kentucky, USA
2023 | 2023-02-14 | Ashland | 85538749 | DKY0121440 | 38830376000040 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NEEDS ADDITIONAL CHECK | Pole in slip | Peach tree ln, Webbville, ky | 2023-10-25
2023 | 2023-02-14 | Ashland | 84454981 | DKY0119687 | 38830376000049 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1947 asset pole | Peachtree ln, Webbville, ky
2023 | 2023-02-14 | Ashland | 84462891 | DKY0119709 | 38830376000095 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole, braced | Peach tree ln, Webbville, ky | 2023-03-23
2023 | 2023-02-14 | Ashland | 84826289 | DKY0120350 | 38830400000004 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Poletop rotted out | KY-1, Kentucky, USA
2023 | 2023-02-14 | Ashland | 84455612 | DKY0119688 | 38830400000007 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1947 asset pole | Rt 1, Webbville, ky | 2023-03-23
2023 | 2023-02-14 | Ashland | 84805380 | DKY0120316 | 38830401000030 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole washed out | Rt 1, Webbville, ky
2023 | 2023-02-14 | Ashland | 84510786 | DKY0119839 | 38830401000039 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1947 asset pole | Rt 1, Webbville, ky
2023 | 2023-02-14 | Ashland | 84496443 | DKY0119791 | 38830401000056 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1952 asset pole | Rt1, Webbville, ky
2023 | 2023-02-15 | Ashland | 84454439 | DKY0119686 | 38830351000078 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1945 asset pole | Bells Trace, Webbville, ky | 2023-06-05
2023 | 2023-02-15 | Ashland | 84449190 | DKY0119678 | 38830352000008 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Low clearance over hayfield | Bells Trace, Webbville, ky | 2023-03-23
2023 | 2023-02-15 | Ashland | 84462766 | DKY0119705 | 38830352000022 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1948 asset pole | Bells trace, Webbville,ky | 2023-03-23
2023 | 2023-02-15 | Ashland | 84456073 | DKY0119691 | 38830352000024 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Definitely not 2001 pole, mid 40’s asset pole | Bells trace, Webbville, ky
2023 | 2023-02-15 | Ashland |  |  | 38830352000033 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | 1 span missing neutral also map discrepancy, pole 352/28 in field 150’ downstream and has the tap, no tap on 352/33 | Bells trace rd, Webbville, ky
2023 | 2023-02-15 | Ashland | 84456523 | DKY0119697 | 38830353000004 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1948 Asset pole, braced | Knotty Poplar rd, Webbville, ky | 2023-03-01
2023 | 2023-02-15 | Ashland |  |  | 38830399000009 |  | 3001002-HITCHINS / WILLARD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Danger tree | Brushy branch rd, Webbville, ky
2023 | 2023-02-15 | Ashland | 84452448 | DKY0119683 | 38830399000032 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten at base, braced 1949 asset pole | Needmore rd, Webbville, ky | 2023-03-15
2023 | 2023-02-15 | Ashland | 84453918 | DKY0119685 | 38830399000033 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1949 asset pole, braced | Brushy branch rd, Webbville, ky | 2023-03-15
2023 | 2023-02-15 | Ashland | 84453286 | DKY0119684 | 38830399000043 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1959 asset secondary pole, braced | Needmore rd, Webbville, ky | 2023-04-19
2023 | 2023-02-16 | Ashland | 84448200 | DKY0119675 | 38830427000078 |  | 3000203-BIG SANDY/YATESVILLE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole—Ethan Whitt | Yatesville road, Louisa ,ky | 2023-03-23
2023 | 2023-02-21 | Ashland | 86108681 | DKY0122268 | 38830247000060 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole—Micheal Thompson | Dry Branc Rd East, Olive Hill, ky
2023 | 2023-02-22 | Ashland |  |  | 38830424000047 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Anchor missing | Rt 2101, Webbville, ky
2023 | 2023-02-22 | Ashland |  |  | 38830424000049 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO |  | Rt 201,Webbville, ky
2023 | 2023-02-22 | Ashland | 85885660 | BR-549 | 38830424000049 | TRUE | 3001002-HITCHINS / WILLARD | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Old service drop laying across telephone; needs removed | Rt 201, Webbville, ky | 2023-09-08
2023 | 2023-02-22 | Ashland |  |  | 38830424000053 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap; primary down, remove xfmr pole and two secondary poles | Rt 1341, Webbville, ky
2023 | 2023-02-22 | Ashland |  |  | 38830424000086 |  | 3001002-HITCHINS / WILLARD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy protector | Fisher town branch rd, webbville | 2023-02-22
2023 | 2023-02-22 | Ashland |  |  | 38830447000011 |  | 3001002-HITCHINS / WILLARD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Broken tree limb hanging on primary and neutral midspan | Cherokee gap rd, Webbville, ky
2023 | 2023-02-22 | Ashland | 84492581 | DKY0119773 | 38830472000060 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1947 asset pole | Parker fork rd, Cherokee, ky | 2023-03-16
2023 | 2023-02-22 | Ashland |  |  | 38830472000069 |  | 3001002-HITCHINS / WILLARD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy protector | Lick fork rd, Cherokee, ky | 2023-02-22
2023 | 2023-02-22 | Ashland | 84623555 | DKY0120015 | 38830472000078 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced asset pole—-may want to remove part of tap, this is an inactive service and no future reconnects | Able branch, Webbville, ky
2023 | 2023-02-22 | Ashland |  |  | 38830472000084 |  | 3001002-HITCHINS / WILLARD | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy protector | Hwy 201, Cherokee, ky | 2023-02-22
2023 | 2023-02-22 | Ashland | 84491577 | DKY0119768 | 38830496000002 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1947 asset pole DS101 | Parker fork rd, Cherokee, ky | 2023-03-16
2023 | 2023-02-22 | Ashland | 84491577 | DKY0119768 | 38830496000002 | TRUE | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1947 asset pole DS101 | Parker fork rd, Cherokee, ky | 2023-03-16
2023 | 2023-02-27 | Ashland | 84589639 | DKY0119957 | 38830278000011 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1941 asset pole | Chapel cut rd, Hitchens, ky
2023 | 2023-02-27 | Ashland |  |  | 38830278000048 |  | 3001002-HITCHINS / WILLARD | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Danger tree | Baier rd, Hitchens,ky
2023 | 2023-02-27 | Ashland | 85969921 | KQY174 | 38830278000261 |  | 3001002-HITCHINS / WILLARD | Service Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove secondary attached to pole and laying on ground—secondary pole gone, opened xfmr to make safe xfmr | Little Huff Run, Kentucky 41143, USA | 2023-09-21
2023 | 2023-02-27 | Ashland |  |  | 38830278000262 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Pole gone, not in field; need WO written to remove from service | Huff Run Rd, Kentucky 41143, USA
2023 | 2023-02-27 | Ashland | 84521594 | DKY0119853 | 38830278D40320 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Two large woodpecker holes near top of pole | Huffs run, Hitchens, ky
2023 | 2023-02-27 | Ashland |  |  | 38830279000088 |  | 3001002-HITCHINS / WILLARD | Line Work | OH |  |  |  | KPC | NO | Stolen neutral | Hitchins, KY 41143, USA
2023 | 2023-02-27 | Ashland | 84526685 | DKY0119862 | 38830304000033 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced 1955 asset pole | Dave’s run, Hitchens, ky
2023 | 2023-03-01 | Ashland | 84822451 | DKY0120343 | 38830328000063 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1949 asset pole. DS101 | Reeves branch, Denton, ky
2023 | 2023-03-01 | Ashland | 84817307 | DKY0120331 | 38830329000077 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; access to pole recently dozed | St Hwy 1496, Willard, ky
2023 | 2023-03-01 | Ashland | 84675144 | DKY0120161 | 38830329000109 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Asset pole; no tap on pole, 10KVA xfmr on pole | Cook Crk, Willard, ky
2023 | 2023-03-14 | Ashland |  |  | 38830182B22543 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NO | Poletop rotten | W 3rd St, Grayson, KY 41143, USA
2023 | 2023-03-14 | Ashland |  |  | 38830182B30247 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Blown arrester | Grayson, KY 41143, USA
2023 | 2023-03-14 | Ashland |  |  | 38830182B30297 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Straighten pole | Carol Malone Blvd, Kentucky 41143, USA
2023 | 2023-03-14 | Ashland | 84662167 | DKY0120096 | 38830182B43607 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Poletop rotted | E 5th St, Grayson, KY 41143, USA
2023 | 2023-03-14 | Ashland | 84649327 | DKY0120076 | 38830182B43614 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Scabbed dead end pole. Need 45’4 | Jim Phillips blvd, Grayson, ky
2023 | 2023-03-14 | Ashland | 85393278 | DKY0121168 | 38830182B43686 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Pole Replacement | Spring st,Grayson, ky | 2023-09-23
2023 | 2023-03-14 | Ashland | 84678049 | DKY0120127 | 38830182D00195 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced secondary asset pole | Webster Ave, Grayson, ky | 2024-01-05
2023 | 2023-03-14 | Ashland | 84663402 | DKY0120105 | 38830182D00206 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Poletop split | Cherrywood Ln, Grayson, KY 41143, USA | 2024-01-18
2023 | 2023-03-14 | Ashland | 84669014 | DKY0120141 | 38830206A31060 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at base | Robert and Mary St, Grayson, KY 41143, USA
2023 | 2023-03-14 | Ashland |  |  | 38830206A31103 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Rotten crossarms | Robert and Mary St, Grayson, KY 41143, USA
2023 | 2023-03-14 | Ashland |  |  | 38830206A31238 |  | 3116102-GRAYSON / DIXIEPARK | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Poletop rotted out | E 3rd St, Grayson, KY 41143, USA
2023 | 2023-03-20 | Ashland |  |  | 38830231000057 |  | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole top burnt off | Robin run, Grayson,ky
2023 | 2023-03-20 | Ashland | 84722482 | DKY0120198 | 38830231000072 |  | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1948 asset pole | Robin run, Grayson, ky
2023 | 2023-03-20 | Ashland |  |  | 38830231000080 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Straighten pole | Robbin ru, Grayson, ky
2023 | 2023-03-20 | Ashland | 84846065 | DKY0120389 | 38830255000013 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Deteriorated crossarm | St Hwy 773, Hitchens, ky
2023 | 2023-03-20 | Ashland | 84852353 | DKY0120392 | 38830255000015 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | Foreign | NO | Deteriorated crossarm | By 773, Grayson, ky | 2023-06-08
2023 | 2023-03-20 | Ashland |  |  | 38830255000079 |  | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Large woodpecker hole between top and middle phases | Miller rd, Hitchens, ky
2023 | 2023-03-20 | Ashland |  |  | 38830255000101 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Straighten pole | Robin run, Grayson, ky
2023 | 2023-03-20 | Ashland |  |  | 38830255000140 |  | 3001001-HITCHINS / DENTON | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | Foreign | NO | Tree limb grown into secondary pulling conductors down | End of Katy branch, Hitchens, ky
2023 | 2023-03-20 | Ashland | 84852822 | DKY0120394 | 38830255000160 | TRUE | 3001001-HITCHINS / DENTON | Line Work | OH | crossarm/braces: broken/split |  |  | Foreign | NO | Rotten crossarm very bad shape | Hwy 773, Hitchens, ky
2023 | 2023-03-20 | Ashland | 84731851 | DKY0120236 | 38830255000226 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Large woodpecker hole | Campbell branch, Hitchens, ky
2023 | 2023-03-20 | Ashland | 84741250 | DKY0120246 | 38830279000127 |  | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced asset pole | Miller rd, Hitchens, ky
2023 | 2023-03-20 | Ashland | 86001902 | 18436572 | 38830279000215 |  | 3001001-HITCHINS / DENTON | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Service knob pulled out of service pole, can now reach service drop from ground | Katy br, Hitchens, ky | 2023-09-26
2023 | 2023-03-20 | Ashland | 84749674 | DKY0120262 | 38830280000007 |  | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Woodpecker hole between arm and c/o bracket; also arm is deteriored | Jordan ln, Hitchens, ky
2023 | 2023-03-20 | Ashland | 84804604 | DKY0120318 | 38830280000013 |  | 3001001-HITCHINS / DENTON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Arm beginning to split; can change out same time as 280/14-in same field | Hwy 773, Hitchens, ky | 2023-06-08
2023 | 2023-03-20 | Ashland | 84814031 | DKY0120321 | 38830280000014 |  | 3001001-HITCHINS / DENTON | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Arm beginning to split on roadside; can change out same time as 280/13-same field | Hwy 773 | 2023-06-08
2023 | 2023-03-20 | Ashland |  |  | 38830280000016 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  |  |  | KPC | NO | Missing neutral | Glancey Fork, Hitchens, ky
2023 | 2023-03-28 | Ashland | 84722614 | DKY0120229 | 38830044C35048 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole rotten at base | Prichard st, Westwood, ky | 2023-05-15
2023 | 2023-03-29 | Ashland |  |  | 38830280000066 |  | 3001001-HITCHINS / DENTON | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Anchor pulled out of ground | Glancy fork
2023 | 2023-03-29 | Ashland | 84794099 | DKY0120295 | 38830280000071 |  | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1963 asset pole | Glancy Fork, Denton, ky
2023 | 2023-03-29 | Ashland | 84792709 | DKY0120293 | 38830280000109 |  | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1968 pole. Rotten at base, need forestry to cut path | Hogdshead hollow, Denton, ky
2023 | 2023-03-29 | Ashland |  |  | 38830280000110 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NEEDS ADDITIONAL CHECK | Large woodpecker hole on top of pole | Hogsheads hollow, Denton,ky
2023 | 2023-03-29 | Ashland |  |  | 38830280000132 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove secondary pole, no secondary attached in field, 280/143 not in field | Glancy Fork, Denton, ky
2023 | 2023-03-29 | Ashland | 84754012 | DKY0120274 | 38830280000135 |  | 3001001-HITCHINS / DENTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced secondary pole | St Hwy 773, Denton, ky
2023 | 2023-03-29 | Ashland |  |  | 38830281000009 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  |  |  | KPC | NO | Stolen neutral | Glancy Fork, Denton, ky
2023 | 2023-03-29 | Ashland |  |  | 38830281000027 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Leaning pole | Glancy Fork, Denton, ky
2023 | 2023-03-29 | Ashland |  |  | 38830305000017 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Suggest pole be removed; dead end xfmr pole and add down guy, no open wire secondary on pole | Hwy 773, Denton, ky
2023 | 2023-03-29 | Ashland |  |  | 38830305000069 |  | 3001001-HITCHINS / DENTON | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Straighten pole | Hwy773, Denton, ky
2023 | 2023-05-24 | Ashland | 86138954 | DKY0122327 | 38830478A31072 |  | 3007906-Busseyville / Walbridge | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced pole | Browns Food Service, Louisa, ky
2023 | 2023-05-24 | Ashland | 85131691 | DKY0120813 | 38830478D10092 |  | 3007906-Busseyville / Walbridge | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Crack in pole about 5’ up, 3 phase, long span over Hwy 644 | Kevin Ave, Louisa, ky | 2024-01-02
2023 | 2023-05-24 | Ashland |  |  | 38830502000189 |  | 3007906-Busseyville / Walbridge | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Deteriorated crossarm | 3085 KY-2565, Louisa, KY 41230, USA
2023 | 2023-05-30 | Ashland |  |  | 38830550000070 |  | 3007906-Busseyville / Walbridge | Line Work | OH |  |  |  | KPC | NO | Neutral down across railroad tracks; neut in yard, cut it because of proximity to open wire to make safe | Chapman st, Louisa ,y
2023 | 2023-05-30 | Ashland |  |  | 38830600000029 | TRUE | 3007906-Busseyville / Walbridge | Forestry | OH |  |  | Pole and address do not match up. | KPC | NO | Vines consuming pole | 11532 Hwy 1690, Louisa ky
2023 | 2023-05-30 | Ashland |  |  | 38830600000029 | TRUE | 3007906-Busseyville / Walbridge | Forestry | OH |  |  | Duplicate from above. | KPC | NO | Vines consuming pole | 11532 Hwy 1690, Louisa ky
2023 | 2023-06-06 | Ashland | 85894867 | DKY0121977 | 38830501000030 |  | 3007905-Busseyville / Mattie | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Broken crossarm | Red branch rd, Louisa, ky | 2023-09-26
2023 | 2023-06-06 | Ashland |  |  | 38830501000034 |  | 3007905-Busseyville / Mattie | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NEEDS ADDITIONAL CHECK | Crossarm bolted to top of pole, has pri tap w down guy on it | St Rt 3395, Louisa, ky
2023 | 2023-06-06 | Ashland | 86587010 | DKY0123074 | 38830501000184 | TRUE | 3007905-Busseyville / Mattie | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole is broken at telephone attachment
2023 | 2023-06-06 | Ashland |  |  | 38830501000252 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  |  | KPC | NO | No neutral | Poor house hill rd, Louisa, ky
2023 | 2023-06-06 | Ashland | 85644373 | DKY0121541 | 38830501000295 |  | 3007905-Busseyville / Mattie | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Crossarm split at end | St Rt 3395, Louisa, ky | 2024-01-02
2023 | 2023-06-06 | Ashland | 86160003 | DKY0122356 | 38830501A40589 |  | 3007905-Busseyville / Mattie | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Broken secondary pole | Broadleaf pole, Louisa, ky | 2024-01-08
2023 | 2023-06-09 | Ashland |  |  | 38830476000054 |  | 3007905-Busseyville / Mattie | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | 2 missing guy protectors | Turkey run rd, Louisa, ky | 2023-06-09
2023 | 2023-06-09 | Ashland |  |  | 38830500000117 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  |  | KPC | NO | Bent poletop pin; long span | Buck run rd, Louisa, ky
2023 | 2023-06-09 | Ashland |  |  | 38830500000225 |  | 3007905-Busseyville / Mattie | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Guy marker missing | Rt 32, Louisa,ky | 2023-06-09
2023 | 2023-06-09 | Ashland |  |  | 38830500C10298 |  | 3007905-Busseyville / Mattie | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Clearance issue; service drop 13’8 over pole | Deer lick run rd, Louisa, ky
2023 | 2023-06-12 | Ashland | 84797167 | DKY0120869 | 38830068C00956 |  | 3001201-HOWARDCOL / 13STREET | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten at base | 4331 Shannon Dr, Ashland, KY 41102, USA | 2023-06-14
2023 | 2023-06-12 | Ashland | 12345678 |  | 38830595000071 |  | 3007905-Busseyville / Mattie | Service Work | OH |  |  | other: customer owned attachment | Customer | NO | Service pole leaning | Hwy 1760, Louisa , ky | 2023-09-01
2023 | 2023-06-12 | Ashland |  |  | 38830595A30118 |  | 3007905-Busseyville / Mattie | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral needs resagged; enter twinning with telephone | Thompson Fork rd, Louisa, ky
2023 | 2023-06-12 | Ashland |  |  | 38830595D30022 |  | 3007905-Busseyville / Mattie | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | NEEDS ADDITIONAL CHECK | Pole washing out | 5741 Hwy 1760, Louisa, ky
2023 | 2023-06-13 | Ashland | 86206748 | DKY0122430 | 38830547000039 |  | 3007905-Busseyville / Mattie | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | 1946 asset pole; in pasture, truck if dry | Mattie rd, Louisa, ky
2023 | 2023-06-13 | Ashland |  |  | 38830547000130 |  | 3007905-Busseyville / Mattie | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Pri and neut needs resagged; clearance issue with neut and telephone | Sycamore br, Louisa, ky
2023 | 2023-06-14 | Ashland |  |  | 38830500000218 |  | 3007905-Busseyville / Mattie | Line Work | UG | UG conduit: damaged or separated |  |  | KPC | YES | Secondary pedestal in road; needs relocated | Cedgap rd, Louisa, ky
2023 | 2023-06-14 | Ashland |  |  | 38830524000236 |  | 3007905-Busseyville / Mattie | Forestry | OH |  |  | This is a customer refusal. | KPC | NO | Trees and vines engulfing pole | Ced Gap Rd, Kentucky, USA
2023 | 2023-06-14 | Ashland |  |  | 38830570000058 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove inactive secondary pole | Mattie rd, Louisa, ky
2023 | 2023-06-14 | Ashland | 85643289 | DKY0121536 | 38830571000058 |  | 3007905-Busseyville / Mattie | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced pole | Newcombe hollow rd, Louisa, ky
2023 | 2023-06-14 | Ashland | 85582447 | DKY0121454 | 38830571000059 |  | 3007905-Busseyville / Mattie | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced pole | Newcombe hollow rd, Louisa, ky
2023 | 2023-06-14 | Ashland |  |  | 38830571000101 |  | 3007905-Busseyville / Mattie | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole washed out, needs relocated | Long fork creek rd, Louisa, ky
2023 | 2023-06-19 | Ashland | 85866776 | 8675309 | 38830499000022 |  | 3007905-Busseyville / Mattie | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | KPC | NO | Abandoned service drop hanging off pole | Muddy Ridge Rd, Kentucky 41201, USA | 2023-09-01
2023 | 2023-06-19 | Ashland | 85994879 | DKY0122096 | 38830522000079 |  | 3007905-Busseyville / Mattie | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole | Tracy branch rd, Louisa, ky
2023 | 2023-06-19 | Ashland |  |  | 38830523000091 |  | 3007905-Busseyville / Mattie | Forestry | OH |  |  | Will address on regular maintenance schedule. | KPC | NO | Pole engulfed in vines | Muddy ridge rd, Louisa, ky
2023 | 2023-06-20 | Ashland |  |  | 38830425000060 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  |  | KPC | NO | Stolen neutral | Irish Crk rd, Louisa, ky
2023 | 2023-06-20 | Ashland |  |  | 38830425000062 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive 4 span tap, pri dwn | Irish Crk rd, Louisa,ky
2023 | 2023-06-20 | Ashland |  |  | 38830473000018 |  | 3007905-Busseyville / Mattie | Line Work | OH |  |  |  | KPC | NO | Missing neutral—long span over holler, may need forestry to clear path | Louisa, KY 41230, USA
2023 | 2023-06-20 | Ashland |  |  | 38830473000018 | TRUE | 3007905-Busseyville / Mattie | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy marker | Oak hill rd, Louisa,ky | 2023-06-20
2023 | 2023-06-20 | Ashland |  |  | 38830473000019 |  | 3007905-Busseyville / Mattie | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy protector | Oak hill rd, Louisa, ky | 2023-06-20
2023 | 2023-06-20 | Ashland |  |  | 38830473000133 |  | 3007905-Busseyville / Mattie | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Burnt pole | Irish Crk rd, Louisa, ky
2023 | 2023-06-20 | Ashland | 85995993 | DKY0122098 | 38830497000026 |  | 3007905-Busseyville / Mattie | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Burnt pole | Right Fork Irish Creek Rd, Kentucky 41180, USA
2023 | 2023-07-12 | Ashland |  |  | 38830254B00245 |  | 3001004-HITCHINS / E K ROAD | Line Work | OH |  |  |  | Foreign | NO | One long span over hollow missing, also resag neutral to this pole, will need forestry to cut path | St Hwy 1444, Hitchens, ky
2023 | 2023-07-12 | Ashland |  |  | 38830254B00298 |  | 3001004-HITCHINS / E K ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | ‘“A” light pole, not on maps, has pole brace | St Hwy 1444, Hitchens, ky
2023 | 2023-07-12 | Ashland |  |  | 38830254D00090 |  | 3001004-HITCHINS / E K ROAD | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Pole needs straightened, may need pushbrace | Intersection Rt 1 and st Hwy 773, Hitchens, ky
2023 | 2023-07-12 | Ashland |  |  | 38830254D00250 | TRUE | 3001004-HITCHINS / E K ROAD | Line Work | OH |  |  |  | Foreign | NO | 3 spans neutral missing | Powell hollow, Hitchens, ky
2023 | 2023-07-12 | Ashland | 85644096 | DKY0121540 | 38830278000132 |  | 3001004-HITCHINS / E K ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Broken pole, long span, sent email to engineering | Huff’s ln, Hitchens, ky | 2023-09-19
2023 | 2023-07-18 | Ashland |  |  | 38830206B28025 | TRUE | 3001004-HITCHINS / E K ROAD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole in slip | S Carol Malone Blvd, Kentucky 41143, USA
2023 | 2023-08-02 | Ashland |  |  | 38830181C00008 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap; 2 spans | St Hwy 1947, Grayson, ky
2023 | 2023-08-02 | Ashland |  |  | 38830183D00022 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole topped with crossarm | Tark hill rd, Grayson, ky
2023 | 2023-08-02 | Ashland | 82839366 | DKY0117500 | 38830183D00034 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole being washing out. Foreign pole | Talk hill rd | 2023-12-04
2023 | 2023-08-02 | Ashland |  |  | 38830183D00195 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten at base | Tara Ct, Grayson, ky
2023 | 2023-08-02 | Ashland |  |  | 38830183D46129 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole and anchor being washed out | Tark Hill Rd, Kentucky 41143, USA
2023 | 2023-08-02 | Ashland |  |  | 38830206A22488 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced secondary pole, may need forestry to trim tree to transfer secondary | S Hord St, Grayson, KY 41143, USA
2023 | 2023-08-02 | Ashland |  |  | 38830206A31211 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | Foreign | NO | Pole leaning pulling service drop | S Carole Malone Ave, Grayson, ky
2023 | 2023-08-02 | Ashland |  |  | 38830206B02386 |  | 3116101-GRAYSON / LANSDOWNE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Replace stub guy pole, need forestry | Hord st, Grayson, ky
2023 | 2023-08-02 | Ashland |  |  | 38830206C02263 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten at base | Chestnut St, Grayson, KY 41143, USA
2023 | 2023-08-02 | Ashland | 85770339 | DKY0121751 | 38830206C02383 |  | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten at base | Poplar Heights Dr, Grayson, KY 41143, USA | 2023-08-22
2023 | 2023-08-02 | Ashland |  |  | 38830206C02445 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten at base | US-60, United States
2023 | 2023-08-02 | Ashland |  |  | 38830207A00061 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Pole is washed out | Damron Branch Rd, Grayson, KY 41143, USA
2023 | 2023-08-02 | Ashland |  |  | 38830207A00136 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten at base | Charles St, Grayson, KY 41143, USA
2023 | 2023-08-02 | Ashland |  |  | 38830207A00142 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | Foreign | YES | Rotten at base | Charles St, Grayson, KY 41143, USA
2023 | 2023-08-02 | Ashland |  |  | 38830230000297 | TRUE | 3001003-HITCHINS / GRAYSON | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Pri off insulator (upstrain) | Kelly Dr, Grayson, ky
2023 | 2023-08-17 | Ashland | 85749205 | 039985055 | 39830976000002 |  | 3000701-GRAYSBRAN / GRAYSBRAN | Service Work | OH | service: unused or abandoned, blanked meter base |  |  | Foreign | NO | Remove abandoned service drop; xfmr de-energized | Ohio River Rd, Kentucky 41144, USA | 2023-08-18
2023 | 2023-09-07 | Ashland | 86004658 |  | 38830271000283 |  | 3000802-HAYWARD / LAWTON | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker , guys/anchors: loose , damaged , need insulator/marker |  | Foreign | NO | Missing guy guard | Mushroom rd, Lawton, ky | 2023-09-26
2023 | 2023-09-07 | Ashland |  |  | 38830272000234 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole washed out; needs relocated; held by rope tied across creek | Triangle ln, Olive Hill, ky
2023 | 2023-09-07 | Ashland |  |  | 38830296000023 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole washed out; needs relocated | Hwy 1620, Olive hill, ky
2023 | 2023-09-07 | Ashland |  |  | 38830296000090 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Resag neutral | Mushroom rd, Lawton, ky
2023 | 2023-09-07 | Ashland |  |  | 38830297000003 |  | 3000802-HAYWARD / LAWTON | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Pole needs guyed or relocated | Hwy 1620, Olive Hill, ky
2023 | 2023-09-10 | Ashland |  |  | 38830246000035 |  | 3000801-HAYWARD / HALDEMAN | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | Foreign | NO | Remove inactive xfmr and open wire secondary | Hwy 1626, Olive hill , ky
2023 | 2023-09-10 | Ashland |  |  | 38830268B00056 |  | 3000801-HAYWARD / HALDEMAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | Foreign | NO | Needs guy marker | Little Perry rd, Haldeman, ky | 2023-09-10
2023 | 2023-09-10 | Ashland |  |  | 38830316000007 |  | 3000801-HAYWARD / HALDEMAN | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | Missing guy guard | Buffalo branch, Haldeman, ky | 2023-09-10
2023 | 2023-09-29 | Ashland | 86037632 | DKY0122151 | 38830375000090 |  | 3001002-HITCHINS / WILLARD | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Low clearance on service drop, need 35’5 lift pole | 12283 Hwy 201, webbville, ky | 2023-10-17
2023 | 2023-10-02 | Ashland |  |  | 38830454D16012 |  | 3001402-LOUISA / HIGHBOTTOM | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole has butt brace; replace pole | S Lock Ave, Louisa, KY 41230, USA
2023 | 2023-10-11 | Ashland |  |  | 38830251000023 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Blown some arrestor | Nazarene hollow, Grahn, ky
2023 | 2023-10-11 | Ashland |  |  | 38830251000056 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Broken pole | Grahn, KY 41164, USA
2023 | 2023-10-11 | Ashland |  |  | 38830251000095 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Rotted crossarms | Rt 182, Grahn, ky
2023 | 2023-10-11 | Ashland |  |  | 38830251000171 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | conductors: resag no clearance issue, damaged, could cause an outage |  | KPC | NO | 2 spans neutral missing | Aden rd, Grahn, ky
2023 | 2023-10-11 | Ashland | 86518368 | DKY0122969 | 38830251000172 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced pole; also burnt | Aden rd, Grahn, ky | 2024-01-03
2023 | 2023-10-16 | Ashland |  |  | 38830251000072 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining , crossarm/braces: broken/split | crossarm/braces: deteriorated, not rotten |  | KPC | YES | Pole is 1941 will need replaced. Also, cross arms rotted | Stallion lane, Grahn, ky
2023 | 2023-10-17 | Ashland |  |  | 38830227000036 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking , inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive xfmr and secondary pole | Dry Fork Rd, Kentucky 41164, USA
2023 | 2023-10-17 | Ashland |  |  | 38830227000088 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NEEDS ADDITIONAL CHECK | Large woodpecker hole in pole | Sparks rd, Grahn, ky
2023 | 2023-10-17 | Ashland |  |  | 38830227C20091 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Several large woodpecker holes in pole; also no brace pole in field; also no line fuse on pole | Sparks rd, Grahn, ky
2023 | 2023-10-17 | Ashland |  |  | 38830251000208 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Inactive xfmr | Grahn, KY 41164, USA
2023 | 2023-10-17 | Ashland | 86505072 | DKY0123046 | 38830251000221 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole | Church ridge, Grahn, ky
2023 | 2023-10-17 | Ashland |  |  | 38830251000272 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH |  |  | transformers: inactive, NOT near waterway or drainage, NOT damaged or leaking | KPC | NO | Might be able to reach inactive xfmr with long reach bucket | Aden rd, Grahn, ky
2023 | 2023-10-17 | Ashland |  |  | 38830252B20303 |  | 3000601-GRAHN / PLEASANTV | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Trees need cut out of right of way | Big sinking creek rd, Grahn, ky
2023 | 2023-10-17 | Ashland |  |  | 38830275000002 | TRUE | 3000601-GRAHN / PLEASANTV | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Broken crossarm; roadside phase laying on arm but is deenergized | Church ridge, Grahn, ky
2023 | 2023-10-17 | Ashland |  |  | 38830275000005 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive tap; primary gone; remove pole | Church ridge, Grahn, ky
2023 | 2023-10-17 | Ashland | 86617899 | DKY0123085 | 38830275000015 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced pole | Church ridge, Grahn, ky
2023 | 2023-10-18 | Ashland |  |  | 38830226000021 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Inactive primary tap; truck to takeoff pole only; remove 226/22–no truck | Grahn rd, Grahn, ky
2023 | 2023-10-18 | Ashland |  |  | 38830226D20205 |  | 3000601-GRAHN / PLEASANTV | Service Work | OH |  |  | other: customer owned attachment | KPC | NO | Solar light attached to pole; spoke to customer, she said they will remove it tonight; e-mail sent to Debbie Kahn | 2286 rt 182, Grahn ky | 2023-10-25
2023 | 2023-10-18 | Ashland |  |  | 38830250000258 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH |  |  | inactive taps: visual inspection - defect found NOT listed in P1 or P2 | KPC | NO | Remove abandoned secondary pole | Kiser hollow, Grahn,ky
2023 | 2023-10-19 | Ashland |  |  | 38830249000080 |  | 3000601-GRAHN / PLEASANTV | Line Work | OH | crossarm/braces: broken/split |  |  | KPC | NO | Broken crossarm brace | Pipeline rd, Grahn, ky
2023 | 2023-10-19 | Ashland |  |  | 38830250000206 |  | 3000601-GRAHN / PLEASANTV | Service Work | OH |  | guys/anchors: loose, damaged, need insulator/marker |  | KPC | NO | 3 missing guy guards | St rt 3298, Olive hill, ky | 2023-10-19
2023 | 2023-10-23 | Ashland | 86174520 | DKY0122377 | 38830287B00115 |  | 3000202-BIG SANDY / BURNAUGH NORTH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole | Mayo trail rd, Burnaugh, ky
2023 | 2023-10-26 | Ashland | 86666175 | DKY0123277 | 38830248000154 |  | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole brace, secondary pole | Tick ridge fork, Olive Hill, ky
2023 | 2023-10-26 | Ashland |  |  | 38830249000060 |  | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Resag neutral, below joint use mid span; truck to 249/57 | Square lick rd, Olive Hill, ky
2023 | 2023-10-26 | Ashland |  |  | 38830249000065 |  | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Resag neutral, below joint use mid span; can get truck to 249/72 if dry | Depart rd, Olive Hill, ky
2023 | 2023-11-02 | Ashland |  |  | 38830248000073 |  | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Clearance issue with joint use and open wire secondary; need to replace with triplex | Tick Ridge Fork, Kentucky 41164, USA
2023 | 2023-11-02 | Ashland | 86365468 |  | 38830249000094 |  | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Service Work | OH | pole ground: broken or missing - EQUIPMENT GROUND |  |  | KPC | NO | Stolen pole ground; too high to reach | Ben's Run Rd, Olive Hill, KY 41164, USA | 2023-11-22
2023 | 2023-11-02 | Ashland |  |  | 38830273000064 |  | 3103103-OLIVEHILL / WEST CARTER ELEMENTARY | Line Work | OH |  |  |  | KPC | NO | Missing neutral | Patrick Cemetery Rd, Kentucky 41164, USA
2023 | 2023-11-10 | Ashland |  |  | 38830381000082 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH |  | crossarm/braces: deteriorated, not rotten |  | KPC | NO | Crossarm in bad shape | US 23, Louisa, ky
2023 | 2023-11-20 | Ashland | 86546612 | DKY0123047 | 38830356000029 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced at base | Long branch rd, Louisa, ky
2023 | 2023-11-20 | Ashland | 8654673 | DKY0123054 | 38830356000100 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Braced at base | Delong branch, Louisa, ky
2023 | 2023-11-20 | Ashland | 86653666 | DKY0123262 | 38830356000101 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Pole braced at base | Delong branch rd, Louisa, ky
2023 | 2023-11-20 | Ashland |  |  | 38830380000063 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Service Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Low service drop, might be able to resag instead of installing lift pole, 8 ft over yard | N Hwy 3, Louisa,ky
2023 | 2023-11-20 | Ashland |  |  | 38830380000111 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | guys/anchors: broken or missing |  |  | KPC | NO | Missing anchor; long span | Hwy 7-7, Louisa, ky
2023 | 2023-11-20 | Ashland |  |  | 38830380000192 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Forestry | OH |  |  | Forestry - DESCRIBE IN COMMENTS | KPC | NO | Pole engulfed in vines | Rt 3, fallsburg, ky
2023 | 2023-11-21 | Ashland |  |  | 38830379000053 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH |  | lightning arresters/insulators: damaged |  | KPC | NO | Damaged pole top pin insulator | Big Cat Fork Rd, Louisa, ky
2023 | 2023-11-21 | Ashland |  |  | 38830403000047 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH |  |  |  | KPC | NO | Neutral come out of sleeve; 1 span | Big cat fork rd, Louisa, ky
2023 | 2023-11-21 | Ashland |  |  | 38830403000191 |  | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | Foreign | NO | Need secondary pole to reroute secondary; secondary laying on joint use | Shady groves rd, Louisa,ky
2023 | 2023-12-06 | Ashland |  |  | 38830380000113 | TRUE | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral out of clevis | Fallsburg, KY 41230, USA
2023 | 2023-12-06 | Ashland |  |  | 38830380000113 | TRUE | 3000201-BIG SANDY / FALLS BURG SOUTH | Line Work | OH | conductors: proper NESC vertical and horizontal clearance - primary, secondary, service |  |  | KPC | NO | Neutral out of clevis | Fallsburg, KY 41230, USA
2023 | 2023-12-07 | Ashland | 863531157 | DKY0122991 | 38830020D47553 |  | 3000301-BELLEFONT / WESTWOOD | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole | Bellefonte rd, bellefonte, ky
2023 | 2023-12-07 | Ashland | 85540064 | DKY0122800 | 38830247000168 |  | 3103101-OLIVEHILL / GLOBE | Line Work | OH | pole: rotten, washed out, broken/split, burned less than 50% remaining |  |  | KPC | YES | Rotten pole and pushbrace | Globe, ky
2023 | 2023-12-11 | Ashland | 86459403 | DKY0122883 | 39830902A00034 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | YES | Leaning pole | US-23, South Shore, KY, USA
2023 | 2023-12-11 | Ashland |  |  | 39830902A00034 | TRUE | 3002001-South Shore / Siloam | Line Work | OH |  | pole: leaning, burned more than 50% remaining |  | KPC | NO | Leaning pole | US-23, South Shore, KY, USA